## 版本
版本 | 20181112 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S35 | 西濱臨SS | 69 | 69kV | 750 | #1MTR(750) |  | CB | PRI CB 52AS | B2,B3,Element | Status | CB | Open/Close | Y | 1;3 | DI-SP |  | Bay1BbM | B/1Bus | T/1MTR |  |  | 0000 |  |  | 1-00-01 |  |  | #1 TR PRI CB 52AS | 750 CB BOX |  |  | aacb | B3/S35_D1 | [8 empty] | #1MTR 750 | PRI CB 52AS | 投入 |  |  |  |  | DNP | 2 |  | W256_L1.DI [0] |  |  | DI
S35 | 西濱臨SS |  |  | 1MTR | #1MTR |  | 81A |  |  | Status | 81RY | Trip/Normal | Y | 3 | DI-SP | [6 empty] | 0010 |  |  | 1-01-03 |  |  | M1 RY 81A | " |  |  |  | B1/S35_D1 | [8 empty] | #1MTR | 81RY | 動作 |  |  |  |  | DNP | 3 |  | W256_L1.DI [10] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | 760 | #2MTR(760) |  | CB | PRI CB 52AS |  | Status | CB | Open/Close | Y | 1;3 | DI-SP |  | Bay1BbM | B/1Bus | T/2MTR |  |  | 0011 |  |  | 1-01-04 |  |  | #2 TR PRI CB 52AS | 760 CB BOX |  |  | aaeb | B3/S35_D1 | [8 empty] | #2MTR 760 | PRI CB 52AS | 投入 |  |  |  |  | DNP | 4 |  | W256_L1.DI [11] |  |  | DI
S35 | 西濱臨SS |  |  | 2MTR | #2MTR |  | 81A |  |  | Status | 81RY | Trip/Normal | Y | 3 | DI-SP | [6 empty] | 0021 |  |  | 1-02-06 |  |  | M2 RY 81A | " |  |  |  | B1/S35_D1 | [8 empty] | #2MTR | 81RY | 動作 |  |  |  |  | DNP | 5 |  | W256_L1.DI [21] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | 670 | 東林西臨一路(670) |  | 87A |  |  | Status | 87RY | Trip/Normal | Y | 1;3 | DI-SP | [6 empty] | 0022 |  |  | 1-02-07 |  |  | 670東林西臨一路 87A |  |  |  |  | B2/S35_A1 | [8 empty] | 東林西臨一路(670) | 87A | 動作 |  |  |  |  | DNP | 6 |  | W256_L1.DI [22] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | 680 | 東林西臨二路(680) |  | 87A |  |  | Status | 87RY | Trip/Normal | Y | 1;3 | DI-SP | [6 empty] | 0023 |  |  | 1-02-08 |  |  | 680東林西臨二路 87A |  |  |  |  | B2/S35_A1 | [8 empty] | 東林西臨二路(680) | 87A | 動作 |  |  |  |  | DNP | 7 |  | W256_L1.DI [23] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | 670 | 東林西臨一路(670) |  | CB |  |  | Status | CB | Open/Close | Y | 1;3 | DI-SP |  | Bay1BbR | B/1Bus | L/P11S351/T2 |  |  | 0064 |  | 0001 | 1-08-00 |  | 1-01 | 東林西臨一路 (670) 52AS | 670 CB BOX |  |  | aaba | B2/S35_A1 | [8 empty] | 東林西臨一路(670) | CB | 投入 |  |  |  |  | DNP | 8 |  | W256_L1.DI [64] |  | W256_L1.DO [1] | DI
S35 | 西濱臨SS | 69 | 69kV | 670 | 東林西臨一路(670) |  | PHA |  |  | Status | PHA | Trip/Normal | Y | 1;3 | DI-SP | [6 empty] | 0065 |  |  | 1-08-01 |  |  | 東林西臨一路 RY 1PHA | M4PL-[4-1] |  |  |  | B2/S35_A1 | [8 empty] | 東林西臨一路(670) | PHA | 動作 |  |  |  |  | DNP | 9 |  | W256_L1.DI [65] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | 670 | 東林西臨一路(670) |  | GDA |  |  | Status | GDA | Trip/Normal | Y | 1;3 | DI-SP | [6 empty] | 0066 |  |  | 1-08-02 |  |  | 東林西臨一路 RY 1GDA | " |  |  |  | B2/S35_A1 | [8 empty] | 東林西臨一路(670) | GDA | 動作 |  |  |  |  | DNP | 10 |  | W256_L1.DI [66] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | 680 | 東林西臨二路(680) |  | CB |  |  | Status | CB | Open/Close | Y | 1;3 | DI-SP |  | Bay1BbR | B/1Bus | L/P11S352/T2 |  |  | 0067 |  | 0002 | 1-08-03 |  | 1-02 | 東林西臨二路 (680) 52AS | 680 CB BOX |  |  | aada | B2/S35_A1 | [8 empty] | 東林西臨二路(680) | CB | 投入 |  |  |  |  | DNP | 11 |  | W256_L1.DI [67] |  | W256_L1.DO [2] | DI
S35 | 西濱臨SS | 69 | 69kV | 680 | 東林西臨二路(680) |  | PHA |  |  | Status | PHA | Trip/Normal | Y | 1;3 | DI-SP | [6 empty] | 0068 |  |  | 1-08-04 |  |  | 東林西臨二路 RY 2PHA | M4PL-[4-1] |  |  |  | B2/S35_A1 | [8 empty] | 東林西臨二路(680) | PHA | 動作 |  |  |  |  | DNP | 12 |  | W256_L1.DI [68] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | 680 | 東林西臨二路(680) |  | GDA |  |  | Status | GDA | Trip/Normal | Y | 1;3 | DI-SP | [6 empty] | 0069 |  |  | 1-08-05 |  |  | 東林西臨二路 RY 2GDA | " |  |  |  | B2/S35_A1 | [8 empty] | 東林西臨二路(680) | GDA | 動作 |  |  |  |  | DNP | 13 |  | W256_L1.DI [69] |  |  | DI
S35 | 西濱臨SS | 0 |  | RTU | RTU |  | Test_CB |  | B2,B3,Element | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0256 |  | 0000 | 1-30-00 |  | 1-00 | TEST C.B. |  |  |  |  | ELEM/ALL | [8 empty] | TEST | CB | 投入 |  |  |  |  | DNP | 14 |  | W256_L1.DI [256] |  | W256_L1.DO [0] | DI
S35 | 西濱臨SS | 0 |  | RTU | RTU |  | RTU_R_L | RTU | B3 | Status | Remote/Local | Loc/Rem | Y | 3 | DI-SP | [6 empty] | 0257 |  |  | 1-30-01 |  |  | L/R STATUS |  |  |  |  | ELEM/S35_D1 | [8 empty] | RTU | R/L | 現場 |  |  |  |  | DNP | 15 |  | W256_L1.DI [257] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | ComPoint |  |  | 87UL | 87BS |  | Status | 87RY U/L | Lock/Use | Y | 3 | DI-SP | [6 empty] | 0282 |  |  | 1-31-10 |  |  | 69kV 87BS | " |  |  |  | B3/S35_D1 | [8 empty] | 69KV | 87BS | 使用 |  |  |  |  | DNP | 16 |  | W256_L1.DI [282] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | 670 | 東林西臨一路(670) |  | 87CFA | CFA | Element | Status | 87CFA | Fault/Normal | Y | 3 | DI-SP | [6 empty] | 0283 |  |  | 1-31-11 |  |  | 東林西臨一路(670)CFA |  |  |  |  | B2/S35_A1 | [8 empty] | 東林西臨一路(670) | CFA | 動作 |  |  |  |  | DNP | 17 |  | W256_L1.DI [283] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | 670 | 東林西臨一路(670) |  | 87UL1 |  | Element | Status | 第1具87RY U/L | Lock/Use | Y | 3 | DI-SP | [6 empty] | 0284 |  | 0070 | 1-31-12 |  | 1-46 | 東林西臨一路(670)#1 87 U/L |  |  |  |  | B2/S35_A1 | [8 empty] | 東林西臨一路(670) | #187 U/L | 使用 |  |  |  |  | DNP | 18 |  | W256_L1.DI [284] |  | W256_L1.DO [70] | DI
S35 | 西濱臨SS | 69 | 69kV | 670 | 東林西臨一路(670) |  | 87UL2 |  | Element | Status | 第2具87RY U/L | Lock/Use | Y | 3 | DI-SP | [6 empty] | 0285 |  | 0071 | 1-31-13 |  | 1-47 | 東林西臨一路(670)#2 87 U/L |  |  |  |  | B2/S35_A1 | [8 empty] | 東林西臨一路(670) | #287 U/L | 使用 |  |  |  |  | DNP | 19 |  | W256_L1.DI [285] |  | W256_L1.DO [71] | DI
S35 | 西濱臨SS | 69 | 69kV | 670 | 東林西臨一路(670) |  | RYFA |  |  | Status | RYFA | Fault/Normal | Y | 3 | DI-SP | [6 empty] | 0288 |  |  | 1-32-00 |  |  | 東林西臨一路(670) RY 故障 1RYFA | M4PL-[5-4] |  |  |  | B2/S35_A1 | [8 empty] | 東林西臨一路(670) | RYFA | 動作 |  |  |  |  | DNP | 20 |  | W256_L1.DI [288] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | 680 | 東林西臨二路(680) |  | RYFA |  |  | Status | RYFA | Fault/Normal | Y | 3 | DI-SP | [6 empty] | 0289 |  |  | 1-32-01 |  |  | 東林西臨二路(680) RY 故障 2RYFA | " |  |  |  | B2/S35_A1 | [8 empty] | 東林西臨二路(680) | RYFA | 動作 |  |  |  |  | DNP | 21 |  | W256_L1.DI [289] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | ComPoint |  |  | 87A | 87BA | B3 | Status | 87RY | Trip/Normal | Y | 1;3 | DI-SP | [6 empty] | 0290 |  |  | 1-32-02 |  |  | 87BA | " |  |  |  | B3/S35_D1 | [8 empty] | 69KV BUS | 87BA | 動作 |  |  |  |  | DNP | 22 |  | W256_L1.DI [290] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | ComPoint |  |  | UVA | BUS欠壓警報 | B3 | Status | 27/59 RY(欠壓或過壓) | Trip/Normal | Y | 3 | DI-SP | [6 empty] | 0291 |  |  | 1-32-03 |  |  | 69KV BUS VUA | " |  |  |  | B3/S35_D1 | [8 empty] | 69KV BUS欠壓警報 | UVA | 動作 |  |  |  |  | DNP | 23 |  | W256_L1.DI [291] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | ComPoint |  |  | 87CTFA |  | B3 | Status | 87RY CT迴路故障 | Fault/Normal | Y | 3 | DI-SP | [6 empty] | 0292 |  |  | 1-32-04 |  |  | BUS RY CT FAILURE ALARM CTFA | " |  |  |  | B3/S35_D1 | [8 empty] | 69KV BUS | CTFA | 動作 |  |  |  |  | DNP | 24 |  | W256_L1.DI [292] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | ComPoint |  |  | BFS | 87BFA | B3 | Status | 斷路器失靈RY U/L | Lock/Use | Y | 3 | DI-SP | [6 empty] | 0293 |  |  | 1-32-05 |  |  | BUS RY FAILURE ALARM 87BFA | " |  |  |  | B3/S35_D1 | [8 empty] | 69KV BUS | 87BFA | 動作 |  |  |  |  | DNP | 25 |  | W256_L1.DI [293] |  |  | DI
S35 | 西濱臨SS | 0 |  | StaDev | 所內設施 |  | ACB1 | 運轉監視ACB-1 | Element | Status | 所內電源ACB1 | Open/Close | Y | 3 | DI-SP | [6 empty] | 0294 |  |  | 1-32-06 |  |  | 運轉監視 ACB-1 ACB1S | " |  |  |  | B3/S35_D1 | [8 empty] | 運轉監視ACB-1 | ACB1S | 動作 |  |  |  |  | DNP | 26 |  | W256_L1.DI [294] |  |  | DI
S35 | 西濱臨SS | 0 |  | StaDev | 所內設施 |  | ACB2 | 運轉監視ACB-2 | Element | Status | 所內電源ACB2 | Open/Close | Y | 3 | DI-SP | [6 empty] | 0295 |  |  | 1-32-07 |  |  | 運轉監視 ACB-2 ACB2S | " |  |  |  | B3/S35_D1 | [8 empty] | 運轉監視ACB-2 | ACB2S | 動作 |  |  |  |  | DNP | 27 |  | W256_L1.DI [295] |  |  | DI
S35 | 西濱臨SS | 0 |  | StaDev | 所內設施 |  | ACB3 | 運轉監視ACB-3 | Element | Status | 所內電源ACB3 | Open/Close | Y | 3 | DI-SP | [6 empty] | 0296 |  |  | 1-32-08 |  |  | 運轉監視 ACB-3 ACB3S | " |  |  |  | B3/S35_D1 | [8 empty] | 運轉監視ACB-3 | ACB3S | 動作 |  |  |  |  | DNP | 28 |  | W256_L1.DI [296] |  |  | DI
S35 | 西濱臨SS | 0 |  | StaDev | 所內設施 |  | Fire | 火災警報 | Element | Status | 火災警報 | Alarm/Normal | Y | 3 | DI-SP | [6 empty] | 0299 |  |  | 1-32-11 |  |  | FIRE | " |  |  |  | ELEM/S35_D1 | [8 empty] | 火災警報 |  | 動作 |  |  |  |  | DNP | 29 |  | W256_L1.DI [299] |  |  | DI
S35 | 西濱臨SS | 11 | 11kV | M1 | #1MTR(M1) |  | 81UL | 81S | B2,B3 | Status | 81RY U/L | Lock/Use | Y | 5 | DI-SP | [6 empty] | 0304 |  |  | 1-33-00 |  |  | M1 81S | CBOX-1-[503] |  |  |  | B2/S35_D1 | [8 empty] | M1 | 81S | 動作 |  |  |  |  | DNP | 30 |  | W256_L1.DI [304] |  |  | DI
S35 | 西濱臨SS | 11 | 11kV | M2 | #2MTR(M2) |  | 81UL | 81S | B2,B3 | Status | 81RY U/L | Lock/Use | Y | 5 | DI-SP | [6 empty] | 0317 |  |  | 1-33-13 |  |  | M2 81S | CBOX-2-[503] |  |  |  | B2/S35_D1 | [8 empty] | M2 | 81S | 動作 |  |  |  |  | DNP | 31 |  | W256_L1.DI [317] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | 680 | 東林西臨二路(680) |  | 87CFA | CFA | Element | Status | 87CFA | Fault/Normal | Y | 3 | DI-SP | [6 empty] | 0331 |  |  | 1-34-11 |  |  | 東林西臨二路(680)CFA |  |  |  |  | B2/S35_A1 | [8 empty] | 東林西臨二路(680) | CFA | 動作 |  |  |  |  | DNP | 32 |  | W256_L1.DI [331] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | 680 | 東林西臨二路(680) |  | 87UL1 |  | Element | Status | 第1具87RY U/L | Lock/Use | Y | 3 | DI-SP | [6 empty] | 0332 |  | 0073 | 1-34-12 |  | 1-49 | 東林西臨二路(680)#1 87 U/L |  |  |  |  | B2/S35_A1 | [8 empty] | 東林西臨二路(680) | #187 U/L | 使用 |  |  |  |  | DNP | 33 |  | W256_L1.DI [332] |  | W256_L1.DO [73] | DI
S35 | 西濱臨SS | 69 | 69kV | 680 | 東林西臨二路(680) |  | 87UL2 |  | Element | Status | 第2具87RY U/L | Lock/Use | Y | 3 | DI-SP | [6 empty] | 0333 |  | 0074 | 1-34-13 |  | 1-4A | 東林西臨二路(680)#2 87 U/L |  |  |  |  | B2/S35_A1 | [8 empty] | 東林西臨二路(680) | #287 U/L | 使用 |  |  |  |  | DNP | 34 |  | W256_L1.DI [333] |  | W256_L1.DO [74] | DI
S35 | 西濱臨SS | 69 | 69kV | ComPoint |  |  | CBF | CB輕故障 |  | Status | 斷路器輕故障 | Fault/Normal | Y | 5 | DI-SP | [6 empty] | 0340 |  |  | 1-35-04 |  |  | 輕故障 69KV CB CBF | " |  |  |  | B3/S35_D1 | [8 empty] | 69KV CB 輕故障 | CBF | 動作 |  |  |  |  | DNP | 35 |  | W256_L1.DI [340] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | ComPoint |  |  | CBA | CB重故障 |  | Status | 斷路器重故障 | Fault/Normal | Y | 3 | DI-SP | [6 empty] | 0341 |  |  | 1-35-05 |  |  | 重故障 69KV CB CBA | " |  |  |  | B3/S35_D1 | [8 empty] | 69KV CB 重故障 | CBA | 動作 |  |  |  |  | DNP | 36 |  | W256_L1.DI [341] |  |  | DI
S35 | 西濱臨SS | 0 |  | StaDev | 所內設施 |  | PSF | 其他輕故障 |  | Status | 變電所內其他輕故障 | Alarm/Normal | Y | 5 | DI-SP | [6 empty] | 0357 |  |  | 1-36-05 |  |  | 其他輕故障 PSF |  | * |  |  | ELEM/S35_D1 | [8 empty] | 其他輕故障 | PSF | 動作 |  |  |  |  | DNP | 37 |  | W256_L1.DI [357] |  |  | DI
S35 | 西濱臨SS | 0 |  | StaDev | 所內設施 |  | PSA | 其他重故障 |  | Status | 變電所內其他重故障 | Alarm/Normal | Y | 3 | DI-SP | [6 empty] | 0358 |  |  | 1-36-06 |  |  | 其他重故障 PSA |  | * |  |  | ELEM/S35_D1 | [8 empty] | 其他重故障 | PSA | 動作 |  |  |  |  | DNP | 38 |  | W256_L1.DI [358] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | 670 | 東林西臨一路(670) |  | DS1 | 671 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0400 | 401 | 0088 | 1-39-00 | 1-39-01 | 1-58 | 東林西臨二路 ES (682E) AS | 670 CB BOX |  |  |  | B2/S35_A1 | [8 empty] | 東林西臨一路(671) | DS | 投入 |  |  |  |  | DNP | 39 |  | W256_L1.DI [400] | W256_L1.DI [401] | W256_L1.DO [88] | DI
S35 | 西濱臨SS | 69 | 69kV | 670 | 東林西臨一路(670) |  | DS2 | 672 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0402 | 403 | 0089 | 1-39-02 | 1-39-03 | 1-59 | #1 TR DS (751) AS | " |  |  |  | B2/S35_A1 | [8 empty] | 東林西臨一路(672) | DS | 投入 |  |  |  |  | DNP | 40 |  | W256_L1.DI [402] | W256_L1.DI [403] | W256_L1.DO [89] | DI
S35 | 西濱臨SS | 69 | 69kV | 670 | 東林西臨一路(670) |  | ES2 | 672E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0404 | 405 | 0090 | 1-39-04 | 1-39-05 | 1-5A | #2 TR DS (761) AS | " |  |  |  | B2/S35_A1 | [8 empty] | 東林西臨一路(672E) | DS | 投入 |  |  |  |  | DNP | 41 |  | W256_L1.DI [404] | W256_L1.DI [405] | W256_L1.DO [90] | DI
S35 | 西濱臨SS | 69 | 69kV | 680 | 東林西臨二路(680) |  | DS1 | 681 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0406 | 407 | 0091 | 1-39-06 | 1-39-07 | 1-5B | Locate Empty | 680 CB BOX |  |  |  | B2/S35_A1 | [8 empty] | 東林西臨二路(681) | DS | 投入 |  |  |  |  | DNP | 42 |  | W256_L1.DI [406] | W256_L1.DI [407] | W256_L1.DO [91] | DI
S35 | 西濱臨SS | 69 | 69kV | 680 | 東林西臨二路(680) |  | DS2 | 682 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0408 | 409 | 0092 | 1-39-08 | 1-39-09 | 1-5C | Locate Empty | " |  |  |  | B2/S35_A1 | [8 empty] | 東林西臨二路(682) | DS | 投入 |  |  |  |  | DNP | 43 |  | W256_L1.DI [408] | W256_L1.DI [409] | W256_L1.DO [92] | DI
S35 | 西濱臨SS | 69 | 69kV | 680 | 東林西臨二路(680) |  | ES2 | 682E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0410 | 411 | 0093 | 1-39-10 | 1-39-11 | 1-5D | Locate Empty | " |  |  |  | B2/S35_A1 | [8 empty] | 東林西臨二路(682E) | DS | 投入 |  |  |  |  | DNP | 44 |  | W256_L1.DI [410] | W256_L1.DI [411] | W256_L1.DO [93] | DI
S35 | 西濱臨SS | 69 | 69kV | 750 | #1MTR(750) |  | DS1 | 751 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0412 | 413 |  | 1-39-12 | 1-39-13 |  | Locate Empty | 750 CB BOX |  |  |  | B3/S35_D1 | [8 empty] | #1 DTR (751) | DS | 投入 |  |  |  |  | DNP | 45 |  | W256_L1.DI [412] | W256_L1.DI [413] |  | DI
S35 | 西濱臨SS | 69 | 69kV | 760 | #2MTR(760) |  | DS1 | 761 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0414 | 415 |  | 1-39-14 | 1-39-15 |  | Locate Empty | 760 CB BOX |  |  |  | B3/S35_D1 | [8 empty] | #2 DTR (761) | DS | 投入 |  |  |  |  | DNP | 46 |  | W256_L1.DI [414] | W256_L1.DI [415] |  | DI
S35 | 西濱臨SS | 0 |  | StaDev | 所內設施 |  | COMM_LA | 通訊告警狀態 | Element | Status | 警報等級5動作1 | Alarm/Normal | Y | 5 | DI-SP | [17 empty] | B3/S35_D1 | [8 empty] | 通訊 | 告警狀態 | SHUTDOWN |  |  |  |  | DNP | 47 |  | W256_S1.DI [4]
S35 | 西濱臨SS | 69 | 69kV | 670 | 東林西臨一路(670) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S35_A1 | [8 empty] | 670LE | 由現場接地 | 投入 |  |  |  |  | DNP | 48 |  | W256_S1.DI [60]
S35 | 西濱臨SS | 69 | 69kV | 670 | 東林西臨一路(670) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S35_A1 | [8 empty] | 670BE | 由現場接地 | 投入 |  |  |  |  | DNP | 49 |  | W256_S1.DI [61]
S35 | 西濱臨SS | 69 | 69kV | 680 | 東林西臨二路(680) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S35_A1 | [8 empty] | 680LE | 由現場接地 | 投入 |  |  |  |  | DNP | 50 |  | W256_S1.DI [62]
S35 | 西濱臨SS | 69 | 69kV | 680 | 東林西臨二路(680) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S35_A1 | [8 empty] | 680BE | 由現場接地 | 投入 |  |  |  |  | DNP | 51 |  | W256_S1.DI [63]
S35 | 西濱臨SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S35_D1 | [8 empty] | 750BE | 由現場接地 | 投入 |  |  |  |  | DNP | 52 |  | W256_S1.DI [64]
S35 | 西濱臨SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S35_D1 | [8 empty] | 750TE | 由現場接地 | 投入 |  |  |  |  | DNP | 53 |  | W256_S1.DI [65]
S35 | 西濱臨SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S35_D1 | [8 empty] | 760BE | 由現場接地 | 投入 |  |  |  |  | DNP | 54 |  | W256_S1.DI [66]
S35 | 西濱臨SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S35_D1 | [8 empty] | 760TE | 由現場接地 | 投入 |  |  |  |  | DNP | 55 |  | W256_S1.DI [67]
S35 | 西濱臨SS | 69 | 69kV | 69B1E | #1BUS(69B1E) |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb1Eth | B/1Bus | [13 empty] | aaab | B2/S35_A1 | [8 empty] | 69B1E | 由現場接地 | 投入 |  |  |  |  | DNP | 56 |  | W256_S1.DI [68]
S35 | 西濱臨SS | 0 |  | StaDev | 所內設施 |  | ADCL1 |  | Element | MvMoment | No1 AI參考點 10% |  |  |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% TEST |  |  |  |  | B3/S35_D1 | [8 empty] | TEST | #1 10% | COUNT |  |  |  |  | DNP | 57 |  | W256_L1.AI [0] |  |  | AI | [18 empty] | 210 | 0 |  |  |  | 190 | 0
S35 | 西濱臨SS | 0 |  | StaDev | 所內設施 |  | ADCH1 |  | Element | MvMoment | No1 AI參考點 90% |  |  |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% TEST |  |  |  |  | B3/S35_D1 | [8 empty] | TEST | #1 90% | COUNT |  |  |  |  | DNP | 58 |  | W256_L1.AI [1] |  |  | AI | [18 empty] | 1810 | 0 |  |  |  | 1790 | 0
S35 | 西濱臨SS | 69 | 69kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  |  |  | AI |  | BUS |  |  |  |  | 0002 |  |  | 1-82 |  |  | 69KV BUS 6V1+- 電壓 | M4PL-[4-6] |  |  | aaa | B2/S35_A1 | [8 empty] | 69KV #1BUS | 電壓 | KV |  |  |  |  | DNP | 59 |  | W256_L1.AI [2] |  |  | AI | [18 empty] | 71.5 | 0 |  |  |  | 65.5 | 0
S35 | 西濱臨SS | 69 | 69kV | 680 | 東林西臨二路(680) |  | MW |  |  | MvMoment | MW |  |  |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 東林西臨二路(680) 1W+- 瓦 | " |  |  |  | B2/S35_A1 | [8 empty] | 東林西臨二路(680) | 瓦 | MW |  |  |  |  | DNP | 60 |  | W256_L1.AI [5] |  |  | AI | [18 empty] | 0 | 0 |  |  |  | 0 | 0
S35 | 西濱臨SS | 69 | 69kV | 680 | 東林西臨二路(680) |  | MVAR |  |  | MvMoment | MVAR |  |  |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 東林西臨二路(680) 1Q+- 乏 | " |  |  |  | B2/S35_A1 | [8 empty] | 東林西臨二路(680) | 乏 | MVAR |  |  |  |  | DNP | 61 |  | W256_L1.AI [6] |  |  | AI | [18 empty] | 0 | 0 |  |  |  | 0 | 0
S35 | 西濱臨SS | 11 | 11kV | M1 | #1MTR(M1) |  | MW |  | B2,B3 | MvMoment | MW |  |  |  | AI | [6 empty] | 0016 |  |  | 1-90 |  |  | #1 TR 1W+- 瓦 | TO 通訊轉換裝置 |  |  |  | B2/S35_D1 | [8 empty] | #1MTR二次側 | 瓦 | MW |  |  |  |  | DNP | 62 |  | W256_L1.AI [16] |  |  | AI | [18 empty] | 0 | 0 |  |  |  | 0 | 0
S35 | 西濱臨SS | 11 | 11kV | M1 | #1MTR(M1) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  |  |  | AI | [6 empty] | 0017 |  |  | 1-91 |  |  | #1 TR 1Q+- 乏 | " |  |  |  | B2/S35_D1 | [8 empty] | #1MTR二次側 | 乏 | MVAR |  |  |  |  | DNP | 63 |  | W256_L1.AI [17] |  |  | AI | [18 empty] | 4.2 | 0 |  |  |  | -3 | 0
S35 | 西濱臨SS | 11 | 11kV | M2 | #2MTR(M2) |  | MW |  | B2,B3 | MvMoment | MW |  |  |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | #2 TR 2W+- 瓦 | " |  |  |  | B2/S35_D1 | [8 empty] | #2MTR二次側 | 瓦 | MW |  |  |  |  | DNP | 64 |  | W256_L1.AI [55] |  |  | AI | [18 empty] | 0 | 0 |  |  |  | 0 | 0
S35 | 西濱臨SS | 11 | 11kV | M2 | #2MTR(M2) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  |  |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | #2 TR 2Q+- 乏 | " |  |  |  | B2/S35_D1 | [8 empty] | #2MTR二次側 | 乏 | MVAR |  |  |  |  | DNP | 65 |  | W256_L1.AI [56] |  |  | AI | [18 empty] | 4.2 | 0 |  |  |  | -3 | 0
S35 | 西濱臨SS | 11 | 11kV | M1 | #1MTR(M1) |  | CB |  | B2,B3 | Status | CB | Open/Close | Y | 1;3 | DI-SP |  | BayFdrE | B/1BUS | T/1MTR |  |  | 0130 | [9 empty] | aaea | B2/S35_D1 | [8 empty] | #1MTR(M1) | CB | 投入 |  | CDC_Mon1_EMPTY,CDC_Cmd_EMPTY,PointList_NULL |  |  | DNP | 66 |  | 1BIT [900130] |  |  | DI
S35 | 西濱臨SS | 11 | 11kV | M1 | #1MTR(M1) |  | DS |  | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S35_D1 | [8 empty] | #1Mtr(M1) | MCSG模擬設定 | 推入 |  |  |  |  | DNP | 67 |  | VD [900000]
S35 | 西濱臨SS | 11 | 11kV | M1 | #1MTR(M1) |  | ES |  | ADD | Status | ES |  | Y | 7 | DI-SP | [17 empty] | B2/S35_D1 | [8 empty] | #1Mtr(M1) | 由現場接地 | 投入 |  |  |  |  | DNP | 68 |  | VD [900064]
S35 | 西濱臨SS | 11 | 11kV | M2 | #2MTR(M2) |  | CB |  | B2,B3 | Status | CB | Open/Close | Y | 1;3 | DI-SP |  | BayFdrE | B/2BUS | T/2MTR |  |  | 0130 | [9 empty] | aaea | B2/S35_D1 | [8 empty] | #1MTR(M1) | CB | 投入 |  | CDC_Mon1_EMPTY,CDC_Cmd_EMPTY,PointList_NULL |  |  | DNP | 69 |  | 1BIT [900130] |  |  | DI
S35 | 西濱臨SS | 11 | 11kV | M2 | #2MTR(M2) |  | DS |  | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S35_D1 | [8 empty] | #1Mtr(M1) | MCSG模擬設定 | 推入 |  |  |  |  | DNP | 70 |  | VD [900000]
S35 | 西濱臨SS | 11 | 11kV | M2 | #2MTR(M2) |  | ES |  | ADD | Status | ES |  | Y | 7 | DI-SP | [17 empty] | B2/S35_D1 | [8 empty] | #1Mtr(M1) | 由現場接地 | 投入 |  |  |  |  | DNP | 71 |  | VD [900064]
S35 | 西濱臨SS | 11 | 11kV | 1BES | #1BUS(1BES) |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb1Eth | B/1Bus | [13 empty] | aaab | B2/S35_D1 | [8 empty] | 1BES | 由現場接地 | 投入 |  |  |  |  | DNP | 72 |  | W256_S1.DI [68]
S35 | 西濱臨SS | 11 | 11kV | 2BES | #2BUS(2BES) |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb1Eth | B/2Bus | [13 empty] | aaab | B2/S35_D1 | [8 empty] | 1BES | 由現場接地 | 投入 |  |  |  |  | DNP | 73 |  | W256_S1.DI [68]
S35 | 西濱臨SS | 11 | 11kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  |  |  | AI |  | BUS |  |  |  |  | 0098 | [5 empty] | 11KV #1 BUS | 電壓 |  |  | ada | B2/S35_D1 | [8 empty] | Point Empty |  |  |  | CDC_Mon1_EMPTY |  |  | DNP | 74 |  | AI [900098]
S35 | 西濱臨SS | 11 | 11kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  |  |  | AI |  | BUS |  |  |  |  | 0098 | [5 empty] | 11KV #2 BUS | 電壓 |  |  | ada | B2/S35_D1 | [8 empty] | Point Empty |  |  |  | CDC_Mon1_EMPTY |  |  | DNP | 75 |  | AI [900098]

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
S35 | 西濱臨SS | 69 | 69kV | CalcPoint |  |  | Vbs1 |  |  | MvMoment |  |  | Y |  |  |  | B2/S35_A1 | [17 empty] | v_best_69_1 | OPRD1: S35/69/1BUS/V
S35 | 西濱臨SS | 69 | 69kV | CalcPoint |  |  | OPRN1 | [9 empty] | B2/S35_A1 | [17 empty] | pwr_cnd1 | OPRD1: S35/69/CalcPoint/Vbs1; OPRD2: NULL; OPRD3: NULL; OPRD4: NULL; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
S35 | 西濱臨SS | 0 |  | CalcPoint |  |  | OPRN2_MW |  |  | MvMoment |  |  | Y |  | AI |  | B1/S35_D1 | [17 empty] | p_sum_3 | OPRD1: S35/11/M1/MW; OPRD2: S35/11/M2/MW; OPRD3: S35/69/680/MW
S35 | 西濱臨SS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/S35_D1 | [17 empty] | pwr_cnd2 | OPRD1: S35/0/CalcPoint/OPRN2_MW
S35 | 西濱臨SS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/S35_D1 | [17 empty] | none
S35 | 西濱臨SS | 69 | 69kV | CalcPoint |  |  | PWR_FAIL |  |  | Status | 全所停電 | Normal/Alarm | Y | 1 | DI-SP |  | B2/S35_A1 | [17 empty] | pwr_fail | OPRD1: S35/69/CalcPoint/OPRN1; OPRD2: NULL; OPRD3: NULL
S35 | 西濱臨SS | 0 |  | CalcPoint |  |  | PWR_FAIL |  |  | Status | 全所停電 | Normal/Alarm | Y | 1 | DI-SP |  | B1/S35_D1 | [17 empty] | pwr_fail | OPRD1: NULL; OPRD2: S35/0/CalcPoint/OPRN2; OPRD3: S35/0/CalcPoint/PRFL_UL
S35 | 西濱臨SS |  |  | 1MTR | #1MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S35_D1 | [17 empty] | amp_cal | OPRD1: S35/11/M1/MW; OPRD2: S35/11/M1/MVAR; OPRD3: S35/69/CalcPoint/Vbs1
S35 | 西濱臨SS |  |  | 2MTR | #2MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S35_D1 | [17 empty] | amp_cal | OPRD1: S35/11/M2/MW; OPRD2: S35/11/M2/MVAR; OPRD3: S35/69/CalcPoint/Vbs1
S35 | 西濱臨SS | 69 | 69kV | 680 | 東林西臨二路(680) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S35_A1 | [17 empty] | amp_cal | OPRD1: S35/69/680/MW; OPRD2: S35/69/680/MVAR; OPRD3: S35/69/CalcPoint/Vbs1
S35 | 西濱臨SS | 11 | 11kV | 1BUS | #1BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S35_D1 | [17 empty] | bus_uv | OPRD1: S35/11/1BUS/V
S35 | 西濱臨SS | 11 | 11kV | 2BUS | #2BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S35_D1 | [17 empty] | bus_uv | OPRD1: S35/11/2BUS/V
S35 | 西濱臨SS |  |  | 1MTR | #1MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S35_D1 | [17 empty] | va_million | OPRD1: S35/11/M1/MW; OPRD2: S35/11/M1/MVAR
S35 | 西濱臨SS |  |  | 2MTR | #2MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S35_D1 | [17 empty] | va_million | OPRD1: S35/11/M2/MW; OPRD2: S35/11/M2/MVAR
S35 | 西濱臨SS |  |  | 1MTR | #1MTR |  | Loading | [9 empty] | B1/S35_D1 | [17 empty] | tr_loading | OPRD1: S35//1MTR/MVA; OPRD2: 0
S35 | 西濱臨SS |  |  | 2MTR | #2MTR |  | Loading | [9 empty] | B1/S35_D1 | [17 empty] | tr_loading | OPRD1: S35//2MTR/MVA; OPRD2: 0
S35 | 西濱臨SS |  |  | 1MTR | #1MTR |  | PF |  |  | MvMoment | Power Factor |  | Y |  | AI |  | B1/S35_D1 | [17 empty] | pf_cal | OPRD1: S35/11/M1/MW; OPRD2: S35/11/M1/MVAR
S35 | 西濱臨SS |  |  | 2MTR | #2MTR |  | PF |  |  | MvMoment | Power Factor |  | Y |  | AI |  | B1/S35_D1 | [17 empty] | pf_cal | OPRD1: S35/11/M2/MW; OPRD2: S35/11/M2/MVAR
S35 | 西濱臨SS | 0 |  | CalcPoint |  |  | MTR_MW |  |  | MvMoment |  |  | Y |  | AI |  | B1/S35_D1 | [17 empty] | tot_tr_2 | OPRD1: S35/11/M1/MW; OPRD2: S35/11/M2/MW
S35 | 西濱臨SS | 0 |  | CalcPoint |  |  | MTR_MVAR |  |  | MvMoment |  |  | Y |  | AI |  | B1/S35_D1 | [17 empty] | tot_tr_2 | OPRD1: S35/11/M1/MVAR; OPRD2: S35/11/M2/MVAR
S35 | 西濱臨SS | 0 |  | RTU_A1 | RTU |  | RTU_R_L | RTU |  | Status | Remote/Local | Loc/Rem | Y | 3 | DI-SP |  | B3/S35_A1 | [17 empty] | Duplicate_DI | OPRD1: S35/0/RTU/RTU_R_L
S35 | 西濱臨SS | 69 | 69kV | ComPoint_D1 |  |  | 87UL | 87BS |  | Status | 87RY U/L | Lock/Use | Y | 3 | DI-SP |  | B3/S35_D1 | [17 empty] | Duplicate_DI | OPRD1: S35/69/ComPoint/87UL
S35 | 西濱臨SS | 69 | 69kV | ComPoint_D1 |  |  | 87A | 87BA |  | Status | 87RY | Trip/Normal | Y | 1;3 | DI-SP |  | B3/S35_D1 | [17 empty] | Duplicate_DI | OPRD1: S35/69/ComPoint/87A
S35 | 西濱臨SS | 69 | 69kV | ComPoint_D1 |  |  | UVA | BUS欠壓警報 |  | Status | 27/59 RY(欠壓或過壓) | Trip/Normal | Y | 3 | DI-SP |  | B3/S35_D1 | [17 empty] | Duplicate_DI | OPRD1: S35/69/ComPoint/UVA
S35 | 西濱臨SS | 69 | 69kV | ComPoint_D1 |  |  | 87CTFA |  |  | Status | 87RY CT迴路故障 | Fault/Normal | Y | 3 | DI-SP |  | B3/S35_D1 | [17 empty] | Duplicate_DI | OPRD1: S35/69/ComPoint/87CTFA
S35 | 西濱臨SS | 69 | 69kV | ComPoint_D1 |  |  | BFS | 87BFA |  | Status | 斷路器失靈RY U/L | Lock/Use | Y | 3 | DI-SP |  | B3/S35_D1 | [17 empty] | Duplicate_DI | OPRD1: S35/69/ComPoint/BFS
S35 | 西濱臨SS | 0 |  | StaDev_A1 | 所內設施 |  | Fire | 火災警報 |  | Status | 火災警報 | Alarm/Normal | Y | 3 | DI-SP |  | B3/S35_A1 | [17 empty] | Duplicate_DI | OPRD1: S35/0/StaDev/Fire
S35 | 西濱臨SS | 69 | 69kV | ComPoint_D1 |  |  | CBF | CB輕故障 |  | Status | 斷路器輕故障 | Fault/Normal | Y | 5 | DI-SP |  | B3/S35_D1 | [17 empty] | Duplicate_DI | OPRD1: S35/69/ComPoint/CBF
S35 | 西濱臨SS | 69 | 69kV | ComPoint_D1 |  |  | CBA | CB重故障 |  | Status | 斷路器重故障 | Fault/Normal | Y | 3 | DI-SP |  | B3/S35_D1 | [17 empty] | Duplicate_DI | OPRD1: S35/69/ComPoint/CBA
S35 | 西濱臨SS | 0 |  | StaDev_A1 | 所內設施 |  | PSF | 其他輕故障 |  | Status | 變電所內其他輕故障 | Alarm/Normal | Y | 5 | DI-SP |  | B3/S35_A1 | [17 empty] | Duplicate_DI | OPRD1: S35/0/StaDev/PSF
S35 | 西濱臨SS | 0 |  | StaDev_A1 | 所內設施 |  | PSA | 其他重故障 |  | Status | 變電所內其他重故障 | Alarm/Normal | Y | 3 | DI-SP |  | B3/S35_A1 | [17 empty] | Duplicate_DI | OPRD1: S35/0/StaDev/PSA

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S35 | 西濱臨SS |  |  | 1MTR | #1MTR |  | PRI CB 52AS | [14 empty] | 0000 | [19 empty] | #1MTR 750 | PRI CB 52AS | 投入 | S35/69/750/CB |  |  |  | DNP | 2 |  | W256_L1.DI [0] |  |  | DI
S35 | 西濱臨SS |  |  | 1MTR | #1MTR |  | 81A | [14 empty] | 0010 | [19 empty] | #1MTR | 81RY | 動作 | S35//1MTR/81A |  |  |  | DNP | 3 |  | W256_L1.DI [10] |  |  | DI
S35 | 西濱臨SS |  |  | 2MTR | #2MTR |  | PRI CB 52AS | [14 empty] | 0011 | [19 empty] | #2MTR 760 | PRI CB 52AS | 投入 | S35/69/760/CB |  |  |  | DNP | 4 |  | W256_L1.DI [11] |  |  | DI
S35 | 西濱臨SS |  |  | 2MTR | #2MTR |  | 81A | [14 empty] | 0021 | [19 empty] | #2MTR | 81RY | 動作 | S35//2MTR/81A |  |  |  | DNP | 5 |  | W256_L1.DI [21] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | 670 | 東林西臨一路(670) |  | 87A | [14 empty] | 0022 | [19 empty] | 東林西臨一路(670) | 87A | 動作 | S35/69/670/87A |  |  |  | DNP | 6 |  | W256_L1.DI [22] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | 680 | 東林西臨二路(680) |  | 87A | [14 empty] | 0023 | [19 empty] | 東林西臨二路(680) | 87A | 動作 | S35/69/680/87A |  |  |  | DNP | 7 |  | W256_L1.DI [23] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | 670 | 東林西臨一路(670) |  | CB | [14 empty] | 0064 |  | 0001 | [17 empty] | 東林西臨一路(670) | CB | 投入 | S35/69/670/CB |  |  |  | DNP | 8 |  | W256_L1.DI [64] |  | W256_L1.DO [1] | DI
S35 | 西濱臨SS | 69 | 69kV | 670 | 東林西臨一路(670) |  | PHA | [14 empty] | 0065 | [19 empty] | 東林西臨一路(670) | PHA | 動作 | S35/69/670/PHA |  |  |  | DNP | 9 |  | W256_L1.DI [65] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | 670 | 東林西臨一路(670) |  | GDA | [14 empty] | 0066 | [19 empty] | 東林西臨一路(670) | GDA | 動作 | S35/69/670/GDA |  |  |  | DNP | 10 |  | W256_L1.DI [66] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | 680 | 東林西臨二路(680) |  | CB | [14 empty] | 0067 |  | 0002 | [17 empty] | 東林西臨二路(680) | CB | 投入 | S35/69/680/CB |  |  |  | DNP | 11 |  | W256_L1.DI [67] |  | W256_L1.DO [2] | DI
S35 | 西濱臨SS | 69 | 69kV | 680 | 東林西臨二路(680) |  | PHA | [14 empty] | 0068 | [19 empty] | 東林西臨二路(680) | PHA | 動作 | S35/69/680/PHA |  |  |  | DNP | 12 |  | W256_L1.DI [68] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | 680 | 東林西臨二路(680) |  | GDA | [14 empty] | 0069 | [19 empty] | 東林西臨二路(680) | GDA | 動作 | S35/69/680/GDA |  |  |  | DNP | 13 |  | W256_L1.DI [69] |  |  | DI
S35 | 西濱臨SS | Manual input | Manual input | TEST | TEST |  | CB | [14 empty] | 0256 |  | 0000 | [17 empty] | TEST | CB | 投入 | S35/0/RTU/Test_CB |  |  |  | DNP | 14 |  | W256_L1.DI [256] |  | W256_L1.DO [0] | DI
S35 | 西濱臨SS | 0 |  | StaDev | 所內設施 |  | RTU_R_L | RTU | [13 empty] | 0257 | [19 empty] | RTU | R/L | 現場 | S35/0/RTU/RTU_R_L |  |  |  | DNP | 15 |  | W256_L1.DI [257] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | ComPoint |  |  | 87UL | [14 empty] | 0282 | [19 empty] | 69KV | 87BS | 使用 | S35/69/ComPoint/87UL |  |  |  | DNP | 16 |  | W256_L1.DI [282] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | 670 | 東林西臨一路(670) |  | CFA | [14 empty] | 0283 | [19 empty] | 東林西臨一路(670) | CFA | 動作 | S35/69/670/87CFA |  |  |  | DNP | 17 |  | W256_L1.DI [283] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | 670 | 東林西臨一路(670) |  | 1_87UL1 | [14 empty] | 0284 |  | 0070 | [17 empty] | 東林西臨一路(670) | #187 U/L | 使用 | S35/69/670/87UL1 |  |  |  | DNP | 18 |  | W256_L1.DI [284] |  | W256_L1.DO [70] | DI
S35 | 西濱臨SS | 69 | 69kV | 670 | 東林西臨一路(670) |  | 1_87UL2 | [14 empty] | 0285 |  | 0071 | [17 empty] | 東林西臨一路(670) | #287 U/L | 使用 | S35/69/670/87UL2 |  |  |  | DNP | 19 |  | W256_L1.DI [285] |  | W256_L1.DO [71] | DI
S35 | 西濱臨SS | 69 | 69kV | 670 | 東林西臨一路(670) |  | RYFA | [14 empty] | 0288 | [19 empty] | 東林西臨一路(670) | RYFA | 動作 | S35/69/670/RYFA |  |  |  | DNP | 20 |  | W256_L1.DI [288] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | 680 | 東林西臨二路(680) |  | RYFA | [14 empty] | 0289 | [19 empty] | 東林西臨二路(680) | RYFA | 動作 | S35/69/680/RYFA |  |  |  | DNP | 21 |  | W256_L1.DI [289] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | BUS | BUS |  | 87A | [14 empty] | 0290 | [19 empty] | 69KV BUS | 87BA | 動作 | S35/69/ComPoint/87A |  |  |  | DNP | 22 |  | W256_L1.DI [290] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | BUS欠壓警報 | BUS欠壓警報 |  | UVA | [14 empty] | 0291 | [19 empty] | 69KV BUS欠壓警報 | UVA | 動作 | S35/69/ComPoint/UVA |  |  |  | DNP | 23 |  | W256_L1.DI [291] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | BUS | BUS |  | 87CTFA | [14 empty] | 0292 | [19 empty] | 69KV BUS | CTFA | 動作 | S35/69/ComPoint/87CTFA |  |  |  | DNP | 24 |  | W256_L1.DI [292] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | BUS | BUS |  | BFS | [14 empty] | 0293 | [19 empty] | 69KV BUS | 87BFA | 動作 | S35/69/ComPoint/BFS |  |  |  | DNP | 25 |  | W256_L1.DI [293] |  |  | DI
S35 | 西濱臨SS | 0 |  | StaDev | 所內設施 |  | ACB1S | 運轉監視ACB-1 | [13 empty] | 0294 | [19 empty] | 運轉監視ACB-1 | ACB1S | 動作 | S35/0/StaDev/ACB1 |  |  |  | DNP | 26 |  | W256_L1.DI [294] |  |  | DI
S35 | 西濱臨SS | 0 |  | StaDev | 所內設施 |  | ACB2S | 運轉監視ACB-2 | [13 empty] | 0295 | [19 empty] | 運轉監視ACB-2 | ACB2S | 動作 | S35/0/StaDev/ACB2 |  |  |  | DNP | 27 |  | W256_L1.DI [295] |  |  | DI
S35 | 西濱臨SS | 0 |  | StaDev | 所內設施 |  | ACB3S | 運轉監視ACB-3 | [13 empty] | 0296 | [19 empty] | 運轉監視ACB-3 | ACB3S | 動作 | S35/0/StaDev/ACB3 |  |  |  | DNP | 28 |  | W256_L1.DI [296] |  |  | DI
S35 | 西濱臨SS | 0 |  | StaDev | 所內設施 |  |  | 火災警報 | [13 empty] | 0299 | [19 empty] | 火災警報 |  | 動作 | S35/0/StaDev/Fire |  |  |  | DNP | 29 |  | W256_L1.DI [299] |  |  | DI
S35 | 西濱臨SS | 0 |  | StaDev | 所內設施 |  | 81UL | M1 | [13 empty] | 0304 | [19 empty] | M1 | 81S | 動作 | S35/11/M1/81UL |  |  |  | DNP | 30 |  | W256_L1.DI [304] |  |  | DI
S35 | 西濱臨SS | 0 |  | StaDev | 所內設施 |  | 81UL | M2 | [13 empty] | 0317 | [19 empty] | M2 | 81S | 動作 | S35/11/M2/81UL |  |  |  | DNP | 31 |  | W256_L1.DI [317] |  |  | DI | D_KEY
S35 | 西濱臨SS | 69 | 69kV | 680 | 東林西臨二路(680) |  | CFA | [14 empty] | 0331 | [19 empty] | 東林西臨二路(680) | CFA | 動作 | S35/69/680/87CFA |  |  |  | DNP | 32 |  | W256_L1.DI [331] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | 680 | 東林西臨二路(680) |  | 1_87UL1 | [14 empty] | 0332 |  | 0073 | [17 empty] | 東林西臨二路(680) | #187 U/L | 使用 | S35/69/680/87UL1 |  |  |  | DNP | 33 |  | W256_L1.DI [332] |  | W256_L1.DO [73] | DI
S35 | 西濱臨SS | 69 | 69kV | 680 | 東林西臨二路(680) |  | 1_87UL2 | [14 empty] | 0333 |  | 0074 | [17 empty] | 東林西臨二路(680) | #287 U/L | 使用 | S35/69/680/87UL2 |  |  |  | DNP | 34 |  | W256_L1.DI [333] |  | W256_L1.DO [74] | DI
S35 | 西濱臨SS | 69 | 69kV | ComPoint |  |  | CBF | CB輕故障 | [13 empty] | 0340 | [19 empty] | 69KV CB 輕故障 | CBF | 動作 | S35/69/ComPoint/CBF |  |  |  | DNP | 35 |  | W256_L1.DI [340] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | ComPoint |  |  | CBA | CB重故障 | [13 empty] | 0341 | [19 empty] | 69KV CB 重故障 | CBA | 動作 | S35/69/ComPoint/CBA |  |  |  | DNP | 36 |  | W256_L1.DI [341] |  |  | DI
S35 | 西濱臨SS | 0 |  | StaDev | 所內設施 |  | PSF | 其他輕故障 | [13 empty] | 0357 | [19 empty] | 其他輕故障 | PSF | 動作 | S35/0/StaDev/PSF |  |  |  | DNP | 37 |  | W256_L1.DI [357] |  |  | DI
S35 | 西濱臨SS | 0 |  | StaDev | 所內設施 |  | PSA | 其他重故障 | [13 empty] | 0358 | [19 empty] | 其他重故障 | PSA | 動作 | S35/0/StaDev/PSA |  |  |  | DNP | 38 |  | W256_L1.DI [358] |  |  | DI
S35 | 西濱臨SS | 69 | 69kV | 670 | 東林西臨一路(670) |  | DS1 | 671 | [13 empty] | 0400 | 401 | 0088 | [17 empty] | 東林西臨一路(671) | DS | 投入 | S35/69/670/DS1 |  |  |  | DNP | 39 |  | W256_L1.DI [400] | W256_L1.DI [401] | W256_L1.DO [88] | DI
S35 | 西濱臨SS | 69 | 69kV | 670 | 東林西臨一路(670) |  | DS2 | 672 | [13 empty] | 0402 | 403 | 0089 | [17 empty] | 東林西臨一路(672) | DS | 投入 | S35/69/670/DS2 |  |  |  | DNP | 40 |  | W256_L1.DI [402] | W256_L1.DI [403] | W256_L1.DO [89] | DI
S35 | 西濱臨SS | 69 | 69kV | 670 | 東林西臨一路(670) |  | DS2 | 672E | [13 empty] | 0404 | 405 | 0090 | [17 empty] | 東林西臨一路(672E) | DS | 投入 | S35/69/670/ES2 |  |  |  | DNP | 41 |  | W256_L1.DI [404] | W256_L1.DI [405] | W256_L1.DO [90] | DI | D_KEY
S35 | 西濱臨SS | 69 | 69kV | 680 | 東林西臨二路(680) |  | DS1 | 681 | [13 empty] | 0406 | 407 | 0091 | [17 empty] | 東林西臨二路(681) | DS | 投入 | S35/69/680/DS1 |  |  |  | DNP | 42 |  | W256_L1.DI [406] | W256_L1.DI [407] | W256_L1.DO [91] | DI
S35 | 西濱臨SS | 69 | 69kV | 680 | 東林西臨二路(680) |  | DS2 | 682 | [13 empty] | 0408 | 409 | 0092 | [17 empty] | 東林西臨二路(682) | DS | 投入 | S35/69/680/DS2 |  |  |  | DNP | 43 |  | W256_L1.DI [408] | W256_L1.DI [409] | W256_L1.DO [92] | DI
S35 | 西濱臨SS | 69 | 69kV | 680 | 東林西臨二路(680) |  | DS2 | 682E | [13 empty] | 0410 | 411 | 0093 | [17 empty] | 東林西臨二路(682E) | DS | 投入 | S35/69/680/ES2 |  |  |  | DNP | 44 |  | W256_L1.DI [410] | W256_L1.DI [411] | W256_L1.DO [93] | DI | D_KEY
S35 | 西濱臨SS | 69 | 69kV | 750 | #1 DTR (750) |  | DS1 | 751 | [13 empty] | 0412 | 413 | [18 empty] | #1 DTR (751) | DS | 投入 | S35/69/750/DS1 |  |  |  | DNP | 45 |  | W256_L1.DI [412] | W256_L1.DI [413] |  | DI
S35 | 西濱臨SS | 69 | 69kV | 760 | #2 DTR (760) |  | DS1 | 761 | [13 empty] | 0414 | 415 | [18 empty] | #2 DTR (761) | DS | 投入 | S35/69/760/DS1 |  |  |  | DNP | 46 |  | W256_L1.DI [414] | W256_L1.DI [415] |  | DI
S35 | 西濱臨SS | 0 |  | StaDev | 所內設施 |  | 告警狀態 | 通訊 | [33 empty] | 通訊 | 告警狀態 | SHUTDOWN | S35/0/StaDev/1A5Other |  |  |  | DNP | 47 |  | W256_S1.DI [4]
S35 | 西濱臨SS | 0 |  | 670 | 東林西臨一路(670) |  | LE0 | 670LE(非取樣點) | [33 empty] | 670LE | 由現場接地 | 投入 | S35/69/670/LE0 |  |  |  | DNP | 48 |  | W256_S1.DI [60]
S35 | 西濱臨SS | 0 |  | 670 | 東林西臨一路(670) |  | BE0 | 670BE(非取樣點) | [33 empty] | 670BE | 由現場接地 | 投入 | S35/69/670/BE0 |  |  |  | DNP | 49 |  | W256_S1.DI [61]
S35 | 西濱臨SS | 0 |  | 680 | 東林西臨二路(680) |  | LE0 | 680LE(非取樣點) | [33 empty] | 680LE | 由現場接地 | 投入 | S35/69/680/LE0 |  |  |  | DNP | 50 |  | W256_S1.DI [62]
S35 | 西濱臨SS | 0 |  | 680 | 東林西臨二路(680) |  | BE0 | 680BE(非取樣點) | [33 empty] | 680BE | 由現場接地 | 投入 | S35/69/680/BE0 |  |  |  | DNP | 51 |  | W256_S1.DI [63]
S35 | 西濱臨SS | 0 |  | 750 | 750BE |  | BE0 | 750BE(非取樣點) | [33 empty] | 750BE | 由現場接地 | 投入 | S35/69/750/BE0 |  |  |  | DNP | 52 |  | W256_S1.DI [64]
S35 | 西濱臨SS | 0 |  | 750 | 750TE |  | TE0 | 750TE(非取樣點) | [33 empty] | 750TE | 由現場接地 | 投入 | S35/69/750/TE0 |  |  |  | DNP | 53 |  | W256_S1.DI [65]
S35 | 西濱臨SS | 0 |  | 760 | 760BE |  | BE0 | 760BE(非取樣點) | [33 empty] | 760BE | 由現場接地 | 投入 | S35/69/760/BE0 |  |  |  | DNP | 54 |  | W256_S1.DI [66]
S35 | 西濱臨SS | 0 |  | 760 | 760TE |  | TE0 | 760TE(非取樣點) | [33 empty] | 760TE | 由現場接地 | 投入 | S35/69/760/TE0 |  |  |  | DNP | 55 |  | W256_S1.DI [67]
S35 | 西濱臨SS | 0 |  | StaDev | 69B1E |  | BE1 | 69B1E(非取樣點) | [33 empty] | 69B1E | 由現場接地 | 投入 | S35/69/69B1E/BE0 |  |  |  | DNP | 56 |  | W256_S1.DI [68]
S35 | 西濱臨SS | 0 |  | StaDev | 所內設施 |  | #1 10%_COUNT | TEST | [13 empty] | 0000 | [8 empty] | COUNT_0_2000 | [10 empty] | TEST | #1 10% | COUNT | S35/0/StaDev/ADCL1 |  |  |  | DNP | 57 |  | W256_L1.AI [0] |  |  | AI | [18 empty] | 210 | 0 |  |  |  | 190 | 0
S35 | 西濱臨SS | 0 |  | StaDev | 所內設施 |  | #1 90%_COUNT | TEST | [13 empty] | 0001 | [8 empty] | COUNT_0_2000 | [10 empty] | TEST | #1 90% | COUNT | S35/0/StaDev/ADCH1 |  |  |  | DNP | 58 |  | W256_L1.AI [1] |  |  | AI | [18 empty] | 1810 | 0 |  |  |  | 1790 | 0
S35 | 西濱臨SS | 69 | 69kV | 1BUS | #1BUS |  | V | [14 empty] | 0002 | [8 empty] | kV_0_90 | [10 empty] | 69KV #1BUS | 電壓 | KV | S35/69/1BUS/V |  |  |  | DNP | 59 |  | W256_L1.AI [2] |  |  | AI | [18 empty] | 71.5 | 0 |  |  |  | 65.5 | 0
S35 | 西濱臨SS | 69 | 69kV | 680 | 東林西臨二路(680) |  | MW | [14 empty] | 0005 | [8 empty] | MW_0_144 | [10 empty] | 東林西臨二路(680) | 瓦 | MW | S35/69/680/MW |  |  |  | DNP | 60 |  | W256_L1.AI [5] |  |  | AI | [18 empty] | 0 | 0 |  |  |  | 0 | 0
S35 | 西濱臨SS | 69 | 69kV | 680 | 東林西臨二路(680) |  | MVAR | [14 empty] | 0006 | [8 empty] | MVAR_0_144 | [10 empty] | 東林西臨二路(680) | 乏 | MVAR | S35/69/680/MVAR |  |  |  | DNP | 61 |  | W256_L1.AI [6] |  |  | AI | [18 empty] | 0 | 0 |  |  |  | 0 | 0
S35 | 西濱臨SS |  |  | 1MTR二次側 | #1MTR二次側 |  | MW | [14 empty] | 0016 | [8 empty] | MW_0_36 | [10 empty] | #1MTR二次側 | 瓦 | MW | S35/11/M1/MW |  |  |  | DNP | 62 |  | W256_L1.AI [16] |  |  | AI | [18 empty] | 0 | 0 |  |  |  | 0 | 0
S35 | 西濱臨SS |  |  | 1MTR二次側 | #1MTR二次側 |  | MVAR | [14 empty] | 0017 | [8 empty] | MVAR_0_36 | [10 empty] | #1MTR二次側 | 乏 | MVAR | S35/11/M1/MVAR |  |  |  | DNP | 63 |  | W256_L1.AI [17] |  |  | AI | [18 empty] | 4.2 | 0 |  |  |  | -3 | 0
S35 | 西濱臨SS |  |  | 2MTR二次側 | #2MTR二次側 |  | MW | [14 empty] | 0055 | [8 empty] | MW_0_36 | [10 empty] | #2MTR二次側 | 瓦 | MW | S35/11/M2/MW |  |  |  | DNP | 64 |  | W256_L1.AI [55] |  |  | AI | [18 empty] | 0 | 0 |  |  |  | 0 | 0
S35 | 西濱臨SS |  |  | 2MTR二次側 | #2MTR二次側 |  | MVAR | [14 empty] | 0056 | [8 empty] | MVAR_0_36 | [10 empty] | #2MTR二次側 | 乏 | MVAR | S35/11/M2/MVAR |  |  |  | DNP | 65 |  | W256_L1.AI [56] |  |  | AI | [18 empty] | 4.2 | 0 |  |  |  | -3 | 0
S35 | 西濱臨SS | 69 | 69kV | 680 | 東林西臨二路(680) |  | I | [23 empty] | A_0_2000 | [10 empty] | 東林西臨二路(680) | 電流 | A |  |  |  |  | DNP | 66 |  | W256_S1.AI [1] | [21 empty] | 702 | 741 |  |  |  | 0 | 0

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo