## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D01 | 下營DS | 161 | 161kV | 1510 | 新營～下營一路(1510) |  | LE0 | 1510LE |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D01_A1 | [8 empty] | 下營DS.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 2 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 161 | 161kV | 1510 | 新營～下營一路(1510) |  | BE0 | 1510BE |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D01_A1 | [8 empty] | 下營DS.1510BE | 1510BE (非取樣點) | LINE161 | [5 empty] | 3 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 161 | 161kV | 1520 | 新營～下營二路(1520) |  | LE0 | 1520LE |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D01_A1 | [8 empty] | 下營DS.1520LE | 1520LE (非取樣點) | LINE161 | [5 empty] | 4 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 161 | 161kV | 1520 | 新營～下營二路(1520) |  | BE0 | 1520BE |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D01_A1 | [8 empty] | 下營DS.1520BE | 1520BE (非取樣點) | LINE161 | [5 empty] | 5 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 161 | 161kV | 1530 | 下營～威致～官田鋼線(1530) |  | LE0 | 1530LE |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D01_A1 | [8 empty] | 下營DS.1530LE | 1530LE (非取樣點) | LINE161 | [5 empty] | 6 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 161 | 161kV | 1530 | 下營～威致～官田鋼線(1530) |  | BE0 | 1530BE |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D01_A1 | [8 empty] | 下營DS.1530BE | 1530BE (非取樣點) | LINE161 | [5 empty] | 7 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D01_A1 | [8 empty] | 下營DS.1501E | 1501E (非取樣點) | TIE | [5 empty] | 8 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D01_A1 | [8 empty] | 下營DS.1502E | 1502E (非取樣點) | TIE | [5 empty] | 9 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | 1750TE |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D01_A1 | [8 empty] | 下營DS.1750TE | 1750TE (非取樣點) | MTR | [5 empty] | 10 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | 1750BE |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D01_A1 | [8 empty] | 下營DS.1750BE | 1750BE (非取樣點) | MTR | [5 empty] | 11 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | 1760TE |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D01_A1 | [8 empty] | 下營DS.1760TE | 1760TE (非取樣點) | MTR | [5 empty] | 12 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | 1760BE |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D01_A1 | [8 empty] | 下營DS.1760BE | 1760BE (非取樣點) | MTR | [5 empty] | 13 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | D1 | 311 |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D01_A1 | [8 empty] | 下營DS.311 | 311 (非取樣點) | MTR | [5 empty] | 14 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | E1 | 311E | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D01_A1 | [8 empty] | 下營DS.311E | 311E (非取樣點) | MTR | [5 empty] | 15 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | D1 | 321 |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D01_A1 | [8 empty] | 下營DS.321 | 321 (非取樣點) | MTR | [5 empty] | 16 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | E1 | 321E | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D01_A1 | [8 empty] | 下營DS.321E | 321E (非取樣點) | MTR | [5 empty] | 17 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | D1 | 331 |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D01_A1 | [8 empty] | 下營DS.331 | 331 (非取樣點) | MTR | [5 empty] | 18 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | E1 | 331E | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D01_A1 | [8 empty] | 下營DS.331E | 331E (非取樣點) | MTR | [5 empty] | 19 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | D1 | 341 |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D01_A1 | [8 empty] | 下營DS.341 | 341 (非取樣點) | MTR | [5 empty] | 20 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | E1 | 341E | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D01_A1 | [8 empty] | 下營DS.341E | 341E (非取樣點) | MTR | [5 empty] | 21 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 11 | 11kV | 100 | TIE(100) |  | E1 | 101E | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D01_A1 | [8 empty] | 下營DS.101E | 101E (非取樣點) | TIE | [5 empty] | 22 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 11 | 11kV | 100 | TIE(100) |  | E2 | 102E | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D01_A1 | [8 empty] | 下營DS.102E | 102E (非取樣點) | TIE | [5 empty] | 23 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 11 | 11kV | 100 | TIE(100) |  | D1 | 101 |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D01_A1 | [8 empty] | 下營DS.101 | 101 (非取樣點) | TIE | [5 empty] | 24 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | 100 | TIE(100) |  | D2 | 102 |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D01_A1 | [8 empty] | 下營DS.102 | 102 (非取樣點) | TIE | [5 empty] | 25 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | 200 | TIE(200) |  | E1 | 201E | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D01_A1 | [8 empty] | 下營DS.201E | 201E (非取樣點) | TIE | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 22 | 22kV | 200 | TIE(200) |  | E2 | 202E | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D01_A1 | [8 empty] | 下營DS.202E | 202E (非取樣點) | TIE | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 22 | 22kV | 200 | TIE(200) |  | D1 | 201 |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D01_A1 | [8 empty] | 下營DS.201 | 201 (非取樣點) | TIE | [5 empty] | 28 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | 200 | TIE(200) |  | D2 | 202 |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D01_A1 | [8 empty] | 下營DS.202 | 202 (非取樣點) | TIE | [5 empty] | 29 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | 210 | #1SC(210) |  | E1 | 211E | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D01_A1 | [8 empty] | 下營DS.211E | 211E (非取樣點) | SC | [5 empty] | 30 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 11 | 11kV | 210 | #1SC(210) |  | D1 | 211 |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D01_A1 | [8 empty] | 下營DS.211 | 211 (非取樣點) | SC | [5 empty] | 31 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | 220 | #2SC(220) |  | E1 | 221E | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D01_A1 | [8 empty] | 下營DS.221E | 221E (非取樣點) | SC | [5 empty] | 32 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 22 | 22kV | 220 | #2SC(220) |  | D1 | 221 |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D01_A1 | [8 empty] | 下營DS.221 | 221 (非取樣點) | SC | [5 empty] | 33 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | 230 | #3SC(230) |  | E1 | 231E | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D01_A1 | [8 empty] | 下營DS.231E | 231E (非取樣點) | SC | [5 empty] | 34 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 11 | 11kV | 230 | #3SC(230) |  | D1 | 231 |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D01_A1 | [8 empty] | 下營DS.231 | 231 (非取樣點) | SC | [5 empty] | 35 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | 240 | #4SC(240) |  | E1 | 241E | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D01_A1 | [8 empty] | 下營DS.241E | 241E (非取樣點) | SC | [5 empty] | 36 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 22 | 22kV | 240 | #4SC(240) |  | D1 | 241 |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D01_A1 | [8 empty] | 下營DS.241 | 241 (非取樣點) | SC | [5 empty] | 37 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | 390 | #1SSTR(390) |  | D1 | 391 | B3 | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D01_A1 | [8 empty] | 下營DS.391 | 391 (非取樣點) | OTHER | [5 empty] | 38 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | 390 | #1SSTR(390) |  | E1 | 391E | B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D01_A1 | [8 empty] | 下營DS.391E | 391E (非取樣點) | OTHER | [5 empty] | 39 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 22 | 22kV | 490 | #2SSTR(490) |  | D1 | 491 | B3 | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D01_A1 | [8 empty] | 下營DS.491 | 491 (非取樣點) | OTHER | [5 empty] | 40 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | 490 | #2SSTR(490) |  | E1 | 491E | B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D01_A1 | [8 empty] | 下營DS.491E | 491E (非取樣點) | OTHER | [5 empty] | 41 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 11 | 11kV | VK21 | 營一線(VK21) |  | DS | VK21_DS | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK21_DS | VK21_DS (非取樣點) | FEEDER | [5 empty] | 42 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | VK21 | 營一線(VK21) |  | ES | VK21_ES | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK21_ES | VK21_ES (非取樣點) | FEEDER | [5 empty] | 43 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 11 | 11kV | VK22 | 營二線(VK22) |  | DS | VK22_DS | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK22_DS | VK22_DS (非取樣點) | FEEDER | [5 empty] | 44 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | VK22 | 營二線(VK22) |  | ES | VK22_ES | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK22_ES | VK22_ES (非取樣點) | FEEDER | [5 empty] | 45 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 11 | 11kV | VK23 | 營三線(VK23) |  | DS | VK23_DS | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK23_DS | VK23_DS (非取樣點) | FEEDER | [5 empty] | 46 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | VK23 | 營三線(VK23) |  | ES | VK23_ES | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK23_ES | VK23_ES (非取樣點) | FEEDER | [5 empty] | 47 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 11 | 11kV | VK24 | 營正線(VK24) |  | DS | VK24_DS | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK24_DS | VK24_DS (非取樣點) | FEEDER | [5 empty] | 48 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | VK24 | 營正線(VK24) |  | ES | VK24_ES | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK24_ES | VK24_ES (非取樣點) | FEEDER | [5 empty] | 49 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 11 | 11kV | VK25 | 營五線(VK25) |  | DS | VK25_DS | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK25_DS | VK25_DS (非取樣點) | FEEDER | [5 empty] | 50 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | VK25 | 營五線(VK25) |  | ES | VK25_ES | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK25_ES | VK25_ES (非取樣點) | FEEDER | [5 empty] | 51 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 22 | 22kV | VK51 | 營五十一線(VK51) |  | DS | VK51_DS | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK51_DS | VK51_DS (非取樣點) | FEEDER | [5 empty] | 52 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | VK51 | 營五十一線(VK51) |  | ES | VK51_ES | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK51_ES | VK51_ES (非取樣點) | FEEDER | [5 empty] | 53 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 22 | 22kV | VK52 | 營五十二線(VK52) |  | DS | VK52_DS | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK52_DS | VK52_DS (非取樣點) | FEEDER | [5 empty] | 54 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | VK52 | 營五十二線(VK52) |  | ES | VK52_ES | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK52_ES | VK52_ES (非取樣點) | FEEDER | [5 empty] | 55 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 22 | 22kV | VK53 | 營五十三線(VK53) |  | DS | VK53_DS | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK53_DS | VK53_DS (非取樣點) | FEEDER | [5 empty] | 56 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | VK53 | 營五十三線(VK53) |  | ES | VK53_ES | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK53_ES | VK53_ES (非取樣點) | FEEDER | [5 empty] | 57 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 22 | 22kV | VK54 | 營五十四線(VK54) |  | DS | VK54_DS | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK54_DS | VK54_DS (非取樣點) | FEEDER | [5 empty] | 58 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | VK54 | 營五十四線(VK54) |  | ES | VK54_ES | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK54_ES | VK54_ES (非取樣點) | FEEDER | [5 empty] | 59 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 22 | 22kV | VK55 | 營五十五線(VK55) |  | DS | VK55_DS | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK55_DS | VK55_DS (非取樣點) | FEEDER | [5 empty] | 60 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | VK55 | 營五十五線(VK55) |  | ES | VK55_ES | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK55_ES | VK55_ES (非取樣點) | FEEDER | [5 empty] | 61 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 11 | 11kV | VK30 | 營十線(VK30) |  | DS | VK30_DS | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK30_DS | VK30_DS (非取樣點) | FEEDER | [5 empty] | 62 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | VK30 | 營十線(VK30) |  | ES | VK30_ES | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK30_ES | VK30_ES (非取樣點) | FEEDER | [5 empty] | 63 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 11 | 11kV | VK29 | 營九線(VK29) |  | DS | VK29_DS | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK29_DS | VK29_DS (非取樣點) | FEEDER | [5 empty] | 64 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | VK29 | 營九線(VK29) |  | ES | VK29_ES | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK29_ES | VK29_ES (非取樣點) | FEEDER | [5 empty] | 65 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 11 | 11kV | VK28 | 營八線(VK28) |  | DS | VK28_DS | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK28_DS | VK28_DS (非取樣點) | FEEDER | [5 empty] | 66 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | VK28 | 營八線(VK28) |  | ES | VK28_ES | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK28_ES | VK28_ES (非取樣點) | FEEDER | [5 empty] | 67 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 11 | 11kV | VK27 | 營七線(VK27) |  | DS | VK27_DS | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK27_DS | VK27_DS (非取樣點) | FEEDER | [5 empty] | 68 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | VK27 | 營七線(VK27) |  | ES | VK27_ES | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK27_ES | VK27_ES (非取樣點) | FEEDER | [5 empty] | 69 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 11 | 11kV | VK26 | 營六線(VK26) |  | DS | VK26_DS | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK26_DS | VK26_DS (非取樣點) | FEEDER | [5 empty] | 70 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | VK26 | 營六線(VK26) |  | ES | VK26_ES | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK26_ES | VK26_ES (非取樣點) | FEEDER | [5 empty] | 71 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 22 | 22kV | VK60 | 營六十線(VK60) |  | DS | VK60_DS | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK60_DS | VK60_DS (非取樣點) | FEEDER | [5 empty] | 72 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | VK60 | 營六十線(VK60) |  | ES | VK60_ES | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK60_ES | VK60_ES (非取樣點) | FEEDER | [5 empty] | 73 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 22 | 22kV | VK59 | 營五十九線(VK59) |  | DS | VK59_DS | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK59_DS | VK59_DS (非取樣點) | FEEDER | [5 empty] | 74 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | VK59 | 營五十九線(VK59) |  | ES | VK59_ES | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK59_ES | VK59_ES (非取樣點) | FEEDER | [5 empty] | 75 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 22 | 22kV | VK58 | 營五十八線(VK58) |  | DS | VK58_DS | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK58_DS | VK58_DS (非取樣點) | FEEDER | [5 empty] | 76 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | VK58 | 營五十八線(VK58) |  | ES | VK58_ES | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK58_ES | VK58_ES (非取樣點) | FEEDER | [5 empty] | 77 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 22 | 22kV | VK57 | 營五十七線(VK57) |  | DS | VK57_DS | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK57_DS | VK57_DS (非取樣點) | FEEDER | [5 empty] | 78 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | VK57 | 營五十七線(VK57) |  | ES | VK57_ES | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK57_ES | VK57_ES (非取樣點) | FEEDER | [5 empty] | 79 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 22 | 22kV | VK56 | 營五十六線(VK56) |  | DS | VK56_DS | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK56_DS | VK56_DS (非取樣點) | FEEDER | [5 empty] | 80 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | VK56 | 營五十六線(VK56) |  | ES | VK56_ES | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D01_D1 | [8 empty] | 下營DS.VK56_ES | VK56_ES (非取樣點) | FEEDER | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | 15B1E | B2,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aaaz | B2/D01_A1 | [8 empty] | 下營DS.15B1E | 15B1E (非取樣點) | BUS | [5 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | 15B2E | B2,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/2Bus | [13 empty] | aaaz | B2/D01_A1 | [8 empty] | 下營DS.15B2E | 15B2E (非取樣點) | BUS | [5 empty] | 83 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 161 | 161kV | 1BUS | #1BUS |  | V |  | B3 | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 161KV_No.1BUS KV_Vbc | KV | 16387 | kV_-210_210(-2000_2000) | aaa | B2/D01_A1 | [8 empty] | 下營DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | [5 empty] | 84 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D01 | 下營DS | 161 | 161kV | 2BUS | #2BUS |  | V |  | B3 | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0003 |  |  | 1-83 |  |  | 161KV_No.2BUS KV_Vbc | KV | 16388 | kV_-210_210(-2000_2000) | aab | B2/D01_A1 | [8 empty] | 下營DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | [5 empty] | 85 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D01 | 下營DS | 161 | 161kV | 1510 | 新營～下營一路(1510) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 1510新營下營一路_MW | MW | 16389 | MW_-560_560(-2000_2000) |  | B2/D01_A1 | [8 empty] | 下營DS.1510_MW | 新營下營一路 MW | LINE161 | [5 empty] | 86 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D01 | 下營DS | 161 | 161kV | 1510 | 新營～下營一路(1510) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 1510新營下營一路_MVAR | MVAR | 16390 | MVAR_-560_560(-2000_2000) |  | B2/D01_A1 | [8 empty] | 下營DS.1510_MVAR | 新營下營一路 MVAR | LINE161 | [5 empty] | 87 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D01 | 下營DS | 161 | 161kV | 1520 | 新營～下營二路(1520) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 1520新營下營二路_MW | MW | 16391 | MW_-560_560(-2000_2000) |  | B2/D01_A1 | [8 empty] | 下營DS.1520_MW | 新營下營二路 MW | LINE161 | [5 empty] | 88 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D01 | 下營DS | 161 | 161kV | 1520 | 新營～下營二路(1520) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 1520新營下營二路_MVAR | MVAR | 16392 | MVAR_-560_560(-2000_2000) |  | B2/D01_A1 | [8 empty] | 下營DS.1520_MVAR | 新營下營二路 MVAR | LINE161 | [5 empty] | 89 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D01 | 下營DS | 161 | 161kV | 1530 | 下營～威致～官田鋼線(1530) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | 1530下營威致官田鋼線_MW | MW | 16393 | MW_-560_560(-2000_2000) |  | B2/D01_A1 | [8 empty] | 下營DS.1530_MW | 下營威致官田鋼 MW | LINE161 | [5 empty] | 90 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D01 | 下營DS | 161 | 161kV | 1530 | 下營～威致～官田鋼線(1530) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 1530下營威致官田鋼線_MVAR | MVAR | 16394 | MVAR_-560_560(-2000_2000) |  | B2/D01_A1 | [8 empty] | 下營DS.1530_MVAR | 下營威致官田鋼 MVAR | LINE161 | [5 empty] | 91 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D01 | 下營DS | 161 | 161kV | 1510 | 新營～下營一路(1510) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0016 |  |  | 1-90 |  |  | 1510新營下營一路_LPD | LPD |  | kV_-210_210(-2000_2000) |  | B2/D01_A1 | [8 empty] | 下營DS.1510LPD_KV | 新營下營一路(1510) LPD KV | LINE161 | [5 empty] | 92 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D01 | 下營DS | 161 | 161kV | 1520 | 新營～下營二路(1520) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0017 |  |  | 1-91 |  |  | 1520新營下營二路_LPD | LPD |  | kV_-210_210(-2000_2000) |  | B2/D01_A1 | [8 empty] | 下營DS.1520LPD_KV | 新營下營二路(1520) LPD KV | LINE161 | [5 empty] | 93 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D01 | 下營DS | 161 | 161kV | 1530 | 下營～威致～官田鋼線(1530) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | 1530下營威致官田鋼線_LPD | LPD |  | kV_-210_210(-2000_2000) |  | B2/D01_A1 | [8 empty] | 下營DS.1530LPD_KV | 下營威致官田鋼(1530) LPD KV | LINE161 | [5 empty] | 94 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D01 | 下營DS | 161 | 161kV | 1500 | TIE(1500) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0024 |  |  | 1-98 |  |  | 1500_AMP | AMP | 16409 | A_-2000_2000(-2000_2000) |  | B2/D01_A1 | [8 empty] | 下營DS.1500TIE_AMP | 1500TIE AMP | TIE | [5 empty] | 95 |  |  |  |  | AI | [5 empty] | C20R1600 | 1520 | 1600 | 1760 | 1968 | 2.27 | -1520 | -1600 | -1760 | -1968 | 1 | 0.01 | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | DCV_P |  |  | MvMoment | 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | 直流P電源電壓 |  |  | kV_-150_150(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.直流P電源電壓 | 直流P電源電壓 | OTHER | [5 empty] | 96 |  |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 | 0.01 | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | DCV_N |  |  | MvMoment | 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | 直流N電源電壓 |  |  | kV_-150_150(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.直流N電源電壓 | 直流N電源電壓 | OTHER | [5 empty] | 97 |  |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 | 0.01 | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D01 | 下營DS |  |  | 1DTR | #1DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | No.1DTR_OIL | ℃ | 16417 | OIL_-120_120(-2000_2000) |  | B1/D01_A1 | [8 empty] | 下營DS.#1DTR_OIL | #1DTR 油溫 | MTR | [5 empty] | 98 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D01 | 下營DS |  |  | 1DTR(A) | #1DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | No.1DTR(A)_TAP | * | 16418 | TAP_-8.5_8.5(0_2000) |  | B1/D01_A1 | [8 empty] | 下營DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | [5 empty] | 99 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D01 | 下營DS |  |  | 1DTR(B) | #1DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | No.1DTR(B)_TAP | * | 16419 | TAP_-8.5_8.5(0_2000) |  | B1/D01_A1 | [8 empty] | 下營DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | [5 empty] | 100 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D01 | 下營DS |  |  | 1DTR(A) | #1DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | No.1DTR(A)_COIL | ℃ | 16420 | COIL_-120_120(-2000_2000) |  | B1/D01_A1 | [8 empty] | 下營DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | [5 empty] | 101 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D01 | 下營DS |  |  | 1DTR(B) | #1DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | No.1DTR(B)_COIL | ℃ | 16421 | COIL_-120_120(-2000_2000) |  | B1/D01_A1 | [8 empty] | 下營DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | [5 empty] | 102 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D01 | 下營DS |  |  | 2DTR | #2DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | No.2DTR_OIL | ℃ | 16422 | OIL_-120_120(-2000_2000) |  | B1/D01_A1 | [8 empty] | 下營DS.#2DTR_OIL | #2DTR 油溫 | MTR | [5 empty] | 103 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D01 | 下營DS |  |  | 2DTR(A) | #2DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | No.2DTR(A)_TAP | * | 16423 | TAP_-8.5_8.5(0_2000) |  | B1/D01_A1 | [8 empty] | 下營DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | [5 empty] | 104 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D01 | 下營DS |  |  | 2DTR(B) | #2DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | No.2DTR(B)_TAP | * | 16424 | TAP_-8.5_8.5(0_2000) |  | B1/D01_A1 | [8 empty] | 下營DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | [5 empty] | 105 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D01 | 下營DS |  |  | 2DTR(A) | #2DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | No.2DTR(A)_COIL | ℃ | 16425 | COIL_-120_120(-2000_2000) |  | B1/D01_A1 | [8 empty] | 下營DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | [5 empty] | 106 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D01 | 下營DS |  |  | 2DTR(B) | #2DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | No.2DTR(B)_COIL | ℃ | 16426 | COIL_-120_120(-2000_2000) |  | B1/D01_A1 | [8 empty] | 下營DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | [5 empty] | 107 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D01 | 下營DS | 11 | 11kV | 1ABUS | #1ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0066 |  |  | 1-C2 |  |  | 11KV_(PT-1A)_Va | KV | 16451 | kV_-9_9(-2000_2000) | aaa | B3/D01_A1 | [8 empty] | 下營DS.11KV#1ABUS_KV | 11KV #1ABUS KV | BUS | [5 empty] | 108 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D01 | 下營DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | 11KV_310_W | KVAR | 16452 | MW_-54_54(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | [5 empty] | 109 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.054 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.054000 | 0.010000
D01 | 下營DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | 11KV_310_Var | KVAR | 16453 | MVAR_-36_36(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | [5 empty] | 110 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.036 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.036000 | 0.010000
D01 | 下營DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | 11KV_310_A1 | AMP | 16454 | A_-3000_3000(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | [5 empty] | 111 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | 11KV_310_A2 | AMP | 16455 | A_-3000_3000(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | [5 empty] | 112 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | 11KV_310_A3 | AMP | 16456 | A_-3000_3000(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | [5 empty] | 113 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 1BBUS | #1BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0072 |  |  | 1-C8 |  |  | 23KV_(PT-1B)_Va | KV | 16457 | kV_-18_18(-2000_2000) | baa | B3/D01_A1 | [8 empty] | 下營DS.23KV#1BBUS_KV | 23KV #1BBUS KV | BUS | [5 empty] | 114 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D01 | 下營DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | 23KV_320_W | KVAR | 16458 | MW_-108_108(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | [5 empty] | 115 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D01 | 下營DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | 23KV_320_Var | KVAR | 16459 | MVAR_-72_72(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | [5 empty] | 116 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D01 | 下營DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | 23KV_320_A1 | AMP | 16460 | A_-3000_3000(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | [5 empty] | 117 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | 23KV_320_A2 | AMP | 16461 | A_-3000_3000(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | [5 empty] | 118 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | 23KV_320_A3 | AMP | 16462 | A_-3000_3000(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | [5 empty] | 119 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 2ABUS | #2ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0078 |  |  | 1-CE |  |  | 11KV_(PT-2A)_Va | KV | 16463 | kV_-9_9(-2000_2000) | aba | B3/D01_A1 | [8 empty] | 下營DS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS | [5 empty] | 120 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D01 | 下營DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | 11KV_330_W | KVAR | 16464 | MW_-54_54(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | [5 empty] | 121 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.054 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.054000 | 0.010000
D01 | 下營DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | 11KV_330_Var | KVAR | 16465 | MVAR_-36_36(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | [5 empty] | 122 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.036 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.036000 | 0.010000
D01 | 下營DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | 11KV_330_A1 | AMP | 16466 | A_-3000_3000(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | [5 empty] | 123 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | 11KV_330_A2 | AMP | 16467 | A_-3000_3000(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | [5 empty] | 124 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | 11KV_330_A3 | AMP | 16468 | A_-3000_3000(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | [5 empty] | 125 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 2BBUS | #2BBUS |  | V |  | B2 | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0084 |  |  | 1-D4 |  |  | 23KV_(PT-2B)_Va | KV | 16469 | kV_-18_18(-2000_2000) | bba | B3/D01_A1 | [8 empty] | 下營DS.23KV#2BBUS_KV | 23KV #2BBUS KV | BUS | [5 empty] | 126 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D01 | 下營DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | 23KV_340_W | KVAR | 16470 | MW_-108_108(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | [5 empty] | 127 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D01 | 下營DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | 23KV_340_Var | KVAR | 16471 | MVAR_-72_72(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | [5 empty] | 128 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D01 | 下營DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | 23KV_340_A1 | AMP | 16472 | A_-3000_3000(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | [5 empty] | 129 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | 23KV_340_A2 | AMP | 16473 | A_-3000_3000(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | [5 empty] | 130 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | 23KV_340_A3 | AMP | 16474 | A_-3000_3000(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | [5 empty] | 131 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 100 | TIE(100) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | 11KV_100_A1 | AMP | 16475 | A_-2000_2000(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.11KV_100_A1 | 11KV 100 R相AMP | TIE | [5 empty] | 132 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 100 | TIE(100) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | 11KV_100_A2 | AMP | 16476 | A_-2000_2000(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.11KV_100_A2 | 11KV 100 S相AMP | TIE | [5 empty] | 133 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 100 | TIE(100) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | 11KV_100_A3 | AMP | 16477 | A_-2000_2000(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.11KV_100_A3 | 11KV 100 T相AMP | TIE | [5 empty] | 134 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 200 | TIE(200) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | 23KV_200_A1 | AMP | 16478 | A_-2000_2000(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.23KV_200_A1 | 23KV 200 R相AMP | TIE | [5 empty] | 135 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 200 | TIE(200) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | 23KV_200_A2 | AMP | 16479 | A_-2000_2000(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.23KV_200_A2 | 23KV 200 S相AMP | TIE | [5 empty] | 136 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 200 | TIE(200) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | 23KV_200_A3 | AMP | 16480 | A_-2000_2000(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.23KV_200_A3 | 23KV 200 T相AMP | TIE | [5 empty] | 137 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK21 | 營一線(VK21) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | 11KV_VK21_Var | KVAR | 16515 | KVAR_-9000_9000(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營一線KVAR | 11KV營一線 KVAR | FEEDER | [5 empty] | 138 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK21 | 營一線(VK21) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | 11KV_VK21_A1 | AMP | 16516 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營一線A1 | 11KV營一線 R相AMP | FEEDER | [5 empty] | 139 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK21 | 營一線(VK21) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | 11KV_VK21_A2 | AMP | 16517 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營一線A2 | 11KV營一線 S相AMP | FEEDER | [5 empty] | 140 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK21 | 營一線(VK21) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0133 |  |  | 2-85 |  |  | 11KV_VK21_A3 | AMP | 16518 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營一線A3 | 11KV營一線 T相AMP | FEEDER | [5 empty] | 141 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK21 | 營一線(VK21) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | 11KV_VK21_A0 | AMP | 16519 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營一線A0 | 11KV營一線 N相AMP | FEEDER | [5 empty] | 142 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK22 | 營二線(VK22) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0135 |  |  | 2-87 |  |  | 11KV_VK22_Var | KVAR | 16520 | KVAR_-9000_9000(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營二線KVAR | 11KV營二線 KVAR | FEEDER | [5 empty] | 143 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK22 | 營二線(VK22) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0136 |  |  | 2-88 |  |  | 11KV_VK22_A1 | AMP | 16521 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營二線A1 | 11KV營二線 R相AMP | FEEDER | [5 empty] | 144 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK22 | 營二線(VK22) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0137 |  |  | 2-89 |  |  | 11KV_VK22_A2 | AMP | 16522 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營二線A2 | 11KV營二線 S相AMP | FEEDER | [5 empty] | 145 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK22 | 營二線(VK22) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0138 |  |  | 2-8A |  |  | 11KV_VK22_A3 | AMP | 16523 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營二線A3 | 11KV營二線 T相AMP | FEEDER | [5 empty] | 146 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK22 | 營二線(VK22) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0139 |  |  | 2-8B |  |  | 11KV_VK22_A0 | AMP | 16524 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營二線A0 | 11KV營二線 N相AMP | FEEDER | [5 empty] | 147 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK23 | 營三線(VK23) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0140 |  |  | 2-8C |  |  | 11KV_VK23_Var | KVAR | 16525 | KVAR_-9000_9000(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營三線KVAR | 11KV營三線 KVAR | FEEDER | [5 empty] | 148 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK23 | 營三線(VK23) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0141 |  |  | 2-8D |  |  | 11KV_VK23_A1 | AMP | 16526 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營三線A1 | 11KV營三線 R相AMP | FEEDER | [5 empty] | 149 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK23 | 營三線(VK23) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0142 |  |  | 2-8E |  |  | 11KV_VK23_A2 | AMP | 16527 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營三線A2 | 11KV營三線 S相AMP | FEEDER | [5 empty] | 150 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK23 | 營三線(VK23) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0143 |  |  | 2-8F |  |  | 11KV_VK23_A3 | AMP | 16528 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營三線A3 | 11KV營三線 T相AMP | FEEDER | [5 empty] | 151 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK23 | 營三線(VK23) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0144 |  |  | 2-90 |  |  | 11KV_VK23_A0 | AMP | 16529 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營三線A0 | 11KV營三線 N相AMP | FEEDER | [5 empty] | 152 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK24 | 營正線(VK24) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0145 |  |  | 2-91 |  |  | 11KV_VK24_Var | KVAR | 16530 | KVAR_-9000_9000(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營正線KVAR | 11KV營正線 KVAR | FEEDER | [5 empty] | 153 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK24 | 營正線(VK24) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0146 |  |  | 2-92 |  |  | 11KV_VK24_A1 | AMP | 16531 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營正線A1 | 11KV營正線 R相AMP | FEEDER | [5 empty] | 154 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK24 | 營正線(VK24) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0147 |  |  | 2-93 |  |  | 11KV_VK24_A2 | AMP | 16532 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營正線A2 | 11KV營正線 S相AMP | FEEDER | [5 empty] | 155 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK24 | 營正線(VK24) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0148 |  |  | 2-94 |  |  | 11KV_VK24_A3 | AMP | 16533 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營正線A3 | 11KV營正線 T相AMP | FEEDER | [5 empty] | 156 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK24 | 營正線(VK24) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0149 |  |  | 2-95 |  |  | 11KV_VK24_A0 | AMP | 16534 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營正線A0 | 11KV營正線 N相AMP | FEEDER | [5 empty] | 157 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK25 | 營五線(VK25) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0150 |  |  | 2-96 |  |  | 11KV_VK25_Var | KVAR | 16535 | KVAR_-9000_9000(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營五線KVAR | 11KV營五線 KVAR | FEEDER | [5 empty] | 158 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK25 | 營五線(VK25) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0151 |  |  | 2-97 |  |  | 11KV_VK25_A1 | AMP | 16536 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營五線A1 | 11KV營五線 R相AMP | FEEDER | [5 empty] | 159 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK25 | 營五線(VK25) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0152 |  |  | 2-98 |  |  | 11KV_VK25_A2 | AMP | 16537 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營五線A2 | 11KV營五線 S相AMP | FEEDER | [5 empty] | 160 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK25 | 營五線(VK25) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0153 |  |  | 2-99 |  |  | 11KV_VK25_A3 | AMP | 16538 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營五線A3 | 11KV營五線 T相AMP | FEEDER | [5 empty] | 161 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK25 | 營五線(VK25) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0154 |  |  | 2-9A |  |  | 11KV_VK25_A0 | AMP | 16539 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營五線A0 | 11KV營五線 N相AMP | FEEDER | [5 empty] | 162 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK51 | 營五十一線(VK51) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0155 |  |  | 2-9B |  |  | 23KV_VK51_Var | KVAR | 16540 | KVAR_-18000_18000(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營51線KVAR | 23KV營51線 KVAR | FEEDER | [5 empty] | 163 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK51 | 營五十一線(VK51) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0156 |  |  | 2-9C |  |  | 23KV_VK51_A1 | AMP | 16541 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營51線A1 | 23KV營51線 R相AMP | FEEDER | [5 empty] | 164 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK51 | 營五十一線(VK51) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0157 |  |  | 2-9D |  |  | 23KV_VK51_A2 | AMP | 16542 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營51線A2 | 23KV營51線 S相AMP | FEEDER | [5 empty] | 165 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK51 | 營五十一線(VK51) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0158 |  |  | 2-9E |  |  | 23KV_VK51_A3 | AMP | 16543 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營51線A3 | 23KV營51線 T相AMP | FEEDER | [5 empty] | 166 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK51 | 營五十一線(VK51) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0159 |  |  | 2-9F |  |  | 23KV_VK51_A0 | AMP | 16544 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營51線A0 | 23KV營51線 N相AMP | FEEDER | [5 empty] | 167 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK52 | 營五十二線(VK52) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0160 |  |  | 2-A0 |  |  | 23KV_VK52_Var | KVAR | 16545 | KVAR_-18000_18000(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營52線KVAR | 23KV營52線 KVAR | FEEDER | [5 empty] | 168 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK52 | 營五十二線(VK52) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0161 |  |  | 2-A1 |  |  | 23KV_VK52_A1 | AMP | 16546 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營52線A1 | 23KV營52線 R相AMP | FEEDER | [5 empty] | 169 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK52 | 營五十二線(VK52) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0162 |  |  | 2-A2 |  |  | 23KV_VK52_A2 | AMP | 16547 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營52線A2 | 23KV營52線 S相AMP | FEEDER | [5 empty] | 170 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK52 | 營五十二線(VK52) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0163 |  |  | 2-A3 |  |  | 23KV_VK52_A3 | AMP | 16548 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營52線A3 | 23KV營52線 T相AMP | FEEDER | [5 empty] | 171 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK52 | 營五十二線(VK52) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0164 |  |  | 2-A4 |  |  | 23KV_VK52_A0 | AMP | 16549 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營52線A0 | 23KV營52線 N相AMP | FEEDER | [5 empty] | 172 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK53 | 營五十三線(VK53) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0165 |  |  | 2-A5 |  |  | 23KV_VK53_Var | KVAR | 16550 | KVAR_-18000_18000(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營53線KVAR | 23KV營53線 KVAR | FEEDER | [5 empty] | 173 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK53 | 營五十三線(VK53) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0166 |  |  | 2-A6 |  |  | 23KV_VK53_A1 | AMP | 16551 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營53線A1 | 23KV營53線 R相AMP | FEEDER | [5 empty] | 174 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK53 | 營五十三線(VK53) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0167 |  |  | 2-A7 |  |  | 23KV_VK53_A2 | AMP | 16552 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營53線A2 | 23KV營53線 S相AMP | FEEDER | [5 empty] | 175 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK53 | 營五十三線(VK53) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0168 |  |  | 2-A8 |  |  | 23KV_VK53_A3 | AMP | 16553 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營53線A3 | 23KV營53線 T相AMP | FEEDER | [5 empty] | 176 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK53 | 營五十三線(VK53) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0169 |  |  | 2-A9 |  |  | 23KV_VK53_A0 | AMP | 16554 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營53線A0 | 23KV營53線 N相AMP | FEEDER | [5 empty] | 177 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK54 | 營五十四線(VK54) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0170 |  |  | 2-AA |  |  | 23KV_VK54_Var | KVAR | 16555 | KVAR_-18000_18000(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營54線KVAR | 23KV營54線 KVAR | FEEDER | [5 empty] | 178 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK54 | 營五十四線(VK54) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0171 |  |  | 2-AB |  |  | 23KV_VK54_A1 | AMP | 16556 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營54線A1 | 23KV營54線 R相AMP | FEEDER | [5 empty] | 179 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK54 | 營五十四線(VK54) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0172 |  |  | 2-AC |  |  | 23KV_VK54_A2 | AMP | 16557 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營54線A2 | 23KV營54線 S相AMP | FEEDER | [5 empty] | 180 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK54 | 營五十四線(VK54) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0173 |  |  | 2-AD |  |  | 23KV_VK54_A3 | AMP | 16558 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營54線A3 | 23KV營54線 T相AMP | FEEDER | [5 empty] | 181 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK54 | 營五十四線(VK54) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0174 |  |  | 2-AE |  |  | 23KV_VK54_A0 | AMP | 16559 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營54線A0 | 23KV營54線 N相AMP | FEEDER | [5 empty] | 182 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK55 | 營五十五線(VK55) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0175 |  |  | 2-AF |  |  | 23KV_VK55_Var | KVAR | 16560 | KVAR_-18000_18000(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營55線KVAR | 23KV營55線 KVAR | FEEDER | [5 empty] | 183 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK55 | 營五十五線(VK55) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0176 |  |  | 2-B0 |  |  | 23KV_VK55_A1 | AMP | 16561 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營55線A1 | 23KV營55線 R相AMP | FEEDER | [5 empty] | 184 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK55 | 營五十五線(VK55) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0177 |  |  | 2-B1 |  |  | 23KV_VK55_A2 | AMP | 16562 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營55線A2 | 23KV營55線 S相AMP | FEEDER | [5 empty] | 185 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK55 | 營五十五線(VK55) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0178 |  |  | 2-B2 |  |  | 23KV_VK55_A3 | AMP | 16563 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營55線A3 | 23KV營55線 T相AMP | FEEDER | [5 empty] | 186 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK55 | 營五十五線(VK55) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0179 |  |  | 2-B3 |  |  | 23KV_VK55_A0 | AMP | 16564 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營55線A0 | 23KV營55線 N相AMP | FEEDER | [5 empty] | 187 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK30 | 營十線(VK30) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0194 |  |  | 2-C2 |  |  | 11KV_VK30_Var | KVAR | 16579 | KVAR_-9000_9000(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營十線KVAR | 11KV營十線 KVAR | FEEDER | [5 empty] | 188 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK30 | 營十線(VK30) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0195 |  |  | 2-C3 |  |  | 11KV_VK30_A1 | AMP | 16580 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營十線A1 | 11KV營十線 R相AMP | FEEDER | [5 empty] | 189 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK30 | 營十線(VK30) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0196 |  |  | 2-C4 |  |  | 11KV_VK30_A2 | AMP | 16581 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營十線A2 | 11KV營十線 S相AMP | FEEDER | [5 empty] | 190 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK30 | 營十線(VK30) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0197 |  |  | 2-C5 |  |  | 11KV_VK30_A3 | AMP | 16582 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營十線A3 | 11KV營十線 T相AMP | FEEDER | [5 empty] | 191 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK30 | 營十線(VK30) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0198 |  |  | 2-C6 |  |  | 11KV_VK30_A0 | AMP | 16583 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營十線A0 | 11KV營十線 N相AMP | FEEDER | [5 empty] | 192 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK29 | 營九線(VK29) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0199 |  |  | 2-C7 |  |  | 11KV_VK29_Var | KVAR | 16584 | KVAR_-9000_9000(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營九線KVAR | 11KV營九線 KVAR | FEEDER | [5 empty] | 193 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK29 | 營九線(VK29) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0200 |  |  | 2-C8 |  |  | 11KV_VK29_A1 | AMP | 16585 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營九線A1 | 11KV營九線 R相AMP | FEEDER | [5 empty] | 194 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK29 | 營九線(VK29) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0201 |  |  | 2-C9 |  |  | 11KV_VK29_A2 | AMP | 16586 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營九線A2 | 11KV營九線 S相AMP | FEEDER | [5 empty] | 195 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK29 | 營九線(VK29) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0202 |  |  | 2-CA |  |  | 11KV_VK29_A3 | AMP | 16587 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營九線A3 | 11KV營九線 T相AMP | FEEDER | [5 empty] | 196 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK29 | 營九線(VK29) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0203 |  |  | 2-CB |  |  | 11KV_VK29_A0 | AMP | 16588 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營九線A0 | 11KV營九線 N相AMP | FEEDER | [5 empty] | 197 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK28 | 營八線(VK28) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0204 |  |  | 2-CC |  |  | 11KV_VK28_Var | KVAR | 16589 | KVAR_-9000_9000(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營八線KVAR | 11KV營八線 KVAR | FEEDER | [5 empty] | 198 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK28 | 營八線(VK28) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0205 |  |  | 2-CD |  |  | 11KV_VK28_A1 | AMP | 16590 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營八線A1 | 11KV營八線 R相AMP | FEEDER | [5 empty] | 199 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK28 | 營八線(VK28) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0206 |  |  | 2-CE |  |  | 11KV_VK28_A2 | AMP | 16591 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營八線A2 | 11KV營八線 S相AMP | FEEDER | [5 empty] | 200 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK28 | 營八線(VK28) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0207 |  |  | 2-CF |  |  | 11KV_VK28_A3 | AMP | 16592 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營八線A3 | 11KV營八線 T相AMP | FEEDER | [5 empty] | 201 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK28 | 營八線(VK28) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0208 |  |  | 2-D0 |  |  | 11KV_VK28_A0 | AMP | 16593 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營八線A0 | 11KV營八線 N相AMP | FEEDER | [5 empty] | 202 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK27 | 營七線(VK27) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0209 |  |  | 2-D1 |  |  | 11KV_VK27_Var | KVAR | 16594 | KVAR_-9000_9000(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營七線KVAR | 11KV營七線 KVAR | FEEDER | [5 empty] | 203 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK27 | 營七線(VK27) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0210 |  |  | 2-D2 |  |  | 11KV_VK27_A1 | AMP | 16595 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營七線A1 | 11KV營七線 R相AMP | FEEDER | [5 empty] | 204 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK27 | 營七線(VK27) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0211 |  |  | 2-D3 |  |  | 11KV_VK27_A2 | AMP | 16596 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營七線A2 | 11KV營七線 S相AMP | FEEDER | [5 empty] | 205 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK27 | 營七線(VK27) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0212 |  |  | 2-D4 |  |  | 11KV_VK27_A3 | AMP | 16597 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營七線A3 | 11KV營七線 T相AMP | FEEDER | [5 empty] | 206 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK27 | 營七線(VK27) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0213 |  |  | 2-D5 |  |  | 11KV_VK27_A0 | AMP | 16598 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營七線A0 | 11KV營七線 N相AMP | FEEDER | [5 empty] | 207 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK26 | 營六線(VK26) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0214 |  |  | 2-D6 |  |  | 11KV_VK26_Var | KVAR | 16599 | KVAR_-9000_9000(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營六線KVAR | 11KV營六線 KVAR | FEEDER | [5 empty] | 208 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK26 | 營六線(VK26) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0215 |  |  | 2-D7 |  |  | 11KV_VK26_A1 | AMP | 16600 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營六線A1 | 11KV營六線 R相AMP | FEEDER | [5 empty] | 209 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK26 | 營六線(VK26) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0216 |  |  | 2-D8 |  |  | 11KV_VK26_A2 | AMP | 16601 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營六線A2 | 11KV營六線 S相AMP | FEEDER | [5 empty] | 210 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK26 | 營六線(VK26) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0217 |  |  | 2-D9 |  |  | 11KV_VK26_A3 | AMP | 16602 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營六線A3 | 11KV營六線 T相AMP | FEEDER | [5 empty] | 211 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | VK26 | 營六線(VK26) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0218 |  |  | 2-DA |  |  | 11KV_VK26_A0 | AMP | 16603 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營六線A0 | 11KV營六線 N相AMP | FEEDER | [5 empty] | 212 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK60 | 營六十線(VK60) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0219 |  |  | 2-DB |  |  | 23KV_VK60_Var | KVAR | 16604 | KVAR_-18000_18000(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營60線KVAR | 23KV營60線 KVAR | FEEDER | [5 empty] | 213 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK60 | 營六十線(VK60) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0220 |  |  | 2-DC |  |  | 23KV_VK60_A1 | AMP | 16605 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營60線A1 | 23KV營60線 R相AMP | FEEDER | [5 empty] | 214 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK60 | 營六十線(VK60) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0221 |  |  | 2-DD |  |  | 23KV_VK60_A2 | AMP | 16606 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營60線A2 | 23KV營60線 S相AMP | FEEDER | [5 empty] | 215 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK60 | 營六十線(VK60) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0222 |  |  | 2-DE |  |  | 23KV_VK60_A3 | AMP | 16607 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營60線A3 | 23KV營60線 T相AMP | FEEDER | [5 empty] | 216 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK60 | 營六十線(VK60) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0223 |  |  | 2-DF |  |  | 23KV_VK60_A0 | AMP | 16608 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營60線A0 | 23KV營60線 N相AMP | FEEDER | [5 empty] | 217 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK59 | 營五十九線(VK59) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0224 |  |  | 2-E0 |  |  | 23KV_VK59_Var | KVAR | 16609 | KVAR_-18000_18000(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營59線KVAR | 23KV營59線 KVAR | FEEDER | [5 empty] | 218 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK59 | 營五十九線(VK59) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0225 |  |  | 2-E1 |  |  | 23KV_VK59_A1 | AMP | 16610 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營59線A1 | 23KV營59線 R相AMP | FEEDER | [5 empty] | 219 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK59 | 營五十九線(VK59) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0226 |  |  | 2-E2 |  |  | 23KV_VK59_A2 | AMP | 16611 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營59線A2 | 23KV營59線 S相AMP | FEEDER | [5 empty] | 220 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK59 | 營五十九線(VK59) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0227 |  |  | 2-E3 |  |  | 23KV_VK59_A3 | AMP | 16612 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營59線A3 | 23KV營59線 T相AMP | FEEDER | [5 empty] | 221 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK59 | 營五十九線(VK59) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0228 |  |  | 2-E4 |  |  | 23KV_VK59_A0 | AMP | 16613 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營59線A0 | 23KV營59線 N相AMP | FEEDER | [5 empty] | 222 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK58 | 營五十八線(VK58) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0229 |  |  | 2-E5 |  |  | 23KV_VK58_Var | KVAR | 16614 | KVAR_-18000_18000(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營58線KVAR | 23KV營58線 KVAR | FEEDER | [5 empty] | 223 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK58 | 營五十八線(VK58) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0230 |  |  | 2-E6 |  |  | 23KV_VK58_A1 | AMP | 16615 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營58線A1 | 23KV營58線 R相AMP | FEEDER | [5 empty] | 224 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK58 | 營五十八線(VK58) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0231 |  |  | 2-E7 |  |  | 23KV_VK58_A2 | AMP | 16616 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營58線A2 | 23KV營58線 S相AMP | FEEDER | [5 empty] | 225 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK58 | 營五十八線(VK58) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0232 |  |  | 2-E8 |  |  | 23KV_VK58_A3 | AMP | 16617 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營58線A3 | 23KV營58線 T相AMP | FEEDER | [5 empty] | 226 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK58 | 營五十八線(VK58) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0233 |  |  | 2-E9 |  |  | 23KV_VK58_A0 | AMP | 16618 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營58線A0 | 23KV營58線 N相AMP | FEEDER | [5 empty] | 227 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK57 | 營五十七線(VK57) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0234 |  |  | 2-EA |  |  | 23KV_VK57_Var | KVAR | 16619 | KVAR_-18000_18000(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營57線KVAR | 23KV營57線 KVAR | FEEDER | [5 empty] | 228 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK57 | 營五十七線(VK57) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0235 |  |  | 2-EB |  |  | 23KV_VK57_A1 | AMP | 16620 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營57線A1 | 23KV營57線 R相AMP | FEEDER | [5 empty] | 229 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK57 | 營五十七線(VK57) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0236 |  |  | 2-EC |  |  | 23KV_VK57_A2 | AMP | 16621 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營57線A2 | 23KV營57線 S相AMP | FEEDER | [5 empty] | 230 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK57 | 營五十七線(VK57) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0237 |  |  | 2-ED |  |  | 23KV_VK57_A3 | AMP | 16622 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營57線A3 | 23KV營57線 T相AMP | FEEDER | [5 empty] | 231 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK57 | 營五十七線(VK57) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0238 |  |  | 2-EE |  |  | 23KV_VK57_A0 | AMP | 16623 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營57線A0 | 23KV營57線 N相AMP | FEEDER | [5 empty] | 232 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK56 | 營五十六線(VK56) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0239 |  |  | 2-EF |  |  | 23KV_VK56_Var | KVAR | 16624 | KVAR_-18000_18000(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營56線KVAR | 23KV營56線 KVAR | FEEDER | [5 empty] | 233 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK56 | 營五十六線(VK56) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0240 |  |  | 2-F0 |  |  | 23KV_VK56_A1 | AMP | 16625 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營56線A1 | 23KV營56線 R相AMP | FEEDER | [5 empty] | 234 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK56 | 營五十六線(VK56) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0241 |  |  | 2-F1 |  |  | 23KV_VK56_A2 | AMP | 16626 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營56線A2 | 23KV營56線 S相AMP | FEEDER | [5 empty] | 235 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK56 | 營五十六線(VK56) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0242 |  |  | 2-F2 |  |  | 23KV_VK56_A3 | AMP | 16627 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營56線A3 | 23KV營56線 T相AMP | FEEDER | [5 empty] | 236 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | VK56 | 營五十六線(VK56) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0243 |  |  | 2-F3 |  |  | 23KV_VK56_A0 | AMP | 16628 | A_-500_500(-2000_2000) |  | B2/D01_D1 | [8 empty] | 下營DS.營56線A0 | 23KV營56線 N相AMP | FEEDER | [5 empty] | 237 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 161 | 161kV | 1510 | 新營～下營一路(1510) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P01D011/T2 |  | 0000 |  |  | 1-00-00 |  |  | 新營下營一路(1510) CB | CB | 1 |  | aaca | B2/D01_A1 | [8 empty] | 下營DS.1510_CB | 1510(新營下營一路) CB | LINE161 | [5 empty] | 238 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 161 | 161kV | 1510 | 新營～下營一路(1510) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0001 |  |  | 1-00-01 |  |  | 新營下營一路(1510) 87A | 87A | 2 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1510_87A | 新營下營一路(1510) 87RY | LINE161 | [5 empty] | 239 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1510 | 新營～下營一路(1510) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0002 |  |  | 1-00-02 |  |  | 新營下營一路(1510) PHA | PHA | 3 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1510_PHA | 新營下營一路(1510) 相間RY | LINE161 | [5 empty] | 240 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1510 | 新營～下營一路(1510) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | 新營下營一路(1510) GDA | GDA | 4 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1510_GDA | 新營下營一路(1510) 接地RY | LINE161 | [5 empty] | 241 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1520 | 新營～下營二路(1520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P01D012/T2 |  | 0004 |  |  | 1-00-04 |  |  | 新營下營二路(1520) CB | CB | 5 |  | aada | B2/D01_A1 | [8 empty] | 下營DS.1520_CB | 1520(新營下營二路) CB | LINE161 | [5 empty] | 242 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 161 | 161kV | 1520 | 新營～下營二路(1520) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0005 |  |  | 1-00-05 |  |  | 新營下營二路(1520) 87A | 87A | 6 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1520_87A | 新營下營二路(1520) 87RY | LINE161 | [5 empty] | 243 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1520 | 新營～下營二路(1520) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | 新營下營二路(1520) PHA | PHA | 7 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1520_PHA | 新營下營二路(1520) 相間RY | LINE161 | [5 empty] | 244 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1520 | 新營～下營二路(1520) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-07 |  |  | 新營下營二路(1520) GDA | GDA | 8 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1520_GDA | 新營下營二路(1520) 接地RY | LINE161 | [5 empty] | 245 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1530 | 下營～威致～官田鋼線(1530) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D01TN01/T2 |  | 0008 |  |  | 1-01-00 |  |  | 下營威致官田鋼線(1530) CB | CB | 9 |  | aafa | B2/D01_A1 | [8 empty] | 下營DS.1530_CB | 1530(下營威致官田鋼) CB | LINE161 | [5 empty] | 246 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 161 | 161kV | 1530 | 下營～威致～官田鋼線(1530) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0010 |  |  | 1-01-02 |  |  | 下營威致官田鋼線(1530) PHA | PHA | 11 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1530_PHA | 下營威致官田鋼(1530) 相間RY | LINE161 | [5 empty] | 247 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1530 | 下營～威致～官田鋼線(1530) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-03 |  |  | 下營威致官田鋼線(1530) GDA | GDA | 12 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1530_GDA | 下營威致官田鋼(1530) 接地RY | LINE161 | [5 empty] | 248 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0040 |  |  | 1-05-00 |  |  | TIE(1500) CB | CB | 41 |  | aagz | B2/D01_A1 | [8 empty] | 下營DS.1500_CB | 1500(TIE) CB | TIE | [5 empty] | 249 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0041 |  |  | 1-05-01 |  |  | TIE(1500) 50A | 50A | 42 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1500_50A | 161KV TIE(1500) 50RY | TIE | [5 empty] | 250 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0042 |  |  | 1-05-02 |  |  | 161KV#1BUS 87BA | 87BA | 43 |  |  | B2/D01_A1 | [8 empty] | 下營DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | [5 empty] | 251 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0043 |  |  | 1-05-03 |  |  | 161KV#2BUS 87BA | 87BA | 44 |  |  | B2/D01_A1 | [8 empty] | 下營DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | [5 empty] | 252 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0044 |  |  | 1-05-04 |  |  | 161KV OSCA | OSCA | 45 |  |  | B3/D01_A1 | [8 empty] | 下營DS.161KV_OSCA | 161KV示波器啟動警報 | OTHER | [5 empty] | 253 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/1DTR |  | 0056 |  |  | 1-07-00 |  |  | NO.1 DTR (1750) CB | CB | 57 |  | aabb | ELEM/D01_A1 | [8 empty] | 下營DS.1750_CB | 1750(#1DTR) CB | MTR | [5 empty] | 254 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS |  |  | 1DTR | #1DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0057 |  |  | 1-07-01 |  |  | No.1DTR 87A | 87A | 58 |  |  | B1/D01_A1 | [8 empty] | 下營DS.#1DTR_87A | #1DTR 87RY | MTR | [5 empty] | 255 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS |  |  | 1DTR | #1DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0058 |  |  | 1-07-02 |  |  | No.1DTR 96PA | 96PA | 59 |  |  | B1/D01_A1 | [8 empty] | 下營DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | [5 empty] | 256 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS |  |  | 1DTR | #1DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0059 |  |  | 1-07-03 |  |  | No.1DTR 51ZA | 51ZA | 60 |  |  | B1/D01_A1 | [8 empty] | 下營DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | [5 empty] | 257 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1750 | #1DTR(1750) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0060 |  |  | 1-07-04 |  |  | No.1DTR PHA | PHA | 61 |  |  | B2/D01_A1 | [8 empty] | 下營DS.#1DTR_51A | #1DTR 51RY | MTR | [5 empty] | 258 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1750 | #1DTR(1750) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0061 |  |  | 1-07-05 |  |  | No.1DTR GDA | GDA | 62 |  |  | B2/D01_A1 | [8 empty] | 下營DS.#1DTR_51NA | #1DTR 51N RY | MTR | [5 empty] | 259 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2DTR |  | 0064 |  |  | 1-08-00 |  |  | NO.2 DTR (1760) CB | CB | 65 |  | aaeb | ELEM/D01_A1 | [8 empty] | 下營DS.1760_CB | 1760(#2DTR) CB | MTR | [5 empty] | 260 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS |  |  | 2DTR | #2DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0065 |  |  | 1-08-01 |  |  | No.2DTR 87A | 87A | 66 |  |  | B1/D01_A1 | [8 empty] | 下營DS.#2DTR_87A | #2DTR 87RY | MTR | [5 empty] | 261 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS |  |  | 2DTR | #2DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0066 |  |  | 1-08-02 |  |  | No.2DTR 96PA | 96PA | 67 |  |  | B1/D01_A1 | [8 empty] | 下營DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | [5 empty] | 262 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS |  |  | 2DTR | #2DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0067 |  |  | 1-08-03 |  |  | No.2DTR 51ZA | 51ZA | 68 |  |  | B1/D01_A1 | [8 empty] | 下營DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | [5 empty] | 263 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1760 | #2DTR(1760) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 |  |  | 1-08-04 |  |  | No.2DTR PHA | PHA | 69 |  |  | B2/D01_A1 | [8 empty] | 下營DS.#2DTR_51A | #2DTR 51RY | MTR | [5 empty] | 264 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1760 | #2DTR(1760) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 |  |  | 1-08-05 |  |  | No.2DTR GDA | GDA | 70 |  |  | B2/D01_A1 | [8 empty] | 下營DS.#2DTR_51NA | #2DTR 51N RY | MTR | [5 empty] | 265 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  | ComPoint |  |  | OLTC_A |  |  | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0072 |  |  | 1-09-00 |  |  | OLTC 15分鐘內連動3次警報 | OLTCA |  |  |  | B3/D01_A1 | [8 empty] | 下營DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | [5 empty] | 266 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | T/1DTR(A) |  |  | 0091 |  |  | 1-0B-03 |  |  | M-1A (310) CB | CB | 92 |  | aaaa | ELEM/D01_A1 | [8 empty] | 下營DS.310_CB | 310(#1DTR) CB | MTR | [5 empty] | 267 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0092 |  |  | 1-0B-04 |  |  | M-1A (310) PHA | PHA | 93 |  |  | B3/D01_A1 | [8 empty] | 下營DS.310_PHA2 | 310開關箱IED RY PHA | OTHER | [5 empty] | 268 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0093 |  |  | 1-0B-05 |  |  | M-1A (310) GDA | GDA | 94 |  |  | B3/D01_A1 | [8 empty] | 下營DS.310_GDA | 310開關箱IED RY GDA | OTHER | [5 empty] | 269 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | T/1DTR(B) |  |  | 0095 |  |  | 1-0B-07 |  |  | M-1B (320) CB | CB | 96 |  | baaa | ELEM/D01_A1 | [8 empty] | 下營DS.320_CB | 320(#1DTR) CB | MTR | [5 empty] | 270 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0096 |  |  | 1-0C-00 |  |  | M-1B (320) PHA | PHA | 97 |  |  | B3/D01_A1 | [8 empty] | 下營DS.320_PHA2 | 320開關箱IED RY PHA | OTHER | [5 empty] | 271 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0097 |  |  | 1-0C-01 |  |  | M-1B (320) GDA | GDA | 98 |  |  | B3/D01_A1 | [8 empty] | 下營DS.320_GDA | 320開關箱IED RY GDA | OTHER | [5 empty] | 272 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | T/2DTR(A) |  |  | 0099 |  |  | 1-0C-03 |  |  | M2-A (330) CB | CB | 100 |  | abia | ELEM/D01_A1 | [8 empty] | 下營DS.330_CB | 330(#2DTR) CB | MTR | [5 empty] | 273 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0100 |  |  | 1-0C-04 |  |  | M2-A (330) PHA | PHA | 101 |  |  | B3/D01_A1 | [8 empty] | 下營DS.330_PHA2 | 330開關箱IED RY PHA | OTHER | [5 empty] | 274 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0101 |  |  | 1-0C-05 |  |  | M2-A (330) GDA | GDA | 102 |  |  | B3/D01_A1 | [8 empty] | 下營DS.330_GDA | 330開關箱IED RY GDA | OTHER | [5 empty] | 275 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | T/2DTR(B) |  |  | 0103 |  |  | 1-0C-07 |  |  | M2-B (340) CB | CB | 104 |  | bbka | ELEM/D01_A1 | [8 empty] | 下營DS.340_CB | 340(#2DTR) CB | MTR | [5 empty] | 276 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0104 |  |  | 1-0D-00 |  |  | M2-B (340) PHA | PHA | 105 |  |  | B3/D01_A1 | [8 empty] | 下營DS.340_PHA2 | 340開關箱IED RY PHA | OTHER | [5 empty] | 277 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0105 |  |  | 1-0D-01 |  |  | M2-B (340) GDA | GDA | 106 |  |  | B3/D01_A1 | [8 empty] | 下營DS.340_GDA | 340開關箱IED RY GDA | OTHER | [5 empty] | 278 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | 100 | TIE(100) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/1ABus | B/2ABus |  |  | 0106 |  |  | 1-0D-02 |  |  | TIE1A (100) CB | CB | 107 |  | aakb | B3/D01_A1 | [8 empty] | 下營DS.100_CB | 100(TIE) CB | TIE | [5 empty] | 279 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 11 | 11kV | 100 | TIE(100) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0107 |  |  | 1-0D-03 |  |  | TIE1A (100) PHA | PHA | 108 |  |  | B3/D01_A1 | [8 empty] | 下營DS.100_51A | 11KV TIE(100) 51RY | TIE | [5 empty] | 280 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | 100 | TIE(100) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0108 |  |  | 1-0D-04 |  |  | TIE1A (100) GDA | GDA | 109 |  |  | B3/D01_A1 | [8 empty] | 下營DS.100_51NA | 11KV TIE(100) 51N RY | TIE | [5 empty] | 281 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | 200 | TIE(200) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/2BBus | B/1BBus |  |  | 0109 |  |  | 1-0D-05 |  |  | TIE2B (200) CB | CB | 110 |  | bbab | B3/D01_A1 | [8 empty] | 下營DS.200_CB | 200(TIE) CB | TIE | [5 empty] | 282 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D01 | 下營DS | 22 | 22kV | 200 | TIE(200) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0110 |  |  | 1-0D-06 |  |  | TIE2B (201) PHA | PHA | 111 |  |  | B3/D01_A1 | [8 empty] | 下營DS.200_51A | 23KV TIE(200) 51RY | TIE | [5 empty] | 283 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | 200 | TIE(200) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0111 |  |  | 1-0D-07 |  |  | TIE2B (202) GDA | GDA | 112 |  |  | B3/D01_A1 | [8 empty] | 下營DS.200_51NA | 23KV TIE(200) 51N RY | TIE | [5 empty] | 284 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0112 |  |  | 1-0E-00 |  |  | M-1A (310) 81A | 81A | 113 |  |  | ELEM/D01_A1 | [8 empty] | 下營DS.310_81A | 310 #1DTR(A) 81RY動作 | OTHER | [5 empty] | 285 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0113 |  |  | 1-0E-01 |  |  | M-1B (320) 81A | 81A | 114 |  |  | ELEM/D01_A1 | [8 empty] | 下營DS.320_81A | 320 #1DTR(B) 81RY動作 | OTHER | [5 empty] | 286 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0114 |  |  | 1-0E-02 |  |  | M2-A (330) 81A | 81A | 115 |  |  | ELEM/D01_A1 | [8 empty] | 下營DS.330_81A | 330 #2DTR(A) 81RY動作 | OTHER | [5 empty] | 287 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0115 |  |  | 1-0E-03 |  |  | M2-B (340) 81A | 81A | 116 |  |  | ELEM/D01_A1 | [8 empty] | 下營DS.340_81A | 340 #2DTR(B) 81RY動作 | OTHER | [5 empty] | 288 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | 210 | #1SC(210) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | C/1SC |  |  | 0128 |  |  | 1-10-00 |  |  | #1SC (210) CB | CB | 129 |  | aabb | B3/D01_A1 | [8 empty] | 下營DS.210_CB | 210(11KV #1SC) CB | SC | [5 empty] | 289 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0129 |  |  | 1-10-01 |  |  | #1SC (210) SCA | SCA | 130 |  |  | B3/D01_A1 | [8 empty] | 下營DS.210_SCA | 11KV #1SC 51,51N RY | SC | [5 empty] | 290 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0130 |  |  | 1-10-02 |  |  | #1SC (210) UVA | UVA | 131 |  |  | B3/D01_A1 | [8 empty] | 下營DS.210_OUVA | 11KV #1SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 291 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | 220 | #2SC(220) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | C/2SC |  |  | 0131 |  |  | 1-10-03 |  |  | #2SC (220) CB | CB | 132 |  | babb | B3/D01_A1 | [8 empty] | 下營DS.220_CB | 220(23KV #2SC) CB | SC | [5 empty] | 292 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | 220 | #2SC(220) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0132 |  |  | 1-10-04 |  |  | #2SC (220) SCA | SCA | 133 |  |  | B3/D01_A1 | [8 empty] | 下營DS.220_SCA | 23KV #2SC 51,51N RY | SC | [5 empty] | 293 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | 220 | #2SC(220) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0133 |  |  | 1-10-05 |  |  | #2SC (220) UVA | UVA | 134 |  |  | B3/D01_A1 | [8 empty] | 下營DS.220_OUVA | 23KV #2SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 294 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | 230 | #3SC(230) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | C/3SC |  |  | 0134 |  |  | 1-10-06 |  |  | #3SC (230) CB | CB | 135 |  | abhb | B3/D01_A1 | [8 empty] | 下營DS.230_CB | 230(11KV #3SC) CB | SC | [5 empty] | 295 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | 230 | #3SC(230) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0135 |  |  | 1-10-07 |  |  | #3SC (230) SCA | SCA | 136 |  |  | B3/D01_A1 | [8 empty] | 下營DS.230_SCA | 11KV #3SC 51,51N RY | SC | [5 empty] | 296 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | 230 | #3SC(230) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0136 |  |  | 1-11-00 |  |  | #3SC (230) UVA | UVA | 137 |  |  | B3/D01_A1 | [8 empty] | 下營DS.230_OUVA | 11KV #3SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 297 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | 240 | #4SC(240) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | C/4SC |  |  | 0137 |  |  | 1-11-01 |  |  | #4SC (240) CB | CB | 138 |  | bbjb | B3/D01_A1 | [8 empty] | 下營DS.240_CB | 240(23KV #4SC) CB | SC | [5 empty] | 298 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | 240 | #4SC(240) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0138 |  |  | 1-11-02 |  |  | #4SC (240) SCA | SCA | 139 |  |  | B3/D01_A1 | [8 empty] | 下營DS.240_SCA | 23KV #4SC 51,51N RY | SC | [5 empty] | 299 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | 240 | #4SC(240) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0139 |  |  | 1-11-03 |  |  | #4SC (240) UVA | UVA | 140 |  |  | B3/D01_A1 | [8 empty] | 下營DS.240_OUVA | 23KV #4SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 300 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | 390 | #1SSTR(390) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | T/1SSTR |  |  | 0140 |  |  | 1-11-04 |  |  | #1SSTR (390) CB | CB | 141 |  | aajb | B3/D01_A1 | [8 empty] | 下營DS.390_CB | 390(#1SSTR) CB | OTHER | [5 empty] | 301 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | 390 | #1SSTR(390) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0141 |  |  | 1-11-05 |  |  | #1SSTR (390) PHA | PHA | 142 |  |  | B3/D01_A1 | [8 empty] | 下營DS.#1SSTR_51A | #1SSTR 51RY | OTHER | [5 empty] | 302 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | 390 | #1SSTR(390) |  | GDA |  | B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0142 |  |  | 1-11-06 |  |  | #1SSTR (390) GDA | GDA | 143 |  |  | B3/D01_A1 | [8 empty] | 下營DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | [5 empty] | 303 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | 490 | #2SSTR(490) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | T/2SSTR |  |  | 0143 |  |  | 1-11-07 |  |  | #2SSTR (490) CB | CB | 144 |  | bbbb | B3/D01_A1 | [8 empty] | 下營DS.490_CB | 490(#2SSTR) CB | OTHER | [5 empty] | 304 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | 490 | #2SSTR(490) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0144 |  |  | 1-12-00 |  |  | #2SSTR (490) PHA | PHA | 145 |  |  | B3/D01_A1 | [8 empty] | 下營DS.#2SSTR_51A | #2SSTR 51RY | OTHER | [5 empty] | 305 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | 490 | #2SSTR(490) |  | GDA |  | B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0145 |  |  | 1-12-01 |  |  | #2SSTR (490) GDA | GDA | 146 |  |  | B3/D01_A1 | [8 empty] | 下營DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | [5 empty] | 306 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK21 | 營一線(VK21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/VK21/T1 |  |  | 0160 |  |  | 1-14-00 |  |  | 11KV營一線 VK21 CB | CB | 161 |  | aacb | B2/D01_D1 | [8 empty] | 下營DS.VK21_CB | VK21(11KV營一線) CB | FEEDER | [5 empty] | 307 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | VK21 | 營一線(VK21) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0161 |  |  | 1-14-01 |  |  | 11KV營一線 VK21 PHA | PHA | 162 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK21_PHA | 11KV營一線(VK21) 相間RY | FEEDER | [5 empty] | 308 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK21 | 營一線(VK21) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0162 |  |  | 1-14-02 |  |  | 11KV營一線 VK21 GDA | GDA | 163 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK21_GDA | 11KV營一線(VK21) 接地RY | FEEDER | [5 empty] | 309 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK22 | 營二線(VK22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/VK22/T1 |  |  | 0163 |  |  | 1-14-03 |  |  | 11KV營二線 VK22 CB | CB | 164 |  | aadb | B2/D01_D1 | [8 empty] | 下營DS.VK22_CB | VK22(11KV營二線) CB | FEEDER | [5 empty] | 310 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | VK22 | 營二線(VK22) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0164 |  |  | 1-14-04 |  |  | 11KV營二線 VK22 PHA | PHA | 165 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK22_PHA | 11KV營二線(VK22) 相間RY | FEEDER | [5 empty] | 311 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK22 | 營二線(VK22) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0165 |  |  | 1-14-05 |  |  | 11KV營二線 VK22 GDA | GDA | 166 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK22_GDA | 11KV營二線(VK22) 接地RY | FEEDER | [5 empty] | 312 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK23 | 營三線(VK23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/VK23/T1 |  |  | 0166 |  |  | 1-14-06 |  |  | 11KV營三線 VK23 CB | CB | 167 |  | aaeb | B2/D01_D1 | [8 empty] | 下營DS.VK23_CB | VK23(11KV營三線) CB | FEEDER | [5 empty] | 313 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | VK23 | 營三線(VK23) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0167 |  |  | 1-14-07 |  |  | 11KV營三線 VK23 PHA | PHA | 168 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK23_PHA | 11KV營三線(VK23) 相間RY | FEEDER | [5 empty] | 314 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK23 | 營三線(VK23) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0168 |  |  | 1-15-00 |  |  | 11KV營三線 VK23 GDA | GDA | 169 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK23_GDA | 11KV營三線(VK23) 接地RY | FEEDER | [5 empty] | 315 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK24 | 營正線(VK24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/VK24/T1 |  |  | 0169 |  |  | 1-15-01 |  |  | 11KV營正線 VK24 CB | CB | 170 |  | aagb | B2/D01_D1 | [8 empty] | 下營DS.VK24_CB | VK24(11KV營正線) CB | FEEDER | [5 empty] | 316 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | VK24 | 營正線(VK24) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0170 |  |  | 1-15-02 |  |  | 11KV營正線 VK24 PHA | PHA | 171 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK24_PHA | 11KV營正線(VK24) 相間RY | FEEDER | [5 empty] | 317 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK24 | 營正線(VK24) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0171 |  |  | 1-15-03 |  |  | 11KV營正線 VK24 GDA | GDA | 172 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK24_GDA | 11KV營正線(VK24) 接地RY | FEEDER | [5 empty] | 318 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK25 | 營五線(VK25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/VK25/T1 |  |  | 0172 |  |  | 1-15-04 |  |  | 11KV營五線 VK25 CB | CB | 173 |  | aaib | B2/D01_D1 | [8 empty] | 下營DS.VK25_CB | VK25(11KV營五線) CB | FEEDER | [5 empty] | 319 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | VK25 | 營五線(VK25) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0173 |  |  | 1-15-05 |  |  | 11KV營五線 VK25 PHA | PHA | 174 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK25_PHA | 11KV營五線(VK25) 相間RY | FEEDER | [5 empty] | 320 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK25 | 營五線(VK25) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0174 |  |  | 1-15-06 |  |  | 11KV營五線 VK25 GDA | GDA | 175 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK25_GDA | 11KV營五線(VK25) 接地RY | FEEDER | [5 empty] | 321 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK51 | 營五十一線(VK51) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/VK51/T1 |  |  | 0175 |  |  | 1-15-07 |  |  | 23KV營五十一線 VK51 CB | CB | 176 |  | bacb | B2/D01_D1 | [8 empty] | 下營DS.VK51_CB | VK51(23KV營51線) CB | FEEDER | [5 empty] | 322 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | VK51 | 營五十一線(VK51) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0176 |  |  | 1-16-00 |  |  | 23KV營五十一線 VK51 PHA | PHA | 177 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK51_PHA | 23KV營51線(VK51) 相間RY | FEEDER | [5 empty] | 323 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK51 | 營五十一線(VK51) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0177 |  |  | 1-16-01 |  |  | 23KV營五十一線 VK51 GDA | GDA | 178 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK51_GDA | 23KV營51線(VK51) 接地RY | FEEDER | [5 empty] | 324 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK52 | 營五十二線(VK52) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/VK52/T1 |  |  | 0178 |  |  | 1-16-02 |  |  | 23KV營五十二線 VK52 CB | CB | 179 |  | badb | B2/D01_D1 | [8 empty] | 下營DS.VK52_CB | VK52(23KV營52線) CB | FEEDER | [5 empty] | 325 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | VK52 | 營五十二線(VK52) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0179 |  |  | 1-16-03 |  |  | 23KV營五十二線 VK52 PHA | PHA | 180 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK52_PHA | 23KV營52線(VK52) 相間RY | FEEDER | [5 empty] | 326 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK52 | 營五十二線(VK52) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0180 |  |  | 1-16-04 |  |  | 23KV營五十二線 VK52 GDA | GDA | 181 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK52_GDA | 23KV營52線(VK52) 接地RY | FEEDER | [5 empty] | 327 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK53 | 營五十三線(VK53) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/VK53/T1 |  |  | 0181 |  |  | 1-16-05 |  |  | 23KV營五十三線 VK53 CB | CB | 182 |  | baeb | B2/D01_D1 | [8 empty] | 下營DS.VK53_CB | VK53(23KV營53線) CB | FEEDER | [5 empty] | 328 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | VK53 | 營五十三線(VK53) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0182 |  |  | 1-16-06 |  |  | 23KV營五十三線 VK53 PHA | PHA | 183 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK53_PHA | 23KV營53線(VK53) 相間RY | FEEDER | [5 empty] | 329 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK53 | 營五十三線(VK53) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0183 |  |  | 1-16-07 |  |  | 23KV營五十三線 VK53 GDA | GDA | 184 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK53_GDA | 23KV營53線(VK53) 接地RY | FEEDER | [5 empty] | 330 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK54 | 營五十四線(VK54) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/VK54/T1 |  |  | 0184 |  |  | 1-17-00 |  |  | 23KV營五十四線 VK54 CB | CB | 185 |  | bagb | B2/D01_D1 | [8 empty] | 下營DS.VK54_CB | VK54(23KV營54線) CB | FEEDER | [5 empty] | 331 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | VK54 | 營五十四線(VK54) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0185 |  |  | 1-17-01 |  |  | 23KV營五十四線 VK54 PHA | PHA | 186 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK54_PHA | 23KV營54線(VK54) 相間RY | FEEDER | [5 empty] | 332 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK54 | 營五十四線(VK54) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0186 |  |  | 1-17-02 |  |  | 23KV營五十四線 VK54 GDA | GDA | 187 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK54_GDA | 23KV營54線(VK54) 接地RY | FEEDER | [5 empty] | 333 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK55 | 營五十五線(VK55) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/VK55/T1 |  |  | 0187 |  |  | 1-17-03 |  |  | 23KV營五十五線 VK55 CB | CB | 188 |  | baib | B2/D01_D1 | [8 empty] | 下營DS.VK55_CB | VK55(23KV營55線) CB | FEEDER | [5 empty] | 334 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | VK55 | 營五十五線(VK55) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0188 |  |  | 1-17-04 |  |  | 23KV營五十五線 VK55 PHA | PHA | 189 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK55_PHA | 23KV營55線(VK55) 相間RY | FEEDER | [5 empty] | 335 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK55 | 營五十五線(VK55) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0189 |  |  | 1-17-05 |  |  | 23KV營五十五線 VK55 GDA | GDA | 190 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK55_GDA | 23KV營55線(VK55) 接地RY | FEEDER | [5 empty] | 336 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK30 | 營十線(VK30) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/VK30/T1 |  |  | 0192 |  |  | 1-18-00 |  |  | 11KV營十線 VK30 CB | CB | 193 |  | abgb | B2/D01_D1 | [8 empty] | 下營DS.VK30_CB | VK30(11KV營十線) CB | FEEDER | [5 empty] | 337 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | VK30 | 營十線(VK30) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0193 |  |  | 1-18-01 |  |  | 11KV營十線 VK30 PHA | PHA | 194 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK30_PHA | 11KV營十線(VK30) 相間RY | FEEDER | [5 empty] | 338 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK30 | 營十線(VK30) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0194 |  |  | 1-18-02 |  |  | 11KV營十線 VK30 GDA | GDA | 195 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK30_GDA | 11KV營十線(VK30) 接地RY | FEEDER | [5 empty] | 339 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK29 | 營九線(VK29) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/VK29/T1 |  |  | 0195 |  |  | 1-18-03 |  |  | 11KV營九線 VK29 CB | CB | 196 |  | abfb | B2/D01_D1 | [8 empty] | 下營DS.VK29_CB | VK29(11KV營九線) CB | FEEDER | [5 empty] | 340 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | VK29 | 營九線(VK29) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0196 |  |  | 1-18-04 |  |  | 11KV營九線 VK29 PHA | PHA | 197 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK29_PHA | 11KV營九線(VK29) 相間RY | FEEDER | [5 empty] | 341 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK29 | 營九線(VK29) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0197 |  |  | 1-18-05 |  |  | 11KV營九線 VK29 GDA | GDA | 198 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK29_GDA | 11KV營九線(VK29) 接地RY | FEEDER | [5 empty] | 342 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK28 | 營八線(VK28) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/VK28/T1 |  |  | 0198 |  |  | 1-18-06 |  |  | 11KV營八線 VK28 CB | CB | 199 |  | abcb | B2/D01_D1 | [8 empty] | 下營DS.VK28_CB | VK28(11KV營八線) CB | FEEDER | [5 empty] | 343 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | VK28 | 營八線(VK28) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0199 |  |  | 1-18-07 |  |  | 11KV營八線 VK28 PHA | PHA | 200 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK28_PHA | 11KV營八線(VK28) 相間RY | FEEDER | [5 empty] | 344 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK28 | 營八線(VK28) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0200 |  |  | 1-19-00 |  |  | 11KV營八線 VK28 GDA | GDA | 201 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK28_GDA | 11KV營八線(VK28) 接地RY | FEEDER | [5 empty] | 345 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK27 | 營七線(VK27) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/VK27/T1 |  |  | 0201 |  |  | 1-19-01 |  |  | 11KV營七線 VK27 CB | CB | 202 |  | abbb | B2/D01_D1 | [8 empty] | 下營DS.VK27_CB | VK27(11KV營七線) CB | FEEDER | [5 empty] | 346 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | VK27 | 營七線(VK27) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0202 |  |  | 1-19-02 |  |  | 11KV營七線 VK27 PHA | PHA | 203 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK27_PHA | 11KV營七線(VK27) 相間RY | FEEDER | [5 empty] | 347 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK27 | 營七線(VK27) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0203 |  |  | 1-19-03 |  |  | 11KV營七線 VK27 GDA | GDA | 204 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK27_GDA | 11KV營七線(VK27) 接地RY | FEEDER | [5 empty] | 348 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK26 | 營六線(VK26) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/VK26/T1 |  |  | 0204 |  |  | 1-19-04 |  |  | 11KV營六線 VK26 CB | CB | 205 |  | abab | B2/D01_D1 | [8 empty] | 下營DS.VK26_CB | VK26(11KV營六線) CB | FEEDER | [5 empty] | 349 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | VK26 | 營六線(VK26) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0205 |  |  | 1-19-05 |  |  | 11KV營六線 VK26 PHA | PHA | 206 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK26_PHA | 11KV營六線(VK26) 相間RY | FEEDER | [5 empty] | 350 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK26 | 營六線(VK26) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0206 |  |  | 1-19-06 |  |  | 11KV營六線 VK26 GDA | GDA | 207 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK26_GDA | 11KV營六線(VK26) 接地RY | FEEDER | [5 empty] | 351 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK60 | 營六十線(VK60) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/VK60/T1 |  |  | 0207 |  |  | 1-19-07 |  |  | 23KV營六十線 VK60 CB | CB | 208 |  | bbib | B2/D01_D1 | [8 empty] | 下營DS.VK60_CB | VK60(23KV營60線) CB | FEEDER | [5 empty] | 352 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | VK60 | 營六十線(VK60) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0208 |  |  | 1-1A-00 |  |  | 23KV營六十線 VK60 PHA | PHA | 209 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK60_PHA | 23KV營60線(VK60) 相間RY | FEEDER | [5 empty] | 353 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK60 | 營六十線(VK60) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0209 |  |  | 1-1A-01 |  |  | 23KV營六十線 VK60 GDA | GDA | 210 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK60_GDA | 23KV營60線(VK60) 接地RY | FEEDER | [5 empty] | 354 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK59 | 營五十九線(VK59) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/VK59/T1 |  |  | 0210 |  |  | 1-1A-02 |  |  | 23KV營五十九線 VK59 CB | CB | 211 |  | bbhb | B2/D01_D1 | [8 empty] | 下營DS.VK59_CB | VK59(23KV營59線) CB | FEEDER | [5 empty] | 355 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | VK59 | 營五十九線(VK59) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0211 |  |  | 1-1A-03 |  |  | 23KV營五十九線 VK59 PHA | PHA | 212 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK59_PHA | 23KV營59線(VK59) 相間RY | FEEDER | [5 empty] | 356 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK59 | 營五十九線(VK59) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0212 |  |  | 1-1A-04 |  |  | 23KV營五十九線 VK59 GDA | GDA | 213 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK59_GDA | 23KV營59線(VK59) 接地RY | FEEDER | [5 empty] | 357 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK58 | 營五十八線(VK58) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/VK58/T1 |  |  | 0213 |  |  | 1-1A-05 |  |  | 23KV營五十八線 VK58 CB | CB | 214 |  | bbeb | B2/D01_D1 | [8 empty] | 下營DS.VK58_CB | VK58(23KV營58線) CB | FEEDER | [5 empty] | 358 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | VK58 | 營五十八線(VK58) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0214 |  |  | 1-1A-06 |  |  | 23KV營五十八線 VK58 PHA | PHA | 215 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK58_PHA | 23KV營58線(VK58) 相間RY | FEEDER | [5 empty] | 359 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK58 | 營五十八線(VK58) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0215 |  |  | 1-1A-07 |  |  | 23KV營五十八線 VK58 GDA | GDA | 216 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK58_GDA | 23KV營58線(VK58) 接地RY | FEEDER | [5 empty] | 360 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK57 | 營五十七線(VK57) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/VK57/T1 |  |  | 0216 |  |  | 1-1B-00 |  |  | 23KV營五十七線 VK57 CB | CB | 217 |  | bbdb | B2/D01_D1 | [8 empty] | 下營DS.VK57_CB | VK57(23KV營57線) CB | FEEDER | [5 empty] | 361 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | VK57 | 營五十七線(VK57) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0217 |  |  | 1-1B-01 |  |  | 23KV營五十七線 VK57 PHA | PHA | 218 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK57_PHA | 23KV營57線(VK57) 相間RY | FEEDER | [5 empty] | 362 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK57 | 營五十七線(VK57) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0218 |  |  | 1-1B-02 |  |  | 23KV營五十七線 VK57 GDA | GDA | 219 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK57_GDA | 23KV營57線(VK57) 接地RY | FEEDER | [5 empty] | 363 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK56 | 營五十六線(VK56) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/VK56/T1 |  |  | 0219 |  |  | 1-1B-03 |  |  | 23KV營五十六線 VK56 CB | CB | 220 |  | bbcb | B2/D01_D1 | [8 empty] | 下營DS.VK56_CB | VK56(23KV營56線) CB | FEEDER | [5 empty] | 364 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | VK56 | 營五十六線(VK56) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0220 |  |  | 1-1B-04 |  |  | 23KV營五十六線 VK56 PHA | PHA | 221 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK56_PHA | 23KV營56線(VK56) 相間RY | FEEDER | [5 empty] | 365 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK56 | 營五十六線(VK56) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0221 |  |  | 1-1B-05 |  |  | 23KV營五十六線 VK56 GDA | GDA | 222 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK56_GDA | 23KV營56線(VK56) 接地RY | FEEDER | [5 empty] | 366 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK21 | 營一線(VK21) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0224 |  |  | 1-1C-00 |  |  | 11KV營一線 VK21 81A | 81A | 225 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK21_81A | 11KV營一線(VK21) 81RY | OTHER | [5 empty] | 367 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK22 | 營二線(VK22) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0225 |  |  | 1-1C-01 |  |  | 11KV營二線 VK22 81A | 81A | 226 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK22_81A | 11KV營二線(VK22) 81RY | OTHER | [5 empty] | 368 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK23 | 營三線(VK23) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0226 |  |  | 1-1C-02 |  |  | 11KV營三線 VK23 81A | 81A | 227 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK23_81A | 11KV營三線(VK23) 81RY | OTHER | [5 empty] | 369 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK24 | 營正線(VK24) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0227 |  |  | 1-1C-03 |  |  | 11KV營正線 VK24 81A | 81A | 228 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK24_81A | 11KV營正線(VK24) 81RY | OTHER | [5 empty] | 370 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK25 | 營五線(VK25) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0228 |  |  | 1-1C-04 |  |  | 11KV營五線 VK25 81A | 81A | 229 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK25_81A | 11KV營五線(VK25) 81RY | OTHER | [5 empty] | 371 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK51 | 營五十一線(VK51) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0229 |  |  | 1-1C-05 |  |  | 23KV營五十一線 VK51 81A | 81A | 230 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK51_81A | 23KV營51線(VK51) 81RY | OTHER | [5 empty] | 372 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK52 | 營五十二線(VK52) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0230 |  |  | 1-1C-06 |  |  | 23KV營五十二線 VK52 81A | 81A | 231 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK52_81A | 23KV營52線(VK52) 81RY | OTHER | [5 empty] | 373 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK53 | 營五十三線(VK53) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0231 |  |  | 1-1C-07 |  |  | 23KV營五十三線 VK53 81A | 81A | 232 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK53_81A | 23KV營53線(VK53) 81RY | OTHER | [5 empty] | 374 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK54 | 營五十四線(VK54) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0232 |  |  | 1-1D-00 |  |  | 23KV營五十四線 VK54 81A | 81A | 233 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK54_81A | 23KV營54線(VK54) 81RY | OTHER | [5 empty] | 375 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK55 | 營五十五線(VK55) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0233 |  |  | 1-1D-01 |  |  | 23KV營五十五線 VK55 81A | 81A | 234 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK55_81A | 23KV營55線(VK55) 81RY | OTHER | [5 empty] | 376 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK30 | 營十線(VK30) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0234 |  |  | 1-1D-02 |  |  | 11KV營十線 VK30 81A | 81A | 235 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK30_81A | 11KV營十線(VK30) 81RY | OTHER | [5 empty] | 377 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK29 | 營九線(VK29) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0235 |  |  | 1-1D-03 |  |  | 11KV營九線 VK29 81A | 81A | 236 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK29_81A | 11KV營九線(VK29) 81RY | OTHER | [5 empty] | 378 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK28 | 營八線(VK28) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0236 |  |  | 1-1D-04 |  |  | 11KV營八線 VK28 81A | 81A | 237 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK28_81A | 11KV營八線(VK28) 81RY | OTHER | [5 empty] | 379 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK27 | 營七線(VK27) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0237 |  |  | 1-1D-05 |  |  | 11KV營七線 VK27 81A | 81A | 238 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK27_81A | 11KV營七線(VK27) 81RY | OTHER | [5 empty] | 380 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK26 | 營六線(VK26) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0238 |  |  | 1-1D-06 |  |  | 11KV營六線 VK26 81A | 81A | 239 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK26_81A | 11KV營六線(VK26) 81RY | OTHER | [5 empty] | 381 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK60 | 營六十線(VK60) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0239 |  |  | 1-1D-07 |  |  | 23KV營六十線 VK60 81A | 81A | 240 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK60_81A | 23KV營60線(VK60) 81RY | OTHER | [5 empty] | 382 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK59 | 營五十九線(VK59) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0240 |  |  | 1-1E-00 |  |  | 23KV營五十九線 VK59 81A | 81A | 241 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK59_81A | 23KV營59線(VK59) 81RY | OTHER | [5 empty] | 383 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK58 | 營五十八線(VK58) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0241 |  |  | 1-1E-01 |  |  | 23KV營五十八線 VK58 81A | 81A | 242 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK58_81A | 23KV營58線(VK58) 81RY | OTHER | [5 empty] | 384 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK57 | 營五十七線(VK57) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0242 |  |  | 1-1E-02 |  |  | 23KV營五十七線 VK57 81A | 81A | 243 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK57_81A | 23KV營57線(VK57) 81RY | OTHER | [5 empty] | 385 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK56 | 營五十六線(VK56) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0243 |  |  | 1-1E-03 |  |  | 23KV營五十六線 VK56 81A | 81A | 244 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK56_81A | 23KV營56線(VK56) 81RY | OTHER | [5 empty] | 386 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0512 |  |  | 1-30-00 |  |  | TEST 52AS | 52AS | 513 |  |  | ELEM/ALL | [8 empty] | 下營DS.TEST_CB | TEST CB | OTHER | [5 empty] | 387 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | Comm_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0513 |  |  | 1-30-01 |  |  | COMM-S/L | Local/Remote | 514 |  |  | B3/D01_A1 | [8 empty] | 下營DS.COMM_S/L | 通訊處理單元 SUPY/LOCAL | OTHER | [5 empty] | 388 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
D01 | 下營DS | 161 | 161kV | 1510 | 新營～下營一路(1510) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0514 |  |  | 1-30-02 |  |  | 新營下營一路(1510) 79UL | 79UL | 515 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1510_79UL | 新營下營一路(1510) 79RY U/L | LINE161 | [5 empty] | 389 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D01 | 下營DS | 161 | 161kV | 1510 | 新營～下營一路(1510) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0515 |  |  | 1-30-03 |  |  | 新營下營一路(1510) 87UL | 87UL | 516 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1510_87UL | 新營下營一路(1510) 87RY U/L | LINE161 | [5 empty] | 390 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D01 | 下營DS | 161 | 161kV | 1520 | 新營～下營二路(1520) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0516 |  |  | 1-30-04 |  |  | 新營下營二路(1520) 79UL | 79UL | 517 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1520_79UL | 新營下營二路(1520) 79RY U/L | LINE161 | [5 empty] | 391 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D01 | 下營DS | 161 | 161kV | 1520 | 新營～下營二路(1520) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0517 |  |  | 1-30-05 |  |  | 新營下營二路(1520) 87UL | 87UL | 518 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1520_87UL | 新營下營二路(1520) 87RY U/L | LINE161 | [5 empty] | 392 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D01 | 下營DS | 161 | 161kV | 1530 | 下營～威致～官田鋼線(1530) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0518 |  |  | 1-30-06 |  |  | 下營威致官田鋼線(1530) 79UL | 79UL | 519 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1530_79UL | 下營威致官田鋼(1530) 79RY U/L | LINE161 | [5 empty] | 393 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D01 | 下營DS | 161 | 161kV | ComPoint |  |  | BUS_RYFA |  |  | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0520 |  |  | 1-30-08 |  |  | 161KV ABUS_87BRYFA | 87BF | 521 |  |  | B3/D01_A1 | [8 empty] | 下營DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | [5 empty] | 394 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | ComPoint |  |  | 12B_CTFA | 161KV BUS CT 回路故障 | Element | Status | #1#2 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0521 |  |  | 1-30-09 |  |  | 161KV ABUS_CTFA | CTFA | 522 |  |  | B3/D01_A1 | [8 empty] | 下營DS.161KV_BUS_CTFA | 161KV BUS CT 回路故障 | OTHER | [5 empty] | 395 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0522 |  |  | 1-30-10 |  |  | 161KV #1BUS-VUA | VUA1 | 523 |  |  | B2/D01_A1 | [8 empty] | 下營DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | [5 empty] | 396 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0523 |  |  | 1-30-11 |  |  | 161KV #2BUS_VUA | VUA2 | 524 |  |  | B2/D01_A1 | [8 empty] | 下營DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | [5 empty] | 397 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0524 |  |  | 1-30-12 |  |  | 161KV #1BUS_87UL | 87B1S | 525 |  |  | B2/D01_A1 | [8 empty] | 下營DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | BUS | [5 empty] | 398 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D01 | 下營DS | 161 | 161kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0525 |  |  | 1-30-13 |  |  | 161KV #2BUS_87UL | 87B2S | 526 |  |  | B2/D01_A1 | [8 empty] | 下營DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | BUS | [5 empty] | 399 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D01 | 下營DS |  |  | 1DTR | #1DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0544 |  |  | 1-32-00 |  |  | No.1DTR 87UL | 87UL | 545 |  |  | B1/D01_A1 | [8 empty] | 下營DS.#1DTR_87UL | #1DTR 87RY U/L | MTR | [5 empty] | 400 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D01 | 下營DS |  |  | 1DTR(A) | #1DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0545 |  |  | 1-32-01 |  |  | No.1DTR(A) A/M | A/M | 546 |  | c | B1/D01_A1 | [8 empty] | 下營DS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | [5 empty] | 401 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | AUTO/MANUAL | AUTO
D01 | 下營DS |  |  | 1DTR(A) | #1DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0546 |  |  | 1-32-02 |  |  | No.1DTR(A) S/L | S/L | 547 |  |  | B1/D01_A1 | [8 empty] | 下營DS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | [5 empty] | 402 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D01 | 下營DS |  |  | 1DTR(B) | #1DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0547 |  |  | 1-32-03 |  |  | No.1DTR(B) A/M | A/M | 548 |  | b | B1/D01_A1 | [8 empty] | 下營DS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | [5 empty] | 403 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | AUTO/MANUAL | AUTO
D01 | 下營DS |  |  | 1DTR(B) | #1DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0548 |  |  | 1-32-04 |  |  | No.1DTR(B) S/L | S/L | 549 |  |  | B1/D01_A1 | [8 empty] | 下營DS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | [5 empty] | 404 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D01 | 下營DS |  |  | 1DTR | #1DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0549 |  |  | 1-32-05 |  |  | No.1DTR 63Q | 63Q | 550 |  |  | B1/D01_A1 | [8 empty] | 下營DS.#1DTR_63Q | #1DTR 63Q RY | MTR | [5 empty] | 405 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D01 | 下營DS |  |  | 1DTR | #1DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0550 |  |  | 1-32-06 |  |  | No.1DTR 96P | 96P | 551 |  |  | B1/D01_A1 | [8 empty] | 下營DS.#1DTR_96P | #1DTR 96P RY | MTR | [5 empty] | 406 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D01 | 下營DS |  |  | 1DTR | #1DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0551 |  |  | 1-32-07 |  |  | No.1DTR 96D | 96D | 552 |  |  | B1/D01_A1 | [8 empty] | 下營DS.#1DTR_96D | #1DTR 96D RY | MTR | [5 empty] | 407 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D01 | 下營DS |  |  | 1DTR | #1DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0552 |  |  | 1-32-08 |  |  | No.1DTR 96B1 | 96B1 | 553 |  |  | B1/D01_A1 | [8 empty] | 下營DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | [5 empty] | 408 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D01 | 下營DS |  |  | 1DTR | #1DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0553 |  |  | 1-32-09 |  |  | No.1DTR 96B2 | 96B2 | 554 |  |  | B1/D01_A1 | [8 empty] | 下營DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | [5 empty] | 409 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D01 | 下營DS |  |  | 1DTR | #1DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0554 |  |  | 1-32-10 |  |  | No.1DTR TRA | TRA | 555 |  | a | B1/D01_A1 | [8 empty] | 下營DS.#1DTR_TRA | #1DTR 重故障 | MTR | [5 empty] | 410 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D01 | 下營DS |  |  | 1DTR | #1DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0555 |  |  | 1-32-11 |  |  | No.1DTR TRF | TRF | 556 |  |  | B1/D01_A1 | [8 empty] | 下營DS.#1DTR_TRF | #1DTR 輕故障 | MTR | [5 empty] | 411 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D01 | 下營DS |  |  | 2DTR | #2DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0556 |  |  | 1-32-12 |  |  | No.2DTR 87UL | 87UL | 557 |  |  | B1/D01_A1 | [8 empty] | 下營DS.#2DTR_87UL | #2DTR 87RY U/L | MTR | [5 empty] | 412 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D01 | 下營DS |  |  | 2DTR(A) | #2DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0557 |  |  | 1-32-13 |  |  | No.2DTR(A) A/M | A/M | 558 |  | c | B1/D01_A1 | [8 empty] | 下營DS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | [5 empty] | 413 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | AUTO/MANUAL | AUTO
D01 | 下營DS |  |  | 2DTR(A) | #2DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0558 |  |  | 1-32-14 |  |  | No.2DTR(A) S/L | S/L | 559 |  |  | B1/D01_A1 | [8 empty] | 下營DS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | [5 empty] | 414 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D01 | 下營DS |  |  | 2DTR(B) | #2DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0559 |  |  | 1-32-15 |  |  | No.2DTR(B) A/M | A/M | 560 |  | b | B1/D01_A1 | [8 empty] | 下營DS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | [5 empty] | 415 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | AUTO/MANUAL | AUTO
D01 | 下營DS |  |  | 2DTR(B) | #2DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0560 |  |  | 1-33-00 |  |  | No.2DTR(B) S/L | S/L | 561 |  |  | B1/D01_A1 | [8 empty] | 下營DS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | [5 empty] | 416 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D01 | 下營DS |  |  | 2DTR | #2DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0561 |  |  | 1-33-01 |  |  | No.2DTR 63Q | 63Q | 562 |  |  | B1/D01_A1 | [8 empty] | 下營DS.#2DTR_63Q | #2DTR 63Q RY | MTR | [5 empty] | 417 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D01 | 下營DS |  |  | 2DTR | #2DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0562 |  |  | 1-33-02 |  |  | No.2DTR 96P | 96P | 563 |  |  | B1/D01_A1 | [8 empty] | 下營DS.#2DTR_96P | #2DTR 96P RY | MTR | [5 empty] | 418 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D01 | 下營DS |  |  | 2DTR | #2DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0563 |  |  | 1-33-03 |  |  | No.2DTR 96D | 96D | 564 |  |  | B1/D01_A1 | [8 empty] | 下營DS.#2DTR_96D | #2DTR 96D RY | MTR | [5 empty] | 419 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D01 | 下營DS |  |  | 2DTR | #2DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0564 |  |  | 1-33-04 |  |  | No.2DTR 96B1 | 96B1 | 565 |  |  | B1/D01_A1 | [8 empty] | 下營DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | [5 empty] | 420 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D01 | 下營DS |  |  | 2DTR | #2DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0565 |  |  | 1-33-05 |  |  | No.2DTR 96B2 | 96B2 | 566 |  |  | B1/D01_A1 | [8 empty] | 下營DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | [5 empty] | 421 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D01 | 下營DS |  |  | 2DTR | #2DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0566 |  |  | 1-33-06 |  |  | No.2DTR TRA | TRA | 567 |  | a | B1/D01_A1 | [8 empty] | 下營DS.#2DTR_TRA | #2DTR 重故障 | MTR | [5 empty] | 422 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D01 | 下營DS |  |  | 2DTR | #2DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0567 |  |  | 1-33-07 |  |  | No.2DTR TRF | TRF | 568 |  |  | B1/D01_A1 | [8 empty] | 下營DS.#2DTR_TRF | #2DTR 輕故障 | MTR | [5 empty] | 423 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D01 | 下營DS |  |  | 1DTR(A) | #1DTR(A) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0608 |  |  | 1-36-00 |  |  | M-1A 81UL | 81UL | 609 |  |  | B1/D01_A1 | [8 empty] | 下營DS.310_81UL | 310 #1DTR(A) 81RY U/L | OTHER | [5 empty] | 424 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D01 | 下營DS |  |  | 1DTR(B) | #1DTR(B) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0609 |  |  | 1-36-01 |  |  | M-1B 81UL | 81UL | 610 |  |  | B1/D01_A1 | [8 empty] | 下營DS.320_81UL | 320 #1DTR(B) 81RY U/L | OTHER | [5 empty] | 425 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D01 | 下營DS |  |  | 2DTR(A) | #2DTR(A) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0610 |  |  | 1-36-02 |  |  | M-2A 81UL | 81UL | 611 |  |  | B1/D01_A1 | [8 empty] | 下營DS.330_81UL | 330 #2DTR(A) 81RY U/L | OTHER | [5 empty] | 426 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D01 | 下營DS |  |  | 2DTR(B) | #2DTR(B) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0611 |  |  | 1-36-03 |  |  | M-2B 81UL | 81UL | 612 |  |  | B1/D01_A1 | [8 empty] | 下營DS.340_81UL | 340 #2DTR(B) 81RY U/L | OTHER | [5 empty] | 427 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D01 | 下營DS | 161 | 161kV | 1510 | 新營～下營一路(1510) |  | DS1 | 1511 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0640 | 641 |  | 1-38-00 | 1-38-01 |  | 新營下營一路1511_DS ON | DS | 641 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1511_DS | 1511(新營下營一路) DS | LINE161 | [5 empty] | 428 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D01 | 下營DS | 161 | 161kV | 1510 | 新營～下營一路(1510) |  | DS2 | 1512 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0642 | 643 |  | 1-38-02 | 1-38-03 |  | 新營下營一路1512_DS ON | DS | 643 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1512_DS | 1512(新營下營一路) DS | LINE161 | [5 empty] | 429 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D01 | 下營DS | 161 | 161kV | 1510 | 新營～下營一路(1510) |  | DS3 | 1513 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0644 | 645 |  | 1-38-04 | 1-38-05 |  | 新營下營一路1513_DS ON | DS | 645 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1513_DS | 1513(新營下營一路) DS | LINE161 | [5 empty] | 430 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D01 | 下營DS | 161 | 161kV | 1510 | 新營～下營一路(1510) |  | ES3 | 1513E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0646 | 647 |  | 1-38-06 | 1-38-07 |  | 新營下營一路1513E_ES ON | ES | 647 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1513E_ES | 1513E(新營下營一路) ES | LINE161 | [5 empty] | 431 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D01 | 下營DS | 161 | 161kV | 1520 | 新營～下營二路(1520) |  | DS1 | 1521 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0648 | 649 |  | 1-38-08 | 1-38-09 |  | 新營下營二路1521_DS ON | DS | 649 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1521_DS | 1521(新營下營二路) DS | LINE161 | [5 empty] | 432 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D01 | 下營DS | 161 | 161kV | 1520 | 新營～下營二路(1520) |  | DS2 | 1522 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0650 | 651 |  | 1-38-10 | 1-38-11 |  | 新營下營二路1522_DS ON | DS | 651 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1522_DS | 1522(新營下營二路) DS | LINE161 | [5 empty] | 433 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D01 | 下營DS | 161 | 161kV | 1520 | 新營～下營二路(1520) |  | DS3 | 1523 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0652 | 653 |  | 1-38-12 | 1-38-13 |  | 新營下營二路1523_DS ON | DS | 653 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1523_DS | 1523(新營下營二路) DS | LINE161 | [5 empty] | 434 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D01 | 下營DS | 161 | 161kV | 1520 | 新營～下營二路(1520) |  | ES3 | 1523E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0654 | 655 |  | 1-38-14 | 1-38-15 |  | 新營下營二路1523E_ES ON | ES | 655 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1523E_ES | 1523E(新營下營二路) ES | LINE161 | [5 empty] | 435 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D01 | 下營DS | 161 | 161kV | 1530 | 下營～威致～官田鋼線(1530) |  | DS1 | 1531 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0656 | 657 |  | 1-39-00 | 1-39-01 |  | 下營威致官田鋼線1531_DS ON | DS | 657 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1531_DS | 1531(下營威致官田鋼) DS | LINE161 | [5 empty] | 436 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D01 | 下營DS | 161 | 161kV | 1530 | 下營～威致～官田鋼線(1530) |  | DS2 | 1532 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0658 | 659 |  | 1-39-02 | 1-39-03 |  | 下營威致官田鋼線1532_DS ON | DS | 659 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1532_DS | 1532(下營威致官田鋼) DS | LINE161 | [5 empty] | 437 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D01 | 下營DS | 161 | 161kV | 1530 | 下營～威致～官田鋼線(1530) |  | DS3 | 1533 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0660 | 661 |  | 1-39-04 | 1-39-05 |  | 下營威致官田鋼線1533_DS ON | DS | 661 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1533_DS | 1533(下營威致官田鋼) DS | LINE161 | [5 empty] | 438 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D01 | 下營DS | 161 | 161kV | 1530 | 下營～威致～官田鋼線(1530) |  | ES3 | 1533E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0662 | 663 |  | 1-39-06 | 1-39-07 |  | 下營威致官田鋼線1533E_ES ON | ES | 663 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1533E_ES | 1533E(下營威致官田鋼) ES | LINE161 | [5 empty] | 439 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D01 | 下營DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0720 | 721 |  | 1-3D-00 | 1-3D-01 |  | 1501_DS ON | DS | 721 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1501_DS | 1501(TIE) DS | TIE | [5 empty] | 440 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D01 | 下營DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0722 | 723 |  | 1-3D-02 | 1-3D-03 |  | 1502_DS ON | DS | 723 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1502_DS | 1502(TIE) DS | TIE | [5 empty] | 441 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D01 | 下營DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0724 | 725 |  | 1-3D-04 | 1-3D-05 |  | 1751_DS ON | DS | 725 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1751_DS | 1751(#1DTR) DS | MTR | [5 empty] | 442 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D01 | 下營DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0726 | 727 |  | 1-3D-06 | 1-3D-07 |  | 1752_DS ON | DS | 727 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1752_DS | 1752(#1DTR) DS | MTR | [5 empty] | 443 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D01 | 下營DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0728 | 729 |  | 1-3D-08 | 1-3D-09 |  | 1761_DS ON | DS | 729 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1761_DS | 1761(#2DTR) DS | MTR | [5 empty] | 444 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D01 | 下營DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0730 | 731 |  | 1-3D-10 | 1-3D-11 |  | 1762_DS ON | DS | 731 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1762_DS | 1762(#2DTR) DS | MTR | [5 empty] | 445 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D01 | 下營DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0732 | 733 |  | 1-3D-12 | 1-3D-13 |  | 1501E_ES ON | ES | 733 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1501E_ES | 1501E(TIE) ES | TIE | [5 empty] | 446 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D01 | 下營DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0734 | 735 |  | 1-3D-14 | 1-3D-15 |  | 1502E_ES ON | ES | 735 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1502E_ES | 1502E(TIE) ES | TIE | [5 empty] | 447 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D01 | 下營DS | 11 | 11kV | B1SC | #1DTR(1A)(1SC) |  | LBS |  | Element | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/210 | C/1SC(B) |  |  | 0740 | 741 |  | 1-3E-04 | 1-3E-05 |  | 210 LBS ON | LBS | 741 |  |  | B3/D01_A1 | [8 empty] | 下營DS.210_LBS | 210(11KV #1SC) LBS | SC | [5 empty] | 448 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D01 | 下營DS | 11 | 11kV | B3SC | #2DTR(2A)(3SC) |  | LBS |  | Element | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/230 | C/3SC(B) |  |  | 0744 | 745 |  | 1-3E-08 | 1-3E-09 |  | 230 LBS ON | LBS | 745 |  |  | B3/D01_A1 | [8 empty] | 下營DS.230_LBS | 230(11KV #3SC) LBS | SC | [5 empty] | 449 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D01 | 下營DS | 11 | 11kV | VK21 | 營一線(VK21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0896 |  |  | 2-38-00 |  |  | 11KV營一線VK21 79UL | 79UL | 897 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK21_79UL | 11KV營一線(VK21) 79RY U/L | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D01 | 下營DS | 11 | 11kV | VK21 | 營一線(VK21) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0897 |  |  | 2-38-01 |  |  | 11KV營一線VK21 LCO TAP | LCO TAP | 898 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK21_LCO_TAP | 11KV營一線(VK21) LCO TAP | FEEDER | [5 empty] | 451 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D01 | 下營DS | 11 | 11kV | VK22 | 營二線(VK22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0898 |  |  | 2-38-02 |  |  | 11KV營二線VK22 79UL | 79UL | 899 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK22_79UL | 11KV營二線(VK22) 79RY U/L | FEEDER | [5 empty] | 452 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D01 | 下營DS | 11 | 11kV | VK22 | 營二線(VK22) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0899 |  |  | 2-38-03 |  |  | 11KV營二線VK22 LCO TAP | LCO TAP | 900 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK22_LCO_TAP | 11KV營二線(VK22) LCO TAP | FEEDER | [5 empty] | 453 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D01 | 下營DS | 11 | 11kV | VK23 | 營三線(VK23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0900 |  |  | 2-38-04 |  |  | 11KV營三線VK23 79UL | 79UL | 901 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK23_79UL | 11KV營三線(VK23) 79RY U/L | FEEDER | [5 empty] | 454 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D01 | 下營DS | 11 | 11kV | VK23 | 營三線(VK23) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0901 |  |  | 2-38-05 |  |  | 11KV營三線VK23 LCO TAP | LCO TAP | 902 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK23_LCO_TAP | 11KV營三線(VK23) LCO TAP | FEEDER | [5 empty] | 455 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D01 | 下營DS | 11 | 11kV | VK24 | 營正線(VK24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0902 |  |  | 2-38-06 |  |  | 11KV營正線VK24 79UL | 79UL | 903 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK24_79UL | 11KV營正線(VK24) 79RY U/L | FEEDER | [5 empty] | 456 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D01 | 下營DS | 11 | 11kV | VK24 | 營正線(VK24) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0903 |  |  | 2-38-07 |  |  | 11KV營正線VK24 LCO TAP | LCO TAP | 904 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK24_LCO_TAP | 11KV營正線(VK24) LCO TAP | FEEDER | [5 empty] | 457 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D01 | 下營DS | 11 | 11kV | VK25 | 營五線(VK25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0904 |  |  | 2-38-08 |  |  | 11KV營五線VK25 79UL | 79UL | 905 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK25_79UL | 11KV營五線(VK25) 79RY U/L | FEEDER | [5 empty] | 458 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D01 | 下營DS | 11 | 11kV | VK25 | 營五線(VK25) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0905 |  |  | 2-38-09 |  |  | 11KV營五線VK25 LCO TAP | LCO TAP | 906 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK25_LCO_TAP | 11KV營五線(VK25) LCO TAP | FEEDER | [5 empty] | 459 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D01 | 下營DS | 22 | 22kV | VK51 | 營五十一線(VK51) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0906 |  |  | 2-38-10 |  |  | 23KV營五十一線VK51 79UL | 79UL | 907 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK51_79UL | 23KV營51線(VK51) 79RY U/L | FEEDER | [5 empty] | 460 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D01 | 下營DS | 22 | 22kV | VK51 | 營五十一線(VK51) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0907 |  |  | 2-38-11 |  |  | 23KV營五十一線VK51 LCO TAP | LCO TAP | 908 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK51_LCO_TAP | 23KV營51線(VK51) LCO TAP | FEEDER | [5 empty] | 461 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D01 | 下營DS | 22 | 22kV | VK52 | 營五十二線(VK52) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0908 |  |  | 2-38-12 |  |  | 23KV營五十二線VK52 79UL | 79UL | 909 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK52_79UL | 23KV營52線(VK52) 79RY U/L | FEEDER | [5 empty] | 462 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D01 | 下營DS | 22 | 22kV | VK52 | 營五十二線(VK52) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0909 |  |  | 2-38-13 |  |  | 23KV營五十二線VK52 LCO TAP | LCO TAP | 910 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK52_LCO_TAP | 23KV營52線(VK52) LCO TAP | FEEDER | [5 empty] | 463 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D01 | 下營DS | 22 | 22kV | VK53 | 營五十三線(VK53) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0910 |  |  | 2-38-14 |  |  | 23KV營五十三線VK53 79UL | 79UL | 911 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK53_79UL | 23KV營53線(VK53) 79RY U/L | FEEDER | [5 empty] | 464 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D01 | 下營DS | 22 | 22kV | VK53 | 營五十三線(VK53) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0911 |  |  | 2-38-15 |  |  | 23KV營五十三線VK53 LCO TAP | LCO TAP | 912 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK53_LCO_TAP | 23KV營53線(VK53) LCO TAP | FEEDER | [5 empty] | 465 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D01 | 下營DS | 22 | 22kV | VK54 | 營五十四線(VK54) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0912 |  |  | 2-39-00 |  |  | 23KV營五十四線VK54 79UL | 79UL | 913 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK54_79UL | 23KV營54線(VK54) 79RY U/L | FEEDER | [5 empty] | 466 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D01 | 下營DS | 22 | 22kV | VK54 | 營五十四線(VK54) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0913 |  |  | 2-39-01 |  |  | 23KV營五十四線VK54 LCO TAP | LCO TAP | 914 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK54_LCO_TAP | 23KV營54線(VK54) LCO TAP | FEEDER | [5 empty] | 467 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D01 | 下營DS | 22 | 22kV | VK55 | 營五十五線(VK55) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0914 |  |  | 2-39-02 |  |  | 23KV營五十五線VK55 79UL | 79UL | 915 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK55_79UL | 23KV營55線(VK55) 79RY U/L | FEEDER | [5 empty] | 468 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D01 | 下營DS | 22 | 22kV | VK55 | 營五十五線(VK55) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0915 |  |  | 2-39-03 |  |  | 23KV營五十五線VK55 LCO TAP | LCO TAP | 916 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK55_LCO_TAP | 23KV營55線(VK55) LCO TAP | FEEDER | [5 empty] | 469 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D01 | 下營DS | 11 | 11kV | VK30 | 營十線(VK30) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0916 |  |  | 2-39-04 |  |  | 11KV營十線VK30 79UL | 79UL | 917 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK30_79UL | 11KV營十線(VK30) 79RY U/L | FEEDER | [5 empty] | 470 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D01 | 下營DS | 11 | 11kV | VK30 | 營十線(VK30) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0917 |  |  | 2-39-05 |  |  | 11KV營十線VK30 LCO TAP | LCO TAP | 918 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK30_LCO_TAP | 11KV營十線(VK30) LCO TAP | FEEDER | [5 empty] | 471 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D01 | 下營DS | 11 | 11kV | VK29 | 營九線(VK29) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0918 |  |  | 2-39-06 |  |  | 11KV營九線VK29 79UL | 79UL | 919 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK29_79UL | 11KV營九線(VK29) 79RY U/L | FEEDER | [5 empty] | 472 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D01 | 下營DS | 11 | 11kV | VK29 | 營九線(VK29) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0919 |  |  | 2-39-07 |  |  | 11KV營九線VK29 LCO TAP | LCO TAP | 920 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK29_LCO_TAP | 11KV營九線(VK29) LCO TAP | FEEDER | [5 empty] | 473 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D01 | 下營DS | 11 | 11kV | VK28 | 營八線(VK28) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0920 |  |  | 2-39-08 |  |  | 11KV營八線VK28 79UL | 79UL | 921 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK28_79UL | 11KV營八線(VK28) 79RY U/L | FEEDER | [5 empty] | 474 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D01 | 下營DS | 11 | 11kV | VK28 | 營八線(VK28) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0921 |  |  | 2-39-09 |  |  | 11KV營八線VK28 LCO TAP | LCO TAP | 922 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK28_LCO_TAP | 11KV營八線(VK28) LCO TAP | FEEDER | [5 empty] | 475 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D01 | 下營DS | 11 | 11kV | VK27 | 營七線(VK27) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0922 |  |  | 2-39-10 |  |  | 11KV營七線VK27 79UL | 79UL | 923 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK27_79UL | 11KV營七線(VK27) 79RY U/L | FEEDER | [5 empty] | 476 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D01 | 下營DS | 11 | 11kV | VK27 | 營七線(VK27) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0923 |  |  | 2-39-11 |  |  | 11KV營七線VK27 LCO TAP | LCO TAP | 924 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK27_LCO_TAP | 11KV營七線(VK27) LCO TAP | FEEDER | [5 empty] | 477 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D01 | 下營DS | 11 | 11kV | VK26 | 營六線(VK26) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0924 |  |  | 2-39-12 |  |  | 11KV營六線VK26 79UL | 79UL | 925 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK26_79UL | 11KV營六線(VK26) 79RY U/L | FEEDER | [5 empty] | 478 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D01 | 下營DS | 11 | 11kV | VK26 | 營六線(VK26) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0925 |  |  | 2-39-13 |  |  | 11KV營六線VK26 LCO TAP | LCO TAP | 926 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK26_LCO_TAP | 11KV營六線(VK26) LCO TAP | FEEDER | [5 empty] | 479 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D01 | 下營DS | 22 | 22kV | VK60 | 營六十線(VK60) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0926 |  |  | 2-39-14 |  |  | 23KV營六十線VK60 79UL | 79UL | 927 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK60_79UL | 23KV營60線(VK60) 79RY U/L | FEEDER | [5 empty] | 480 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D01 | 下營DS | 22 | 22kV | VK60 | 營六十線(VK60) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0927 |  |  | 2-39-15 |  |  | 23KV營六十線VK60 LCO TAP | LCO TAP | 928 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK60_LCO_TAP | 23KV營60線(VK60) LCO TAP | FEEDER | [5 empty] | 481 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D01 | 下營DS | 22 | 22kV | VK59 | 營五十九線(VK59) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0928 |  |  | 2-3A-00 |  |  | 23KV營五十九線VK59 79UL | 79UL | 929 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK59_79UL | 23KV營59線(VK59) 79RY U/L | FEEDER | [5 empty] | 482 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D01 | 下營DS | 22 | 22kV | VK59 | 營五十九線(VK59) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0929 |  |  | 2-3A-01 |  |  | 23KV營五十九線VK59 LCO TAP | LCO TAP | 930 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK59_LCO_TAP | 23KV營59線(VK59) LCO TAP | FEEDER | [5 empty] | 483 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D01 | 下營DS | 22 | 22kV | VK58 | 營五十八線(VK58) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0930 |  |  | 2-3A-02 |  |  | 23KV營五十八線VK58 79UL | 79UL | 931 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK58_79UL | 23KV營58線(VK58) 79RY U/L | FEEDER | [5 empty] | 484 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D01 | 下營DS | 22 | 22kV | VK58 | 營五十八線(VK58) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0931 |  |  | 2-3A-03 |  |  | 23KV營五十八線VK58 LCO TAP | LCO TAP | 932 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK58_LCO_TAP | 23KV營58線(VK58) LCO TAP | FEEDER | [5 empty] | 485 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D01 | 下營DS | 22 | 22kV | VK57 | 營五十七線(VK57) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0932 |  |  | 2-3A-04 |  |  | 23KV營五十七線VK57 79UL | 79UL | 933 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK57_79UL | 23KV營57線(VK57) 79RY U/L | FEEDER | [5 empty] | 486 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D01 | 下營DS | 22 | 22kV | VK57 | 營五十七線(VK57) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0933 |  |  | 2-3A-05 |  |  | 23KV營五十七線VK57 LCO TAP | LCO TAP | 934 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK57_LCO_TAP | 23KV營57線(VK57) LCO TAP | FEEDER | [5 empty] | 487 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D01 | 下營DS | 22 | 22kV | VK56 | 營五十六線(VK56) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0934 |  |  | 2-3A-06 |  |  | 23KV營五十六線VK56 79UL | 79UL | 935 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK56_79UL | 23KV營56線(VK56) 79RY U/L | FEEDER | [5 empty] | 488 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D01 | 下營DS | 22 | 22kV | VK56 | 營五十六線(VK56) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0935 |  |  | 2-3A-07 |  |  | 23KV營五十六線VK56 LCO TAP | LCO TAP | 936 |  |  | B2/D01_D1 | [8 empty] | 下營DS.VK56_LCO_TAP | 23KV營56線(VK56) LCO TAP | FEEDER | [5 empty] | 489 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0952 |  |  | 2-3B-08 |  |  | 直流充電機故障 | CHG1 |  |  |  | B3/D01_A1 | [8 empty] | 下營DS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | [5 empty] | 490 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0953 |  |  | 2-3B-09 |  |  | 通訊充電機故障 | CHG2 | 954 |  |  | B3/D01_A1 | [8 empty] | 下營DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | [5 empty] | 491 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0954 |  |  | 2-3B-10 |  |  | 通訊室AC故障 | ACFA | 955 |  |  | B3/D01_A1 | [8 empty] | 下營DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | [5 empty] | 492 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | R_Temp |  |  | Status | 溫度警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0957 |  |  | 2-3B-13 |  |  | 通訊室或控制室溫度警報 | TEMPA | 958 |  |  | B3/D01_A1 | [8 empty] | 下營DS.通信機房溫度 | 通訊室或控制室溫度警報 | OTHER | [5 empty] | 493 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0958 |  |  | 2-3B-14 |  |  | 直流電源DCA | DCA | 959 |  |  | ELEM/D01_A1 | [8 empty] | 下營DS.直流電源DCA | 直流電源故障警報 | OTHER | [5 empty] | 494 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0959 |  |  | 2-3B-15 |  |  | 直流電源DCE | DCE | 960 |  |  | ELEM/D01_A1 | [8 empty] | 下營DS.直流電源DCE | 直流電源接地故障警報 | OTHER | [5 empty] | 495 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0960 |  |  | 2-3C-00 |  |  | 變電所所內欠壓警報 | STUV | 961 |  |  | ELEM/D01_A1 | [8 empty] | 下營DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | [5 empty] | 496 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0961 |  |  | 2-3C-01 |  |  | 161KV示波器警報 | 161KV_OSCF | 962 |  |  | B3/D01_A1 | [8 empty] | 下營DS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | [5 empty] | 497 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | 1A5Other | 變電所監視系統警報SUPA | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0962 |  |  | 2-3C-02 |  |  | 所內監視系統警報障 | SUPA | 963 |  |  | B3/D01_A1 | [8 empty] | 下營DS.SUPA | 所內監視系統警報 | OTHER | [5 empty] | 498 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | 2A5Other | 集油池抽水泵警報 | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0963 |  |  | 2-3C-03 |  |  | 集油池抽水泵警報 | OWF | 964 |  |  | B3/D01_A1 | [8 empty] | 下營DS.抽水泵警報 | 抽水泵故障警報 | OTHER | [5 empty] | 499 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | GEN | 緊急發電機運轉 | Element | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0964 |  |  | 2-3C-04 |  |  | 緊急發電機運轉 |  | 965 |  |  | B3/D01_A1 | [8 empty] | 下營DS.GEN | 緊急發電機運轉 | OTHER | [5 empty] | 500 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ON/OFF | OFF
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | UPSA |  |  | Status | UPS故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0966 |  |  | 2-3C-06 |  |  | 不斷電源系統設備警報 | UPSA | 967 |  |  | B3/D01_A1 | [8 empty] | 下營DS.SCADA_UPS | SCADA UPS故障 | OTHER | [5 empty] | 501 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0967 |  |  | 2-3C-07 |  |  | 所內電源ACBA | ACBA | 968 |  |  | B3/D01_A1 | [8 empty] | 下營DS.所內電源ACBA | 所內電源故障警報 | OTHER | [5 empty] | 502 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0968 |  |  | 2-3C-08 |  |  | 所內電源ACB1 | ACB1S | 969 |  |  | B3/D01_A1 | [8 empty] | 下營DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | [5 empty] | 503 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0969 |  |  | 2-3C-09 |  |  | 所內電源ACB2 | ACB2S | 970 |  |  | B3/D01_A1 | [8 empty] | 下營DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | [5 empty] | 504 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | ACBT |  |  | Status | 所內電源ACB TIE | Close/Open | Y | 3 | DI-SP | [6 empty] | 0970 |  |  | 2-3C-10 |  |  | 所內電源ACB TIE | ACB3S | 971 |  |  | B3/D01_A1 | [8 empty] | 下營DS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | [5 empty] | 505 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ON/OFF | OFF
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | Door1 |  |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0971 |  |  | 2-3C-11 |  |  | 無人化門禁(1) | DOR1 | 972 |  |  | B3/D01_A1 | [8 empty] | 下營DS.無人化門禁(1) | 無人化門禁(1)電動大小門 | OTHER | [5 empty] | 506 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | Door2 |  |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0972 |  |  | 2-3C-12 |  |  | 無人化門禁(2) | DOR2 | 973 |  |  | B3/D01_A1 | [8 empty] | 下營DS.無人化門禁(2) | 無人化門禁(2)建築物大門 | OTHER | [5 empty] | 507 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | Fire1 | 受信總機 |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0973 |  |  | 2-3C-13 |  |  | 火災警報(1)受信總機 | 火災警報(1) | 974 |  |  | B3/D01_A1 | [8 empty] | 下營DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | [5 empty] | 508 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | Fire2 |  |  | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0974 |  |  | 2-3C-14 |  |  | 火災警報(2) | 火災警報(2) | (無接線)975 |  |  | B3/D01_A1 | [8 empty] | 下營DS.火災警報(2) | 火災警報(2) | OTHER | [5 empty] | 509 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | OilLeak1 |  |  | Status | 洩油池水位警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0975 |  |  | 2-3C-15 |  |  | 集油池第一段淹水警報 | WPF | 976 |  |  | B3/D01_A1 | [8 empty] | 下營DS.洩油池水位(1) | 洩油池水位(1) | OTHER | [5 empty] | 510 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | OilLeak2 |  |  | Status | 洩油池水位警報2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0976 |  |  | 2-3D-00 |  |  | 集油池第二段淹水警報 | WPA | 977 |  |  | B3/D01_A1 | [8 empty] | 下營DS.洩油池水位(2) | 洩油池水位(2) | OTHER | [5 empty] | 511 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | Lights1 | 景觀照明 |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0977 |  |  | 2-3D-01 |  |  | 景觀照明 | FLA | 978 |  |  | B3/D01_A1 | [8 empty] | 下營DS.開關場照明(A) | 景觀照明 | OTHER | [5 empty] | 512 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | DD_Light |  |  | Status | 路燈照明 | OFF/ON | Y | 5 | DI-SP | [6 empty] | 0978 |  |  | 2-3D-02 |  |  | 路燈 | FLB | 979 |  |  | B3/D01_A1 | [8 empty] | 下營DS.開關場照明(B) | 路燈照明 | OTHER | [5 empty] | 513 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | Water1 |  |  | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0979 |  |  | 2-3D-03 |  |  | 地下室第一區第一段淹水警報 | 1UW1 | 980 |  |  | B3/D01_A1 | [8 empty] | 下營DS.水位警報(1) | A區地下室水位警報(1) | OTHER | [5 empty] | 514 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | Water2 |  |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0980 |  |  | 2-3D-04 |  |  | 地下室第一區第二段淹水警報 | 1UW2 | 981 |  |  | B3/D01_A1 | [8 empty] | 下營DS.水位警報(2) | A區地下室水位警報(2) | OTHER | [5 empty] | 515 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | ComPoint |  |  | 60A |  |  | Status | 電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0983 |  |  | 2-3D-07 |  |  | 23KV_SC_60A | 60A | 984 |  |  | B3/D01_A1 | [8 empty] | 下營DS.11KV_SC_60A | 23/11KV SC 60A | OTHER |  | CDC_Mon1_DPC,DNP_DI_Mon1_DPC |  |  |  | 516 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1510 | 新營～下營一路(1510) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0992 |  |  | 2-3E-00 |  |  | 新營下營一路1510 87CFA | 87CFA | 993 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1510_87CFA | 新營下營一路(1510)87RY通訊故障 | OTHER | [5 empty] | 517 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1520 | 新營～下營二路(1520) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0993 |  |  | 2-3E-01 |  |  | 新營下營二路1520 87CFA | 87CFA | 994 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1520_87CFA | 新營下營二路(1520)87RY通訊故障 | OTHER | [5 empty] | 518 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1510 | 新營～下營一路(1510) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0995 |  |  | 2-3E-03 |  |  | 新營下營一路1510 RYFA | RYFA | 996 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1510_RYFA | 新營下營一路(1510)數位電驛故障 | OTHER | [5 empty] | 519 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1520 | 新營～下營二路(1520) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0996 |  |  | 2-3E-04 |  |  | 新營下營二路1520 RYFA | RYFA | 997 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1520_RYFA | 新營下營二路(1520)數位電驛故障 | OTHER | [5 empty] | 520 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1530 | 下營～威致～官田鋼線(1530) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0997 |  |  | 2-3E-05 |  |  | 下營威致官田鋼線1530 RYFA | RYFA | 998 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1530_RYFA | 下營威致官田鋼(1530)數位RY故障 | OTHER | [5 empty] | 521 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0998 |  |  | 2-3E-06 |  |  | TIE 50SA | 50SA | 999 |  |  | B2/D01_A1 | [8 empty] | 下營DS.1500_50SA | 161KV TIE(1500) 50RY 測試/正常 | TIE | [5 empty] | 522 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Test | Test | 1 |  |  | TEST/NORMAL | NORMAL
D01 | 下營DS | 0 |  | ComPoint |  |  | GRZ100 |  |  | Status | 電驛GRZ100閉鎖 | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1003 |  |  | 2-3E-11 |  |  | 本所各GRZ100 Ry U/L | GRZ100 Ry U/L | LOCK為1 |  |  | B3/D01_A1 | [8 empty] | 下營DS.BVS_RY | BVS GRZ100 RY U/L | OTHER | [5 empty] | 523 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | LOCK/USE | USE
D01 | 下營DS | 161 | 161kV | ComPoint |  |  | 25TA |  |  | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1004 |  |  | 2-3E-12 |  |  | H161KV 25TA | H161KV 25TA | 1005 |  |  | B3/D01_A1 | [8 empty] | 下營DS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | [5 empty] | 524 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1005 |  |  | 2-3E-13 |  |  | H161KV CBA | H161KV CBA | 1006 |  |  | B3/D01_A1 | [8 empty] | 下營DS.161KV_CBA | 161KV斷路器重故障 | OTHER | [5 empty] | 525 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1006 |  |  | 2-3E-14 |  |  | H161KV CBF | H161KV CBF | 1007 |  |  | B3/D01_A1 | [8 empty] | 下營DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | [5 empty] | 526 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | MCC |  |  | Status | MCC電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1007 |  |  | 2-3E-15 |  |  | H161KV MCCA | H161KV MCCA | 1008 |  |  | B3/D01_A1 | [8 empty] | 下營DS.MCC故障 | MCC電驛故障 | OTHER | [5 empty] | 527 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1009 |  |  | 2-3F-01 |  |  | H161KV RCA | H161KV RCA | 1010 |  |  | B3/D01_A1 | [8 empty] | 下營DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | [5 empty] | 528 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | ComPoint |  |  | FDR_CBA |  |  | Status | 11/22kV斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1010 |  |  | 2-3F-02 |  |  | M23KV CBA | M23KV CBA | 1011 |  |  | ELEM/D01_D1 | [8 empty] | 下營DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | [5 empty] | 529 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | ComPoint |  |  | FDR_CBF |  |  | Status | 11/22kV斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1011 |  |  | 2-3F-03 |  |  | M23KV CBF | M23KV CBF | 1012 |  |  | ELEM/D01_D1 | [8 empty] | 下營DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | [5 empty] | 530 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | ComPoint |  |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1012 |  |  | 2-3F-04 |  |  | M23KV LOA | M23KV LOA | 1013 |  |  | B3/D01_A1 | [8 empty] | 下營DS.11/23KV_LOA | 11/23KV饋線復閉失敗閉鎖 | OTHER | [5 empty] | 531 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | PMCC |  |  | Status | PMCC電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1013 |  |  | 2-3F-05 |  |  | M23KV PMCCA | M23KV PMCCA | 1014 |  |  | B3/D01_A1 | [8 empty] | 下營DS.PMCC故障 | PMCC電驛故障 | OTHER | [5 empty] | 532 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | TCA |  |  | Status | 斷路器跳脫迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1015 |  |  | 2-3F-07 |  |  | TCA_ALL | TCA_ALL | 1016 |  |  | B3/D01_A1 | [8 empty] | 下營DS.TCA | 斷路器跳脫回路故障 | OTHER | [5 empty] | 533 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | GPSA |  |  | Status | GPS故障警報 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1016 |  |  | 2-3F-08 |  |  | GPSA | GPSA | 1017 |  |  | B3/D01_A1 | [8 empty] | 下營DS.GPSA | LOCAL GPS故障 | OTHER | [5 empty] | 534 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | SCADAA |  |  | Status | LocalSCADA故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1017 |  |  | 2-3F-09 |  |  | 變電所SCADA故障 | SCADA | 1018 |  |  | B3/D01_A1 | [8 empty] | 下營DS.SCADA故障 | 變電所SCADA故障 | OTHER | [5 empty] | 535 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | SCADAA | 變電所SCADA_B故障 | Element | Status | 警報等級5動作4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1018 |  |  | 2-3F-10 |  |  | 通訊處理單元故障警報 | COMMA | 1019 |  |  | B3/D01_A1 | [8 empty] | 下營DS.COMMA | 變電所SCADA_B故障 | OTHER | [5 empty] | 536 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | FiberA | IED 通訊光纖故障 | Element | Status | SCADA光纖故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1019 |  |  | 2-3F-11 |  |  | NPORT_DCA | NPORT_DCA | 1020 |  |  | B3/D01_A1 | [8 empty] | 下營DS.NPORT_DCA | IED 通訊光纖故障 | OTHER | [5 empty] | 537 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | 7A5Other | 備援主機故障 | Element | Status | 警報等級5動作7 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1020 |  |  | 2-3F-12 |  |  | Redundant Error | COMMB | 1021 |  |  | B3/D01_A1 | [8 empty] | 下營DS.COMMB | 備援主機故障 | OTHER | [5 empty] | 538 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | 5A5Other | 通訊主機(A)故障 |  | Status | 警報等級5動作5 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1021 |  |  | 2-3F-13 |  |  | Switch Nport Error | SWITCHA | 1022 |  |  | B3/D01_A1 | [8 empty] | 下營DS.NPORTA | 通訊主機(A)故障 | OTHER | [5 empty] | 539 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | 6A5Other | 通訊主機(B)故障 |  | Status | 警報等級5動作6 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1022 |  |  | 2-3F-14 |  |  | SCADA通訊光纖故障警報 | FIBERA | 1023 |  |  | B3/D01_A1 | [8 empty] | 下營DS.FIBERA | 通訊主機(B)故障 | OTHER | [5 empty] | 540 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | 8A5Other | MODEM POWER FAIL故障 | Element | Status | 警報等級5動作8 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1023 |  |  | 2-3F-15 |  |  | MODEM power fail | MODEM | 1024 |  |  | B3/D01_A1 | [8 empty] | 下營DS.MODEMA | MODEM POWER FAIL故障 | OTHER | [5 empty] | 541 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  | RTU | RTU |  | ADCH1 |  | INSERT | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | Locate Empty | * |  | ADCH_-2000_2000(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.AI_ADCH1 | AI90%參考點 ADCH1 | OTHER | [5 empty] | 542 | DNPAIPoint | DS051 |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D01 | 下營DS | 0 |  | RTU | RTU |  | ADCH2 |  | INSERT | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | Locate Empty | * |  | ADCH_-2000_2000(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.AI_ADCH2 | AI90%參考點 ADCH2 | OTHER | [5 empty] | 543 | DNPAIPoint | DS051 |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D01 | 下營DS | 0 |  | RTU | RTU |  | ADCH3 |  | INSERT | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | Locate Empty |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.AI_ADCH3 | AI90%參考點 ADCH3 | OTHER | [5 empty] | 544 | DNPAIPoint | DS051 |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D01 | 下營DS | 0 |  | RTU | RTU |  | ADCH4 |  | INSERT | MvMoment | No4 AI參考點 90% |  | Y |  | AI | [6 empty] | 0193 |  |  | 2-C1 |  |  | Locate Empty | * |  | ADCH_-2000_2000(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.AI_ADCH4 | AI90%參考點 ADCH4 | OTHER | [5 empty] | 545 | DNPAIPoint | DS051 |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D01 | 下營DS | 0 |  | RTU | RTU |  | ADCL1 |  | INSERT | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | Locate Empty | * |  | ADCL_-2000_2000(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.AI_ADCL1 | AI10%參考點 ADCL1 | OTHER | [5 empty] | 546 | DNPAIPoint | DS051 |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D01 | 下營DS | 0 |  | RTU | RTU |  | ADCL2 |  | INSERT | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | Locate Empty | * |  | ADCL_-2000_2000(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.AI_ADCL2 | AI10%參考點 ADCL2 | OTHER | [5 empty] | 547 | DNPAIPoint | DS051 |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D01 | 下營DS | 0 |  | RTU | RTU |  | ADCL3 |  | INSERT | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | Locate Empty |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.AI_ADCL3 | AI10%參考點 ADCL3 | OTHER | [5 empty] | 548 | DNPAIPoint | DS051 |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D01 | 下營DS | 0 |  | RTU | RTU |  | ADCL4 |  | INSERT | MvMoment | No4 AI參考點 10% |  | Y |  | AI | [6 empty] | 0192 |  |  | 2-C0 |  |  | Locate Empty | * |  | ADCL_-2000_2000(-2000_2000) |  | B3/D01_A1 | [8 empty] | 下營DS.AI_ADCL4 | AI10%參考點 ADCL4 | OTHER | [5 empty] | 549 | DNPAIPoint | DS051 |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | 51A |  | INSERT | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0062 |  |  | 1-07-06 |  |  | Locate Empty |  | 63 |  |  | B3/D01_A1 | [8 empty] | 下營DS.310_51A | #1DTR二次側(310) 51RY | MTR | [5 empty] | 550 | DNPDIPoint | DS051 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | 51A |  | INSERT | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0063 |  |  | 1-07-07 |  |  | Locate Empty |  | 64 |  |  | B3/D01_A1 | [8 empty] | 下營DS.320_51A | #1DTR二次側(320) 51RY | MTR | [5 empty] | 551 | DNPDIPoint | DS051 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | 51A |  | INSERT | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0070 |  |  | 1-08-06 |  |  | Locate Empty |  |  |  |  | B3/D01_A1 | [8 empty] | 下營DS.330_51A | #2DTR二次側(330) 51RY | MTR | [5 empty] | 552 | DNPDIPoint | DS051 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | 51A |  | INSERT | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0071 |  |  | 1-08-07 |  |  | Locate Empty |  |  |  |  | B3/D01_A1 | [8 empty] | 下營DS.340_51A | #2DTR二次側(340) 51RY | MTR | [5 empty] | 553 | DNPDIPoint | DS051 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  | ComPoint | 其他輕故障 |  | PSF | 其他輕故障 | INSERT | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0965 |  |  | 2-3C-05 |  |  | Locate Empty |  | 966 |  |  | B3/D01_A1 | [8 empty] | 下營DS.其他輕故障 | 變電所內其他輕故障 | OTHER | [5 empty] | 554 | DNPDIPoint | DS051 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | Burglar1 | 無人化防盜(1) | INSERT | Status | 無人化防盜1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0985 | [10 empty] | B3/D01_A1 | [8 empty] | 下營DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER |  | CDC_Mon1_EMPTY,PointList_NULL |  |  |  | 555 | DNPDIPoint | DS051 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | Water3 | 水位警報(3) | INSERT | Status | 地下室淹水3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0981 |  |  | 2-3D-05 |  |  | Locate Empty | 2UW1 | 982 |  |  | B3/D01_A1 | [8 empty] | 下營DS.水位警報(3) | B區地下室水位警報(1) | OTHER | [5 empty] | 556 | DNPDIPoint | DS051 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  | StaDev | 所內設施 |  | Water4 | 水位警報(4) | INSERT | Status | 地下室淹水4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0982 |  |  | 2-3D-06 |  |  | Locate Empty | 2UW2 | 983 |  |  | B3/D01_A1 | [8 empty] | 下營DS.水位警報(4) | B區地下室水位警報(2) | OTHER | [5 empty] | 557 | DNPDIPoint | DS051 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
D01 | 下營DS | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/D01_A1 | [12 empty] | 下營DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: D01/161/1BUS/V; OPRD2: D01/161/2BUS/V
D01 | 下營DS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/D01_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: D01/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
D01 | 下營DS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/D01_A1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_3 | OPRD1: D01/161/1510/MW; OPRD2: D01/161/1520/MW; OPRD3: D01/161/1530/MW
D01 | 下營DS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/D01_A1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: D01/0/CalcPoint/OPRN2_MW
D01 | 下營DS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/D01_A1 | [17 empty] | none
D01 | 下營DS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/D01_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: D01/0/CalcPoint/OPRN1; OPRD2: D01/0/CalcPoint/OPRN2; OPRD3: D01/0/CalcPoint/PRFL_UL
D01 | 下營DS |  |  | 1DTR | 1DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D01_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D01/11/310/I_R; OPRD2: D01/22/320/I_R
D01 | 下營DS |  |  | 1DTR | 1DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D01_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D01/11/310/I_S; OPRD2: D01/22/320/I_S
D01 | 下營DS |  |  | 1DTR | 1DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D01_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D01/11/310/I_T; OPRD2: D01/22/320/I_T
D01 | 下營DS |  |  | 2DTR | 2DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D01_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D01/11/330/I_R; OPRD2: D01/22/340/I_R
D01 | 下營DS |  |  | 2DTR | 2DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D01_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D01/11/330/I_S; OPRD2: D01/22/340/I_S
D01 | 下營DS |  |  | 2DTR | 2DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D01_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D01/11/330/I_T; OPRD2: D01/22/340/I_T
D01 | 下營DS | 161 | 161kV | 1510 | 新營～下營一路(1510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D01_A1 | [12 empty] | 下營DS.1510_AMP | 新營下營一路 AMP | LINE161 | AMP_CAL | C20R1790 | amp_cal | OPRD1: D01/161/1510/MW; OPRD2: D01/161/1510/MVAR; OPRD3: D01/0/CalcPoint/Vbs4
D01 | 下營DS | 161 | 161kV | 1520 | 新營～下營二路(1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D01_A1 | [12 empty] | 下營DS.1520_AMP | 新營下營二路 AMP | LINE161 | AMP_CAL | C20R1790 | amp_cal | OPRD1: D01/161/1520/MW; OPRD2: D01/161/1520/MVAR; OPRD3: D01/0/CalcPoint/Vbs4
D01 | 下營DS | 161 | 161kV | 1530 | 下營～威致～官田鋼線(1530) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D01_A1 | [12 empty] | 下營DS.1530_AMP | 下營威致官田鋼 AMP | LINE161 | AMP_CAL | C20R0964 | amp_cal | OPRD1: D01/161/1530/MW; OPRD2: D01/161/1530/MVAR; OPRD3: D01/0/CalcPoint/Vbs4
D01 | 下營DS | 11 | 11kV | 1ABUS | #1ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D01_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D01/11/1ABUS/V
D01 | 下營DS | 11 | 11kV | 2ABUS | #2ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D01_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D01/11/2ABUS/V
D01 | 下營DS | 22 | 22kV | 1BBUS | #1BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D01_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D01/22/1BBUS/V
D01 | 下營DS | 22 | 22kV | 2BBUS | #2BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D01_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D01/22/2BBUS/V
D01 | 下營DS |  |  | 1DTR(A) | #1DTR(A) |  | TR_PERM | [9 empty] | B1/D01_A1 | [12 empty] | 下營DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D01//1DTR(A)/SupLocal; OPRD2: D01//1DTR(A)/Tap Chan
D01 | 下營DS |  |  | 1DTR(B) | #1DTR(B) |  | TR_PERM | [9 empty] | B1/D01_A1 | [12 empty] | 下營DS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D01//1DTR(B)/SupLocal; OPRD2: D01//1DTR(B)/Tap Chan
D01 | 下營DS |  |  | 2DTR(A) | #2DTR(A) |  | TR_PERM | [9 empty] | B1/D01_A1 | [12 empty] | 下營DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D01//2DTR(A)/SupLocal; OPRD2: D01//2DTR(A)/Tap Chan
D01 | 下營DS |  |  | 2DTR(B) | #2DTR(B) |  | TR_PERM | [9 empty] | B1/D01_A1 | [12 empty] | 下營DS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D01//2DTR(B)/SupLocal; OPRD2: D01//2DTR(B)/Tap Chan
D01 | 下營DS | 11 | 11kV | VK21 | 營一線(VK21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D01/11/1ABUS/V; OPRD2: D01/11/VK21/I_R; OPRD3: D01/11/VK21/I_S; OPRD4: D01/11/VK21/I_T
D01 | 下營DS | 11 | 11kV | VK22 | 營二線(VK22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D01/11/1ABUS/V; OPRD2: D01/11/VK22/I_R; OPRD3: D01/11/VK22/I_S; OPRD4: D01/11/VK22/I_T
D01 | 下營DS | 11 | 11kV | VK23 | 營三線(VK23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D01/11/1ABUS/V; OPRD2: D01/11/VK23/I_R; OPRD3: D01/11/VK23/I_S; OPRD4: D01/11/VK23/I_T
D01 | 下營DS | 11 | 11kV | VK24 | 營正線(VK24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D01/11/1ABUS/V; OPRD2: D01/11/VK24/I_R; OPRD3: D01/11/VK24/I_S; OPRD4: D01/11/VK24/I_T
D01 | 下營DS | 11 | 11kV | VK25 | 營五線(VK25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D01/11/1ABUS/V; OPRD2: D01/11/VK25/I_R; OPRD3: D01/11/VK25/I_S; OPRD4: D01/11/VK25/I_T
D01 | 下營DS | 11 | 11kV | VK26 | 營六線(VK26) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D01/11/2ABUS/V; OPRD2: D01/11/VK26/I_R; OPRD3: D01/11/VK26/I_S; OPRD4: D01/11/VK26/I_T
D01 | 下營DS | 11 | 11kV | VK27 | 營七線(VK27) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D01/11/2ABUS/V; OPRD2: D01/11/VK27/I_R; OPRD3: D01/11/VK27/I_S; OPRD4: D01/11/VK27/I_T
D01 | 下營DS | 11 | 11kV | VK28 | 營八線(VK28) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D01/11/2ABUS/V; OPRD2: D01/11/VK28/I_R; OPRD3: D01/11/VK28/I_S; OPRD4: D01/11/VK28/I_T
D01 | 下營DS | 11 | 11kV | VK29 | 營九線(VK29) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D01/11/2ABUS/V; OPRD2: D01/11/VK29/I_R; OPRD3: D01/11/VK29/I_S; OPRD4: D01/11/VK29/I_T
D01 | 下營DS | 11 | 11kV | VK30 | 營十線(VK30) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D01/11/2ABUS/V; OPRD2: D01/11/VK30/I_R; OPRD3: D01/11/VK30/I_S; OPRD4: D01/11/VK30/I_T
D01 | 下營DS | 22 | 22kV | VK51 | 營五十一線(VK51) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D01/22/1BBUS/V; OPRD2: D01/22/VK51/I_R; OPRD3: D01/22/VK51/I_S; OPRD4: D01/22/VK51/I_T
D01 | 下營DS | 22 | 22kV | VK52 | 營五十二線(VK52) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D01/22/1BBUS/V; OPRD2: D01/22/VK52/I_R; OPRD3: D01/22/VK52/I_S; OPRD4: D01/22/VK52/I_T
D01 | 下營DS | 22 | 22kV | VK53 | 營五十三線(VK53) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D01/22/1BBUS/V; OPRD2: D01/22/VK53/I_R; OPRD3: D01/22/VK53/I_S; OPRD4: D01/22/VK53/I_T
D01 | 下營DS | 22 | 22kV | VK54 | 營五十四線(VK54) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D01/22/1BBUS/V; OPRD2: D01/22/VK54/I_R; OPRD3: D01/22/VK54/I_S; OPRD4: D01/22/VK54/I_T
D01 | 下營DS | 22 | 22kV | VK55 | 營五十五線(VK55) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D01/22/1BBUS/V; OPRD2: D01/22/VK55/I_R; OPRD3: D01/22/VK55/I_S; OPRD4: D01/22/VK55/I_T
D01 | 下營DS | 22 | 22kV | VK56 | 營五十六線(VK56) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D01/22/2BBUS/V; OPRD2: D01/22/VK56/I_R; OPRD3: D01/22/VK56/I_S; OPRD4: D01/22/VK56/I_T
D01 | 下營DS | 22 | 22kV | VK57 | 營五十七線(VK57) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D01/22/2BBUS/V; OPRD2: D01/22/VK57/I_R; OPRD3: D01/22/VK57/I_S; OPRD4: D01/22/VK57/I_T
D01 | 下營DS | 22 | 22kV | VK58 | 營五十八線(VK58) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D01/22/2BBUS/V; OPRD2: D01/22/VK58/I_R; OPRD3: D01/22/VK58/I_S; OPRD4: D01/22/VK58/I_T
D01 | 下營DS | 22 | 22kV | VK59 | 營五十九線(VK59) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D01/22/2BBUS/V; OPRD2: D01/22/VK59/I_R; OPRD3: D01/22/VK59/I_S; OPRD4: D01/22/VK59/I_T
D01 | 下營DS | 22 | 22kV | VK60 | 營六十線(VK60) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D01/22/2BBUS/V; OPRD2: D01/22/VK60/I_R; OPRD3: D01/22/VK60/I_S; OPRD4: D01/22/VK60/I_T
D01 | 下營DS | 11 | 11kV | VK21 | 營一線(VK21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D01/11/VK21/kVA; OPRD2: D01/11/VK21/KVAR
D01 | 下營DS | 11 | 11kV | VK22 | 營二線(VK22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D01/11/VK22/kVA; OPRD2: D01/11/VK22/KVAR
D01 | 下營DS | 11 | 11kV | VK23 | 營三線(VK23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D01/11/VK23/kVA; OPRD2: D01/11/VK23/KVAR
D01 | 下營DS | 11 | 11kV | VK24 | 營正線(VK24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D01/11/VK24/kVA; OPRD2: D01/11/VK24/KVAR
D01 | 下營DS | 11 | 11kV | VK25 | 營五線(VK25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D01/11/VK25/kVA; OPRD2: D01/11/VK25/KVAR
D01 | 下營DS | 11 | 11kV | VK26 | 營六線(VK26) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D01/11/VK26/kVA; OPRD2: D01/11/VK26/KVAR
D01 | 下營DS | 11 | 11kV | VK27 | 營七線(VK27) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D01/11/VK27/kVA; OPRD2: D01/11/VK27/KVAR
D01 | 下營DS | 11 | 11kV | VK28 | 營八線(VK28) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D01/11/VK28/kVA; OPRD2: D01/11/VK28/KVAR
D01 | 下營DS | 11 | 11kV | VK29 | 營九線(VK29) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D01/11/VK29/kVA; OPRD2: D01/11/VK29/KVAR
D01 | 下營DS | 11 | 11kV | VK30 | 營十線(VK30) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D01/11/VK30/kVA; OPRD2: D01/11/VK30/KVAR
D01 | 下營DS | 22 | 22kV | VK51 | 營五十一線(VK51) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D01/22/VK51/kVA; OPRD2: D01/22/VK51/KVAR
D01 | 下營DS | 22 | 22kV | VK52 | 營五十二線(VK52) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D01/22/VK52/kVA; OPRD2: D01/22/VK52/KVAR
D01 | 下營DS | 22 | 22kV | VK53 | 營五十三線(VK53) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D01/22/VK53/kVA; OPRD2: D01/22/VK53/KVAR
D01 | 下營DS | 22 | 22kV | VK54 | 營五十四線(VK54) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D01/22/VK54/kVA; OPRD2: D01/22/VK54/KVAR
D01 | 下營DS | 22 | 22kV | VK55 | 營五十五線(VK55) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D01/22/VK55/kVA; OPRD2: D01/22/VK55/KVAR
D01 | 下營DS | 22 | 22kV | VK56 | 營五十六線(VK56) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D01/22/VK56/kVA; OPRD2: D01/22/VK56/KVAR
D01 | 下營DS | 22 | 22kV | VK57 | 營五十七線(VK57) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D01/22/VK57/kVA; OPRD2: D01/22/VK57/KVAR
D01 | 下營DS | 22 | 22kV | VK58 | 營五十八線(VK58) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D01/22/VK58/kVA; OPRD2: D01/22/VK58/KVAR
D01 | 下營DS | 22 | 22kV | VK59 | 營五十九線(VK59) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D01/22/VK59/kVA; OPRD2: D01/22/VK59/KVAR
D01 | 下營DS | 22 | 22kV | VK60 | 營六十線(VK60) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D01/22/VK60/kVA; OPRD2: D01/22/VK60/KVAR
D01 | 下營DS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D01_A1 | [12 empty] | 下營DS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D01/11/210/CB; OPRD2: 6.9; OPRD3: 0
D01 | 下營DS | 11 | 11kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D01_A1 | [12 empty] | 下營DS.230_SC_MVAR | 11KV#3SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D01/11/230/CB; OPRD2: 6.9; OPRD3: 0
D01 | 下營DS | 22 | 22kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D01_A1 | [12 empty] | 下營DS.220_SC_MVAR | 23KV#2SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D01/22/220/CB; OPRD2: 13.8; OPRD3: 0
D01 | 下營DS | 22 | 22kV | 240 | #4SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D01_A1 | [12 empty] | 下營DS.240_SC_MVAR | 23KV#4SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D01/22/240/CB; OPRD2: 13.8; OPRD3: 0
D01 | 下營DS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/D01_A1 | [12 empty] | 下營DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_10 |  | com_alarm_30 | D01//1DTR/96B1 | D01//1DTR/96B2 | D01//1DTR/63Q | D01//1DTR/96D | D01//1DTR/51ZA | D01//1DTR/TRA | D01//1DTR/87A | D01//1DTR/96PA | D01//2DTR/96B2 | D01//2DTR/96D | D01//2DTR/TRA | D01//2DTR/96B1 | D01//2DTR/87A | D01//2DTR/63Q | D01//2DTR/51ZA | D01//2DTR/96PA | D01/11/310/GDA | D01/11/310/PHA | D01/11/330/PHA | D01/11/330/GDA | D01/161/1750/GDA | D01/161/1750/PHA | D01/161/1760/GDA | D01/161/1760/PHA | D01/161/1BUS/87A | D01/161/2BUS/87A | D01/22/320/GDA | D01/22/320/PHA | D01/22/340/GDA | D01/22/340/PHA
D01 | 下營DS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/D01_A1 | [12 empty] | 下營DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | STATION_FAULT_2 |  | com_alarm_2 | OPRD1: D01//1DTR/TRF; OPRD2: D01//2DTR/TRF
D01 | 下營DS | 161 | 161kV | 1750_D1 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D01_D1 | [17 empty] | lamp2CC | OPRD1: D01/161/1750/CB
D01 | 下營DS | 161 | 161kV | 1760_D1 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D01_D1 | [17 empty] | lamp2CC | OPRD1: D01/161/1760/CB
D01 | 下營DS | 11 | 11kV | 310_D1 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D01_D1 | [17 empty] | lamp2CC | OPRD1: D01/11/310/CB
D01 | 下營DS | 22 | 22kV | 320_D1 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D01_D1 | [17 empty] | lamp2CC | OPRD1: D01/22/320/CB
D01 | 下營DS | 11 | 11kV | 330_D1 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D01_D1 | [17 empty] | lamp2CC | OPRD1: D01/11/330/CB
D01 | 下營DS | 22 | 22kV | 340_D1 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D01_D1 | [17 empty] | lamp2CC | OPRD1: D01/22/340/CB
D01 | 下營DS | 11 | 11kV | 310_D1 | #1DTR(A)(310) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/D01_D1 | [17 empty] | lamp2CC | OPRD1: D01/11/310/81A
D01 | 下營DS | 22 | 22kV | 320_D1 | #1DTR(B)(320) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/D01_D1 | [17 empty] | lamp2CC | OPRD1: D01/22/320/81A
D01 | 下營DS | 11 | 11kV | 330_D1 | #2DTR(A)(330) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/D01_D1 | [17 empty] | lamp2CC | OPRD1: D01/11/330/81A
D01 | 下營DS | 22 | 22kV | 340_D1 | #2DTR(B)(340) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/D01_D1 | [17 empty] | lamp2CC | OPRD1: D01/22/340/81A
D01 | 下營DS | 0 |  | StaDev_D1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D01_D1 | [17 empty] | lamp2CC | OPRD1: D01/0/StaDev/DCE
D01 | 下營DS | 0 |  | StaDev_D1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D01_D1 | [17 empty] | lamp2CC | OPRD1: D01/0/StaDev/DCA
D01 | 下營DS | 0 |  | StaDev_D1 | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/D01_D1 | [17 empty] | lamp2CC | OPRD1: D01/0/StaDev/STUV

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D01 | 下營DS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 下營DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | D01/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
D01 | 下營DS | 161 | 161kV | 1510 | 新營下營一路(1510) |  | I | [25 empty] | ADCS_N | [8 empty] | 下營DS.1510_AMP | 新營下營一路 AMP | LINE161 | D01/161/1510/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D01 | 下營DS | 161 | 161kV | 1520 | 新營下營二路(1520) |  | I | [25 empty] | ADCS_N | [8 empty] | 下營DS.1520_AMP | 新營下營二路 AMP | LINE161 | D01/161/1520/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D01 | 下營DS | 0 |  |  |  |  | 營一線KVA | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營一線KVA | 11KV營一線KVA | FEEDER |  |  | KVA_CAL |  |  | 5 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營一線KW | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營一線KW | 11KV營一線KW | FEEDER |  |  | KW_CAL |  |  | 6 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營七線KVA | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營七線KVA | 11KV營七線KVA | FEEDER |  |  | KVA_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營七線KW | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營七線KW | 11KV營七線KW | FEEDER |  |  | KW_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營九線KVA | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營九線KVA | 11KV營九線KVA | FEEDER |  |  | KVA_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營九線KW | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營九線KW | 11KV營九線KW | FEEDER |  |  | KW_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營二線KVA | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營二線KVA | 11KV營二線KVA | FEEDER |  |  | KVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營二線KW | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營二線KW | 11KV營二線KW | FEEDER |  |  | KW_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營八線KVA | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營八線KVA | 11KV營八線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營八線KW | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營八線KW | 11KV營八線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營十線KVA | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營十線KVA | 11KV營十線KVA | FEEDER |  |  | KVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營十線KW | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營十線KW | 11KV營十線KW | FEEDER |  |  | KW_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營三線KVA | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營三線KVA | 11KV營三線KVA | FEEDER |  |  | KVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營三線KW | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營三線KW | 11KV營三線KW | FEEDER |  |  | KW_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營五線KVA | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營五線KVA | 11KV營五線KVA | FEEDER |  |  | KVA_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營五線KW | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營五線KW | 11KV營五線KW | FEEDER |  |  | KW_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營六線KVA | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營六線KVA | 11KV營六線KVA | FEEDER |  |  | KVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營六線KW | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營六線KW | 11KV營六線KW | FEEDER |  |  | KW_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營正線KVA | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營正線KVA | 11KV營正線KVA | FEEDER |  |  | KVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營正線KW | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營正線KW | 11KV營正線KW | FEEDER |  |  | KW_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營51線KVA | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營51線KVA | 23KV營51線KVA | FEEDER |  |  | KVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營51線KW | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營51線KW | 23KV營51線KW | FEEDER |  |  | KW_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營52線KVA | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營52線KVA | 23KV營52線KVA | FEEDER |  |  | KVA_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營52線KW | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營52線KW | 23KV營52線KW | FEEDER |  |  | KW_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營53線KVA | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營53線KVA | 23KV營53線KVA | FEEDER |  |  | KVA_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營53線KW | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營53線KW | 23KV營53線KW | FEEDER |  |  | KW_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營54線KVA | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營54線KVA | 23KV營54線KVA | FEEDER |  |  | KVA_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營54線KW | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營54線KW | 23KV營54線KW | FEEDER |  |  | KW_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營55線KVA | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營55線KVA | 23KV營55線KVA | FEEDER |  |  | KVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營55線KW | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營55線KW | 23KV營55線KW | FEEDER |  |  | KW_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營56線KVA | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營56線KVA | 23KV營56線KVA | FEEDER |  |  | KVA_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營56線KW | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營56線KW | 23KV營56線KW | FEEDER |  |  | KW_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營57線KVA | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營57線KVA | 23KV營57線KVA | FEEDER |  |  | KVA_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營57線KW | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營57線KW | 23KV營57線KW | FEEDER |  |  | KW_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營58線KVA | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營58線KVA | 23KV營58線KVA | FEEDER |  |  | KVA_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營58線KW | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營58線KW | 23KV營58線KW | FEEDER |  |  | KW_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營59線KVA | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營59線KVA | 23KV營59線KVA | FEEDER |  |  | KVA_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營59線KW | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營59線KW | 23KV營59線KW | FEEDER |  |  | KW_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營60線KVA | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營60線KVA | 23KV營60線KVA | FEEDER |  |  | KVA_CAL |  |  | 43 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  |  |  |  | 營60線KW | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.營60線KW | 23KV營60線KW | FEEDER |  |  | KW_CAL |  |  | 44 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 下營DS.#1DTR(A)_MVA | #1DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 45 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D01 | 下營DS | 0 |  | 1DTR(A) | #1DTR(A) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 下營DS.#1DTR(A)_LOAD | #1DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 46 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D01 | 下營DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PF | [25 empty] | ADCS_N | [8 empty] | 下營DS.#1DTR(A)_PF | #1DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 47 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D01 | 下營DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 下營DS.#1DTR(B)_MVA | #1DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 48 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D01 | 下營DS | 0 |  | 1DTR(B) | #1DTR(B) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 下營DS.#1DTR(B)_LOAD | #1DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 49 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D01 | 下營DS | 0 |  | 1DTR(B) | #1DTR(B) |  | PF | [25 empty] | ADCS_N | [8 empty] | 下營DS.#1DTR(B)_PF | #1DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 50 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D01 | 下營DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 下營DS.#2DTR(A)_MVA | #2DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 51 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D01 | 下營DS | 0 |  | 2DTR(A) | #2DTR(A) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 下營DS.#2DTR(A)_LOAD | #2DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 52 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D01 | 下營DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PF | [25 empty] | ADCS_N | [8 empty] | 下營DS.#2DTR(A)_PF | #2DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 53 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D01 | 下營DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 下營DS.#2DTR(B)_MVA | #2DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 54 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D01 | 下營DS | 0 |  | 2DTR(B) | #2DTR(B) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 下營DS.#2DTR(B)_LOAD | #2DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 55 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D01 | 下營DS | 0 |  | 2DTR(B) | #2DTR(B) |  | PF | [25 empty] | ADCS_N | [8 empty] | 下營DS.#2DTR(B)_PF | #2DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 56 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D01 | 下營DS | 0 |  | 1DTR | #1DTR |  | MW | [25 empty] | ADCS_N | [8 empty] | 下營DS.#1DTR_MW | #1DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 57 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  | 1DTR | #1DTR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 下營DS.#1DTR_MVAR | #1DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 58 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  | 1DTR | #1DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 下營DS.#1DTR_MVA | #1DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 59 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D01 | 下營DS | 0 |  | 1DTR | #1DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 下營DS.#1DTR_LOAD | #1DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 60 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D01 | 下營DS | 0 |  | 1DTR | #1DTR |  | PF | [25 empty] | ADCS_N | [8 empty] | 下營DS.#1DTR_PF | #1DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 61 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D01 | 下營DS | 0 |  | 2DTR | #2DTR |  | MW | [25 empty] | ADCS_N | [8 empty] | 下營DS.#2DTR_MW | #2DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 62 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  | 2DTR | #2DTR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 下營DS.#2DTR_MVAR | #2DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 63 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  | 2DTR | #2DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 下營DS.#2DTR_MVA | #2DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 64 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D01 | 下營DS | 0 |  | 2DTR | #2DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 下營DS.#2DTR_LOAD | #2DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 65 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D01 | 下營DS | 0 |  | 2DTR | #2DTR |  | PF | [25 empty] | ADCS_N | [8 empty] | 下營DS.#2DTR_PF | #2DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 66 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D01 | 下營DS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 下營DS.210_SC_MVAR | 11KV#1SC MVAR | SC | D01/11/210/MVAR |  | SC_LBS_11 |  |  | 67 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 11 | 11kV | 230_SC | #3SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 下營DS.230_SC_MVAR | 11KV#3SC MVAR | SC | D01/11/230/MVAR |  | SC_LBS_11 |  |  | 68 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 22 | 22kV | 220_SC | #2SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 下營DS.220_SC_MVAR | 23KV#2SC MVAR | SC | D01/22/220/MVAR |  | SC_CAL_23 |  |  | 69 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 22 | 22kV | 240_SC | #4SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 下營DS.240_SC_MVAR | 23KV#4SC MVAR | SC | D01/22/240/MVAR |  | SC_CAL_23 |  |  | 70 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  | TRTOT | 下營主變瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 下營DS.TRTOT_MW | 下營主變瞬時供電量 MW | OTHER |  |  | MTR_PQ_CAL |  |  | 71 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 0 |  | TRTOT | 下營主變瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 下營DS.TRTOT_MVAR | 下營主變瞬時供電量 MVAR | OTHER |  |  | MTR_PQ_CAL |  |  | 72 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 161 | 161kV | 1530 | 下營威致官田鋼(1530) |  | I | [25 empty] | ADCS_N | [8 empty] | 下營DS.1530_AMP | 下營威致官田鋼 AMP | LINE161 | D01/161/1530/I |  | AMP_CAL |  |  | 73 | CalcAIPoint | [21 empty] | C20R0964 | 867.599976 | 867.599976 | 964.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D01 | 下營DS | 161 | 161kV | 1510_AMP | 新營下營一路 | [27 empty] | ADCS_N | [8 empty] | 下營DS.1510_AMP_A | 新營下營一路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 74 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D01 | 下營DS | 0 |  | 100_CB | 100(100_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.100_CB_3 | 100 CB (D3) | TIE |  |  | AD_LAMP_DD_1 |  |  | 75 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | 200_CB | 200(200_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.200_CB_3 | 200 CB (D3) | TIE |  |  | AD_LAMP_DD_1 |  |  | 76 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | 1750_CB | #1DTR(1750_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.1750_CB_3 | 1750(#1DTR) CB (D3) | MTR |  |  | AD_LAMP_DD_1 |  |  | 77 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | 310_CB | #1DTR(310_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.310_CB_3 | 310(#1DTR) CB (D3) | MTR |  |  | AD_LAMP_DD_1 |  |  | 78 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | 320_CB | #1DTR(320_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.320_CB_3 | 320(#1DTR) CB (D3) | MTR |  |  | AD_LAMP_DD_1 |  |  | 79 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | 1760_CB | #2DTR(1760_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.1760_CB_3 | 1760(#2DTR) CB (D3) | MTR |  |  | AD_LAMP_DD_1 |  |  | 80 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | 330_CB | #2DTR(330_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.330_CB_3 | 330(#2DTR) CB (D3) | MTR |  |  | AD_LAMP_DD_1 |  |  | 81 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | 340_CB | #2DTR(340_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.340_CB_3 | 340(#2DTR) CB (D3) | MTR |  |  | AD_LAMP_DD_1 |  |  | 82 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | 210_CB | #1SC(210_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.210_CB_3 | 210(11KV #1SC) CB (D3) | SC |  |  | AD_LAMP_DD_1 |  |  | 83 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | 230_CB | #3SC(230_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.230_CB_3 | 230(11KV #3SC) CB (D3) | SC |  |  | AD_LAMP_DD_1 |  |  | 84 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | 220_CB | #2SC(220_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.220_CB_3 | 220(23KV #2SC) CB (D3) | SC |  |  | AD_LAMP_DD_1 |  |  | 85 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | 240_CB | #4SC(240_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.240_CB_3 | 240(23KV #4SC) CB (D3) | SC |  |  | AD_LAMP_DD_1 |  |  | 86 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | 11__CBA | 11/斷路器重故障(11__CBA) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.11/23KV_CBA_3 | 11/23KV斷路器重故障 (D3) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 87 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | 11__CBF | 11/斷路器輕故障(11__CBF) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.11/23KV_CBF_3 | 11/23KV斷路器輕故障 (D3) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 88 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  | COMM_S_L | 通訊處理單元 |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.COMM_S/L_3 | 通訊處理單元 SUPY/LOCAL (D3) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 89 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D01 | 下營DS | 0 |  | PMCC故障 | PMCC電驛故障 |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.PMCC故障_3 | PMCC電驛故障 (D3) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 90 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  | TCA | 斷路器跳脫回路故障 |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.TCA_3 | 斷路器跳脫回路故障 (D3) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 91 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_N | [8 empty] | 下營DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | D01/0/CalcPoint/SUBA |  | STATION_FAULT_10 |  |  | 92 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 變電所輕故障點燈 | 變電所輕故障點燈 |  | SUBF | [25 empty] | ADCS_N | [8 empty] | 下營DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | D01/0/CalcPoint/SUBF |  | STATION_FAULT_2 |  |  | 93 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.變電所重故障_3 | 變電所重故障點燈 (D3) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 94 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.變電所輕故障_3 | 變電所輕故障點燈 (D3) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 95 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1520_AMP | 新營下營二路 | [27 empty] | ADCS_N | [8 empty] | 下營DS.1520_AMP_A | 新營下營二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 96 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D01 | 下營DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PERM | [25 empty] | ADCS_N | [8 empty] | 下營DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | D01//1DTR(A)/TR_PERM |  | DTR_PERM |  |  | 97 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D01 | 下營DS | 0 |  | 1DTR(B) | #1DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 下營DS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | D01//1DTR(B)/TR_PERM |  | DTR_PERM |  |  | 98 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D01 | 下營DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PERM | [25 empty] | ADCS_N | [8 empty] | 下營DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | D01//2DTR(A)/TR_PERM |  | DTR_PERM |  |  | 99 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D01 | 下營DS | 0 |  | 2DTR(B) | #2DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 下營DS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | D01//2DTR(B)/TR_PERM |  | DTR_PERM |  |  | 100 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D01 | 下營DS | 0 |  | 1DTR_MVA | #1DTR | [27 empty] | ADCS_N | [8 empty] | 下營DS.#1DTR_MVA_A | #1DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 101 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D01 | 下營DS | 0 |  | 1DTR_MVA | #1DTR |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.#1DTR_MVA_3 | #1DTR MVA 點燈 (D3) | MTR |  |  | AD_LAMP_DD_2 |  |  | 102 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D01 | 下營DS | 0 |  | 2DTR_MVA | #2DTR | [27 empty] | ADCS_N | [8 empty] | 下營DS.#2DTR_MVA_A | #2DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 103 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D01 | 下營DS | 0 |  | 2DTR_MVA | #2DTR |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.#2DTR_MVA_3 | #2DTR MVA 點燈 (D3) | MTR |  |  | AD_LAMP_DD_2 |  |  | 104 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D01 | 下營DS | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_N | [8 empty] | 下營DS.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_DS |  |  | 105 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1530_AMP | 下營威致官田鋼 | [27 empty] | ADCS_N | [8 empty] | 下營DS.1530_AMP_A | 下營威致官田鋼 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 106 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D01 | 下營DS | 0 |  | 2DTR_MVA | #2DTR(B) |  | 4 | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.#2DTR_MVA_4 | #2DTR(B) MVA 點燈 (D3) | MTR |  |  | MAP_SET |  |  | 107 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D01 | 下營DS | 0 |  | 1DTR_MVA | #1DTR(B) |  | 4 | [25 empty] | DDCS3_1 | [8 empty] | 下營DS.#1DTR_MVA_4 | #1DTR(B) MVA 點燈 (D3) | MTR |  |  | MAP_SET |  |  | 108 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D01 | 下營DS | 0 |  | 1ABUS | #1ABUS |  | 11KV#1ABUSC | [25 empty] | CDCS | [8 empty] | 下營DS.11KV#1ABUSC | #1ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 109 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D01 | 下營DS | 0 |  | 1BBUS | #1BBUS |  | 23KV#1BBUSC | [25 empty] | CDCS | [8 empty] | 下營DS.23KV#1BBUSC | #1BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 110 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D01 | 下營DS | 0 |  | 2ABUS | #2ABUS |  | 11KV#2ABUSC | [25 empty] | CDCS | [8 empty] | 下營DS.11KV#2ABUSC | #2ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 111 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D01 | 下營DS | 0 |  | 2BBUS | #2BBUS |  | 23KV#2BBUSC | [25 empty] | CDCS | [8 empty] | 下營DS.23KV#2BBUSC | #2BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 112 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D01 | 下營DS | 0 |  | TAP_OVER | TAP |  | SET | [25 empty] | ADCS_N | [8 empty] | 下營DS.TAP_OVER_SET | TAP OVER HI/LO ALARM | MTR |  |  | 5000_CB_T4 |  |  | 113 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D01 | 下營DS | 0 |  | BUS_OVER | BUS |  | SET | [25 empty] | ADCS_N | [8 empty] | 下營DS.BUS_OVER_SET | BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B4 |  |  | 114 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D01 | 下營DS | 0 |  | 注意OLTC | 注意OLTC |  | BUS電壓異常 | [25 empty] | ADCS_N | [8 empty] | 下營DS.BUS電壓異常 | 注意OLTC Tap位置,並將RPDC閉鎖 | OTHER |  |  | STATION_FAULT_2 |  |  | 115 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1BUS | #1BUS |  | V | [14 empty] | 0002 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | D01/161/1BUS/V |  |  |  | DNP | 116 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D01 | 下營DS | 161 | 161kV | 2BUS | #2BUS |  | V | [14 empty] | 0003 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | D01/161/2BUS/V |  |  |  | DNP | 117 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D01 | 下營DS | 161 | 161kV | 1510 | 新營下營一路(1510) |  | MW | [14 empty] | 0004 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.1510_MW | 新營下營一路 MW | LINE161 | D01/161/1510/MW |  |  |  | DNP | 118 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D01 | 下營DS | 161 | 161kV | 1510 | 新營下營一路(1510) |  | MVAR | [14 empty] | 0005 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.1510_MVAR | 新營下營一路 MVAR | LINE161 | D01/161/1510/MVAR |  |  |  | DNP | 119 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D01 | 下營DS | 161 | 161kV | 1510LPD | 新營下營一路(1510) |  | V | [14 empty] | 0016 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.1510LPD_KV | 新營下營一路(1510) LPD KV | LINE161 | D01/161/1510/V |  |  |  | DNP | 120 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D01 | 下營DS | 161 | 161kV | 1520 | 新營下營二路(1520) |  | MW | [14 empty] | 0006 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.1520_MW | 新營下營二路 MW | LINE161 | D01/161/1520/MW |  |  |  | DNP | 121 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D01 | 下營DS | 161 | 161kV | 1520 | 新營下營二路(1520) |  | MVAR | [14 empty] | 0007 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.1520_MVAR | 新營下營二路 MVAR | LINE161 | D01/161/1520/MVAR |  |  |  | DNP | 122 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D01 | 下營DS | 161 | 161kV | 1520LPD | 新營下營二路(1520) |  | V | [14 empty] | 0017 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.1520LPD_KV | 新營下營二路(1520) LPD KV | LINE161 | D01/161/1520/V |  |  |  | DNP | 123 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D01 | 下營DS | 11 | 11kV | 1ABUS | #1ABUS |  | V | [14 empty] | 0066 | [8 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.11KV#1ABUS_KV | 11KV #1ABUS KV | BUS | D01/11/1ABUS/V |  |  |  | DNP | 124 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D01 | 下營DS | 11 | 11kV | 2ABUS | #2ABUS |  | V | [14 empty] | 0078 | [8 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS | D01/11/2ABUS/V |  |  |  | DNP | 125 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D01 | 下營DS | 22 | 22kV | 1BBUS | #1BBUS |  | V | [14 empty] | 0072 | [8 empty] | kV_-18_18(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.23KV#1BBUS_KV | 23KV #1BBUS KV | BUS | D01/22/1BBUS/V |  |  |  | DNP | 126 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D01 | 下營DS | 22 | 22kV | 2BBUS | #2BBUS |  | V | [14 empty] | 0084 | [8 empty] | kV_-18_18(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.23KV#2BBUS_KV | 23KV #2BBUS KV | BUS | D01/22/2BBUS/V |  |  |  | DNP | 127 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D01 | 下營DS | 11 | 11kV | 營一線 | 營一線 |  | 營一線KVAR | [14 empty] | 0130 | [8 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營一線KVAR | 11KV營一線 KVAR | FEEDER | D01/11/VK21/KVAR |  |  |  | DNP | 128 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營一線 | 營一線 |  | 營一線A1 | [14 empty] | 0131 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營一線A1 | 11KV營一線 R相AMP | FEEDER | D01/11/VK21/I_R |  |  |  | DNP | 129 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營一線 | 營一線 |  | 營一線A2 | [14 empty] | 0132 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營一線A2 | 11KV營一線 S相AMP | FEEDER | D01/11/VK21/I_S |  |  |  | DNP | 130 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營一線 | 營一線 |  | 營一線A3 | [14 empty] | 0133 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營一線A3 | 11KV營一線 T相AMP | FEEDER | D01/11/VK21/I_T |  |  |  | DNP | 131 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營一線 | 營一線 |  | 營一線A0 | [14 empty] | 0134 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營一線A0 | 11KV營一線 N相AMP | FEEDER | D01/11/VK21/I_N |  |  |  | DNP | 132 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營七線 | 營七線 |  | 營七線KVAR | [14 empty] | 0209 | [8 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營七線KVAR | 11KV營七線 KVAR | FEEDER | D01/11/VK27/KVAR |  |  |  | DNP | 133 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營七線 | 營七線 |  | 營七線A1 | [14 empty] | 0210 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營七線A1 | 11KV營七線 R相AMP | FEEDER | D01/11/VK27/I_R |  |  |  | DNP | 134 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營七線 | 營七線 |  | 營七線A2 | [14 empty] | 0211 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營七線A2 | 11KV營七線 S相AMP | FEEDER | D01/11/VK27/I_S |  |  |  | DNP | 135 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營七線 | 營七線 |  | 營七線A3 | [14 empty] | 0212 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營七線A3 | 11KV營七線 T相AMP | FEEDER | D01/11/VK27/I_T |  |  |  | DNP | 136 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營七線 | 營七線 |  | 營七線A0 | [14 empty] | 0213 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營七線A0 | 11KV營七線 N相AMP | FEEDER | D01/11/VK27/I_N |  |  |  | DNP | 137 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營九線 | 營九線 |  | 營九線KVAR | [14 empty] | 0199 | [8 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營九線KVAR | 11KV營九線 KVAR | FEEDER | D01/11/VK29/KVAR |  |  |  | DNP | 138 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營九線 | 營九線 |  | 營九線A1 | [14 empty] | 0200 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營九線A1 | 11KV營九線 R相AMP | FEEDER | D01/11/VK29/I_R |  |  |  | DNP | 139 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營九線 | 營九線 |  | 營九線A2 | [14 empty] | 0201 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營九線A2 | 11KV營九線 S相AMP | FEEDER | D01/11/VK29/I_S |  |  |  | DNP | 140 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營九線 | 營九線 |  | 營九線A3 | [14 empty] | 0202 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營九線A3 | 11KV營九線 T相AMP | FEEDER | D01/11/VK29/I_T |  |  |  | DNP | 141 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營九線 | 營九線 |  | 營九線A0 | [14 empty] | 0203 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營九線A0 | 11KV營九線 N相AMP | FEEDER | D01/11/VK29/I_N |  |  |  | DNP | 142 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營二線 | 營二線 |  | 營二線KVAR | [14 empty] | 0135 | [8 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營二線KVAR | 11KV營二線 KVAR | FEEDER | D01/11/VK22/KVAR |  |  |  | DNP | 143 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營二線 | 營二線 |  | 營二線A1 | [14 empty] | 0136 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營二線A1 | 11KV營二線 R相AMP | FEEDER | D01/11/VK22/I_R |  |  |  | DNP | 144 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營二線 | 營二線 |  | 營二線A2 | [14 empty] | 0137 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營二線A2 | 11KV營二線 S相AMP | FEEDER | D01/11/VK22/I_S |  |  |  | DNP | 145 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營二線 | 營二線 |  | 營二線A3 | [14 empty] | 0138 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營二線A3 | 11KV營二線 T相AMP | FEEDER | D01/11/VK22/I_T |  |  |  | DNP | 146 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營二線 | 營二線 |  | 營二線A0 | [14 empty] | 0139 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營二線A0 | 11KV營二線 N相AMP | FEEDER | D01/11/VK22/I_N |  |  |  | DNP | 147 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營八線 | 營八線 |  | 營八線KVAR | [14 empty] | 0204 | [8 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營八線KVAR | 11KV營八線 KVAR | FEEDER | D01/11/VK28/KVAR |  |  |  | DNP | 148 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營八線 | 營八線 |  | 營八線A1 | [14 empty] | 0205 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營八線A1 | 11KV營八線 R相AMP | FEEDER | D01/11/VK28/I_R |  |  |  | DNP | 149 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營八線 | 營八線 |  | 營八線A2 | [14 empty] | 0206 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營八線A2 | 11KV營八線 S相AMP | FEEDER | D01/11/VK28/I_S |  |  |  | DNP | 150 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營八線 | 營八線 |  | 營八線A3 | [14 empty] | 0207 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營八線A3 | 11KV營八線 T相AMP | FEEDER | D01/11/VK28/I_T |  |  |  | DNP | 151 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營八線 | 營八線 |  | 營八線A0 | [14 empty] | 0208 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營八線A0 | 11KV營八線 N相AMP | FEEDER | D01/11/VK28/I_N |  |  |  | DNP | 152 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營十線 | 營十線 |  | 營十線KVAR | [14 empty] | 0194 | [8 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營十線KVAR | 11KV營十線 KVAR | FEEDER | D01/11/VK30/KVAR |  |  |  | DNP | 153 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營十線 | 營十線 |  | 營十線A1 | [14 empty] | 0195 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營十線A1 | 11KV營十線 R相AMP | FEEDER | D01/11/VK30/I_R |  |  |  | DNP | 154 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營十線 | 營十線 |  | 營十線A2 | [14 empty] | 0196 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營十線A2 | 11KV營十線 S相AMP | FEEDER | D01/11/VK30/I_S |  |  |  | DNP | 155 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營十線 | 營十線 |  | 營十線A3 | [14 empty] | 0197 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營十線A3 | 11KV營十線 T相AMP | FEEDER | D01/11/VK30/I_T |  |  |  | DNP | 156 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營十線 | 營十線 |  | 營十線A0 | [14 empty] | 0198 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營十線A0 | 11KV營十線 N相AMP | FEEDER | D01/11/VK30/I_N |  |  |  | DNP | 157 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營三線 | 營三線 |  | 營三線KVAR | [14 empty] | 0140 | [8 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營三線KVAR | 11KV營三線 KVAR | FEEDER | D01/11/VK23/KVAR |  |  |  | DNP | 158 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營三線 | 營三線 |  | 營三線A1 | [14 empty] | 0141 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營三線A1 | 11KV營三線 R相AMP | FEEDER | D01/11/VK23/I_R |  |  |  | DNP | 159 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營三線 | 營三線 |  | 營三線A2 | [14 empty] | 0142 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營三線A2 | 11KV營三線 S相AMP | FEEDER | D01/11/VK23/I_S |  |  |  | DNP | 160 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營三線 | 營三線 |  | 營三線A3 | [14 empty] | 0143 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營三線A3 | 11KV營三線 T相AMP | FEEDER | D01/11/VK23/I_T |  |  |  | DNP | 161 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營三線 | 營三線 |  | 營三線A0 | [14 empty] | 0144 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營三線A0 | 11KV營三線 N相AMP | FEEDER | D01/11/VK23/I_N |  |  |  | DNP | 162 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營五線 | 營五線 |  | 營五線KVAR | [14 empty] | 0150 | [8 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營五線KVAR | 11KV營五線 KVAR | FEEDER | D01/11/VK25/KVAR |  |  |  | DNP | 163 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營五線 | 營五線 |  | 營五線A1 | [14 empty] | 0151 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營五線A1 | 11KV營五線 R相AMP | FEEDER | D01/11/VK25/I_R |  |  |  | DNP | 164 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營五線 | 營五線 |  | 營五線A2 | [14 empty] | 0152 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營五線A2 | 11KV營五線 S相AMP | FEEDER | D01/11/VK25/I_S |  |  |  | DNP | 165 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營五線 | 營五線 |  | 營五線A3 | [14 empty] | 0153 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營五線A3 | 11KV營五線 T相AMP | FEEDER | D01/11/VK25/I_T |  |  |  | DNP | 166 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營五線 | 營五線 |  | 營五線A0 | [14 empty] | 0154 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營五線A0 | 11KV營五線 N相AMP | FEEDER | D01/11/VK25/I_N |  |  |  | DNP | 167 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營六線 | 營六線 |  | 營六線KVAR | [14 empty] | 0214 | [8 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營六線KVAR | 11KV營六線 KVAR | FEEDER | D01/11/VK26/KVAR |  |  |  | DNP | 168 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營六線 | 營六線 |  | 營六線A1 | [14 empty] | 0215 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營六線A1 | 11KV營六線 R相AMP | FEEDER | D01/11/VK26/I_R |  |  |  | DNP | 169 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營六線 | 營六線 |  | 營六線A2 | [14 empty] | 0216 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營六線A2 | 11KV營六線 S相AMP | FEEDER | D01/11/VK26/I_S |  |  |  | DNP | 170 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營六線 | 營六線 |  | 營六線A3 | [14 empty] | 0217 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營六線A3 | 11KV營六線 T相AMP | FEEDER | D01/11/VK26/I_T |  |  |  | DNP | 171 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營六線 | 營六線 |  | 營六線A0 | [14 empty] | 0218 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營六線A0 | 11KV營六線 N相AMP | FEEDER | D01/11/VK26/I_N |  |  |  | DNP | 172 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營正線 | 營正線 |  | 營正線KVAR | [14 empty] | 0145 | [8 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營正線KVAR | 11KV營正線 KVAR | FEEDER | D01/11/VK24/KVAR |  |  |  | DNP | 173 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營正線 | 營正線 |  | 營正線A1 | [14 empty] | 0146 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營正線A1 | 11KV營正線 R相AMP | FEEDER | D01/11/VK24/I_R |  |  |  | DNP | 174 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營正線 | 營正線 |  | 營正線A2 | [14 empty] | 0147 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營正線A2 | 11KV營正線 S相AMP | FEEDER | D01/11/VK24/I_S |  |  |  | DNP | 175 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營正線 | 營正線 |  | 營正線A3 | [14 empty] | 0148 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營正線A3 | 11KV營正線 T相AMP | FEEDER | D01/11/VK24/I_T |  |  |  | DNP | 176 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | 營正線 | 營正線 |  | 營正線A0 | [14 empty] | 0149 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營正線A0 | 11KV營正線 N相AMP | FEEDER | D01/11/VK24/I_N |  |  |  | DNP | 177 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營51線 | 營51線 |  | 營51線KVAR | [14 empty] | 0155 | [8 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營51線KVAR | 23KV營51線 KVAR | FEEDER | D01/22/VK51/KVAR |  |  |  | DNP | 178 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營51線 | 營51線 |  | 營51線A1 | [14 empty] | 0156 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營51線A1 | 23KV營51線 R相AMP | FEEDER | D01/22/VK51/I_R |  |  |  | DNP | 179 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營51線 | 營51線 |  | 營51線A2 | [14 empty] | 0157 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營51線A2 | 23KV營51線 S相AMP | FEEDER | D01/22/VK51/I_S |  |  |  | DNP | 180 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營51線 | 營51線 |  | 營51線A3 | [14 empty] | 0158 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營51線A3 | 23KV營51線 T相AMP | FEEDER | D01/22/VK51/I_T |  |  |  | DNP | 181 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營51線 | 營51線 |  | 營51線A0 | [14 empty] | 0159 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營51線A0 | 23KV營51線 N相AMP | FEEDER | D01/22/VK51/I_N |  |  |  | DNP | 182 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營52線 | 營52線 |  | 營52線KVAR | [14 empty] | 0160 | [8 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營52線KVAR | 23KV營52線 KVAR | FEEDER | D01/22/VK52/KVAR |  |  |  | DNP | 183 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營52線 | 營52線 |  | 營52線A1 | [14 empty] | 0161 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營52線A1 | 23KV營52線 R相AMP | FEEDER | D01/22/VK52/I_R |  |  |  | DNP | 184 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營52線 | 營52線 |  | 營52線A2 | [14 empty] | 0162 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營52線A2 | 23KV營52線 S相AMP | FEEDER | D01/22/VK52/I_S |  |  |  | DNP | 185 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營52線 | 營52線 |  | 營52線A3 | [14 empty] | 0163 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營52線A3 | 23KV營52線 T相AMP | FEEDER | D01/22/VK52/I_T |  |  |  | DNP | 186 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營52線 | 營52線 |  | 營52線A0 | [14 empty] | 0164 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營52線A0 | 23KV營52線 N相AMP | FEEDER | D01/22/VK52/I_N |  |  |  | DNP | 187 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營53線 | 營53線 |  | 營53線KVAR | [14 empty] | 0165 | [8 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營53線KVAR | 23KV營53線 KVAR | FEEDER | D01/22/VK53/KVAR |  |  |  | DNP | 188 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營53線 | 營53線 |  | 營53線A1 | [14 empty] | 0166 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營53線A1 | 23KV營53線 R相AMP | FEEDER | D01/22/VK53/I_R |  |  |  | DNP | 189 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營53線 | 營53線 |  | 營53線A2 | [14 empty] | 0167 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營53線A2 | 23KV營53線 S相AMP | FEEDER | D01/22/VK53/I_S |  |  |  | DNP | 190 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營53線 | 營53線 |  | 營53線A3 | [14 empty] | 0168 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營53線A3 | 23KV營53線 T相AMP | FEEDER | D01/22/VK53/I_T |  |  |  | DNP | 191 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營53線 | 營53線 |  | 營53線A0 | [14 empty] | 0169 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營53線A0 | 23KV營53線 N相AMP | FEEDER | D01/22/VK53/I_N |  |  |  | DNP | 192 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營54線 | 營54線 |  | 營54線KVAR | [14 empty] | 0170 | [8 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營54線KVAR | 23KV營54線 KVAR | FEEDER | D01/22/VK54/KVAR |  |  |  | DNP | 193 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營54線 | 營54線 |  | 營54線A1 | [14 empty] | 0171 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營54線A1 | 23KV營54線 R相AMP | FEEDER | D01/22/VK54/I_R |  |  |  | DNP | 194 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營54線 | 營54線 |  | 營54線A2 | [14 empty] | 0172 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營54線A2 | 23KV營54線 S相AMP | FEEDER | D01/22/VK54/I_S |  |  |  | DNP | 195 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營54線 | 營54線 |  | 營54線A3 | [14 empty] | 0173 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營54線A3 | 23KV營54線 T相AMP | FEEDER | D01/22/VK54/I_T |  |  |  | DNP | 196 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營54線 | 營54線 |  | 營54線A0 | [14 empty] | 0174 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營54線A0 | 23KV營54線 N相AMP | FEEDER | D01/22/VK54/I_N |  |  |  | DNP | 197 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營55線 | 營55線 |  | 營55線KVAR | [14 empty] | 0175 | [8 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營55線KVAR | 23KV營55線 KVAR | FEEDER | D01/22/VK55/KVAR |  |  |  | DNP | 198 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營55線 | 營55線 |  | 營55線A1 | [14 empty] | 0176 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營55線A1 | 23KV營55線 R相AMP | FEEDER | D01/22/VK55/I_R |  |  |  | DNP | 199 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營55線 | 營55線 |  | 營55線A2 | [14 empty] | 0177 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營55線A2 | 23KV營55線 S相AMP | FEEDER | D01/22/VK55/I_S |  |  |  | DNP | 200 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營55線 | 營55線 |  | 營55線A3 | [14 empty] | 0178 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營55線A3 | 23KV營55線 T相AMP | FEEDER | D01/22/VK55/I_T |  |  |  | DNP | 201 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營55線 | 營55線 |  | 營55線A0 | [14 empty] | 0179 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營55線A0 | 23KV營55線 N相AMP | FEEDER | D01/22/VK55/I_N |  |  |  | DNP | 202 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營56線 | 營56線 |  | 營56線KVAR | [14 empty] | 0239 | [8 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營56線KVAR | 23KV營56線 KVAR | FEEDER | D01/22/VK56/KVAR |  |  |  | DNP | 203 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營56線 | 營56線 |  | 營56線A1 | [14 empty] | 0240 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營56線A1 | 23KV營56線 R相AMP | FEEDER | D01/22/VK56/I_R |  |  |  | DNP | 204 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營56線 | 營56線 |  | 營56線A2 | [14 empty] | 0241 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營56線A2 | 23KV營56線 S相AMP | FEEDER | D01/22/VK56/I_S |  |  |  | DNP | 205 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營56線 | 營56線 |  | 營56線A3 | [14 empty] | 0242 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營56線A3 | 23KV營56線 T相AMP | FEEDER | D01/22/VK56/I_T |  |  |  | DNP | 206 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營56線 | 營56線 |  | 營56線A0 | [14 empty] | 0243 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營56線A0 | 23KV營56線 N相AMP | FEEDER | D01/22/VK56/I_N |  |  |  | DNP | 207 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營57線 | 營57線 |  | 營57線KVAR | [14 empty] | 0234 | [8 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營57線KVAR | 23KV營57線 KVAR | FEEDER | D01/22/VK57/KVAR |  |  |  | DNP | 208 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營57線 | 營57線 |  | 營57線A1 | [14 empty] | 0235 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營57線A1 | 23KV營57線 R相AMP | FEEDER | D01/22/VK57/I_R |  |  |  | DNP | 209 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營57線 | 營57線 |  | 營57線A2 | [14 empty] | 0236 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營57線A2 | 23KV營57線 S相AMP | FEEDER | D01/22/VK57/I_S |  |  |  | DNP | 210 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營57線 | 營57線 |  | 營57線A3 | [14 empty] | 0237 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營57線A3 | 23KV營57線 T相AMP | FEEDER | D01/22/VK57/I_T |  |  |  | DNP | 211 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營57線 | 營57線 |  | 營57線A0 | [14 empty] | 0238 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營57線A0 | 23KV營57線 N相AMP | FEEDER | D01/22/VK57/I_N |  |  |  | DNP | 212 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營58線 | 營58線 |  | 營58線KVAR | [14 empty] | 0229 | [8 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營58線KVAR | 23KV營58線 KVAR | FEEDER | D01/22/VK58/KVAR |  |  |  | DNP | 213 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營58線 | 營58線 |  | 營58線A1 | [14 empty] | 0230 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營58線A1 | 23KV營58線 R相AMP | FEEDER | D01/22/VK58/I_R |  |  |  | DNP | 214 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營58線 | 營58線 |  | 營58線A2 | [14 empty] | 0231 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營58線A2 | 23KV營58線 S相AMP | FEEDER | D01/22/VK58/I_S |  |  |  | DNP | 215 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營58線 | 營58線 |  | 營58線A3 | [14 empty] | 0232 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營58線A3 | 23KV營58線 T相AMP | FEEDER | D01/22/VK58/I_T |  |  |  | DNP | 216 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營58線 | 營58線 |  | 營58線A0 | [14 empty] | 0233 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營58線A0 | 23KV營58線 N相AMP | FEEDER | D01/22/VK58/I_N |  |  |  | DNP | 217 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營59線 | 營59線 |  | 營59線KVAR | [14 empty] | 0224 | [8 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營59線KVAR | 23KV營59線 KVAR | FEEDER | D01/22/VK59/KVAR |  |  |  | DNP | 218 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營59線 | 營59線 |  | 營59線A1 | [14 empty] | 0225 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營59線A1 | 23KV營59線 R相AMP | FEEDER | D01/22/VK59/I_R |  |  |  | DNP | 219 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營59線 | 營59線 |  | 營59線A2 | [14 empty] | 0226 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營59線A2 | 23KV營59線 S相AMP | FEEDER | D01/22/VK59/I_S |  |  |  | DNP | 220 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營59線 | 營59線 |  | 營59線A3 | [14 empty] | 0227 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營59線A3 | 23KV營59線 T相AMP | FEEDER | D01/22/VK59/I_T |  |  |  | DNP | 221 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營59線 | 營59線 |  | 營59線A0 | [14 empty] | 0228 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營59線A0 | 23KV營59線 N相AMP | FEEDER | D01/22/VK59/I_N |  |  |  | DNP | 222 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營60線 | 營60線 |  | 營60線KVAR | [14 empty] | 0219 | [8 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營60線KVAR | 23KV營60線 KVAR | FEEDER | D01/22/VK60/KVAR |  |  |  | DNP | 223 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營60線 | 營60線 |  | 營60線A1 | [14 empty] | 0220 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營60線A1 | 23KV營60線 R相AMP | FEEDER | D01/22/VK60/I_R |  |  |  | DNP | 224 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營60線 | 營60線 |  | 營60線A2 | [14 empty] | 0221 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營60線A2 | 23KV營60線 S相AMP | FEEDER | D01/22/VK60/I_S |  |  |  | DNP | 225 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營60線 | 營60線 |  | 營60線A3 | [14 empty] | 0222 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營60線A3 | 23KV營60線 T相AMP | FEEDER | D01/22/VK60/I_T |  |  |  | DNP | 226 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | 營60線 | 營60線 |  | 營60線A0 | [14 empty] | 0223 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS3_1 | [8 empty] | 下營DS.營60線A0 | 23KV營60線 N相AMP | FEEDER | D01/22/VK60/I_N |  |  |  | DNP | 227 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 0 |  | 1500TIE | 1500TIE |  | I | [14 empty] | 0024 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.1500TIE_AMP | 1500TIE AMP | TIE | D01/161/1500/I_R |  |  |  | DNP | 228 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | _200 | 200 |  | I_R | [14 empty] | 0093 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.23KV_200_A1 | 23KV 200 R相AMP | TIE | D01/22/200/I_R |  |  |  | DNP | 229 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | _200 | 200 |  | I_S | [14 empty] | 0094 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.23KV_200_A2 | 23KV 200 S相AMP | TIE | D01/22/200/I_S |  |  |  | DNP | 230 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 22 | 22kV | _200 | 200 |  | I_T | [14 empty] | 0095 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.23KV_200_A3 | 23KV 200 T相AMP | TIE | D01/22/200/I_T |  |  |  | DNP | 231 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MW | [14 empty] | 0067 | [8 empty] | MW_-54_54(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | D01/11/310/KW |  |  |  | DNP | 232 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.054000 | 0.010000
D01 | 下營DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVAR | [14 empty] | 0068 | [8 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | D01/11/310/KVAR |  |  |  | DNP | 233 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.036000 | 0.010000
D01 | 下營DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_R | [14 empty] | 0069 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | D01/11/310/I_R |  |  |  | DNP | 234 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D01 | 下營DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_S | [14 empty] | 0070 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | D01/11/310/I_S |  |  |  | DNP | 235 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D01 | 下營DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_T | [14 empty] | 0071 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | D01/11/310/I_T |  |  |  | DNP | 236 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D01 | 下營DS | 0 |  | 1DTR | #1DTR |  | OilTemp | [14 empty] | 0032 | [8 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.#1DTR_OIL | #1DTR 油溫 | MTR | D01//1DTR/OilTemp |  |  |  | DNP | 237 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D01 | 下營DS | 0 |  | 1DTR(A) | #1DTR(A) |  | CoilTemp | [14 empty] | 0035 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | D01//1DTR(A)/CoilTemp |  |  |  | DNP | 238 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D01 | 下營DS | 0 |  | 1DTR(A) | #1DTR(A) |  | TapPosMv | [14 empty] | 0033 |  | 0101 | [6 empty] | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 下營DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | D01//1DTR(A)/TapPosMv |  |  |  | DNP | 239 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D01 | 下營DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MW | [14 empty] | 0073 | [8 empty] | MW_-108_108(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | D01/22/320/KW |  |  |  | DNP | 240 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D01 | 下營DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVAR | [14 empty] | 0074 | [8 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | D01/22/320/KVAR |  |  |  | DNP | 241 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D01 | 下營DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_R | [14 empty] | 0075 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | D01/22/320/I_R |  |  |  | DNP | 242 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D01 | 下營DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_S | [14 empty] | 0076 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | D01/22/320/I_S |  |  |  | DNP | 243 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D01 | 下營DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_T | [14 empty] | 0077 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | D01/22/320/I_T |  |  |  | DNP | 244 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D01 | 下營DS | 0 |  | 1DTR(B) | #1DTR(B) |  | CoilTemp | [14 empty] | 0036 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | D01//1DTR(B)/CoilTemp |  |  |  | DNP | 245 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D01 | 下營DS | 0 |  | 1DTR(B) | #1DTR(B) |  | TapPosMv | [14 empty] | 0034 |  | 0102 | [6 empty] | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 下營DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | D01//1DTR(B)/TapPosMv |  |  |  | DNP | 246 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D01 | 下營DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MW | [14 empty] | 0079 | [8 empty] | MW_-54_54(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | D01/11/330/KW |  |  |  | DNP | 247 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.054000 | 0.010000
D01 | 下營DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVAR | [14 empty] | 0080 | [8 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | D01/11/330/KVAR |  |  |  | DNP | 248 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.036000 | 0.010000
D01 | 下營DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_R | [14 empty] | 0081 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | D01/11/330/I_R |  |  |  | DNP | 249 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D01 | 下營DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_S | [14 empty] | 0082 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | D01/11/330/I_S |  |  |  | DNP | 250 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D01 | 下營DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_T | [14 empty] | 0083 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | D01/11/330/I_T |  |  |  | DNP | 251 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D01 | 下營DS | 0 |  | 2DTR | #2DTR |  | OilTemp | [14 empty] | 0037 | [8 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.#2DTR_OIL | #2DTR 油溫 | MTR | D01//2DTR/OilTemp |  |  |  | DNP | 252 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D01 | 下營DS | 0 |  | 2DTR(A) | #2DTR(A) |  | CoilTemp | [14 empty] | 0040 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | D01//2DTR(A)/CoilTemp |  |  |  | DNP | 253 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D01 | 下營DS | 0 |  | 2DTR(A) | #2DTR(A) |  | TapPosMv | [14 empty] | 0038 |  | 0108 | [6 empty] | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 下營DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | D01//2DTR(A)/TapPosMv |  |  |  | DNP | 254 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D01 | 下營DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MW | [14 empty] | 0085 | [8 empty] | MW_-108_108(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | D01/22/340/KW |  |  |  | DNP | 255 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D01 | 下營DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVAR | [14 empty] | 0086 | [8 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | D01/22/340/KVAR |  |  |  | DNP | 256 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D01 | 下營DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_R | [14 empty] | 0087 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | D01/22/340/I_R |  |  |  | DNP | 257 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D01 | 下營DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_S | [14 empty] | 0088 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | D01/22/340/I_S |  |  |  | DNP | 258 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D01 | 下營DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_T | [14 empty] | 0089 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | D01/22/340/I_T |  |  |  | DNP | 259 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D01 | 下營DS | 0 |  | 2DTR(B) | #2DTR(B) |  | CoilTemp | [14 empty] | 0041 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | D01//2DTR(B)/CoilTemp |  |  |  | DNP | 260 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D01 | 下營DS | 0 |  | 2DTR(B) | #2DTR(B) |  | TapPosMv | [14 empty] | 0039 |  | 0109 | [6 empty] | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 下營DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | D01//2DTR(B)/TapPosMv |  |  |  | DNP | 261 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D01 | 下營DS | 0 |  |  |  |  | DCV_N | [14 empty] | 0026 | [8 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.直流N電源電壓 | 直流N電源電壓 | OTHER | D01/0/StaDev/DCV_N |  |  |  | DNP | 262 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D01 | 下營DS | 0 |  |  |  |  | DCV_P | [14 empty] | 0025 | [8 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.直流P電源電壓 | 直流P電源電壓 | OTHER | D01/0/StaDev/DCV_P |  |  |  | DNP | 263 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D01 | 下營DS | 0 |  | AI | AI90%參考點 |  | ADCH1 | [14 empty] | 0001 | [8 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.AI_ADCH1 | AI90%參考點 ADCH1 | OTHER | D01/0/RTU/ADCH1 |  |  |  | DNP | 264 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D01 | 下營DS | 0 |  | AI | AI90%參考點 |  | ADCH2 | [14 empty] | 0065 | [8 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.AI_ADCH2 | AI90%參考點 ADCH2 | OTHER | D01/0/RTU/ADCH2 |  |  |  | DNP | 265 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D01 | 下營DS | 0 |  | AI | AI90%參考點 |  | ADCH3 | [14 empty] | 0129 | [8 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.AI_ADCH3 | AI90%參考點 ADCH3 | OTHER | D01/0/RTU/ADCH3 |  |  |  | DNP | 266 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D01 | 下營DS | 0 |  | AI | AI90%參考點 |  | ADCH4 | [14 empty] | 0193 | [8 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.AI_ADCH4 | AI90%參考點 ADCH4 | OTHER | D01/0/RTU/ADCH4 |  |  |  | DNP | 267 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D01 | 下營DS | 0 |  | AI | AI10%參考點 |  | ADCL1 | [14 empty] | 0000 | [8 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.AI_ADCL1 | AI10%參考點 ADCL1 | OTHER | D01/0/RTU/ADCL1 |  |  |  | DNP | 268 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D01 | 下營DS | 0 |  | AI | AI10%參考點 |  | ADCL2 | [14 empty] | 0064 | [8 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.AI_ADCL2 | AI10%參考點 ADCL2 | OTHER | D01/0/RTU/ADCL2 |  |  |  | DNP | 269 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D01 | 下營DS | 0 |  | AI | AI10%參考點 |  | ADCL3 | [14 empty] | 0128 | [8 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.AI_ADCL3 | AI10%參考點 ADCL3 | OTHER | D01/0/RTU/ADCL3 |  |  |  | DNP | 270 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D01 | 下營DS | 0 |  | AI | AI10%參考點 |  | ADCL4 | [14 empty] | 0192 | [8 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.AI_ADCL4 | AI10%參考點 ADCL4 | OTHER | D01/0/RTU/ADCL4 |  |  |  | DNP | 271 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | _100 | 100 |  | I_R | [14 empty] | 0090 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.11KV_100_A1 | 11KV 100 R相AMP | TIE | D01/11/100/I_R |  |  |  | DNP | 272 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | _100 | 100 |  | I_S | [14 empty] | 0091 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.11KV_100_A2 | 11KV 100 S相AMP | TIE | D01/11/100/I_S |  |  |  | DNP | 273 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 11 | 11kV | _100 | 100 |  | I_T | [14 empty] | 0092 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.11KV_100_A3 | 11KV 100 T相AMP | TIE | D01/11/100/I_T |  |  |  | DNP | 274 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D01 | 下營DS | 161 | 161kV | 1530 | 下營威致官田鋼(1530) |  | MW | [14 empty] | 0008 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.1530_MW | 下營威致官田鋼 MW | LINE161 | D01/161/1530/MW |  |  |  | DNP | 275 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D01 | 下營DS | 161 | 161kV | 1530 | 下營威致官田鋼(1530) |  | MVAR | [14 empty] | 0009 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.1530_MVAR | 下營威致官田鋼 MVAR | LINE161 | D01/161/1530/MVAR |  |  |  | DNP | 276 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D01 | 下營DS | 161 | 161kV | 1530LPD | 下營威致官田鋼(1530) |  | V | [14 empty] | 0018 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 下營DS.1530LPD_KV | 下營威致官田鋼(1530) LPD KV | LINE161 | D01/161/1530/V |  |  |  | DNP | 277 | DNPAIPoint | DS051 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D01 | 下營DS | 161 | 161kV | 1510 | 新營下營一路(1510) |  | PHA | [14 empty] | 0002 | [10 empty] | 161KV_N | [8 empty] | 下營DS.1510_PHA | 新營下營一路(1510) 相間RY | LINE161 | D01/161/1510/PHA |  |  |  | DNP | 278 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1510 | 新營下營一路(1510) |  | GDA | [14 empty] | 0003 | [10 empty] | 161KV_N | [8 empty] | 下營DS.1510_GDA | 新營下營一路(1510) 接地RY | LINE161 | D01/161/1510/GDA |  |  |  | DNP | 279 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1510 | 新營下營一路(1510) |  | 87A | [14 empty] | 0001 | [10 empty] | 161KV_N | [8 empty] | 下營DS.1510_87A | 新營下營一路(1510) 87RY | LINE161 | D01/161/1510/87A |  |  |  | DNP | 280 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1510 | 新營下營一路(1510) |  | 87UL | [14 empty] | 0515 |  | 0006 | [8 empty] | ADCS_N | [8 empty] | 下營DS.1510_87UL | 新營下營一路(1510) 87RY U/L | LINE161 | D01/161/1510/87UL |  |  |  | DNP | 281 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | USE
D01 | 下營DS | 161 | 161kV | 1510 | 新營下營一路(1510) |  | CB | [14 empty] | 0000 |  | 0000 | [8 empty] | 161KV_N | [8 empty] | 下營DS.1510_CB | 1510(新營下營一路) CB | LINE161 | D01/161/1510/CB |  |  |  | DNP | 282 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 161 | 161kV | 1510 | 新營下營一路(1510) |  | 79UL | [14 empty] | 0514 |  | 0005 | [8 empty] | ADCS_N | [8 empty] | 下營DS.1510_79UL | 新營下營一路(1510) 79RY U/L | LINE161 | D01/161/1510/79UL |  |  |  | DNP | 283 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | USE
D01 | 下營DS | 161 | 161kV | 1510 | 新營下營一路(1510) |  | DS1 | 1511 | [13 empty] | 0640 | 641 | 0001 | [8 empty] | ADCS_N | [8 empty] | 下營DS.1511_DS | 1511(新營下營一路) DS | LINE161 | D01/161/1510/DS1 |  |  |  | DNP | 284 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D01 | 下營DS | 161 | 161kV | 1510 | 新營下營一路(1510) |  | DS2 | 1512 | [13 empty] | 0642 | 643 | 0002 | [8 empty] | ADCS_N | [8 empty] | 下營DS.1512_DS | 1512(新營下營一路) DS | LINE161 | D01/161/1510/DS2 |  |  |  | DNP | 285 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D01 | 下營DS | 161 | 161kV | 1510 | 新營下營一路(1510) |  | DS3 | 1513 | [13 empty] | 0644 | 645 | 0003 | [8 empty] | ADCS_N | [8 empty] | 下營DS.1513_DS | 1513(新營下營一路) DS | LINE161 | D01/161/1510/DS3 |  |  |  | DNP | 286 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D01 | 下營DS | 161 | 161kV | 1510 | 新營下營一路(1510) |  | E3 | 1513E | [13 empty] | 0646 | 647 | 0004 | [8 empty] | ADCS_N | [8 empty] | 下營DS.1513E_ES | 1513E(新營下營一路) ES | LINE161 | D01/161/1510/ES3 |  |  |  | DNP | 287 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D01 | 下營DS | 161 | 161kV | 1520 | 新營下營二路(1520) |  | PHA | [14 empty] | 0006 | [10 empty] | 161KV_N | [8 empty] | 下營DS.1520_PHA | 新營下營二路(1520) 相間RY | LINE161 | D01/161/1520/PHA |  |  |  | DNP | 288 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1520 | 新營下營二路(1520) |  | GDA | [14 empty] | 0007 | [10 empty] | 161KV_N | [8 empty] | 下營DS.1520_GDA | 新營下營二路(1520) 接地RY | LINE161 | D01/161/1520/GDA |  |  |  | DNP | 289 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1520 | 新營下營二路(1520) |  | 87A | [14 empty] | 0005 | [10 empty] | 161KV_N | [8 empty] | 下營DS.1520_87A | 新營下營二路(1520) 87RY | LINE161 | D01/161/1520/87A |  |  |  | DNP | 290 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1520 | 新營下營二路(1520) |  | 87UL | [14 empty] | 0517 |  | 0013 | [8 empty] | ADCS_N | [8 empty] | 下營DS.1520_87UL | 新營下營二路(1520) 87RY U/L | LINE161 | D01/161/1520/87UL |  |  |  | DNP | 291 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | USE
D01 | 下營DS | 161 | 161kV | 1520 | 新營下營二路(1520) |  | CB | [14 empty] | 0004 |  | 0007 | [8 empty] | 161KV_N | [8 empty] | 下營DS.1520_CB | 1520(新營下營二路) CB | LINE161 | D01/161/1520/CB |  |  |  | DNP | 292 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 161 | 161kV | 1520 | 新營下營二路(1520) |  | 79UL | [14 empty] | 0516 |  | 0012 | [8 empty] | ADCS_N | [8 empty] | 下營DS.1520_79UL | 新營下營二路(1520) 79RY U/L | LINE161 | D01/161/1520/79UL |  |  |  | DNP | 293 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | USE
D01 | 下營DS | 161 | 161kV | 1520 | 新營下營二路(1520) |  | DS1 | 1521 | [13 empty] | 0648 | 649 | 0008 | [8 empty] | ADCS_N | [8 empty] | 下營DS.1521_DS | 1521(新營下營二路) DS | LINE161 | D01/161/1520/DS1 |  |  |  | DNP | 294 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D01 | 下營DS | 161 | 161kV | 1520 | 新營下營二路(1520) |  | DS2 | 1522 | [13 empty] | 0650 | 651 | 0009 | [8 empty] | ADCS_N | [8 empty] | 下營DS.1522_DS | 1522(新營下營二路) DS | LINE161 | D01/161/1520/DS2 |  |  |  | DNP | 295 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D01 | 下營DS | 161 | 161kV | 1520 | 新營下營二路(1520) |  | DS3 | 1523 | [13 empty] | 0652 | 653 | 0010 | [8 empty] | ADCS_N | [8 empty] | 下營DS.1523_DS | 1523(新營下營二路) DS | LINE161 | D01/161/1520/DS3 |  |  |  | DNP | 296 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D01 | 下營DS | 161 | 161kV | 1520 | 新營下營二路(1520) |  | E3 | 1523E | [13 empty] | 0654 | 655 | 0011 | [8 empty] | ADCS_N | [8 empty] | 下營DS.1523E_ES | 1523E(新營下營二路) ES | LINE161 | D01/161/1520/ES3 |  |  |  | DNP | 297 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D01 | 下營DS | 11 | 11kV | VK21 | 營一線(VK21) |  | PHA | [14 empty] | 0161 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK21_PHA | 11KV營一線(VK21) 相間RY | FEEDER | D01/11/VK21/PHA |  |  |  | DNP | 298 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK21 | 營一線(VK21) |  | GDA | [14 empty] | 0162 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK21_GDA | 11KV營一線(VK21) 接地RY | FEEDER | D01/11/VK21/GDA |  |  |  | DNP | 299 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK21 | 營一線(VK21) 79RY |  | 79UL | [14 empty] | 0896 |  | 0161 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK21_79UL | 11KV營一線(VK21) 79RY U/L | FEEDER | D01/11/VK21/79UL |  |  |  | DNP | 300 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | USE
D01 | 下營DS | 11 | 11kV | VK21_LCO | 營一線(VK21) LCO |  | TapPosMv | [14 empty] | 0897 |  | 0162 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK21_LCO_TAP | 11KV營一線(VK21) LCO TAP | FEEDER | D01/11/VK21/ADJ |  |  |  | DNP | 301 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D01 | 下營DS | 11 | 11kV | VK21 | VK21(11KV營一線) |  | CB | [14 empty] | 0160 |  | 0160 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK21_CB | VK21(11KV營一線) CB | FEEDER | D01/11/VK21/CB |  |  |  | DNP | 302 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | VK22 | 營二線(VK22) |  | PHA | [14 empty] | 0164 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK22_PHA | 11KV營二線(VK22) 相間RY | FEEDER | D01/11/VK22/PHA |  |  |  | DNP | 303 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK22 | 營二線(VK22) |  | GDA | [14 empty] | 0165 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK22_GDA | 11KV營二線(VK22) 接地RY | FEEDER | D01/11/VK22/GDA |  |  |  | DNP | 304 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK22 | 營二線(VK22) 79RY |  | 79UL | [14 empty] | 0898 |  | 0164 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK22_79UL | 11KV營二線(VK22) 79RY U/L | FEEDER | D01/11/VK22/79UL |  |  |  | DNP | 305 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | USE
D01 | 下營DS | 11 | 11kV | VK22_LCO | 營二線(VK22) LCO |  | TapPosMv | [14 empty] | 0899 |  | 0165 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK22_LCO_TAP | 11KV營二線(VK22) LCO TAP | FEEDER | D01/11/VK22/ADJ |  |  |  | DNP | 306 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D01 | 下營DS | 11 | 11kV | VK22 | VK22(11KV營二線) |  | CB | [14 empty] | 0163 |  | 0163 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK22_CB | VK22(11KV營二線) CB | FEEDER | D01/11/VK22/CB |  |  |  | DNP | 307 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | VK23 | 營三線(VK23) |  | PHA | [14 empty] | 0167 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK23_PHA | 11KV營三線(VK23) 相間RY | FEEDER | D01/11/VK23/PHA |  |  |  | DNP | 308 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK23 | 營三線(VK23) |  | GDA | [14 empty] | 0168 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK23_GDA | 11KV營三線(VK23) 接地RY | FEEDER | D01/11/VK23/GDA |  |  |  | DNP | 309 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK23 | 營三線(VK23) 79RY |  | 79UL | [14 empty] | 0900 |  | 0167 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK23_79UL | 11KV營三線(VK23) 79RY U/L | FEEDER | D01/11/VK23/79UL |  |  |  | DNP | 310 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | USE
D01 | 下營DS | 11 | 11kV | VK23_LCO | 營三線(VK23) LCO |  | TapPosMv | [14 empty] | 0901 |  | 0168 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK23_LCO_TAP | 11KV營三線(VK23) LCO TAP | FEEDER | D01/11/VK23/ADJ |  |  |  | DNP | 311 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D01 | 下營DS | 11 | 11kV | VK23 | VK23(11KV營三線) |  | CB | [14 empty] | 0166 |  | 0166 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK23_CB | VK23(11KV營三線) CB | FEEDER | D01/11/VK23/CB |  |  |  | DNP | 312 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | VK24 | 營正線(VK24) |  | PHA | [14 empty] | 0170 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK24_PHA | 11KV營正線(VK24) 相間RY | FEEDER | D01/11/VK24/PHA |  |  |  | DNP | 313 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK24 | 營正線(VK24) |  | GDA | [14 empty] | 0171 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK24_GDA | 11KV營正線(VK24) 接地RY | FEEDER | D01/11/VK24/GDA |  |  |  | DNP | 314 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK24 | 營正線(VK24) 79RY |  | 79UL | [14 empty] | 0902 |  | 0170 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK24_79UL | 11KV營正線(VK24) 79RY U/L | FEEDER | D01/11/VK24/79UL |  |  |  | DNP | 315 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | USE
D01 | 下營DS | 11 | 11kV | VK24_LCO | 營正線(VK24) LCO |  | TapPosMv | [14 empty] | 0903 |  | 0171 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK24_LCO_TAP | 11KV營正線(VK24) LCO TAP | FEEDER | D01/11/VK24/ADJ |  |  |  | DNP | 316 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D01 | 下營DS | 11 | 11kV | VK24 | VK24(11KV營正線) |  | CB | [14 empty] | 0169 |  | 0169 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK24_CB | VK24(11KV營正線) CB | FEEDER | D01/11/VK24/CB |  |  |  | DNP | 317 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | VK25 | 營五線(VK25) |  | PHA | [14 empty] | 0173 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK25_PHA | 11KV營五線(VK25) 相間RY | FEEDER | D01/11/VK25/PHA |  |  |  | DNP | 318 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK25 | 營五線(VK25) |  | GDA | [14 empty] | 0174 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK25_GDA | 11KV營五線(VK25) 接地RY | FEEDER | D01/11/VK25/GDA |  |  |  | DNP | 319 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK25 | 營五線(VK25) 79RY |  | 79UL | [14 empty] | 0904 |  | 0173 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK25_79UL | 11KV營五線(VK25) 79RY U/L | FEEDER | D01/11/VK25/79UL |  |  |  | DNP | 320 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | USE
D01 | 下營DS | 11 | 11kV | VK25_LCO | 營五線(VK25) LCO |  | TapPosMv | [14 empty] | 0905 |  | 0174 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK25_LCO_TAP | 11KV營五線(VK25) LCO TAP | FEEDER | D01/11/VK25/ADJ |  |  |  | DNP | 321 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D01 | 下營DS | 11 | 11kV | VK25 | VK25(11KV營五線) |  | CB | [14 empty] | 0172 |  | 0172 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK25_CB | VK25(11KV營五線) CB | FEEDER | D01/11/VK25/CB |  |  |  | DNP | 322 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | VK26 | 營六線(VK26) |  | PHA | [14 empty] | 0205 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK26_PHA | 11KV營六線(VK26) 相間RY | FEEDER | D01/11/VK26/PHA |  |  |  | DNP | 323 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK26 | 營六線(VK26) |  | GDA | [14 empty] | 0206 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK26_GDA | 11KV營六線(VK26) 接地RY | FEEDER | D01/11/VK26/GDA |  |  |  | DNP | 324 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK26 | 營六線(VK26) 79RY |  | 79UL | [14 empty] | 0924 |  | 0211 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK26_79UL | 11KV營六線(VK26) 79RY U/L | FEEDER | D01/11/VK26/79UL |  |  |  | DNP | 325 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | USE
D01 | 下營DS | 11 | 11kV | VK26_LCO | 營六線(VK26) LCO |  | TapPosMv | [14 empty] | 0925 |  | 0212 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK26_LCO_TAP | 11KV營六線(VK26) LCO TAP | FEEDER | D01/11/VK26/ADJ |  |  |  | DNP | 326 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D01 | 下營DS | 11 | 11kV | VK26 | VK26(11KV營六線) |  | CB | [14 empty] | 0204 |  | 0210 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK26_CB | VK26(11KV營六線) CB | FEEDER | D01/11/VK26/CB |  |  |  | DNP | 327 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | VK27 | 營七線(VK27) |  | PHA | [14 empty] | 0202 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK27_PHA | 11KV營七線(VK27) 相間RY | FEEDER | D01/11/VK27/PHA |  |  |  | DNP | 328 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK27 | 營七線(VK27) |  | GDA | [14 empty] | 0203 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK27_GDA | 11KV營七線(VK27) 接地RY | FEEDER | D01/11/VK27/GDA |  |  |  | DNP | 329 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK27 | 營七線(VK27) 79RY |  | 79UL | [14 empty] | 0922 |  | 0208 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK27_79UL | 11KV營七線(VK27) 79RY U/L | FEEDER | D01/11/VK27/79UL |  |  |  | DNP | 330 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | USE
D01 | 下營DS | 11 | 11kV | VK27_LCO | 營七線(VK27) LCO |  | TapPosMv | [14 empty] | 0923 |  | 0209 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK27_LCO_TAP | 11KV營七線(VK27) LCO TAP | FEEDER | D01/11/VK27/ADJ |  |  |  | DNP | 331 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D01 | 下營DS | 11 | 11kV | VK27 | VK27(11KV營七線) |  | CB | [14 empty] | 0201 |  | 0207 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK27_CB | VK27(11KV營七線) CB | FEEDER | D01/11/VK27/CB |  |  |  | DNP | 332 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | VK28 | 營八線(VK28) |  | PHA | [14 empty] | 0199 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK28_PHA | 11KV營八線(VK28) 相間RY | FEEDER | D01/11/VK28/PHA |  |  |  | DNP | 333 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK28 | 營八線(VK28) |  | GDA | [14 empty] | 0200 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK28_GDA | 11KV營八線(VK28) 接地RY | FEEDER | D01/11/VK28/GDA |  |  |  | DNP | 334 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK28 | 營八線(VK28) 79RY |  | 79UL | [14 empty] | 0920 |  | 0205 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK28_79UL | 11KV營八線(VK28) 79RY U/L | FEEDER | D01/11/VK28/79UL |  |  |  | DNP | 335 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | USE
D01 | 下營DS | 11 | 11kV | VK28_LCO | 營八線(VK28) LCO |  | TapPosMv | [14 empty] | 0921 |  | 0206 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK28_LCO_TAP | 11KV營八線(VK28) LCO TAP | FEEDER | D01/11/VK28/ADJ |  |  |  | DNP | 336 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D01 | 下營DS | 11 | 11kV | VK28 | VK28(11KV營八線) |  | CB | [14 empty] | 0198 |  | 0204 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK28_CB | VK28(11KV營八線) CB | FEEDER | D01/11/VK28/CB |  |  |  | DNP | 337 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | VK29 | 營九線(VK29) |  | PHA | [14 empty] | 0196 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK29_PHA | 11KV營九線(VK29) 相間RY | FEEDER | D01/11/VK29/PHA |  |  |  | DNP | 338 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK29 | 營九線(VK29) |  | GDA | [14 empty] | 0197 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK29_GDA | 11KV營九線(VK29) 接地RY | FEEDER | D01/11/VK29/GDA |  |  |  | DNP | 339 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK29 | 營九線(VK29) 79RY |  | 79UL | [14 empty] | 0918 |  | 0202 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK29_79UL | 11KV營九線(VK29) 79RY U/L | FEEDER | D01/11/VK29/79UL |  |  |  | DNP | 340 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | USE
D01 | 下營DS | 11 | 11kV | VK29_LCO | 營九線(VK29) LCO |  | TapPosMv | [14 empty] | 0919 |  | 0203 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK29_LCO_TAP | 11KV營九線(VK29) LCO TAP | FEEDER | D01/11/VK29/ADJ |  |  |  | DNP | 341 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D01 | 下營DS | 11 | 11kV | VK29 | VK29(11KV營九線) |  | CB | [14 empty] | 0195 |  | 0201 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK29_CB | VK29(11KV營九線) CB | FEEDER | D01/11/VK29/CB |  |  |  | DNP | 342 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | VK30 | 營十線(VK30) |  | PHA | [14 empty] | 0193 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK30_PHA | 11KV營十線(VK30) 相間RY | FEEDER | D01/11/VK30/PHA |  |  |  | DNP | 343 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK30 | 營十線(VK30) |  | GDA | [14 empty] | 0194 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK30_GDA | 11KV營十線(VK30) 接地RY | FEEDER | D01/11/VK30/GDA |  |  |  | DNP | 344 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK30 | 營十線(VK30) 79RY |  | 79UL | [14 empty] | 0916 |  | 0199 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK30_79UL | 11KV營十線(VK30) 79RY U/L | FEEDER | D01/11/VK30/79UL |  |  |  | DNP | 345 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | USE
D01 | 下營DS | 11 | 11kV | VK30_LCO | 營十線(VK30) LCO |  | TapPosMv | [14 empty] | 0917 |  | 0200 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK30_LCO_TAP | 11KV營十線(VK30) LCO TAP | FEEDER | D01/11/VK30/ADJ |  |  |  | DNP | 346 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D01 | 下營DS | 11 | 11kV | VK30 | VK30(11KV營十線) |  | CB | [14 empty] | 0192 |  | 0198 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK30_CB | VK30(11KV營十線) CB | FEEDER | D01/11/VK30/CB |  |  |  | DNP | 347 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | VK51 | 營51線(VK51) |  | PHA | [14 empty] | 0176 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK51_PHA | 23KV營51線(VK51) 相間RY | FEEDER | D01/22/VK51/PHA |  |  |  | DNP | 348 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK51 | 營51線(VK51) |  | GDA | [14 empty] | 0177 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK51_GDA | 23KV營51線(VK51) 接地RY | FEEDER | D01/22/VK51/GDA |  |  |  | DNP | 349 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK51 | 營51線(VK51) 79RY |  | 79UL | [14 empty] | 0906 |  | 0176 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK51_79UL | 23KV營51線(VK51) 79RY U/L | FEEDER | D01/22/VK51/79UL |  |  |  | DNP | 350 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | USE
D01 | 下營DS | 22 | 22kV | VK51_LCO | 營51線(VK51) LCO |  | TapPosMv | [14 empty] | 0907 |  | 0177 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK51_LCO_TAP | 23KV營51線(VK51) LCO TAP | FEEDER | D01/22/VK51/ADJ |  |  |  | DNP | 351 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D01 | 下營DS | 22 | 22kV | VK51 | VK51(23KV營51線) |  | CB | [14 empty] | 0175 |  | 0175 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK51_CB | VK51(23KV營51線) CB | FEEDER | D01/22/VK51/CB |  |  |  | DNP | 352 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | VK52 | 營52線(VK52) |  | PHA | [14 empty] | 0179 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK52_PHA | 23KV營52線(VK52) 相間RY | FEEDER | D01/22/VK52/PHA |  |  |  | DNP | 353 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK52 | 營52線(VK52) |  | GDA | [14 empty] | 0180 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK52_GDA | 23KV營52線(VK52) 接地RY | FEEDER | D01/22/VK52/GDA |  |  |  | DNP | 354 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK52 | 營52線(VK52) 79RY |  | 79UL | [14 empty] | 0908 |  | 0179 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK52_79UL | 23KV營52線(VK52) 79RY U/L | FEEDER | D01/22/VK52/79UL |  |  |  | DNP | 355 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | USE
D01 | 下營DS | 22 | 22kV | VK52_LCO | 營52線(VK52) LCO |  | TapPosMv | [14 empty] | 0909 |  | 0180 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK52_LCO_TAP | 23KV營52線(VK52) LCO TAP | FEEDER | D01/22/VK52/ADJ |  |  |  | DNP | 356 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D01 | 下營DS | 22 | 22kV | VK52 | VK52(23KV營52線) |  | CB | [14 empty] | 0178 |  | 0178 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK52_CB | VK52(23KV營52線) CB | FEEDER | D01/22/VK52/CB |  |  |  | DNP | 357 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | VK53 | 營53線(VK53) |  | PHA | [14 empty] | 0182 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK53_PHA | 23KV營53線(VK53) 相間RY | FEEDER | D01/22/VK53/PHA |  |  |  | DNP | 358 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK53 | 營53線(VK53) |  | GDA | [14 empty] | 0183 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK53_GDA | 23KV營53線(VK53) 接地RY | FEEDER | D01/22/VK53/GDA |  |  |  | DNP | 359 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK53 | 營53線(VK53) 79RY |  | 79UL | [14 empty] | 0910 |  | 0182 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK53_79UL | 23KV營53線(VK53) 79RY U/L | FEEDER | D01/22/VK53/79UL |  |  |  | DNP | 360 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | USE
D01 | 下營DS | 22 | 22kV | VK53_LCO | 營53線(VK53) LCO |  | TapPosMv | [14 empty] | 0911 |  | 0183 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK53_LCO_TAP | 23KV營53線(VK53) LCO TAP | FEEDER | D01/22/VK53/ADJ |  |  |  | DNP | 361 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D01 | 下營DS | 22 | 22kV | VK53 | VK53(23KV營53線) |  | CB | [14 empty] | 0181 |  | 0181 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK53_CB | VK53(23KV營53線) CB | FEEDER | D01/22/VK53/CB |  |  |  | DNP | 362 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | VK54 | 營54線(VK54) |  | PHA | [14 empty] | 0185 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK54_PHA | 23KV營54線(VK54) 相間RY | FEEDER | D01/22/VK54/PHA |  |  |  | DNP | 363 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK54 | 營54線(VK54) |  | GDA | [14 empty] | 0186 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK54_GDA | 23KV營54線(VK54) 接地RY | FEEDER | D01/22/VK54/GDA |  |  |  | DNP | 364 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK54 | 營54線(VK54) 79RY |  | 79UL | [14 empty] | 0912 |  | 0185 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK54_79UL | 23KV營54線(VK54) 79RY U/L | FEEDER | D01/22/VK54/79UL |  |  |  | DNP | 365 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | USE
D01 | 下營DS | 22 | 22kV | VK54_LCO | 營54線(VK54) LCO |  | TapPosMv | [14 empty] | 0913 |  | 0186 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK54_LCO_TAP | 23KV營54線(VK54) LCO TAP | FEEDER | D01/22/VK54/ADJ |  |  |  | DNP | 366 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D01 | 下營DS | 22 | 22kV | VK54 | VK54(23KV營54線) |  | CB | [14 empty] | 0184 |  | 0184 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK54_CB | VK54(23KV營54線) CB | FEEDER | D01/22/VK54/CB |  |  |  | DNP | 367 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | VK55 | 營55線(VK55) |  | PHA | [14 empty] | 0188 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK55_PHA | 23KV營55線(VK55) 相間RY | FEEDER | D01/22/VK55/PHA |  |  |  | DNP | 368 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK55 | 營55線(VK55) |  | GDA | [14 empty] | 0189 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK55_GDA | 23KV營55線(VK55) 接地RY | FEEDER | D01/22/VK55/GDA |  |  |  | DNP | 369 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK55 | 營55線(VK55) 79RY |  | 79UL | [14 empty] | 0914 |  | 0188 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK55_79UL | 23KV營55線(VK55) 79RY U/L | FEEDER | D01/22/VK55/79UL |  |  |  | DNP | 370 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | USE
D01 | 下營DS | 22 | 22kV | VK55_LCO | 營55線(VK55) LCO |  | TapPosMv | [14 empty] | 0915 |  | 0189 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK55_LCO_TAP | 23KV營55線(VK55) LCO TAP | FEEDER | D01/22/VK55/ADJ |  |  |  | DNP | 371 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D01 | 下營DS | 22 | 22kV | VK55 | VK55(23KV營55線) |  | CB | [14 empty] | 0187 |  | 0187 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK55_CB | VK55(23KV營55線) CB | FEEDER | D01/22/VK55/CB |  |  |  | DNP | 372 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | VK56 | 營56線(VK56) |  | PHA | [14 empty] | 0220 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK56_PHA | 23KV營56線(VK56) 相間RY | FEEDER | D01/22/VK56/PHA |  |  |  | DNP | 373 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK56 | 營56線(VK56) |  | GDA | [14 empty] | 0221 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK56_GDA | 23KV營56線(VK56) 接地RY | FEEDER | D01/22/VK56/GDA |  |  |  | DNP | 374 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK56 | 營56線(VK56) 79RY |  | 79UL | [14 empty] | 0934 |  | 0226 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK56_79UL | 23KV營56線(VK56) 79RY U/L | FEEDER | D01/22/VK56/79UL |  |  |  | DNP | 375 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | USE
D01 | 下營DS | 22 | 22kV | VK56_LCO | 營56線(VK56) LCO |  | TapPosMv | [14 empty] | 0935 |  | 0227 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK56_LCO_TAP | 23KV營56線(VK56) LCO TAP | FEEDER | D01/22/VK56/ADJ |  |  |  | DNP | 376 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D01 | 下營DS | 22 | 22kV | VK56 | VK56(23KV營56線) |  | CB | [14 empty] | 0219 |  | 0225 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK56_CB | VK56(23KV營56線) CB | FEEDER | D01/22/VK56/CB |  |  |  | DNP | 377 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | VK57 | 營57線(VK57) |  | PHA | [14 empty] | 0217 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK57_PHA | 23KV營57線(VK57) 相間RY | FEEDER | D01/22/VK57/PHA |  |  |  | DNP | 378 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK57 | 營57線(VK57) |  | GDA | [14 empty] | 0218 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK57_GDA | 23KV營57線(VK57) 接地RY | FEEDER | D01/22/VK57/GDA |  |  |  | DNP | 379 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK57 | 營57線(VK57) 79RY |  | 79UL | [14 empty] | 0932 |  | 0223 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK57_79UL | 23KV營57線(VK57) 79RY U/L | FEEDER | D01/22/VK57/79UL |  |  |  | DNP | 380 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | USE
D01 | 下營DS | 22 | 22kV | VK57_LCO | 營57線(VK57) LCO |  | TapPosMv | [14 empty] | 0933 |  | 0224 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK57_LCO_TAP | 23KV營57線(VK57) LCO TAP | FEEDER | D01/22/VK57/ADJ |  |  |  | DNP | 381 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D01 | 下營DS | 22 | 22kV | VK57 | VK57(23KV營57線) |  | CB | [14 empty] | 0216 |  | 0222 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK57_CB | VK57(23KV營57線) CB | FEEDER | D01/22/VK57/CB |  |  |  | DNP | 382 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | VK58 | 營58線(VK58) |  | PHA | [14 empty] | 0214 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK58_PHA | 23KV營58線(VK58) 相間RY | FEEDER | D01/22/VK58/PHA |  |  |  | DNP | 383 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK58 | 營58線(VK58) |  | GDA | [14 empty] | 0215 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK58_GDA | 23KV營58線(VK58) 接地RY | FEEDER | D01/22/VK58/GDA |  |  |  | DNP | 384 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK58 | 營58線(VK58) 79RY |  | 79UL | [14 empty] | 0930 |  | 0220 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK58_79UL | 23KV營58線(VK58) 79RY U/L | FEEDER | D01/22/VK58/79UL |  |  |  | DNP | 385 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | USE
D01 | 下營DS | 22 | 22kV | VK58_LCO | 營58線(VK58) LCO |  | TapPosMv | [14 empty] | 0931 |  | 0221 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK58_LCO_TAP | 23KV營58線(VK58) LCO TAP | FEEDER | D01/22/VK58/ADJ |  |  |  | DNP | 386 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D01 | 下營DS | 22 | 22kV | VK58 | VK58(23KV營58線) |  | CB | [14 empty] | 0213 |  | 0219 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK58_CB | VK58(23KV營58線) CB | FEEDER | D01/22/VK58/CB |  |  |  | DNP | 387 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | VK59 | 營59線(VK59) |  | PHA | [14 empty] | 0211 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK59_PHA | 23KV營59線(VK59) 相間RY | FEEDER | D01/22/VK59/PHA |  |  |  | DNP | 388 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK59 | 營59線(VK59) |  | GDA | [14 empty] | 0212 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK59_GDA | 23KV營59線(VK59) 接地RY | FEEDER | D01/22/VK59/GDA |  |  |  | DNP | 389 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK59 | 營59線(VK59) 79RY |  | 79UL | [14 empty] | 0928 |  | 0217 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK59_79UL | 23KV營59線(VK59) 79RY U/L | FEEDER | D01/22/VK59/79UL |  |  |  | DNP | 390 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | USE
D01 | 下營DS | 22 | 22kV | VK59_LCO | 營59線(VK59) LCO |  | TapPosMv | [14 empty] | 0929 |  | 0218 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK59_LCO_TAP | 23KV營59線(VK59) LCO TAP | FEEDER | D01/22/VK59/ADJ |  |  |  | DNP | 391 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D01 | 下營DS | 22 | 22kV | VK59 | VK59(23KV營59線) |  | CB | [14 empty] | 0210 |  | 0216 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK59_CB | VK59(23KV營59線) CB | FEEDER | D01/22/VK59/CB |  |  |  | DNP | 392 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | VK60 | 營60線(VK60) |  | PHA | [14 empty] | 0208 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK60_PHA | 23KV營60線(VK60) 相間RY | FEEDER | D01/22/VK60/PHA |  |  |  | DNP | 393 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK60 | 營60線(VK60) |  | GDA | [14 empty] | 0209 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK60_GDA | 23KV營60線(VK60) 接地RY | FEEDER | D01/22/VK60/GDA |  |  |  | DNP | 394 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK60 | 營60線(VK60) 79RY |  | 79UL | [14 empty] | 0926 |  | 0214 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK60_79UL | 23KV營60線(VK60) 79RY U/L | FEEDER | D01/22/VK60/79UL |  |  |  | DNP | 395 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | USE
D01 | 下營DS | 22 | 22kV | VK60_LCO | 營60線(VK60) LCO |  | TapPosMv | [14 empty] | 0927 |  | 0215 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK60_LCO_TAP | 23KV營60線(VK60) LCO TAP | FEEDER | D01/22/VK60/ADJ |  |  |  | DNP | 396 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D01 | 下營DS | 22 | 22kV | VK60 | VK60(23KV營60線) |  | CB | [14 empty] | 0207 |  | 0213 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.VK60_CB | VK60(23KV營60線) CB | FEEDER | D01/22/VK60/CB |  |  |  | DNP | 397 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | 100 | TIE(100) |  | CB | [14 empty] | 0106 |  | 0132 | [8 empty] | ADCS_N | [8 empty] | 下營DS.100_CB | 100(TIE) CB | TIE | D01/11/100/CB |  |  |  | DNP | 398 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | 100 | TIE(100) |  | 51A | [14 empty] | 0107 | [10 empty] | ADCS_N | [8 empty] | 下營DS.100_51A | 11KV TIE(100) 51RY | TIE | D01/11/100/PHA |  |  |  | DNP | 399 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 100 | TIE(100) |  | 51NA | [14 empty] | 0108 | [10 empty] | ADCS_N | [8 empty] | 下營DS.100_51NA | 11KV TIE(100) 51N RY | TIE | D01/11/100/GDA |  |  |  | DNP | 400 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [14 empty] | 0040 |  | 0070 | [8 empty] | 161KV_N | [8 empty] | 下營DS.1500_CB | 1500(TIE) CB | TIE | D01/161/1500/CB |  |  |  | DNP | 401 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | 1500 | TIE(1500) |  | 50A | [14 empty] | 0041 | [10 empty] | 161KV_N | [8 empty] | 下營DS.1500_50A | 161KV TIE(1500) 50RY | TIE | D01/161/1500/50A |  |  |  | DNP | 402 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [13 empty] | 0720 | 721 | 0071 | [8 empty] | ADCS_N | [8 empty] | 下營DS.1501_DS | 1501(TIE) DS | TIE | D01/161/1500/DS1 |  |  |  | DNP | 403 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D01 | 下營DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [13 empty] | 0722 | 723 | 0072 | [8 empty] | ADCS_N | [8 empty] | 下營DS.1502_DS | 1502(TIE) DS | TIE | D01/161/1500/DS2 |  |  |  | DNP | 404 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D01 | 下營DS | 0 |  | 1500 | TIE(1500) |  | 50SA | [14 empty] | 0998 | [10 empty] | ADCS_N | [8 empty] | 下營DS.1500_50SA | 161KV TIE(1500) 50RY 測試/正常 | TIE | D01/161/1500/50SA |  |  |  | DNP | 405 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TEST/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [13 empty] | 0732 | 733 | [9 empty] | ADCS_N | [8 empty] | 下營DS.1501E_ES | 1501E(TIE) ES | TIE | D01/161/1500/ES1 |  |  |  | DNP | 406 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D01 | 下營DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [13 empty] | 0734 | 735 | [9 empty] | ADCS_N | [8 empty] | 下營DS.1502E_ES | 1502E(TIE) ES | TIE | D01/161/1500/ES2 |  |  |  | DNP | 407 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D01 | 下營DS | 0 |  | 200 | TIE(200) |  | CB | [14 empty] | 0109 |  | 0133 | [8 empty] | ADCS_N | [8 empty] | 下營DS.200_CB | 200(TIE) CB | TIE | D01/22/200/CB |  |  |  | DNP | 408 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | 200 | TIE(200) |  | 51A | [14 empty] | 0110 | [10 empty] | ADCS_N | [8 empty] | 下營DS.200_51A | 23KV TIE(200) 51RY | TIE | D01/22/200/PHA |  |  |  | DNP | 409 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 200 | TIE(200) |  | 51NA | [14 empty] | 0111 | [10 empty] | ADCS_N | [8 empty] | 下營DS.200_51NA | 23KV TIE(200) 51N RY | TIE | D01/22/200/GDA |  |  |  | DNP | 410 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 390 | #1SSTR(390) |  | CB | [14 empty] | 0140 |  | 0134 | [8 empty] | ADCS_N | [8 empty] | 下營DS.390_CB | 390(#1SSTR) CB | OTHER | D01/11/390/CB |  |  |  | DNP | 411 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | 1SSTR | #1SSTR |  | 51A | [14 empty] | 0141 | [10 empty] | ADCS_N | [8 empty] | 下營DS.#1SSTR_51A | #1SSTR 51RY | OTHER | D01/11/390/PHA |  |  |  | DNP | 412 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 1SSTR | #1SSTR |  | 51NA | [14 empty] | 0142 | [10 empty] | ADCS_N | [8 empty] | 下營DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | D01/11/390/GDA |  |  |  | DNP | 413 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 490 | #2SSTR(490) |  | CB | [14 empty] | 0143 |  | 0135 | [8 empty] | ADCS_N | [8 empty] | 下營DS.490_CB | 490(#2SSTR) CB | OTHER | D01/22/490/CB |  |  |  | DNP | 414 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | 2SSTR | #2SSTR |  | 51A | [14 empty] | 0144 | [10 empty] | ADCS_N | [8 empty] | 下營DS.#2SSTR_51A | #2SSTR 51RY | OTHER | D01/22/490/PHA |  |  |  | DNP | 415 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 2SSTR | #2SSTR |  | 51NA | [14 empty] | 0145 | [10 empty] | ADCS_N | [8 empty] | 下營DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | D01/22/490/GDA |  |  |  | DNP | 416 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB | [14 empty] | 0056 |  | 0096 | [8 empty] | 161KV_N | [8 empty] | 下營DS.1750_CB | 1750(#1DTR) CB | MTR | D01/161/1750/CB |  |  |  | DNP | 417 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | 310 | #1DTR(310) |  | CB | [14 empty] | 0091 |  | 0128 | [8 empty] | ADCS_N | [8 empty] | 下營DS.310_CB | 310(#1DTR) CB | MTR | D01/11/310/CB |  |  |  | DNP | 418 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | 320 | #1DTR(320) |  | CB | [14 empty] | 0095 |  | 0129 | [8 empty] | ADCS_N | [8 empty] | 下營DS.320_CB | 320(#1DTR) CB | MTR | D01/22/320/CB |  |  |  | DNP | 419 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | 1DTR | #1DTR |  | 51A | [14 empty] | 0060 | [10 empty] | 161KV_N | [8 empty] | 下營DS.#1DTR_51A | #1DTR 51RY | MTR | D01/161/1750/PHA |  |  |  | DNP | 420 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 1DTR | #1DTR |  | 51NA | [14 empty] | 0061 | [10 empty] | 161KV_N | [8 empty] | 下營DS.#1DTR_51NA | #1DTR 51N RY | MTR | D01/161/1750/GDA |  |  |  | DNP | 421 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 1DTR | #1DTR |  | 51ZA | [14 empty] | 0059 | [10 empty] | 161KV_N | [8 empty] | 下營DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | D01//1DTR/51ZA |  |  |  | DNP | 422 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 1DTR | #1DTR |  | 87A | [14 empty] | 0057 | [10 empty] | 161KV_N | [8 empty] | 下營DS.#1DTR_87A | #1DTR 87RY | MTR | D01//1DTR/87A |  |  |  | DNP | 423 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 1DTR | #1DTR |  | 87UL | [14 empty] | 0544 | [10 empty] | ADCS_N | [8 empty] | 下營DS.#1DTR_87UL | #1DTR 87RY U/L | MTR | D01//1DTR/87UL |  |  |  | DNP | 424 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | USE
D01 | 下營DS | 0 |  | 310 | #1DTR(310) |  | 51A | [14 empty] | 0062 | [10 empty] | ADCS_N | [8 empty] | 下營DS.310_51A | #1DTR二次側(310) 51RY | MTR | D01/11/310/51A |  |  |  | DNP | 425 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 320 | #1DTR(320) |  | 51A | [14 empty] | 0063 | [10 empty] | ADCS_N | [8 empty] | 下營DS.320_51A | #1DTR二次側(320) 51RY | MTR | D01/22/320/51A |  |  |  | DNP | 426 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 1DTR | #1DTR |  | 96PA | [14 empty] | 0058 | [10 empty] | 161KV_N | [8 empty] | 下營DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | D01//1DTR/96PA |  |  |  | DNP | 427 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 1DTR | #1DTR |  | 96D | [14 empty] | 0551 | [10 empty] | ADCS_N | [8 empty] | 下營DS.#1DTR_96D | #1DTR 96D RY | MTR | D01//1DTR/96D |  |  |  | DNP | 428 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 1DTR | #1DTR |  | 96P | [14 empty] | 0550 | [10 empty] | ADCS_N | [8 empty] | 下營DS.#1DTR_96P | #1DTR 96P RY | MTR | D01//1DTR/96P |  |  |  | DNP | 429 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 1DTR | #1DTR |  | 63Q | [14 empty] | 0549 | [10 empty] | ADCS_N | [8 empty] | 下營DS.#1DTR_63Q | #1DTR 63Q RY | MTR | D01//1DTR/63Q |  |  |  | DNP | 430 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 1DTR | #1DTR |  | 96B1 | [14 empty] | 0552 | [10 empty] | ADCS_N | [8 empty] | 下營DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | D01//1DTR/96B1 |  |  |  | DNP | 431 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 1DTR | #1DTR |  | 96B2 | [14 empty] | 0553 | [10 empty] | ADCS_N | [8 empty] | 下營DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | D01//1DTR/96B2 |  |  |  | DNP | 432 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 1DTR | #1DTR |  | TRA | [14 empty] | 0554 | [10 empty] | ADCS_N | [8 empty] | 下營DS.#1DTR_TRA | #1DTR 重故障 | MTR | D01//1DTR/TRA |  |  |  | DNP | 433 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 1DTR | #1DTR |  | TRF | [14 empty] | 0555 | [10 empty] | ADCS_N | [8 empty] | 下營DS.#1DTR_TRF | #1DTR 輕故障 | MTR | D01//1DTR/TRF |  |  |  | DNP | 434 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 1DTR(A) | #1DTR(A) |  | SupLocal | [14 empty] | 0546 | [10 empty] | ADCS_N | [8 empty] | 下營DS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | D01//1DTR(A)/Tap Chan |  |  |  | DNP | 435 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D01 | 下營DS | 0 |  | 1DTR(A) | #1DTR(A) |  | A_M | [14 empty] | 0545 |  | 0099 | [8 empty] | ADCS_N | [8 empty] | 下營DS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | D01//1DTR(A)/SupLocal |  |  |  | DNP | 436 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D01 | 下營DS | 0 |  | 1DTR(B) | #1DTR(B) |  | SupLocal | [14 empty] | 0548 | [10 empty] | ADCS_N | [8 empty] | 下營DS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | D01//1DTR(B)/Tap Chan |  |  |  | DNP | 437 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D01 | 下營DS | 0 |  | 1DTR(B) | #1DTR(B) |  | A_M | [14 empty] | 0547 |  | 0100 | [8 empty] | ADCS_N | [8 empty] | 下營DS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | D01//1DTR(B)/SupLocal |  |  |  | DNP | 438 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D01 | 下營DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 | [13 empty] | 0724 | 725 | 0097 | [8 empty] | ADCS_N | [8 empty] | 下營DS.1751_DS | 1751(#1DTR) DS | MTR | D01/161/1750/DS1 |  |  |  | DNP | 439 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D01 | 下營DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 | [13 empty] | 0726 | 727 | 0098 | [8 empty] | ADCS_N | [8 empty] | 下營DS.1752_DS | 1752(#1DTR) DS | MTR | D01/161/1750/DS2 |  |  |  | DNP | 440 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D01 | 下營DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB | [14 empty] | 0064 |  | 0103 | [8 empty] | 161KV_N | [8 empty] | 下營DS.1760_CB | 1760(#2DTR) CB | MTR | D01/161/1760/CB |  |  |  | DNP | 441 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | 330 | #2DTR(330) |  | CB | [14 empty] | 0099 |  | 0130 | [8 empty] | ADCS_N | [8 empty] | 下營DS.330_CB | 330(#2DTR) CB | MTR | D01/11/330/CB |  |  |  | DNP | 442 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | 340 | #2DTR(340) |  | CB | [14 empty] | 0103 |  | 0131 | [8 empty] | ADCS_N | [8 empty] | 下營DS.340_CB | 340(#2DTR) CB | MTR | D01/22/340/CB |  |  |  | DNP | 443 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | 2DTR | #2DTR |  | 51A | [14 empty] | 0068 | [10 empty] | 161KV_N | [8 empty] | 下營DS.#2DTR_51A | #2DTR 51RY | MTR | D01/161/1760/PHA |  |  |  | DNP | 444 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 2DTR | #2DTR |  | 51NA | [14 empty] | 0069 | [10 empty] | 161KV_N | [8 empty] | 下營DS.#2DTR_51NA | #2DTR 51N RY | MTR | D01/161/1760/GDA |  |  |  | DNP | 445 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 2DTR | #2DTR |  | 51ZA | [14 empty] | 0067 | [10 empty] | 161KV_N | [8 empty] | 下營DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | D01//2DTR/51ZA |  |  |  | DNP | 446 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 2DTR | #2DTR |  | 87A | [14 empty] | 0065 | [10 empty] | 161KV_N | [8 empty] | 下營DS.#2DTR_87A | #2DTR 87RY | MTR | D01//2DTR/87A |  |  |  | DNP | 447 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 2DTR | #2DTR |  | 87UL | [14 empty] | 0556 | [10 empty] | ADCS_N | [8 empty] | 下營DS.#2DTR_87UL | #2DTR 87RY U/L | MTR | D01//2DTR/87UL |  |  |  | DNP | 448 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | USE
D01 | 下營DS | 0 |  | 330 | #2DTR(330) |  | 51A | [14 empty] | 0070 | [10 empty] | ADCS_N | [8 empty] | 下營DS.330_51A | #2DTR二次側(330) 51RY | MTR | D01/11/330/51A |  |  |  | DNP | 449 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 340 | #2DTR(340) |  | 51A | [14 empty] | 0071 | [10 empty] | ADCS_N | [8 empty] | 下營DS.340_51A | #2DTR二次側(340) 51RY | MTR | D01/22/340/51A |  |  |  | DNP | 450 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 2DTR | #2DTR |  | 96PA | [14 empty] | 0066 | [10 empty] | 161KV_N | [8 empty] | 下營DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | D01//2DTR/96PA |  |  |  | DNP | 451 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 2DTR | #2DTR |  | 96D | [14 empty] | 0563 | [10 empty] | ADCS_N | [8 empty] | 下營DS.#2DTR_96D | #2DTR 96D RY | MTR | D01//2DTR/96D |  |  |  | DNP | 452 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 2DTR | #2DTR |  | 96P | [14 empty] | 0562 | [10 empty] | ADCS_N | [8 empty] | 下營DS.#2DTR_96P | #2DTR 96P RY | MTR | D01//2DTR/96P |  |  |  | DNP | 453 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 2DTR | #2DTR |  | 63Q | [14 empty] | 0561 | [10 empty] | ADCS_N | [8 empty] | 下營DS.#2DTR_63Q | #2DTR 63Q RY | MTR | D01//2DTR/63Q |  |  |  | DNP | 454 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 2DTR | #2DTR |  | 96B1 | [14 empty] | 0564 | [10 empty] | ADCS_N | [8 empty] | 下營DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | D01//2DTR/96B1 |  |  |  | DNP | 455 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 2DTR | #2DTR |  | 96B2 | [14 empty] | 0565 | [10 empty] | ADCS_N | [8 empty] | 下營DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | D01//2DTR/96B2 |  |  |  | DNP | 456 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 2DTR | #2DTR |  | TRA | [14 empty] | 0566 | [10 empty] | ADCS_N | [8 empty] | 下營DS.#2DTR_TRA | #2DTR 重故障 | MTR | D01//2DTR/TRA |  |  |  | DNP | 457 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 2DTR | #2DTR |  | TRF | [14 empty] | 0567 | [10 empty] | ADCS_N | [8 empty] | 下營DS.#2DTR_TRF | #2DTR 輕故障 | MTR | D01//2DTR/TRF |  |  |  | DNP | 458 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 2DTR(A) | #2DTR(A) |  | SupLocal | [14 empty] | 0558 | [10 empty] | ADCS_N | [8 empty] | 下營DS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | D01//2DTR(A)/Tap Chan |  |  |  | DNP | 459 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D01 | 下營DS | 0 |  | 2DTR(A) | #2DTR(A) |  | A_M | [14 empty] | 0557 |  | 0106 | [8 empty] | ADCS_N | [8 empty] | 下營DS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | D01//2DTR(A)/SupLocal |  |  |  | DNP | 460 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D01 | 下營DS | 0 |  | 2DTR(B) | #2DTR(B) |  | SupLocal | [14 empty] | 0560 | [10 empty] | ADCS_N | [8 empty] | 下營DS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | D01//2DTR(B)/Tap Chan |  |  |  | DNP | 461 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D01 | 下營DS | 0 |  | 2DTR(B) | #2DTR(B) |  | A_M | [14 empty] | 0559 |  | 0107 | [8 empty] | ADCS_N | [8 empty] | 下營DS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | D01//2DTR(B)/SupLocal |  |  |  | DNP | 462 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D01 | 下營DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 | [13 empty] | 0728 | 729 | 0104 | [8 empty] | ADCS_N | [8 empty] | 下營DS.1761_DS | 1761(#2DTR) DS | MTR | D01/161/1760/DS1 |  |  |  | DNP | 463 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D01 | 下營DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 | [13 empty] | 0730 | 731 | 0105 | [8 empty] | ADCS_N | [8 empty] | 下營DS.1762_DS | 1762(#2DTR) DS | MTR | D01/161/1760/DS2 |  |  |  | DNP | 464 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D01 | 下營DS | 11 | 11kV | 210 | #1SC(210) |  | CB | [14 empty] | 0128 |  | 0136 | [8 empty] | ADCS_N | [8 empty] | 下營DS.210_CB | 210(11KV #1SC) CB | SC | D01/11/210/CB |  |  |  | DNP | 465 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [14 empty] | 0129 | [10 empty] | ADCS_N | [8 empty] | 下營DS.210_SCA | 11KV #1SC 51,51N RY | SC | D01/11/210/SCA |  |  |  | DNP | 466 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [14 empty] | 0130 | [10 empty] | ADCS_N | [8 empty] | 下營DS.210_OUVA | 11KV #1SC 27,59RY(欠壓或過壓) | SC | D01/11/210/UVA |  |  |  | DNP | 467 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | 210 | #1SC(210) |  | LBS | [14 empty] | 0740 | 741 | 0137 | [8 empty] | ADCS_N | [8 empty] | 下營DS.210_LBS | 210(11KV #1SC) LBS | SC | D01/11/1SC/LBS |  |  |  | DNP | 468 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D01 | 下營DS | 11 | 11kV | 230 | #3SC(230) |  | CB | [14 empty] | 0134 |  | 0140 | [8 empty] | ADCS_N | [8 empty] | 下營DS.230_CB | 230(11KV #3SC) CB | SC | D01/11/230/CB |  |  |  | DNP | 469 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 11 | 11kV | 230 | #3SC(230) |  | SCA | [14 empty] | 0135 | [10 empty] | ADCS_N | [8 empty] | 下營DS.230_SCA | 11KV #3SC 51,51N RY | SC | D01/11/230/SCA |  |  |  | DNP | 470 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | 230 | #3SC(230) |  | UVA | [14 empty] | 0136 | [10 empty] | ADCS_N | [8 empty] | 下營DS.230_OUVA | 11KV #3SC 27,59RY(欠壓或過壓) | SC | D01/11/230/UVA |  |  |  | DNP | 471 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | 230 | #3SC(230) |  | LBS | [14 empty] | 0744 | 745 | 0141 | [8 empty] | ADCS_N | [8 empty] | 下營DS.230_LBS | 230(11KV #3SC) LBS | SC | D01/11/3SC/LBS |  |  |  | DNP | 472 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D01 | 下營DS | 22 | 22kV | 220 | #2SC(220) |  | CB | [14 empty] | 0131 |  | 0138 | [8 empty] | ADCS_N | [8 empty] | 下營DS.220_CB | 220(23KV #2SC) CB | SC | D01/22/220/CB |  |  |  | DNP | 473 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | 220 | #2SC(220) |  | SCA | [14 empty] | 0132 | [10 empty] | ADCS_N | [8 empty] | 下營DS.220_SCA | 23KV #2SC 51,51N RY | SC | D01/22/220/SCA |  |  |  | DNP | 474 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | 220 | #2SC(220) |  | UVA | [14 empty] | 0133 | [10 empty] | ADCS_N | [8 empty] | 下營DS.220_OUVA | 23KV #2SC 27,59RY(欠壓或過壓) | SC | D01/22/220/UVA |  |  |  | DNP | 475 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | 240 | #4SC(240) |  | CB | [14 empty] | 0137 |  | 0142 | [8 empty] | ADCS_N | [8 empty] | 下營DS.240_CB | 240(23KV #4SC) CB | SC | D01/22/240/CB |  |  |  | DNP | 476 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 22 | 22kV | 240 | #4SC(240) |  | SCA | [14 empty] | 0138 | [10 empty] | ADCS_N | [8 empty] | 下營DS.240_SCA | 23KV #4SC 51,51N RY | SC | D01/22/240/SCA |  |  |  | DNP | 477 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | 240 | #4SC(240) |  | UVA | [14 empty] | 0139 | [10 empty] | ADCS_N | [8 empty] | 下營DS.240_OUVA | 23KV #4SC 27,59RY(欠壓或過壓) | SC | D01/22/240/UVA |  |  |  | DNP | 478 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1611BUS | #1BUS |  | VUA | [14 empty] | 0522 | [10 empty] | ADCS_N | [8 empty] | 下營DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | D01/161/1BUS/BUS_VUA |  |  |  | DNP | 479 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1611BUS | #1BUS |  | 87A | [14 empty] | 0042 | [10 empty] | 161KV_N | [8 empty] | 下營DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | D01/161/1BUS/87A |  |  |  | DNP | 480 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1611BUS | #1BUS |  | 87UL | [14 empty] | 0524 |  | 0078 | [8 empty] | ADCS_N | [8 empty] | 下營DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | BUS | D01/161/1BUS/87UL |  |  |  | DNP | 481 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | USE
D01 | 下營DS | 161 | 161kV | 1612BUS | #2BUS |  | VUA | [14 empty] | 0523 | [10 empty] | ADCS_N | [8 empty] | 下營DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | D01/161/2BUS/BUS_VUA |  |  |  | DNP | 482 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1612BUS | #2BUS |  | 87A | [14 empty] | 0043 | [10 empty] | 161KV_N | [8 empty] | 下營DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | D01/161/2BUS/87A |  |  |  | DNP | 483 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1612BUS | #2BUS |  | 87UL | [14 empty] | 0525 |  | 0079 | [8 empty] | ADCS_N | [8 empty] | 下營DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | BUS | D01/161/2BUS/87UL |  |  |  | DNP | 484 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | USE
D01 | 下營DS | 22 | 22kV | 11_ | 11/ |  | CBA | [14 empty] | 1010 | [10 empty] | ADCS_N | [8 empty] | 下營DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | D01/22/ComPoint/FDR_CBA |  |  |  | DNP | 485 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | 11_ | 11/ |  | CBF | [14 empty] | 1011 | [10 empty] | ADCS_N | [8 empty] | 下營DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | D01/22/ComPoint/FDR_CBF |  |  |  | DNP | 486 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | _SC | 23/ SC |  | 60A | [14 empty] | 0983 | [10 empty] | ADCS_N | [8 empty] | 下營DS.11KV_SC_60A | 23/11KV SC 60A | OTHER | D01/22/ComPoint/60A |  |  |  | DNP | 487 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV |  |  |  | CBA | [14 empty] | 1005 | [10 empty] | ADCS_N | [8 empty] | 下營DS.161KV_CBA | 161KV斷路器重故障 | OTHER | D01/161/ComPoint/CBA |  |  |  | DNP | 488 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV |  |  |  | CBF | [14 empty] | 1006 | [10 empty] | ADCS_N | [8 empty] | 下營DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | D01/161/ComPoint/CBF |  |  |  | DNP | 489 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | LINE | LINE |  | RCA | [14 empty] | 1009 | [10 empty] | ADCS_N | [8 empty] | 下營DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | D01/161/ComPoint/RCA |  |  |  | DNP | 490 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  | TEST | TEST |  | CB | [14 empty] | 0512 |  | 0077 | [8 empty] | ADCS_N | [8 empty] | 下營DS.TEST_CB | TEST CB | OTHER | D01/0/RTU/Test_CB |  |  |  | DNP | 491 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  |  |  |  | Fire1 | [14 empty] | 0973 | [10 empty] | ADCS_N | [8 empty] | 下營DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | D01/0/StaDev/Fire1 |  |  |  | DNP | 492 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  |  |  |  | Fire2 | [14 empty] | 0974 | [10 empty] | ADCS_N | [8 empty] | 下營DS.火災警報(2) | 火災警報(2) | OTHER | D01/0/StaDev/Fire2 |  |  |  | DNP | 493 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  |  |  |  | 25TA | [14 empty] | 1004 | [10 empty] | ADCS_N | [8 empty] | 下營DS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | D01/161/ComPoint/25TA |  |  |  | DNP | 494 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  |  |  |  | SUBF | [14 empty] | 0965 | [10 empty] | ADCS_N | [8 empty] | 下營DS.其他輕故障 | 變電所內其他輕故障 | OTHER | D01/0/ComPoint/PSF |  |  |  | DNP | 495 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  |  |  |  | ACB1 | [14 empty] | 0968 | [10 empty] | ADCS_N | [8 empty] | 下營DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | D01/0/StaDev/ACB1 |  |  |  | DNP | 496 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ON/OFF | ON
D01 | 下營DS | 0 |  |  |  |  | ACB2 | [14 empty] | 0969 | [10 empty] | ADCS_N | [8 empty] | 下營DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | D01/0/StaDev/ACB2 |  |  |  | DNP | 497 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ON/OFF | ON
D01 | 下營DS | 0 |  |  |  |  | ACBA | [14 empty] | 0967 | [10 empty] | ADCS_N | [8 empty] | 下營DS.所內電源ACBA | 所內電源故障警報 | OTHER | D01/0/StaDev/ACBA |  |  |  | DNP | 498 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 所內電源開關ACB | 所內電源開關ACB |  | ACBT | [14 empty] | 0970 | [10 empty] | ADCS_N | [8 empty] | 下營DS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | D01/0/StaDev/ACBT |  |  |  | DNP | 499 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ON/OFF | OFF
D01 | 下營DS | 0 |  |  |  |  | STUV | [14 empty] | 0960 | [10 empty] | ADCS_N | [8 empty] | 下營DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | D01/0/StaDev/STUV |  |  |  | DNP | 500 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  |  |  |  | CHG1 | [14 empty] | 0952 | [10 empty] | ADCS_N | [8 empty] | 下營DS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | D01/0/StaDev/CHG1 |  |  |  | DNP | 501 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  |  |  |  | DCA | [14 empty] | 0958 | [10 empty] | ADCS_N | [8 empty] | 下營DS.直流電源DCA | 直流電源故障警報 | OTHER | D01/0/StaDev/DCE |  |  |  | DNP | 502 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  |  |  |  | DCE | [14 empty] | 0959 | [10 empty] | ADCS_N | [8 empty] | 下營DS.直流電源DCE | 直流電源接地故障警報 | OTHER | D01/0/StaDev/DCA |  |  |  | DNP | 503 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  |  |  |  | CHG2 | [14 empty] | 0953 | [10 empty] | ADCS_N | [8 empty] | 下營DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | D01/0/StaDev/CHG2 |  |  |  | DNP | 504 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  |  |  |  | CommACF | [14 empty] | 0954 | [10 empty] | ADCS_N | [8 empty] | 下營DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | D01/0/StaDev/CommACF |  |  |  | DNP | 505 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  |  |  |  | Burglar1 | [14 empty] | 0985 | [10 empty] | ADCS_N | [8 empty] | 下營DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | D01/0/StaDev/Burglar1 |  |  |  | DNP | 506 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  |  |  |  | Door1 | [14 empty] | 0971 | [10 empty] | ADCS_N | [8 empty] | 下營DS.無人化門禁(1) | 無人化門禁(1)電動大小門 | OTHER | D01/0/StaDev/Door1 |  |  |  | DNP | 507 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  |  |  |  | Lights1 | [14 empty] | 0977 |  | 0075 | [8 empty] | ADCS_N | [8 empty] | 下營DS.開關場照明(A) | 景觀照明 | OTHER | D01/0/StaDev/Lights1 |  |  |  | DNP | 508 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ON/OFF | OFF
D01 | 下營DS | 0 |  |  |  |  | Lights2 | [14 empty] | 0978 |  | 0076 | [8 empty] | DDCS3_1 | [8 empty] | 下營DS.開關場照明(B) | 路燈照明 | OTHER | D01/0/StaDev/DD_Light |  |  |  | DNP | 509 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ON/OFF | OFF
D01 | 下營DS | 0 |  | 1510 | 新營下營一路(1510) |  | 87CFA | [14 empty] | 0992 | [10 empty] | ADCS_N | [8 empty] | 下營DS.1510_87CFA | 新營下營一路(1510)87RY通訊故障 | OTHER | D01/161/1510/87CFA |  |  |  | DNP | 510 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 1510 | 新營下營一路(1510) |  | RYFA | [14 empty] | 0995 | [10 empty] | ADCS_N | [8 empty] | 下營DS.1510_RYFA | 新營下營一路(1510)數位電驛故障 | OTHER | D01/161/1510/RYFA |  |  |  | DNP | 511 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 1520 | 新營下營二路(1520) |  | RYFA | [14 empty] | 0996 | [10 empty] | ADCS_N | [8 empty] | 下營DS.1520_RYFA | 新營下營二路(1520)數位電驛故障 | OTHER | D01/161/1520/RYFA |  |  |  | DNP | 512 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | _BUS | BUS |  | 87CTFA | [14 empty] | 0521 | [10 empty] | ADCS_N | [8 empty] | 下營DS.161KV_BUS_CTFA | 161KV BUS CT 回路故障 | OTHER | D01/161/ComPoint/12B_CTFA |  |  |  | DNP | 513 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | _BUS | BUS |  | RYFA | [14 empty] | 0520 | [10 empty] | ADCS_N | [8 empty] | 下營DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | D01/161/ComPoint/BUS_RYFA |  |  |  | DNP | 514 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV |  |  |  | OSCA | [14 empty] | 0044 | [10 empty] | ADCS_N | [8 empty] | 下營DS.161KV_OSCA | 161KV示波器啟動警報 | OTHER | D01/161/ComPoint/OSCA |  |  |  | DNP | 515 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV |  |  |  | OSCF | [14 empty] | 0961 | [10 empty] | ADCS_N | [8 empty] | 下營DS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | D01/161/ComPoint/OSCF |  |  |  | DNP | 516 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 310 | #1DTR(310) |  | 81A | [14 empty] | 0112 | [10 empty] | ADCS_N | [8 empty] | 下營DS.310_81A | 310 #1DTR(A) 81RY動作 | OTHER | D01/11/310/81A |  |  |  | DNP | 517 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 310 | #1DTR(310) |  | 81UL | [14 empty] | 0608 |  | 0144 | [8 empty] | ADCS_N | [8 empty] | 下營DS.310_81UL | 310 #1DTR(A) 81RY U/L | OTHER | D01//1DTR(A)/81UL |  |  |  | DNP | 518 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | USE
D01 | 下營DS | 0 |  | 310 | #1DTR(310) |  | GDA | [14 empty] | 0093 | [10 empty] | ADCS_N | [8 empty] | 下營DS.310_GDA | 310開關箱IED RY GDA | OTHER | D01/11/310/GDA |  |  |  | DNP | 519 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 310 | #1DTR(310) |  | PHA2 | [14 empty] | 0092 | [10 empty] | ADCS_N | [8 empty] | 下營DS.310_PHA2 | 310開關箱IED RY PHA | OTHER | D01/11/310/PHA |  |  |  | DNP | 520 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 320 | #1DTR(320) |  | 81A | [14 empty] | 0113 | [10 empty] | ADCS_N | [8 empty] | 下營DS.320_81A | 320 #1DTR(B) 81RY動作 | OTHER | D01/22/320/81A |  |  |  | DNP | 521 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 320 | #1DTR(320) |  | 81UL | [14 empty] | 0609 |  | 0145 | [8 empty] | ADCS_N | [8 empty] | 下營DS.320_81UL | 320 #1DTR(B) 81RY U/L | OTHER | D01//1DTR(B)/81UL |  |  |  | DNP | 522 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | USE
D01 | 下營DS | 0 |  | 320 | #1DTR(320) |  | GDA | [14 empty] | 0097 | [10 empty] | ADCS_N | [8 empty] | 下營DS.320_GDA | 320開關箱IED RY GDA | OTHER | D01/22/320/GDA |  |  |  | DNP | 523 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 320 | #1DTR(320) |  | PHA2 | [14 empty] | 0096 | [10 empty] | ADCS_N | [8 empty] | 下營DS.320_PHA2 | 320開關箱IED RY PHA | OTHER | D01/22/320/PHA |  |  |  | DNP | 524 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 330 | #2DTR(330) |  | 81A | [14 empty] | 0114 | [10 empty] | ADCS_N | [8 empty] | 下營DS.330_81A | 330 #2DTR(A) 81RY動作 | OTHER | D01/11/330/81A |  |  |  | DNP | 525 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 330 | #2DTR(330) |  | 81UL | [14 empty] | 0610 |  | 0146 | [8 empty] | ADCS_N | [8 empty] | 下營DS.330_81UL | 330 #2DTR(A) 81RY U/L | OTHER | D01//2DTR(A)/81UL |  |  |  | DNP | 526 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | USE
D01 | 下營DS | 0 |  | 330 | #2DTR(330) |  | GDA | [14 empty] | 0101 | [10 empty] | ADCS_N | [8 empty] | 下營DS.330_GDA | 330開關箱IED RY GDA | OTHER | D01/11/330/GDA |  |  |  | DNP | 527 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 330 | #2DTR(330) |  | PHA2 | [14 empty] | 0100 | [10 empty] | ADCS_N | [8 empty] | 下營DS.330_PHA2 | 330開關箱IED RY PHA | OTHER | D01/11/330/PHA |  |  |  | DNP | 528 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 340 | #2DTR(340) |  | 81A | [14 empty] | 0115 | [10 empty] | ADCS_N | [8 empty] | 下營DS.340_81A | 340 #2DTR(B) 81RY動作 | OTHER | D01/22/340/81A |  |  |  | DNP | 529 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 340 | #2DTR(340) |  | 81UL | [14 empty] | 0611 |  | 0147 | [8 empty] | ADCS_N | [8 empty] | 下營DS.340_81UL | 340 #2DTR(B) 81RY U/L | OTHER | D01//2DTR(B)/81UL |  |  |  | DNP | 530 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | USE
D01 | 下營DS | 0 |  | 340 | #2DTR(340) |  | GDA | [14 empty] | 0105 | [10 empty] | ADCS_N | [8 empty] | 下營DS.340_GDA | 340開關箱IED RY GDA | OTHER | D01/22/340/GDA |  |  |  | DNP | 531 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 340 | #2DTR(340) |  | PHA2 | [14 empty] | 0104 | [10 empty] | ADCS_N | [8 empty] | 下營DS.340_PHA2 | 340開關箱IED RY PHA | OTHER | D01/22/340/PHA |  |  |  | DNP | 532 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  |  |  |  | COMMA | [14 empty] | 1018 | [10 empty] | ADCS_N | [8 empty] | 下營DS.COMMA | 變電所SCADA_B故障 | OTHER | D01/0/StaDev/4A5Other |  |  |  | DNP | 533 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  | COMM | 通訊處理單元 |  | SupLocal | [14 empty] | 0513 | [10 empty] | ADCS_N | [8 empty] | 下營DS.COMM_S/L | 通訊處理單元 SUPY/LOCAL | OTHER | D01/0/StaDev/Comm_R_L |  |  |  | DNP | 534 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D01 | 下營DS | 0 |  | LOCAL | LOCAL |  | GPSA | [14 empty] | 1016 | [10 empty] | ADCS_N | [8 empty] | 下營DS.GPSA | LOCAL GPS故障 | OTHER | D01/0/StaDev/GPSA |  |  |  | DNP | 535 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  |  |  |  | MCC | [14 empty] | 1007 | [10 empty] | ADCS_N | [8 empty] | 下營DS.MCC故障 | MCC電驛故障 | OTHER | D01/0/StaDev/MCC |  |  |  | DNP | 536 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  | MODEM | MODEM |  | MODEMA | [14 empty] | 1023 | [10 empty] | ADCS_N | [8 empty] | 下營DS.MODEMA | MODEM POWER FAIL故障 | OTHER | D01/0/StaDev/8A5Other |  |  |  | DNP | 537 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  |  |  |  | PMCC | [14 empty] | 1013 | [10 empty] | ADCS_N | [8 empty] | 下營DS.PMCC故障 | PMCC電驛故障 | OTHER | D01/0/StaDev/PMCC |  |  |  | DNP | 538 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  | SCADA | SCADA |  | UPS | [14 empty] | 0966 | [10 empty] | ADCS_N | [8 empty] | 下營DS.SCADA_UPS | SCADA UPS故障 | OTHER | D01/0/StaDev/UPSA |  |  |  | DNP | 539 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  |  |  |  | SCADAA | [14 empty] | 1017 | [10 empty] | ADCS_N | [8 empty] | 下營DS.SCADA故障 | 變電所SCADA故障 | OTHER | D01/0/StaDev/SCADAA |  |  |  | DNP | 540 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  |  |  |  | SUPA | [14 empty] | 0962 | [10 empty] | ADCS_N | [8 empty] | 下營DS.SUPA | 所內監視系統警報 | OTHER | D01/0/StaDev/1A5Other |  |  |  | DNP | 541 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  |  |  |  | TCA | [14 empty] | 1015 | [10 empty] | ADCS_N | [8 empty] | 下營DS.TCA | 斷路器跳脫回路故障 | OTHER | D01/0/StaDev/TCA |  |  |  | DNP | 542 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK21 | 營一線(VK21) |  | 81A | [14 empty] | 0224 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK21_81A | 11KV營一線(VK21) 81RY | OTHER | D01/11/VK21/81A |  |  |  | DNP | 543 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK22 | 營二線(VK22) |  | 81A | [14 empty] | 0225 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK22_81A | 11KV營二線(VK22) 81RY | OTHER | D01/11/VK22/81A |  |  |  | DNP | 544 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK23 | 營三線(VK23) |  | 81A | [14 empty] | 0226 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK23_81A | 11KV營三線(VK23) 81RY | OTHER | D01/11/VK23/81A |  |  |  | DNP | 545 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK24 | 營正線(VK24) |  | 81A | [14 empty] | 0227 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK24_81A | 11KV營正線(VK24) 81RY | OTHER | D01/11/VK24/81A |  |  |  | DNP | 546 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK25 | 營五線(VK25) |  | 81A | [14 empty] | 0228 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK25_81A | 11KV營五線(VK25) 81RY | OTHER | D01/11/VK25/81A |  |  |  | DNP | 547 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK26 | 營六線(VK26) |  | 81A | [14 empty] | 0238 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK26_81A | 11KV營六線(VK26) 81RY | OTHER | D01/11/VK26/81A |  |  |  | DNP | 548 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK27 | 營七線(VK27) |  | 81A | [14 empty] | 0237 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK27_81A | 11KV營七線(VK27) 81RY | OTHER | D01/11/VK27/81A |  |  |  | DNP | 549 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK28 | 營八線(VK28) |  | 81A | [14 empty] | 0236 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK28_81A | 11KV營八線(VK28) 81RY | OTHER | D01/11/VK28/81A |  |  |  | DNP | 550 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK29 | 營九線(VK29) |  | 81A | [14 empty] | 0235 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK29_81A | 11KV營九線(VK29) 81RY | OTHER | D01/11/VK29/81A |  |  |  | DNP | 551 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | VK30 | 營十線(VK30) |  | 81A | [14 empty] | 0234 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK30_81A | 11KV營十線(VK30) 81RY | OTHER | D01/11/VK30/81A |  |  |  | DNP | 552 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK51 | 營51線(VK51) |  | 81A | [14 empty] | 0229 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK51_81A | 23KV營51線(VK51) 81RY | OTHER | D01/22/VK51/81A |  |  |  | DNP | 553 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK52 | 營52線(VK52) |  | 81A | [14 empty] | 0230 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK52_81A | 23KV營52線(VK52) 81RY | OTHER | D01/22/VK52/81A |  |  |  | DNP | 554 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK53 | 營53線(VK53) |  | 81A | [14 empty] | 0231 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK53_81A | 23KV營53線(VK53) 81RY | OTHER | D01/22/VK53/81A |  |  |  | DNP | 555 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK54 | 營54線(VK54) |  | 81A | [14 empty] | 0232 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK54_81A | 23KV營54線(VK54) 81RY | OTHER | D01/22/VK54/81A |  |  |  | DNP | 556 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK55 | 營55線(VK55) |  | 81A | [14 empty] | 0233 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK55_81A | 23KV營55線(VK55) 81RY | OTHER | D01/22/VK55/81A |  |  |  | DNP | 557 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK56 | 營56線(VK56) |  | 81A | [14 empty] | 0243 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK56_81A | 23KV營56線(VK56) 81RY | OTHER | D01/22/VK56/81A |  |  |  | DNP | 558 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK57 | 營57線(VK57) |  | 81A | [14 empty] | 0242 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK57_81A | 23KV營57線(VK57) 81RY | OTHER | D01/22/VK57/81A |  |  |  | DNP | 559 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK58 | 營58線(VK58) |  | 81A | [14 empty] | 0241 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK58_81A | 23KV營58線(VK58) 81RY | OTHER | D01/22/VK58/81A |  |  |  | DNP | 560 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK59 | 營59線(VK59) |  | 81A | [14 empty] | 0240 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK59_81A | 23KV營59線(VK59) 81RY | OTHER | D01/22/VK59/81A |  |  |  | DNP | 561 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | VK60 | 營60線(VK60) |  | 81A | [14 empty] | 0239 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.VK60_81A | 23KV營60線(VK60) 81RY | OTHER | D01/22/VK60/81A |  |  |  | DNP | 562 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 0 |  |  |  |  | 水位警報(1) | [14 empty] | 0979 | [10 empty] | ADCS_N | [8 empty] | 下營DS.水位警報(1) | A區地下室水位警報(1) | OTHER | D01/0/StaDev/Water1 |  |  |  | DNP | 563 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  |  |  |  | 水位警報(2) | [14 empty] | 0980 | [10 empty] | ADCS_N | [8 empty] | 下營DS.水位警報(2) | A區地下室水位警報(2) | OTHER | D01/0/StaDev/Water2 |  |  |  | DNP | 564 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  |  |  |  | 水位警報(3) | [14 empty] | 0981 | [10 empty] | ADCS_N | [8 empty] | 下營DS.水位警報(3) | B區地下室水位警報(1) | OTHER | D01/0/StaDev/Water3 |  |  |  | DNP | 565 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  |  |  |  | 水位警報(4) | [14 empty] | 0982 | [10 empty] | ADCS_N | [8 empty] | 下營DS.水位警報(4) | B區地下室水位警報(2) | OTHER | D01/0/StaDev/Water4 |  |  |  | DNP | 566 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  |  |  |  | 抽水泵警報 | [14 empty] | 0963 | [10 empty] | ADCS_N | [8 empty] | 下營DS.抽水泵警報 | 抽水泵故障警報 | OTHER | D01/0/StaDev/2A5Other |  |  |  | DNP | 567 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  |  |  |  | 洩油池水位(1) | [14 empty] | 0975 | [10 empty] | ADCS_N | [8 empty] | 下營DS.洩油池水位(1) | 洩油池水位(1) | OTHER | D01/0/StaDev/OilLeak1 |  |  |  | DNP | 568 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  |  |  |  | 洩油池水位(2) | [14 empty] | 0976 | [10 empty] | ADCS_N | [8 empty] | 下營DS.洩油池水位(2) | 洩油池水位(2) | OTHER | D01/0/StaDev/OilLeak2 |  |  |  | DNP | 569 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  |  |  |  | 通信機房溫度 | [14 empty] | 0957 | [10 empty] | ADCS_N | [8 empty] | 下營DS.通信機房溫度 | 通訊室或控制室溫度警報 | OTHER | D01/0/StaDev/R_Temp |  |  |  | DNP | 570 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 22 | 22kV | 11_ | 11/ |  | LOA | [14 empty] | 1012 | [10 empty] | DDCS3_1 | [8 empty] | 下營DS.11/23KV_LOA | 11/23KV饋線復閉失敗閉鎖 | OTHER | D01/22/ComPoint/LOA |  |  |  | DNP | 571 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 0 |  | 1520 | 新營下營二路(1520) |  | 87CFA | [14 empty] | 0993 | [10 empty] | ADCS_N | [8 empty] | 下營DS.1520_87CFA | 新營下營二路(1520)87RY通訊故障 | OTHER | D01/161/1520/87CFA |  |  |  | DNP | 572 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  |  |  |  | COMMB | [14 empty] | 1020 | [10 empty] | ADCS_N | [8 empty] | 下營DS.COMMB | 備援主機故障 | OTHER | D01/0/StaDev/7A5Other |  |  |  | DNP | 573 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  |  |  |  | FiberA | [14 empty] | 1022 | [10 empty] | ADCS_N | [8 empty] | 下營DS.FIBERA | 通訊主機(B)故障 | OTHER | D01/0/StaDev/6A5Other |  |  |  | DNP | 574 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  |  |  |  | NPORTA | [14 empty] | 1021 | [10 empty] | ADCS_N | [8 empty] | 下營DS.NPORTA | 通訊主機(A)故障 | OTHER | D01/0/StaDev/5A5Other |  |  |  | DNP | 575 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  | NPORT | IED |  | DCA | [14 empty] | 1019 | [10 empty] | ADCS_N | [8 empty] | 下營DS.NPORT_DCA | IED 通訊光纖故障 | OTHER | D01/0/StaDev/FiberA |  |  |  | DNP | 576 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1530 | 下營威致官田鋼(1530) |  | PHA | [14 empty] | 0010 | [10 empty] | 161KV_N | [8 empty] | 下營DS.1530_PHA | 下營威致官田鋼(1530) 相間RY | LINE161 | D01/161/1530/PHA |  |  |  | DNP | 577 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1530 | 下營威致官田鋼(1530) |  | GDA | [14 empty] | 0011 | [10 empty] | 161KV_N | [8 empty] | 下營DS.1530_GDA | 下營威致官田鋼(1530) 接地RY | LINE161 | D01/161/1530/GDA |  |  |  | DNP | 578 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D01 | 下營DS | 161 | 161kV | 1530 | 下營威致官田鋼(1530) |  | CB | [14 empty] | 0008 |  | 0014 | [8 empty] | 161KV_N | [8 empty] | 下營DS.1530_CB | 1530(下營威致官田鋼) CB | LINE161 | D01/161/1530/CB |  |  |  | DNP | 579 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 161 | 161kV | 1530 | 下營威致官田鋼(1530) |  | 79UL | [14 empty] | 0518 |  | 0019 | [8 empty] | ADCS_N | [8 empty] | 下營DS.1530_79UL | 下營威致官田鋼(1530) 79RY U/L | LINE161 | D01/161/1530/79UL |  |  |  | DNP | 580 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | USE/LOCK | USE
D01 | 下營DS | 161 | 161kV | 1530 | 下營威致官田鋼(1530) |  | DS1 | 1531 | [13 empty] | 0656 | 657 | 0015 | [8 empty] | ADCS_N | [8 empty] | 下營DS.1531_DS | 1531(下營威致官田鋼) DS | LINE161 | D01/161/1530/DS1 |  |  |  | DNP | 581 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D01 | 下營DS | 161 | 161kV | 1530 | 下營威致官田鋼(1530) |  | DS2 | 1532 | [13 empty] | 0658 | 659 | 0016 | [8 empty] | ADCS_N | [8 empty] | 下營DS.1532_DS | 1532(下營威致官田鋼) DS | LINE161 | D01/161/1530/DS2 |  |  |  | DNP | 582 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D01 | 下營DS | 161 | 161kV | 1530 | 下營威致官田鋼(1530) |  | DS3 | 1533 | [13 empty] | 0660 | 661 | 0017 | [8 empty] | ADCS_N | [8 empty] | 下營DS.1533_DS | 1533(下營威致官田鋼) DS | LINE161 | D01/161/1530/DS3 |  |  |  | DNP | 583 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D01 | 下營DS | 161 | 161kV | 1530 | 下營威致官田鋼(1530) |  | E3 | 1533E | [13 empty] | 0662 | 663 | 0018 | [8 empty] | ADCS_N | [8 empty] | 下營DS.1533E_ES | 1533E(下營威致官田鋼) ES | LINE161 | D01/161/1530/ES3 |  |  |  | DNP | 584 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D01 | 下營DS | 0 |  | 1530 | 下營威致官田鋼(1530) |  | RYFA | [14 empty] | 0997 | [10 empty] | ADCS_N | [8 empty] | 下營DS.1530_RYFA | 下營威致官田鋼(1530)數位RY故障 | OTHER | D01/161/1530/RYFA |  |  |  | DNP | 585 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D01 | 下營DS | 0 |  |  |  |  | Door2 | [14 empty] | 0972 | [10 empty] | ADCS_N | [8 empty] | 下營DS.無人化門禁(2) | 無人化門禁(2)建築物大門 | OTHER | D01/0/StaDev/Door2 |  |  |  | DNP | 586 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | BVS | BVS |  | RY | [14 empty] | 1003 | [10 empty] | ADCS_N | [8 empty] | 下營DS.BVS_RY | BVS GRZ100 RY U/L | OTHER | D01/0/ComPoint/GRZ100 |  |  |  | DNP | 587 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | LOCK/USE | USE
D01 | 下營DS | 0 |  |  |  |  | GEN | [14 empty] | 0964 | [10 empty] | ADCS_N | [8 empty] | 下營DS.GEN | 緊急發電機運轉 | OTHER | D01/0/StaDev/3A5Other |  |  |  | DNP | 588 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ON/OFF | OFF
D01 | 下營DS | 0 |  | OLTC | OLTC |  | OLTCA | [14 empty] | 0072 | [10 empty] | ADCS_N | [8 empty] | 下營DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | D01/0/ComPoint/OLTC_A |  |  |  | DNP | 589 | DNPDIPoint | DS051 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D01 | 下營DS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 下營DS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 590 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 11 | 11kV | 230_SC | #3SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 下營DS.230_SC_CAP | 11KV#3SC 容量 | SC | [5 empty] | 591 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 22 | 22kV | 220_SC | #2SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 下營DS.220_SC_CAP | 23KV#2SC 容量 | SC | [5 empty] | 592 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 22 | 22kV | 240_SC | #4SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 下營DS.240_SC_CAP | 23KV#4SC 容量 | SC | [5 empty] | 593 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D01 | 下營DS | 161 | 161kV | 1510 | 新營下營一路(1510) |  | LE0 | 1510LE | [24 empty] | ADCS_N | [8 empty] | 下營DS.1510LE | 1510LE (非取樣點) | LINE161 | D01/161/1510/LE0 |  |  |  |  | 594 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 161 | 161kV | 1510 | 新營下營一路(1510) |  | BE0 | 1510BE | [24 empty] | ADCS_N | [8 empty] | 下營DS.1510BE | 1510BE (非取樣點) | LINE161 | D01/161/1510/BE0 |  |  |  |  | 595 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 161 | 161kV | 1520 | 新營下營二路(1520) |  | LE0 | 1520LE | [24 empty] | ADCS_N | [8 empty] | 下營DS.1520LE | 1520LE (非取樣點) | LINE161 | D01/161/1520/LE0 |  |  |  |  | 596 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 161 | 161kV | 1520 | 新營下營二路(1520) |  | BE0 | 1520BE | [24 empty] | ADCS_N | [8 empty] | 下營DS.1520BE | 1520BE (非取樣點) | LINE161 | D01/161/1520/BE0 |  |  |  |  | 597 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | VK21 | VK21_DS |  | DS1 | VK21_DS | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK21_DS | VK21_DS (非取樣點) | FEEDER | D01/11/VK21/DS |  |  |  |  | 598 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | VK21 | VK21_ES |  | LE0 | VK21_ES | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK21_ES | VK21_ES (非取樣點) | FEEDER | D01/11/VK21/ES |  |  |  |  | 599 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | VK22 | VK22_DS |  | DS1 | VK22_DS | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK22_DS | VK22_DS (非取樣點) | FEEDER | D01/11/VK22/DS |  |  |  |  | 600 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | VK22 | VK22_ES |  | LE0 | VK22_ES | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK22_ES | VK22_ES (非取樣點) | FEEDER | D01/11/VK22/ES |  |  |  |  | 601 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | VK23 | VK23_DS |  | DS1 | VK23_DS | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK23_DS | VK23_DS (非取樣點) | FEEDER | D01/11/VK23/DS |  |  |  |  | 602 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | VK23 | VK23_ES |  | LE0 | VK23_ES | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK23_ES | VK23_ES (非取樣點) | FEEDER | D01/11/VK23/ES |  |  |  |  | 603 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | VK24 | VK24_DS |  | DS1 | VK24_DS | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK24_DS | VK24_DS (非取樣點) | FEEDER | D01/11/VK24/DS |  |  |  |  | 604 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | VK24 | VK24_ES |  | LE0 | VK24_ES | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK24_ES | VK24_ES (非取樣點) | FEEDER | D01/11/VK24/ES |  |  |  |  | 605 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | VK25 | VK25_DS |  | DS1 | VK25_DS | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK25_DS | VK25_DS (非取樣點) | FEEDER | D01/11/VK25/DS |  |  |  |  | 606 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | VK25 | VK25_ES |  | LE0 | VK25_ES | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK25_ES | VK25_ES (非取樣點) | FEEDER | D01/11/VK25/ES |  |  |  |  | 607 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | VK26 | VK26_DS |  | DS1 | VK26_DS | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK26_DS | VK26_DS (非取樣點) | FEEDER | D01/11/VK26/DS |  |  |  |  | 608 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | VK26 | VK26_ES |  | LE0 | VK26_ES | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK26_ES | VK26_ES (非取樣點) | FEEDER | D01/11/VK26/ES |  |  |  |  | 609 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | VK27 | VK27_DS |  | DS1 | VK27_DS | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK27_DS | VK27_DS (非取樣點) | FEEDER | D01/11/VK27/DS |  |  |  |  | 610 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | VK27 | VK27_ES |  | LE0 | VK27_ES | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK27_ES | VK27_ES (非取樣點) | FEEDER | D01/11/VK27/ES |  |  |  |  | 611 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | VK28 | VK28_DS |  | DS1 | VK28_DS | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK28_DS | VK28_DS (非取樣點) | FEEDER | D01/11/VK28/DS |  |  |  |  | 612 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | VK28 | VK28_ES |  | LE0 | VK28_ES | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK28_ES | VK28_ES (非取樣點) | FEEDER | D01/11/VK28/ES |  |  |  |  | 613 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | VK29 | VK29_DS |  | DS1 | VK29_DS | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK29_DS | VK29_DS (非取樣點) | FEEDER | D01/11/VK29/DS |  |  |  |  | 614 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | VK29 | VK29_ES |  | LE0 | VK29_ES | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK29_ES | VK29_ES (非取樣點) | FEEDER | D01/11/VK29/ES |  |  |  |  | 615 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | VK30 | VK30_DS |  | DS1 | VK30_DS | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK30_DS | VK30_DS (非取樣點) | FEEDER | D01/11/VK30/DS |  |  |  |  | 616 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | VK30 | VK30_ES |  | LE0 | VK30_ES | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK30_ES | VK30_ES (非取樣點) | FEEDER | D01/11/VK30/ES |  |  |  |  | 617 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | VK51 | VK51_DS |  | DS1 | VK51_DS | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK51_DS | VK51_DS (非取樣點) | FEEDER | D01/22/VK51/DS |  |  |  |  | 618 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | VK51 | VK51_ES |  | LE0 | VK51_ES | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK51_ES | VK51_ES (非取樣點) | FEEDER | D01/22/VK51/ES |  |  |  |  | 619 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | VK52 | VK52_DS |  | DS1 | VK52_DS | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK52_DS | VK52_DS (非取樣點) | FEEDER | D01/22/VK52/DS |  |  |  |  | 620 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | VK52 | VK52_ES |  | LE0 | VK52_ES | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK52_ES | VK52_ES (非取樣點) | FEEDER | D01/22/VK52/ES |  |  |  |  | 621 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | VK53 | VK53_DS |  | DS1 | VK53_DS | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK53_DS | VK53_DS (非取樣點) | FEEDER | D01/22/VK53/DS |  |  |  |  | 622 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | VK53 | VK53_ES |  | LE0 | VK53_ES | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK53_ES | VK53_ES (非取樣點) | FEEDER | D01/22/VK53/ES |  |  |  |  | 623 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | VK54 | VK54_DS |  | DS1 | VK54_DS | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK54_DS | VK54_DS (非取樣點) | FEEDER | D01/22/VK54/DS |  |  |  |  | 624 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | VK54 | VK54_ES |  | LE0 | VK54_ES | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK54_ES | VK54_ES (非取樣點) | FEEDER | D01/22/VK54/ES |  |  |  |  | 625 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | VK55 | VK55_DS |  | DS1 | VK55_DS | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK55_DS | VK55_DS (非取樣點) | FEEDER | D01/22/VK55/DS |  |  |  |  | 626 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | VK55 | VK55_ES |  | LE0 | VK55_ES | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK55_ES | VK55_ES (非取樣點) | FEEDER | D01/22/VK55/ES |  |  |  |  | 627 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | VK56 | VK56_DS |  | DS1 | VK56_DS | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK56_DS | VK56_DS (非取樣點) | FEEDER | D01/22/VK56/DS |  |  |  |  | 628 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | VK56 | VK56_ES |  | LE0 | VK56_ES | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK56_ES | VK56_ES (非取樣點) | FEEDER | D01/22/VK56/ES |  |  |  |  | 629 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | VK57 | VK57_DS |  | DS1 | VK57_DS | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK57_DS | VK57_DS (非取樣點) | FEEDER | D01/22/VK57/DS |  |  |  |  | 630 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | VK57 | VK57_ES |  | LE0 | VK57_ES | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK57_ES | VK57_ES (非取樣點) | FEEDER | D01/22/VK57/ES |  |  |  |  | 631 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | VK58 | VK58_DS |  | DS1 | VK58_DS | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK58_DS | VK58_DS (非取樣點) | FEEDER | D01/22/VK58/DS |  |  |  |  | 632 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | VK58 | VK58_ES |  | LE0 | VK58_ES | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK58_ES | VK58_ES (非取樣點) | FEEDER | D01/22/VK58/ES |  |  |  |  | 633 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | VK59 | VK59_DS |  | DS1 | VK59_DS | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK59_DS | VK59_DS (非取樣點) | FEEDER | D01/22/VK59/DS |  |  |  |  | 634 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | VK59 | VK59_ES |  | LE0 | VK59_ES | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK59_ES | VK59_ES (非取樣點) | FEEDER | D01/22/VK59/ES |  |  |  |  | 635 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | VK60 | VK60_DS |  | DS1 | VK60_DS | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK60_DS | VK60_DS (非取樣點) | FEEDER | D01/22/VK60/DS |  |  |  |  | 636 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | VK60 | VK60_ES |  | LE0 | VK60_ES | [24 empty] | DDCS3_1 | [8 empty] | 下營DS.VK60_ES | VK60_ES (非取樣點) | FEEDER | D01/22/VK60/ES |  |  |  |  | 637 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | 100 | TIE(100) |  | E1 | 101E | [24 empty] | ADCS_N | [8 empty] | 下營DS.101E | 101E (非取樣點) | TIE | D01/11/100/E1 |  |  |  |  | 638 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | 100 | TIE(100) |  | E2 | 102E | [24 empty] | ADCS_N | [8 empty] | 下營DS.102E | 102E (非取樣點) | TIE | D01/11/100/E2 |  |  |  |  | 639 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | 101 | 101 |  | 101 | 101 | [24 empty] | ADCS_N | [8 empty] | 下營DS.101 | 101 (非取樣點) | TIE | D01/11/100/D1 |  |  |  |  | 640 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | 102 | 102 |  | 102 | 102 | [24 empty] | ADCS_N | [8 empty] | 下營DS.102 | 102 (非取樣點) | TIE | D01/11/100/D2 |  |  |  |  | 641 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | 200 | TIE(200) |  | E1 | 201E | [24 empty] | ADCS_N | [8 empty] | 下營DS.201E | 201E (非取樣點) | TIE | D01/22/200/E1 |  |  |  |  | 642 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | 200 | TIE(200) |  | E2 | 202E | [24 empty] | ADCS_N | [8 empty] | 下營DS.202E | 202E (非取樣點) | TIE | D01/22/200/E2 |  |  |  |  | 643 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | 201 | 201 |  | 201 | 201 | [24 empty] | ADCS_N | [8 empty] | 下營DS.201 | 201 (非取樣點) | TIE | D01/22/200/D1 |  |  |  |  | 644 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | 202 | 202 |  | 202 | 202 | [24 empty] | ADCS_N | [8 empty] | 下營DS.202 | 202 (非取樣點) | TIE | D01/22/200/D2 |  |  |  |  | 645 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | 391 | 391 |  | 391 | 391 | [24 empty] | ADCS_N | [8 empty] | 下營DS.391 | 391 (非取樣點) | OTHER | D01/11/390/D1 |  |  |  |  | 646 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | 391E | 391E |  | 391E | 391E | [24 empty] | ADCS_N | [8 empty] | 下營DS.391E | 391E (非取樣點) | OTHER | D01/11/390/E1 |  |  |  |  | 647 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | 491 | 491 |  | 491 | 491 | [24 empty] | ADCS_N | [8 empty] | 下營DS.491 | 491 (非取樣點) | OTHER | D01/22/490/D1 |  |  |  |  | 648 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | 491E | 491E |  | 491E | 491E | [24 empty] | ADCS_N | [8 empty] | 下營DS.491E | 491E (非取樣點) | OTHER | D01/22/490/E1 |  |  |  |  | 649 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | 1750TE | [24 empty] | ADCS_N | [8 empty] | 下營DS.1750TE | 1750TE (非取樣點) | MTR | D01/161/1750/TE0 |  |  |  |  | 650 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | 1750BE | [24 empty] | ADCS_N | [8 empty] | 下營DS.1750BE | 1750BE (非取樣點) | MTR | D01/161/1750/BE0 |  |  |  |  | 651 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | 311 | 311 |  | 311 | 311 | [24 empty] | ADCS_N | [8 empty] | 下營DS.311 | 311 (非取樣點) | MTR | D01/11/310/D1 |  |  |  |  | 652 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | 310 | #1DTR(310) |  | E1 | 311E | [24 empty] | ADCS_N | [8 empty] | 下營DS.311E | 311E (非取樣點) | MTR | D01/11/310/E1 |  |  |  |  | 653 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | 321 | 321 |  | 321 | 321 | [24 empty] | ADCS_N | [8 empty] | 下營DS.321 | 321 (非取樣點) | MTR | D01/22/320/D1 |  |  |  |  | 654 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | 320 | #1DTR(320) |  | E1 | 321E | [24 empty] | ADCS_N | [8 empty] | 下營DS.321E | 321E (非取樣點) | MTR | D01/22/320/E1 |  |  |  |  | 655 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | 1760TE | [24 empty] | ADCS_N | [8 empty] | 下營DS.1760TE | 1760TE (非取樣點) | MTR | D01/161/1760/TE0 |  |  |  |  | 656 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | 1760BE | [24 empty] | ADCS_N | [8 empty] | 下營DS.1760BE | 1760BE (非取樣點) | MTR | D01/161/1760/BE0 |  |  |  |  | 657 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | 331 | 331 |  | 331 | 331 | [24 empty] | ADCS_N | [8 empty] | 下營DS.331 | 331 (非取樣點) | MTR | D01/11/330/D1 |  |  |  |  | 658 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | 330 | #2DTR(330) |  | E1 | 331E | [24 empty] | ADCS_N | [8 empty] | 下營DS.331E | 331E (非取樣點) | MTR | D01/11/330/E1 |  |  |  |  | 659 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | 341 | 341 |  | 341 | 341 | [24 empty] | ADCS_N | [8 empty] | 下營DS.341 | 341 (非取樣點) | MTR | D01/22/340/D1 |  |  |  |  | 660 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | 340 | #2DTR(340) |  | E1 | 341E | [24 empty] | ADCS_N | [8 empty] | 下營DS.341E | 341E (非取樣點) | MTR | D01/22/340/E1 |  |  |  |  | 661 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | 211E | 211E |  | 211E | 211E | [24 empty] | ADCS_N | [8 empty] | 下營DS.211E | 211E (非取樣點) | SC | D01/11/210/E1 |  |  |  |  | 662 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | 211 | 211 |  | 211 | 211 | [24 empty] | ADCS_N | [8 empty] | 下營DS.211 | 211 (非取樣點) | SC | D01/11/210/D1 |  |  |  |  | 663 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | 231E | 231E |  | 231E | 231E | [24 empty] | ADCS_N | [8 empty] | 下營DS.231E | 231E (非取樣點) | SC | D01/11/230/E1 |  |  |  |  | 664 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | 231 | 231 |  | 231 | 231 | [24 empty] | ADCS_N | [8 empty] | 下營DS.231 | 231 (非取樣點) | SC | D01/11/230/D1 |  |  |  |  | 665 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | 221E | 221E |  | 221E | 221E | [24 empty] | ADCS_N | [8 empty] | 下營DS.221E | 221E (非取樣點) | SC | D01/22/220/E1 |  |  |  |  | 666 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | 221 | 221 |  | 221 | 221 | [24 empty] | ADCS_N | [8 empty] | 下營DS.221 | 221 (非取樣點) | SC | D01/22/220/D1 |  |  |  |  | 667 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | 241E | 241E |  | 241E | 241E | [24 empty] | ADCS_N | [8 empty] | 下營DS.241E | 241E (非取樣點) | SC | D01/22/240/E1 |  |  |  |  | 668 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | 241 | 241 |  | 241 | 241 | [24 empty] | ADCS_N | [8 empty] | 下營DS.241 | 241 (非取樣點) | SC | D01/22/240/D1 |  |  |  |  | 669 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | 15B1E | 15B1E |  | BE1 | 15B1E | [24 empty] | ADCS_N | [8 empty] | 下營DS.15B1E | 15B1E (非取樣點) | BUS | D01/161/161B1E/BE1 |  |  |  |  | 670 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | 15B2E | 15B2E |  | BE2 | 15B2E | [24 empty] | ADCS_N | [8 empty] | 下營DS.15B2E | 15B2E (非取樣點) | BUS | D01/161/161B2E/BE2 |  |  |  |  | 671 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | ADCS_N | [8 empty] | 下營DS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 672 | NotelDIPoint | [38 empty] | START/STOP | STOP
D01 | 下營DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [24 empty] | ADCS_N | [8 empty] | 下營DS.1501E | 1501E (非取樣點) | TIE | D01/161/1500/E1 |  |  |  |  | 673 | NotelDIPoint |  |  |  |  | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [24 empty] | ADCS_N | [8 empty] | 下營DS.1502E | 1502E (非取樣點) | TIE | D01/161/1500/E2 |  |  |  |  | 674 | NotelDIPoint |  |  |  |  | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 161 | 161kV | 1530 | 下營威致官田鋼(1530) |  | LE0 | 1530LE | [24 empty] | ADCS_N | [8 empty] | 下營DS.1530LE | 1530LE (非取樣點) | LINE161 | D01/161/1530/LE0 |  |  |  |  | 675 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 161 | 161kV | 1530 | 下營威致官田鋼(1530) |  | BE0 | 1530BE | [24 empty] | ADCS_N | [8 empty] | 下營DS.1530BE | 1530BE (非取樣點) | LINE161 | D01/161/1530/BE0 |  |  |  |  | 676 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | 1A | #1A |  | BE | #1A_BE | [24 empty] | ADCS_N | [8 empty] | 下營DS.#1A_BE | #1A BE(非取樣點) | OTHER | [5 empty] | 677 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | 1B | #1B |  | BE | #1B_BE | [24 empty] | ADCS_N | [8 empty] | 下營DS.#1B_BE | #1B BE(非取樣點) | OTHER | [5 empty] | 678 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | 2A | #2A |  | BE | #2A_BE | [24 empty] | ADCS_N | [8 empty] | 下營DS.#2A_BE | #2A BE(非取樣點) | OTHER | [5 empty] | 679 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | 2B | #2B |  | BE | #2B_BE | [24 empty] | ADCS_N | [8 empty] | 下營DS.#2B_BE | #2B BE(非取樣點) | OTHER | [5 empty] | 680 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | 1ABUS | 1ABUS |  | PTD | 1ABUS_PTD | [24 empty] | ADCS_N | [8 empty] | 下營DS.1ABUS_PTD | #1ABUS_PTD(非取樣點) | OTHER | [5 empty] | 681 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | 1ABUS | 1ABUS |  | PTE | 1ABUS_PTE | [24 empty] | ADCS_N | [8 empty] | 下營DS.1ABUS_PTE | #1ABUS_PTE(非取樣點) | OTHER | [5 empty] | 682 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | 1BBUS | 1BBUS |  | PTD | 1BBUS_PTD | [24 empty] | ADCS_N | [8 empty] | 下營DS.1BBUS_PTD | #1BBUS_PTD(非取樣點) | OTHER | [5 empty] | 683 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | 1BBUS | 1BBUS |  | PTE | 1BBUS_PTE | [24 empty] | ADCS_N | [8 empty] | 下營DS.1BBUS_PTE | #1BBUS_PTE(非取樣點) | OTHER | [5 empty] | 684 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | 2ABUS | 2ABUS |  | PTD | 2ABUS_PTD | [24 empty] | ADCS_N | [8 empty] | 下營DS.2ABUS_PTD | #2ABUS_PTD(非取樣點) | OTHER | [5 empty] | 685 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | 2ABUS | 2ABUS |  | PTE | 2ABUS_PTE | [24 empty] | ADCS_N | [8 empty] | 下營DS.2ABUS_PTE | #2ABUS_PTE(非取樣點) | OTHER | [5 empty] | 686 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D01 | 下營DS | 0 |  | 2BBUS | 2BBUS |  | PTD | 2BBUS_PTD | [24 empty] | ADCS_N | [8 empty] | 下營DS.2BBUS_PTD | #2BBUS_PTD(非取樣點) | OTHER | [5 empty] | 687 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D01 | 下營DS | 0 |  | 2BBUS | 2BBUS |  | PTE | 2BBUS_PTE | [24 empty] | ADCS_N | [8 empty] | 下營DS.2BBUS_PTE | #2BBUS_PTE(非取樣點) | OTHER | [5 empty] | 688 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo