## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
C05 | 積六CS | 161 | 161kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0002 | [9 empty] | aaa | B1/C05_A1 | [16 empty] | 2 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1500 | TIE(1500) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0008 | [10 empty] | B1/C05_A1 | [16 empty] | 3 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1720 | 積十四～積六線(1720) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0006 | [10 empty] | B1/C05_A1 | [16 empty] | 4 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1730 | 南科～積六線(1730) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0007 | [10 empty] | B1/C05_A1 | [16 empty] | 5 | [10 empty] | C20R1228 | 1166.6 | 1228 | 1350.8 | 1510.4 |  | -1166.6 | -1228 | -1350.8 | -1510.4
C04 | 積十四 | 161 | 161kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0018 | [9 empty] | aaa | B1/C04_A1 | [16 empty] | 6 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1500 | TIE(1500) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0024 | [10 empty] | B1/C04_A1 | [16 empty] | 7 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1520 | 積十四～積六線(1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0022 | [10 empty] | B1/C04_A1 | [16 empty] | 8 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1540 | 康寧～積十四線(1540) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0023 | [10 empty] | B1/C04_A1 | [16 empty] | 9 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 161 | 161kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0034 | [9 empty] | aaa | B1/C02_A1 | [16 empty] | 10 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 161 | 161kV | 1520 | 南科～康寧線(1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0038 | [10 empty] | B1/C02_A1 | [16 empty] | 11 | [10 empty] | C20R0964 | 915.8 | 964 | 1060.4 | 1185.7 |  | -915.8 | -964 | -1060.4 | -1185.7
C02 | 康寧CS | 161 | 161kV | 1540 | 康寧～積十四線(1540) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0039 | [10 empty] | B1/C02_A1 | [16 empty] | 12 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0050 | [9 empty] | aaa | B1/C03_A1 | [16 empty] | 13 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0051 | [9 empty] | aab | B1/C03_A1 | [16 empty] | 14 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1500 | TIE(1500) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0056 | [10 empty] | B1/C03_A1 | [16 empty] | 15 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1710 | 和鑫二～積P3線(1710) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0054 | [10 empty] | B1/C03_A1 | [16 empty] | 16 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1720 | 南科～積P3線(1720) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0055 | [10 empty] | B1/C03_A1 | [16 empty] | 17 | [10 empty] | C20R1930 | 1833.5 | 1930 | 2000 | 2001 |  | -1833.5 | -1930 | -2000 | -2001
C08 | 積E五 | 161 | 161kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0066 | [9 empty] | aaa | B1/C08_A1 | [16 empty] | 18 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0067 | [9 empty] | aab | B1/C08_A1 | [16 empty] | 19 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1500 | TIE(1500) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0072 | [10 empty] | B1/C08_A1 | [16 empty] | 20 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1530 | 積E五~積E七線(1530) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0070 | [10 empty] | B1/C08_A1 | [16 empty] | 21 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1540 | 積E六~積E五線(1540) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0071 | [10 empty] | B1/C08_A1 | [16 empty] | 22 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0082 | [9 empty] | aaa | B1/C09_A1 | [16 empty] | 23 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0083 | [9 empty] | aab | B1/C09_A1 | [16 empty] | 24 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1530 | 積E六~積E五線(1530) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0087 | [10 empty] | B1/C09_A1 | [16 empty] | 25 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1540 | 南科~積E六線(1540) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0086 | [10 empty] | B1/C09_A1 | [16 empty] | 26 | [10 empty] | C20R1928 | 1831.6 | 1928 | 2000 | 2001 |  | -1831.6 | -1928 | -2000 | -2001
C09 | 積E六 | 161 | 161kV | 1500 | TIE(1500) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0088 | [10 empty] | B1/C09_A1 | [16 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0088 | [9 empty] | aaa | B1/C06_A1 | [16 empty] | 28 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0089 | [9 empty] | aab | B1/C06_A1 | [16 empty] | 29 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1520 | 三福一~積E七線(1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0103 | [10 empty] | B1/C06_A1 | [16 empty] | 30 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0102 | [10 empty] | B1/C06_A1 | [16 empty] | 31 | [10 empty] | C20R1478 | 1404.1 | 1478 | 1625.8 | 1817.9 |  | -1404.1 | -1478 | -1625.8 | -1817.9
C07 | 積E七 | 161 | 161kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0130 | [9 empty] | aaa | B1/C07_A1 | [16 empty] | 32 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0131 | [9 empty] | aab | B1/C07_A1 | [16 empty] | 33 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1500 | TIE(1500) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0136 | [10 empty] | B1/C07_A1 | [16 empty] | 34 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1520 | 三福一~積E七線(1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0135 | [10 empty] | B1/C07_A1 | [16 empty] | 35 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1530 | 積E五~積E七線(1530) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0134 | [10 empty] | B1/C07_A1 | [16 empty] | 36 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0114 | [9 empty] | aaa | B1/C01_A1 | [16 empty] | 37 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0115 | [9 empty] | aab | B1/C01_A1 | [16 empty] | 38 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1510 | 和鑫二～積P3線(1510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0118 | [10 empty] | B1/C01_A1 | [16 empty] | 39 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1520 | 南科和鑫二線 (1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0119 | [10 empty] | B1/C01_A1 | [16 empty] | 40 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0000 | [9 empty] | aadz | B1/C05_A1 | [16 empty] | 41 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0001 | [10 empty] | B1/C05_A1 | [16 empty] | 42 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1720 | 積十四～積六線(1720) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0002 | [9 empty] | aafa | B1/C05_A1 | [16 empty] | 43 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1720 | 積十四～積六線(1720) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 | [10 empty] | B1/C05_A1 | [16 empty] | 44 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1730 | 南科～積六線(1730) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0004 | [9 empty] | aaba | B1/C05_A1 | [16 empty] | 45 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1730 | 南科～積六線(1730) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0005 | [10 empty] | B1/C05_A1 | [16 empty] | 46 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1730 | 南科～積六線(1730) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 | [10 empty] | B1/C05_A1 | [16 empty] | 47 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1720 | 積十四～積六線(1720) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 | [10 empty] | B1/C05_A1 | [16 empty] | 48 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1650 | #1MTR(1650) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0008 | [9 empty] | aacb | B1/C05_A1 | [16 empty] | 49 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS |  |  | 1MTR | #1MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 | [10 empty] | B1/C05_A1 | [16 empty] | 50 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1660 | #2MTR(1660) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0010 | [9 empty] | aaeb | B1/C05_A1 | [16 empty] | 51 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS |  |  | 2MTR | #2MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 | [10 empty] | B1/C05_A1 | [16 empty] | 52 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0024 | [10 empty] | B1/C05_A1 | [16 empty] | 53 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1720 | 積十四～積六線(1720) |  | 87UL1 |  |  | Status | 第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0025 | [10 empty] | B1/C05_A1 | [16 empty] | 54 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1720 | 積十四～積六線(1720) |  | 87UL2 |  |  | Status | 第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0026 | [10 empty] | B1/C05_A1 | [16 empty] | 55 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 0 |  | StaDev | 所內設施 |  | DTUA | 資料收集設備內部異常故障警報 | [13 empty] | 0027 | [10 empty] | B1/C05_A1 | [16 empty] | 56 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS |  |  | 1MTR | #1MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0028 | [10 empty] | B1/C05_A1 | [16 empty] | 57 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS |  |  | 1MTR | #1MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0029 | [9 empty] | a | B1/C05_A1 | [16 empty] | 58 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS |  |  | 1MTR | #1MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0030 | [10 empty] | B1/C05_A1 | [16 empty] | 59 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS |  |  | 2MTR | #2MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0031 | [10 empty] | B1/C05_A1 | [16 empty] | 60 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS |  |  | 2MTR | #2MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0032 | [9 empty] | a | B1/C05_A1 | [16 empty] | 61 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS |  |  | 2MTR | #2MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0033 | [10 empty] | B1/C05_A1 | [16 empty] | 62 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1730 | 南科～積六線(1730) |  | 87UL1 |  |  | Status | 第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0034 | [10 empty] | B1/C05_A1 | [16 empty] | 63 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1730 | 南科～積六線(1730) |  | 87UL2 |  |  | Status | 第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0035 | [10 empty] | B1/C05_A1 | [16 empty] | 64 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 0 |  | StaDev | 所內設施 |  | DTU_CFA | 資料收集設備通訊故障警報 |  | Status | DTU 通訊異常 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0046 | [10 empty] | B1/C05_A1 | [16 empty] | 65 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 0 |  | StaDev | 所內設施 |  | OFA | 光纖通訊故障 | [13 empty] | 0047 | [10 empty] | B1/C05_A1 | [16 empty] | 66 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1500 | TIE(1500) |  | DS | 1501 |  | Status | DS | Open/Close | Y | 7 | DI-SP | [6 empty] | 0048 | [10 empty] | B1/C05_A1 | [16 empty] | 67 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | 15B1E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0050 | [9 empty] | aaaz | B1/C05_A1 | [16 empty] | 68 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | 15B2E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0051 | [9 empty] | aaaz | B1/C05_A1 | [16 empty] | 69 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1720 | 積十四～積六線(1720) |  | DS1 | 1721 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0052 | [10 empty] | B1/C05_A1 | [16 empty] | 70 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1720 | 積十四～積六線(1720) |  | DS2 | 1722 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0053 | [10 empty] | B1/C05_A1 | [16 empty] | 71 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1720 | 積十四～積六線(1720) |  | ES2 | 1722E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0054 | [10 empty] | B1/C05_A1 | [16 empty] | 72 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1720 | 積十四～積六線(1720) |  | LE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0055 | [10 empty] | B1/C05_A1 | [16 empty] | 73 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1720 | 積十四～積六線(1720) |  | BE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0056 | [10 empty] | B1/C05_A1 | [16 empty] | 74 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1730 | 南科～積六線(1730) |  | DS1 | 1731 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0057 | [10 empty] | B1/C05_A1 | [16 empty] | 75 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1730 | 南科～積六線(1730) |  | DS2 | 1732 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0058 | [10 empty] | B1/C05_A1 | [16 empty] | 76 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1730 | 南科～積六線(1730) |  | ES2 | 1732E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0059 | [10 empty] | B1/C05_A1 | [16 empty] | 77 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1730 | 南科～積六線(1730) |  | LE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0060 | [10 empty] | B1/C05_A1 | [16 empty] | 78 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1730 | 南科～積六線(1730) |  | BE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0061 | [10 empty] | B1/C05_A1 | [16 empty] | 79 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1730 | 南科～積六線(1730) |  | DS3 | 1733(備用) |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0062 | [10 empty] | B1/C05_A1 | [16 empty] | 80 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1730 | 南科～積六線(1730) |  | ES3 | 1733E(備用) |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0063 | [10 empty] | B1/C05_A1 | [16 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 0 |  | StaDev | 所內設施 |  | UPS_DCA | AC故障 | [13 empty] | 0067 | [10 empty] | B1/C05_A1 | [16 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 0 |  | StaDev | 所內設施 |  | UPS_ACA | DC故障 | [13 empty] | 0068 | [10 empty] | B1/C05_A1 | [16 empty] | 83 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1650 | #1MTR(1650) |  | DS | 1651 |  | Status | DS | Open/Close | Y | 7 | DI-SP | [6 empty] | 0069 | [10 empty] | B1/C05_A1 | [16 empty] | 84 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1650 | #1MTR(1650) |  | BE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0070 | [10 empty] | B1/C05_A1 | [16 empty] | 85 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1650 | #1MTR(1650) |  | TE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0071 | [10 empty] | B1/C05_A1 | [16 empty] | 86 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1660 | #2MTR(1660) |  | DS | 1661 |  | Status | DS | Open/Close | Y | 7 | DI-SP | [6 empty] | 0072 | [10 empty] | B1/C05_A1 | [16 empty] | 87 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1660 | #2MTR(1660) |  | BE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0073 | [10 empty] | B1/C05_A1 | [16 empty] | 88 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C05 | 積六CS | 161 | 161kV | 1660 | #2MTR(1660) |  | TE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0074 | [10 empty] | B1/C05_A1 | [16 empty] | 89 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0096 | [9 empty] | aadz | B1/C04_A1 | [16 empty] | 90 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0097 | [10 empty] | B1/C04_A1 | [16 empty] | 91 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1520 | 積十四～積六線(1520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0098 | [9 empty] | aaba | B1/C04_A1 | [16 empty] | 92 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1520 | 積十四～積六線(1520) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0099 | [10 empty] | B1/C04_A1 | [16 empty] | 93 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1540 | 康寧～積十四線(1540) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0100 | [9 empty] | aafa | B1/C04_A1 | [16 empty] | 94 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1540 | 康寧～積十四線(1540) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0101 | [10 empty] | B1/C04_A1 | [16 empty] | 95 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1520 | 積十四～積六線(1520) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0102 | [10 empty] | B1/C04_A1 | [16 empty] | 96 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1650 | #1MTR(1650) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0104 | [9 empty] | aacb | B1/C04_A1 | [16 empty] | 97 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 |  |  | 1MTR | #1MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0105 | [10 empty] | B1/C04_A1 | [16 empty] | 98 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1660 | #2MTR(1660) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0106 | [9 empty] | aaeb | B1/C04_A1 | [16 empty] | 99 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 |  |  | 2MTR | #2MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0107 | [10 empty] | B1/C04_A1 | [16 empty] | 100 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0120 | [10 empty] | B1/C04_A1 | [16 empty] | 101 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1540 | 康寧～積十四線(1540) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0122 | [10 empty] | B1/C04_A1 | [16 empty] | 102 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 0 |  | StaDev | 所內設施 |  | DTUA | 資料收集設備內部異常故障警報 | [13 empty] | 0123 | [10 empty] | B1/C04_A1 | [16 empty] | 103 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 |  |  | 1MTR | #1MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0124 | [10 empty] | B1/C04_A1 | [16 empty] | 104 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 |  |  | 1MTR | #1MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0125 | [9 empty] | a | B1/C04_A1 | [16 empty] | 105 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 |  |  | 1MTR | #1MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0126 | [10 empty] | B1/C04_A1 | [16 empty] | 106 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 |  |  | 2MTR | #2MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0127 | [10 empty] | B1/C04_A1 | [16 empty] | 107 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 |  |  | 2MTR | #2MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0128 | [9 empty] | a | B1/C04_A1 | [16 empty] | 108 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 |  |  | 2MTR | #2MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0129 | [10 empty] | B1/C04_A1 | [16 empty] | 109 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1520 | 積十四～積六線(1520) |  | 87UL1 |  |  | Status | 第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0130 | [10 empty] | B1/C04_A1 | [16 empty] | 110 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1520 | 積十四～積六線(1520) |  | 87UL2 |  |  | Status | 第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0131 | [10 empty] | B1/C04_A1 | [16 empty] | 111 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 0 |  | StaDev | 所內設施 |  | DTU_CFA | 資料收集設備通訊故障警報 |  | Status | DTU 通訊異常 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0142 | [10 empty] | B1/C04_A1 | [16 empty] | 112 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 0 |  | StaDev | 所內設施 |  | OFA | 光纖通訊故障 | [13 empty] | 0143 | [10 empty] | B1/C04_A1 | [16 empty] | 113 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1500 | TIE(1500) |  | DS | 1501 |  | Status | DS | Open/Close | Y | 7 | DI-SP | [6 empty] | 0144 | [10 empty] | B1/C04_A1 | [16 empty] | 114 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | 15B1E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0146 | [9 empty] | aaaz | B1/C04_A1 | [16 empty] | 115 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | 15B2E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0147 | [9 empty] | aaaz | B1/C04_A1 | [16 empty] | 116 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1520 | 積十四～積六線(1520) |  | DS1 | 1521 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0148 | [10 empty] | B1/C04_A1 | [16 empty] | 117 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1520 | 積十四～積六線(1520) |  | DS2 | 1522 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0149 | [10 empty] | B1/C04_A1 | [16 empty] | 118 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1520 | 積十四～積六線(1520) |  | ES2 | 1522E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0150 | [10 empty] | B1/C04_A1 | [16 empty] | 119 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1520 | 積十四～積六線(1520) |  | LE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0151 | [10 empty] | B1/C04_A1 | [16 empty] | 120 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1520 | 積十四～積六線(1520) |  | BE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0152 | [10 empty] | B1/C04_A1 | [16 empty] | 121 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1520 | 積十四～積六線(1520) |  | DS3 | 1523(備用) |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0153 | [10 empty] | B1/C04_A1 | [16 empty] | 122 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1520 | 積十四～積六線(1520) |  | ES3 | 1523E(備用) |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0154 | [10 empty] | B1/C04_A1 | [16 empty] | 123 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1540 | 康寧～積十四線(1540) |  | DS1 | 1541 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0155 | [10 empty] | B1/C04_A1 | [16 empty] | 124 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1540 | 康寧～積十四線(1540) |  | DS2 | 1542 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0156 | [10 empty] | B1/C04_A1 | [16 empty] | 125 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1540 | 康寧～積十四線(1540) |  | ES2 | 1542E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0157 | [10 empty] | B1/C04_A1 | [16 empty] | 126 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1540 | 康寧～積十四線(1540) |  | LE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0158 | [10 empty] | B1/C04_A1 | [16 empty] | 127 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1540 | 康寧～積十四線(1540) |  | BE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0159 | [10 empty] | B1/C04_A1 | [16 empty] | 128 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 0 |  | StaDev | 所內設施 |  | UPS_DCA | AC故障 | [13 empty] | 0163 | [10 empty] | B1/C04_A1 | [16 empty] | 129 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 0 |  | StaDev | 所內設施 |  | UPS_ACA | DC故障 | [13 empty] | 0164 | [10 empty] | B1/C04_A1 | [16 empty] | 130 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1650 | #1MTR(1650) |  | DS | 1651 |  | Status | DS | Open/Close | Y | 7 | DI-SP | [6 empty] | 0165 | [10 empty] | B1/C04_A1 | [16 empty] | 131 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1650 | #1MTR(1650) |  | BE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0166 | [10 empty] | B1/C04_A1 | [16 empty] | 132 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1650 | #1MTR(1650) |  | TE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0167 | [10 empty] | B1/C04_A1 | [16 empty] | 133 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1660 | #2MTR(1660) |  | DS | 1661 |  | Status | DS | Open/Close | Y | 7 | DI-SP | [6 empty] | 0168 | [10 empty] | B1/C04_A1 | [16 empty] | 134 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1660 | #2MTR(1660) |  | BE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0169 | [10 empty] | B1/C04_A1 | [16 empty] | 135 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C04 | 積十四 | 161 | 161kV | 1660 | #2MTR(1660) |  | TE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0170 | [10 empty] | B1/C04_A1 | [16 empty] | 136 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0192 | [9 empty] | aacz | B1/C02_A1 | [16 empty] | 137 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0193 | [10 empty] | B1/C02_A1 | [16 empty] | 138 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 161 | 161kV | 1520 | 南科～康寧線(1520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0194 | [9 empty] | aaaa | B1/C02_A1 | [16 empty] | 139 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 161 | 161kV | 1520 | 南科～康寧線(1520) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0195 | [10 empty] | B1/C02_A1 | [16 empty] | 140 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 161 | 161kV | 1540 | 康寧～積十四線(1540) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0196 | [9 empty] | aada | B1/C02_A1 | [16 empty] | 141 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 161 | 161kV | 1540 | 康寧～積十四線(1540) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0197 | [10 empty] | B1/C02_A1 | [16 empty] | 142 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 161 | 161kV | 1650 | #1MTR(1650) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0200 | [9 empty] | aabb | B1/C02_A1 | [16 empty] | 143 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS |  |  | 1MTR | #1MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0201 | [10 empty] | B1/C02_A1 | [16 empty] | 144 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 161 | 161kV | 1660 | #2MTR(1660) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0202 | [9 empty] | aaeb | B1/C02_A1 | [16 empty] | 145 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS |  |  | 2MTR | #2MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0203 | [10 empty] | B1/C02_A1 | [16 empty] | 146 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0216 | [10 empty] | B1/C02_A1 | [16 empty] | 147 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 161 | 161kV | 1520 | 南科～康寧線(1520) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0217 | [10 empty] | B1/C02_A1 | [16 empty] | 148 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 161 | 161kV | 1540 | 康寧～積十四線(1540) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0218 | [10 empty] | B1/C02_A1 | [16 empty] | 149 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 0 |  | StaDev | 所內設施 |  | DTUA | 資料收集設備內部異常故障警報 | [13 empty] | 0219 | [10 empty] | B1/C02_A1 | [16 empty] | 150 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS |  |  | 1MTR | #1MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0220 | [10 empty] | B1/C02_A1 | [16 empty] | 151 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS |  |  | 1MTR | #1MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0221 | [9 empty] | a | B1/C02_A1 | [16 empty] | 152 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS |  |  | 1MTR | #1MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0222 | [10 empty] | B1/C02_A1 | [16 empty] | 153 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS |  |  | 2MTR | #2MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0223 | [10 empty] | B1/C02_A1 | [16 empty] | 154 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS |  |  | 2MTR | #2MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0224 | [9 empty] | a | B1/C02_A1 | [16 empty] | 155 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS |  |  | 2MTR | #2MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0225 | [10 empty] | B1/C02_A1 | [16 empty] | 156 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 0 |  | StaDev | 所內設施 |  | DTU_CFA | 資料收集設備通訊故障警報 |  | Status | DTU 通訊異常 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0238 | [10 empty] | B1/C02_A1 | [16 empty] | 157 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 0 |  | StaDev | 所內設施 |  | OFA | 光纖通訊故障 | [13 empty] | 0239 | [10 empty] | B1/C02_A1 | [16 empty] | 158 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 161 | 161kV | 1500 | TIE(1500) |  | DS | 1501 |  | Status | DS | Open/Close | Y | 7 | DI-SP | [6 empty] | 0240 | [10 empty] | B1/C02_A1 | [16 empty] | 159 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | 15B1E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0242 | [9 empty] | aaaz | B1/C02_A1 | [16 empty] | 160 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | 15B2E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0243 | [9 empty] | aaaz | B1/C02_A1 | [16 empty] | 161 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 161 | 161kV | 1520 | 南科～康寧線(1520) |  | DS1 | 1521 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0244 | [10 empty] | B1/C02_A1 | [16 empty] | 162 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 161 | 161kV | 1520 | 南科～康寧線(1520) |  | DS2 | 1522 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0245 | [10 empty] | B1/C02_A1 | [16 empty] | 163 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 161 | 161kV | 1520 | 南科～康寧線(1520) |  | ES2 | 1522E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0246 | [10 empty] | B1/C02_A1 | [16 empty] | 164 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 161 | 161kV | 1520 | 南科～康寧線(1520) |  | LE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0247 | [10 empty] | B1/C02_A1 | [16 empty] | 165 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 161 | 161kV | 1520 | 南科～康寧線(1520) |  | BE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0248 | [10 empty] | B1/C02_A1 | [16 empty] | 166 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 161 | 161kV | 1540 | 康寧～積十四線(1540) |  | DS1 | 1541 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0249 | [10 empty] | B1/C02_A1 | [16 empty] | 167 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 161 | 161kV | 1540 | 康寧～積十四線(1540) |  | DS2 | 1542 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0250 | [10 empty] | B1/C02_A1 | [16 empty] | 168 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 161 | 161kV | 1540 | 康寧～積十四線(1540) |  | ES2 | 1542E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0251 | [10 empty] | B1/C02_A1 | [16 empty] | 169 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 161 | 161kV | 1540 | 康寧～積十四線(1540) |  | LE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0252 | [10 empty] | B1/C02_A1 | [16 empty] | 170 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 161 | 161kV | 1540 | 康寧～積十四線(1540) |  | BE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0253 | [10 empty] | B1/C02_A1 | [16 empty] | 171 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 0 |  | StaDev | 所內設施 |  | UPS_DCA | AC故障 | [13 empty] | 0257 | [10 empty] | B1/C02_A1 | [16 empty] | 172 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 0 |  | StaDev | 所內設施 |  | UPS_ACA | DC故障 | [13 empty] | 0258 | [10 empty] | B1/C02_A1 | [16 empty] | 173 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 161 | 161kV | 1650 | #1MTR(1650) |  | DS | 1651 |  | Status | DS | Open/Close | Y | 7 | DI-SP | [6 empty] | 0259 | [10 empty] | B1/C02_A1 | [16 empty] | 174 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 161 | 161kV | 1650 | #1MTR(1650) |  | BE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0260 | [10 empty] | B1/C02_A1 | [16 empty] | 175 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 161 | 161kV | 1650 | #1MTR(1650) |  | TE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0261 | [10 empty] | B1/C02_A1 | [16 empty] | 176 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 161 | 161kV | 1660 | #2MTR(1660) |  | DS | 1661 |  | Status | DS | Open/Close | Y | 7 | DI-SP | [6 empty] | 0262 | [10 empty] | B1/C02_A1 | [16 empty] | 177 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 161 | 161kV | 1660 | #2MTR(1660) |  | BE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0263 | [10 empty] | B1/C02_A1 | [16 empty] | 178 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C02 | 康寧CS | 161 | 161kV | 1660 | #2MTR(1660) |  | TE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0264 | [10 empty] | B1/C02_A1 | [16 empty] | 179 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0288 | [9 empty] | aacz | B1/C03_A1 | [16 empty] | 180 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1710 | 和鑫二～積P3線(1710) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0290 | [9 empty] | aaba | B1/C03_A1 | [16 empty] | 181 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1720 | 南科～積P3線(1720) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0292 | [9 empty] | aaaa | B1/C03_A1 | [16 empty] | 182 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1650 | #1MTR(1650) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0296 | [9 empty] | aaeb | B1/C03_A1 | [16 empty] | 183 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1660 | #2MTR(1660) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0298 | [9 empty] | aafb | B1/C03_A1 | [16 empty] | 184 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1670 | #3MTR(1670) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0300 | [9 empty] | aagb | B1/C03_A1 | [16 empty] | 185 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS |  |  | 3MTR | #3MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0301 | [10 empty] | B1/C03_A1 | [16 empty] | 186 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1680 | #4MTR(1680) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0302 | [9 empty] | aahb | B1/C03_A1 | [16 empty] | 187 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS |  |  | 4MTR | #4MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0303 | [10 empty] | B1/C03_A1 | [16 empty] | 188 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1710 | 和鑫二～積P3線(1710) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0313 | [10 empty] | B1/C03_A1 | [16 empty] | 189 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1720 | 南科～積P3線(1720) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0314 | [10 empty] | B1/C03_A1 | [16 empty] | 190 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS |  |  | 3MTR | #3MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0322 | [10 empty] | B1/C03_A1 | [16 empty] | 191 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS |  |  | 3MTR | #3MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0323 | [9 empty] | a | B1/C03_A1 | [16 empty] | 192 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS |  |  | 3MTR | #3MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0324 | [10 empty] | B1/C03_A1 | [16 empty] | 193 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS |  |  | 4MTR | #4MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0325 | [10 empty] | B1/C03_A1 | [16 empty] | 194 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS |  |  | 4MTR | #4MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0326 | [9 empty] | a | B1/C03_A1 | [16 empty] | 195 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS |  |  | 4MTR | #4MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0327 | [10 empty] | B1/C03_A1 | [16 empty] | 196 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 0 |  | StaDev | 所內設施 |  | DTU_CFA | 資料收集設備通訊故障警報 |  | Status | DTU 通訊異常 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0334 | [10 empty] | B1/C03_A1 | [16 empty] | 197 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 0 |  | StaDev | 所內設施 |  | OFA | 光纖通訊故障 | [13 empty] | 0335 | [10 empty] | B1/C03_A1 | [16 empty] | 198 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0336 | [10 empty] | B1/C03_A1 | [16 empty] | 199 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0337 | [10 empty] | B1/C03_A1 | [16 empty] | 200 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0338 | [10 empty] | B1/C03_A1 | [16 empty] | 201 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0339 | [10 empty] | B1/C03_A1 | [16 empty] | 202 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | 15B1E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0340 | [9 empty] | aadz | B1/C03_A1 | [16 empty] | 203 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | 15B2E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0341 | [9 empty] | aadz | B1/C03_A1 | [16 empty] | 204 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1710 | 和鑫二～積P3線(1710) |  | DS1 | 1711 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0342 | [10 empty] | B1/C03_A1 | [16 empty] | 205 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1710 | 和鑫二～積P3線(1710) |  | DS2 | 1712 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0343 | [10 empty] | B1/C03_A1 | [16 empty] | 206 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1710 | 和鑫二～積P3線(1710) |  | DS3 | 1713 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0345 | [10 empty] | B1/C03_A1 | [16 empty] | 207 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1710 | 和鑫二～積P3線(1710) |  | ES3 | 1713E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0346 | [10 empty] | B1/C03_A1 | [16 empty] | 208 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1710 | 和鑫二～積P3線(1710) |  | LE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0347 | [10 empty] | B1/C03_A1 | [16 empty] | 209 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1710 | 和鑫二～積P3線(1710) |  | BE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0348 | [10 empty] | B1/C03_A1 | [16 empty] | 210 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1720 | 南科～積P3線(1720) |  | DS1 | 1721 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0349 | [10 empty] | B1/C03_A1 | [16 empty] | 211 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1720 | 南科～積P3線(1720) |  | DS2 | 1722 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0350 | [10 empty] | B1/C03_A1 | [16 empty] | 212 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1720 | 南科～積P3線(1720) |  | DS3 | 1723 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0352 | [10 empty] | B1/C03_A1 | [16 empty] | 213 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1720 | 南科～積P3線(1720) |  | ES3 | 1723E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0353 | [10 empty] | B1/C03_A1 | [16 empty] | 214 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1720 | 南科～積P3線(1720) |  | LE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0354 | [10 empty] | B1/C03_A1 | [16 empty] | 215 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1720 | 南科～積P3線(1720) |  | BE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0355 | [10 empty] | B1/C03_A1 | [16 empty] | 216 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1650 | #1MTR(1650) |  | DS1 | 1651 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0360 | [10 empty] | B1/C03_A1 | [16 empty] | 217 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1650 | #1MTR(1650) |  | DS2 | 1652 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0361 | [10 empty] | B1/C03_A1 | [16 empty] | 218 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1650 | #1MTR(1650) |  | BE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0362 | [10 empty] | B1/C03_A1 | [16 empty] | 219 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1650 | #1MTR(1650) |  | TE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0363 | [10 empty] | B1/C03_A1 | [16 empty] | 220 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1660 | #2MTR(1660) |  | DS1 | 1661 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0364 | [10 empty] | B1/C03_A1 | [16 empty] | 221 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1660 | #2MTR(1660) |  | DS2 | 1662 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0365 | [10 empty] | B1/C03_A1 | [16 empty] | 222 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1660 | #2MTR(1660) |  | BE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0366 | [10 empty] | B1/C03_A1 | [16 empty] | 223 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1660 | #2MTR(1660) |  | TE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0367 | [10 empty] | B1/C03_A1 | [16 empty] | 224 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1670 | #3MTR(1670) |  | DS1 | 1671 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0368 | [10 empty] | B1/C03_A1 | [16 empty] | 225 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1670 | #3MTR(1670) |  | DS2 | 1672 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0369 | [10 empty] | B1/C03_A1 | [16 empty] | 226 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1670 | #3MTR(1670) |  | BE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0370 | [10 empty] | B1/C03_A1 | [16 empty] | 227 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1670 | #3MTR(1670) |  | TE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0371 | [10 empty] | B1/C03_A1 | [16 empty] | 228 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1680 | #4MTR(1680) |  | DS1 | 1681 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0372 | [10 empty] | B1/C03_A1 | [16 empty] | 229 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1680 | #4MTR(1680) |  | DS2 | 1682 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0373 | [10 empty] | B1/C03_A1 | [16 empty] | 230 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1680 | #4MTR(1680) |  | BE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0374 | [10 empty] | B1/C03_A1 | [16 empty] | 231 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C03 | 積P3CS | 161 | 161kV | 1680 | #4MTR(1680) |  | TE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0375 | [10 empty] | B1/C03_A1 | [16 empty] | 232 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0384 | [9 empty] | aadz | B1/C08_A1 | [16 empty] | 233 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0385 | [10 empty] | B1/C08_A1 | [16 empty] | 234 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1530 | 積E五~積E七線(1530) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0386 | [9 empty] | aaca | B1/C08_A1 | [16 empty] | 235 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1530 | 積E五~積E七線(1530) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0387 | [10 empty] | B1/C08_A1 | [16 empty] | 236 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1540 | 積E六~積E五線(1540) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0388 | [9 empty] | aaba | B1/C08_A1 | [16 empty] | 237 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1540 | 積E六~積E五線(1540) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0389 | [10 empty] | B1/C08_A1 | [16 empty] | 238 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1650 | #1MTR(1650) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0392 | [9 empty] | aafb | B1/C08_A1 | [16 empty] | 239 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 |  |  | 1MTR | #1MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0393 | [10 empty] | B1/C08_A1 | [16 empty] | 240 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1660 | #2MTR(1660) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0394 | [9 empty] | aagb | B1/C08_A1 | [16 empty] | 241 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 |  |  | 2MTR | #2MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0395 | [10 empty] | B1/C08_A1 | [16 empty] | 242 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1670 | #3MTR(1670) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0396 | [9 empty] | aahb | B1/C08_A1 | [16 empty] | 243 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 |  |  | 3MTR | #3MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0397 | [10 empty] | B1/C08_A1 | [16 empty] | 244 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1680 | #4MTR(1680) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0398 | [9 empty] | aaib | B1/C08_A1 | [16 empty] | 245 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 |  |  | 4MTR | #4MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0399 | [10 empty] | B1/C08_A1 | [16 empty] | 246 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0408 | [10 empty] | B1/C08_A1 | [16 empty] | 247 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1530 | 積E五~積E七線(1530) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0409 | [10 empty] | B1/C08_A1 | [16 empty] | 248 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1540 | 積E六~積E五線(1540) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0410 | [10 empty] | B1/C08_A1 | [16 empty] | 249 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 0 |  | StaDev | 所內設施 |  | DTUA | 資料收集設備內部異常故障警報 | [13 empty] | 0411 | [10 empty] | B1/C08_A1 | [16 empty] | 250 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 |  |  | 1MTR | #1MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0412 | [10 empty] | B1/C08_A1 | [16 empty] | 251 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 |  |  | 1MTR | #1MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0413 | [9 empty] | a | B1/C08_A1 | [16 empty] | 252 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 |  |  | 1MTR | #1MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0414 | [10 empty] | B1/C08_A1 | [16 empty] | 253 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 |  |  | 2MTR | #2MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0415 | [10 empty] | B1/C08_A1 | [16 empty] | 254 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 |  |  | 2MTR | #2MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0416 | [9 empty] | a | B1/C08_A1 | [16 empty] | 255 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 |  |  | 2MTR | #2MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0417 | [10 empty] | B1/C08_A1 | [16 empty] | 256 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 |  |  | 3MTR | #3MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0418 | [10 empty] | B1/C08_A1 | [16 empty] | 257 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 |  |  | 3MTR | #3MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0419 | [9 empty] | a | B1/C08_A1 | [16 empty] | 258 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 |  |  | 3MTR | #3MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0420 | [10 empty] | B1/C08_A1 | [16 empty] | 259 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 |  |  | 4MTR | #4MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0421 | [10 empty] | B1/C08_A1 | [16 empty] | 260 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 |  |  | 4MTR | #4MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0422 | [9 empty] | a | B1/C08_A1 | [16 empty] | 261 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 |  |  | 4MTR | #4MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0423 | [10 empty] | B1/C08_A1 | [16 empty] | 262 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 0 |  | StaDev | 所內設施 |  | DTU_CFA | 資料收集設備通訊故障警報 |  | Status | DTU 通訊異常 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0430 | [10 empty] | B1/C08_A1 | [16 empty] | 263 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 0 |  | StaDev | 所內設施 |  | OFA | 光纖通訊故障 | [13 empty] | 0431 | [10 empty] | B1/C08_A1 | [16 empty] | 264 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0432 | [10 empty] | B1/C08_A1 | [16 empty] | 265 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0433 | [10 empty] | B1/C08_A1 | [16 empty] | 266 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0434 | [10 empty] | B1/C08_A1 | [16 empty] | 267 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0435 | [10 empty] | B1/C08_A1 | [16 empty] | 268 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | 15B1E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0436 | [9 empty] | aaaz | B1/C08_A1 | [16 empty] | 269 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | 15B2E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0437 | [9 empty] | aaaz | B1/C08_A1 | [16 empty] | 270 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1530 | 積E五~積E七線(1530) |  | DS1 | 1531 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0438 | [10 empty] | B1/C08_A1 | [16 empty] | 271 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1530 | 積E五~積E七線(1530) |  | DS2 | 1532 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0439 | [10 empty] | B1/C08_A1 | [16 empty] | 272 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1530 | 積E五~積E七線(1530) |  | DS3 | 1533 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0440 | [10 empty] | B1/C08_A1 | [16 empty] | 273 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1530 | 積E五~積E七線(1530) |  | ES3 | 1533E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0441 | [10 empty] | B1/C08_A1 | [16 empty] | 274 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1530 | 積E五~積E七線(1530) |  | LE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0442 | [10 empty] | B1/C08_A1 | [16 empty] | 275 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1530 | 積E五~積E七線(1530) |  | BE1 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0443 | [9 empty] | no rule | B1/C08_A1 | [16 empty] | 276 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1530 | 積E五~積E七線(1530) |  | BE2 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0444 | [9 empty] | no rule | B1/C08_A1 | [16 empty] | 277 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1540 | 積E六~積E五線(1540) |  | DS1 | 1541 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0445 | [10 empty] | B1/C08_A1 | [16 empty] | 278 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1540 | 積E六~積E五線(1540) |  | DS2 | 1542 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0446 | [10 empty] | B1/C08_A1 | [16 empty] | 279 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1540 | 積E六~積E五線(1540) |  | DS3 | 1543 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0447 | [10 empty] | B1/C08_A1 | [16 empty] | 280 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1540 | 積E六~積E五線(1540) |  | ES3 | 1543E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0448 | [10 empty] | B1/C08_A1 | [16 empty] | 281 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1540 | 積E六~積E五線(1540) |  | LE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0449 | [10 empty] | B1/C08_A1 | [16 empty] | 282 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1540 | 積E六~積E五線(1540) |  | BE1 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0450 | [9 empty] | no rule | B1/C08_A1 | [16 empty] | 283 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1540 | 積E六~積E五線(1540) |  | BE2 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0451 | [9 empty] | no rule | B1/C08_A1 | [16 empty] | 284 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 0 |  | StaDev | 所內設施 |  | UPS_DCA | AC故障 | [13 empty] | 0454 | [10 empty] | B1/C08_A1 | [16 empty] | 285 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 0 |  | StaDev | 所內設施 |  | UPS_ACA | DC故障 | [13 empty] | 0455 | [10 empty] | B1/C08_A1 | [16 empty] | 286 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1650 | #1MTR(1650) |  | DS1 | 1651 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0456 | [10 empty] | B1/C08_A1 | [16 empty] | 287 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1650 | #1MTR(1650) |  | DS2 | 1652 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0457 | [10 empty] | B1/C08_A1 | [16 empty] | 288 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1650 | #1MTR(1650) |  | BE1 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0458 | [9 empty] | no rule | B1/C08_A1 | [16 empty] | 289 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1650 | #1MTR(1650) |  | BE2 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0459 | [9 empty] | no rule | B1/C08_A1 | [16 empty] | 290 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1650 | #1MTR(1650) |  | TE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0460 | [10 empty] | B1/C08_A1 | [16 empty] | 291 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1660 | #2MTR(1660) |  | DS1 | 1661 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0461 | [10 empty] | B1/C08_A1 | [16 empty] | 292 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1660 | #2MTR(1660) |  | DS2 | 1662 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0462 | [10 empty] | B1/C08_A1 | [16 empty] | 293 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1660 | #2MTR(1660) |  | BE1 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0463 | [9 empty] | no rule | B1/C08_A1 | [16 empty] | 294 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1660 | #2MTR(1660) |  | BE2 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0464 | [9 empty] | no rule | B1/C08_A1 | [16 empty] | 295 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1660 | #2MTR(1660) |  | TE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0465 | [10 empty] | B1/C08_A1 | [16 empty] | 296 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1670 | #3MTR(1670) |  | DS1 | 1671 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0466 | [10 empty] | B1/C08_A1 | [16 empty] | 297 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1670 | #3MTR(1670) |  | DS2 | 1672 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0467 | [10 empty] | B1/C08_A1 | [16 empty] | 298 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1670 | #3MTR(1670) |  | BE1 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0468 | [9 empty] | no rule | B1/C08_A1 | [16 empty] | 299 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1670 | #3MTR(1670) |  | BE2 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0469 | [9 empty] | no rule | B1/C08_A1 | [16 empty] | 300 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1670 | #3MTR(1670) |  | TE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0470 | [10 empty] | B1/C08_A1 | [16 empty] | 301 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1680 | #4MTR(1680) |  | DS1 | 1681 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0471 | [10 empty] | B1/C08_A1 | [16 empty] | 302 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1680 | #4MTR(1680) |  | DS2 | 1682 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0472 | [10 empty] | B1/C08_A1 | [16 empty] | 303 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1680 | #4MTR(1680) |  | BE1 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0473 | [9 empty] | no rule | B1/C08_A1 | [16 empty] | 304 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1680 | #4MTR(1680) |  | BE2 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0474 | [9 empty] | no rule | B1/C08_A1 | [16 empty] | 305 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C08 | 積E五 | 161 | 161kV | 1680 | #4MTR(1680) |  | TE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0475 | [10 empty] | B1/C08_A1 | [16 empty] | 306 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0480 | [9 empty] | aadz | B1/C09_A1 | [16 empty] | 307 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1530 | 積E六~積E五線(1530) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0482 | [9 empty] | aaca | B1/C09_A1 | [16 empty] | 308 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1540 | 南科~積E六線(1540) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0484 | [9 empty] | aaba | B1/C09_A1 | [16 empty] | 309 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1650 | #5MTR(1650) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0488 | [9 empty] | aafb | B1/C09_A1 | [16 empty] | 310 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1660 | #6MTR(1660) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0490 | [9 empty] | aagb | B1/C09_A1 | [16 empty] | 311 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1670 | #7MTR(1670) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0492 | [9 empty] | aahb | B1/C09_A1 | [16 empty] | 312 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1680 | #8MTR(1680) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0494 | [9 empty] | aaib | B1/C09_A1 | [16 empty] | 313 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 0 |  | StaDev | 所內設施 |  | DTU_CFA | 資料收集設備通訊故障警報 |  | Status | DTU 通訊異常 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0526 | [10 empty] | B1/C09_A1 | [16 empty] | 314 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 0 |  | StaDev | 所內設施 |  | OFA | 光纖通訊故障 | [13 empty] | 0527 | [10 empty] | B1/C09_A1 | [16 empty] | 315 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0528 | [10 empty] | B1/C09_A1 | [16 empty] | 316 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0529 | [10 empty] | B1/C09_A1 | [16 empty] | 317 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0530 | [10 empty] | B1/C09_A1 | [16 empty] | 318 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0531 | [10 empty] | B1/C09_A1 | [16 empty] | 319 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | 15B1E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0532 | [9 empty] | aaaz | B1/C09_A1 | [16 empty] | 320 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | 15B2E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0533 | [9 empty] | aaaz | B1/C09_A1 | [16 empty] | 321 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1540 | 南科~積E六線(1540) |  | DS3 | 1543 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0534 | [10 empty] | B1/C09_A1 | [16 empty] | 322 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1540 | 南科~積E六線(1540) |  | DS1 | 1541 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0535 | [10 empty] | B1/C09_A1 | [16 empty] | 323 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1540 | 南科~積E六線(1540) |  | ES3 | 1543E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0536 | [10 empty] | B1/C09_A1 | [16 empty] | 324 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1540 | 南科~積E六線(1540) |  | DS2 | 1542 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0537 | [10 empty] | B1/C09_A1 | [16 empty] | 325 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1540 | 南科~積E六線(1540) |  | BE1 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0538 | [9 empty] | no rule | B1/C09_A1 | [16 empty] | 326 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1540 | 南科~積E六線(1540) |  | LE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0539 | [10 empty] | B1/C09_A1 | [16 empty] | 327 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1540 | 南科~積E六線(1540) |  | BE2 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0540 | [9 empty] | no rule | B1/C09_A1 | [16 empty] | 328 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1530 | 積E六~積E五線(1530) |  | DS3 | 1533 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0541 | [10 empty] | B1/C09_A1 | [16 empty] | 329 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1530 | 積E六~積E五線(1530) |  | DS1 | 1531 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0542 | [10 empty] | B1/C09_A1 | [16 empty] | 330 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1530 | 積E六~積E五線(1530) |  | ES3 | 1533E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0543 | [10 empty] | B1/C09_A1 | [16 empty] | 331 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1530 | 積E六~積E五線(1530) |  | DS2 | 1532 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0544 | [10 empty] | B1/C09_A1 | [16 empty] | 332 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1530 | 積E六~積E五線(1530) |  | BE1 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0545 | [9 empty] | no rule | B1/C09_A1 | [16 empty] | 333 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1530 | 積E六~積E五線(1530) |  | LE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0546 | [10 empty] | B1/C09_A1 | [16 empty] | 334 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1530 | 積E六~積E五線(1530) |  | BE2 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0547 | [9 empty] | no rule | B1/C09_A1 | [16 empty] | 335 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1650 | #5MTR(1650) |  | DS1 | 1651 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0552 | [10 empty] | B1/C09_A1 | [16 empty] | 336 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1650 | #5MTR(1650) |  | DS2 | 1652 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0553 | [10 empty] | B1/C09_A1 | [16 empty] | 337 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1650 | #5MTR(1650) |  | BE1 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0554 | [9 empty] | no rule | B1/C09_A1 | [16 empty] | 338 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1650 | #5MTR(1650) |  | BE2 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0555 | [9 empty] | no rule | B1/C09_A1 | [16 empty] | 339 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1650 | #5MTR(1650) |  | TE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0556 | [10 empty] | B1/C09_A1 | [16 empty] | 340 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1660 | #6MTR(1660) |  | DS1 | 1661 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0557 | [10 empty] | B1/C09_A1 | [16 empty] | 341 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1660 | #6MTR(1660) |  | DS2 | 1662 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0558 | [10 empty] | B1/C09_A1 | [16 empty] | 342 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1660 | #6MTR(1660) |  | BE1 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0559 | [9 empty] | no rule | B1/C09_A1 | [16 empty] | 343 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1660 | #6MTR(1660) |  | BE2 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0560 | [9 empty] | no rule | B1/C09_A1 | [16 empty] | 344 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1660 | #6MTR(1660) |  | TE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0561 | [10 empty] | B1/C09_A1 | [16 empty] | 345 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1670 | #7MTR(1670) |  | DS1 | 1671 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0562 | [10 empty] | B1/C09_A1 | [16 empty] | 346 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1670 | #7MTR(1670) |  | DS2 | 1672 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0563 | [10 empty] | B1/C09_A1 | [16 empty] | 347 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1670 | #7MTR(1670) |  | BE1 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0564 | [9 empty] | no rule | B1/C09_A1 | [16 empty] | 348 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1670 | #7MTR(1670) |  | BE2 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0565 | [9 empty] | no rule | B1/C09_A1 | [16 empty] | 349 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1670 | #7MTR(1670) |  | TE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0566 | [10 empty] | B1/C09_A1 | [16 empty] | 350 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1680 | #8MTR(1680) |  | DS1 | 1681 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0567 | [10 empty] | B1/C09_A1 | [16 empty] | 351 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1680 | #8MTR(1680) |  | DS2 | 1682 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0568 | [10 empty] | B1/C09_A1 | [16 empty] | 352 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1680 | #8MTR(1680) |  | BE1 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0569 | [9 empty] | no rule | B1/C09_A1 | [16 empty] | 353 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1680 | #8MTR(1680) |  | BE2 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0570 | [9 empty] | no rule | B1/C09_A1 | [16 empty] | 354 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1680 | #8MTR(1680) |  | TE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0571 | [10 empty] | B1/C09_A1 | [16 empty] | 355 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0576 | [9 empty] | aacz | B1/C06_A1 | [16 empty] | 356 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0577 | [10 empty] | B1/C06_A1 | [16 empty] | 357 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0578 | [9 empty] | aaaa | B1/C06_A1 | [16 empty] | 358 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0579 | [10 empty] | B1/C06_A1 | [16 empty] | 359 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0580 | [10 empty] | B1/C06_A1 | [16 empty] | 360 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1520 | 三福一~積E七線(1520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0581 | [9 empty] | aaba | B1/C06_A1 | [16 empty] | 361 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1520 | 三福一~積E七線(1520) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0582 | [10 empty] | B1/C06_A1 | [16 empty] | 362 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1520 | 三福一~積E七線(1520) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0583 | [10 empty] | B1/C06_A1 | [16 empty] | 363 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1650 | #1MTR(1650) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0584 | [9 empty] | aaeb | B1/C06_A1 | [16 empty] | 364 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1530 | 積E六~積E五線(1530) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0585 | [10 empty] | B1/C09_A1 | [16 empty] | 365 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1660 | #2MTR(1660) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0585 | [9 empty] | aafb | B1/C06_A1 | [16 empty] | 366 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C09 | 積E六 | 161 | 161kV | 1540 | 南科~積E六線(1540) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0586 | [10 empty] | B1/C09_A1 | [16 empty] | 367 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0586 | [10 empty] | B1/C06_A1 | [16 empty] | 368 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0587 | [10 empty] | B1/C06_A1 | [16 empty] | 369 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0588 | [10 empty] | B1/C06_A1 | [16 empty] | 370 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | 21A |  |  | Status | 21RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0589 | [10 empty] | B1/C06_A1 | [16 empty] | 371 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | DTTA |  |  | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0590 | [10 empty] | B1/C06_A1 | [16 empty] | 372 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1520 | 三福一~積E七線(1520) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0591 | [10 empty] | B1/C06_A1 | [16 empty] | 373 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1520 | 三福一~積E七線(1520) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0592 | [10 empty] | B1/C06_A1 | [16 empty] | 374 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1520 | 三福一~積E七線(1520) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0593 | [10 empty] | B1/C06_A1 | [16 empty] | 375 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1520 | 三福一~積E七線(1520) |  | 21A |  |  | Status | 21RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0594 | [10 empty] | B1/C06_A1 | [16 empty] | 376 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1520 | 三福一~積E七線(1520) |  | DTTA |  |  | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0595 | [10 empty] | B1/C06_A1 | [16 empty] | 377 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0596 | [10 empty] | B1/C06_A1 | [16 empty] | 378 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0597 | [10 empty] | B1/C06_A1 | [16 empty] | 379 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | 87UL1 |  |  | Status | 第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0601 | [10 empty] | B1/C06_A1 | [16 empty] | 380 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | 87UL2 |  |  | Status | 第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0602 | [10 empty] | B1/C06_A1 | [16 empty] | 381 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1520 | 三福一~積E七線(1520) |  | 87UL1 |  |  | Status | 第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0603 | [10 empty] | B1/C06_A1 | [16 empty] | 382 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1520 | 三福一~積E七線(1520) |  | 87UL2 |  |  | Status | 第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0604 | [10 empty] | B1/C06_A1 | [16 empty] | 383 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0605 | [10 empty] | B1/C06_A1 | [16 empty] | 384 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1520 | 三福一~積E七線(1520) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0606 | [10 empty] | B1/C06_A1 | [16 empty] | 385 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 0 |  | StaDev | 所內設施 |  | OFA | 光纖通訊故障 | [13 empty] | 0613 | [10 empty] | B1/C06_A1 | [16 empty] | 386 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0614 | [10 empty] | B1/C06_A1 | [16 empty] | 387 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0615 | [10 empty] | B1/C06_A1 | [16 empty] | 388 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0616 | [10 empty] | B1/C06_A1 | [16 empty] | 389 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0617 | [10 empty] | B1/C06_A1 | [16 empty] | 390 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | 15B1E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0618 | [9 empty] | aadz | B1/C06_A1 | [16 empty] | 391 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | 15B2E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0619 | [9 empty] | aadz | B1/C06_A1 | [16 empty] | 392 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1520 | 三福一~積E七線(1520) |  | DS3 | 1523 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0620 | [10 empty] | B1/C06_A1 | [16 empty] | 393 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1520 | 三福一~積E七線(1520) |  | DS1 | 1521 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0621 | [10 empty] | B1/C06_A1 | [16 empty] | 394 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1520 | 三福一~積E七線(1520) |  | ES3 | 1523E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0622 | [10 empty] | B1/C06_A1 | [16 empty] | 395 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1520 | 三福一~積E七線(1520) |  | DS2 | 1522 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0623 | [10 empty] | B1/C06_A1 | [16 empty] | 396 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1520 | 三福一~積E七線(1520) |  | BE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0624 | [10 empty] | B1/C06_A1 | [16 empty] | 397 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1520 | 三福一~積E七線(1520) |  | LE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0625 | [10 empty] | B1/C06_A1 | [16 empty] | 398 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | DS3 | 1533 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0627 | [10 empty] | B1/C06_A1 | [16 empty] | 399 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | DS1 | 1531 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0628 | [10 empty] | B1/C06_A1 | [16 empty] | 400 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | ES3 | 1533E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0629 | [10 empty] | B1/C06_A1 | [16 empty] | 401 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | DS2 | 1532 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0630 | [10 empty] | B1/C06_A1 | [16 empty] | 402 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | BE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0631 | [10 empty] | B1/C06_A1 | [16 empty] | 403 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | LE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0632 | [10 empty] | B1/C06_A1 | [16 empty] | 404 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1650 | #1MTR(1650) |  | DS1 | 1651 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0636 | [10 empty] | B1/C06_A1 | [16 empty] | 405 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1650 | #1MTR(1650) |  | DS2 | 1652 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0637 | [10 empty] | B1/C06_A1 | [16 empty] | 406 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1650 | #1MTR(1650) |  | BE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0638 | [10 empty] | B1/C06_A1 | [16 empty] | 407 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1650 | #1MTR(1650) |  | TE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0639 | [10 empty] | B1/C06_A1 | [16 empty] | 408 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1660 | #2MTR(1660) |  | DS1 | 1661 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0640 | [10 empty] | B1/C06_A1 | [16 empty] | 409 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1660 | #2MTR(1660) |  | DS2 | 1662 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0641 | [10 empty] | B1/C06_A1 | [16 empty] | 410 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1660 | #2MTR(1660) |  | BE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0642 | [10 empty] | B1/C06_A1 | [16 empty] | 411 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C06 | 三福一 | 161 | 161kV | 1660 | #2MTR(1660) |  | TE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0643 | [10 empty] | B1/C06_A1 | [16 empty] | 412 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0760 | [9 empty] | aadz | B1/C07_A1 | [16 empty] | 413 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0761 | [10 empty] | B1/C07_A1 | [16 empty] | 414 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1530 | 積E五~積E七線(1530) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0762 | [9 empty] | aaba | B1/C07_A1 | [16 empty] | 415 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1530 | 積E五~積E七線(1530) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0763 | [10 empty] | B1/C07_A1 | [16 empty] | 416 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1520 | 三福一~積E七線(1520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0764 | [9 empty] | aaca | B1/C07_A1 | [16 empty] | 417 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1520 | 三福一~積E七線(1520) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0765 | [10 empty] | B1/C07_A1 | [16 empty] | 418 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1650 | #1MTR(1650) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0768 | [9 empty] | aafb | B1/C07_A1 | [16 empty] | 419 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 |  |  | 1MTR | #1MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0769 | [10 empty] | B1/C07_A1 | [16 empty] | 420 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1660 | #2MTR(1660) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0770 | [9 empty] | aagb | B1/C07_A1 | [16 empty] | 421 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 |  |  | 2MTR | #2MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0771 | [10 empty] | B1/C07_A1 | [16 empty] | 422 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1670 | #3MTR(1670) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0772 | [9 empty] | aahb | B1/C07_A1 | [16 empty] | 423 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 |  |  | 3MTR | #3MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0773 | [10 empty] | B1/C07_A1 | [16 empty] | 424 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1680 | #4MTR(1680) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0774 | [9 empty] | aaib | B1/C07_A1 | [16 empty] | 425 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 |  |  | 4MTR | #4MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0775 | [10 empty] | B1/C07_A1 | [16 empty] | 426 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0776 | [10 empty] | B1/C07_A1 | [16 empty] | 427 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1530 | 積E五~積E七線(1530) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0777 | [10 empty] | B1/C07_A1 | [16 empty] | 428 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1520 | 三福一~積E七線(1520) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0778 | [10 empty] | B1/C07_A1 | [16 empty] | 429 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 |  |  | 1MTR | #1MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0779 | [10 empty] | B1/C07_A1 | [16 empty] | 430 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 |  |  | 2MTR | #2MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0780 | [10 empty] | B1/C07_A1 | [16 empty] | 431 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 |  |  | 3MTR | #3MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0781 | [10 empty] | B1/C07_A1 | [16 empty] | 432 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 |  |  | 4MTR | #4MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0782 | [10 empty] | B1/C07_A1 | [16 empty] | 433 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 0 |  | StaDev | 所內設施 |  | OFA | 光纖通訊故障 | [13 empty] | 0793 | [10 empty] | B1/C07_A1 | [16 empty] | 434 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0794 | [10 empty] | B1/C07_A1 | [16 empty] | 435 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0795 | [10 empty] | B1/C07_A1 | [16 empty] | 436 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0796 | [10 empty] | B1/C07_A1 | [16 empty] | 437 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0797 | [10 empty] | B1/C07_A1 | [16 empty] | 438 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | 15B1E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0798 | [9 empty] | aaaz | B1/C07_A1 | [16 empty] | 439 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | 15B2E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0799 | [9 empty] | aaaz | B1/C07_A1 | [16 empty] | 440 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1530 | 積E五~積E七線(1530) |  | DS3 | 1533 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0800 | [10 empty] | B1/C07_A1 | [16 empty] | 441 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1530 | 積E五~積E七線(1530) |  | DS1 | 1531 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0801 | [10 empty] | B1/C07_A1 | [16 empty] | 442 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1530 | 積E五~積E七線(1530) |  | ES3 | 1533E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0802 | [10 empty] | B1/C07_A1 | [16 empty] | 443 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1530 | 積E五~積E七線(1530) |  | DS2 | 1532 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0803 | [10 empty] | B1/C07_A1 | [16 empty] | 444 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1530 | 積E五~積E七線(1530) |  | BE1 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0804 | [9 empty] | no rule | B1/C07_A1 | [16 empty] | 445 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1530 | 積E五~積E七線(1530) |  | LE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0805 | [10 empty] | B1/C07_A1 | [16 empty] | 446 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1530 | 積E五~積E七線(1530) |  | BE2 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0806 | [9 empty] | no rule | B1/C07_A1 | [16 empty] | 447 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1520 | 三福一~積E七線(1520) |  | DS3 | 1523 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0807 | [10 empty] | B1/C07_A1 | [16 empty] | 448 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1520 | 三福一~積E七線(1520) |  | DS1 | 1521 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0808 | [10 empty] | B1/C07_A1 | [16 empty] | 449 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1520 | 三福一~積E七線(1520) |  | ES3 | 1523E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0809 | [10 empty] | B1/C07_A1 | [16 empty] | 450 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1520 | 三福一~積E七線(1520) |  | DS2 | 1522 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0810 | [10 empty] | B1/C07_A1 | [16 empty] | 451 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1520 | 三福一~積E七線(1520) |  | BE1 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0811 | [9 empty] | no rule | B1/C07_A1 | [16 empty] | 452 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1520 | 三福一~積E七線(1520) |  | LE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0812 | [10 empty] | B1/C07_A1 | [16 empty] | 453 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1520 | 三福一~積E七線(1520) |  | BE2 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0813 | [9 empty] | no rule | B1/C07_A1 | [16 empty] | 454 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1650 | #1MTR(1650) |  | DS1 | 1651 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0816 | [10 empty] | B1/C07_A1 | [16 empty] | 455 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1650 | #1MTR(1650) |  | DS2 | 1652 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0817 | [10 empty] | B1/C07_A1 | [16 empty] | 456 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1650 | #1MTR(1650) |  | BE1 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0818 | [9 empty] | no rule | B1/C07_A1 | [16 empty] | 457 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1650 | #1MTR(1650) |  | BE2 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0819 | [9 empty] | no rule | B1/C07_A1 | [16 empty] | 458 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1650 | #1MTR(1650) |  | TE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0820 | [10 empty] | B1/C07_A1 | [16 empty] | 459 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1660 | #2MTR(1660) |  | DS1 | 1661 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0821 | [10 empty] | B1/C07_A1 | [16 empty] | 460 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1660 | #2MTR(1660) |  | DS2 | 1662 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0822 | [10 empty] | B1/C07_A1 | [16 empty] | 461 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1660 | #2MTR(1660) |  | BE1 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0823 | [9 empty] | no rule | B1/C07_A1 | [16 empty] | 462 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1660 | #2MTR(1660) |  | BE2 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0824 | [9 empty] | no rule | B1/C07_A1 | [16 empty] | 463 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1660 | #2MTR(1660) |  | TE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0825 | [10 empty] | B1/C07_A1 | [16 empty] | 464 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1670 | #3MTR(1670) |  | DS1 | 1671 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0826 | [10 empty] | B1/C07_A1 | [16 empty] | 465 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1670 | #3MTR(1670) |  | DS2 | 1672 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0827 | [10 empty] | B1/C07_A1 | [16 empty] | 466 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1670 | #3MTR(1670) |  | BE1 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0828 | [9 empty] | no rule | B1/C07_A1 | [16 empty] | 467 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1670 | #3MTR(1670) |  | BE2 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0829 | [9 empty] | no rule | B1/C07_A1 | [16 empty] | 468 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1670 | #3MTR(1670) |  | TE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0830 | [10 empty] | B1/C07_A1 | [16 empty] | 469 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1680 | #4MTR(1680) |  | DS1 | 1681 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0831 | [10 empty] | B1/C07_A1 | [16 empty] | 470 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1680 | #4MTR(1680) |  | DS2 | 1682 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0832 | [10 empty] | B1/C07_A1 | [16 empty] | 471 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1680 | #4MTR(1680) |  | BE1 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0833 | [9 empty] | no rule | B1/C07_A1 | [16 empty] | 472 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1680 | #4MTR(1680) |  | BE2 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0834 | [9 empty] | no rule | B1/C07_A1 | [16 empty] | 473 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C07 | 積E七 | 161 | 161kV | 1680 | #4MTR(1680) |  | TE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0835 | [10 empty] | B1/C07_A1 | [16 empty] | 474 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0664 | [9 empty] | aadz | B1/C01_A1 | [16 empty] | 475 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0665 | [10 empty] | B1/C01_A1 | [16 empty] | 476 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1510 | 和鑫二～積P3線(1510) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0666 | [9 empty] | aaba | B1/C01_A1 | [16 empty] | 477 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1510 | 和鑫二～積P3線(1510) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0667 | [10 empty] | B1/C01_A1 | [16 empty] | 478 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1520 | 南科和鑫二線(1520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0668 | [9 empty] | aaca | B1/C01_A1 | [16 empty] | 479 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1520 | 南科和鑫二線(1520) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0669 | [10 empty] | B1/C01_A1 | [16 empty] | 480 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1650 | #1MTR(1650) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0672 | [9 empty] | aafb | B1/C01_A1 | [16 empty] | 481 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1660 | #2MTR(1660) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0674 | [9 empty] | aagb | B1/C01_A1 | [16 empty] | 482 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1510 | 和鑫二～積P3線(1510) |  | 87UL1 |  |  | Status | 第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0689 | [10 empty] | B1/C01_A1 | [16 empty] | 483 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1520 | 南科和鑫二線(1520) |  | 87UL1 |  |  | Status | 第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0690 | [10 empty] | B1/C01_A1 | [16 empty] | 484 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 0 |  | StaDev | 所內設施 |  | OFA | 光纖通訊故障 | [13 empty] | 0705 | [10 empty] | B1/C01_A1 | [16 empty] | 485 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0706 | [10 empty] | B1/C01_A1 | [16 empty] | 486 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0707 | [10 empty] | B1/C01_A1 | [16 empty] | 487 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0708 | [10 empty] | B1/C01_A1 | [16 empty] | 488 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0709 | [10 empty] | B1/C01_A1 | [16 empty] | 489 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | 15B1E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0710 | [9 empty] | aaaz | B1/C01_A1 | [16 empty] | 490 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | 15B2E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0711 | [9 empty] | aaaz | B1/C01_A1 | [16 empty] | 491 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1510 | 和鑫二～積P3線(1510) |  | DS3 | 1513 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0712 | [10 empty] | B1/C01_A1 | [16 empty] | 492 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1510 | 和鑫二～積P3線(1510) |  | DS4 | 1514 |  | Status | DS4 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0713 | [10 empty] | B1/C01_A1 | [16 empty] | 493 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1510 | 和鑫二～積P3線(1510) |  | DS1 | 1511 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0714 | [10 empty] | B1/C01_A1 | [16 empty] | 494 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1510 | 和鑫二～積P3線(1510) |  | DS2 | 1512 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0715 | [10 empty] | B1/C01_A1 | [16 empty] | 495 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1510 | 和鑫二～積P3線(1510) |  | ES3_1 | 1513E1 | [13 empty] | 0716 | [10 empty] | B1/C01_A1 | [16 empty] | 496 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1510 | 和鑫二～積P3線(1510) |  | ES4 | 1514E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0717 | [10 empty] | B1/C01_A1 | [16 empty] | 497 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1510 | 和鑫二～積P3線(1510) |  | ES3_2 | 1513E2 | [13 empty] | 0718 | [10 empty] | B1/C01_A1 | [16 empty] | 498 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1510 | 和鑫二～積P3線(1510) |  | LE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0719 | [10 empty] | B1/C01_A1 | [16 empty] | 499 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1510 | 和鑫二～積P3線(1510) |  | BE1 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0720 | [9 empty] | no rule | B1/C01_A1 | [16 empty] | 500 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1510 | 和鑫二～積P3線(1510) |  | BE2 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0721 | [9 empty] | no rule | B1/C01_A1 | [16 empty] | 501 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1520 | 南科和鑫二線(1520) |  | DS3 | 1523 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0722 | [10 empty] | B1/C01_A1 | [16 empty] | 502 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1520 | 南科和鑫二線(1520) |  | DS4 | 1524 |  | Status | DS4 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0723 | [10 empty] | B1/C01_A1 | [16 empty] | 503 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1520 | 南科和鑫二線(1520) |  | DS1 | 1521 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0724 | [10 empty] | B1/C01_A1 | [16 empty] | 504 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1520 | 南科和鑫二線(1520) |  | DS2 | 1522 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0725 | [10 empty] | B1/C01_A1 | [16 empty] | 505 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1520 | 南科和鑫二線(1520) |  | ES3_1 | 1523E1 | [13 empty] | 0726 | [10 empty] | B1/C01_A1 | [16 empty] | 506 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1520 | 南科和鑫二線(1520) |  | ES4 | 1524E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0727 | [10 empty] | B1/C01_A1 | [16 empty] | 507 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1520 | 南科和鑫二線(1520) |  | ES3_2 | 1523E2 | [13 empty] | 0728 | [10 empty] | B1/C01_A1 | [16 empty] | 508 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1520 | 南科和鑫二線(1520) |  | LE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0729 | [10 empty] | B1/C01_A1 | [16 empty] | 509 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1520 | 南科和鑫二線(1520) |  | BE1 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0730 | [9 empty] | no rule | B1/C01_A1 | [16 empty] | 510 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1520 | 南科和鑫二線(1520) |  | BE2 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0731 | [9 empty] | no rule | B1/C01_A1 | [16 empty] | 511 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1650 | #1MTR(1650) |  | DS1 | 1651 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0736 | [10 empty] | B1/C01_A1 | [16 empty] | 512 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1650 | #1MTR(1650) |  | DS2 | 1652 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0737 | [10 empty] | B1/C01_A1 | [16 empty] | 513 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1650 | #1MTR(1650) |  | BE1 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0738 | [9 empty] | no rule | B1/C01_A1 | [16 empty] | 514 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1650 | #1MTR(1650) |  | BE2 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0739 | [9 empty] | no rule | B1/C01_A1 | [16 empty] | 515 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1650 | #1MTR(1650) |  | TE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0740 | [10 empty] | B1/C01_A1 | [16 empty] | 516 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1660 | #2MTR(1660) |  | DS1 | 1661 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0741 | [10 empty] | B1/C01_A1 | [16 empty] | 517 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1660 | #2MTR(1660) |  | DS2 | 1662 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0742 | [10 empty] | B1/C01_A1 | [16 empty] | 518 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1660 | #2MTR(1660) |  | BE1 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0743 | [9 empty] | no rule | B1/C01_A1 | [16 empty] | 519 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1660 | #2MTR(1660) |  | BE2 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0744 | [9 empty] | no rule | B1/C01_A1 | [16 empty] | 520 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1660 | #2MTR(1660) |  | TE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0745 | [10 empty] | B1/C01_A1 | [16 empty] | 521 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1510 | 和鑫二～積P3線(1510) |  | 87UL2 |  |  | Status | 第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [17 empty] | B1/C01_A1 | [16 empty] | 522 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1520 | 南科和鑫二線(1520) |  | 87UL2 |  |  | Status | 第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [17 empty] | B1/C01_A1 | [16 empty] | 523 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 1BUS | #1BUS |  | 87UL | (非取樣點) |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [17 empty] | B1/C01_A1 | [16 empty] | 524 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C01 | 和鑫二 | 161 | 161kV | 2BUS | #2BUS |  | 87UL | (非取樣點) |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [17 empty] | B1/C01_A1 | [16 empty] | 525 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
C01 | 和鑫二 | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/C01_A1 | [12 empty] | 和鑫二.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: C01/161/1BUS/V; OPRD2: C01/161/2BUS/V
C02 | 康寧CS | 0 |  | CalcPoint |  |  | Vbs3 | [9 empty] | B1/C02_A1 | [15 empty] | BEST_SOURCE_161KV_1 |  | v_best_161_1 | OPRD1: C02/161/1BUS/V
C03 | 積P3CS | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/C03_A1 | [12 empty] | 積P3CS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: C03/161/1BUS/V; OPRD2: C03/161/2BUS/V
C04 | 積十四 | 0 |  | CalcPoint |  |  | Vbs3 | [9 empty] | B1/C04_A1 | [15 empty] | BEST_SOURCE_161KV_1 |  | v_best_161_1 | OPRD1: C04/161/1BUS/V
C05 | 積六CS | 0 |  | CalcPoint |  |  | Vbs3 | [9 empty] | B1/C05_A1 | [15 empty] | BEST_SOURCE_161KV_1 |  | v_best_161_1 | OPRD1: C05/161/1BUS/V
C06 | 三福一 | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/C06_A1 | [12 empty] | 三福一.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: C06/161/1BUS/V; OPRD2: C06/161/2BUS/V
C07 | 積E七 | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/C07_A1 | [12 empty] | 積E七.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: C07/161/1BUS/V; OPRD2: C07/161/2BUS/V
C08 | 積E五 | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/C08_A1 | [12 empty] | 積E五.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: C08/161/1BUS/V; OPRD2: C08/161/2BUS/V
C09 | 積E六 | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/C09_A1 | [12 empty] | 積E六.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: C09/161/1BUS/V; OPRD2: C09/161/2BUS/V
C02 | 康寧CS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/C02_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: C02/0/CalcPoint/Vbs3; OPRD4: NULL; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
C07 | 積E七 | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/C07_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: C07/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
C05 | 積六CS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/C05_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: C05/0/CalcPoint/Vbs3; OPRD4: NULL; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
C09 | 積E六 | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/C09_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: C09/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
C03 | 積P3CS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/C03_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: C03/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
C01 | 和鑫二 | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/C01_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: C01/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
C08 | 積E五 | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/C08_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: C08/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
C06 | 三福一 | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/C06_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: C06/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
C04 | 積十四 | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/C04_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: C04/0/CalcPoint/Vbs3; OPRD4: NULL; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
C06 | 三福一 | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/C06_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: C06/0/CalcPoint/OPRN1; OPRD2: NULL; OPRD3: NULL
C09 | 積E六 | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/C09_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: C09/0/CalcPoint/OPRN1; OPRD2: NULL; OPRD3: NULL
C01 | 和鑫二 | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/C01_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: C01/0/CalcPoint/OPRN1; OPRD2: NULL; OPRD3: NULL
C05 | 積六CS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/C05_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: C05/0/CalcPoint/OPRN1; OPRD2: NULL; OPRD3: NULL
C04 | 積十四 | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/C04_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: C04/0/CalcPoint/OPRN1; OPRD2: NULL; OPRD3: NULL
C03 | 積P3CS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/C03_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: C03/0/CalcPoint/OPRN1; OPRD2: NULL; OPRD3: NULL
C07 | 積E七 | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/C07_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: C07/0/CalcPoint/OPRN1; OPRD2: NULL; OPRD3: NULL
C02 | 康寧CS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/C02_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: C02/0/CalcPoint/OPRN1; OPRD2: NULL; OPRD3: NULL
C08 | 積E五 | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/C08_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: C08/0/CalcPoint/OPRN1; OPRD2: NULL; OPRD3: NULL
C02 | 康寧CS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/C02_A1 | [15 empty] | STATION_FAULT_1 |  | com_alarm_4 | OPRD1: C02//1MTR/TRA; OPRD2: C02//1MTR/87A; OPRD3: C02//2MTR/TRA; OPRD4: C02//2MTR/87A
C03 | 積P3CS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/C03_A1 | [15 empty] | STATION_FAULT_1 |  | com_alarm_4 | OPRD1: C03//3MTR/TRA; OPRD2: C03//3MTR/87A; OPRD3: C03//4MTR/TRA; OPRD4: C03//4MTR/87A
C04 | 積十四 | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/C04_A1 | [15 empty] | STATION_FAULT_1 |  | com_alarm_4 | OPRD1: C04//1MTR/TRA; OPRD2: C04//1MTR/87A; OPRD3: C04//2MTR/TRA; OPRD4: C04//2MTR/87A
C05 | 積六CS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/C05_A1 | [15 empty] | STATION_FAULT_1 |  | com_alarm_4 | OPRD1: C05//1MTR/TRA; OPRD2: C05//1MTR/87A; OPRD3: C05//2MTR/TRA; OPRD4: C05//2MTR/87A
C07 | 積E七 | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/C07_A1 | [15 empty] | STATION_FAULT_1 |  | com_alarm_4 | OPRD1: C07//1MTR/87A; OPRD2: C07//2MTR/87A; OPRD3: C07//3MTR/87A; OPRD4: C07//4MTR/87A
C08 | 積E五 | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/C08_A1 | [15 empty] | STATION_FAULT_1 |  | com_alarm_8 | OPRD1: C08//1MTR/TRA; OPRD2: C08//1MTR/87A; OPRD3: C08//2MTR/TRA; OPRD4: C08//2MTR/87A; OPRD5: C08//3MTR/87A; OPRD6: C08//3MTR/TRA; OPRD7: C08//4MTR/TRA; OPRD8: C08//4MTR/87A
C02 | 康寧CS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/C02_A1 | [15 empty] | STATION_FAULT_1 |  | com_alarm_2 | OPRD1: C02//1MTR/TRF; OPRD2: C02//2MTR/TRF
C03 | 積P3CS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/C03_A1 | [15 empty] | STATION_FAULT_1 |  | com_alarm_2 | OPRD1: C03//3MTR/TRF; OPRD2: C03//4MTR/TRF
C04 | 積十四 | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/C04_A1 | [15 empty] | STATION_FAULT_1 |  | com_alarm_2 | OPRD1: C04//1MTR/TRF; OPRD2: C04//2MTR/TRF
C05 | 積六CS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/C05_A1 | [15 empty] | STATION_FAULT_1 |  | com_alarm_2 | OPRD1: C05//1MTR/TRF; OPRD2: C05//2MTR/TRF
C08 | 積E五 | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/C08_A1 | [15 empty] | STATION_FAULT_1 |  | com_alarm_4 | OPRD1: C08//1MTR/TRF; OPRD2: C08//2MTR/TRF; OPRD3: C08//3MTR/TRF; OPRD4: C08//4MTR/TRF

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
C99 | 南科CS | 161 | 161kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 積六CS.161KV#1BUS_KV | 161KV #1BUS KV | BUS |  |  |  |  | CDC | 2 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
C99 | 南科CS | 0 |  | 1500TIE | 1500TIE |  | I | [17 empty] | 1-88 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 積六CS.1500TIE_AMP | 1500TIE AMP | TIE |  |  |  |  | CDC | 3 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | [17 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
C99 | 南科CS | 0 |  | 1720 | 積十四積六線(1720) |  | I | [17 empty] | 1-86 | [5 empty] | A_-2500_2500(-2000_2000) |  | ADCS_S | [8 empty] | 積六CS.1720_AMP | 積十四積六線 AMP | OTHER |  |  |  |  | CDC | 4 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | [17 empty] | C25R1228 | 1105.000000 | 1105.000000 | 1228.000000 | 2500.000000 | 1.000000 | -1105.000000 | -1105.000000 | -1228.000000 | -2500.000000 | 1.000000 | 0.010000
C99 | 南科CS | 0 |  | 1730 | 南科積六線(1730) |  | I | [17 empty] | 1-87 | [5 empty] | A_-2500_2500(-2000_2000) |  | ADCS_S | [8 empty] | 積六CS.1730_AMP | 南科積六線 AMP | OTHER |  |  |  |  | CDC | 5 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | [17 empty] | C25R1228 | 1105.000000 | 1105.000000 | 1228.000000 | 2500.000000 | 1.000000 | -1105.000000 | -1105.000000 | -1228.000000 | -2500.000000 | 1.000000 | 0.010000
C99 | 南科CS | 0 |  | AI | AI90%參考點 |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 積六CS.AI_ADCH1 | AI90%參考點 ADCH1 | OTHER |  |  |  |  | CDC | 6 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
C99 | 南科CS | 0 |  | AI | AI10%參考點 |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 積六CS.AI_ADCL1 | AI10%參考點 ADCL1 | OTHER |  |  |  |  | CDC | 7 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
C99 | 南科CS | 161 | 161kV | 1BUS | #1BUS |  | V | [17 empty] | 1-92 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 積十四.161KV#1BUS_KV | 161KV #1BUS KV | BUS |  |  |  |  | CDC | 8 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | D_KEY | [16 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
C99 | 南科CS | 0 |  | 1500TIE | 1500TIE |  | I | [17 empty] | 1-98 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 積十四.1500TIE_AMP | 1500TIE AMP | TIE |  |  |  |  | CDC | 9 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | D_KEY | [16 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
C99 | 南科CS | 0 |  | 1520 | 積十四積六線(1520) |  | I | [17 empty] | 1-96 | [5 empty] | A_-2500_2500(-2000_2000) |  | ADCS_S | [8 empty] | 積十四.1520_AMP | 積十四積六線 AMP | OTHER |  |  |  |  | CDC | 10 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | [17 empty] | C25R1228 | 1105.000000 | 1105.000000 | 1228.000000 | 2500.000000 | 1.000000 | -1105.000000 | -1105.000000 | -1228.000000 | -2500.000000 | 1.000000 | 0.010000
C99 | 南科CS | 0 |  | 1540 | 康寧積十四線(1540) |  | I | [17 empty] | 1-97 | [5 empty] | A_-2500_2500(-2000_2000) |  | ADCS_S | [8 empty] | 積十四.1540_AMP | 康寧積十四線 AMP | OTHER |  |  |  |  | CDC | 11 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | [17 empty] | C25R1228 | 1105.000000 | 1105.000000 | 1228.000000 | 2500.000000 | 1.000000 | -1105.000000 | -1105.000000 | -1228.000000 | -2500.000000 | 1.000000 | 0.010000
C99 | 南科CS | 161 | 161kV | 1BUS | #1BUS |  | V | [17 empty] | 1-A2 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 康寧CS.161KV#1BUS_KV | 161KV #1BUS KV | BUS |  |  |  |  | CDC | 12 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | D_KEY | [16 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
C99 | 南科CS | 0 |  | 1520 | 南科康寧線(1520) |  | I | [17 empty] | 1-A6 | [5 empty] | A_-2500_2500(-2000_2000) |  | ADCS_S | [8 empty] | 康寧CS.1520_AMP | 南科康寧線 AMP | OTHER |  |  |  |  | CDC | 13 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | D_KEY | [16 empty] | C25R1228 | 1105.000000 | 1105.000000 | 1228.000000 | 2500.000000 | 1.000000 | -1105.000000 | -1105.000000 | -1228.000000 | -2500.000000 | 1.000000 | 0.010000
C99 | 南科CS | 0 |  | 1540 | 康寧積十四線(1540) |  | I | [17 empty] | 1-A8 | [5 empty] | A_-2500_2500(-2000_2000) |  | ADCS_S | [8 empty] | 康寧CS.1540_AMP | 康寧積十四線 AMP | OTHER |  |  |  |  | CDC | 14 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | D_KEY | [16 empty] | C25R1228 | 1105.000000 | 1105.000000 | 1228.000000 | 2500.000000 | 1.000000 | -1105.000000 | -1105.000000 | -1228.000000 | -2500.000000 | 1.000000 | 0.010000
C99 | 南科CS | 161 | 161kV | 1BUS | #1BUS |  | V | [17 empty] | 1-B2 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 積P3CS.161KV#1BUS_KV | 161KV #1BUS KV | BUS |  |  |  |  | CDC | 15 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | D_KEY | [16 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
C99 | 南科CS | 161 | 161kV | 2BUS | #2BUS |  | V | [17 empty] | 1-B3 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 積P3CS.161KV#2BUS_KV | 161KV #2BUS KV | BUS |  |  |  |  | CDC | 16 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
C99 | 南科CS | 0 |  | 1500TIE | 1500TIE |  | I | [17 empty] | 1-B8 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 積P3CS.1500TIE_AMP | 1500TIE AMP | TIE |  |  |  |  | CDC | 17 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | D_KEY | [16 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
C99 | 南科CS | 0 |  | 1710 | 和鑫二積P3線(1710) |  | I | [17 empty] | 1-B6 | [5 empty] | A_-2500_2500(-2000_2000) |  | ADCS_S | [8 empty] | 積P3CS.1710_AMP | 和鑫二積P3線 AMP | OTHER |  |  |  |  | CDC | 18 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | [17 empty] | C20R1930 | 1737.800049 | 1737.800049 | 1930.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
C99 | 南科CS | 0 |  | 1720 | 南科積P3線(1720) |  | I | [17 empty] | 1-B7 | [5 empty] | A_-2500_2500(-2000_2000) |  | ADCS_S | [8 empty] | 積P3CS.1720_AMP | 南科積P3線 AMP | OTHER |  |  |  |  | CDC | 19 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | D_KEY | [16 empty] | C20R1930 | 1737.800049 | 1737.800049 | 1930.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
C99 | 南科CS | 161 | 161kV | 1BUS | #1BUS |  | V | [17 empty] | 1-C2 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 積E五.161KV#1BUS_KV | 161KV #1BUS KV | BUS |  |  |  |  | CDC | 20 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | D_KEY | [16 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
C99 | 南科CS | 161 | 161kV | 2BUS | #2BUS |  | V | [17 empty] | 1-C3 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 積E五.161KV#2BUS_KV | 161KV #2BUS KV | BUS |  |  |  |  | CDC | 21 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | D_KEY | [16 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
C99 | 南科CS | 0 |  | 1500TIE | 1500TIE |  | I | [17 empty] | 1-C8 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 積E五.1500TIE_AMP | 1500TIE AMP | TIE |  |  |  |  | CDC | 22 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | D_KEY | [16 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
C99 | 南科CS | 0 |  | 1530 | 積E五積E七線(1530) |  | I | [17 empty] | 1-C6 | [5 empty] | A_-2500_2500(-2000_2000) |  | ADCS_S | [8 empty] | 積E五.1530_AMP | 積E五積E七線 AMP | OTHER |  |  |  |  | CDC | 23 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | [17 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
C99 | 南科CS | 0 |  | 1540 | 積E五積E六線(1540) |  | I | [17 empty] | 1-C7 | [5 empty] | A_-2500_2500(-2000_2000) |  | ADCS_S | [8 empty] | 積E五.1540_AMP | 積E五積E六線 AMP | OTHER |  |  |  |  | CDC | 24 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | D_KEY | [16 empty] | C20R1930 | 1737.800049 | 1737.800049 | 1930.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
C99 | 南科CS | 161 | 161kV | 1BUS | #1BUS |  | V | [17 empty] | 1-D2 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 積E六.161KV#1BUS_KV | 161KV #1BUS KV | BUS |  |  |  |  | CDC | 25 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | D_KEY | [16 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
C99 | 南科CS | 161 | 161kV | 2BUS | #2BUS |  | V | [17 empty] | 1-D3 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 積E六.161KV#2BUS_KV | 161KV #2BUS KV | BUS |  |  |  |  | CDC | 26 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | D_KEY | [16 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
C99 | 南科CS | 0 |  | 1530 | 積E五積E六線(1530) |  | I | [17 empty] | 1-D7 | [5 empty] | A_-2500_2500(-2000_2000) |  | ADCS_S | [8 empty] | 積E六.1530_AMP | 積E五積E六線 AMP | OTHER |  |  |  |  | CDC | 27 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | D_KEY | [16 empty] | C20R1930 | 1737.800049 | 1737.800049 | 1930.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
C99 | 南科CS | 0 |  | 1540 | 南科積E六線(1540) |  | I | [17 empty] | 1-D6 | [5 empty] | A_-2500_2500(-2000_2000) |  | ADCS_S | [8 empty] | 積E六.1540_AMP | 南科積E六線 AMP | OTHER |  |  |  |  | CDC | 28 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | D_KEY | [16 empty] | C20R1930 | 1737.800049 | 1737.800049 | 1930.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
C99 | 南科CS | 0 |  | 1500TIE | 1500TIE |  | I | [17 empty] | 1-D8 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 積E六.1500TIE_AMP | 1500TIE AMP | TIE |  |  |  |  | CDC | 29 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | D_KEY | [16 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
C99 | 南科CS | 161 | 161kV | 1BUS | #1BUS |  | V | [17 empty] | 1-E2 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 三福一.161KV#1BUS_KV | 161KV #1BUS KV | BUS |  |  |  |  | CDC | 30 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | D_KEY | [16 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
C99 | 南科CS | 161 | 161kV | 2BUS | #2BUS |  | V | [17 empty] | 1-E3 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 三福一.161KV#2BUS_KV | 161KV #2BUS KV | BUS |  |  |  |  | CDC | 31 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | D_KEY | [16 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
C99 | 南科CS | 0 |  | 1520 | 三福一積E七線(1520) |  | I | [17 empty] | 1-E7 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 三福一.1520_AMP | 三福一積E七線 AMP | OTHER |  |  |  |  | CDC | 32 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | D_KEY | [16 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
C99 | 南科CS | 0 |  | 1530 | 南科三福一線(1530) |  | I | [17 empty] | 1-E6 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 三福一.1530_AMP | 南科三福一線 AMP | OTHER |  |  |  |  | CDC | 33 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | D_KEY | [16 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
C99 | 南科CS | 161 | 161kV | 1BUS | #1BUS |  | V | [17 empty] | 2-82 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 積E七.161KV#1BUS_KV | 161KV #1BUS KV | BUS |  |  |  |  | CDC | 34 | GENERICAIPoint | CS001_L2 | CDC2_AI |  | AI | D_KEY | [16 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
C99 | 南科CS | 161 | 161kV | 2BUS | #2BUS |  | V | [17 empty] | 2-83 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 積E七.161KV#2BUS_KV | 161KV #2BUS KV | BUS |  |  |  |  | CDC | 35 | GENERICAIPoint | CS001_L2 | CDC2_AI |  | AI | D_KEY | [16 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
C99 | 南科CS | 0 |  | 1500TIE | 1500TIE |  | I | [17 empty] | 2-88 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 積E七.1500TIE_AMP | 1500TIE AMP | TIE |  |  |  |  | CDC | 36 | GENERICAIPoint | CS001_L2 | CDC2_AI |  | AI | D_KEY | [16 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
C99 | 南科CS | 0 |  | 1520 | 三福一積E七線(1520) |  | I | [17 empty] | 2-87 | [5 empty] | A_-2500_2500(-2000_2000) |  | ADCS_S | [8 empty] | 積E七.1520_AMP | 三福一積E七線 AMP | OTHER |  |  |  |  | CDC | 37 | GENERICAIPoint | CS001_L2 | CDC2_AI |  | AI | D_KEY | [16 empty] | C20R1930 | 1737.800049 | 1737.800049 | 1930.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
C99 | 南科CS | 0 |  | 1530 | 積E五積E七線(1530) |  | I | [17 empty] | 2-86 | [5 empty] | A_-2500_2500(-2000_2000) |  | ADCS_S | [8 empty] | 積E七.1530_AMP | 積E五積E七線 AMP | OTHER |  |  |  |  | CDC | 38 | GENERICAIPoint | CS001_L2 | CDC2_AI |  | AI | D_KEY | [16 empty] | C20R1930 | 1737.800049 | 1737.800049 | 1930.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
C99 | 南科CS | 161 | 161kV | 1BUS | #1BUS |  | V | [17 empty] | 1-F2 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 和鑫二.161KV#1BUS_KV | 161KV #1BUS KV | BUS |  |  |  |  | CDC | 39 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | D_KEY | [16 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
C99 | 南科CS | 161 | 161kV | 2BUS | #2BUS |  | V | [17 empty] | 1-F3 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 和鑫二.161KV#2BUS_KV | 161KV #2BUS KV | BUS |  |  |  |  | CDC | 40 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | D_KEY | [16 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
C99 | 南科CS | 0 |  | 1510 | 和鑫二積P3線(1510) |  | I | [17 empty] | 1-F6 | [5 empty] | A_-2500_2500(-2000_2000) |  | ADCS_S | [8 empty] | 和鑫二.1510_AMP | 和鑫二積P3線 AMP | OTHER |  |  |  |  | CDC | 41 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | [17 empty] | C20R1930 | 1737.800049 | 1737.800049 | 1930.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
C99 | 南科CS | 0 |  | 1520 | 南科和鑫二線(1520) |  | I | [17 empty] | 1-F7 | [5 empty] | A_-2500_2500(-2000_2000) |  | ADCS_S | [8 empty] | 和鑫二.1520_AMP | 南科和鑫二線 AMP | OTHER |  |  |  |  | CDC | 42 | GENERICAIPoint | CS001_L1 | CDC2_AI |  | AI | D_KEY | [16 empty] | C20R1930 | 1737.800049 | 1737.800049 | 1930.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
C99 | 南科CS | 0 |  | 1DTR | #1DTR |  | 87A | [17 empty] | 1-01-01 | [7 empty] | ADCS_S | [8 empty] | 積六CS.#1DTR_87A | #1DTR 87RY | OTHER |  |  |  |  | CDC | 43 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1DTR | #1DTR |  | 87UL | [17 empty] | 1-30-06 | [7 empty] | ADCS_S | [8 empty] | 積六CS.#1DTR_87UL | #1DTR 87RY U/L | OTHER |  |  |  |  | CDC | 44 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
C99 | 南科CS | 0 |  | 1DTR | #1DTR |  | TRA | [17 empty] | 1-30-05 | [7 empty] | ADCS_S | [8 empty] | 積六CS.#1DTR_TRA | #1DTR 重故障 | OTHER |  |  |  |  | CDC | 45 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1DTR | #1DTR |  | TRF | [17 empty] | 1-30-04 | [7 empty] | ADCS_S | [8 empty] | 積六CS.#1DTR_TRF | #1DTR 輕故障 | OTHER |  |  |  |  | CDC | 46 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 2DTR | #2DTR |  | 87A | [17 empty] | 1-01-03 | [7 empty] | ADCS_S | [8 empty] | 積六CS.#2DTR_87A | #2DTR 87RY | OTHER |  |  |  |  | CDC | 47 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 2DTR | #2DTR |  | 87UL | [17 empty] | 1-30-09 | [7 empty] | ADCS_S | [8 empty] | 積六CS.#2DTR_87UL | #2DTR 87RY U/L | OTHER |  |  |  |  | CDC | 48 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
C99 | 南科CS | 0 |  | 2DTR | #2DTR |  | TRA | [17 empty] | 1-30-08 | [7 empty] | ADCS_S | [8 empty] | 積六CS.#2DTR_TRA | #2DTR 重故障 | OTHER |  |  |  |  | CDC | 49 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 2DTR | #2DTR |  | TRF | [17 empty] | 1-30-07 | [7 empty] | ADCS_S | [8 empty] | 積六CS.#2DTR_TRF | #2DTR 輕故障 | OTHER |  |  |  |  | CDC | 50 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1500 | 1500 |  | 50A | [17 empty] | 1-00-01 | [7 empty] | ADCS_S | [8 empty] | 積六CS.1500_50A | 161KV TIE(1500) 50RY | OTHER |  |  |  |  | CDC | 51 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1500 | 1500 |  | 50UL | [17 empty] | 1-30-00 | [7 empty] | ADCS_S | [8 empty] | 積六CS.1500_50UL | 161KV TIE(1500) 50RY UL | OTHER |  |  |  |  | CDC | 52 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [17 empty] | 1-00-00 | [7 empty] | ADCS_S | [8 empty] | 積六CS.1500_CB | 1500(TIE) CB | OTHER |  |  |  |  | CDC | 53 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [16 empty] | 1-31-08 | [7 empty] | ADCS_S | [8 empty] | 積六CS.1501_DS | 1501(TIE) DS | OTHER |  |  |  |  | CDC | 54 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 0 |  | 15B1E | 15B1E |  | BE1 | 15B1E | [16 empty] | 1-31-10 | [7 empty] | ADCS_S | [8 empty] | 積六CS.15B1E_ES | 15B1E ES | OTHER |  |  |  |  | CDC | 55 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 0 |  | 15B2E | 15B2E |  | BE2 | 15B2E | [16 empty] | 1-31-11 | [7 empty] | ADCS_S | [8 empty] | 積六CS.15B2E_ES | 15B2E ES | OTHER |  |  |  |  | CDC | 56 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | BE0 | 1650BE | [16 empty] | 1-32-14 | [7 empty] | ADCS_S | [8 empty] | 積六CS.1650BE_ES | 1650BE(#1DTR) ES | OTHER |  |  |  |  | CDC | 57 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | TE0 | 1650TE | [16 empty] | 1-32-15 | [7 empty] | ADCS_S | [8 empty] | 積六CS.1650TE_ES | 1650TE(#1DTR) ES | OTHER |  |  |  |  | CDC | 58 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | CB | [17 empty] | 1-01-00 | [7 empty] | ADCS_S | [8 empty] | 積六CS.1650_CB | 1650(#1DTR) CB | OTHER |  |  |  |  | CDC | 59 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | DS1 | 1651 | [16 empty] | 1-32-13 | [7 empty] | ADCS_S | [8 empty] | 積六CS.1651_DS | 1651(#1DTR) DS | OTHER |  |  |  |  | CDC | 60 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | BE0 | 1660BE | [16 empty] | 1-33-01 | [7 empty] | ADCS_S | [8 empty] | 積六CS.1660BE_ES | 1660BE(#2DTR) ES | OTHER |  |  |  |  | CDC | 61 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | TE0 | 1660TE | [16 empty] | 1-33-02 | [7 empty] | ADCS_S | [8 empty] | 積六CS.1660TE_ES | 1660TE(#2DTR) ES | OTHER |  |  |  |  | CDC | 62 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | CB | [17 empty] | 1-01-02 | [7 empty] | ADCS_S | [8 empty] | 積六CS.1660_CB | 1660(#2DTR) CB | OTHER |  |  |  |  | CDC | 63 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | DS1 | 1661 | [16 empty] | 1-33-00 | [7 empty] | ADCS_S | [8 empty] | 積六CS.1661_DS | 1661(#2DTR) DS | OTHER |  |  |  |  | CDC | 64 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1720 | 積十四積六線(1720) |  | BE0 | 1720BE | [16 empty] | 1-32-00 | [7 empty] | ADCS_S | [8 empty] | 積六CS.1720BE_ES | 1720BE(積十四積六線) ES | OTHER |  |  |  |  | CDC | 65 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1720 | 積十四積六線(1720) |  | LE0 | 1720LE | [16 empty] | 1-31-15 | [7 empty] | ADCS_S | [8 empty] | 積六CS.1720LE_ES | 1720LE(積十四積六線) ES | OTHER |  |  |  |  | CDC | 66 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1720 | 積十四積六線(1720) |  | CB | [17 empty] | 1-00-02 | [7 empty] | ADCS_S | [8 empty] | 積六CS.1720_CB | 1720(積十四積六線) CB | OTHER |  |  |  |  | CDC | 67 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1720 | 積十四積六線(1720) |  | DS1 | 1721 | [16 empty] | 1-31-12 | [7 empty] | ADCS_S | [8 empty] | 積六CS.1721_DS | 1721(積十四積六線) DS | OTHER |  |  |  |  | CDC | 68 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1720 | 積十四積六線(1720) |  | E2 | 1722E | [16 empty] | 1-31-14 | [7 empty] | ADCS_S | [8 empty] | 積六CS.1722E_ES | 1722E(積十四積六線) ES | OTHER |  |  |  |  | CDC | 69 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1720 | 積十四積六線(1720) |  | DS2 | 1722 | [16 empty] | 1-31-13 | [7 empty] | ADCS_S | [8 empty] | 積六CS.1722_DS | 1722(積十四積六線) DS | OTHER |  |  |  |  | CDC | 70 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1730 | 南科積六線(1730) |  | BE0 | 1730BE | [16 empty] | 1-32-05 | [7 empty] | ADCS_S | [8 empty] | 積六CS.1730BE_ES | 1730BE(南科積六線) ES | OTHER |  |  |  |  | CDC | 71 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1730 | 南科積六線(1730) |  | LE0 | 1730LE | [16 empty] | 1-32-04 | [7 empty] | ADCS_S | [8 empty] | 積六CS.1730LE_ES | 1730LE(南科積六線) ES | OTHER |  |  |  |  | CDC | 72 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1730 | 南科積六線(1730) |  | CB | [17 empty] | 1-00-04 | [7 empty] | ADCS_S | [8 empty] | 積六CS.1730_CB | 1730(南科積六線) CB | OTHER |  |  |  |  | CDC | 73 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1730 | 南科積六線(1730) |  | DS1 | 1731 | [16 empty] | 1-32-01 | [7 empty] | ADCS_S | [8 empty] | 積六CS.1731_DS | 1731(南科積六線) DS | OTHER |  |  |  |  | CDC | 74 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1730 | 南科積六線(1730) |  | E2 | 1732E | [16 empty] | 1-32-03 | [7 empty] | ADCS_S | [8 empty] | 積六CS.1732E_ES | 1732E(南科積六線) ES | OTHER |  |  |  |  | CDC | 75 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1730 | 南科積六線(1730) |  | DS2 | 1732 | [16 empty] | 1-32-02 | [7 empty] | ADCS_S | [8 empty] | 積六CS.1732_DS | 1732(南科積六線) DS | OTHER |  |  |  |  | CDC | 76 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1730 | 南科積六線(1730) |  | E3 | 1733E | [16 empty] | 1-32-07 | [7 empty] | ADCS_S | [8 empty] | 積六CS.1733E_ES | 1733E(備用線) ES | OTHER |  |  |  |  | CDC | 77 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1730 | 南科積六線(1730) |  | DS3 | 1733 | [16 empty] | 1-32-06 | [7 empty] | ADCS_S | [8 empty] | 積六CS.1733_DS | 1733(備用線) DS | OTHER |  |  |  |  | CDC | 78 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 0 |  | 1DTR | #1DTR |  | 87A | [17 empty] | 1-04-01 | [7 empty] | ADCS_S | [8 empty] | 積十四.#1DTR_87A | #1DTR 87RY | OTHER |  |  |  |  | CDC | 79 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1DTR | #1DTR |  | 87UL | [17 empty] | 1-34-14 | [7 empty] | ADCS_S | [8 empty] | 積十四.#1DTR_87UL | #1DTR 87RY U/L | OTHER |  |  |  |  | CDC | 80 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | USE/LOCK | USE
C99 | 南科CS | 0 |  | 1DTR | #1DTR |  | TRA | [17 empty] | 1-34-13 | [7 empty] | ADCS_S | [8 empty] | 積十四.#1DTR_TRA | #1DTR 重故障 | OTHER |  |  |  |  | CDC | 81 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1DTR | #1DTR |  | TRF | [17 empty] | 1-34-12 | [7 empty] | ADCS_S | [8 empty] | 積十四.#1DTR_TRF | #1DTR 輕故障 | OTHER |  |  |  |  | CDC | 82 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 2DTR | #2DTR |  | 87A | [17 empty] | 1-04-03 | [7 empty] | ADCS_S | [8 empty] | 積十四.#2DTR_87A | #2DTR 87RY | OTHER |  |  |  |  | CDC | 83 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 2DTR | #2DTR |  | 87UL | [17 empty] | 1-35-01 | [7 empty] | ADCS_S | [8 empty] | 積十四.#2DTR_87UL | #2DTR 87RY U/L | OTHER |  |  |  |  | CDC | 84 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | USE/LOCK | USE
C99 | 南科CS | 0 |  | 2DTR | #2DTR |  | TRA | [17 empty] | 1-35-00 | [7 empty] | ADCS_S | [8 empty] | 積十四.#2DTR_TRA | #2DTR 重故障 | OTHER |  |  |  |  | CDC | 85 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 2DTR | #2DTR |  | TRF | [17 empty] | 1-34-15 | [7 empty] | ADCS_S | [8 empty] | 積十四.#2DTR_TRF | #2DTR 輕故障 | OTHER |  |  |  |  | CDC | 86 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1500 | TIE(1500) |  | 50A | [17 empty] | 1-03-01 | [7 empty] | ADCS_S | [8 empty] | 積十四.1500_50A | 161KV TIE(1500) 50RY | OTHER |  |  |  |  | CDC | 87 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1500 | TIE(1500) |  | 50UL | [17 empty] | 1-34-08 | [7 empty] | ADCS_S | [8 empty] | 積十四.1500_50UL | 161KV TIE(1500) 50RY UL | OTHER |  |  |  |  | CDC | 88 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | USE/LOCK | USE
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [17 empty] | 1-03-00 | [7 empty] | ADCS_S | [8 empty] | 積十四.1500_CB | 1500(TIE) CB | OTHER |  |  |  |  | CDC | 89 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [16 empty] | 1-36-00 | [7 empty] | ADCS_S | [8 empty] | 積十四.1501_DS | 1501(TIE) DS | OTHER |  |  |  |  | CDC | 90 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | BE0 | 1520BE | [16 empty] | 1-36-08 | [7 empty] | ADCS_S | [8 empty] | 積十四.1520BE_ES | 1520BE(積十四積六線) ES | OTHER |  |  |  |  | CDC | 91 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | LE0 | 1520LE | [16 empty] | 1-36-07 | [7 empty] | ADCS_S | [8 empty] | 積十四.1520LE_ES | 1520LE(積十四積六線) ES | OTHER |  |  |  |  | CDC | 92 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | CB | [17 empty] | 1-03-02 | [7 empty] | ADCS_S | [8 empty] | 積十四.1520_CB | 1520(積十四積六線) CB | OTHER |  |  |  |  | CDC | 93 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | DS1 | 1521 | [16 empty] | 1-36-04 | [7 empty] | ADCS_S | [8 empty] | 積十四.1521_DS | 1521(積十四積六線) DS | OTHER |  |  |  |  | CDC | 94 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | E2 | 1522E | [16 empty] | 1-36-06 | [7 empty] | ADCS_S | [8 empty] | 積十四.1522E_ES | 1522E(積十四積六線) ES | OTHER |  |  |  |  | CDC | 95 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | DS2 | 1522 | [16 empty] | 1-36-05 | [7 empty] | ADCS_S | [8 empty] | 積十四.1522_DS | 1522(積十四積六線) DS | OTHER |  |  |  |  | CDC | 96 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | E3 | 1523E | [16 empty] | 1-36-10 | [7 empty] | ADCS_S | [8 empty] | 積十四.1523E_ES | 1523E(備用線) ES | OTHER |  |  |  |  | CDC | 97 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | DS3 | 1523 | [16 empty] | 1-36-09 | [7 empty] | ADCS_S | [8 empty] | 積十四.1523_DS | 1523(備用線) DS | OTHER |  |  |  |  | CDC | 98 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1540 | 康寧積十四線(1540) |  | BE0 | 1540BE | [16 empty] | 1-36-15 | [7 empty] | ADCS_S | [8 empty] | 積十四.1540BE_ES | 1540BE(康寧積十四線) ES | OTHER |  |  |  |  | CDC | 99 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1540 | 康寧積十四線(1540) |  | LE0 | 1540LE | [16 empty] | 1-36-14 | [7 empty] | ADCS_S | [8 empty] | 積十四.1540LE_ES | 1540LE(康寧積十四線) ES | OTHER |  |  |  |  | CDC | 100 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 0 |  | 1540 | 康寧積十四線(1540) |  | 87A | [17 empty] | 1-03-05 | [7 empty] | ADCS_S | [8 empty] | 積十四.1540_87A | 1540(康寧積十四線) 87RY | OTHER |  |  |  |  | CDC | 101 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1540 | 康寧積十四線(1540) |  | 87UL | [17 empty] | 1-34-10 | [7 empty] | ADCS_S | [8 empty] | 積十四.1540_87UL | 1540(康寧積十四線) 87RY U/L | OTHER |  |  |  |  | CDC | 102 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
C99 | 南科CS | 161 | 161kV | 1540 | 康寧積十四線(1540) |  | CB | [17 empty] | 1-03-04 | [7 empty] | ADCS_S | [8 empty] | 積十四.1540_CB | 1540(康寧積十四線) CB | OTHER |  |  |  |  | CDC | 103 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1540 | 康寧積十四線(1540) |  | DS1 | 1541 | [16 empty] | 1-36-11 | [7 empty] | ADCS_S | [8 empty] | 積十四.1541_DS | 1541(康寧積十四線) DS | OTHER |  |  |  |  | CDC | 104 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1540 | 康寧積十四線(1540) |  | E2 | 1542E | [16 empty] | 1-36-13 | [7 empty] | ADCS_S | [8 empty] | 積十四.1542E_ES | 1542E(康寧積十四線) ES | OTHER |  |  |  |  | CDC | 105 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1540 | 康寧積十四線(1540) |  | DS2 | 1542 | [16 empty] | 1-36-12 | [7 empty] | ADCS_S | [8 empty] | 積十四.1542_DS | 1542(康寧積十四線) DS | OTHER |  |  |  |  | CDC | 106 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 0 |  | 15B1E | 15B1E |  | BE1 | 15B1E | [16 empty] | 1-36-02 | [7 empty] | ADCS_S | [8 empty] | 積十四.15B1E_ES | 15B1E ES | OTHER |  |  |  |  | CDC | 107 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 0 |  | 15B2E | 15B2E |  | BE2 | 15B2E | [16 empty] | 1-36-03 | [7 empty] | ADCS_S | [8 empty] | 積十四.15B2E_ES | 15B2E ES | OTHER |  |  |  |  | CDC | 108 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | BE0 | 1650BE | [16 empty] | 1-37-06 | [7 empty] | ADCS_S | [8 empty] | 積十四.1650BE_ES | 1650BE(#1DTR) ES | OTHER |  |  |  |  | CDC | 109 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | TE0 | 1650TE | [16 empty] | 1-37-07 | [7 empty] | ADCS_S | [8 empty] | 積十四.1650TE_ES | 1650TE(#1DTR) ES | OTHER |  |  |  |  | CDC | 110 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | CB | [17 empty] | 1-04-00 | [7 empty] | ADCS_S | [8 empty] | 積十四.1650_CB | 1650(#1DTR) CB | OTHER |  |  |  |  | CDC | 111 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | DS1 | 1651 | [16 empty] | 1-37-05 | [7 empty] | ADCS_S | [8 empty] | 積十四.1651_DS | 1651(#1DTR) DS | OTHER |  |  |  |  | CDC | 112 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | BE0 | 1660BE | [16 empty] | 1-37-09 | [7 empty] | ADCS_S | [8 empty] | 積十四.1660BE_ES | 1660BE(#2DTR) ES | OTHER |  |  |  |  | CDC | 113 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | TE0 | 1660TE | [16 empty] | 1-37-10 | [7 empty] | ADCS_S | [8 empty] | 積十四.1660TE_ES | 1660TE(#2DTR) ES | OTHER |  |  |  |  | CDC | 114 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | CB | [17 empty] | 1-04-02 | [7 empty] | ADCS_S | [8 empty] | 積十四.1660_CB | 1660(#2DTR) CB | OTHER |  |  |  |  | CDC | 115 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | DS1 | 1661 | [16 empty] | 1-37-08 | [7 empty] | ADCS_S | [8 empty] | 積十四.1661_DS | 1661(#2DTR) DS | OTHER |  |  |  |  | CDC | 116 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 0 |  |  |  |  | OFA通訊故障 | [17 empty] | 1-35-15 | [7 empty] | ADCS_S | [8 empty] | 積十四.OFA通訊故障 | OFA光纖通訊故障警報 | OTHER |  |  |  |  | CDC | 117 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | UPS | UPS |  | AC_Fault | [17 empty] | 1-37-03 | [7 empty] | ADCS_S | [8 empty] | 積十四.UPS_AC故障 | UPS AC故障警報 | OTHER |  |  |  |  | CDC | 118 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | UPS | UPS |  | DC故障 | [17 empty] | 1-37-04 | [7 empty] | ADCS_S | [8 empty] | 積十四.UPS_DC故障 | UPS DC故障警報 | OTHER |  |  |  |  | CDC | 119 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  |  |  |  | 設備內部故障 | [17 empty] | 1-34-11 | [7 empty] | ADCS_S | [8 empty] | 積十四.設備內部故障 | 資料收集設備內部異常故障警報 | OTHER |  |  |  |  | CDC | 120 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  |  |  |  | 設備通訊故障 | [17 empty] | 1-35-14 | [7 empty] | ADCS_S | [8 empty] | 積十四.設備通訊故障 | 資料收集設備通訊故障警報 | OTHER |  |  |  |  | CDC | 121 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1DTR | #1DTR |  | 87A | [17 empty] | 1-07-01 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.#1DTR_87A | #1DTR 87RY | OTHER |  |  |  |  | CDC | 122 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1DTR | #1DTR |  | 87UL | [17 empty] | 1-39-06 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.#1DTR_87UL | #1DTR 87RY U/L | OTHER |  |  |  |  | CDC | 123 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | USE/LOCK | USE
C99 | 南科CS | 0 |  | 1DTR | #1DTR |  | TRA | [17 empty] | 1-39-05 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.#1DTR_TRA | #1DTR 重故障 | OTHER |  |  |  |  | CDC | 124 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1DTR | #1DTR |  | TRF | [17 empty] | 1-39-04 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.#1DTR_TRF | #1DTR 輕故障 | OTHER |  |  |  |  | CDC | 125 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 2DTR | #2DTR |  | 87A | [17 empty] | 1-07-03 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.#2DTR_87A | #2DTR 87RY | OTHER |  |  |  |  | CDC | 126 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 2DTR | #2DTR |  | 87UL | [17 empty] | 1-39-09 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.#2DTR_87UL | #2DTR 87RY U/L | OTHER |  |  |  |  | CDC | 127 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | USE/LOCK | USE
C99 | 南科CS | 0 |  | 2DTR | #2DTR |  | TRA | [17 empty] | 1-39-08 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.#2DTR_TRA | #2DTR 重故障 | OTHER |  |  |  |  | CDC | 128 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 2DTR | #2DTR |  | TRF | [17 empty] | 1-39-07 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.#2DTR_TRF | #2DTR 輕故障 | OTHER |  |  |  |  | CDC | 129 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1500 | TIE(1500) |  | 50A | [17 empty] | 1-06-01 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.1500_50A | 161KV TIE(1500) 50RY | OTHER |  |  |  |  | CDC | 130 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1500 | TIE(1500) |  | 50UL | [17 empty] | 1-39-00 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.1500_50UL | 161KV TIE(1500) 50RY UL | OTHER |  |  |  |  | CDC | 131 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | USE/LOCK | USE
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [17 empty] | 1-06-00 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.1500_CB | 1500(TIE) CB | OTHER |  |  |  |  | CDC | 132 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [16 empty] | 1-3A-08 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.1501_DS | 1501(TIE) DS | OTHER |  |  |  |  | CDC | 133 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | BE0 | 1520BE | [16 empty] | 1-3B-00 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.1520BE_ES | 1520BE(南科康寧線) ES | OTHER |  |  |  |  | CDC | 134 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | LE0 | 1520LE | [16 empty] | 1-3A-15 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.1520LE_ES | 1520LE(南科康寧線) ES | OTHER |  |  |  |  | CDC | 135 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 0 |  | 1520 | 積十四積六線(1520) |  | 87A | [17 empty] | 1-06-03 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.1520_87A | 1520(南科康寧線) 87RY | OTHER |  |  |  |  | CDC | 136 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1520 | 積十四積六線(1520) |  | 87UL | [17 empty] | 1-39-01 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.1520_87UL | 1520(南科康寧線) 87RY U/L | OTHER |  |  |  |  | CDC | 137 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | CB | [17 empty] | 1-06-02 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.1520_CB | 1520(南科康寧線) CB | OTHER |  |  |  |  | CDC | 138 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | DS1 | 1521 | [16 empty] | 1-3A-12 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.1521_DS | 1521(南科康寧線) DS | OTHER |  |  |  |  | CDC | 139 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | E2 | 1522E | [16 empty] | 1-3A-14 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.1522E_ES | 1522E(南科康寧線) ES | OTHER |  |  |  |  | CDC | 140 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | DS2 | 1522 | [16 empty] | 1-3A-13 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.1522_DS | 1522(南科康寧線) DS | OTHER |  |  |  |  | CDC | 141 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1540 | 康寧積十四線(1540) |  | BE0 | 1540BE | [16 empty] | 1-3B-05 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.1540BE_ES | 1540BE(康寧積十四線) ES | OTHER |  |  |  |  | CDC | 142 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1540 | 康寧積十四線(1540) |  | LE0 | 1540LE | [16 empty] | 1-3B-04 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.1540LE_ES | 1540LE(康寧積十四線) ES | OTHER |  |  |  |  | CDC | 143 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 0 |  | 1540 | 康寧積十四線(1540) |  | 87A | [17 empty] | 1-06-05 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.1540_87A | 1540(康寧積十四線) 87RY | OTHER |  |  |  |  | CDC | 144 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1540 | 康寧積十四線(1540) |  | 87UL | [17 empty] | 1-39-02 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.1540_87UL | 1540(康寧積十四線) 87RY U/L | OTHER |  |  |  |  | CDC | 145 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | USE/LOCK | USE
C99 | 南科CS | 161 | 161kV | 1540 | 康寧積十四線(1540) |  | CB | [17 empty] | 1-06-04 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.1540_CB | 1540(康寧積十四線) CB | OTHER |  |  |  |  | CDC | 146 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1540 | 康寧積十四線(1540) |  | DS1 | 1541 | [16 empty] | 1-3B-01 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.1541_DS | 1541(康寧積十四線) DS | OTHER |  |  |  |  | CDC | 147 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1540 | 康寧積十四線(1540) |  | E2 | 1542E | [16 empty] | 1-3B-03 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.1542E_ES | 1542E(康寧積十四線) ES | OTHER |  |  |  |  | CDC | 148 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1540 | 康寧積十四線(1540) |  | DS2 | 1542 | [16 empty] | 1-3B-02 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.1542_DS | 1542(康寧積十四線) DS | OTHER |  |  |  |  | CDC | 149 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 0 |  | 15B1E | 15B1E |  | BE1 | 15B1E | [16 empty] | 1-3A-10 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.15B1E_ES | 15B1E ES | OTHER |  |  |  |  | CDC | 150 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 0 |  | 15B2E | 15B2E |  | BE2 | 15B2E | [16 empty] | 1-3A-11 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.15B2E_ES | 15B2E ES | OTHER |  |  |  |  | CDC | 151 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | BE0 | 1650BE | [16 empty] | 1-3B-12 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.1650BE_ES | 1650BE(#1DTR) ES | OTHER |  |  |  |  | CDC | 152 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | TE0 | 1650TE | [16 empty] | 1-3B-13 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.1650TE_ES | 1650TE(#1DTR) ES | OTHER |  |  |  |  | CDC | 153 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | CB | [17 empty] | 1-07-00 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.1650_CB | 1650(#1DTR) CB | OTHER |  |  |  |  | CDC | 154 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | DS1 | 1651 | [16 empty] | 1-3B-11 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.1651_DS | 1651(#1DTR) DS | OTHER |  |  |  |  | CDC | 155 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | BE0 | 1660BE | [16 empty] | 1-3B-15 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.1660BE_ES | 1660BE(#2DTR) ES | OTHER |  |  |  |  | CDC | 156 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | TE0 | 1660TE | [16 empty] | 1-3C-00 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.1660TE_ES | 1660TE(#2DTR) ES | OTHER |  |  |  |  | CDC | 157 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | CB | [17 empty] | 1-07-02 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.1660_CB | 1660(#2DTR) CB | OTHER |  |  |  |  | CDC | 158 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | DS1 | 1661 | [16 empty] | 1-3B-14 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.1661_DS | 1661(#2DTR) DS | OTHER |  |  |  |  | CDC | 159 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 0 |  |  |  |  | OFA通訊故障 | [17 empty] | 1-3A-07 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.OFA通訊故障 | OFA光纖通訊故障警報 | OTHER |  |  |  |  | CDC | 160 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | UPS | UPS |  | AC_Fault | [17 empty] | 1-3B-09 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.UPS_AC故障 | UPS AC故障警報 | OTHER |  |  |  |  | CDC | 161 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | UPS | UPS |  | DC故障 | [17 empty] | 1-3B-10 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.UPS_DC故障 | UPS DC故障警報 | OTHER |  |  |  |  | CDC | 162 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  |  |  |  | 設備內部故障 | [17 empty] | 1-39-03 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.設備內部故障 | 資料收集設備內部異常故障警報 | OTHER |  |  |  |  | CDC | 163 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  |  |  |  | 設備通訊故障 | [17 empty] | 1-3A-06 | [7 empty] | ADCS_S | [8 empty] | 康寧CS.設備通訊故障 | 資料收集設備通訊故障警報 | OTHER |  |  |  |  | CDC | 164 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  |  |  |  | OFA通訊故障 | [17 empty] | 1-31-07 | [7 empty] | ADCS_S | [8 empty] | 積六CS.OFA通訊故障 | OFA光纖通訊故障警報 | OTHER |  |  |  |  | CDC | 165 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | UPS | UPS |  | AC_Fault | [17 empty] | 1-32-11 | [7 empty] | ADCS_S | [8 empty] | 積六CS.UPS_AC故障 | UPS AC故障警報 | OTHER |  |  |  |  | CDC | 166 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | UPS | UPS |  | DC故障 | [17 empty] | 1-32-12 | [7 empty] | ADCS_S | [8 empty] | 積六CS.UPS_DC故障 | UPS DC故障警報 | OTHER |  |  |  |  | CDC | 167 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  |  |  |  | 設備內部故障 | [17 empty] | 1-30-03 | [7 empty] | ADCS_S | [8 empty] | 積六CS.設備內部故障 | 資料收集設備內部異常故障警報 | OTHER |  |  |  |  | CDC | 168 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  |  |  |  | 設備通訊故障 | [17 empty] | 1-31-06 | [7 empty] | ADCS_S | [8 empty] | 積六CS.設備通訊故障 | 資料收集設備通訊故障警報 | OTHER |  |  |  |  | CDC | 169 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [17 empty] | 1-09-00 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1500_CB | 1500(TIE) CB | OTHER |  |  |  |  | CDC | 170 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [16 empty] | 1-3F-02 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1501E_ES | 1501E ES | OTHER |  |  |  |  | CDC | 171 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [16 empty] | 1-3F-00 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1501_DS | 1501(TIE) DS | OTHER |  |  |  |  | CDC | 172 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [16 empty] | 1-3F-03 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1502E_ES | 1502E ES | OTHER |  |  |  |  | CDC | 173 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [16 empty] | 1-3F-01 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1502_DS | 1502(TIE) DS | OTHER |  |  |  |  | CDC | 174 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 0 |  | 15B1E | 15B1E |  | BE1 | 15B1E | [16 empty] | 1-3F-04 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.15B1E_ES | 15B1E ES | OTHER |  |  |  |  | CDC | 175 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 0 |  | 15B2E | 15B2E |  | BE2 | 15B2E | [16 empty] | 1-3F-05 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.15B2E_ES | 15B2E ES | OTHER |  |  |  |  | CDC | 176 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1710 | 和鑫二積P3線(1710) |  | BE0 | 1710BE | [16 empty] | 1-3F-12 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1710BE_ES | 1710BE(和鑫二積P3線) ES | OTHER |  |  |  |  | CDC | 177 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1710 | 和鑫二積P3線(1710) |  | LE0 | 1710LE | [16 empty] | 1-3F-11 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1710LE_ES | 1710LE(和鑫二積P3線) ES | OTHER |  |  |  |  | CDC | 178 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1710 | 和鑫二積P3線(1710) |  | CB | [17 empty] | 1-09-02 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1710_CB | 1710(和鑫二積P3線) CB | OTHER |  |  |  |  | CDC | 179 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1710 | 和鑫二積P3線(1710) |  | DS1 | 1711 | [16 empty] | 1-3F-06 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1711_DS | 1711(和鑫二積P3線) DS | OTHER |  |  |  |  | CDC | 180 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1710 | 和鑫二積P3線(1710) |  | DS2 | 1712 | [16 empty] | 1-3F-07 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1712_DS | 1712(和鑫二積P3線) DS | OTHER |  |  |  |  | CDC | 181 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1710 | 和鑫二積P3線(1710) |  | E3 | 1713E | [16 empty] | 1-3F-10 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1713E_ES | 1713E(和鑫二積P3線) ES | OTHER |  |  |  |  | CDC | 182 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1710 | 和鑫二積P3線(1710) |  | DS3 | 1713 | [16 empty] | 1-3F-09 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1713_DS | 1713(和鑫二積P3線) DS | OTHER |  |  |  |  | CDC | 183 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1720 | 積十四積六線(1720) |  | BE0 | 1720BE | [16 empty] | 2-30-03 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1720BE_ES | 1720BE(南科積P3線) ES | OTHER |  |  |  |  | CDC | 184 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1720 | 積十四積六線(1720) |  | LE0 | 1720LE | [16 empty] | 2-30-02 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1720LE_ES | 1720LE(南科積P3線) ES | OTHER |  |  |  |  | CDC | 185 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1720 | 積十四積六線(1720) |  | CB | [17 empty] | 1-09-04 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1720_CB | 1720(南科積P3線) CB | OTHER |  |  |  |  | CDC | 186 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1720 | 積十四積六線(1720) |  | DS1 | 1721 | [16 empty] | 1-3F-13 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1721_DS | 1721(南科積P3線) DS | OTHER |  |  |  |  | CDC | 187 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1720 | 積十四積六線(1720) |  | DS2 | 1722 | [16 empty] | 1-3F-14 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1722_DS | 1722(南科積P3線) DS | OTHER |  |  |  |  | CDC | 188 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1720 | 積十四積六線(1720) |  | E3 | 1723E | [16 empty] | 2-30-01 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1723E_ES | 1723E(南科積P3線) ES | OTHER |  |  |  |  | CDC | 189 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1720 | 積十四積六線(1720) |  | DS3 | 1723 | [16 empty] | 2-30-00 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1723_DS | 1723(南科積P3線) DS | OTHER |  |  |  |  | CDC | 190 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 0 |  |  |  |  | OFA通訊故障 | [17 empty] | 1-3E-15 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.OFA通訊故障 | OFA光纖通訊故障警報 | OTHER |  |  |  |  | CDC | 191 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  |  |  |  | 設備通訊故障 | [17 empty] | 1-3E-14 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.設備通訊故障 | 資料收集設備通訊故障警報 | OTHER |  |  |  |  | CDC | 192 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | BE0 | 1650BE | [16 empty] | 2-30-10 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1650BE_ES | 1650BE(#1DTR) ES | OTHER |  |  |  |  | CDC | 193 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | TE0 | 1650TE | [16 empty] | 2-30-11 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1650TE_ES | 1650TE(#1DTR) ES | OTHER |  |  |  |  | CDC | 194 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | CB | [17 empty] | 1-0A-00 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1650_CB | 1650(#1DTR) CB | OTHER |  |  |  |  | CDC | 195 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | DS1 | 1651 | [16 empty] | 2-30-08 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1651_DS | 1651(#1DTR) DS | OTHER |  |  |  |  | CDC | 196 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | DS2 | 1652 | [16 empty] | 2-30-09 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1652_DS | 1652(#1DTR) DS | OTHER |  |  |  |  | CDC | 197 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | BE0 | 1660BE | [16 empty] | 2-30-14 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1660BE_ES | 1660BE(#2DTR) ES | OTHER |  |  |  |  | CDC | 198 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | TE0 | 1660TE | [16 empty] | 2-30-15 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1660TE_ES | 1660TE(#2DTR) ES | OTHER |  |  |  |  | CDC | 199 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | CB | [17 empty] | 1-0A-02 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1660_CB | 1660(#2DTR) CB | OTHER |  |  |  |  | CDC | 200 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | DS1 | 1661 | [16 empty] | 2-30-12 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1661_DS | 1661(#2DTR) DS | OTHER |  |  |  |  | CDC | 201 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | DS2 | 1662 | [16 empty] | 2-30-13 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1662_DS | 1662(#2DTR) DS | OTHER |  |  |  |  | CDC | 202 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 0 |  | 3DTR | #3DTR |  | 87A | [17 empty] | 1-0A-05 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.#3DTR_87A | #3DTR 87RY | OTHER |  |  |  |  | CDC | 203 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 3DTR | #3DTR |  | 87UL | [17 empty] | 1-3E-04 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.#3DTR_87UL | #3DTR 87RY U/L | OTHER |  |  |  |  | CDC | 204 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
C99 | 南科CS | 0 |  | 3DTR | #3DTR |  | TRA | [17 empty] | 1-3E-03 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.#3DTR_TRA | #3DTR 重故障 | OTHER |  |  |  |  | CDC | 205 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 3DTR | #3DTR |  | TRF | [17 empty] | 1-3E-02 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.#3DTR_TRF | #3DTR 輕故障 | OTHER |  |  |  |  | CDC | 206 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 4DTR | #4DTR |  | 87A | [17 empty] | 1-0A-07 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.#4DTR_87A | #4DTR 87RY | OTHER |  |  |  |  | CDC | 207 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 4DTR | #4DTR |  | 87UL | [17 empty] | 1-3E-07 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.#4DTR_87UL | #4DTR 87RY U/L | OTHER |  |  |  |  | CDC | 208 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
C99 | 南科CS | 0 |  | 4DTR | #4DTR |  | TRA | [17 empty] | 1-3E-06 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.#4DTR_TRA | #4DTR 重故障 | OTHER |  |  |  |  | CDC | 209 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 4DTR | #4DTR |  | TRF | [17 empty] | 1-3E-05 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.#4DTR_TRF | #4DTR 輕故障 | OTHER |  |  |  |  | CDC | 210 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 161 | 161kV | 1670 | #3DTR(1670) |  | BE0 | 1670BE | [16 empty] | 2-31-02 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1670BE_ES | 1670BE(#3DTR) ES | OTHER |  |  |  |  | CDC | 211 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1670 | #3DTR(1670) |  | TE0 | 1670TE | [16 empty] | 2-31-03 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1670TE_ES | 1670TE(#3DTR) ES | OTHER |  |  |  |  | CDC | 212 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1670 | #3DTR(1670) |  | CB | [17 empty] | 1-0A-04 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1670_CB | 1670(#3DTR) CB | OTHER |  |  |  |  | CDC | 213 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1670 | #3DTR(1670) |  | DS1 | 1671 | [16 empty] | 2-31-00 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1671_DS | 1671(#3DTR) DS | OTHER |  |  |  |  | CDC | 214 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1670 | #3DTR(1670) |  | DS2 | 1672 | [16 empty] | 2-31-01 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1672_DS | 1672(#3DTR) DS | OTHER |  |  |  |  | CDC | 215 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1680 | #4DTR(1680) |  | BE0 | 1680BE | [16 empty] | 2-31-06 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1680BE_ES | 1680BE(#4DTR) ES | OTHER |  |  |  |  | CDC | 216 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1680 | #4DTR(1680) |  | TE0 | 1680TE | [16 empty] | 2-31-07 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1680TE_ES | 1680TE(#4DTR) ES | OTHER |  |  |  |  | CDC | 217 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1680 | #4DTR(1680) |  | CB | [17 empty] | 1-0A-06 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1680_CB | 1680(#4DTR) CB | OTHER |  |  |  |  | CDC | 218 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1680 | #4DTR(1680) |  | DS1 | 1681 | [16 empty] | 2-31-04 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1681_DS | 1681(#4DTR) DS | OTHER |  |  |  |  | CDC | 219 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1680 | #4DTR(1680) |  | DS2 | 1682 | [16 empty] | 2-31-05 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1682_DS | 1682(#4DTR) DS | OTHER |  |  |  |  | CDC | 220 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 0 |  | 1710 | 和鑫二積P3線(1710) |  | 87UL | [17 empty] | 1-3D-09 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1710_87UL | 1710(和鑫二積P3線) 87RY U/L | OTHER |  |  |  |  | CDC | 221 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
C99 | 南科CS | 0 |  | 1720 | 積十四積六線(1720) |  | 87UL | [17 empty] | 1-3D-10 | [7 empty] | ADCS_S | [8 empty] | 積P3CS.1720_87UL | 1720(南科積P3線) 87RY U/L | OTHER |  |  |  |  | CDC | 222 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [17 empty] | 1-0C-00 | [7 empty] | ADCS_S | [8 empty] | 積E五.1500_CB | 1500(TIE) CB | OTHER |  |  |  |  | CDC | 223 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [16 empty] | 2-33-10 | [7 empty] | ADCS_S | [8 empty] | 積E五.1501E_ES | 1501E ES | OTHER |  |  |  |  | CDC | 224 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [16 empty] | 2-33-08 | [7 empty] | ADCS_S | [8 empty] | 積E五.1501_DS | 1501(TIE) DS | OTHER |  |  |  |  | CDC | 225 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [16 empty] | 2-33-11 | [7 empty] | ADCS_S | [8 empty] | 積E五.1502E_ES | 1502E ES | OTHER |  |  |  |  | CDC | 226 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [16 empty] | 2-33-09 | [7 empty] | ADCS_S | [8 empty] | 積E五.1502_DS | 1502(TIE) DS | OTHER |  |  |  |  | CDC | 227 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1530 | 積E五積E七線(1530) |  | BE10 | 1530BE1 | [16 empty] | 2-34-03 | [7 empty] | ADCS_S | [8 empty] | 積E五.1530BE1_ES | 1530BE1(積E五積E七線) ES | OTHER |  |  |  |  | CDC | 228 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1530 | 積E五積E七線(1530) |  | BE20 | 1530BE2 | [16 empty] | 2-34-04 | [7 empty] | ADCS_S | [8 empty] | 積E五.1530BE2_ES | 1530BE2(積E五積E七線) ES | OTHER |  |  |  |  | CDC | 229 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1530 | 積E五積E七線(1530) |  | LE0 | 1530LE | [16 empty] | 2-34-02 | [7 empty] | ADCS_S | [8 empty] | 積E五.1530LE_ES | 1530LE(積E五積E七線) ES | OTHER |  |  |  |  | CDC | 230 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 0 |  | 1530 | 積E五積E七線(1530) |  | 87UL | [17 empty] | 2-32-01 | [7 empty] | ADCS_S | [8 empty] | 積E五.1530_87UL | 1530(積E五積E七線) 87RY U/L | OTHER |  |  |  |  | CDC | 231 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
C99 | 南科CS | 161 | 161kV | 1530 | 積E五積E七線(1530) |  | CB | [17 empty] | 1-0C-02 | [7 empty] | ADCS_S | [8 empty] | 積E五.1530_CB | 1530(積E五積E七線) CB | OTHER |  |  |  |  | CDC | 232 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1530 | 積E五積E七線(1530) |  | DS1 | 1531 | [16 empty] | 2-33-14 | [7 empty] | ADCS_S | [8 empty] | 積E五.1531_DS | 1531(積E五積E七線) DS | OTHER |  |  |  |  | CDC | 233 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1530 | 積E五積E七線(1530) |  | DS2 | 1532 | [16 empty] | 2-33-15 | [7 empty] | ADCS_S | [8 empty] | 積E五.1532_DS | 1532(積E五積E七線) DS | OTHER |  |  |  |  | CDC | 234 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1530 | 積E五積E七線(1530) |  | E3 | 1533E | [16 empty] | 2-34-01 | [7 empty] | ADCS_S | [8 empty] | 積E五.1533E_ES | 1533E(積E五積E七線) ES | OTHER |  |  |  |  | CDC | 235 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1530 | 積E五積E七線(1530) |  | DS3 | 1533 | [16 empty] | 2-34-00 | [7 empty] | ADCS_S | [8 empty] | 積E五.1533_DS | 1533(積E五積E七線) DS | OTHER |  |  |  |  | CDC | 236 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1540 | 康寧積十四線(1540) |  | BE10 | 1540BE1 | [16 empty] | 2-34-10 | [7 empty] | ADCS_S | [8 empty] | 積E五.1540BE1_ES | 1540BE1(積E五積E六線) ES | OTHER |  |  |  |  | CDC | 237 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1540 | 康寧積十四線(1540) |  | BE20 | 1540BE2 | [16 empty] | 2-34-11 | [7 empty] | ADCS_S | [8 empty] | 積E五.1540BE2_ES | 1540BE2(積E五積E六線) ES | OTHER |  |  |  |  | CDC | 238 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1540 | 康寧積十四線(1540) |  | LE0 | 1540LE | [16 empty] | 2-34-09 | [7 empty] | ADCS_S | [8 empty] | 積E五.1540LE_ES | 1540LE(積E五積E六線) ES | OTHER |  |  |  |  | CDC | 239 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 0 |  | 1540 | 康寧積十四線(1540) |  | 87UL | [17 empty] | 2-32-02 | [7 empty] | ADCS_S | [8 empty] | 積E五.1540_87UL | 1540(積E五積E六線) 87RY U/L | OTHER |  |  |  |  | CDC | 240 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | USE/LOCK | USE
C99 | 南科CS | 161 | 161kV | 1540 | 康寧積十四線(1540) |  | CB | [17 empty] | 1-0C-04 | [7 empty] | ADCS_S | [8 empty] | 積E五.1540_CB | 1540(積E五積E六線) CB | OTHER |  |  |  |  | CDC | 241 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1540 | 康寧積十四線(1540) |  | DS1 | 1541 | [16 empty] | 2-34-05 | [7 empty] | ADCS_S | [8 empty] | 積E五.1541_DS | 1541(積E五積E六線) DS | OTHER |  |  |  |  | CDC | 242 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1540 | 康寧積十四線(1540) |  | DS2 | 1542 | [16 empty] | 2-34-06 | [7 empty] | ADCS_S | [8 empty] | 積E五.1542_DS | 1542(積E五積E六線) DS | OTHER |  |  |  |  | CDC | 243 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1540 | 康寧積十四線(1540) |  | E3 | 1543E | [16 empty] | 2-34-08 | [7 empty] | ADCS_S | [8 empty] | 積E五.1543E_ES | 1543E(積E五積E六線) ES | OTHER |  |  |  |  | CDC | 244 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1540 | 康寧積十四線(1540) |  | DS3 | 1543 | [16 empty] | 2-34-07 | [7 empty] | ADCS_S | [8 empty] | 積E五.1543_DS | 1543(積E五積E六線) DS | OTHER |  |  |  |  | CDC | 245 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 0 |  | 15B1E | 15B1E |  | BE1 | 15B1E | [16 empty] | 2-33-12 | [7 empty] | ADCS_S | [8 empty] | 積E五.15B1E_ES | 15B1E ES | OTHER |  |  |  |  | CDC | 246 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 0 |  | 15B2E | 15B2E |  | BE2 | 15B2E | [16 empty] | 2-33-13 | [7 empty] | ADCS_S | [8 empty] | 積E五.15B2E_ES | 15B2E ES | OTHER |  |  |  |  | CDC | 247 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | BE10 | 1650BE1 | [16 empty] | 2-35-02 | [7 empty] | ADCS_S | [8 empty] | 積E五.1650BE1_ES | 1650BE1(#1MTR) ES | OTHER |  |  |  |  | CDC | 248 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | BE20 | 1650BE2 | [16 empty] | 2-35-03 | [7 empty] | ADCS_S | [8 empty] | 積E五.1650BE2_ES | 1650BE2(#1MTR) ES | OTHER |  |  |  |  | CDC | 249 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | TE0 | 1650TE | [16 empty] | 2-35-04 | [7 empty] | ADCS_S | [8 empty] | 積E五.1650TE_ES | 1650TE(#1MTR) ES | OTHER |  |  |  |  | CDC | 250 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | CB | [17 empty] | 1-0D-00 | [7 empty] | ADCS_S | [8 empty] | 積E五.1650_CB | 1650(#1MTR) CB | OTHER |  |  |  |  | CDC | 251 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | DS1 | 1651 | [16 empty] | 2-35-00 | [7 empty] | ADCS_S | [8 empty] | 積E五.1651_DS | 1651(#1MTR) DS | OTHER |  |  |  |  | CDC | 252 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | DS2 | 1652 | [16 empty] | 2-35-01 | [7 empty] | ADCS_S | [8 empty] | 積E五.1652_DS | 1652(#1MTR) DS | OTHER |  |  |  |  | CDC | 253 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | BE10 | 1660BE1 | [16 empty] | 2-35-07 | [7 empty] | ADCS_S | [8 empty] | 積E五.1660BE1_ES | 1660BE1(#2MTR) ES | OTHER |  |  |  |  | CDC | 254 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | BE20 | 1660BE2 | [16 empty] | 2-35-08 | [7 empty] | ADCS_S | [8 empty] | 積E五.1660BE2_ES | 1660BE2(#2MTR) ES | OTHER |  |  |  |  | CDC | 255 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | TE0 | 1660TE | [16 empty] | 2-35-09 | [7 empty] | ADCS_S | [8 empty] | 積E五.1660TE_ES | 1660TE(#2MTR) ES | OTHER |  |  |  |  | CDC | 256 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | CB | [17 empty] | 1-0D-02 | [7 empty] | ADCS_S | [8 empty] | 積E五.1660_CB | 1660(#2MTR) CB | OTHER |  |  |  |  | CDC | 257 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | DS1 | 1661 | [16 empty] | 2-35-05 | [7 empty] | ADCS_S | [8 empty] | 積E五.1661_DS | 1661(#2MTR) DS | OTHER |  |  |  |  | CDC | 258 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | DS2 | 1662 | [16 empty] | 2-35-06 | [7 empty] | ADCS_S | [8 empty] | 積E五.1662_DS | 1662(#2MTR) DS | OTHER |  |  |  |  | CDC | 259 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1670 | #3DTR(1670) |  | BE10 | 1670BE1 | [16 empty] | 2-35-12 | [7 empty] | ADCS_S | [8 empty] | 積E五.1670BE1_ES | 1670BE1(#3MTR) ES | OTHER |  |  |  |  | CDC | 260 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1670 | #3DTR(1670) |  | BE20 | 1670BE2 | [16 empty] | 2-35-13 | [7 empty] | ADCS_S | [8 empty] | 積E五.1670BE2_ES | 1670BE2(#3MTR) ES | OTHER |  |  |  |  | CDC | 261 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1670 | #3DTR(1670) |  | TE0 | 1670TE | [16 empty] | 2-35-14 | [7 empty] | ADCS_S | [8 empty] | 積E五.1670TE_ES | 1670TE(#3MTR) ES | OTHER |  |  |  |  | CDC | 262 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1670 | #3DTR(1670) |  | CB | [17 empty] | 1-0D-04 | [7 empty] | ADCS_S | [8 empty] | 積E五.1670_CB | 1670(#3MTR) CB | OTHER |  |  |  |  | CDC | 263 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1670 | #3DTR(1670) |  | DS1 | 1671 | [16 empty] | 2-35-10 | [7 empty] | ADCS_S | [8 empty] | 積E五.1671_DS | 1671(#3MTR) DS | OTHER |  |  |  |  | CDC | 264 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1670 | #3DTR(1670) |  | DS2 | 1672 | [16 empty] | 2-35-11 | [7 empty] | ADCS_S | [8 empty] | 積E五.1672_DS | 1672(#3MTR) DS | OTHER |  |  |  |  | CDC | 265 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1680 | #4DTR(1680) |  | BE10 | 1680BE1 | [16 empty] | 2-36-01 | [7 empty] | ADCS_S | [8 empty] | 積E五.1680BE1_ES | 1680BE1(#4MTR) ES | OTHER |  |  |  |  | CDC | 266 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1680 | #4DTR(1680) |  | BE20 | 1680BE2 | [16 empty] | 2-36-02 | [7 empty] | ADCS_S | [8 empty] | 積E五.1680BE2_ES | 1680BE2(#4MTR) ES | OTHER |  |  |  |  | CDC | 267 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1680 | #4DTR(1680) |  | TE0 | 1680TE | [16 empty] | 2-36-03 | [7 empty] | ADCS_S | [8 empty] | 積E五.1680TE_ES | 1680TE(#4MTR) ES | OTHER |  |  |  |  | CDC | 268 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1680 | #4DTR(1680) |  | CB | [17 empty] | 1-0D-06 | [7 empty] | ADCS_S | [8 empty] | 積E五.1680_CB | 1680(#4MTR) CB | OTHER |  |  |  |  | CDC | 269 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1680 | #4DTR(1680) |  | DS1 | 1681 | [16 empty] | 2-35-15 | [7 empty] | ADCS_S | [8 empty] | 積E五.1681_DS | 1681(#4MTR) DS | OTHER |  |  |  |  | CDC | 270 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1680 | #4DTR(1680) |  | DS2 | 1682 | [16 empty] | 2-36-00 | [7 empty] | ADCS_S | [8 empty] | 積E五.1682_DS | 1682(#4MTR) DS | OTHER |  |  |  |  | CDC | 271 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 0 |  |  |  |  | OFA通訊故障 | [17 empty] | 2-33-07 | [7 empty] | ADCS_S | [8 empty] | 積E五.OFA通訊故障 | OFA光纖通訊故障警報 | OTHER |  |  |  |  | CDC | 272 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  |  |  |  | 設備通訊故障 | [17 empty] | 2-33-06 | [7 empty] | ADCS_S | [8 empty] | 積E五.設備通訊故障 | 資料收集設備通訊故障警報 | OTHER |  |  |  |  | CDC | 273 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  |  |  |  | 設備內部故障 | [17 empty] | 2-32-03 | [7 empty] | ADCS_S | [8 empty] | 積E五.設備內部故障 | 資料收集設備內部異常故障警報 | OTHER |  |  |  |  | CDC | 274 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1MTR | #1MTR |  | 87A | [17 empty] | 1-0D-01 | [7 empty] | ADCS_S | [8 empty] | 積E五.#1MTR_87A | #1MTR 87RY | OTHER |  |  |  |  | CDC | 275 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1MTR | #1MTR |  | 87UL | [17 empty] | 2-32-06 | [7 empty] | ADCS_S | [8 empty] | 積E五.#1MTR_87UL | #1MTR 87RY U/L | OTHER |  |  |  |  | CDC | 276 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
C99 | 南科CS | 0 |  | 1MTR | #1MTR |  | TRA | [17 empty] | 2-32-05 | [7 empty] | ADCS_S | [8 empty] | 積E五.#1MTR_TRA | #1MTR 重故障 | OTHER |  |  |  |  | CDC | 277 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1MTR | #1MTR |  | TRF | [17 empty] | 2-32-04 | [7 empty] | ADCS_S | [8 empty] | 積E五.#1MTR_TRF | #1MTR 輕故障 | OTHER |  |  |  |  | CDC | 278 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 2MTR | #2MTR |  | 87A | [17 empty] | 1-0D-03 | [7 empty] | ADCS_S | [8 empty] | 積E五.#2MTR_87A | #2MTR 87RY | OTHER |  |  |  |  | CDC | 279 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 2MTR | #2MTR |  | 87UL | [17 empty] | 2-32-09 | [7 empty] | ADCS_S | [8 empty] | 積E五.#2MTR_87UL | #2MTR 87RY U/L | OTHER |  |  |  |  | CDC | 280 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
C99 | 南科CS | 0 |  | 2MTR | #2MTR |  | TRA | [17 empty] | 2-32-08 | [7 empty] | ADCS_S | [8 empty] | 積E五.#2MTR_TRA | #2MTR 重故障 | OTHER |  |  |  |  | CDC | 281 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 2MTR | #2MTR |  | TRF | [17 empty] | 2-32-07 | [7 empty] | ADCS_S | [8 empty] | 積E五.#2MTR_TRF | #2MTR 輕故障 | OTHER |  |  |  |  | CDC | 282 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 3MTR | #3MTR |  | 87A | [17 empty] | 1-0D-05 | [7 empty] | ADCS_S | [8 empty] | 積E五.#3MTR_87A | #3MTR 87RY | OTHER |  |  |  |  | CDC | 283 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 3MTR | #3MTR |  | 87UL | [17 empty] | 2-32-12 | [7 empty] | ADCS_S | [8 empty] | 積E五.#3MTR_87UL | #3MTR 87RY U/L | OTHER |  |  |  |  | CDC | 284 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
C99 | 南科CS | 0 |  | 3MTR | #3MTR |  | TRA | [17 empty] | 2-32-11 | [7 empty] | ADCS_S | [8 empty] | 積E五.#3MTR_TRA | #3MTR 重故障 | OTHER |  |  |  |  | CDC | 285 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 3MTR | #3MTR |  | TRF | [17 empty] | 2-32-10 | [7 empty] | ADCS_S | [8 empty] | 積E五.#3MTR_TRF | #3MTR 輕故障 | OTHER |  |  |  |  | CDC | 286 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 4MTR | #4MTR |  | 87A | [17 empty] | 1-0D-07 | [7 empty] | ADCS_S | [8 empty] | 積E五.#4MTR_87A | #4MTR 87RY | OTHER |  |  |  |  | CDC | 287 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 4MTR | #4MTR |  | 87UL | [17 empty] | 2-32-15 | [7 empty] | ADCS_S | [8 empty] | 積E五.#4MTR_87UL | #4MTR 87RY U/L | OTHER |  |  |  |  | CDC | 288 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
C99 | 南科CS | 0 |  | 4MTR | #4MTR |  | TRA | [17 empty] | 2-32-14 | [7 empty] | ADCS_S | [8 empty] | 積E五.#4MTR_TRA | #4MTR 重故障 | OTHER |  |  |  |  | CDC | 289 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 4MTR | #4MTR |  | TRF | [17 empty] | 2-32-13 | [7 empty] | ADCS_S | [8 empty] | 積E五.#4MTR_TRF | #4MTR 輕故障 | OTHER |  |  |  |  | CDC | 290 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1500 | TIE(1500) |  | 50A | [17 empty] | 1-0C-01 | [7 empty] | ADCS_S | [8 empty] | 積E五.1500_50A | 161KV TIE(1500) 50RY | OTHER |  |  |  |  | CDC | 291 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1500 | TIE(1500) |  | 50UL | [17 empty] | 2-32-00 | [7 empty] | ADCS_S | [8 empty] | 積E五.1500_50UL | 161KV TIE(1500) 50RY UL | OTHER |  |  |  |  | CDC | 292 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | USE/LOCK | USE
C99 | 南科CS | 0 |  | 1530 | 積E五積E七線(1530) |  | 87A | [17 empty] | 1-0C-03 | [7 empty] | ADCS_S | [8 empty] | 積E五.1530_87A | 1530(積E五積E七線) 87RY | OTHER |  |  |  |  | CDC | 293 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1540 | 康寧積十四線(1540) |  | 87A | [17 empty] | 1-0C-05 | [7 empty] | ADCS_S | [8 empty] | 積E五.1540_87A | 1540(積E五積E六線) 87RY | OTHER |  |  |  |  | CDC | 294 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | UPS | UPS |  | AC_Fault | [17 empty] | 2-34-14 | [7 empty] | ADCS_S | [8 empty] | 積E五.UPS_AC故障 | UPS AC故障警報 | OTHER |  |  |  |  | CDC | 295 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | UPS | UPS |  | DC故障 | [17 empty] | 2-34-15 | [7 empty] | ADCS_S | [8 empty] | 積E五.UPS_DC故障 | UPS DC故障警報 | OTHER |  |  |  |  | CDC | 296 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 161 | 161kV | 1530 | 積E五積E七線(1530) |  | CB | [17 empty] | 1-0F-02 | [7 empty] | ADCS_S | [8 empty] | 積E六.1530_CB | 1530(積E五積E六線) CB | OTHER |  |  |  |  | CDC | 297 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1540 | 康寧積十四線(1540) |  | CB | [17 empty] | 1-0F-04 | [7 empty] | ADCS_S | [8 empty] | 積E六.1540_CB | 1540(南科積E六線) CB | OTHER |  |  |  |  | CDC | 298 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [17 empty] | 1-0F-00 | [7 empty] | ADCS_S | [8 empty] | 積E六.1500_CB | 1500(TIE) CB | OTHER |  |  |  |  | CDC | 299 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [16 empty] | 2-38-02 | [7 empty] | ADCS_S | [8 empty] | 積E六.1501E_ES | 1501E ES | OTHER |  |  |  |  | CDC | 300 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [16 empty] | 2-38-00 | [7 empty] | ADCS_S | [8 empty] | 積E六.1501_DS | 1501(TIE) DS | OTHER |  |  |  |  | CDC | 301 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [16 empty] | 2-38-03 | [7 empty] | ADCS_S | [8 empty] | 積E六.1502E_ES | 1502E ES | OTHER |  |  |  |  | CDC | 302 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [16 empty] | 2-38-01 | [7 empty] | ADCS_S | [8 empty] | 積E六.1502_DS | 1502(TIE) DS | OTHER |  |  |  |  | CDC | 303 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1530 | 積E五積E七線(1530) |  | BE10 | 1530BE1 | [16 empty] | 2-39-01 | [7 empty] | ADCS_S | [8 empty] | 積E六.1530BE1_ES | 1530BE1(積E五積E六線) ES | OTHER |  |  |  |  | CDC | 304 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1530 | 積E五積E七線(1530) |  | BE20 | 1530BE2 | [16 empty] | 2-39-03 | [7 empty] | ADCS_S | [8 empty] | 積E六.1530BE2_ES | 1530BE2(積E五積E六線) ES | OTHER |  |  |  |  | CDC | 305 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1530 | 積E五積E七線(1530) |  | LE0 | 1530LE | [16 empty] | 2-39-02 | [7 empty] | ADCS_S | [8 empty] | 積E六.1530LE_ES | 1530LE(積E五積E六線) ES | OTHER |  |  |  |  | CDC | 306 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 0 |  | 1530 | 積E五積E七線(1530) |  | 87UL | [17 empty] | 2-36-09 | [7 empty] | ADCS_S | [8 empty] | 積E六.1530_87UL | 1530(積E五積E六線) 87RY U/L | OTHER |  |  |  |  | CDC | 307 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | USE/LOCK | USE
C99 | 南科CS | 161 | 161kV | 1530 | 積E五積E七線(1530) |  | DS1 | 1531 | [16 empty] | 2-38-14 | [7 empty] | ADCS_S | [8 empty] | 積E六.1531_DS | 1531(積E五積E六線) DS | OTHER |  |  |  |  | CDC | 308 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1530 | 積E五積E七線(1530) |  | DS2 | 1532 | [16 empty] | 2-39-00 | [7 empty] | ADCS_S | [8 empty] | 積E六.1532_DS | 1532(積E五積E六線) DS | OTHER |  |  |  |  | CDC | 309 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1530 | 積E五積E七線(1530) |  | E3 | 1533E | [16 empty] | 2-38-15 | [7 empty] | ADCS_S | [8 empty] | 積E六.1533E_ES | 1533E(積E五積E六線) ES | OTHER |  |  |  |  | CDC | 310 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1530 | 積E五積E七線(1530) |  | DS3 | 1533 | [16 empty] | 2-38-13 | [7 empty] | ADCS_S | [8 empty] | 積E六.1533_DS | 1533(積E五積E六線) DS | OTHER |  |  |  |  | CDC | 311 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1540 | 康寧積十四線(1540) |  | BE10 | 1540BE1 | [16 empty] | 2-38-10 | [7 empty] | ADCS_S | [8 empty] | 積E六.1540BE1_ES | 1540BE1(南科積E六線) ES | OTHER |  |  |  |  | CDC | 312 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1540 | 康寧積十四線(1540) |  | BE20 | 1540BE2 | [16 empty] | 2-38-12 | [7 empty] | ADCS_S | [8 empty] | 積E六.1540BE2_ES | 1540BE2(南科積E六線) ES | OTHER |  |  |  |  | CDC | 313 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1540 | 康寧積十四線(1540) |  | LE0 | 1540LE | [16 empty] | 2-38-11 | [7 empty] | ADCS_S | [8 empty] | 積E六.1540LE_ES | 1540LE(南科積E六線) ES | OTHER |  |  |  |  | CDC | 314 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 0 |  | 1540 | 康寧積十四線(1540) |  | 87UL | [17 empty] | 2-36-10 | [7 empty] | ADCS_S | [8 empty] | 積E六.1540_87UL | 1540(南科積E六線) 87RY U/L | OTHER |  |  |  |  | CDC | 315 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | USE/LOCK | USE
C99 | 南科CS | 161 | 161kV | 1540 | 康寧積十四線(1540) |  | DS1 | 1541 | [16 empty] | 2-38-07 | [7 empty] | ADCS_S | [8 empty] | 積E六.1541_DS | 1541(南科積E六線) DS | OTHER |  |  |  |  | CDC | 316 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1540 | 康寧積十四線(1540) |  | DS2 | 1542 | [16 empty] | 2-38-09 | [7 empty] | ADCS_S | [8 empty] | 積E六.1542_DS | 1542(南科積E六線) DS | OTHER |  |  |  |  | CDC | 317 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1540 | 康寧積十四線(1540) |  | E3 | 1543E | [16 empty] | 2-38-08 | [7 empty] | ADCS_S | [8 empty] | 積E六.1543E_ES | 1543E(南科積E六線) ES | OTHER |  |  |  |  | CDC | 318 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1540 | 康寧積十四線(1540) |  | DS3 | 1543 | [16 empty] | 2-38-06 | [7 empty] | ADCS_S | [8 empty] | 積E六.1543_DS | 1543(南科積E六線) DS | OTHER |  |  |  |  | CDC | 319 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 0 |  | 15B1E | 15B1E |  | BE1 | 15B1E | [16 empty] | 2-38-04 | [7 empty] | ADCS_S | [8 empty] | 積E六.15B1E_ES | 15B1E ES | OTHER |  |  |  |  | CDC | 320 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 0 |  | 15B2E | 15B2E |  | BE2 | 15B2E | [16 empty] | 2-38-05 | [7 empty] | ADCS_S | [8 empty] | 積E六.15B2E_ES | 15B2E ES | OTHER |  |  |  |  | CDC | 321 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | BE10 | 1650BE1 | [16 empty] | 2-39-10 | [7 empty] | ADCS_S | [8 empty] | 積E六.1650BE1_ES | 1650BE1(#5MTR) ES | OTHER |  |  |  |  | CDC | 322 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | BE20 | 1650BE2 | [16 empty] | 2-39-11 | [7 empty] | ADCS_S | [8 empty] | 積E六.1650BE2_ES | 1650BE2(#5MTR) ES | OTHER |  |  |  |  | CDC | 323 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | TE0 | 1650TE | [16 empty] | 2-39-12 | [7 empty] | ADCS_S | [8 empty] | 積E六.1650TE_ES | 1650TE(#5MTR) ES | OTHER |  |  |  |  | CDC | 324 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | CB | [17 empty] | 1-10-00 | [7 empty] | ADCS_S | [8 empty] | 積E六.1650_CB | 1650(#5MTR) CB | OTHER |  |  |  |  | CDC | 325 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | DS1 | 1651 | [16 empty] | 2-39-08 | [7 empty] | ADCS_S | [8 empty] | 積E六.1651_DS | 1651(#5MTR) DS | OTHER |  |  |  |  | CDC | 326 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | DS2 | 1652 | [16 empty] | 2-39-09 | [7 empty] | ADCS_S | [8 empty] | 積E六.1652_DS | 1652(#5MTR) DS | OTHER |  |  |  |  | CDC | 327 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | BE10 | 1660BE1 | [16 empty] | 2-39-15 | [7 empty] | ADCS_S | [8 empty] | 積E六.1660BE1_ES | 1660BE1(#6MTR) ES | OTHER |  |  |  |  | CDC | 328 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | BE20 | 1660BE2 | [16 empty] | 2-3A-00 | [7 empty] | ADCS_S | [8 empty] | 積E六.1660BE2_ES | 1660BE2(#6MTR) ES | OTHER |  |  |  |  | CDC | 329 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | TE0 | 1660TE | [16 empty] | 2-3A-01 | [7 empty] | ADCS_S | [8 empty] | 積E六.1660TE_ES | 1660TE(#6MTR) ES | OTHER |  |  |  |  | CDC | 330 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | CB | [17 empty] | 1-10-02 | [7 empty] | ADCS_S | [8 empty] | 積E六.1660_CB | 1660(#6MTR) CB | OTHER |  |  |  |  | CDC | 331 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | DS1 | 1661 | [16 empty] | 2-39-13 | [7 empty] | ADCS_S | [8 empty] | 積E六.1661_DS | 1661(#6MTR) DS | OTHER |  |  |  |  | CDC | 332 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | DS2 | 1662 | [16 empty] | 2-39-14 | [7 empty] | ADCS_S | [8 empty] | 積E六.1662_DS | 1662(#6MTR) DS | OTHER |  |  |  |  | CDC | 333 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1670 | #3DTR(1670) |  | BE10 | 1670BE1 | [16 empty] | 2-3A-04 | [7 empty] | ADCS_S | [8 empty] | 積E六.1670BE1_ES | 1670BE1(#7MTR) ES | OTHER |  |  |  |  | CDC | 334 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1670 | #3DTR(1670) |  | BE20 | 1670BE2 | [16 empty] | 2-3A-05 | [7 empty] | ADCS_S | [8 empty] | 積E六.1670BE2_ES | 1670BE2(#7MTR) ES | OTHER |  |  |  |  | CDC | 335 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1670 | #3DTR(1670) |  | TE0 | 1670TE | [16 empty] | 2-3A-06 | [7 empty] | ADCS_S | [8 empty] | 積E六.1670TE_ES | 1670TE(#7MTR) ES | OTHER |  |  |  |  | CDC | 336 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1670 | #3DTR(1670) |  | CB | [17 empty] | 1-10-04 | [7 empty] | ADCS_S | [8 empty] | 積E六.1670_CB | 1670(#7MTR) CB | OTHER |  |  |  |  | CDC | 337 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1670 | #3DTR(1670) |  | DS1 | 1671 | [16 empty] | 2-3A-02 | [7 empty] | ADCS_S | [8 empty] | 積E六.1671_DS | 1671(#7MTR) DS | OTHER |  |  |  |  | CDC | 338 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1670 | #3DTR(1670) |  | DS2 | 1672 | [16 empty] | 2-3A-03 | [7 empty] | ADCS_S | [8 empty] | 積E六.1672_DS | 1672(#7MTR) DS | OTHER |  |  |  |  | CDC | 339 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1680 | #4DTR(1680) |  | BE10 | 1680BE1 | [16 empty] | 2-3A-09 | [7 empty] | ADCS_S | [8 empty] | 積E六.1680BE1_ES | 1680BE1(#8MTR) ES | OTHER |  |  |  |  | CDC | 340 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1680 | #4DTR(1680) |  | BE20 | 1680BE2 | [16 empty] | 2-3A-10 | [7 empty] | ADCS_S | [8 empty] | 積E六.1680BE2_ES | 1680BE2(#8MTR) ES | OTHER |  |  |  |  | CDC | 341 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1680 | #4DTR(1680) |  | TE0 | 1680TE | [16 empty] | 2-3A-11 | [7 empty] | ADCS_S | [8 empty] | 積E六.1680TE_ES | 1680TE(#8MTR) ES | OTHER |  |  |  |  | CDC | 342 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1680 | #4DTR(1680) |  | CB | [17 empty] | 1-10-06 | [7 empty] | ADCS_S | [8 empty] | 積E六.1680_CB | 1680(#8MTR) CB | OTHER |  |  |  |  | CDC | 343 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1680 | #4DTR(1680) |  | DS1 | 1681 | [16 empty] | 2-3A-07 | [7 empty] | ADCS_S | [8 empty] | 積E六.1681_DS | 1681(#8MTR) DS | OTHER |  |  |  |  | CDC | 344 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1680 | #4DTR(1680) |  | DS2 | 1682 | [16 empty] | 2-3A-08 | [7 empty] | ADCS_S | [8 empty] | 積E六.1682_DS | 1682(#8MTR) DS | OTHER |  |  |  |  | CDC | 345 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 0 |  |  |  |  | OFA通訊故障 | [17 empty] | 2-37-15 | [7 empty] | ADCS_S | [8 empty] | 積E六.OFA通訊故障 | OFA光纖通訊故障警報 | OTHER |  |  |  |  | CDC | 346 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  |  |  |  | 設備通訊故障 | [17 empty] | 2-37-14 | [7 empty] | ADCS_S | [8 empty] | 積E六.設備通訊故障 | 資料收集設備通訊故障警報 | OTHER |  |  |  |  | CDC | 347 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1500 | TIE(1500) |  | 50A | [17 empty] | 1-12-01 | [7 empty] | ADCS_S | [8 empty] | 三福一.1500_50A | 161KV TIE(1500) 50RY | OTHER |  |  |  |  | CDC | 348 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [17 empty] | 1-12-00 | [7 empty] | ADCS_S | [8 empty] | 三福一.1500_CB | 1500(TIE) CB | OTHER |  |  |  |  | CDC | 349 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [16 empty] | 2-3C-00 | [7 empty] | ADCS_S | [8 empty] | 三福一.1501E_ES | 1501E ES | OTHER |  |  |  |  | CDC | 350 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [16 empty] | 2-3B-14 | [7 empty] | ADCS_S | [8 empty] | 三福一.1501_DS | 1501(TIE) DS | OTHER |  |  |  |  | CDC | 351 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [16 empty] | 2-3C-01 | [7 empty] | ADCS_S | [8 empty] | 三福一.1502E_ES | 1502E ES | OTHER |  |  |  |  | CDC | 352 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [16 empty] | 2-3B-15 | [7 empty] | ADCS_S | [8 empty] | 三福一.1502_DS | 1502(TIE) DS | OTHER |  |  |  |  | CDC | 353 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | BE0 | 1520BE | [16 empty] | 2-3C-08 | [7 empty] | ADCS_S | [8 empty] | 三福一.1520BE_ES | 1520BE(三福一積E七線) ES | OTHER |  |  |  |  | CDC | 354 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | LE0 | 1520LE | [16 empty] | 2-3C-09 | [7 empty] | ADCS_S | [8 empty] | 三福一.1520LE_ES | 1520LE(三福一積E七線) ES | OTHER |  |  |  |  | CDC | 355 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 0 |  | 1520 | 積十四積六線(1520) |  | 87A1 | [17 empty] | 1-12-06 | [7 empty] | ADCS_S | [8 empty] | 三福一.1520_187A | 1520(三福一積E七線) #1 87RY | OTHER |  |  |  |  | CDC | 356 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1520 | 積十四積六線(1520) |  | 187UL | [17 empty] | 2-3B-03 | [7 empty] | ADCS_S | [8 empty] | 三福一.1520_187UL | 1520(三福一積E七線) #1 87U/L | OTHER |  |  |  |  | CDC | 357 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
C99 | 南科CS | 0 |  | 1520 | 積十四積六線(1520) |  | 21SA | [17 empty] | 1-14-02 | [7 empty] | ADCS_S | [8 empty] | 三福一.1520_21SA | 三福一積E七線(1520) 21SA | OTHER |  |  |  |  | CDC | 358 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1520 | 積十四積六線(1520) |  | 87A2 | [17 empty] | 1-12-07 | [7 empty] | ADCS_S | [8 empty] | 三福一.1520_287A | 1520(三福一積E七線) #2 87RY | OTHER |  |  |  |  | CDC | 359 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1520 | 積十四積六線(1520) |  | 287UL | [17 empty] | 2-3B-04 | [7 empty] | ADCS_S | [8 empty] | 三福一.1520_287UL | 1520(三福一積E七線) #2 87U/L | OTHER |  |  |  |  | CDC | 360 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
C99 | 南科CS | 0 |  | 1520 | 積十四積六線(1520) |  | 79UL | [17 empty] | 2-3B-06 | [7 empty] | ADCS_S | [8 empty] | 三福一.1520_79UL | 1520(三福一積E七線) 79U/L | OTHER |  |  |  |  | CDC | 361 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
C99 | 南科CS | 0 |  | 1520 | 積十四積六線(1520) |  | 87CFA | [17 empty] | 1-13-07 | [7 empty] | ADCS_S | [8 empty] | 三福一.1520_87CFA | 三福一積E七線1520 RY通信故障 | OTHER |  |  |  |  | CDC | 362 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | CB | [17 empty] | 1-12-05 | [7 empty] | ADCS_S | [8 empty] | 三福一.1520_CB | 1520(三福一積E七線) CB | OTHER |  |  |  |  | CDC | 363 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 0 |  | 1520 | 積十四積六線(1520) |  | DTTA | [17 empty] | 1-14-03 | [7 empty] | ADCS_S | [8 empty] | 三福一.1520_DTTA | 三福一積E七線(1520) 遠方遙跳 | OTHER |  |  |  |  | CDC | 364 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1520 | 積十四積六線(1520) |  | GDA | [17 empty] | 1-14-01 | [7 empty] | ADCS_S | [8 empty] | 三福一.1520_GDA | 三福一積E七線(1520) GDA | OTHER |  |  |  |  | CDC | 365 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1520 | 積十四積六線(1520) |  | PHA | [17 empty] | 1-14-00 | [7 empty] | ADCS_S | [8 empty] | 三福一.1520_PHA | 三福一積E七線(1520) PHA | OTHER |  |  |  |  | CDC | 366 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | DS1 | 1521 | [16 empty] | 2-3C-05 | [7 empty] | ADCS_S | [8 empty] | 三福一.1521_DS | 1521(三福一積E七線) DS | OTHER |  |  |  |  | CDC | 367 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | DS2 | 1522 | [16 empty] | 2-3C-07 | [7 empty] | ADCS_S | [8 empty] | 三福一.1522_DS | 1522(三福一積E七線) DS | OTHER |  |  |  |  | CDC | 368 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | E3 | 1523E | [16 empty] | 2-3C-06 | [7 empty] | ADCS_S | [8 empty] | 三福一.1523E_ES | 1523E(三福一積E七線) ES | OTHER |  |  |  |  | CDC | 369 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | DS3 | 1523 | [16 empty] | 2-3C-04 | [7 empty] | ADCS_S | [8 empty] | 三福一.1523_DS | 1523(三福一積E七線) DS | OTHER |  |  |  |  | CDC | 370 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1530 | 積E五積E七線(1530) |  | BE0 | 1530BE | [16 empty] | 2-3C-15 | [7 empty] | ADCS_S | [8 empty] | 三福一.1530BE_ES | 1530BE(南科三福一線) ES | OTHER |  |  |  |  | CDC | 371 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1530 | 積E五積E七線(1530) |  | LE0 | 1530LE | [16 empty] | 2-3D-00 | [7 empty] | ADCS_S | [8 empty] | 三福一.1530LE_ES | 1530LE(南科三福一線) ES | OTHER |  |  |  |  | CDC | 372 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 0 |  | 1530 | 積E五積E七線(1530) |  | 87A1 | [17 empty] | 1-12-03 | [7 empty] | ADCS_S | [8 empty] | 三福一.1530_187A | 1530(南科三福一線) #1 87RY | OTHER |  |  |  |  | CDC | 373 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1530 | 積E五積E七線(1530) |  | 187UL | [17 empty] | 2-3B-01 | [7 empty] | ADCS_S | [8 empty] | 三福一.1530_187UL | 1530(南科三福一線) #1 87U/L | OTHER |  |  |  |  | CDC | 374 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
C99 | 南科CS | 0 |  | 1530 | 積E五積E七線(1530) |  | 21SA | [17 empty] | 1-13-05 | [7 empty] | ADCS_S | [8 empty] | 三福一.1530_21SA | 南科三福一線(1530) 21SA | OTHER |  |  |  |  | CDC | 375 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1530 | 積E五積E七線(1530) |  | 87A2 | [17 empty] | 1-12-04 | [7 empty] | ADCS_S | [8 empty] | 三福一.1530_287A | 1530(南科三福一線) #2 87RY | OTHER |  |  |  |  | CDC | 376 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1530 | 積E五積E七線(1530) |  | 287UL | [17 empty] | 2-3B-02 | [7 empty] | ADCS_S | [8 empty] | 三福一.1530_287UL | 1530(南科三福一線) #2 87U/L | OTHER |  |  |  |  | CDC | 377 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
C99 | 南科CS | 0 |  | 1530 | 積E五積E七線(1530) |  | 79UL | [17 empty] | 2-3B-05 | [7 empty] | ADCS_S | [8 empty] | 三福一.1530_79UL | 1530(南科三福一線) 79U/L | OTHER |  |  |  |  | CDC | 378 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
C99 | 南科CS | 0 |  | 1530 | 積E五積E七線(1530) |  | 87CFA | [17 empty] | 1-13-02 | [7 empty] | ADCS_S | [8 empty] | 三福一.1530_87CFA | 南科三福一線(1530)RY通信故障 | OTHER |  |  |  |  | CDC | 379 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
C99 | 南科CS | 161 | 161kV | 1530 | 積E五積E七線(1530) |  | CB | [17 empty] | 1-12-02 | [7 empty] | ADCS_S | [8 empty] | 三福一.1530_CB | 1530(南科三福一線) CB | OTHER |  |  |  |  | CDC | 380 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 0 |  | 1530 | 積E五積E七線(1530) |  | DTTA | [17 empty] | 1-13-06 | [7 empty] | ADCS_S | [8 empty] | 三福一.1530_DTTA | 南科三福一線(1530) 遠方遙跳 | OTHER |  |  |  |  | CDC | 381 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1530 | 積E五積E七線(1530) |  | GDA | [17 empty] | 1-13-04 | [7 empty] | ADCS_S | [8 empty] | 三福一.1530_GDA | 南科三福一線(1530) GDA | OTHER |  |  |  |  | CDC | 382 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1530 | 積E五積E七線(1530) |  | PHA | [17 empty] | 1-13-03 | [7 empty] | ADCS_S | [8 empty] | 三福一.1530_PHA | 南科三福一線(1530) PHA | OTHER |  |  |  |  | CDC | 383 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 161 | 161kV | 1530 | 積E五積E七線(1530) |  | DS1 | 1531 | [16 empty] | 2-3C-12 | [7 empty] | ADCS_S | [8 empty] | 三福一.1531_DS | 1531(南科三福一線) DS | OTHER |  |  |  |  | CDC | 384 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1530 | 積E五積E七線(1530) |  | DS2 | 1532 | [16 empty] | 2-3C-14 | [7 empty] | ADCS_S | [8 empty] | 三福一.1532_DS | 1532(南科三福一線) DS | OTHER |  |  |  |  | CDC | 385 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1530 | 積E五積E七線(1530) |  | E3 | 1533E | [16 empty] | 2-3C-13 | [7 empty] | ADCS_S | [8 empty] | 三福一.1533E_ES | 1533E(南科三福一線) ES | OTHER |  |  |  |  | CDC | 386 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1530 | 積E五積E七線(1530) |  | DS3 | 1533 | [16 empty] | 2-3C-11 | [7 empty] | ADCS_S | [8 empty] | 三福一.1533_DS | 1533(南科三福一線) DS | OTHER |  |  |  |  | CDC | 387 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 0 |  | 15B1E | 15B1E |  | BE1 | 15B1E | [16 empty] | 2-3C-02 | [7 empty] | ADCS_S | [8 empty] | 三福一.15B1E_ES | 15B1E ES | OTHER |  |  |  |  | CDC | 388 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 0 |  | 15B2E | 15B2E |  | BE2 | 15B2E | [16 empty] | 2-3C-03 | [7 empty] | ADCS_S | [8 empty] | 三福一.15B2E_ES | 15B2E ES | OTHER |  |  |  |  | CDC | 389 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | BE0 | 1650BE | [16 empty] | 2-3D-06 | [7 empty] | ADCS_S | [8 empty] | 三福一.1650BE_ES | 1650BE(#1MTR) ES | OTHER |  |  |  |  | CDC | 390 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | TE0 | 1650TE | [16 empty] | 2-3D-07 | [7 empty] | ADCS_S | [8 empty] | 三福一.1650TE_ES | 1650TE(#1MTR) ES | OTHER |  |  |  |  | CDC | 391 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | CB | [17 empty] | 1-13-00 | [7 empty] | ADCS_S | [8 empty] | 三福一.1650_CB | 1650(#1MTR) CB | OTHER |  |  |  |  | CDC | 392 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | DS1 | 1651 | [16 empty] | 2-3D-04 | [7 empty] | ADCS_S | [8 empty] | 三福一.1651_DS | 1651(#1MTR) DS | OTHER |  |  |  |  | CDC | 393 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | DS2 | 1652 | [16 empty] | 2-3D-05 | [7 empty] | ADCS_S | [8 empty] | 三福一.1652_DS | 1652(#1MTR) DS | OTHER |  |  |  |  | CDC | 394 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | BE0 | 1660BE | [16 empty] | 2-3D-10 | [7 empty] | ADCS_S | [8 empty] | 三福一.1660BE_ES | 1660BE(#2MTR) ES | OTHER |  |  |  |  | CDC | 395 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | TE0 | 1660TE | [16 empty] | 2-3D-11 | [7 empty] | ADCS_S | [8 empty] | 三福一.1660TE_ES | 1660TE(#2MTR) ES | OTHER |  |  |  |  | CDC | 396 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | CB | [17 empty] | 1-13-01 | [7 empty] | ADCS_S | [8 empty] | 三福一.1660_CB | 1660(#2MTR) CB | OTHER |  |  |  |  | CDC | 397 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | DS1 | 1661 | [16 empty] | 2-3D-08 | [7 empty] | ADCS_S | [8 empty] | 三福一.1661_DS | 1661(#2MTR) DS | OTHER |  |  |  |  | CDC | 398 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | DS2 | 1662 | [16 empty] | 2-3D-09 | [7 empty] | ADCS_S | [8 empty] | 三福一.1662_DS | 1662(#2MTR) DS | OTHER |  |  |  |  | CDC | 399 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 0 |  |  |  |  | OFA通訊故障 | [17 empty] | 2-3B-13 | [7 empty] | ADCS_S | [8 empty] | 三福一.OFA通訊故障 | OFA光纖通訊故障警報 | OTHER |  |  |  |  | CDC | 400 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 161 | 161kV | BUS | BUS |  | 187UL | [17 empty] | 1-14-04 | [7 empty] | ADCS_S | [8 empty] | 三福一.161KV_187UL | 161KV BUS #1 87U/L | OTHER |  |  |  |  | CDC | 401 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | USE/LOCK | USE
C99 | 南科CS | 161 | 161kV | BUS | BUS |  | 287UL | [17 empty] | 1-14-05 | [7 empty] | ADCS_S | [8 empty] | 三福一.161KV_287UL | 161KV BUS #2 87U/L | OTHER |  |  |  |  | CDC | 402 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | USE/LOCK | USE
C99 | 南科CS | 0 |  | 1500 | TIE(1500) |  | 50A | [17 empty] | 1-18-01 | [7 empty] | ADCS_S | [8 empty] | 積E七.1500_50A | 161KV TIE(1500) 50RY | OTHER |  |  |  |  | CDC | 403 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1500 | TIE(1500) |  | 50UL | [17 empty] | 3-34-00 | [7 empty] | ADCS_S | [8 empty] | 積E七.1500_50UL | 161KV TIE(1500) 50RY UL | OTHER |  |  |  |  | CDC | 404 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | USE/LOCK | USE
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [17 empty] | 1-18-00 | [7 empty] | ADCS_S | [8 empty] | 積E七.1500_CB | 1500(TIE) CB | OTHER |  |  |  |  | CDC | 405 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [16 empty] | 3-35-04 | [7 empty] | ADCS_S | [8 empty] | 積E七.1501E_ES | 1501E ES | OTHER |  |  |  |  | CDC | 406 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [16 empty] | 3-35-02 | [7 empty] | ADCS_S | [8 empty] | 積E七.1501_DS | 1501(TIE) DS | OTHER |  |  |  |  | CDC | 407 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [16 empty] | 3-35-05 | [7 empty] | ADCS_S | [8 empty] | 積E七.1502E_ES | 1502E ES | OTHER |  |  |  |  | CDC | 408 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [16 empty] | 3-35-03 | [7 empty] | ADCS_S | [8 empty] | 積E七.1502_DS | 1502(TIE) DS | OTHER |  |  |  |  | CDC | 409 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | BE10 | 1520BE1 | [16 empty] | 3-36-03 | [7 empty] | ADCS_S | [8 empty] | 積E七.1520BE1_ES | 1520BE1(三福一積E七線) ES | OTHER |  |  |  |  | CDC | 410 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | BE20 | 1520BE2 | [16 empty] | 3-36-05 | [7 empty] | ADCS_S | [8 empty] | 積E七.1520BE2_ES | 1520BE2(三福一積E七線) ES | OTHER |  |  |  |  | CDC | 411 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | LE0 | 1520LE | [16 empty] | 3-36-04 | [7 empty] | ADCS_S | [8 empty] | 積E七.1520LE_ES | 1520LE(三福一積E七線) ES | OTHER |  |  |  |  | CDC | 412 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 0 |  | 1520 | 積十四積六線(1520) |  | 87A | [17 empty] | 1-18-05 | [7 empty] | ADCS_S | [8 empty] | 積E七.1520_87A | 1520(三福一積E七線) 87RY | OTHER |  |  |  |  | CDC | 413 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1520 | 積十四積六線(1520) |  | 87UL | [17 empty] | 3-34-02 | [7 empty] | ADCS_S | [8 empty] | 積E七.1520_87UL | 1520(三福一積E七線) 87RY U/L | OTHER |  |  |  |  | CDC | 414 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | USE/LOCK | USE
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | CB | [17 empty] | 1-18-04 | [7 empty] | ADCS_S | [8 empty] | 積E七.1520_CB | 1520(三福一積E七線) CB | OTHER |  |  |  |  | CDC | 415 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | DS1 | 1521 | [16 empty] | 3-36-00 | [7 empty] | ADCS_S | [8 empty] | 積E七.1521_DS | 1521(三福一積E七線) DS | OTHER |  |  |  |  | CDC | 416 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | DS2 | 1522 | [16 empty] | 3-36-02 | [7 empty] | ADCS_S | [8 empty] | 積E七.1522_DS | 1522(三福一積E七線) DS | OTHER |  |  |  |  | CDC | 417 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | E3 | 1523E | [16 empty] | 3-36-01 | [7 empty] | ADCS_S | [8 empty] | 積E七.1523E_ES | 1523E(三福一積E七線) ES | OTHER |  |  |  |  | CDC | 418 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | DS3 | 1523 | [16 empty] | 3-35-15 | [7 empty] | ADCS_S | [8 empty] | 積E七.1523_DS | 1523(三福一積E七線) DS | OTHER |  |  |  |  | CDC | 419 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1530 | 積E五積E七線(1530) |  | BE10 | 1530BE1 | [16 empty] | 3-35-12 | [7 empty] | ADCS_S | [8 empty] | 積E七.1530BE1_ES | 1530BE1(積E五積E七線) ES | OTHER |  |  |  |  | CDC | 420 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1530 | 積E五積E七線(1530) |  | BE20 | 1530BE2 | [16 empty] | 3-35-14 | [7 empty] | ADCS_S | [8 empty] | 積E七.1530BE2_ES | 1530BE2(積E五積E七線) ES | OTHER |  |  |  |  | CDC | 421 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1530 | 積E五積E七線(1530) |  | LE0 | 1530LE | [16 empty] | 3-35-13 | [7 empty] | ADCS_S | [8 empty] | 積E七.1530LE_ES | 1530LE(積E五積E七線) ES | OTHER |  |  |  |  | CDC | 422 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 0 |  | 1530 | 積E五積E七線(1530) |  | 87A | [17 empty] | 1-18-03 | [7 empty] | ADCS_S | [8 empty] | 積E七.1530_87A | 1530(積E五積E七線) 87RY | OTHER |  |  |  |  | CDC | 423 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1530 | 積E五積E七線(1530) |  | 87UL | [17 empty] | 3-34-01 | [7 empty] | ADCS_S | [8 empty] | 積E七.1530_87UL | 1530(積E五積E七線) 87RY U/L | OTHER |  |  |  |  | CDC | 424 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | USE/LOCK | USE
C99 | 南科CS | 161 | 161kV | 1530 | 積E五積E七線(1530) |  | CB | [17 empty] | 1-18-02 | [7 empty] | ADCS_S | [8 empty] | 積E七.1530_CB | 1530(積E五積E七線) CB | OTHER |  |  |  |  | CDC | 425 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1530 | 積E五積E七線(1530) |  | DS1 | 1531 | [16 empty] | 3-35-09 | [7 empty] | ADCS_S | [8 empty] | 積E七.1531_DS | 1531(積E五積E七線) DS | OTHER |  |  |  |  | CDC | 426 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1530 | 積E五積E七線(1530) |  | DS2 | 1532 | [16 empty] | 3-35-11 | [7 empty] | ADCS_S | [8 empty] | 積E七.1532_DS | 1532(積E五積E七線) DS | OTHER |  |  |  |  | CDC | 427 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1530 | 積E五積E七線(1530) |  | E3 | 1533E | [16 empty] | 3-35-10 | [7 empty] | ADCS_S | [8 empty] | 積E七.1533E_ES | 1533E(積E五積E七線) ES | OTHER |  |  |  |  | CDC | 428 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1530 | 積E五積E七線(1530) |  | DS3 | 1533 | [16 empty] | 3-35-08 | [7 empty] | ADCS_S | [8 empty] | 積E七.1533_DS | 1533(積E五積E七線) DS | OTHER |  |  |  |  | CDC | 429 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 0 |  | 15B1E | 15B1E |  | BE1 | 15B1E | [16 empty] | 3-35-06 | [7 empty] | ADCS_S | [8 empty] | 積E七.15B1E_ES | 15B1E ES | OTHER |  |  |  |  | CDC | 430 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 0 |  | 15B2E | 15B2E |  | BE2 | 15B2E | [16 empty] | 3-35-07 | [7 empty] | ADCS_S | [8 empty] | 積E七.15B2E_ES | 15B2E ES | OTHER |  |  |  |  | CDC | 431 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | BE10 | 1650BE1 | [16 empty] | 3-36-10 | [7 empty] | ADCS_S | [8 empty] | 積E七.1650BE1_ES | 1650BE1(#1MTR) ES | OTHER |  |  |  |  | CDC | 432 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | BE20 | 1650BE2 | [16 empty] | 3-36-11 | [7 empty] | ADCS_S | [8 empty] | 積E七.1650BE2_ES | 1650BE2(#1MTR) ES | OTHER |  |  |  |  | CDC | 433 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | TE0 | 1650TE | [16 empty] | 3-36-12 | [7 empty] | ADCS_S | [8 empty] | 積E七.1650TE_ES | 1650TE(#1MTR) ES | OTHER |  |  |  |  | CDC | 434 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | CB | [17 empty] | 1-19-00 | [7 empty] | ADCS_S | [8 empty] | 積E七.1650_CB | 1650(#1MTR) CB | OTHER |  |  |  |  | CDC | 435 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | DS1 | 1651 | [16 empty] | 3-36-08 | [7 empty] | ADCS_S | [8 empty] | 積E七.1651_DS | 1651(#1MTR) DS | OTHER |  |  |  |  | CDC | 436 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | DS2 | 1652 | [16 empty] | 3-36-09 | [7 empty] | ADCS_S | [8 empty] | 積E七.1652_DS | 1652(#1MTR) DS | OTHER |  |  |  |  | CDC | 437 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | BE10 | 1660BE1 | [16 empty] | 3-36-15 | [7 empty] | ADCS_S | [8 empty] | 積E七.1660BE1_ES | 1660BE1(#2MTR) ES | OTHER |  |  |  |  | CDC | 438 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | BE20 | 1660BE2 | [16 empty] | 3-37-00 | [7 empty] | ADCS_S | [8 empty] | 積E七.1660BE2_ES | 1660BE2(#2MTR) ES | OTHER |  |  |  |  | CDC | 439 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | TE0 | 1660TE | [16 empty] | 3-37-01 | [7 empty] | ADCS_S | [8 empty] | 積E七.1660TE_ES | 1660TE(#2MTR) ES | OTHER |  |  |  |  | CDC | 440 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | CB | [17 empty] | 1-19-02 | [7 empty] | ADCS_S | [8 empty] | 積E七.1660_CB | 1660(#2MTR) CB | OTHER |  |  |  |  | CDC | 441 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | DS1 | 1661 | [16 empty] | 3-36-13 | [7 empty] | ADCS_S | [8 empty] | 積E七.1661_DS | 1661(#2MTR) DS | OTHER |  |  |  |  | CDC | 442 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | DS2 | 1662 | [16 empty] | 3-36-14 | [7 empty] | ADCS_S | [8 empty] | 積E七.1662_DS | 1662(#2MTR) DS | OTHER |  |  |  |  | CDC | 443 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1670 | #3DTR(1670) |  | BE10 | 1670BE1 | [16 empty] | 3-37-04 | [7 empty] | ADCS_S | [8 empty] | 積E七.1670BE1_ES | 1670BE1(#3MTR) ES | OTHER |  |  |  |  | CDC | 444 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1670 | #3DTR(1670) |  | BE20 | 1670BE2 | [16 empty] | 3-37-05 | [7 empty] | ADCS_S | [8 empty] | 積E七.1670BE2_ES | 1670BE2(#3MTR) ES | OTHER |  |  |  |  | CDC | 445 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1670 | #3DTR(1670) |  | TE0 | 1670TE | [16 empty] | 3-37-06 | [7 empty] | ADCS_S | [8 empty] | 積E七.1670TE_ES | 1670TE(#3MTR) ES | OTHER |  |  |  |  | CDC | 446 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1670 | #3DTR(1670) |  | CB | [17 empty] | 1-19-04 | [7 empty] | ADCS_S | [8 empty] | 積E七.1670_CB | 1670(#3MTR) CB | OTHER |  |  |  |  | CDC | 447 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1670 | #3DTR(1670) |  | DS1 | 1671 | [16 empty] | 3-37-02 | [7 empty] | ADCS_S | [8 empty] | 積E七.1671_DS | 1671(#3MTR) DS | OTHER |  |  |  |  | CDC | 448 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1670 | #3DTR(1670) |  | DS2 | 1672 | [16 empty] | 3-37-03 | [7 empty] | ADCS_S | [8 empty] | 積E七.1672_DS | 1672(#3MTR) DS | OTHER |  |  |  |  | CDC | 449 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1680 | #4DTR(1680) |  | BE10 | 1680BE1 | [16 empty] | 3-37-09 | [7 empty] | ADCS_S | [8 empty] | 積E七.1680BE1_ES | 1680BE1(#4MTR) ES | OTHER |  |  |  |  | CDC | 450 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1680 | #4DTR(1680) |  | BE20 | 1680BE2 | [16 empty] | 3-37-10 | [7 empty] | ADCS_S | [8 empty] | 積E七.1680BE2_ES | 1680BE2(#4MTR) ES | OTHER |  |  |  |  | CDC | 451 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1680 | #4DTR(1680) |  | TE0 | 1680TE | [16 empty] | 3-37-11 | [7 empty] | ADCS_S | [8 empty] | 積E七.1680TE_ES | 1680TE(#4MTR) ES | OTHER |  |  |  |  | CDC | 452 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1680 | #4DTR(1680) |  | CB | [17 empty] | 1-19-06 | [7 empty] | ADCS_S | [8 empty] | 積E七.1680_CB | 1680(#4MTR) CB | OTHER |  |  |  |  | CDC | 453 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1680 | #4DTR(1680) |  | DS1 | 1681 | [16 empty] | 3-37-07 | [7 empty] | ADCS_S | [8 empty] | 積E七.1681_DS | 1681(#4MTR) DS | OTHER |  |  |  |  | CDC | 454 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1680 | #4DTR(1680) |  | DS2 | 1682 | [16 empty] | 3-37-08 | [7 empty] | ADCS_S | [8 empty] | 積E七.1682_DS | 1682(#4MTR) DS | OTHER |  |  |  |  | CDC | 455 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 0 |  |  |  |  | OFA通訊故障 | [17 empty] | 3-35-01 | [7 empty] | ADCS_S | [8 empty] | 積E七.OFA通訊故障 | OFA光纖通訊故障警報 | OTHER |  |  |  |  | CDC | 456 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1MTR | #1MTR |  | 87A | [17 empty] | 1-19-01 | [7 empty] | ADCS_S | [8 empty] | 積E七.#1MTR_87A | #1MTR 87RY | OTHER |  |  |  |  | CDC | 457 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1MTR | #1MTR |  | 87UL | [17 empty] | 3-34-03 | [7 empty] | ADCS_S | [8 empty] | 積E七.#1MTR_87UL | #1MTR 87RY U/L | OTHER |  |  |  |  | CDC | 458 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | USE/LOCK | USE
C99 | 南科CS | 0 |  | 2MTR | #2MTR |  | 87A | [17 empty] | 1-19-03 | [7 empty] | ADCS_S | [8 empty] | 積E七.#2MTR_87A | #2MTR 87RY | OTHER |  |  |  |  | CDC | 459 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 2MTR | #2MTR |  | 87UL | [17 empty] | 3-34-04 | [7 empty] | ADCS_S | [8 empty] | 積E七.#2MTR_87UL | #2MTR 87RY U/L | OTHER |  |  |  |  | CDC | 460 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | USE/LOCK | USE
C99 | 南科CS | 0 |  | 3MTR | #3MTR |  | 87A | [17 empty] | 1-19-05 | [7 empty] | ADCS_S | [8 empty] | 積E七.#3MTR_87A | #3MTR 87RY | OTHER |  |  |  |  | CDC | 461 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 3MTR | #3MTR |  | 87UL | [17 empty] | 3-34-05 | [7 empty] | ADCS_S | [8 empty] | 積E七.#3MTR_87UL | #3MTR 87RY U/L | OTHER |  |  |  |  | CDC | 462 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | USE/LOCK | USE
C99 | 南科CS | 0 |  | 4MTR | #4MTR |  | 87A | [17 empty] | 1-19-07 | [7 empty] | ADCS_S | [8 empty] | 積E七.#4MTR_87A | #4MTR 87RY | OTHER |  |  |  |  | CDC | 463 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 4MTR | #4MTR |  | 87UL | [17 empty] | 3-34-06 | [7 empty] | ADCS_S | [8 empty] | 積E七.#4MTR_87UL | #4MTR 87RY U/L | OTHER |  |  |  |  | CDC | 464 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | USE/LOCK | USE
C99 | 南科CS | 0 |  | 1500 | TIE(1500) |  | 50A | [17 empty] | 1-15-01 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1500_50A | 161KV TIE(1500) 50RY | OTHER |  |  |  |  | CDC | 465 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [17 empty] | 1-15-00 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1500_CB | 1500(TIE) CB | OTHER |  |  |  |  | CDC | 466 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [16 empty] | 3-30-04 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1501E_ES | 1501E ES | OTHER |  |  |  |  | CDC | 467 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [16 empty] | 3-30-02 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1501_DS | 1501(TIE) DS | OTHER |  |  |  |  | CDC | 468 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [16 empty] | 3-30-05 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1502E_ES | 1502E ES | OTHER |  |  |  |  | CDC | 469 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [16 empty] | 3-30-03 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1502_DS | 1502(TIE) DS | OTHER |  |  |  |  | CDC | 470 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1510 | 和鑫二積P3線(1510) |  | BE10 | 1510BE1 | [16 empty] | 3-31-00 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1510BE1_ES | 1510BE1(和鑫二積P3線) ES | OTHER |  |  |  |  | CDC | 471 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1510 | 和鑫二積P3線(1510) |  | BE20 | 1510BE2 | [16 empty] | 3-31-01 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1510BE2_ES | 1510BE2(和鑫二積P3線) ES | OTHER |  |  |  |  | CDC | 472 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1510 | 和鑫二積P3線(1510) |  | LE0 | 1510LE | [16 empty] | 3-30-15 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1510LE_ES | 1510LE(和鑫二積P3線) ES | OTHER |  |  |  |  | CDC | 473 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 0 |  | 1510 | 和鑫二積P3線(1510) |  | 87A | [17 empty] | 1-15-03 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1510_87A | 1510(和鑫二積P3線) 87RY | OTHER |  |  |  |  | CDC | 474 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 161 | 161kV | 1510 | 和鑫二積P3線(1510) |  | CB | [17 empty] | 1-15-02 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1510_CB | 1510(和鑫二積P3線) CB | OTHER |  |  |  |  | CDC | 475 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1510 | 和鑫二積P3線(1510) |  | DS1 | 1511 | [16 empty] | 3-30-10 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1511_DS | 1511(和鑫二積P3線) DS | OTHER |  |  |  |  | CDC | 476 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1510 | 和鑫二積P3線(1510) |  | DS2 | 1512 | [16 empty] | 3-30-11 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1512_DS | 1512(和鑫二積P3線) DS | OTHER |  |  |  |  | CDC | 477 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1510 | 和鑫二積P3線(1510) |  | E13 | 1513E1 | [16 empty] | 3-30-12 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1513E1_ES | 1513E1(和鑫二積P3線) ES | OTHER |  |  |  |  | CDC | 478 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1510 | 和鑫二積P3線(1510) |  | E23 | 1513E2 | [16 empty] | 3-30-14 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1513E2_ES | 1513E2(和鑫二積P3線) ES | OTHER |  |  |  |  | CDC | 479 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1510 | 和鑫二積P3線(1510) |  | DS3 | 1513 | [16 empty] | 3-30-08 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1513_DS | 1513(和鑫二積P3線) DS | OTHER |  |  |  |  | CDC | 480 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1510 | 和鑫二積P3線(1510) |  | E4 | 1514E | [16 empty] | 3-30-13 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1514E_ES | 1514E(和鑫二積P3線) ES | OTHER |  |  |  |  | CDC | 481 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1510 | 和鑫二積P3線(1510) |  | DS4 | 1514 | [16 empty] | 3-30-09 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1514_DS | 1514(和鑫二積P3線) DS | OTHER |  |  |  |  | CDC | 482 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | BE10 | 1520BE1 | [16 empty] | 3-31-10 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1520BE1_ES | 1520BE1(南科和鑫二線) ES | OTHER |  |  |  |  | CDC | 483 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | BE20 | 1520BE2 | [16 empty] | 3-31-11 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1520BE2_ES | 1520BE2(南科和鑫二線) ES | OTHER |  |  |  |  | CDC | 484 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | LE0 | 1520LE | [16 empty] | 3-31-09 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1520LE_ES | 1520LE(南科和鑫二線) ES | OTHER |  |  |  |  | CDC | 485 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 0 |  | 1520 | 積十四積六線(1520) |  | 87A | [17 empty] | 1-15-05 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1520_87A | 1520(南科和鑫二線) 87RY | OTHER |  |  |  |  | CDC | 486 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | CB | [17 empty] | 1-15-04 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1520_CB | 1520(南科和鑫二線) CB | OTHER |  |  |  |  | CDC | 487 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | DS1 | 1521 | [16 empty] | 3-31-04 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1521_DS | 1521(南科和鑫二線) DS | OTHER |  |  |  |  | CDC | 488 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | DS2 | 1522 | [16 empty] | 3-31-05 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1522_DS | 1522(南科和鑫二線) DS | OTHER |  |  |  |  | CDC | 489 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | E13 | 1523E1 | [16 empty] | 3-31-06 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1523E1_ES | 1523E1(南科和鑫二線) ES | OTHER |  |  |  |  | CDC | 490 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | E23 | 1523E2 | [16 empty] | 3-31-08 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1523E2_ES | 1523E2(南科和鑫二線) ES | OTHER |  |  |  |  | CDC | 491 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | DS3 | 1523 | [16 empty] | 3-31-02 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1523_DS | 1523(南科和鑫二線) DS | OTHER |  |  |  |  | CDC | 492 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | E4 | 1524E | [16 empty] | 3-31-07 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1524E_ES | 1524E(南科和鑫二線) ES | OTHER |  |  |  |  | CDC | 493 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1520 | 積十四積六線(1520) |  | DS4 | 1524 | [16 empty] | 3-31-03 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1524_DS | 1524(南科和鑫二線) DS | OTHER |  |  |  |  | CDC | 494 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 0 |  | 15B1E | 15B1E |  | BE1 | 15B1E | [16 empty] | 3-30-06 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.15B1E_ES | 15B1E ES | OTHER |  |  |  |  | CDC | 495 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 0 |  | 15B2E | 15B2E |  | BE2 | 15B2E | [16 empty] | 3-30-07 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.15B2E_ES | 15B2E ES | OTHER |  |  |  |  | CDC | 496 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | BE10 | 1650BE1 | [16 empty] | 3-32-02 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1650BE1_ES | 1650BE1(#1MTR) ES | OTHER |  |  |  |  | CDC | 497 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | BE20 | 1650BE2 | [16 empty] | 3-32-03 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1650BE2_ES | 1650BE2(#1MTR) ES | OTHER |  |  |  |  | CDC | 498 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | TE0 | 1650TE | [16 empty] | 3-32-04 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1650TE_ES | 1650TE(#1MTR) ES | OTHER |  |  |  |  | CDC | 499 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | CB | [17 empty] | 1-16-00 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1650_CB | 1650(#1MTR) CB | OTHER |  |  |  |  | CDC | 500 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | DS1 | 1651 | [16 empty] | 3-32-00 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1651_DS | 1651(#1MTR) DS | OTHER |  |  |  |  | CDC | 501 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1650 | #1DTR(1650) |  | DS2 | 1652 | [16 empty] | 3-32-01 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1652_DS | 1652(#1MTR) DS | OTHER |  |  |  |  | CDC | 502 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | BE10 | 1660BE1 | [16 empty] | 3-32-07 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1660BE1_ES | 1660BE1(#2MTR) ES | OTHER |  |  |  |  | CDC | 503 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | BE20 | 1660BE2 | [16 empty] | 3-32-08 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1660BE2_ES | 1660BE2(#2MTR) ES | OTHER |  |  |  |  | CDC | 504 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | TE0 | 1660TE | [16 empty] | 3-32-09 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1660TE_ES | 1660TE(#2MTR) ES | OTHER |  |  |  |  | CDC | 505 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | CB | [17 empty] | 1-16-02 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1660_CB | 1660(#2MTR) CB | OTHER |  |  |  |  | CDC | 506 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | DS1 | 1661 | [16 empty] | 3-32-05 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1661_DS | 1661(#2MTR) DS | OTHER |  |  |  |  | CDC | 507 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
C99 | 南科CS | 161 | 161kV | 1660 | #2DTR(1660) |  | DS2 | 1662 | [16 empty] | 3-32-06 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1662_DS | 1662(#2MTR) DS | OTHER |  |  |  |  | CDC | 508 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
C99 | 南科CS | 0 |  |  |  |  | OFA通訊故障 | [17 empty] | 3-30-01 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.OFA通訊故障 | OFA光纖通訊故障警報 | OTHER |  |  |  |  | CDC | 509 | GENERICDIPoint | CS001_L3 | CDC2_DI |  | DI | D_KEY | [33 empty] | ALARM/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1510 | 和鑫二積P3線(1510) |  | 1_87UL1 | [17 empty] | 2-3F-01 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1510_87UL1 | 1510(和鑫二積P3線) #1 87U/L | OTHER |  |  |  |  | CDC | 510 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
C99 | 南科CS | 0 |  | 1510 | 和鑫二積P3線(1510) |  | 1_87UL2 | [17 empty] | 2-3F-02 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1510_87UL2 | 1510(和鑫二積P3線) #2 87U/L | OTHER |  |  |  |  | CDC | 511 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
C99 | 南科CS | 0 |  | 1520 | 積十四積六線(1520) |  | 1_87UL1 | [17 empty] | 2-3F-03 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1520_87UL1 | 1520(南科和鑫二線) #1 87U/L | OTHER |  |  |  |  | CDC | 512 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
C99 | 南科CS | 0 |  | 1520 | 積十四積六線(1520) |  | 1_87UL2 | [17 empty] | 2-3F-04 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.1520_87UL2 | 1520(南科和鑫二線) #2 87U/L | OTHER |  |  |  |  | CDC | 513 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
C99 | 南科CS | 161 | 161kV | BUS | BUS |  | 187UL | [17 empty] | 2-3F-05 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.161KV_187UL | 161KV BUS #1 87U/L | OTHER |  |  |  |  | CDC | 514 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | USE/LOCK | USE
C99 | 南科CS | 161 | 161kV | BUS | BUS |  | 287UL | [17 empty] | 2-3F-06 | [7 empty] | ADCS_S | [8 empty] | 和鑫二.161KV_287UL | 161KV BUS #2 87U/L | OTHER |  |  |  |  | CDC | 515 | GENERICDIPoint | CS001_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | USE/LOCK | USE
C99 | 南科CS | 0 |  | 1730 | 南科積六線(1730) |  | 1_87UL1 | [17 empty] | 1-30-10 | [7 empty] | ADCS_S | [8 empty] | 積六CS.1730_87UL1 | 南科積六線(1730) 87RY1 U/L | OTHER |  |  |  |  | CDC | 516 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
C99 | 南科CS | 0 |  | 1730 | 南科積六線(1730) |  | 1_87UL2 | [17 empty] | 1-30-11 | [7 empty] | ADCS_S | [8 empty] | 積六CS.1730_87UL2 | 南科積六線(1730) 87RY2 U/L | OTHER |  |  |  |  | CDC | 517 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
C99 | 南科CS | 0 |  | 1730 | 南科積六線(1730) |  | 87A1 | [17 empty] | 1-00-05 | [7 empty] | ADCS_S | [8 empty] | 積六CS.1730_87A1 | 1730(南科積六線) 87RY1 | OTHER |  |  |  |  | CDC | 518 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1730 | 南科積六線(1730) |  | 87A2 | [17 empty] | 1-00-06 | [7 empty] | ADCS_S | [8 empty] | 積六CS.1730_87A2 | 1730(南科積六線) 87RY2 | OTHER |  |  |  |  | CDC | 519 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1720 | 積十四積六線(1720) |  | 87A1 | [17 empty] | 1-00-03 | [7 empty] | ADCS_S | [8 empty] | 積六CS.1720_87A1 | 1720(積十四積六線) 87RY1 | OTHER |  |  |  |  | CDC | 520 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1720 | 積十四積六線(1720) |  | 87A2 | [17 empty] | 1-00-07 | [7 empty] | ADCS_S | [8 empty] | 積六CS.1720_87A2 | 1720(積十四積六線) 87RY2 | OTHER |  |  |  |  | CDC | 521 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1720 | 積十四積六線(1720) |  | 1_87UL1 | [17 empty] | 1-30-01 | [7 empty] | ADCS_S | [8 empty] | 積六CS.1720_87UL1 | 1720(積十四積六線) 87RY1 U/L | OTHER |  |  |  |  | CDC | 522 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
C99 | 南科CS | 0 |  | 1720 | 積十四積六線(1720) |  | 1_87UL2 | [17 empty] | 1-30-02 | [7 empty] | ADCS_S | [8 empty] | 積六CS.1720_87UL2 | 1720(積十四積六線) 87RY2 U/L | OTHER |  |  |  |  | CDC | 523 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
C99 | 南科CS | 0 |  | 1520 | 積十四積六線(1520) |  | 87A1 | [17 empty] | 1-03-03 | [7 empty] | ADCS_S | [8 empty] | 積十四.1520_87A1 | 1520(積十四積六線) 87RY1 | OTHER |  |  |  |  | CDC | 524 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1520 | 積十四積六線(1520) |  | 87A2 | [17 empty] | 1-03-06 | [7 empty] | ADCS_S | [8 empty] | 積十四.1520_87A2 | 1520(積十四積六線) 87RY2 | OTHER |  |  |  |  | CDC | 525 | GENERICDIPoint | CS001_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | TRIP/NORMAL | NORMAL
C99 | 南科CS | 0 |  | 1520 | 積十四積六線(1520) |  | 1_87UL1 | [17 empty] | 1-35-02 | [7 empty] | ADCS_S | [8 empty] | 積十四.1520_87UL1 | 1520(積十四積六線) 87RY1 U/L | OTHER |  |  |  |  | CDC | 526 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | USE/LOCK | USE
C99 | 南科CS | 0 |  | 1520 | 積十四積六線(1520) |  | 1_87UL2 | [17 empty] | 1-35-03 | [7 empty] | ADCS_S | [8 empty] | 積十四.1520_87UL2 | 1520(積十四積六線) 87RY2 U/L | OTHER |  |  |  |  | CDC | 527 | GENERICDIPoint | CS001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | USE/LOCK | USE
C05 | 積六CS | 161 | 161kV | 2BUS | #2BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 積六CS.161KV#2BUS_KV | 161KV #2BUS KV | BUS |  |  | BUS_CAL_V |  |  | 528 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
C04 | 積十四CS | 161 | 161kV | 2BUS | #2BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 積十四.161KV#2BUS_KV | 161KV #2BUS KV | BUS |  |  | BUS_CAL_V |  |  | 529 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
C02 | 康寧CS | 161 | 161kV | 2BUS | #2BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 康寧CS.161KV#2BUS_KV | 161KV #2BUS KV | BUS |  |  | BUS_CAL_V |  |  | 530 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
C03 | 積P3CS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 積P3CS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | C03/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 531 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
C08 | 積E五CS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 積E五.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | C08/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 532 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
C09 | 積E六CS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 積E六.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | C09/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 533 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
C06 | 三福一CS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 三福一.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | C06/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 534 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
C07 | 積E七CS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 積E七.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | C07/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 535 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
C01 | 和鑫二CS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 和鑫二.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | C01/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 536 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo