## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D03 | 南濱DS | 161 | 161kV | 1510 | 安南～南濱一路(1510) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_A1 | [8 empty] | 南濱DS.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 2 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1510 | 安南～南濱一路(1510) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_A1 | [8 empty] | 南濱DS.1510BE | 1510BE (非取樣點) | LINE161 | [5 empty] | 3 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1520 | 安南～南濱二路(1520) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_A1 | [8 empty] | 南濱DS.1520LE | 1520LE (非取樣點) | LINE161 | [5 empty] | 4 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1520 | 安南～南濱二路(1520) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_A1 | [8 empty] | 南濱DS.1520BE | 1520BE (非取樣點) | LINE161 | [5 empty] | 5 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱～安瀚線(1530) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_A1 | [8 empty] | 南濱DS.1530LE | 1530LE (非取樣點) | LINE161 | [5 empty] | 6 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱～安瀚線(1530) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_A1 | [8 empty] | 南濱DS.1530BE | 1530BE (非取樣點) | LINE161 | [5 empty] | 7 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱～凸版線(1540) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_A1 | [8 empty] | 南濱DS.1540LE | 1540LE (非取樣點) | LINE161 | [5 empty] | 8 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱～凸版線(1540) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_A1 | [8 empty] | 南濱DS.1540BE | 1540BE (非取樣點) | LINE161 | [5 empty] | 9 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1550 | 南濱～鹿耳紅線(1550) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_A1 | [8 empty] | 南濱DS.1550LE | 1550LE (非取樣點) | LINE161 | [5 empty] | 10 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1550 | 南濱～鹿耳紅線(1550) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_A1 | [8 empty] | 南濱DS.1550BE | 1550BE (非取樣點) | LINE161 | [5 empty] | 11 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1560 | 南濱～鹿耳白線(1560) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_A1 | [8 empty] | 南濱DS.1560LE | 1560LE (非取樣點) | LINE161 | [5 empty] | 12 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1560 | 南濱～鹿耳白線(1560) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_A1 | [8 empty] | 南濱DS.1560BE | 1560BE (非取樣點) | LINE161 | [5 empty] | 13 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_A1 | [8 empty] | 南濱DS.1501E | 1501E (非取樣點) | TIE | [5 empty] | 14 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_A1 | [8 empty] | 南濱DS.1502E | 1502E (非取樣點) | TIE | [5 empty] | 15 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_A1 | [8 empty] | 南濱DS.1750TE | 1750TE (非取樣點) | MTR | [5 empty] | 16 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_A1 | [8 empty] | 南濱DS.1750BE | 1750BE (非取樣點) | MTR | [5 empty] | 17 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | D1 | 311(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.311 | 311 (非取樣點) | MTR | [5 empty] | 18 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | E1 | 311E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.311E | 311E (非取樣點) | MTR | [5 empty] | 19 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | D1 | 321(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.321 | 321 (非取樣點) | MTR | [5 empty] | 20 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | E1 | 321E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.321E | 321E (非取樣點) | MTR | [5 empty] | 21 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_A1 | [8 empty] | 南濱DS.1760TE | 1760TE (非取樣點) | MTR | [5 empty] | 22 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_A1 | [8 empty] | 南濱DS.1760BE | 1760BE (非取樣點) | MTR | [5 empty] | 23 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | D1 | 331(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.331 | 331 (非取樣點) | MTR | [5 empty] | 24 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | E1 | 331E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.331E | 331E (非取樣點) | MTR | [5 empty] | 25 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | D1 | 341(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.341 | 341 (非取樣點) | MTR | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | E1 | 341E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.341E | 341E (非取樣點) | MTR | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_A1 | [8 empty] | 南濱DS.1770TE | 1770TE (非取樣點) | MTR | [5 empty] | 28 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_A1 | [8 empty] | 南濱DS.1770BE | 1770BE (非取樣點) | MTR | [5 empty] | 29 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 22 | 22kV | 350 | #3DTR(350) |  | D1 | 351(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.351 | 351 (非取樣點) | MTR | [5 empty] | 30 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | 350 | #3DTR(350) |  | E1 | 351E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.351E | 351E (非取樣點) | MTR | [5 empty] | 31 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1780 | #4DTR(1780) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_A1 | [8 empty] | 南濱DS.1780TE | 1780TE (非取樣點) | MTR | [5 empty] | 32 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1780 | #4DTR(1780) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_A1 | [8 empty] | 南濱DS.1780BE | 1780BE (非取樣點) | MTR | [5 empty] | 33 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 22 | 22kV | 370 | #4DTR(370) |  | D1 | 371(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.371 | 371 (非取樣點) | MTR | [5 empty] | 34 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | 370 | #4DTR(370) |  | E1 | 371E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.371E | 371E (非取樣點) | MTR | [5 empty] | 35 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | 210 | #1SC(210) |  | E1 | 211E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.211E | 211E (非取樣點) | SC | [5 empty] | 36 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | 210 | #1SC(210) |  | DS1 | 211(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.211 | 211 (非取樣點) | SC | [5 empty] | 37 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K311 | 濱11線(K311) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K311_DS | K311_DS (非取樣點) | FEEDER | [5 empty] | 38 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K311 | 濱11線(K311) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K311_ES | K311_ES (非取樣點) | FEEDER | [5 empty] | 39 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | K312 | 濱12線(K312) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K312_DS | K312_DS (非取樣點) | FEEDER | [5 empty] | 40 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K312 | 濱12線(K312) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K312_ES | K312_ES (非取樣點) | FEEDER | [5 empty] | 41 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | K313 | 濱13線(K313) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K313_DS | K313_DS (非取樣點) | FEEDER | [5 empty] | 42 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K313 | 濱13線(K313) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K313_ES | K313_ES (非取樣點) | FEEDER | [5 empty] | 43 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | K314 | 濱14線(K314) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K314_DS | K314_DS (非取樣點) | FEEDER | [5 empty] | 44 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K314 | 濱14線(K314) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K314_ES | K314_ES (非取樣點) | FEEDER | [5 empty] | 45 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | K315 | 濱15線(K315) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K315_DS | K315_DS (非取樣點) | FEEDER | [5 empty] | 46 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K315 | 濱15線(K315) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K315_ES | K315_ES (非取樣點) | FEEDER | [5 empty] | 47 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | 100 | TIE(100) |  | D1 | 101(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.101 | 101 (非取樣點) | TIE | [5 empty] | 48 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | 100 | TIE(100) |  | D2 | 102(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.102 | 102 (非取樣點) | TIE | [5 empty] | 49 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | 100 | TIE(100) |  | E1 | 101E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.101E | 101E(非取樣點) | OTHER | [5 empty] | 50 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | 100 | TIE(100) |  | E2 | 102E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.102E | 102E(非取樣點) | OTHER | [5 empty] | 51 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | 390 | #1SSTR(390) |  | D1 | 391(非取樣點) | B3 | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.391 | 391 (非取樣點) | OTHER | [5 empty] | 52 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | 390 | #1SSTR(390) |  | E1 | 391E(非取樣點) | B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.391E | 391E (非取樣點) | OTHER | [5 empty] | 53 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | 220 | #2SC(220) |  | E1 | 221E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.221E | 221E (非取樣點) | SC | [5 empty] | 54 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | 220 | #2SC(220) |  | DS1 | 221(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.221 | 221 (非取樣點) | SC | [5 empty] | 55 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K316 | 濱16線(K316) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K316_DS | K316_DS (非取樣點) | FEEDER | [5 empty] | 56 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K316 | 濱16線(K316) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K316_ES | K316_ES (非取樣點) | FEEDER | [5 empty] | 57 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | K317 | 濱17線(K317) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K317_DS | K317_DS (非取樣點) | FEEDER | [5 empty] | 58 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K317 | 濱17線(K317) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K317_ES | K317_ES (非取樣點) | FEEDER | [5 empty] | 59 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | K318 | 濱18線(K318) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K318_DS | K318_DS (非取樣點) | FEEDER | [5 empty] | 60 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K318 | 濱18線(K318) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K318_ES | K318_ES (非取樣點) | FEEDER | [5 empty] | 61 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | K319 | 濱19線(K319) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K319_DS | K319_DS (非取樣點) | FEEDER | [5 empty] | 62 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K319 | 濱19線(K319) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K319_ES | K319_ES (非取樣點) | FEEDER | [5 empty] | 63 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | K320 | 濱20線(K320) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K320_DS | K320_DS (非取樣點) | FEEDER | [5 empty] | 64 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K320 | 濱20線(K320) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K320_ES | K320_ES (非取樣點) | FEEDER | [5 empty] | 65 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | 230 | #3SC(230) |  | E1 | 231E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.231E | 231E (非取樣點) | SC | [5 empty] | 66 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | 230 | #3SC(230) |  | DS1 | 231(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.231 | 231 (非取樣點) | SC | [5 empty] | 67 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K321 | 濱21線(K321) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K321_DS | K321_DS (非取樣點) | FEEDER | [5 empty] | 68 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K321 | 濱21線(K321) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K321_ES | K321_ES (非取樣點) | FEEDER | [5 empty] | 69 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | K322 | 濱22線(K322) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K322_DS | K322_DS (非取樣點) | FEEDER | [5 empty] | 70 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K322 | 濱22線(K322) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K322_ES | K322_ES (非取樣點) | FEEDER | [5 empty] | 71 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | K323 | 濱23線(K323) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K323_DS | K323_DS (非取樣點) | FEEDER | [5 empty] | 72 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K323 | 濱23線(K323) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K323_ES | K323_ES (非取樣點) | FEEDER | [5 empty] | 73 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | K324 | 濱24線(K324) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K324_DS | K324_DS (非取樣點) | FEEDER | [5 empty] | 74 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K324 | 濱24線(K324) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K324_ES | K324_ES (非取樣點) | FEEDER | [5 empty] | 75 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | K325 | 濱25線(K325) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K325_DS | K325_DS (非取樣點) | FEEDER | [5 empty] | 76 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K325 | 濱25線(K325) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K325_ES | K325_ES (非取樣點) | FEEDER | [5 empty] | 77 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | 240 | #4SC(240) |  | E1 | 241E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.241E | 241E (非取樣點) | SC | [5 empty] | 78 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | 240 | #4SC(240) |  | DS1 | 241(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.241 | 241 (非取樣點) | SC | [5 empty] | 79 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K326 | 濱26線(K326) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K326_DS | K326_DS (非取樣點) | FEEDER | [5 empty] | 80 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K326 | 濱26線(K326) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K326_ES | K326_ES (非取樣點) | FEEDER | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | K327 | 濱27線(K327) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K327_DS | K327_DS (非取樣點) | FEEDER | [5 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K327 | 濱27線(K327) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K327_ES | K327_ES (非取樣點) | FEEDER | [5 empty] | 83 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | K328 | 濱28線(K328) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K328_DS | K328_DS (非取樣點) | FEEDER | [5 empty] | 84 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K328 | 濱28線(K328) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K328_ES | K328_ES (非取樣點) | FEEDER | [5 empty] | 85 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | K329 | 濱29線(K329) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K329_DS | K329_DS (非取樣點) | FEEDER | [5 empty] | 86 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K329 | 濱29線(K329) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K329_ES | K329_ES (非取樣點) | FEEDER | [5 empty] | 87 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | K330 | 濱30線(K330) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K330_DS | K330_DS (非取樣點) | FEEDER | [5 empty] | 88 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K330 | 濱30線(K330) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K330_ES | K330_ES (非取樣點) | FEEDER | [5 empty] | 89 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | 200 | TIE(200) |  | D1 | 201(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.201 | 201 (非取樣點) | TIE | [5 empty] | 90 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | 200 | TIE(200) |  | D2 | 202(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.202 | 202 (非取樣點) | TIE | [5 empty] | 91 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | 200 | TIE(200) |  | E1 | 201E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.201E | 201E(非取樣點) | OTHER | [5 empty] | 92 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | 200 | TIE(200) |  | E2 | 202E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.202E | 202E(非取樣點) | OTHER | [5 empty] | 93 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 22 | 22kV | 250 | #5SC(250) |  | E1 | 251E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.251E | 251E (非取樣點) | SC | [5 empty] | 94 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 22 | 22kV | 250 | #5SC(250) |  | ES | 250_ES | DEL | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D03_A1 | [16 empty] | 95 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D03 | 南濱DS | 22 | 22kV | 250 | #5SC(250) |  | D1 | 251(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.251 | 251 (非取樣點) | SC | [5 empty] | 96 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K361 | 濱61線(K361) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K361_DS | K361_DS (非取樣點) | FEEDER | [5 empty] | 97 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K361 | 濱61線(K361) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K361_ES | K361_ES (非取樣點) | FEEDER | [5 empty] | 98 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 22 | 22kV | K362 | 濱62線(K362) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K362_DS | K362_DS (非取樣點) | FEEDER | [5 empty] | 99 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K362 | 濱62線(K362) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K362_ES | K362_ES (非取樣點) | FEEDER | [5 empty] | 100 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 22 | 22kV | K363 | 濱63線(K363) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K363_DS | K363_DS (非取樣點) | FEEDER | [5 empty] | 101 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K363 | 濱63線(K363) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K363_ES | K363_ES (非取樣點) | FEEDER | [5 empty] | 102 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 22 | 22kV | K364 | 濱64線(K364) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K364_DS | K364_DS (非取樣點) | FEEDER | [5 empty] | 103 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K364 | 濱64線(K364) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K364_ES | K364_ES (非取樣點) | FEEDER | [5 empty] | 104 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 22 | 22kV | K365 | 濱65線(K365) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K365_DS | K365_DS (非取樣點) | FEEDER | [5 empty] | 105 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K365 | 濱65線(K365) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K365_ES | K365_ES (非取樣點) | FEEDER | [5 empty] | 106 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 22 | 22kV | K366 | 濱66線(K366) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K366_DS | K366_DS (非取樣點) | FEEDER | [5 empty] | 107 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K366 | 濱66線(K366) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K366_ES | K366_ES (非取樣點) | FEEDER | [5 empty] | 108 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 22 | 22kV | K367 | 濱67線(K367) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K367_DS | K367_DS (非取樣點) | FEEDER | [5 empty] | 109 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K367 | 濱67線(K367) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K367_ES | K367_ES (非取樣點) | FEEDER | [5 empty] | 110 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 22 | 22kV | K368 | 濱68線(K368) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K368_DS | K368_DS (非取樣點) | FEEDER | [5 empty] | 111 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K368 | 濱68線(K368) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K368_ES | K368_ES (非取樣點) | FEEDER | [5 empty] | 112 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 22 | 22kV | 260 | #6SC(260) |  | E1 | 261E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.261E | 261E (非取樣點) | SC | [5 empty] | 113 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 22 | 22kV | 260 | #6SC(260) |  | ES | 260_ES | DEL | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D03_A1 | [16 empty] | 114 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D03 | 南濱DS | 22 | 22kV | 260 | #6SC(260) |  | D1 | 261(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.261 | 261 (非取樣點) | SC | [5 empty] | 115 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | 300 | TIE(300) |  | D1 | 301(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.301 | 301 (非取樣點) | TIE | [5 empty] | 116 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | 300 | TIE(300) |  | D2 | 302(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.302 | 302 (非取樣點) | TIE | [5 empty] | 117 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | 300 | TIE(300) |  | E1 | 301E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.301E | 301E(非取樣點) | OTHER | [5 empty] | 118 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 22 | 22kV | 300 | TIE(300) |  | E2 | 302E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.302E | 302E(非取樣點) | OTHER | [5 empty] | 119 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 22 | 22kV | 270 | #7SC(270) |  | E1 | 271E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.271E | 271E (非取樣點) | SC | [5 empty] | 120 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 22 | 22kV | 270 | #7SC(270) |  | ES | 270_ES | DEL | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D03_A1 | [16 empty] | 121 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D03 | 南濱DS | 22 | 22kV | 270 | #7SC(270) |  | D1 | 271(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.271 | 271 (非取樣點) | SC | [5 empty] | 122 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K371 | 濱71線(K371) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K371_DS | K371_DS (非取樣點) | FEEDER | [5 empty] | 123 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K371 | 濱71線(K371) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K371_ES | K371_ES (非取樣點) | FEEDER | [5 empty] | 124 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 22 | 22kV | K372 | 濱72線(K372) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K372_DS | K372_DS (非取樣點) | FEEDER | [5 empty] | 125 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K372 | 濱72線(K372) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K372_ES | K372_ES (非取樣點) | FEEDER | [5 empty] | 126 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 22 | 22kV | K373 | 濱73線(K373) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K373_DS | K373_DS (非取樣點) | FEEDER | [5 empty] | 127 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K373 | 濱73線(K373) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K373_ES | K373_ES (非取樣點) | FEEDER | [5 empty] | 128 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 22 | 22kV | K374 | 濱74線(K374) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K374_DS | K374_DS (非取樣點) | FEEDER | [5 empty] | 129 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K374 | 濱74線(K374) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K374_ES | K374_ES (非取樣點) | FEEDER | [5 empty] | 130 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 22 | 22kV | K375 | 濱75線(K375) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K375_DS | K375_DS (非取樣點) | FEEDER | [5 empty] | 131 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K375 | 濱75線(K375) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K375_ES | K375_ES (非取樣點) | FEEDER | [5 empty] | 132 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 22 | 22kV | K376 | 濱76線(K376) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K376_DS | K376_DS (非取樣點) | FEEDER | [5 empty] | 133 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K376 | 濱76線(K376) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K376_ES | K376_ES (非取樣點) | FEEDER | [5 empty] | 134 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 22 | 22kV | K377 | 濱77線(K377) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K377_DS | K377_DS (非取樣點) | FEEDER | [5 empty] | 135 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K377 | 濱77線(K377) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K377_ES | K377_ES (非取樣點) | FEEDER | [5 empty] | 136 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 22 | 22kV | K378 | 濱78線(K378) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K378_DS | K378_DS (非取樣點) | FEEDER | [5 empty] | 137 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K378 | 濱78線(K378) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D03_D1 | [8 empty] | 南濱DS.K378_ES | K378_ES (非取樣點) | FEEDER | [5 empty] | 138 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 22 | 22kV | 280 | #8SC(280) |  | E1 | 281E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.281E | 281E (非取樣點) | SC | [5 empty] | 139 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 22 | 22kV | 280 | #8SC(280) |  | ES | 280_ES | DEL | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D03_A1 | [16 empty] | 140 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D03 | 南濱DS | 22 | 22kV | 280 | #8SC(280) |  | D1 | 281(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.281 | 281 (非取樣點) | SC | [5 empty] | 141 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | 490 | #2SSTR(490) |  | D1 | 491(非取樣點) | B3 | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.491 | 491 (非取樣點) | OTHER | [5 empty] | 142 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | 490 | #2SSTR(490) |  | E1 | 491E(非取樣點) | B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D03_A1 | [8 empty] | 南濱DS.491E | 491E (非取樣點) | OTHER | [5 empty] | 143 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | 15B1E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aaaz | B2/D03_A1 | [8 empty] | 南濱DS.15B1E | 15B1E (非取樣點) | BUS | [5 empty] | 144 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | 15B2E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/2Bus | [13 empty] | aaaz | B2/D03_A1 | [8 empty] | 南濱DS.15B2E | 15B2E (非取樣點) | BUS | [5 empty] | 145 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | RTU | RTU |  | ADCL1 |  |  | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | [5 empty] | 146 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | RTU | RTU |  | ADCH1 |  |  | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.1 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | [5 empty] | 147 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 161 | 161kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 161KV #1BUS | KV | 161KV #1BUS 電壓 | kV_-210_210(-2000_2000) | aaa | B2/D03_A1 | [8 empty] | 南濱DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | [5 empty] | 148 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D03 | 南濱DS | 161 | 161kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0003 |  |  | 1-83 |  |  | 161KV #2BUS | KV | 161KV #2BUS 電壓 | kV_-210_210(-2000_2000) | aab | B2/D03_A1 | [8 empty] | 南濱DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | [5 empty] | 149 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D03 | 南濱DS | 161 | 161kV | 1510 | 安南～南濱一路(1510) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | L1 | MW | 安南南濱一路1510 瓦 | MW_-560_560(-2000_2000) |  | B2/D03_A1 | [8 empty] | 南濱DS.1510_MW | 安南南濱一路 MW | LINE161 | [5 empty] | 150 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D03 | 南濱DS | 161 | 161kV | 1510 | 安南～南濱一路(1510) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | L1 | MVAR | 安南南濱一路1510 乏 | MVAR_-560_560(-2000_2000) |  | B2/D03_A1 | [8 empty] | 南濱DS.1510_MVAR | 安南南濱一路 MVAR | LINE161 | [5 empty] | 151 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D03 | 南濱DS | 161 | 161kV | 1520 | 安南～南濱二路(1520) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | L2 | MW | 安南南濱二路1520 瓦 | MW_-560_560(-2000_2000) |  | B2/D03_A1 | [8 empty] | 南濱DS.1520_MW | 安南南濱二路 MW | LINE161 | [5 empty] | 152 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D03 | 南濱DS | 161 | 161kV | 1520 | 安南～南濱二路(1520) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | L2 | MVAR | 安南南濱二路1520 乏 | MVAR_-560_560(-2000_2000) |  | B2/D03_A1 | [8 empty] | 南濱DS.1520_MVAR | 安南南濱二路 MVAR | LINE161 | [5 empty] | 153 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱～安瀚線(1530) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | 1530 | MW | 南濱安瀚線 1530 瓦 | MW_-560_560(-2000_2000) |  | B2/D03_A1 | [8 empty] | 南濱DS.1530_MW | 南濱安瀚線 MW | LINE161 | [5 empty] | 154 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱～安瀚線(1530) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 1530 | MVAR | 南濱安瀚線 1530 乏 | MVAR_-560_560(-2000_2000) |  | B2/D03_A1 | [8 empty] | 南濱DS.1530_MVAR | 南濱安瀚線 MVAR | LINE161 | [5 empty] | 155 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱～凸版線(1540) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | 1540 | MW | 南濱凸版線 1540瓦 | MW_-560_560(-2000_2000) |  | B2/D03_A1 | [8 empty] | 南濱DS.1540_MW | 南濱凸版線 MW | LINE161 | [5 empty] | 156 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱～凸版線(1540) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | 1540 | MVAR | 南濱凸版線 1540乏 | MVAR_-560_560(-2000_2000) |  | B2/D03_A1 | [8 empty] | 南濱DS.1540_MVAR | 南濱凸版線 MVAR | LINE161 | [5 empty] | 157 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D03 | 南濱DS | 161 | 161kV | 1550 | 南濱～鹿耳紅線(1550) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0012 |  |  | 1-8C |  |  | 1550 | MW | 南濱鹿耳紅線 1550 瓦 | MW_-560_560(-2000_2000) |  | B2/D03_A1 | [8 empty] | 南濱DS.1550_MW | 南濱鹿耳紅線 MW | LINE161 | [5 empty] | 158 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D03 | 南濱DS | 161 | 161kV | 1550 | 南濱～鹿耳紅線(1550) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0013 |  |  | 1-8D |  |  | 1550 | MVAR | 南濱鹿耳紅線 1550 乏 | MVAR_-560_560(-2000_2000) |  | B2/D03_A1 | [8 empty] | 南濱DS.1550_MVAR | 南濱鹿耳紅線 MVAR | LINE161 | [5 empty] | 159 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D03 | 南濱DS | 161 | 161kV | 1560 | 南濱～鹿耳白線(1560) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0014 |  |  | 1-8E |  |  | 1560 | MW | 南濱鹿耳白線 1560瓦 | MW_-560_560(-2000_2000) |  | B2/D03_A1 | [8 empty] | 南濱DS.1560_MW | 南濱鹿耳白線 MW | LINE161 | [5 empty] | 160 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D03 | 南濱DS | 161 | 161kV | 1560 | 南濱～鹿耳白線(1560) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0015 |  |  | 1-8F |  |  | 1560 | MVAR | 南濱鹿耳白線 1560乏 | MVAR_-560_560(-2000_2000) |  | B2/D03_A1 | [8 empty] | 南濱DS.1560_MVAR | 南濱鹿耳白線 MVAR | LINE161 | [5 empty] | 161 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D03 | 南濱DS | 0 |  | StaDev | 所內設施 |  | DCV_P |  |  | MvMoment | 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | DCV | 65 | DC-P電壓 | kV_-150_150(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.直流P電源電壓 | 直流P電源電壓 | OTHER | [5 empty] | 162 |  |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 | 0.01 | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D03 | 南濱DS | 0 |  | StaDev | 所內設施 |  | DCV_N |  |  | MvMoment | 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | DCV | -65 | DC-N電壓 | kV_-150_150(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.直流N電源電壓 | 直流N電源電壓 | OTHER | [5 empty] | 163 |  |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 | 0.01 | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D03 | 南濱DS | 161 | 161kV | 1500 | TIE(1500) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0024 |  |  | 1-98 |  |  | 161KV TIE | A | (1500) R相電流 | A_-2000_2000(-2000_2000) |  | B2/D03_A1 | [8 empty] | 南濱DS.1500TIE_AMP | 1500TIE AMP | TIE | [5 empty] | 164 |  |  |  |  | AI | [5 empty] | C20R1600 | 1520 | 1600 | 1760 | 1968 | 2.27 | -1520 | -1600 | -1760 | -1968 | 1 | 0.01 | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS |  |  | 1DTR | #1DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | NO.1 DTR. | ℃ | NO.1 DTR. 油溫 | OIL_-120_120(-2000_2000) |  | B1/D03_A1 | [8 empty] | 南濱DS.#1DTR_OIL | #1DTR 油溫 | MTR | [5 empty] | 165 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D03 | 南濱DS |  |  | 1DTR(A) | #1DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | NO.1 DTR.A | ℃ | NO.1 DTR.A 線溫 | COIL_-120_120(-2000_2000) |  | B1/D03_A1 | [8 empty] | 南濱DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | [5 empty] | 166 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D03 | 南濱DS |  |  | 1DTR(B) | #1DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0027 |  |  | 1-9B |  |  | NO.1 DTR.B | ℃ | NO.1 DTR.B 線溫 | COIL_-120_120(-2000_2000) |  | B1/D03_A1 | [8 empty] | 南濱DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | [5 empty] | 167 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D03 | 南濱DS |  |  | 1DTR(A) | #1DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | NO.1 DTR.A | 升/降 | NO.1 DTR.A TAP | TAP_-8.5_8.5(0_2000) |  | B1/D03_A1 | [8 empty] | 南濱DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | [5 empty] | 168 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D03 | 南濱DS |  |  | 1DTR(B) | #1DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | NO.1 DTR.B | 升/降 | NO.1 DTR.B TAP | TAP_-8.5_8.5(0_2000) |  | B1/D03_A1 | [8 empty] | 南濱DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | [5 empty] | 169 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D03 | 南濱DS |  |  | 2DTR | #2DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | NO.2 DTR. | ℃ | NO.2 DTR. 油溫 | OIL_-120_120(-2000_2000) |  | B1/D03_A1 | [8 empty] | 南濱DS.#2DTR_OIL | #2DTR 油溫 | MTR | [5 empty] | 170 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D03 | 南濱DS |  |  | 2DTR(A) | #2DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | NO.2 DTR.A | ℃ | NO.2 DTR.A 線溫 | COIL_-120_120(-2000_2000) |  | B1/D03_A1 | [8 empty] | 南濱DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | [5 empty] | 171 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D03 | 南濱DS |  |  | 2DTR(B) | #2DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | NO.2 DTR.B | ℃ | NO.2 DTR.B 線溫 | COIL_-120_120(-2000_2000) |  | B1/D03_A1 | [8 empty] | 南濱DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | [5 empty] | 172 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D03 | 南濱DS |  |  | 2DTR(A) | #2DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | NO.2 DTR.A | 升/降 | NO.2 DTR.A TAP | TAP_-8.5_8.5(0_2000) |  | B1/D03_A1 | [8 empty] | 南濱DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | [5 empty] | 173 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D03 | 南濱DS |  |  | 2DTR(B) | #2DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | NO.2 DTR.B | 升/降 | NO.2 DTR.B TAP | TAP_-8.5_8.5(0_2000) |  | B1/D03_A1 | [8 empty] | 南濱DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | [5 empty] | 174 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D03 | 南濱DS |  |  | 3DTR | #3DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | NO.3 DTR. | ℃ | NO.3 DTR. 油溫 | OIL_-120_120(-2000_2000) |  | B1/D03_A1 | [8 empty] | 南濱DS.#3DTR_OIL | #3DTR 油溫 | MTR | [5 empty] | 175 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D03 | 南濱DS |  |  | 3DTR | #3DTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | NO.3 DTR. | ℃ | NO.3 DTR. 線溫 | COIL_-120_120(-2000_2000) |  | B1/D03_A1 | [8 empty] | 南濱DS.#3DTR_COIL | #3DTR 線溫 | MTR | [5 empty] | 176 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D03 | 南濱DS |  |  | 3DTR | #3DTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | NO.3 DTR. | 升/降 | NO.3 DTR. TAP | TAP_-8.5_8.5(0_2000) |  | B1/D03_A1 | [8 empty] | 南濱DS.#3DTR_TAP | #3DTR OLTC TAP | MTR | [5 empty] | 177 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D03 | 南濱DS |  |  | 4DTR | #4DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | NO.4 DTR. | ℃ | NO.4 DTR. 油溫 | OIL_-120_120(-2000_2000) |  | B1/D03_A1 | [8 empty] | 南濱DS.#4DTR_OIL | #4DTR 油溫 | MTR | [5 empty] | 178 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D03 | 南濱DS |  |  | 4DTR | #4DTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | NO.4 DTR. | ℃ | NO.4 DTR. 線溫 | COIL_-120_120(-2000_2000) |  | B1/D03_A1 | [8 empty] | 南濱DS.#4DTR_COIL | #4DTR 線溫 | MTR | [5 empty] | 179 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D03 | 南濱DS |  |  | 4DTR | #4DTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | NO.4 DTR. | 升/降 | NO.4 DTR. TAP | TAP_-8.5_8.5(0_2000) |  | B1/D03_A1 | [8 empty] | 南濱DS.#4DTR_TAP | #4DTR OLTC TAP | MTR | [5 empty] | 180 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D03 | 南濱DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | D-1A | MW | D-1A 310 瓦 | MW_-54_54(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | [5 empty] | 181 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | D-1A | MVAR | D-1A 310 乏 | MVAR_-36_36(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | [5 empty] | 182 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | D-1A | A | D-1A 310 R相電流 | A_-3000_3000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | [5 empty] | 183 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | D-1A | A | D-1A 310 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | [5 empty] | 184 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | D-1A | A | D-1A 310 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | [5 empty] | 185 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 1ABUS | #1ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0046 |  |  | 1-AE |  |  | PT-1A | KV | #1A PT R相電壓 | kV_-9_9(-2000_2000) | aba | B3/D03_A1 | [8 empty] | 南濱DS.11KV#1ABUS_KV | 11KV #1ABUS KV | BUS | [5 empty] | 186 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D03 | 南濱DS | 11 | 11kV | K311 | 濱11線(K311) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | F1 | KVAR | 濱11線 K311 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱11線KVAR | 11KV濱11線 KVAR | FEEDER | [5 empty] | 187 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K311 | 濱11線(K311) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | F1 | A | 濱11線 K311 R相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱11線A1 | 11KV濱11線 R相AMP | FEEDER | [5 empty] | 188 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K311 | 濱11線(K311) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | F1 | A | 濱11線 K311 S相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱11線A2 | 11KV濱11線 S相AMP | FEEDER | [5 empty] | 189 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K311 | 濱11線(K311) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | F1 | A | 濱11線 K311 T相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱11線A3 | 11KV濱11線 T相AMP | FEEDER | [5 empty] | 190 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K311 | 濱11線(K311) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | F1 | A | 濱11線 K311 N相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱11線A0 | 11KV濱11線 N相AMP | FEEDER | [5 empty] | 191 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K312 | 濱12線(K312) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | F2 | KVAR | 濱12線 K312 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱12線KVAR | 11KV濱12線 KVAR | FEEDER | [5 empty] | 192 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K312 | 濱12線(K312) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | F2 | A | 濱12線 K312 R相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱12線A1 | 11KV濱12線 R相AMP | FEEDER | [5 empty] | 193 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K312 | 濱12線(K312) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | F2 | A | 濱12線 K312 S 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱12線A2 | 11KV濱12線 S相AMP | FEEDER | [5 empty] | 194 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K312 | 濱12線(K312) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | F2 | A | 濱12線 K312 T 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱12線A3 | 11KV濱12線 T相AMP | FEEDER | [5 empty] | 195 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K312 | 濱12線(K312) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | F2 | A | 濱12線 K312 N 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱12線A0 | 11KV濱12線 N相AMP | FEEDER | [5 empty] | 196 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K313 | 濱13線(K313) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | F3 | KVAR | 濱13線 K313 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱13線KVAR | 11KV濱13線 KVAR | FEEDER | [5 empty] | 197 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K313 | 濱13線(K313) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | F3 | A | 濱13線 K313 R相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱13線A1 | 11KV濱13線 R相AMP | FEEDER | [5 empty] | 198 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K313 | 濱13線(K313) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | F3 | A | 濱13線 K313 S 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱13線A2 | 11KV濱13線 S相AMP | FEEDER | [5 empty] | 199 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K313 | 濱13線(K313) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0060 |  |  | 1-BC |  |  | F3 | A | 濱13線 K313 T 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱13線A3 | 11KV濱13線 T相AMP | FEEDER | [5 empty] | 200 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K313 | 濱13線(K313) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | F3 | A | 濱13線 K313 N 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱13線A0 | 11KV濱13線 N相AMP | FEEDER | [5 empty] | 201 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K314 | 濱14線(K314) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | F4 | KVAR | 濱14線 K314 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱14線KVAR | 11KV濱14線 KVAR | FEEDER | [5 empty] | 202 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K314 | 濱14線(K314) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0063 |  |  | 1-BF |  |  | F4 | A | 濱14線 K314 R 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱14線A1 | 11KV濱14線 R相AMP | FEEDER | [5 empty] | 203 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | RTU | RTU |  | ADCL2 |  |  | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | [5 empty] | 204 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | RTU | RTU |  | ADCH2 |  |  | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.2 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | [5 empty] | 205 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K314 | 濱14線(K314) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | F4 | A | 濱14線 K314 S 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱14線A2 | 11KV濱14線 S相AMP | FEEDER | [5 empty] | 206 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K314 | 濱14線(K314) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | F4 | A | 濱14線 K314 T 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱14線A3 | 11KV濱14線 T相AMP | FEEDER | [5 empty] | 207 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K314 | 濱14線(K314) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | F4 | A | 濱14線 K314 N 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱14線A0 | 11KV濱14線 N相AMP | FEEDER | [5 empty] | 208 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K315 | 濱15線(K315) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | F5 | KVAR | 濱15線 K315 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱15線KVAR | 11KV濱15線 KVAR | FEEDER | [5 empty] | 209 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K315 | 濱15線(K315) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | F5 | A | 濱15線 K315 R 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱15線A1 | 11KV濱15線 R相AMP | FEEDER | [5 empty] | 210 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K315 | 濱15線(K315) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | F5 | A | 濱15線 K315 S 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱15線A2 | 11KV濱15線 S相AMP | FEEDER | [5 empty] | 211 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K315 | 濱15線(K315) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | F5 | A | 濱15線 K315 T 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱15線A3 | 11KV濱15線 T相AMP | FEEDER | [5 empty] | 212 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K315 | 濱15線(K315) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | F5 | A | 濱15線 K315 N相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱15線A0 | 11KV濱15線 N相AMP | FEEDER | [5 empty] | 213 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 100 | TIE(100) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | TIE-1 | A | TIE-1 100 R 相電流 | A_-2000_2000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.11KV_100_A1 | 11KV 100 R相AMP | TIE | [5 empty] | 214 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 100 | TIE(100) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | TIE-1 | A | TIE-1 100 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.11KV_100_A2 | 11KV 100 S相AMP | TIE | [5 empty] | 215 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 100 | TIE(100) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | TIE-1 | A | TIE-1 100 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.11KV_100_A3 | 11KV 100 T相AMP | TIE | [5 empty] | 216 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | D-1B | MW | D-1B 320 瓦 | MW_-54_54(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | [5 empty] | 217 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | D-1B | MVAR | D-1B 320 乏 | MVAR_-36_36(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | [5 empty] | 218 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | D-1B | A | D-1B 320 R相電流 | A_-3000_3000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | [5 empty] | 219 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | D-1B | A | D-1B 320 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | [5 empty] | 220 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | D-1B | A | D-1B 320 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | [5 empty] | 221 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 1BBUS | #1BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0082 |  |  | 1-D2 |  |  | PT-1B | KV | #1B PT R相電壓 | kV_-9_9(-2000_2000) | aca | B3/D03_A1 | [8 empty] | 南濱DS.11KV#1BBUS_KV | 11KV #1BBUS KV | BUS | [5 empty] | 222 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D03 | 南濱DS | 11 | 11kV | K316 | 濱16線(K316) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | F6 | KVAR | 濱16線 K316 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱16線KVAR | 11KV濱16線 KVAR | FEEDER | [5 empty] | 223 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K316 | 濱16線(K316) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | F6 | A | 濱16線 K316 R 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱16線A1 | 11KV濱16線 R相AMP | FEEDER | [5 empty] | 224 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K316 | 濱16線(K316) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | F6 | A | 濱16線 K316 S相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱16線A2 | 11KV濱16線 S相AMP | FEEDER | [5 empty] | 225 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K316 | 濱16線(K316) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | F6 | A | 濱16線 K316 T相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱16線A3 | 11KV濱16線 T相AMP | FEEDER | [5 empty] | 226 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K316 | 濱16線(K316) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | F6 | A | 濱16線 K316 N相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱16線A0 | 11KV濱16線 N相AMP | FEEDER | [5 empty] | 227 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K317 | 濱17線(K317) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | F7 | KVAR | 濱17線 K317 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱17線KVAR | 11KV濱17線 KVAR | FEEDER | [5 empty] | 228 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K317 | 濱17線(K317) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | F7 | A | 濱17線 K317 R相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱17線A1 | 11KV濱17線 R相AMP | FEEDER | [5 empty] | 229 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K317 | 濱17線(K317) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | F7 | A | 濱17線 K317 S相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱17線A2 | 11KV濱17線 S相AMP | FEEDER | [5 empty] | 230 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K317 | 濱17線(K317) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | F7 | A | 濱17線 K317 T相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱17線A3 | 11KV濱17線 T相AMP | FEEDER | [5 empty] | 231 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K317 | 濱17線(K317) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | F7 | A | 濱17線 K317 N相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱17線A0 | 11KV濱17線 N相AMP | FEEDER | [5 empty] | 232 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K318 | 濱18線(K318) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | F8 | KVAR | 濱18線 K318 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱18線KVAR | 11KV濱18線 KVAR | FEEDER | [5 empty] | 233 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K318 | 濱18線(K318) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | F8 | A | 濱18線 K318 R相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱18線A1 | 11KV濱18線 R相AMP | FEEDER | [5 empty] | 234 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K318 | 濱18線(K318) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | F8 | A | 濱18線 K318 S相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱18線A2 | 11KV濱18線 S相AMP | FEEDER | [5 empty] | 235 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K318 | 濱18線(K318) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | F8 | A | 濱18線 K318 T相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱18線A3 | 11KV濱18線 T相AMP | FEEDER | [5 empty] | 236 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K318 | 濱18線(K318) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | F8 | A | 濱18線 K318 N相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱18線A0 | 11KV濱18線 N相AMP | FEEDER | [5 empty] | 237 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K319 | 濱19線(K319) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0098 |  |  | 1-E2 |  |  | F9 | KVAR | 濱19線 K319 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱19線KVAR | 11KV濱19線 KVAR | FEEDER | [5 empty] | 238 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K319 | 濱19線(K319) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | F9 | A | 濱19線 K319 R相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱19線A1 | 11KV濱19線 R相AMP | FEEDER | [5 empty] | 239 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K319 | 濱19線(K319) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | F9 | A | 濱19線 K319 S 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱19線A2 | 11KV濱19線 S相AMP | FEEDER | [5 empty] | 240 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K319 | 濱19線(K319) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0101 |  |  | 1-E5 |  |  | F9 | A | 濱19線 K319 T相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱19線A3 | 11KV濱19線 T相AMP | FEEDER | [5 empty] | 241 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K319 | 濱19線(K319) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | F9 | A | 濱19線 K319 N相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱19線A0 | 11KV濱19線 N相AMP | FEEDER | [5 empty] | 242 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K320 | 濱20線(K320) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | F10 | KVAR | 濱20線 K320 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱20線KVAR | 11KV濱20線 KVAR | FEEDER | [5 empty] | 243 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K320 | 濱20線(K320) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | F10 | A | 濱20線 K320 R相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱20線A1 | 11KV濱20線 R相AMP | FEEDER | [5 empty] | 244 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K320 | 濱20線(K320) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | F10 | A | 濱20線 K320 S 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱20線A2 | 11KV濱20線 S相AMP | FEEDER | [5 empty] | 245 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K320 | 濱20線(K320) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | F10 | A | 濱20線 K320 T相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱20線A3 | 11KV濱20線 T相AMP | FEEDER | [5 empty] | 246 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K320 | 濱20線(K320) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | F10 | A | 濱20線 K320 N相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱20線A0 | 11KV濱20線 N相AMP | FEEDER | [5 empty] | 247 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | D-2A | MW | D-2A 330 瓦 | MW_-54_54(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | [5 empty] | 248 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | D-2A | MVAR | D-2A 330 乏 | MVAR_-36_36(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | [5 empty] | 249 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | D-2A | A | D-2A 330 R 相電流 | A_-3000_3000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | [5 empty] | 250 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | D-2A | A | D-2A 330 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | [5 empty] | 251 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | D-2A | A | D-2A 330 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | [5 empty] | 252 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 2ABUS | #2ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0113 |  |  | 1-F1 |  |  | PT-2A | KV | #2A PT R相電壓 | kV_-9_9(-2000_2000) | aaa | B3/D03_A1 | [8 empty] | 南濱DS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS | [5 empty] | 253 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D03 | 南濱DS | 11 | 11kV | K321 | 濱21線(K321) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | F11 | KVAR | 濱21線 K321 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱21線KVAR | 11KV濱21線 KVAR | FEEDER | [5 empty] | 254 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K321 | 濱21線(K321) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | F11 | A | 濱21線 K321 R 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱21線A1 | 11KV濱21線 R相AMP | FEEDER | [5 empty] | 255 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K321 | 濱21線(K321) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | F11 | A | 濱21線 K321 S相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱21線A2 | 11KV濱21線 S相AMP | FEEDER | [5 empty] | 256 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K321 | 濱21線(K321) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | F11 | A | 濱21線 K321 T相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱21線A3 | 11KV濱21線 T相AMP | FEEDER | [5 empty] | 257 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K321 | 濱21線(K321) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | F11 | A | 濱21線 K321 N相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱21線A0 | 11KV濱21線 N相AMP | FEEDER | [5 empty] | 258 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K322 | 濱22線(K322) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | F12 | KVAR | 濱22線 K322 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱22線KVAR | 11KV濱22線 KVAR | FEEDER | [5 empty] | 259 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K322 | 濱22線(K322) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | F12 | A | 濱22線 K322 R相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱22線A1 | 11KV濱22線 R相AMP | FEEDER | [5 empty] | 260 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K322 | 濱22線(K322) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | F12 | A | 濱22線 K322 S相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱22線A2 | 11KV濱22線 S相AMP | FEEDER | [5 empty] | 261 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K322 | 濱22線(K322) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | F12 | A | 濱22線 K322 T相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱22線A3 | 11KV濱22線 T相AMP | FEEDER | [5 empty] | 262 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K322 | 濱22線(K322) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | F12 | A | 濱22線 K322 N相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱22線A0 | 11KV濱22線 N相AMP | FEEDER | [5 empty] | 263 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K323 | 濱23線(K323) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | F13 | KVAR | 濱23線 K323 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱23線KVAR | 11KV濱23線 KVAR | FEEDER | [5 empty] | 264 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K323 | 濱23線(K323) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | F13 | A | 濱23線 K323 R 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱23線A1 | 11KV濱23線 R相AMP | FEEDER | [5 empty] | 265 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K323 | 濱23線(K323) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | F13 | A | 濱23線 K323 S 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱23線A2 | 11KV濱23線 S相AMP | FEEDER | [5 empty] | 266 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K323 | 濱23線(K323) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | F13 | A | 濱23線 K323 T相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱23線A3 | 11KV濱23線 T相AMP | FEEDER | [5 empty] | 267 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | RTU | RTU |  | ADCL3 |  |  | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.3 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | [5 empty] | 268 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | RTU | RTU |  | ADCH3 |  |  | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.3 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | [5 empty] | 269 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K323 | 濱23線(K323) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | F13 | A | 濱23線 K323 N相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱23線A0 | 11KV濱23線 N相AMP | FEEDER | [5 empty] | 270 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K324 | 濱24線(K324) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | F14 | KVAR | 濱24線 K324 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱24線KVAR | 11KV濱24線 KVAR | FEEDER | [5 empty] | 271 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K324 | 濱24線(K324) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | F14 | A | 濱24線 K324 R 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱24線A1 | 11KV濱24線 R相AMP | FEEDER | [5 empty] | 272 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K324 | 濱24線(K324) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0133 |  |  | 2-85 |  |  | F14 | A | 濱24線 K324 S 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱24線A2 | 11KV濱24線 S相AMP | FEEDER | [5 empty] | 273 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K324 | 濱24線(K324) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | F14 | A | 濱24線 K324 T 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱24線A3 | 11KV濱24線 T相AMP | FEEDER | [5 empty] | 274 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K324 | 濱24線(K324) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0135 |  |  | 2-87 |  |  | F14 | A | 濱24線 K324 N相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱24線A0 | 11KV濱24線 N相AMP | FEEDER | [5 empty] | 275 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K325 | 濱25線(K325) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0136 |  |  | 2-88 |  |  | F15 | KVAR | 濱25線 K325 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱25線KVAR | 11KV濱25線 KVAR | FEEDER | [5 empty] | 276 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K325 | 濱25線(K325) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0137 |  |  | 2-89 |  |  | F15 | A | 濱25線 K325 R 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱25線A1 | 11KV濱25線 R相AMP | FEEDER | [5 empty] | 277 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K325 | 濱25線(K325) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0138 |  |  | 2-8A |  |  | F15 | A | 濱25線 K325 S 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱25線A2 | 11KV濱25線 S相AMP | FEEDER | [5 empty] | 278 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K325 | 濱25線(K325) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0139 |  |  | 2-8B |  |  | F15 | A | 濱25線 K325 T 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱25線A3 | 11KV濱25線 T相AMP | FEEDER | [5 empty] | 279 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K325 | 濱25線(K325) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0140 |  |  | 2-8C |  |  | F15 | A | 濱25線 K325 N相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱25線A0 | 11KV濱25線 N相AMP | FEEDER | [5 empty] | 280 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0141 |  |  | 2-8D |  |  | D-2B | MW | D-2B 340 瓦 | MW_-54_54(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | [5 empty] | 281 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0142 |  |  | 2-8E |  |  | D-2B | MVAR | D-2B 340 乏 | MVAR_-36_36(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | [5 empty] | 282 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0143 |  |  | 2-8F |  |  | D-2B | A | D-2B 340 R 相電流 | A_-3000_3000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | [5 empty] | 283 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0144 |  |  | 2-90 |  |  | D-2B | A | D-2B 340 S 相電流 | A_-3000_3000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | [5 empty] | 284 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0145 |  |  | 2-91 |  |  | D-2B | A | D-2B 340 T 相電流 | A_-3000_3000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | [5 empty] | 285 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 2BBUS | #2BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0146 |  |  | 2-92 |  |  | PT-2B | KV | #2B PT R相電壓 | kV_-9_9(-2000_2000) | ada | B3/D03_A1 | [8 empty] | 南濱DS.11KV#2BBUS_KV | 11KV #2BBUS KV | BUS | [5 empty] | 286 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D03 | 南濱DS | 11 | 11kV | K326 | 濱26線(K326) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0147 |  |  | 2-93 |  |  | F16 | KVAR | 濱26線 K326 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱26線KVAR | 11KV濱26線 KVAR | FEEDER | [5 empty] | 287 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K326 | 濱26線(K326) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0148 |  |  | 2-94 |  |  | F16 | A | 濱26線 K326 R 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱26線A1 | 11KV濱26線 R相AMP | FEEDER | [5 empty] | 288 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K326 | 濱26線(K326) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0149 |  |  | 2-95 |  |  | F16 | A | 濱26線 K326 S 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱26線A2 | 11KV濱26線 S相AMP | FEEDER | [5 empty] | 289 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K326 | 濱26線(K326) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0150 |  |  | 2-96 |  |  | F16 | A | 濱26線 K326 T 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱26線A3 | 11KV濱26線 T相AMP | FEEDER | [5 empty] | 290 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K326 | 濱26線(K326) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0151 |  |  | 2-97 |  |  | F16 | A | 濱26線 K326 N相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱26線A0 | 11KV濱26線 N相AMP | FEEDER | [5 empty] | 291 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K327 | 濱27線(K327) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0152 |  |  | 2-98 |  |  | F17 | KVAR | 濱27線 K327 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱27線KVAR | 11KV濱27線 KVAR | FEEDER | [5 empty] | 292 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K327 | 濱27線(K327) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0153 |  |  | 2-99 |  |  | F17 | A | 濱27線 K327 R 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱27線A1 | 11KV濱27線 R相AMP | FEEDER | [5 empty] | 293 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K327 | 濱27線(K327) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0154 |  |  | 2-9A |  |  | F17 | A | 濱27線 K327 S 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱27線A2 | 11KV濱27線 S相AMP | FEEDER | [5 empty] | 294 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K327 | 濱27線(K327) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0155 |  |  | 2-9B |  |  | F17 | A | 濱27線 K327 T 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱27線A3 | 11KV濱27線 T相AMP | FEEDER | [5 empty] | 295 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K327 | 濱27線(K327) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0156 |  |  | 2-9C |  |  | F17 | A | 濱27線 K327 N相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱27線A0 | 11KV濱27線 N相AMP | FEEDER | [5 empty] | 296 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K328 | 濱28線(K328) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0157 |  |  | 2-9D |  |  | F18 | KVAR | 濱28線 K328 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱28線KVAR | 11KV濱28線 KVAR | FEEDER | [5 empty] | 297 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K328 | 濱28線(K328) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0158 |  |  | 2-9E |  |  | F18 | A | 濱28線 K328 R 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱28線A1 | 11KV濱28線 R相AMP | FEEDER | [5 empty] | 298 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K328 | 濱28線(K328) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0159 |  |  | 2-9F |  |  | F18 | A | 濱28線 K328 S 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱28線A2 | 11KV濱28線 S相AMP | FEEDER | [5 empty] | 299 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K328 | 濱28線(K328) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0160 |  |  | 2-A0 |  |  | F18 | A | 濱28線 K328 T 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱28線A3 | 11KV濱28線 T相AMP | FEEDER | [5 empty] | 300 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K328 | 濱28線(K328) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0161 |  |  | 2-A1 |  |  | F18 | A | 濱28線 K328 N相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱28線A0 | 11KV濱28線 N相AMP | FEEDER | [5 empty] | 301 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K329 | 濱29線(K329) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0162 |  |  | 2-A2 |  |  | F19 | KVAR | 濱29線 K329 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱29線KVAR | 11KV濱29線 KVAR | FEEDER | [5 empty] | 302 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K329 | 濱29線(K329) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0163 |  |  | 2-A3 |  |  | F19 | A | 濱29線 K329 R 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱29線A1 | 11KV濱29線 R相AMP | FEEDER | [5 empty] | 303 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K329 | 濱29線(K329) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0164 |  |  | 2-A4 |  |  | F19 | A | 濱29線 K329 S 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱29線A2 | 11KV濱29線 S相AMP | FEEDER | [5 empty] | 304 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K329 | 濱29線(K329) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0165 |  |  | 2-A5 |  |  | F19 | A | 濱29線 K329 T 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱29線A3 | 11KV濱29線 T相AMP | FEEDER | [5 empty] | 305 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K329 | 濱29線(K329) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0166 |  |  | 2-A6 |  |  | F19 | A | 濱29線 K329 N相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱29線A0 | 11KV濱29線 N相AMP | FEEDER | [5 empty] | 306 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K330 | 濱30線(K330) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0167 |  |  | 2-A7 |  |  | F20 | KVAR | 濱30線 K330 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱30線KVAR | 11KV濱30線 KVAR | FEEDER | [5 empty] | 307 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K330 | 濱30線(K330) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0168 |  |  | 2-A8 |  |  | F20 | A | 濱30線 K330 R 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱30線A1 | 11KV濱30線 R相AMP | FEEDER | [5 empty] | 308 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K330 | 濱30線(K330) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0169 |  |  | 2-A9 |  |  | F20 | A | 濱30線 K330 S 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱30線A2 | 11KV濱30線 S相AMP | FEEDER | [5 empty] | 309 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K330 | 濱30線(K330) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0170 |  |  | 2-AA |  |  | F20 | A | 濱30線 K330 T 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱30線A3 | 11KV濱30線 T相AMP | FEEDER | [5 empty] | 310 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | K330 | 濱30線(K330) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0171 |  |  | 2-AB |  |  | F20 | A | 濱30線 K330 N相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱30線A0 | 11KV濱30線 N相AMP | FEEDER | [5 empty] | 311 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 200 | TIE(200) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0172 |  |  | 2-AC |  |  | TIE-2 | A | TIE-2 200 R 相電流 | A_-2000_2000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.11KV_200_A1 | 11KV 200 R相AMP | TIE | [5 empty] | 312 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 200 | TIE(200) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0173 |  |  | 2-AD |  |  | TIE-2 | A | TIE-2 200 S 相電流 | A_-2000_2000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.11KV_200_A2 | 11KV 200 S相AMP | TIE | [5 empty] | 313 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 200 | TIE(200) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0174 |  |  | 2-AE |  |  | TIE-2 | A | TIE-2 200 T 相電流 | A_-2000_2000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.11KV_200_A3 | 11KV 200 T相AMP | TIE | [5 empty] | 314 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 350 | #3DTR(350) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0175 |  |  | 2-AF |  |  | D-3 | MW | D-3 350 瓦 | MW_-108_108(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.#3DTR_MW | #3DTR二次側 MW | MTR | [5 empty] | 315 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.216 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 350 | #3DTR(350) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0176 |  |  | 2-B0 |  |  | D-3 | MVAR | D-3 350 乏 | MVAR_-72_72(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.#3DTR_MVAR | #3DTR二次側 MVAR | MTR | [5 empty] | 316 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 350 | #3DTR(350) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0177 |  |  | 2-B1 |  |  | D-3 | A | D-3 350 R 相電流 | A_-3000_3000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.#3DTR_A1 | #3DTR二次側 R相AMP | MTR | [5 empty] | 317 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 350 | #3DTR(350) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0178 |  |  | 2-B2 |  |  | D-3 | A | D-3 350 S 相電流 | A_-3000_3000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.#3DTR_A2 | #3DTR二次側 S相AMP | MTR | [5 empty] | 318 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 350 | #3DTR(350) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0179 |  |  | 2-B3 |  |  | D-3 | A | D-3 350 T 相電流 | A_-3000_3000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.#3DTR_A3 | #3DTR二次側 T相AMP | MTR | [5 empty] | 319 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 3BUS | #3BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0180 |  |  | 2-B4 |  |  | PT-3 | KV | #3 PT R相電壓 | kV_-18_18(-2000_2000) | baa | B3/D03_A1 | [8 empty] | 南濱DS.23KV#3BUS_KV | 23KV #3BUS KV | BUS | [5 empty] | 320 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D03 | 南濱DS | 22 | 22kV | K361 | 濱61線(K361) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0181 |  |  | 2-B5 |  |  | F21 | A | 濱61線 K361 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱61線KVAR | 23KV濱61線 KVAR | FEEDER | [5 empty] | 321 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K361 | 濱61線(K361) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0182 |  |  | 2-B6 |  |  | F21 | A | 濱61線 K361 R 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱61線A1 | 23KV濱61線 R相AMP | FEEDER | [5 empty] | 322 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K361 | 濱61線(K361) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0183 |  |  | 2-B7 |  |  | F21 | A | 濱61線 K361 S 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱61線A2 | 23KV濱61線 S相AMP | FEEDER | [5 empty] | 323 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K361 | 濱61線(K361) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0184 |  |  | 2-B8 |  |  | F21 | A | 濱61線 K361 T 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱61線A3 | 23KV濱61線 T相AMP | FEEDER | [5 empty] | 324 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K361 | 濱61線(K361) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0185 |  |  | 2-B9 |  |  | F21 | A | 濱61線 K361 N相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱61線A0 | 23KV濱61線 N相AMP | FEEDER | [5 empty] | 325 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K362 | 濱62線(K362) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0186 |  |  | 2-BA |  |  | F22 | KVAR | 濱62線 K362 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱62線KVAR | 23KV濱62線 KVAR | FEEDER | [5 empty] | 326 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K362 | 濱62線(K362) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0187 |  |  | 2-BB |  |  | F22 | A | 濱62線 K362 R 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱62線A1 | 23KV濱62線 R相AMP | FEEDER | [5 empty] | 327 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K362 | 濱62線(K362) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0188 |  |  | 2-BC |  |  | F22 | A | 濱62線 K362 S 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱62線A2 | 23KV濱62線 S相AMP | FEEDER | [5 empty] | 328 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K362 | 濱62線(K362) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0189 |  |  | 2-BD |  |  | F22 | A | 濱62線 K362 T 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱62線A3 | 23KV濱62線 T相AMP | FEEDER | [5 empty] | 329 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K362 | 濱62線(K362) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0190 |  |  | 2-BE |  |  | F22 | A | 濱62線 K362 N相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱62線A0 | 23KV濱62線 N相AMP | FEEDER | [5 empty] | 330 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K363 | 濱63線(K363) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0191 |  |  | 2-BF |  |  | F23 | KVAR | 濱63線 K363 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱63線KVAR | 23KV濱63線 KVAR | FEEDER | [5 empty] | 331 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D03 | 南濱DS | 0 |  | RTU | RTU |  | ADCL4 |  |  | MvMoment | No4 AI參考點 10% |  | Y |  | AI | [6 empty] | 0192 |  |  | 2-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.4 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | [5 empty] | 332 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | RTU | RTU |  | ADCH4 |  |  | MvMoment | No4 AI參考點 90% |  | Y |  | AI | [6 empty] | 0193 |  |  | 2-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.4 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | [5 empty] | 333 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K363 | 濱63線(K363) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0194 |  |  | 2-C2 |  |  | F23 | A | 濱63線 K363 R 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱63線A1 | 23KV濱63線 R相AMP | FEEDER | [5 empty] | 334 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K363 | 濱63線(K363) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0195 |  |  | 2-C3 |  |  | F23 | A | 濱63線 K363 S 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱63線A2 | 23KV濱63線 S相AMP | FEEDER | [5 empty] | 335 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K363 | 濱63線(K363) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0196 |  |  | 2-C4 |  |  | F23 | A | 濱63線 K363 T 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱63線A3 | 23KV濱63線 T相AMP | FEEDER | [5 empty] | 336 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K363 | 濱63線(K363) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0197 |  |  | 2-C5 |  |  | F23 | A | 濱63線 K363 N相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱63線A0 | 23KV濱63線 N相AMP | FEEDER | [5 empty] | 337 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K364 | 濱64線(K364) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0198 |  |  | 2-C6 |  |  | F24 | KVAR | 濱64線 K364 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱64線KVAR | 23KV濱64線 KVAR | FEEDER | [5 empty] | 338 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K364 | 濱64線(K364) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0199 |  |  | 2-C7 |  |  | F24 | A | 濱64線 K364 R 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱64線A1 | 23KV濱64線 R相AMP | FEEDER | [5 empty] | 339 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K364 | 濱64線(K364) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0200 |  |  | 2-C8 |  |  | F24 | A | 濱64線 K364 S 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱64線A2 | 23KV濱64線 S相AMP | FEEDER | [5 empty] | 340 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K364 | 濱64線(K364) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0201 |  |  | 2-C9 |  |  | F24 | A | 濱64線 K364 T 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱64線A3 | 23KV濱64線 T相AMP | FEEDER | [5 empty] | 341 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K364 | 濱64線(K364) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0202 |  |  | 2-CA |  |  | F24 | A | 濱64線 K364 N相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱64線A0 | 23KV濱64線 N相AMP | FEEDER | [5 empty] | 342 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K365 | 濱65線(K365) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0203 |  |  | 2-CB |  |  | F25 | KVAR | 濱65線 K365 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱65線KVAR | 23KV濱65線 KVAR | FEEDER | [5 empty] | 343 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K365 | 濱65線(K365) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0204 |  |  | 2-CC |  |  | F25 | A | 濱65線 K365 R 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱65線A1 | 23KV濱65線 R相AMP | FEEDER | [5 empty] | 344 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K365 | 濱65線(K365) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0205 |  |  | 2-CD |  |  | F25 | A | 濱65線 K365 S 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱65線A2 | 23KV濱65線 S相AMP | FEEDER | [5 empty] | 345 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K365 | 濱65線(K365) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0206 |  |  | 2-CE |  |  | F25 | A | 濱65線 K365 T 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱65線A3 | 23KV濱65線 T相AMP | FEEDER | [5 empty] | 346 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K365 | 濱65線(K365) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0207 |  |  | 2-CF |  |  | F25 | A | 濱65線 K365 N相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱65線A0 | 23KV濱65線 N相AMP | FEEDER | [5 empty] | 347 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K366 | 濱66線(K366) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0208 |  |  | 2-D0 |  |  | F26 | KVAR | 濱66線 K366 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱66線KVAR | 23KV濱66線 KVAR | FEEDER | [5 empty] | 348 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K366 | 濱66線(K366) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0209 |  |  | 2-D1 |  |  | F26 | A | 濱66線 K366 R 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱66線A1 | 23KV濱66線 R相AMP | FEEDER | [5 empty] | 349 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K366 | 濱66線(K366) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0210 |  |  | 2-D2 |  |  | F26 | A | 濱66線 K366 S 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱66線A2 | 23KV濱66線 S相AMP | FEEDER | [5 empty] | 350 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K366 | 濱66線(K366) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0211 |  |  | 2-D3 |  |  | F26 | A | 濱66線 K366 T 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱66線A3 | 23KV濱66線 T相AMP | FEEDER | [5 empty] | 351 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K366 | 濱66線(K366) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0212 |  |  | 2-D4 |  |  | F26 | A | 濱66線 K366 N相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱66線A0 | 23KV濱66線 N相AMP | FEEDER | [5 empty] | 352 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K367 | 濱67線(K367) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0213 |  |  | 2-D5 |  |  | F27 | KVAR | 濱67線 K367 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱67線KVAR | 23KV濱67線 KVAR | FEEDER | [5 empty] | 353 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K367 | 濱67線(K367) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0214 |  |  | 2-D6 |  |  | F27 | A | 濱67線 K367 R 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱67線A1 | 23KV濱67線 R相AMP | FEEDER | [5 empty] | 354 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K367 | 濱67線(K367) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0215 |  |  | 2-D7 |  |  | F27 | A | 濱67線 K367 S 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱67線A2 | 23KV濱67線 S相AMP | FEEDER | [5 empty] | 355 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K367 | 濱67線(K367) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0216 |  |  | 2-D8 |  |  | F27 | A | 濱67線 K367 T 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱67線A3 | 23KV濱67線 T相AMP | FEEDER | [5 empty] | 356 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K367 | 濱67線(K367) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0217 |  |  | 2-D9 |  |  | F27 | A | 濱67線 K367 N相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱67線A0 | 23KV濱67線 N相AMP | FEEDER | [5 empty] | 357 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K368 | 濱68線(K368) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0218 |  |  | 2-DA |  |  | F28 | KVAR | 濱68線 K368 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱68線KVAR | 23KV濱68線 KVAR | FEEDER | [5 empty] | 358 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K368 | 濱68線(K368) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0219 |  |  | 2-DB |  |  | F28 | A | 濱68線 K368 R 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱68線A1 | 23KV濱68線 R相AMP | FEEDER | [5 empty] | 359 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K368 | 濱68線(K368) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0220 |  |  | 2-DC |  |  | F28 | A | 濱68線 K368 S 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱68線A2 | 23KV濱68線 S相AMP | FEEDER | [5 empty] | 360 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K368 | 濱68線(K368) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0221 |  |  | 2-DD |  |  | F28 |  | 濱68線 K368 T 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱68線A3 | 23KV濱68線 T相AMP | FEEDER | [5 empty] | 361 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K368 | 濱68線(K368) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0222 |  |  | 2-DE |  |  | F28 | A | 濱68線 K368 N相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱68線A0 | 23KV濱68線 N相AMP | FEEDER | [5 empty] | 362 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 370 | #4DTR(370) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0223 |  |  | 2-DF |  |  | D-4 | MW | D-4 370 瓦 | MW_-108_108(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.#4DTR_MW | #4DTR二次側 MW | MTR | [5 empty] | 363 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.216 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 370 | #4DTR(370) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0224 |  |  | 2-E0 |  |  | D-4 | MVAR | D-4 370 乏 | MVAR_-72_72(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.#4DTR_MVAR | #4DTR二次側 MVAR | MTR | [5 empty] | 364 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 370 | #4DTR(370) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0225 |  |  | 2-E1 |  |  | D-4 | A | D-4 370 R 相電流 | A_-3000_3000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.#4DTR_A1 | #4DTR二次側 R相AMP | MTR | [5 empty] | 365 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 370 | #4DTR(370) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0226 |  |  | 2-E2 |  |  | D-4 | A | D-4 370 S 相電流 | A_-3000_3000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.#4DTR_A2 | #4DTR二次側 S相AMP | MTR | [5 empty] | 366 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 370 | #4DTR(370) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0227 |  |  | 2-E3 |  |  | D-4 | A | D-4 370 T 相電流 | A_-3000_3000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.#4DTR_A3 | #4DTR二次側 T相AMP | MTR | [5 empty] | 367 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 4BUS | #4BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0228 |  |  | 2-E4 |  |  | PT-4 | KV | #4 PT R相電壓 | kV_-18_18(-2000_2000) | bba | B3/D03_A1 | [8 empty] | 南濱DS.23KV#4BUS_KV | 23KV #4BUS KV | BUS | [5 empty] | 368 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D03 | 南濱DS | 22 | 22kV | K371 | 濱71線(K371) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0229 |  |  | 2-E5 |  |  | F29 | KVAR | 濱71線 K371 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱71線KVAR | 23KV濱71線 KVAR | FEEDER | [5 empty] | 369 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K371 | 濱71線(K371) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0230 |  |  | 2-E6 |  |  | F29 | A | 濱71線 K371 R 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱71線A1 | 23KV濱71線 R相AMP | FEEDER | [5 empty] | 370 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K371 | 濱71線(K371) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0231 |  |  | 2-E7 |  |  | F29 | A | 濱71線 K371 S 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱71線A2 | 23KV濱71線 S相AMP | FEEDER | [5 empty] | 371 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K371 | 濱71線(K371) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0232 |  |  | 2-E8 |  |  | F29 | A | 濱71線 K371 T 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱71線A3 | 23KV濱71線 T相AMP | FEEDER | [5 empty] | 372 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K371 | 濱71線(K371) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0233 |  |  | 2-E9 |  |  | F29 | A | 濱71線 K371 N相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱71線A0 | 23KV濱71線 N相AMP | FEEDER | [5 empty] | 373 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K372 | 濱72線(K372) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0234 |  |  | 2-EA |  |  | F30 | KVAR | 濱72線 K372 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱72線KVAR | 23KV濱72線 KVAR | FEEDER | [5 empty] | 374 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K372 | 濱72線(K372) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0235 |  |  | 2-EB |  |  | F30 | A | 濱72線 K372 R 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱72線A1 | 23KV濱72線 R相AMP | FEEDER | [5 empty] | 375 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K372 | 濱72線(K372) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0236 |  |  | 2-EC |  |  | F30 | A | 濱72線 K372 S 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱72線A2 | 23KV濱72線 S相AMP | FEEDER | [5 empty] | 376 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K372 | 濱72線(K372) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0237 |  |  | 2-ED |  |  | F30 | A | 濱72線 K372 T 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱72線A3 | 23KV濱72線 T相AMP | FEEDER | [5 empty] | 377 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K372 | 濱72線(K372) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0238 |  |  | 2-EE |  |  | F30 | A | 濱72線 K372 N相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱72線A0 | 23KV濱72線 N相AMP | FEEDER | [5 empty] | 378 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K373 | 濱73線(K373) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0239 |  |  | 2-EF |  |  | F31 | KVAR | 濱73線 K373 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱73線KVAR | 23KV濱73線 KVAR | FEEDER | [5 empty] | 379 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K373 | 濱73線(K373) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0240 |  |  | 2-F0 |  |  | F31 | A | 濱73線 K373 R 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱73線A1 | 23KV濱73線 R相AMP | FEEDER | [5 empty] | 380 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K373 | 濱73線(K373) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0241 |  |  | 2-F1 |  |  | F31 | A | 濱73線 K373 S 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱73線A2 | 23KV濱73線 S相AMP | FEEDER | [5 empty] | 381 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K373 | 濱73線(K373) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0242 |  |  | 2-F2 |  |  | F31 | A | 濱73線 K373 T 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱73線A3 | 23KV濱73線 T相AMP | FEEDER | [5 empty] | 382 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K373 | 濱73線(K373) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0243 |  |  | 2-F3 |  |  | F31 | A | 濱73線 K373 N相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱73線A0 | 23KV濱73線 N相AMP | FEEDER | [5 empty] | 383 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K374 | 濱74線(K374) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0244 |  |  | 2-F4 |  |  | F32 | KVAR | 濱74線 K374 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱74線KVAR | 23KV濱74線 KVAR | FEEDER | [5 empty] | 384 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K374 | 濱74線(K374) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0245 |  |  | 2-F5 |  |  | F32 | A | 濱74線 K374 R 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱74線A1 | 23KV濱74線 R相AMP | FEEDER | [5 empty] | 385 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K374 | 濱74線(K374) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0246 |  |  | 2-F6 |  |  | F32 | A | 濱74線 K374 S 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱74線A2 | 23KV濱74線 S相AMP | FEEDER | [5 empty] | 386 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K374 | 濱74線(K374) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0247 |  |  | 2-F7 |  |  | F32 | A | 濱74線 K374 T 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱74線A3 | 23KV濱74線 T相AMP | FEEDER | [5 empty] | 387 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K374 | 濱74線(K374) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0248 |  |  | 2-F8 |  |  | F32 | A | 濱74線 K374 N相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱74線A0 | 23KV濱74線 N相AMP | FEEDER | [5 empty] | 388 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K375 | 濱75線(K375) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0249 |  |  | 2-F9 |  |  | F33 | KVAR | 濱75線 K375 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱75線KVAR | 23KV濱75線 KVAR | FEEDER | [5 empty] | 389 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K375 | 濱75線(K375) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0250 |  |  | 2-FA |  |  | F33 | A | 濱75線 K375 R 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱75線A1 | 23KV濱75線 R相AMP | FEEDER | [5 empty] | 390 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K375 | 濱75線(K375) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0251 |  |  | 2-FB |  |  | F33 | A | 濱75線 K375 S 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱75線A2 | 23KV濱75線 S相AMP | FEEDER | [5 empty] | 391 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K375 | 濱75線(K375) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0252 |  |  | 2-FC |  |  | F33 | A | 濱75線 K375 T 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱75線A3 | 23KV濱75線 T相AMP | FEEDER | [5 empty] | 392 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K375 | 濱75線(K375) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0253 |  |  | 2-FD |  |  | F33 | A | 濱75線 K375 N相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱75線A0 | 23KV濱75線 N相AMP | FEEDER | [5 empty] | 393 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K376 | 濱76線(K376) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0254 |  |  | 2-FE |  |  | F34 | KVAR | 濱76線 K376 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱76線KVAR | 23KV濱76線 KVAR | FEEDER | [5 empty] | 394 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K376 | 濱76線(K376) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0255 |  |  | 2-FF |  |  | F34 | A | 濱76線 K376 R 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱76線A1 | 23KV濱76線 R相AMP | FEEDER | [5 empty] | 395 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | RTU | RTU |  | ADCL5 |  |  | MvMoment | No5 AI參考點 10% |  | Y |  | AI | [6 empty] | 0256 |  |  | 3-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.4 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.AI_ADCL5 | AI 10%參考點 ADCL5 | OTHER | [5 empty] | 396 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | RTU | RTU |  | ADCH5 |  |  | MvMoment | No5 AI參考點 90% |  | Y |  | AI | [6 empty] | 0257 |  |  | 3-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.4 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.AI_ADCH5 | AI 90%參考點 ADCH5 | OTHER | [5 empty] | 397 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K376 | 濱76線(K376) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0258 |  |  | 3-82 |  |  | F34 | A | 濱76線 K376 S 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱76線A2 | 23KV濱76線 S相AMP | FEEDER | [5 empty] | 398 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K376 | 濱76線(K376) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0259 |  |  | 3-83 |  |  | F34 | A | 濱76線 K376 T 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱76線A3 | 23KV濱76線 T相AMP | FEEDER | [5 empty] | 399 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K376 | 濱76線(K376) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0260 |  |  | 3-84 |  |  | F34 | A | 濱76線 K376 N相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱76線A0 | 23KV濱76線 N相AMP | FEEDER | [5 empty] | 400 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K377 | 濱77線(K377) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0261 |  |  | 3-85 |  |  | F35 | KVAR | 濱77線 K377 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱77線KVAR | 23KV濱77線 KVAR | FEEDER | [5 empty] | 401 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K377 | 濱77線(K377) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0262 |  |  | 3-86 |  |  | F35 | A | 濱77線 K377 R 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱77線A1 | 23KV濱77線 R相AMP | FEEDER | [5 empty] | 402 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K377 | 濱77線(K377) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0263 |  |  | 3-87 |  |  | F35 | A | 濱77線 K377 S 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱77線A2 | 23KV濱77線 S相AMP | FEEDER | [5 empty] | 403 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K377 | 濱77線(K377) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0264 |  |  | 3-88 |  |  | F35 | A | 濱77線 K377 T 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱77線A3 | 23KV濱77線 T相AMP | FEEDER | [5 empty] | 404 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K377 | 濱77線(K377) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0265 |  |  | 3-89 |  |  | F35 | A | 濱77線 K377 N相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱77線A0 | 23KV濱77線 N相AMP | FEEDER | [5 empty] | 405 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K378 | 濱78線(K378) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0266 |  |  | 3-8A |  |  | F36 | KVAR | 濱78線 K378 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱78線KVAR | 23KV濱78線 KVAR | FEEDER | [5 empty] | 406 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K378 | 濱78線(K378) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0267 |  |  | 3-8B |  |  | F36 | A | 濱78線 K378 R 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱78線A1 | 23KV濱78線 R相AMP | FEEDER | [5 empty] | 407 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K378 | 濱78線(K378) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0268 |  |  | 3-8C |  |  | F36 | A | 濱78線 K378 S 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱78線A2 | 23KV濱78線 S相AMP | FEEDER | [5 empty] | 408 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K378 | 濱78線(K378) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0269 |  |  | 3-8D |  |  | F36 | A | 濱78線 K378 T 相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱78線A3 | 23KV濱78線 T相AMP | FEEDER | [5 empty] | 409 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | K378 | 濱78線(K378) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0270 |  |  | 3-8E |  |  | F36 | A | 濱78線 K378 N相電流 | A_-600_600(-2000_2000) |  | B2/D03_D1 | [8 empty] | 南濱DS.濱78線A0 | 23KV濱78線 N相AMP | FEEDER | [5 empty] | 410 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 300 | TIE(300) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0271 |  |  | 3-8F |  |  | TIE-4 | A | TIE-4 300 R 相電流 | A_-2000_2000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.23KV_300_A1 | 23KV 300 R相AMP | TIE | [5 empty] | 411 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 300 | TIE(300) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0272 |  |  | 3-90 |  |  | TIE-4 | A | TIE-4 300 S 相電流 | A_-2000_2000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.23KV_300_A2 | 23KV 300 S相AMP | TIE | [5 empty] | 412 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 300 | TIE(300) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0273 |  |  | 3-91 |  |  | TIE-4 | A | TIE-4 300 T 相電流 | A_-2000_2000(-2000_2000) |  | B3/D03_A1 | [8 empty] | 南濱DS.23KV_300_A3 | 23KV 300 T相AMP | TIE | [5 empty] | 413 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 161 | 161kV | 1510 | 安南～南濱一路(1510) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P02D031/T2 |  | 0000 |  |  | 1-00-00 |  |  | 1510 | ON/OFF | 安南南濱一路(1510)CB ON/OFF |  | aaca | B2/D03_A1 | [8 empty] | 南濱DS.1510_CB | 1510(安南南濱一路) CB | LINE161 | [5 empty] | 414 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 161 | 161kV | 1510 | 安南～南濱一路(1510) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0001 |  |  | 1-00-01 |  |  | 1510 | 87A | 安南南濱一路(1510)87A |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1510_87A | 安南南濱一路(1510) 87RY | LINE161 | [5 empty] | 415 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1510 | 安南～南濱一路(1510) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | 1510 | PHA | 安南南濱一路(1510)PHA |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1510_PHA | 安南南濱一路(1510) 相間RY | LINE161 | [5 empty] | 416 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1510 | 安南～南濱一路(1510) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0004 |  |  | 1-00-04 |  |  | 1510 | GDA | 安南南濱一路(1510)GDA |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1510_GDA | 安南南濱一路(1510) 接地RY | LINE161 | [5 empty] | 417 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1520 | 安南～南濱二路(1520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P02D032/T2 |  | 0005 |  |  | 1-00-05 |  |  | 1520 | ON/OFF | 安南南濱二路(1520)CB ON/OFF |  | aaea | B2/D03_A1 | [8 empty] | 南濱DS.1520_CB | 1520(安南南濱二路) CB | LINE161 | [5 empty] | 418 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 161 | 161kV | 1520 | 安南～南濱二路(1520) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | 1520 | 87A | 安南南濱二路(1520)87A |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1520_87A | 安南南濱二路(1520) 87RY | LINE161 | [5 empty] | 419 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1520 | 安南～南濱二路(1520) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-01-00 |  |  | 1520 | PHA | 安南南濱二路(1520)PHA |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1520_PHA | 安南南濱二路(1520) 相間RY | LINE161 | [5 empty] | 420 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1520 | 安南～南濱二路(1520) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | 1520 | GDA | 安南南濱二路(1520)GDA |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1520_GDA | 安南南濱二路(1520) 接地RY | LINE161 | [5 empty] | 421 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱～安瀚線(1530) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D03C33/T1 |  | 0010 |  |  | 1-01-02 |  |  | 1530 | ON/OFF | 南濱安瀚線(1530)CB ON/OFF |  | aaga | B2/D03_A1 | [8 empty] | 南濱DS.1530_CB | 1530(南濱安瀚線) CB | LINE161 | [5 empty] | 422 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱～安瀚線(1530) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-03 |  |  | 1530 | 187A | 南濱安瀚線(1530) 187A |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1530_87A1 | 南濱安瀚線(1530) 第一套 87RY | LINE161 | [5 empty] | 423 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱～安瀚線(1530) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0012 |  |  | 1-01-04 |  |  | 1530 | 287A | 南濱安瀚線(1530) 287A |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1530_87A2 | 南濱安瀚線(1530) 第二套 87RY | LINE161 | [5 empty] | 424 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱～安瀚線(1530) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0013 |  |  | 1-01-05 |  |  | 1530 | PHA | 南濱安瀚線(1530)PHA |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1530_PHA | 南濱安瀚線(1530) 相間RY | LINE161 | [5 empty] | 425 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱～安瀚線(1530) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-06 |  |  | 1530 | GDA | 南濱安瀚線(1530)GDA |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1530_GDA | 南濱安瀚線(1530) 接地RY | LINE161 | [5 empty] | 426 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱～凸版線(1540) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D03C28/T1 |  | 0015 |  |  | 1-01-07 |  |  | 1540 | ON/OFF | 南濱凸版線(1540)CB ON/OFF |  | aaha | B2/D03_A1 | [8 empty] | 南濱DS.1540_CB | 1540(南濱凸版線) CB | LINE161 | [5 empty] | 427 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱～凸版線(1540) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-02-00 |  |  | 1540 | 187A | 南濱凸版線(1540) 187A |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1540_87A1 | 南濱凸版線(1540) 第一套 87RY | LINE161 | [5 empty] | 428 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱～凸版線(1540) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0017 |  |  | 1-02-01 |  |  | 1540 | 287A | 南濱凸版線(1540) 287A |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1540_87A2 | 南濱凸版線(1540) 第二套 87RY | LINE161 | [5 empty] | 429 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱～凸版線(1540) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 |  |  | 1-02-02 |  |  | 1540 | PHA | 南濱凸版線(1540)PHA |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1540_PHA | 南濱凸版線(1540) 相間RY | LINE161 | [5 empty] | 430 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱～凸版線(1540) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0019 |  |  | 1-02-03 |  |  | 1540 | GDA | 南濱凸版線(1540)GDA |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1540_GDA | 南濱凸版線(1540) 接地RY | LINE161 | [5 empty] | 431 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1550 | 南濱～鹿耳紅線(1550) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D03D28R/T1 |  | 0020 |  |  | 1-02-04 |  |  | 1550 | ON/OFF | 南濱鹿耳紅線(1550)CB ON/OFF |  | aaka | B2/D03_A1 | [8 empty] | 南濱DS.1550_CB | 1550(南濱鹿耳紅線) CB | LINE161 | [5 empty] | 432 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 161 | 161kV | 1550 | 南濱～鹿耳紅線(1550) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-05 |  |  | 1550 | 87A | 南濱鹿耳紅線(1550) 87A |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1550_87A | 南濱鹿耳紅線(1550) 87RY | LINE161 | [5 empty] | 433 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1550 | 南濱～鹿耳紅線(1550) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0023 |  |  | 1-02-07 |  |  | 1550 | PHA | 南濱鹿耳紅線(1550)PHA |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1550_PHA | 南濱鹿耳紅線(1550) 相間RY | LINE161 | [5 empty] | 434 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1550 | 南濱～鹿耳紅線(1550) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0024 |  |  | 1-03-00 |  |  | 1550 | GDA | 南濱鹿耳紅線(1550)GDA |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1550_GDA | 南濱鹿耳紅線(1550) 接地RY | LINE161 | [5 empty] | 435 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1560 | 南濱～鹿耳白線(1560) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D03D28W/T1 |  | 0025 |  |  | 1-03-01 |  |  | 1560 | ON/OFF | 南濱鹿耳白線(1560)CB ON/OFF |  | aala | B2/D03_A1 | [8 empty] | 南濱DS.1560_CB | 1560(南濱鹿耳白線) CB | LINE161 | [5 empty] | 436 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 161 | 161kV | 1560 | 南濱～鹿耳白線(1560) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0026 |  |  | 1-03-02 |  |  | 1560 | 87A | 南濱鹿耳白線(1560) 87A |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1560_87A | 南濱鹿耳白線(1560) 87RY | LINE161 | [5 empty] | 437 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1560 | 南濱～鹿耳白線(1560) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0028 |  |  | 1-03-04 |  |  | 1560 | PHA | 南濱鹿耳白線(1560)PHA |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1560_PHA | 南濱鹿耳白線(1560) 相間RY | LINE161 | [5 empty] | 438 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1560 | 南濱～鹿耳白線(1560) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0029 |  |  | 1-03-05 |  |  | 1560 | GDA | 南濱鹿耳白線(1560)GDA |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1560_GDA | 南濱鹿耳白線(1560) 接地RY | LINE161 | [5 empty] | 439 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0050 |  |  | 1-06-02 |  |  | Locate Empty |  | TIE(1500)CB 52AS |  | aafz | B2/D03_A1 | [8 empty] | 南濱DS.1500_CB | 1500(TIE) CB | TIE | [5 empty] | 440 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0051 |  |  | 1-06-03 |  |  | Locate Empty |  | TIE(1500)RY 50A |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1500_50A | 161KV TIE(1500) 50RY | TIE | [5 empty] | 441 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | 161KV #1 BUS | 87B1A | 161KV #1BUS 87A |  |  | B2/D03_A1 | [8 empty] | 南濱DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | [5 empty] | 442 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0053 |  |  | 1-06-05 |  |  | 161KV #2 BUS | 87B2A | 161KV #2BUS 87A |  |  | B2/D03_A1 | [8 empty] | 南濱DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | [5 empty] | 443 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0054 |  |  | 1-06-06 |  |  | Locate Empty |  | 161KV 79 RY RCA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | [5 empty] | 444 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0055 |  |  | 1-06-07 |  |  | OSCA | A/N | 161KV示波器啟動警報OSCA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.161KV_OSCA | 161KV示波器啟動警報 | OTHER | [5 empty] | 445 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/1DTR |  | 0056 |  |  | 1-07-00 |  |  | Locate Empty |  | NO.1 1750 CB 52AS |  | aabb | ELEM/D03_A1 | [8 empty] | 南濱DS.1750_CB | 1750(#1DTR) CB | MTR | [5 empty] | 446 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS |  |  | 1DTR | #1DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0057 |  |  | 1-07-01 |  |  | Locate Empty |  | NO.1 DTR 87A 87A |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#1DTR_87A | #1DTR 87RY | MTR | [5 empty] | 447 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS |  |  | 1DTR | #1DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0058 |  |  | 1-07-02 |  |  | Locate Empty |  | NO.1 DTR 機械保護動作(96PA) |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | [5 empty] | 448 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS |  |  | 1DTR | #1DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0059 |  |  | 1-07-03 |  |  | Locate Empty |  | NO.1 DTR 51ZA 51ZA |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | [5 empty] | 449 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS |  |  | 1DTR | #1DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0060 |  |  | 1-07-04 |  |  | Locate Empty |  | NO.1 DTR PHA PHA |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#1DTR_51A | #1DTR 51RY | MTR | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS |  |  | 1DTR | #1DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0061 |  |  | 1-07-05 |  |  | Locate Empty |  | NO.1 DTR GDA GDA |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#1DTR_51NA | #1DTR 51N RY | MTR | [5 empty] | 451 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | T/1DTR(A) |  |  | 0062 |  |  | 1-07-06 |  |  | Locate Empty |  | D1A 310 CB 52AS |  | abhb | ELEM/D03_A1 | [8 empty] | 南濱DS.310_CB | 310(#1DTR) CB | MTR | [5 empty] | 452 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0063 |  |  | 1-07-07 |  |  | Locate Empty |  | D1A 310 (51-3φ)PHA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.310_51A | #1DTR二次側(310) 51RY | MTR | [5 empty] | 453 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0064 |  |  | 1-08-00 |  |  | Locate Empty |  | D1A 310 PHA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.310_PHA2 | 310開關箱IED RY PHA | OTHER | [5 empty] | 454 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0065 |  |  | 1-08-01 |  |  | Locate Empty |  | D1A 310 GDA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.310_GDA | 310開關箱IED RY GDA | OTHER | [5 empty] | 455 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | T/1DTR(B) |  |  | 0066 |  |  | 1-08-02 |  |  | Locate Empty |  | D1B 320 CB 52AS |  | acca | ELEM/D03_A1 | [8 empty] | 南濱DS.320_CB | 320(#1DTR) CB | MTR | [5 empty] | 456 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0067 |  |  | 1-08-03 |  |  | Locate Empty |  | D1B 320 (51-3φ)PHA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.320_51A | #1DTR二次側(320) 51RY | MTR | [5 empty] | 457 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 |  |  | 1-08-04 |  |  | Locate Empty |  | D1B 320 PHA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.320_PHA2 | 320開關箱IED RY PHA | OTHER | [5 empty] | 458 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 |  |  | 1-08-05 |  |  | Locate Empty |  | D1B 320 GDA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.320_GDA | 320開關箱IED RY GDA | OTHER | [5 empty] | 459 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2DTR |  | 0070 |  |  | 1-08-06 |  |  | Locate Empty |  | NO.2 1760 CB 52AS |  | aadb | ELEM/D03_A1 | [8 empty] | 南濱DS.1760_CB | 1760(#2DTR) CB | MTR | [5 empty] | 460 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS |  |  | 2DTR | #2DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0071 |  |  | 1-08-07 |  |  | Locate Empty |  | NO.2 DTR 87A 87A |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#2DTR_87A | #2DTR 87RY | MTR | [5 empty] | 461 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS |  |  | 2DTR | #2DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0072 |  |  | 1-09-00 |  |  | Locate Empty |  | NO.2 DTR 機械保護動作(96PA) |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | [5 empty] | 462 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS |  |  | 2DTR | #2DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0073 |  |  | 1-09-01 |  |  | Locate Empty |  | NO.2 DTR 51ZA 51ZA |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | [5 empty] | 463 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS |  |  | 2DTR | #2DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-09-02 |  |  | Locate Empty |  | NO.2 DTR PHA |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#2DTR_PHA | 2DTR PHA | OTHER | [5 empty] | 464 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS |  |  | 2DTR | #2DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0075 |  |  | 1-09-03 |  |  | Locate Empty |  | NO.2 DTR GDA |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#2DTR_GDA | 2DTR GDA | OTHER | [5 empty] | 465 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | T/2DTR(A) |  |  | 0076 |  |  | 1-09-04 |  |  | Locate Empty |  | D2A 330 CB 52AS |  | aaia | ELEM/D03_A1 | [8 empty] | 南濱DS.330_CB | 330(#2DTR) CB | MTR | [5 empty] | 466 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0077 |  |  | 1-09-05 |  |  | Locate Empty |  | D2A 330 81 A |  |  | ELEM/D03_A1 | [8 empty] | 南濱DS.81RY_A/S(1) | 330 81RY A/S | OTHER | [5 empty] | 467 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
D03 | 南濱DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0078 |  |  | 1-09-06 |  |  | Locate Empty |  | D2A 330 PHA PHA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.330_PHA2 | 330開關箱IED RY PHA | OTHER | [5 empty] | 468 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0079 |  |  | 1-09-07 |  |  | Locate Empty |  | D2A 330 GDA GDA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.330_GDA | 330開關箱IED RY GDA | OTHER | [5 empty] | 469 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | T/2DTR(B) |  |  | 0080 |  |  | 1-0A-00 |  |  | Locate Empty |  | D2B 340 CB 52AS |  | adba | ELEM/D03_A1 | [8 empty] | 南濱DS.340_CB | 340(#2DTR) CB | MTR | [5 empty] | 470 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0081 |  |  | 1-0A-01 |  |  | Locate Empty |  | D2B 340 81 A |  |  | ELEM/D03_A1 | [8 empty] | 南濱DS.81RY_A/S(2) | 340 81RY A/S | OTHER | [5 empty] | 471 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
D03 | 南濱DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0082 |  |  | 1-0A-02 |  |  | Locate Empty |  | D2B 340 PHA PHA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.340_PHA2 | 340開關箱IED RY PHA | OTHER | [5 empty] | 472 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0083 |  |  | 1-0A-03 |  |  | Locate Empty |  | D2B 340 GDA GDA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.340_GDA | 340開關箱IED RY GDA | OTHER | [5 empty] | 473 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/3DTR |  | 0084 |  |  | 1-0A-04 |  |  | Locate Empty |  | NO.3 1770 CB 52AS |  | aaib | ELEM/D03_A1 | [8 empty] | 南濱DS.1770_CB | 1770(#3DTR) CB | MTR | [5 empty] | 474 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS |  |  | 3DTR | #3DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0085 |  |  | 1-0A-05 |  |  | Locate Empty |  | NO.3 DTR 87A 87A |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#3DTR_87A | #3DTR 87RY | MTR | [5 empty] | 475 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS |  |  | 3DTR | #3DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0086 |  |  | 1-0A-06 |  |  | Locate Empty |  | NO.3 DTR 機械保護動作(96PA) |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#3DTR_96PA | #3DTR 機械保護動作 | MTR | [5 empty] | 476 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS |  |  | 3DTR | #3DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0087 |  |  | 1-0A-07 |  |  | Locate Empty |  | NO.3 DTR 51ZA 51ZA |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#3DTR_51ZA | #3DTR 51Z RY | MTR | [5 empty] | 477 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS |  |  | 3DTR | #3DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0088 |  |  | 1-0B-00 |  |  | Locate Empty |  | NO.3 DTR PHA PHA |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#3DTR_51A | #3DTR 51RY | MTR | [5 empty] | 478 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS |  |  | 3DTR | #3DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0089 |  |  | 1-0B-01 |  |  | Locate Empty |  | NO.3 DTR GDA GDA |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#3DTR_51NA | #3DTR 51N RY | MTR | [5 empty] | 479 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | 350 | #3DTR(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3Bus | T/3DTR |  |  | 0090 |  |  | 1-0B-02 |  |  | Locate Empty |  | D3 350 CB 52AS |  | bala | ELEM/D03_A1 | [8 empty] | 南濱DS.350_CB | 350(#3DTR) CB | MTR | [5 empty] | 480 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | 350 | #3DTR(350) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0091 |  |  | 1-0B-03 |  |  | Locate Empty |  | D3 350 (51-3φ)PHA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.350_51A | #3DTR二次側(350) 51RY | MTR | [5 empty] | 481 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | 350 | #3DTR(350) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0092 |  |  | 1-0B-04 |  |  | Locate Empty |  | D3 350 PHA PHA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.350_PHA2 | 350開關箱IED RY PHA | OTHER | [5 empty] | 482 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | 350 | #3DTR(350) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0093 |  |  | 1-0B-05 |  |  | Locate Empty |  | D3 350 GDA GDA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.350_GDA | 350開關箱IED RY GDA | OTHER | [5 empty] | 483 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1780 | #4DTR(1780) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/4DTR |  | 0094 |  |  | 1-0B-06 |  |  | Locate Empty |  | NO.4 1780 CB 52AS |  | aajb | ELEM/D03_A1 | [8 empty] | 南濱DS.1780_CB | 1780(#4DTR) CB | MTR | [5 empty] | 484 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS |  |  | 4DTR | #4DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0095 |  |  | 1-0B-07 |  |  | Locate Empty |  | NO.4 DTR 87A 87A |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#4DTR_87A | #4DTR 87RY | MTR | [5 empty] | 485 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS |  |  | 4DTR | #4DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0096 |  |  | 1-0C-00 |  |  | Locate Empty |  | NO.4 DTR 機械保護動作(96PA) |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#4DTR_96PA | #4DTR 機械保護動作 | MTR | [5 empty] | 486 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS |  |  | 4DTR | #4DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0097 |  |  | 1-0C-01 |  |  | Locate Empty |  | NO.4 DTR 51ZA 51ZA |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#4DTR_51ZA | #4DTR 51Z RY | MTR | [5 empty] | 487 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS |  |  | 4DTR | #4DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0098 |  |  | 1-0C-02 |  |  | Locate Empty |  | NO.4 DTR PHA PHA |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#4DTR_51A | #4DTR 51RY | MTR | [5 empty] | 488 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS |  |  | 4DTR | #4DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0099 |  |  | 1-0C-03 |  |  | Locate Empty |  | NO.4 DTR GDA GDA |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#4DTR_51NA | #4DTR 51N RY | MTR | [5 empty] | 489 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | 370 | #4DTR(370) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4Bus | T/4DTR |  |  | 0100 |  |  | 1-0C-04 |  |  | Locate Empty |  | D4 370 CB 52AS |  | bbba | ELEM/D03_A1 | [8 empty] | 南濱DS.370_CB | 370(#4DTR) CB | MTR | [5 empty] | 490 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | 370 | #4DTR(370) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0101 |  |  | 1-0C-05 |  |  | Locate Empty |  | D4 370 (51-3φ)PHA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.370_51A | #4DTR二次側(370) 51RY | MTR | [5 empty] | 491 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | 370 | #4DTR(370) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0102 |  |  | 1-0C-06 |  |  | Locate Empty |  | D4 370 PHA PHA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.370_PHA2 | 370開關箱IED RY PHA | OTHER | [5 empty] | 492 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | 370 | #4DTR(370) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0103 |  |  | 1-0C-07 |  |  | Locate Empty |  | D4 370 GDA GDA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.370_GDA | 370開關箱IED RY GDA | OTHER | [5 empty] | 493 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | RTU | RTU |  | RTU_MCT |  |  | Status | RTU Master Ry | Open/Close | Y | E | DI-SP | [6 empty] | 0104 |  |  | 1-0D-00 |  |  | 161RTU | MCT_ SOE | RTU MASTER RY SOE |  |  | B3/D03_A1 | [16 empty] | 494 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D03 | 南濱DS | 11 | 11kV | 210 | #1SC(210) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | A/LBS210^C/1SC(A) |  |  | 0160 |  |  | 1-14-00 |  |  | #1ASC | ON/OFF | #1SC 210 CB 52AS |  | abgb | B3/D03_A1 | [8 empty] | 南濱DS.210_CB | 210(11KV #1SC) CB | SC | [5 empty] | 495 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0161 |  |  | 1-14-01 |  |  | #1ASC | SCA | #1SC 210 CB RY SCA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.210_SCA | 11KV #1SC 51,51N RY | SC | [5 empty] | 496 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0162 |  |  | 1-14-02 |  |  | #1ASC | UVA | #1SC 210 CB RY UVA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | [5 empty] | 497 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K311 | 濱11線(K311) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/K311/T1 |  |  | 0163 |  |  | 1-14-03 |  |  | F1 | ON/OFF | 濱11線 K311 CB 52AS |  | abfb | B2/D03_D1 | [8 empty] | 南濱DS.K311_CB | K311(11KV濱11線) CB | FEEDER | [5 empty] | 498 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K311 | 濱11線(K311) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0164 |  |  | 1-14-04 |  |  | F1 | PHA | 濱11線 K311 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K311_PHA | 11KV濱11線(K311) 相間RY | FEEDER | [5 empty] | 499 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K311 | 濱11線(K311) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0165 |  |  | 1-14-05 |  |  | F1 | GDA | 濱11線 K311 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K311_GDA | 11KV濱11線(K311) 接地RY | FEEDER | [5 empty] | 500 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K312 | 濱12線(K312) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/K312/T1 |  |  | 0166 |  |  | 1-14-06 |  |  | F2 | ON/OFF | 濱12線 K312 CB 52AS |  | abeb | B2/D03_D1 | [8 empty] | 南濱DS.K312_CB | K312(11KV濱12線) CB | FEEDER | [5 empty] | 501 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K312 | 濱12線(K312) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0167 |  |  | 1-14-07 |  |  | F2 | PHA | 濱12線 K312 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K312_PHA | 11KV濱12線(K312) 相間RY | FEEDER | [5 empty] | 502 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K312 | 濱12線(K312) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0168 |  |  | 1-15-00 |  |  | F2 | GDA | 濱12線 K312 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K312_GDA | 11KV濱12線(K312) 接地RY | FEEDER | [5 empty] | 503 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K313 | 濱13線(K313) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/K313/T1 |  |  | 0169 |  |  | 1-15-01 |  |  | F3 | ON/OFF | 濱13線 K313 CB 52AS |  | abdb | B2/D03_D1 | [8 empty] | 南濱DS.K313_CB | K313(11KV濱13線) CB | FEEDER | [5 empty] | 504 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K313 | 濱13線(K313) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0170 |  |  | 1-15-02 |  |  | F3 | PHA | 濱13線 K313 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K313_PHA | 11KV濱13線(K313) 相間RY | FEEDER | [5 empty] | 505 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K313 | 濱13線(K313) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0171 |  |  | 1-15-03 |  |  | F3 | GDA | 濱13線 K313 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K313_GDA | 11KV濱13線(K313) 接地RY | FEEDER | [5 empty] | 506 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K314 | 濱14線(K314) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/K314/T1 |  |  | 0172 |  |  | 1-15-04 |  |  | F4 | ON/OFF | 濱14線 K314 CB 52AS |  | abcb | B2/D03_D1 | [8 empty] | 南濱DS.K314_CB | K314(11KV濱14線) CB | FEEDER | [5 empty] | 507 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K314 | 濱14線(K314) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0173 |  |  | 1-15-05 |  |  | F4 | PHA | 濱14線 K314 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K314_PHA | 11KV濱14線(K314) 相間RY | FEEDER | [5 empty] | 508 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K314 | 濱14線(K314) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0174 |  |  | 1-15-06 |  |  | F4 | GDA | 濱14線 K314 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K314_GDA | 11KV濱14線(K314) 接地RY | FEEDER | [5 empty] | 509 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K315 | 濱15線(K315) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/K315/T1 |  |  | 0175 |  |  | 1-15-07 |  |  | F5 | ON/OFF | 濱15線 K315 CB 52AS |  | abbb | B2/D03_D1 | [8 empty] | 南濱DS.K315_CB | K315(11KV濱15線) CB | FEEDER | [5 empty] | 510 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K315 | 濱15線(K315) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0176 |  |  | 1-16-00 |  |  | F5 | PHA | 濱15線 K315 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K315_PHA | 11KV濱15線(K315) 相間RY | FEEDER | [5 empty] | 511 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K315 | 濱15線(K315) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0177 |  |  | 1-16-01 |  |  | F5 | GDA | 濱15線 K315 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K315_GDA | 11KV濱15線(K315) 接地RY | FEEDER | [5 empty] | 512 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 100 | TIE(100) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/1ABus | B/2ABus |  |  | 0178 |  |  | 1-16-02 |  |  | TIE-1 | ON/OFF | TIE-1 100 CB 52AS |  | abab | B3/D03_A1 | [8 empty] | 南濱DS.100_CB | 100(TIE) CB | TIE | [5 empty] | 513 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | 100 | TIE(100) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0179 |  |  | 1-16-03 |  |  | TIE-1 | PHA | TIE-1 100 RY PHA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.100_51A | 11KV TIE(100) 51RY | TIE | [5 empty] | 514 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 100 | TIE(100) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0180 |  |  | 1-16-04 |  |  | TIE-1 | GDA | TIE-1 100 RY GDA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.100_51NA | 11KV TIE(100) 51N RY | TIE | [5 empty] | 515 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 390 | #1SSTR(390) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | T/1SSTR |  |  | 0181 |  |  | 1-16-05 |  |  | #1SSTR | ON/OFF | SSTR-1 390 CB 52AS |  | acbb | B3/D03_A1 | [8 empty] | 南濱DS.390_CB | 390(#1SSTR) CB | OTHER | [5 empty] | 516 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | 390 | #1SSTR(390) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0182 |  |  | 1-16-06 |  |  | #1SSTR | PHA | SSTR-1 390 RY PHA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.#1SSTR_51A | #1SSTR 51RY | OTHER | [5 empty] | 517 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 390 | #1SSTR(390) |  | GDA |  | B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0183 |  |  | 1-16-07 |  |  | #1SSTR | GDA | SSTR-1 390 RY GDA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | [5 empty] | 518 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 220 | #2SC(220) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | A/LBS220^C/2SC(A) |  |  | 0184 |  |  | 1-17-00 |  |  | #1BSC | ON/OFF | #2SC 220 CB 52AS |  | acdb | B3/D03_A1 | [8 empty] | 南濱DS.220_CB | 220(11KV #2SC) CB | SC | [5 empty] | 519 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0185 |  |  | 1-17-01 |  |  | #1BSC | SCA | #2SC 220 CB RY SCA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.220_SCA | 11KV #2SC 51,51N RY | SC | [5 empty] | 520 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0186 |  |  | 1-17-02 |  |  | #1BSC | UVA | #2SC 220 CB RY UVA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | [5 empty] | 521 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K316 | 濱16線(K316) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/K316/T1 |  |  | 0187 |  |  | 1-17-03 |  |  | F6 | ON/OFF | 濱16線 K316 CB 52AS |  | aceb | B2/D03_D1 | [8 empty] | 南濱DS.K316_CB | K316(11KV濱16線) CB | FEEDER | [5 empty] | 522 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K316 | 濱16線(K316) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0188 |  |  | 1-17-04 |  |  | F6 | PHA | 濱16線 K316 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K316_PHA | 11KV濱16線(K316) 相間RY | FEEDER | [5 empty] | 523 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K316 | 濱16線(K316) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0189 |  |  | 1-17-05 |  |  | F6 | GDA | 濱16線 K316 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K316_GDA | 11KV濱16線(K316) 接地RY | FEEDER | [5 empty] | 524 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K317 | 濱17線(K317) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/K317/T1 |  |  | 0190 |  |  | 1-17-06 |  |  | F7 | ON/OFF | 濱17線 K317 CB 52AS |  | acfb | B2/D03_D1 | [8 empty] | 南濱DS.K317_CB | K317(11KV濱17線) CB | FEEDER | [5 empty] | 525 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K317 | 濱17線(K317) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0191 |  |  | 1-17-07 |  |  | F7 | PHA | 濱17線 K317 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K317_PHA | 11KV濱17線(K317) 相間RY | FEEDER | [5 empty] | 526 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K317 | 濱17線(K317) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0192 |  |  | 1-18-00 |  |  | F7 | GDA | 濱17線 K317 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K317_GDA | 11KV濱17線(K317) 接地RY | FEEDER | [5 empty] | 527 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K318 | 濱18線(K318) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/K318/T1 |  |  | 0193 |  |  | 1-18-01 |  |  | F8 | ON/OFF | 濱18線 K318 CB 52AS |  | acgb | B2/D03_D1 | [8 empty] | 南濱DS.K318_CB | K318(11KV濱18線) CB | FEEDER | [5 empty] | 528 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K318 | 濱18線(K318) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0194 |  |  | 1-18-02 |  |  | F8 | PHA | 濱18線 K318 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K318_PHA | 11KV濱18線(K318) 相間RY | FEEDER | [5 empty] | 529 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K318 | 濱18線(K318) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0195 |  |  | 1-18-03 |  |  | F8 | GDA | 濱18線 K318 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K318_GDA | 11KV濱18線(K318) 接地RY | FEEDER | [5 empty] | 530 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K319 | 濱19線(K319) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/K319/T1 |  |  | 0196 |  |  | 1-18-04 |  |  | F9 | ON/OFF | 濱19線 K319 CB 52AS |  | achb | B2/D03_D1 | [8 empty] | 南濱DS.K319_CB | K319(11KV濱19線) CB | FEEDER | [5 empty] | 531 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K319 | 濱19線(K319) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0197 |  |  | 1-18-05 |  |  | F9 | PHA | 濱19線 K319 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K319_PHA | 11KV濱19線(K319) 相間RY | FEEDER | [5 empty] | 532 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K319 | 濱19線(K319) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0198 |  |  | 1-18-06 |  |  | F9 | GDA | 濱19線 K319 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K319_GDA | 11KV濱19線(K319) 接地RY | FEEDER | [5 empty] | 533 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K320 | 濱20線(K320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/K320/T1 |  |  | 0199 |  |  | 1-18-07 |  |  | F10 | ON/OFF | 濱20線 K320 CB 52AS |  | acib | B2/D03_D1 | [8 empty] | 南濱DS.K320_CB | K320(11KV濱20線) CB | FEEDER | [5 empty] | 534 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K320 | 濱20線(K320) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0200 |  |  | 1-19-00 |  |  | F10 | PHA | 濱20線 K320 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K320_PHA | 11KV濱20線(K320) 相間RY | FEEDER | [5 empty] | 535 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K320 | 濱20線(K320) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0201 |  |  | 1-19-01 |  |  | F10 | GDA | 濱20線 K320 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K320_GDA | 11KV濱20線(K320) 接地RY | FEEDER | [5 empty] | 536 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 230 | #3SC(230) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | A/LBS230^C/3SC(A) |  |  | 0256 |  |  | 2-00-00 |  |  | #2ASC | ON/OFF | #3SC 230 CB 52AS |  | aahb | B3/D03_A1 | [8 empty] | 南濱DS.230_CB | 230(11KV #3SC) CB | SC | [5 empty] | 537 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | 230 | #3SC(230) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0257 |  |  | 2-00-01 |  |  | #2ASC | SCA | #3SC 230 RY SCA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.230_SCA | 11KV #3SC 51,51N RY | SC | [5 empty] | 538 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 230 | #3SC(230) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0258 |  |  | 2-00-02 |  |  | #2ASC | UVA | #3SC 230 RY UVA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | [5 empty] | 539 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K321 | 濱21線(K321) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/K321/T1 |  |  | 0259 |  |  | 2-00-03 |  |  | F11 | ON/OFF | 濱21線 K321 CB 52AS |  | aagb | B2/D03_D1 | [8 empty] | 南濱DS.K321_CB | K321(11KV濱21線) CB | FEEDER | [5 empty] | 540 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K321 | 濱21線(K321) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0260 |  |  | 2-00-04 |  |  | F11 | PHA | 濱21線 K321 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K321_PHA | 11KV濱21線(K321) 相間RY | FEEDER | [5 empty] | 541 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K321 | 濱21線(K321) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0261 |  |  | 2-00-05 |  |  | F11 | GDA | 濱21線 K321 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K321_GDA | 11KV濱21線(K321) 接地RY | FEEDER | [5 empty] | 542 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K322 | 濱22線(K322) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/K322/T1 |  |  | 0262 |  |  | 2-00-06 |  |  | F12 | ON/OFF | 濱22線 K322 CB 52AS |  | aafb | B2/D03_D1 | [8 empty] | 南濱DS.K322_CB | K322(11KV濱22線) CB | FEEDER | [5 empty] | 543 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K322 | 濱22線(K322) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0263 |  |  | 2-00-07 |  |  | F12 | PHA | 濱22線 K322 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K322_PHA | 11KV濱22線(K322) 相間RY | FEEDER | [5 empty] | 544 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K322 | 濱22線(K322) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0264 |  |  | 2-01-00 |  |  | F12 | GDA | 濱22線 K322 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K322_GDA | 11KV濱22線(K322) 接地RY | FEEDER | [5 empty] | 545 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K323 | 濱23線(K323) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/K323/T1 |  |  | 0265 |  |  | 2-01-01 |  |  | F13 | ON/OFF | 濱23線 K323 CB 52AS |  | aaeb | B2/D03_D1 | [8 empty] | 南濱DS.K323_CB | K323(11KV濱23線) CB | FEEDER | [5 empty] | 546 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K323 | 濱23線(K323) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0266 |  |  | 2-01-02 |  |  | F13 | PHA | 濱23線 K323 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K323_PHA | 11KV濱23線(K323) 相間RY | FEEDER | [5 empty] | 547 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K323 | 濱23線(K323) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0267 |  |  | 2-01-03 |  |  | F13 | GDA | 濱23線 K323 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K323_GDA | 11KV濱23線(K323) 接地RY | FEEDER | [5 empty] | 548 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K324 | 濱24線(K324) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/K324/T1 |  |  | 0268 |  |  | 2-01-04 |  |  | F14 | ON/OFF | 濱24線 K324 CB 52AS |  | aabb | B2/D03_D1 | [8 empty] | 南濱DS.K324_CB | K324(11KV濱24線) CB | FEEDER | [5 empty] | 549 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K324 | 濱24線(K324) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0269 |  |  | 2-01-05 |  |  | F14 | PHA | 濱24線 K324 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K324_PHA | 11KV濱24線(K324) 相間RY | FEEDER | [5 empty] | 550 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K324 | 濱24線(K324) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0270 |  |  | 2-01-06 |  |  | F14 | GDA | 濱24線 K324 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K324_GDA | 11KV濱24線(K324) 接地RY | FEEDER | [5 empty] | 551 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K325 | 濱25線(K325) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/K325/T1 |  |  | 0271 |  |  | 2-01-07 |  |  | F15 | ON/OFF | 濱25線 K325 CB 52AS |  | aaab | B2/D03_D1 | [8 empty] | 南濱DS.K325_CB | K325(11KV濱25線) CB | FEEDER | [5 empty] | 552 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K325 | 濱25線(K325) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0272 |  |  | 2-02-00 |  |  | F15 | PHA | 濱25線 K325 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K325_PHA | 11KV濱25線(K325) 相間RY | FEEDER | [5 empty] | 553 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K325 | 濱25線(K325) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0273 |  |  | 2-02-01 |  |  | F15 | GDA | 濱25線 K325 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K325_GDA | 11KV濱25線(K325) 接地RY | FEEDER | [5 empty] | 554 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 240 | #4SC(240) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | A/LBS240^C/4SC(A) |  |  | 0274 |  |  | 2-02-02 |  |  | #2BSC | ON/OFF | #4SC 240 CB 52AS |  | adcb | B3/D03_A1 | [8 empty] | 南濱DS.240_CB | 240(11KV #4SC) CB | SC | [5 empty] | 555 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | 240 | #4SC(240) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0275 |  |  | 2-02-03 |  |  | #2BSC | SCA | #4SC 240 RY SCA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.240_SCA | 11KV #4SC 51,51N RY | SC | [5 empty] | 556 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 240 | #4SC(240) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0276 |  |  | 2-02-04 |  |  | #2BSC | UVA | #4SC 240 RY UVA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.240_UVA | 11KV #4SC 27RY(欠壓) | SC | [5 empty] | 557 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K326 | 濱26線(K326) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/K326/T1 |  |  | 0277 |  |  | 2-02-05 |  |  | F16 | ON/OFF | 濱26線 K326 CB 52AS |  | addb | B2/D03_D1 | [8 empty] | 南濱DS.K326_CB | K326(11KV濱26線) CB | FEEDER | [5 empty] | 558 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K326 | 濱26線(K326) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0278 |  |  | 2-02-06 |  |  | F16 | PHA | 濱26線 K326 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K326_PHA | 11KV濱26線(K326) 相間RY | FEEDER | [5 empty] | 559 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K326 | 濱26線(K326) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0279 |  |  | 2-02-07 |  |  | F16 | GDA | 濱26線 K326 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K326_GDA | 11KV濱26線(K326) 接地RY | FEEDER | [5 empty] | 560 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K327 | 濱27線(K327) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/K327/T1 |  |  | 0280 |  |  | 2-03-00 |  |  | F17 | ON/OFF | 濱27線 K327 CB 52AS |  | adeb | B2/D03_D1 | [8 empty] | 南濱DS.K327_CB | K327(11KV濱27線) CB | FEEDER | [5 empty] | 561 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K327 | 濱27線(K327) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0281 |  |  | 2-03-01 |  |  | F17 | PHA | 濱27線 K327 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K327_PHA | 11KV濱27線(K327) 相間RY | FEEDER | [5 empty] | 562 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K327 | 濱27線(K327) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0282 |  |  | 2-03-02 |  |  | F17 | GDA | 濱27線 K327 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K327_GDA | 11KV濱27線(K327) 接地RY | FEEDER | [5 empty] | 563 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K328 | 濱28線(K328) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/K328/T1 |  |  | 0283 |  |  | 2-03-03 |  |  | F18 | ON/OFF | 濱28線 K328 CB 52AS |  | adfb | B2/D03_D1 | [8 empty] | 南濱DS.K328_CB | K328(11KV濱28線) CB | FEEDER | [5 empty] | 564 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K328 | 濱28線(K328) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0284 |  |  | 2-03-04 |  |  | F18 | PHA | 濱28線 K328 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K328_PHA | 11KV濱28線(K328) 相間RY | FEEDER | [5 empty] | 565 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K328 | 濱28線(K328) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0285 |  |  | 2-03-05 |  |  | F18 | GDA | 濱28線 K328 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K328_GDA | 11KV濱28線(K328) 接地RY | FEEDER | [5 empty] | 566 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K329 | 濱29線(K329) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/K329/T1 |  |  | 0286 |  |  | 2-03-06 |  |  | F19 | ON/OFF | 濱29線 K329 CB 52AS |  | adib | B2/D03_D1 | [8 empty] | 南濱DS.K329_CB | K329(11KV濱29線) CB | FEEDER | [5 empty] | 567 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K329 | 濱29線(K329) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0287 |  |  | 2-03-07 |  |  | F19 | PHA | 濱29線 K329 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K329_PHA | 11KV濱29線(K329) 相間RY | FEEDER | [5 empty] | 568 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K329 | 濱29線(K329) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0288 |  |  | 2-04-00 |  |  | F19 | GDA | 濱29線 K329 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K329_GDA | 11KV濱29線(K329) 接地RY | FEEDER | [5 empty] | 569 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K330 | 濱30線(K330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/K330/T1 |  |  | 0289 |  |  | 2-04-01 |  |  | F20 | ON/OFF | 濱30線 K330 CB 52AS |  | adjb | B2/D03_D1 | [8 empty] | 南濱DS.K330_CB | K330(11KV濱30線) CB | FEEDER | [5 empty] | 570 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K330 | 濱30線(K330) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0290 |  |  | 2-04-02 |  |  | F20 | PHA | 濱30線 K330 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K330_PHA | 11KV濱30線(K330) 相間RY | FEEDER | [5 empty] | 571 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K330 | 濱30線(K330) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0291 |  |  | 2-04-03 |  |  | F20 | GDA | 濱30線 K330 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K330_GDA | 11KV濱30線(K330) 接地RY | FEEDER | [5 empty] | 572 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 200 | TIE(200) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/2BBus | B/1BBus |  |  | 0292 |  |  | 2-04-04 |  |  | TIE-2 | ON/OFF | TIE-2 200 CB 52AS |  | adab | B3/D03_A1 | [8 empty] | 南濱DS.200_CB | 200(TIE) CB | TIE | [5 empty] | 573 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | 200 | TIE(200) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0293 |  |  | 2-04-05 |  |  | TIE-2 | PHA | TIE-2 200 RY PHA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.200_51A | 11KV TIE(200) 51RY | TIE | [5 empty] | 574 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 200 | TIE(200) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0294 |  |  | 2-04-06 |  |  | TIE-2 | GDA | TIE-2 200 RY GDA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.200_51NA | 11KV TIE(200) 51N RY | TIE | [5 empty] | 575 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | 250 | #5SC(250) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3Bus | C/5SC |  |  | 0295 |  |  | 2-04-07 |  |  | #3ASC | ON/OFF | #5SC 250 CB 52AS |  | bakb | B3/D03_A1 | [8 empty] | 南濱DS.250_CB | 250(23KV #5SC) CB | SC | [5 empty] | 576 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | 250 | #5SC(250) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0296 |  |  | 2-05-00 |  |  | #3ASC | SCA | #5SC 250 RY SCA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.250_SCA | 23KV #5SC 51,51N RY | SC | [5 empty] | 577 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | 250 | #5SC(250) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0297 |  |  | 2-05-01 |  |  | #3ASC | UVA | #5SC 250 RY UVA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.250_UVA | 23KV #5SC 27RY(欠壓) | SC | [5 empty] | 578 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K361 | 濱61線(K361) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/K361/T1 |  |  | 0298 |  |  | 2-05-02 |  |  | F21 | ON/OFF | 濱61線 K361 CB 52AS |  | bajb | B2/D03_D1 | [8 empty] | 南濱DS.K361_CB | K361(23KV濱61線) CB | FEEDER | [5 empty] | 579 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K361 | 濱61線(K361) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0299 |  |  | 2-05-03 |  |  | F21 | PHA | 濱61線 K361 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K361_PHA | 23KV濱61線(K361) 相間RY | FEEDER | [5 empty] | 580 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K361 | 濱61線(K361) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0300 |  |  | 2-05-04 |  |  | F21 | GDA | 濱61線 K361 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K361_GDA | 23KV濱61線(K361) 接地RY | FEEDER | [5 empty] | 581 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K362 | 濱62線(K362) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/K362/T1 |  |  | 0301 |  |  | 2-05-05 |  |  | F22 | ON/OFF | 濱62線 K362 CB 52AS |  | baib | B2/D03_D1 | [8 empty] | 南濱DS.K362_CB | K362(23KV濱62線) CB | FEEDER | [5 empty] | 582 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K362 | 濱62線(K362) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0302 |  |  | 2-05-06 |  |  | F22 | PHA | 濱62線 K362 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K362_PHA | 23KV濱62線(K362) 相間RY | FEEDER | [5 empty] | 583 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K362 | 濱62線(K362) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0303 |  |  | 2-05-07 |  |  | F22 | GDA | 濱62線 K362 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K362_GDA | 23KV濱62線(K362) 接地RY | FEEDER | [5 empty] | 584 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K363 | 濱63線(K363) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/K363/T1 |  |  | 0304 |  |  | 2-06-00 |  |  | F23 | ON/OFF | 濱63線 K363 CB 52AS |  | bahb | B2/D03_D1 | [8 empty] | 南濱DS.K363_CB | K363(23KV濱63線) CB | FEEDER | [5 empty] | 585 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K363 | 濱63線(K363) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0305 |  |  | 2-06-01 |  |  | F23 | PHA | 濱63線 K363 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K363_PHA | 23KV濱63線(K363) 相間RY | FEEDER | [5 empty] | 586 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K363 | 濱63線(K363) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0306 |  |  | 2-06-02 |  |  | F23 | GDA | 濱63線 K363 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K363_GDA | 23KV濱63線(K363) 接地RY | FEEDER | [5 empty] | 587 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K364 | 濱64線(K364) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/K364/T1 |  |  | 0307 |  |  | 2-06-03 |  |  | F24 | ON/OFF | 濱64線 K364 CB 52AS |  | bafb | B2/D03_D1 | [8 empty] | 南濱DS.K364_CB | K364(23KV濱64線) CB | FEEDER | [5 empty] | 588 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K364 | 濱64線(K364) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0308 |  |  | 2-06-04 |  |  | F24 | PHA | 濱64線 K364 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K364_PHA | 23KV濱64線(K364) 相間RY | FEEDER | [5 empty] | 589 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K364 | 濱64線(K364) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0309 |  |  | 2-06-05 |  |  | F24 | GDA | 濱64線 K364 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K364_GDA | 23KV濱64線(K364) 接地RY | FEEDER | [5 empty] | 590 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K365 | 濱65線(K365) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/K365/T1 |  |  | 0310 |  |  | 2-06-06 |  |  | F25 | ON/OFF | 濱65線 K365 CB 52AS |  | baeb | B2/D03_D1 | [8 empty] | 南濱DS.K365_CB | K365(23KV濱65線) CB | FEEDER | [5 empty] | 591 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K365 | 濱65線(K365) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0311 |  |  | 2-06-07 |  |  | F25 | PHA | 濱65線 K365 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K365_PHA | 23KV濱65線(K365) 相間RY | FEEDER | [5 empty] | 592 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K365 | 濱65線(K365) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0312 |  |  | 2-07-00 |  |  | F25 | GDA | 濱65線 K365 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K365_GDA | 23KV濱65線(K365) 接地RY | FEEDER | [5 empty] | 593 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K366 | 濱66線(K366) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/K366/T1 |  |  | 0313 |  |  | 2-07-01 |  |  | F26 | ON/OFF | 濱66線 K366 CB 52AS |  | badb | B2/D03_D1 | [8 empty] | 南濱DS.K366_CB | K366(23KV濱66線) CB | FEEDER | [5 empty] | 594 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K366 | 濱66線(K366) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0314 |  |  | 2-07-02 |  |  | F26 | PHA | 濱66線 K366 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K366_PHA | 23KV濱66線(K366) 相間RY | FEEDER | [5 empty] | 595 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K366 | 濱66線(K366) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0315 |  |  | 2-07-03 |  |  | F26 | GDA | 濱66線 K366 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K366_GDA | 23KV濱66線(K366) 接地RY | FEEDER | [5 empty] | 596 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K367 | 濱67線(K367) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/K367/T1 |  |  | 0316 |  |  | 2-07-04 |  |  | F27 | ON/OFF | 濱67線 K367 CB 52AS |  | bacb | B2/D03_D1 | [8 empty] | 南濱DS.K367_CB | K367(23KV濱67線) CB | FEEDER | [5 empty] | 597 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K367 | 濱67線(K367) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0317 |  |  | 2-07-05 |  |  | F27 | PHA | 濱67線 K367 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K367_PHA | 23KV濱67線(K367) 相間RY | FEEDER | [5 empty] | 598 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K367 | 濱67線(K367) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0318 |  |  | 2-07-06 |  |  | F27 | GDA | 濱67線 K367 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K367_GDA | 23KV濱67線(K367) 接地RY | FEEDER | [5 empty] | 599 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K368 | 濱68線(K368) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/K368/T1 |  |  | 0319 |  |  | 2-07-07 |  |  | F28 | ON/OFF | 濱68線 K368 CB 52AS |  | babb | B2/D03_D1 | [8 empty] | 南濱DS.K368_CB | K368(23KV濱68線) CB | FEEDER | [5 empty] | 600 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K368 | 濱68線(K368) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0320 |  |  | 2-08-00 |  |  | F28 | PHA | 濱68線 K368 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K368_PHA | 23KV濱68線(K368) 相間RY | FEEDER | [5 empty] | 601 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K368 | 濱68線(K368) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0321 |  |  | 2-08-01 |  |  | F28 | GDA | 濱68線 K368 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K368_GDA | 23KV濱68線(K368) 接地RY | FEEDER | [5 empty] | 602 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | 260 | #6SC(260) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3Bus | C/6SC |  |  | 0322 |  |  | 2-08-02 |  |  | #3BSC | ON/OFF | #6SC 260 CB 52AS |  | baab | B3/D03_A1 | [8 empty] | 南濱DS.260_CB | 260(23KV #6SC) CB | SC | [5 empty] | 603 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | 260 | #6SC(260) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0323 |  |  | 2-08-03 |  |  | #3BSC | SCA | #6SC 260 RY SCA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.260_SCA | 23KV #6SC 51,51N RY | SC | [5 empty] | 604 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | 260 | #6SC(260) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0324 |  |  | 2-08-04 |  |  | #3BSC | UVA | #6SC 260 RY UVA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.260_UVA | 23KV #6SC 27RY(欠壓) | SC | [5 empty] | 605 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | 300 | TIE(300) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/4Bus | B/3Bus |  |  | 0325 |  |  | 2-08-05 |  |  | TIE-4 | ON/OFF | TIE-4 300 CB 52AS |  | bbab | B3/D03_A1 | [8 empty] | 南濱DS.300_CB | 300(TIE) CB | TIE | [5 empty] | 606 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D03 | 南濱DS | 22 | 22kV | 300 | TIE(300) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0326 |  |  | 2-08-06 |  |  | TIE-4 | PHA | TIE-4 300 RY PHA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.300_51A | 23KV TIE(300) 51RY | TIE | [5 empty] | 607 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | 300 | TIE(300) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0327 |  |  | 2-08-07 |  |  | TIE-4 | GDA | TIE-4 300 RY GDA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.300_51NA | 23KV TIE(300) 51N RY | TIE | [5 empty] | 608 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | 270 | #7SC(270) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4Bus | C/7SC |  |  | 0328 |  |  | 2-09-00 |  |  | #4ASC | ON/OFF | #7SC 270 CB 52AS |  | bbcb | B3/D03_A1 | [8 empty] | 南濱DS.270_CB | 270(23KV #7SC) CB | SC | [5 empty] | 609 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | 270 | #7SC(270) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0329 |  |  | 2-09-01 |  |  | #4ASC | SCA | #7SC 270 RY SCA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.270_SCA | 23KV #7SC 51,51N RY | SC | [5 empty] | 610 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | 270 | #7SC(270) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0330 |  |  | 2-09-02 |  |  | #4ASC | UVA | #7SC 270 RY UVA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.270_UVA | 23KV #7SC 27RY(欠壓) | SC | [5 empty] | 611 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K371 | 濱71線(K371) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4Bus | L/K371/T1 |  |  | 0331 |  |  | 2-09-03 |  |  | F29 | ON/OFF | 濱71線 K371 CB 52AS |  | bbdb | B2/D03_D1 | [8 empty] | 南濱DS.K371_CB | K371(23KV濱71線) CB | FEEDER | [5 empty] | 612 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K371 | 濱71線(K371) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0332 |  |  | 2-09-04 |  |  | F29 | PHA | 濱71線 K371 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K371_PHA | 23KV濱71線(K371) 相間RY | FEEDER | [5 empty] | 613 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K371 | 濱71線(K371) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0333 |  |  | 2-09-05 |  |  | F29 | GDA | 濱71線 K371 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K371_GDA | 23KV濱71線(K371) 接地RY | FEEDER | [5 empty] | 614 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K372 | 濱72線(K372) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4Bus | L/K372/T1 |  |  | 0334 |  |  | 2-09-06 |  |  | F30 | ON/OFF | 濱72線 K372 CB 52AS |  | bbeb | B2/D03_D1 | [8 empty] | 南濱DS.K372_CB | K372(23KV濱72線) CB | FEEDER | [5 empty] | 615 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K372 | 濱72線(K372) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0335 |  |  | 2-09-07 |  |  | F30 | PHA | 濱72線 K372 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K372_PHA | 23KV濱72線(K372) 相間RY | FEEDER | [5 empty] | 616 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K372 | 濱72線(K372) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0336 |  |  | 2-0A-00 |  |  | F30 | GDA | 濱72線 K372 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K372_GDA | 23KV濱72線(K372) 接地RY | FEEDER | [5 empty] | 617 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K373 | 濱73線(K373) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4Bus | L/K373/T1 |  |  | 0337 |  |  | 2-0A-01 |  |  | F31 | ON/OFF | 濱73線 K373 CB 52AS |  | bbfb | B2/D03_D1 | [8 empty] | 南濱DS.K373_CB | K373(23KV濱73線) CB | FEEDER | [5 empty] | 618 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K373 | 濱73線(K373) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0338 |  |  | 2-0A-02 |  |  | F31 | PHA | 濱73線 K373 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K373_PHA | 23KV濱73線(K373) 相間RY | FEEDER | [5 empty] | 619 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K373 | 濱73線(K373) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0339 |  |  | 2-0A-03 |  |  | F31 | GDA | 濱73線 K373 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K373_GDA | 23KV濱73線(K373) 接地RY | FEEDER | [5 empty] | 620 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K374 | 濱74線(K374) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4Bus | L/K374/T1 |  |  | 0340 |  |  | 2-0A-04 |  |  | F32 | ON/OFF | 濱74線 K374 CB 52AS |  | bbhb | B2/D03_D1 | [8 empty] | 南濱DS.K374_CB | K374(23KV濱74線) CB | FEEDER | [5 empty] | 621 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K374 | 濱74線(K374) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0341 |  |  | 2-0A-05 |  |  | F32 | PHA | 濱74線 K374 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K374_PHA | 23KV濱74線(K374) 相間RY | FEEDER | [5 empty] | 622 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K374 | 濱74線(K374) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0342 |  |  | 2-0A-06 |  |  | F32 | GDA | 濱74線 K374 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K374_GDA | 23KV濱74線(K374) 接地RY | FEEDER | [5 empty] | 623 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K375 | 濱75線(K375) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4Bus | L/K375/T1 |  |  | 0343 |  |  | 2-0A-07 |  |  | F33 | ON/OFF | 濱75線 K375 CB 52AS |  | bbib | B2/D03_D1 | [8 empty] | 南濱DS.K375_CB | K375(23KV濱75線) CB | FEEDER | [5 empty] | 624 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K375 | 濱75線(K375) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0344 |  |  | 2-0B-00 |  |  | F33 | PHA | 濱75線 K375 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K375_PHA | 23KV濱75線(K375) 相間RY | FEEDER | [5 empty] | 625 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K375 | 濱75線(K375) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0345 |  |  | 2-0B-01 |  |  | F33 | GDA | 濱75線 K375 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K375_GDA | 23KV濱75線(K375) 接地RY | FEEDER | [5 empty] | 626 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K376 | 濱76線(K376) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4Bus | L/K376/T1 |  |  | 0346 |  |  | 2-0B-02 |  |  | F34 | ON/OFF | 濱76線 K376 CB 52AS |  | bbjb | B2/D03_D1 | [8 empty] | 南濱DS.K376_CB | K376(23KV濱76線) CB | FEEDER | [5 empty] | 627 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K376 | 濱76線(K376) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0347 |  |  | 2-0B-03 |  |  | F34 | PHA | 濱76線 K376 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K376_PHA | 23KV濱76線(K376) 相間RY | FEEDER | [5 empty] | 628 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K376 | 濱76線(K376) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0348 |  |  | 2-0B-04 |  |  | F34 | GDA | 濱76線 K376 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K376_GDA | 23KV濱76線(K376) 接地RY | FEEDER | [5 empty] | 629 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K377 | 濱77線(K377) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4Bus | L/K377/T1 |  |  | 0349 |  |  | 2-0B-05 |  |  | F35 | ON/OFF | 濱77線 K377 CB 52AS |  | bbkb | B2/D03_D1 | [8 empty] | 南濱DS.K377_CB | K377(23KV濱77線) CB | FEEDER | [5 empty] | 630 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K377 | 濱77線(K377) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0350 |  |  | 2-0B-06 |  |  | F35 | PHA | 濱77線 K377 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K377_PHA | 23KV濱77線(K377) 相間RY | FEEDER | [5 empty] | 631 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K377 | 濱77線(K377) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0351 |  |  | 2-0B-07 |  |  | F35 | GDA | 濱77線 K377 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K377_GDA | 23KV濱77線(K377) 接地RY | FEEDER | [5 empty] | 632 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K378 | 濱78線(K378) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4Bus | L/K378/T1 |  |  | 0352 |  |  | 2-0C-00 |  |  | F36 | ON/OFF | 濱78線 K378 CB 52AS |  | bblb | B2/D03_D1 | [8 empty] | 南濱DS.K378_CB | K378(23KV濱78線) CB | FEEDER | [5 empty] | 633 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K378 | 濱78線(K378) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0353 |  |  | 2-0C-01 |  |  | F36 | PHA | 濱78線 K378 RY PHA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K378_PHA | 23KV濱78線(K378) 相間RY | FEEDER | [5 empty] | 634 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K378 | 濱78線(K378) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0354 |  |  | 2-0C-02 |  |  | F36 | GDA | 濱78線 K378 RY GDA |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K378_GDA | 23KV濱78線(K378) 接地RY | FEEDER | [5 empty] | 635 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | 280 | #8SC(280) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4Bus | C/8SC |  |  | 0355 |  |  | 2-0C-03 |  |  | #4BSC | ON/OFF | #8SC 280 CB 52AS |  | bbmb | B3/D03_A1 | [8 empty] | 南濱DS.280_CB | 280(23KV #8SC) CB | SC | [5 empty] | 636 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | 280 | #8SC(280) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0356 |  |  | 2-0C-04 |  |  | #4BSC | SCA | #8SC 280 RY SCA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.280_SCA | 23KV #8SC 51,51N RY | SC | [5 empty] | 637 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | 280 | #8SC(280) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0357 |  |  | 2-0C-05 |  |  | #4BSC | UVA | #8SC 280 RY UVA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.280_UVA | 23KV #8SC 27RY(欠壓) | SC | [5 empty] | 638 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | 490 | #2SSTR(490) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4Bus | T/2SSTR |  |  | 0358 |  |  | 2-0C-06 |  |  | #2SSTR | ON/OFF | SSTR-2 490 CB 52AS |  | bbnb | B3/D03_A1 | [8 empty] | 南濱DS.490_CB | 490(#2SSTR) CB | OTHER | [5 empty] | 639 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | 490 | #2SSTR(490) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0359 |  |  | 2-0C-07 |  |  | #2SSTR | PHA | SSTR-2 490 RY PHA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.#2SSTR_51A | #2SSTR 51RY | OTHER | [5 empty] | 640 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | 490 | #2SSTR(490) |  | GDA |  | B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0360 |  |  | 2-0D-00 |  |  | #2SSTR | GDA | SSTR-2 490 RY GDA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | [5 empty] | 641 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0768 |  |  | 1-30-00 |  |  | Test CB | ON/OFF | TEST C.B. |  |  | ELEM/ALL | [8 empty] | 南濱DS.TEST_CB | TEST CB | OTHER | [5 empty] | 642 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | RTU | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0769 |  |  | 1-30-01 |  |  | Locate Empty | L/R | LOCAL/REMOTE STATUS |  |  | ELEM/D03_A1 | [8 empty] | 南濱DS.RTU_S/L | RTU SUPY/LOCAL | OTHER | [5 empty] | 643 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
D03 | 南濱DS | 161 | 161kV | 1510 | 安南～南濱一路(1510) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0770 |  |  | 1-30-02 |  |  | 1510 | USE/LOCK | 安南南濱一路(1510) 87S |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1510_87UL | 安南南濱一路(1510) 87RY U/L | LINE161 | [5 empty] | 644 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1510 | 安南～南濱一路(1510) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0771 |  |  | 1-30-03 |  |  | 1510 | USE/LOCK | 安南南濱一路(1510) 79S |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1510_79UL | 安南南濱一路(1510) 79RY U/L | LINE161 | [5 empty] | 645 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1520 | 安南～南濱二路(1520) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0772 |  |  | 1-30-04 |  |  | 1520 | USE/LOCK | 安南南濱二路(1520) 87S |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1520_87UL | 安南南濱二路(1520) 87RY U/L | LINE161 | [5 empty] | 646 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1520 | 安南～南濱二路(1520) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0773 |  |  | 1-30-05 |  |  | 1520 | USE/LOCK | 安南南濱二路(1520) 79S |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1520_79UL | 安南南濱二路(1520) 79RY U/L | LINE161 | [5 empty] | 647 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱～安瀚線(1530) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0774 |  |  | 1-30-06 |  |  | 1530 | USE/LOCK | 南濱安瀚線(1530) 187S |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1530_87UL1 | 安瀚線(1530) 第一套 87RY U/L | LINE161 | [5 empty] | 648 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱～安瀚線(1530) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0775 |  |  | 1-30-07 |  |  | 1530 | USE/LOCK | 南濱安瀚線(1530) 79S |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1530_79UL | 南濱安瀚線(1530) 79RY U/L | LINE161 | [5 empty] | 649 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱～凸版線(1540) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0776 |  |  | 1-30-08 |  |  | 1540 | USE/LOCK | 南濱凸版線(1540) 187S |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1540_87UL1 | 凸版線(1540) 第一套 87RY U/L | LINE161 | [5 empty] | 650 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱～凸版線(1540) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0777 |  |  | 1-30-09 |  |  | 1540 | USE/LOCK | 南濱凸版線(1540) 79S |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1540_79UL | 南濱凸版線(1540) 79RY U/L | LINE161 | [5 empty] | 651 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1550 | 南濱～鹿耳紅線(1550) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0778 |  |  | 1-30-10 |  |  | 1550 | USE/LOCK | 南濱鹿耳紅線(1550) 87S |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1550_87UL | 南濱鹿耳紅線(1550) 87RY U/L | LINE161 | [5 empty] | 652 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1550 | 南濱～鹿耳紅線(1550) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0779 |  |  | 1-30-11 |  |  | 1550 | USE/LOCK | 南濱鹿耳紅線(1550) 79S |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1550_79UL | 南濱鹿耳紅線(1550) 79RY U/L | LINE161 | [5 empty] | 653 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1560 | 南濱～鹿耳白線(1560) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0780 |  |  | 1-30-12 |  |  | 1560 | USE/LOCK | 南濱鹿耳白線(1560) 87S |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1560_87UL | 南濱鹿耳白線(1560) 87RY U/L | LINE161 | [5 empty] | 654 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1560 | 南濱～鹿耳白線(1560) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0781 |  |  | 1-30-13 |  |  | 1560 | USE/LOCK | 南濱鹿耳白線(1560) 79S |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1560_79UL | 南濱鹿耳白線(1560) 79RY U/L | LINE161 | [5 empty] | 655 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0790 |  |  | 1-31-06 |  |  | 161kV #1 BUS | USE/LOCK | 161KV #1 BUS╴87UL |  |  | B2/D03_A1 | [8 empty] | 南濱DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | [5 empty] | 656 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0791 |  |  | 1-31-07 |  |  | 161kV #2 BUS | USE/LOCK | 161KV #2 BUS╴87UL |  |  | B2/D03_A1 | [8 empty] | 南濱DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | [5 empty] | 657 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS |  |  | 1DTR | #1DTR |  | 87UL1 |  |  | Status | 第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0792 |  |  | 1-31-08 |  |  | Locate Empty | USE/LOCK | NO.1 D.TR. 187S |  |  | B1/D03_A1 | [8 empty] | 南濱DS.161#1DTR_187UL | 161KV #1DTR 187RY U/L | OTHER | [5 empty] | 658 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS |  |  | 1DTR(A) | #1DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0793 |  |  | 1-31-09 |  |  | Locate Empty | 遙控/現場 | NO.1 D.TR. S/L (A) 143R1S3 |  | c | B1/D03_A1 | [8 empty] | 南濱DS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | [5 empty] | 659 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D03 | 南濱DS |  |  | 1DTR(A) | #1DTR(A) |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0794 |  |  | 1-31-10 |  |  | Locate Empty | OLTC A/M | NO.1 D.TR. A/M (A) 1AX-S1 |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | [5 empty] | 660 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D03 | 南濱DS |  |  | 1DTR | #1DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0795 |  |  | 1-31-11 |  |  | Locate Empty | A/N | NO.1 D.TR.重故障 1TRA |  | a | B1/D03_A1 | [8 empty] | 南濱DS.#1DTR_TRA | #1DTR 重故障 | MTR | [5 empty] | 661 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS |  |  | 1DTR | #1DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0796 |  |  | 1-31-12 |  |  | Locate Empty | A/N | NO.1 D.TR.輕故障 1TRF |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#1DTR_TRF | #1DTR 輕故障 | MTR | [5 empty] | 662 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS |  |  | 1DTR(B) | #1DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0797 |  |  | 1-31-13 |  |  | Locate Empty | 遙控/現場 | NO.1 D.TR. S/L (B) 143R2S3 |  | b | B1/D03_A1 | [8 empty] | 南濱DS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | [5 empty] | 663 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D03 | 南濱DS |  |  | 1DTR(B) | #1DTR(B) |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0798 |  |  | 1-31-14 |  |  | Locate Empty | OLTC A/M | NO.1 D.TR. A/M (B) 1AX-S2 |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | [5 empty] | 664 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D03 | 南濱DS |  |  | 2DTR | #2DTR |  | 87UL1 |  |  | Status | 第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0799 |  |  | 1-31-15 |  |  | Locate Empty | USE/LOCK | NO.2 D.TR. 187S |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#2DTR_187S | #2DTR 187RY U/L | OTHER | [5 empty] | 665 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS |  |  | 2DTR(A) | #2DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0800 |  |  | 1-32-00 |  |  | Locate Empty | 遙控/現場 | NO.2 D.TR. S/L (A) 43R1S3 |  | c | B1/D03_A1 | [8 empty] | 南濱DS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | [5 empty] | 666 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D03 | 南濱DS |  |  | 2DTR(A) | #2DTR(A) |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0801 |  |  | 1-32-01 |  |  | Locate Empty | OLTC A/M | NO.2 D.TR. A/M (A) AX-S1 |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | [5 empty] | 667 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D03 | 南濱DS |  |  | 2DTR | #2DTR |  | TRA |  | B3 | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0802 |  |  | 1-32-02 |  |  | Locate Empty | A/N | NO.2 D.TR.重故障 TRA |  | a | B1/D03_A1 | [8 empty] | 南濱DS.#2DTR_TRA | #2DTR 重故障 | MTR | [5 empty] | 668 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS |  |  | 2DTR(A) | #2DTR(A) |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0803 |  |  | 1-32-03 |  |  | Locate Empty | A/N | NO.2 D.TR.輕故障 TRF |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#2DTR_TRF | #2DTR 輕故障 | MTR | [5 empty] | 669 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS |  |  | 2DTR(B) | #2DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0804 |  |  | 1-32-04 |  |  | Locate Empty | 遙控/現場 | NO.2 D.TR. S/L (B) 43R2S3 |  | b | B1/D03_A1 | [8 empty] | 南濱DS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | [5 empty] | 670 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D03 | 南濱DS |  |  | 2DTR(B) | #2DTR(B) |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0805 |  |  | 1-32-05 |  |  | Locate Empty | OLTC A/M | NO.2 D.TR. A/M (B) AX-S2 |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | [5 empty] | 671 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D03 | 南濱DS |  |  | 3DTR | #3DTR |  | 87UL1 |  |  | Status | 第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0806 |  |  | 1-32-06 |  |  | Locate Empty | USE/LOCK | NO.3 D.TR. 87S |  |  | B1/D03_A1 | [8 empty] | 南濱DS.161#3DTR_187UL | 161KV #3DTR 187RY U/L | OTHER | [5 empty] | 672 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS |  |  | 3DTR | #3DTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0807 |  |  | 1-32-07 |  |  | Locate Empty | 遙控/現場 | NO.3 D.TR. S/L (A) 43R1S3 |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#3DTR_S/L | #3DTR OLTC S/L | MTR | [5 empty] | 673 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D03 | 南濱DS |  |  | 3DTR | #3DTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0808 |  |  | 1-32-08 |  |  | Locate Empty | OLTC A/M | NO.3 D.TR. A/M (A) AX-S |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#3DTR_A/M | #3DTR OLTC A/M | MTR | [5 empty] | 674 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D03 | 南濱DS |  |  | 3DTR | #3DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR |  |  |  |  | 0809 |  |  | 1-32-09 |  |  | Locate Empty | A/N | NO.3 D.TR.重故障 TRA |  | a | B1/D03_A1 | [8 empty] | 南濱DS.#3DTR_TRA | #3DTR 重故障 | MTR | [5 empty] | 675 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS |  |  | 3DTR | #3DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0810 |  |  | 1-32-10 |  |  | Locate Empty | A/N | NO.3 D.TR.輕故障 TRF |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#3DTR_TRF | #3DTR 輕故障 | MTR | [5 empty] | 676 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS |  |  | 4DTR | #4DTR |  | 87UL1 |  |  | Status | 第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0811 |  |  | 1-32-11 |  |  | Locate Empty | USE/LOCK | NO.4 D.TR. 87S |  |  | B1/D03_A1 | [8 empty] | 南濱DS.161#4DTR_187UL | 161KV #4DTR 187RY U/L | OTHER | [5 empty] | 677 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS |  |  | 4DTR | #4DTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0812 |  |  | 1-32-12 |  |  | Locate Empty | 遙控/現場 | NO.4 D.TR. S/L (A) 43R1S3 |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#4DTR_S/L | #4DTR OLTC S/L | MTR | [5 empty] | 678 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D03 | 南濱DS |  |  | 4DTR | #4DTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0813 |  |  | 1-32-13 |  |  | Locate Empty | OLTC A/M | NO.4 D.TR. A/M (A) AX-S |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#4DTR_A/M | #4DTR OLTC A/M | MTR | [5 empty] | 679 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D03 | 南濱DS |  |  | 4DTR | #4DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR |  |  |  |  | 0814 |  |  | 1-32-14 |  |  | Locate Empty | A/N | NO.4 D.TR.重故障 TRA |  | a | B1/D03_A1 | [8 empty] | 南濱DS.#4DTR_TRA | #4DTR 重故障 | MTR | [5 empty] | 680 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS |  |  | 4DTR | #4DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0815 |  |  | 1-32-15 |  |  | Locate Empty | A/N | NO.4 D.TR.輕故障 TRF |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#4DTR_TRF | #4DTR 輕故障 | MTR | [5 empty] | 681 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1510 | 安南～南濱一路(1510) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0816 |  |  | 1-33-00 |  |  | Locate Empty | A/N | 安南南濱一路1510 87LA RY故障 |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1510_87LA | 安南南濱一路(1510) RY/DC故障 | OTHER | [5 empty] | 682 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1510 | 安南～南濱一路(1510) |  | 85CFA |  |  | Status | 85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0817 |  |  | 1-33-01 |  |  | Locate Empty | A/N | 安南南濱一路1510 RAOA TONE故障 |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1510_RAOA | 安南南濱一路(1510) 87L通訊故障 | OTHER | [5 empty] | 683 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1520 | 安南～南濱二路(1520) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0818 |  |  | 1-33-02 |  |  | Locate Empty | A/N | 安南南濱二路1520 87LA RY故障 |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1520_87LA | 安南南濱二路(1520) RY/DC故障 | OTHER | [5 empty] | 684 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1520 | 安南～南濱二路(1520) |  | 85CFA |  |  | Status | 85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0819 |  |  | 1-33-03 |  |  | Locate Empty | A/N | 安南南濱二路1520 RAOA TONE故障 |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1520_RAOA | 安南南濱二路(1520) 87L通訊故障 | OTHER | [5 empty] | 685 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱～安瀚線(1530) |  | RYFA1 |  | B3 | Status | 第1具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0820 |  |  | 1-33-04 |  |  | Locate Empty | A/N | 南濱安瀚線1530 RYFA故障 |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1530_187LA | 南濱安瀚線(1530) 1RY/DC故障 | OTHER | [5 empty] | 686 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱～安瀚線(1530) |  | 87CFA1 |  |  | Status | 第1具87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0821 |  |  | 1-33-05 |  |  | Locate Empty | A/N | 南濱安瀚線1530 87CFA故障 |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1530_1RAOA | 南濱安瀚線(1530) 187L通訊故障 | OTHER | [5 empty] | 687 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱～凸版線(1540) |  | RYFA1 |  | B3 | Status | 第1具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0822 |  |  | 1-33-06 |  |  | Locate Empty | A/N | 南濱凸版線1540 RYFA故障 |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1540_187LA | 南濱凸版線(1540) 1RY/DC故障 | OTHER | [5 empty] | 688 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱～凸版線(1540) |  | 87CFA1 |  |  | Status | 第1具87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0823 |  |  | 1-33-07 |  |  | Locate Empty | A/N | 南濱凸版線1540 87CFA故障 |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1540_1RAOA | 南濱凸版線(1540) 187L通訊故障 | OTHER | [5 empty] | 689 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1550 | 南濱～鹿耳紅線(1550) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0824 |  |  | 1-33-08 |  |  | Locate Empty | A/N | 南濱鹿耳紅線1550 87CFA故障 |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1550_87CFA | 南濱鹿耳紅線(1550)87RY通訊故障 | OTHER | [5 empty] | 690 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1550 | 南濱～鹿耳紅線(1550) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0825 |  |  | 1-33-09 |  |  | Locate Empty | A/N | 南濱鹿耳紅線1550 RYFA故障 |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1550_RYFA | 南濱鹿耳紅線(1550)數位電驛故障 | OTHER | [5 empty] | 691 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1560 | 南濱～鹿耳白線(1560) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0826 |  |  | 1-33-10 |  |  | Locate Empty | A/N | 南濱鹿耳白線1560 87CFA故障 |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1560_87CFA | 南濱鹿耳白線(1560)87RY通訊故障 | OTHER | [5 empty] | 692 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1560 | 南濱～鹿耳白線(1560) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0827 |  |  | 1-33-11 |  |  | Locate Empty | A/N | 南濱鹿耳白線1560 RYFA故障 |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1560_RYFA | 南濱鹿耳白線(1560)數位電驛故障 | OTHER | [5 empty] | 693 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | StaDev | 所內設施 |  | Fire1 | 受信總機 |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0836 |  |  | 1-34-04 |  |  | 火災警報(1) | A/N | 火災警報(1)受信總機 |  |  | B3/D03_A1 | [8 empty] | 南濱DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | [5 empty] | 694 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | StaDev | 所內設施 |  | Fire2 |  |  | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0837 |  |  | 1-34-05 |  |  | 火災警報(2) | A/N | 火災警報(2) |  |  | B3/D03_A1 | [8 empty] | 南濱DS.火災警報(2) | 火災警報(2) | OTHER | [5 empty] | 695 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | StaDev | 所內設施 |  | Fire3 |  |  | Status | 火災警報3 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0838 |  |  | 1-34-06 |  |  | 火災警報(3) | A/N | 火災警報(3) |  |  | B3/D03_A1 | [8 empty] | 南濱DS.火災警報(3) | 火災警報(3) | OTHER | [5 empty] | 696 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | StaDev | 所內設施 |  | Fire4 |  |  | Status | 火災警報4 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0839 |  |  | 1-34-07 |  |  | 火災警報(4) | A/N | 火災警報(4) |  |  | B3/D03_A1 | [8 empty] | 南濱DS.火災警報(4) | 火災警報(4) | OTHER | [5 empty] | 697 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | StaDev | 所內設施 |  | Fire5 |  |  | Status | 火災警報5 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0840 |  |  | 1-34-08 |  |  | 火災警報(5) | A/N | 火災警報(5) |  |  | B3/D03_A1 | [8 empty] | 南濱DS.火災警報(5) | 火災警報(5) | OTHER | [5 empty] | 698 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | StaDev | 所內設施 |  | Door1 | 1樓門禁警報 |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0841 |  |  | 1-34-09 |  |  | Locate Empty | A/N | 無人化門禁(一) 1樓門禁警報 |  |  | B3/D03_A1 | [8 empty] | 南濱DS.無人化門禁(1) | 無人化門禁(1)1樓門禁警報 | OTHER | [5 empty] | 699 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | StaDev | 所內設施 |  | Door2 | 控制室門禁警報 |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0842 |  |  | 1-34-10 |  |  | Locate Empty | A/N | 無人化門禁(二) 控制室門禁警報 |  |  | B3/D03_A1 | [8 empty] | 南濱DS.無人化門禁(2) | 無人化門禁(2)控制室門禁警報 | OTHER | [5 empty] | 700 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | StaDev | 所內設施 |  | Door3 | 保全警報 |  | Status | 無人化門禁3 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0843 |  |  | 1-34-11 |  |  | Locate Empty | A/N | 無人化門禁(三) 保全警報 |  |  | B3/D03_A1 | [8 empty] | 南濱DS.無人化防盜(1) | 無人化防盜(1)保全警報 | OTHER | [5 empty] | 701 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | StaDev | 所內設施 |  | Door4 |  |  | Status | 無人化門禁4 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0844 |  |  | 1-34-12 |  |  | Locate Empty | A/N | 無人化門禁(四) |  |  | B3/D03_A1 | [8 empty] | 南濱DS.無人化防盜(2) | 無人化防盜(2) | OTHER | [5 empty] | 702 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | StaDev | 所內設施 |  | Door5 | 無人化門禁(五) |  | Status | 無人化門禁5 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0845 |  |  | 1-34-13 |  |  | Locate Empty | A/N | 無人化門禁(五) |  |  | B3/D03_A1 | [8 empty] | 南濱DS.無人化防盜(3) | 無人化防盜(3) | OTHER | [5 empty] | 703 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | StaDev | 所內設施 |  | Lights1 |  |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0846 |  |  | 1-34-14 |  |  | Locate Empty | ON/OFF | 無人化開關場照明(A) FLA(備用) |  |  | B3/D03_A1 | [16 empty] | 704 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D03 | 南濱DS | 0 |  | StaDev | 所內設施 |  | Lights2 |  |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0847 |  |  | 1-34-15 |  |  | Locate Empty | ON/OFF | 無人化開關場照明(B) FLB(備用) |  |  | B3/D03_A1 | [16 empty] | 705 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D03 | 南濱DS | 0 |  | StaDev | 所內設施 |  | AIRCON |  |  | Status | 冷氣跳脫 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0848 |  |  | 1-35-00 |  |  | 空調機 | A/M | 空調機跳脫警報 |  |  | B3/D03_A1 | [8 empty] | 南濱DS.空調機故障 | 空調機故障或電源跳脫 | OTHER | [5 empty] | 706 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | NORMAL/FAULT | NORMAL
D03 | 南濱DS | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0849 |  |  | 1-35-01 |  |  | Locate Empty | 加壓/正常 | 161KV BUS 150SA |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | [5 empty] | 707 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Test | Test | 1 |  |  | TEST/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | ComPoint |  |  | OPA |  |  | Status | 充油電纜低壓警報 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0850 |  |  | 1-35-02 |  |  | Locate Empty | A/N | 充油電纜警報 OPA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | [5 empty] | 708 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0851 |  |  | 1-35-03 |  |  | ACB1 | ON/OFF | 所內電源ACB1 |  |  | B3/D03_A1 | [8 empty] | 南濱DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | [5 empty] | 709 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D03 | 南濱DS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0852 |  |  | 1-35-04 |  |  | ACB2 | ON/OFF | 所內電源ACB1 |  |  | B3/D03_A1 | [8 empty] | 南濱DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | [5 empty] | 710 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D03 | 南濱DS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0853 |  |  | 1-35-05 |  |  | Locate Empty | A/N | 所內欠壓警報 STUV |  |  | ELEM/D03_A1 | [8 empty] | 南濱DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | [5 empty] | 711 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0854 |  |  | 1-35-06 |  |  | Locate Empty | A/N | 161KV CB 重故障 CBA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.161KV_CBA | 161KV斷路器重故障 | OTHER | [5 empty] | 712 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0855 |  |  | 1-35-07 |  |  | Locate Empty | A/N | 161KV CB 輕故障 CBF |  |  | B3/D03_A1 | [8 empty] | 南濱DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | [5 empty] | 713 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0856 |  |  | 1-35-08 |  |  | Locate Empty | A/N | NFB跳脫警報 DCA |  |  | ELEM/D03_A1 | [8 empty] | 南濱DS.直流電源DCA | 直流電源故障警報 | OTHER | [5 empty] | 714 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0857 |  |  | 1-35-09 |  |  | Locate Empty | A/N | ACB警報 ACBA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.所內電源ACBA | 所內電源故障警報 | OTHER | [5 empty] | 715 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0858 |  |  | 1-35-10 |  |  | Locate Empty | A/N | 161KV NO.1 BUS欠壓 VUA1 |  |  | B2/D03_A1 | [8 empty] | 南濱DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | [5 empty] | 716 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0859 |  |  | 1-35-11 |  |  | Locate Empty | A/N | 161KV NO.2 BUS欠壓 VUA2 |  |  | B2/D03_A1 | [8 empty] | 南濱DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | [5 empty] | 717 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0860 |  |  | 1-35-12 |  |  | Locate Empty | A/N | 充電機警報 CHG1 |  |  | B3/D03_A1 | [8 empty] | 南濱DS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | [5 empty] | 718 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0861 |  |  | 1-35-13 |  |  | Locate Empty | A/N | DC接地警報 DCE |  |  | ELEM/D03_A1 | [8 empty] | 南濱DS.直流電源DCE | 直流電源接地故障警報 | OTHER | [5 empty] | 719 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | ComPoint |  |  | COMT |  |  | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0862 |  |  | 1-35-14 |  |  | Locate Empty | A/N | 161KV CB空壓機超時運轉 COMT |  |  | B3/D03_A1 | [8 empty] | 南濱DS.161空壓機COMT | 161KV空壓機運轉超時警報 | OTHER | [5 empty] | 720 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | ComPoint |  |  | 60A |  |  | Status | 電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0863 |  |  | 1-35-15 |  |  | Locate Empty | A/N | 23KV SC 60-RY 警報 60A |  |  | B3/D03_A1 | [8 empty] | 南濱DS.23KV_SC_60A | 23/11KV SC 60A | OTHER | [5 empty] | 721 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | StaDev | 所內設施 |  | PSA | PSF (其他輕故障) |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0864 |  |  | 1-36-00 |  |  | Locate Empty |  | PSF (其他輕故障) |  |  | B3/D03_A1 | [8 empty] | 南濱DS.其他輕故障 | 變電所內其他輕故障 | OTHER | [5 empty] | 722 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | StaDev | 所內設施 |  | PSF | PSA (其他重故障) |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0865 |  |  | 1-36-01 |  |  | Locate Empty |  | PSA (其他重故障) |  |  | B3/D03_A1 | [8 empty] | 南濱DS.其他重故障 | 變電所內其他重故障 | OTHER | [5 empty] | 723 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | ComPoint |  |  | FDR_CBA |  |  | Status | 11/22kV斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0866 |  |  | 1-36-02 |  |  | Locate Empty | A/N | 22KV CB重故障 CBA |  |  | ELEM/D03_D1 | [8 empty] | 南濱DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | [5 empty] | 724 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | ComPoint |  |  | FDR_CBF |  |  | Status | 11/22kV斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0867 |  |  | 1-36-03 |  |  | Locate Empty | A/N | 22KV CB輕故障 CBF |  |  | ELEM/D03_D1 | [8 empty] | 南濱DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | [5 empty] | 725 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | ComPoint |  |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0868 |  |  | 1-36-04 |  |  | Locate Empty | A/N | 22KV FEEDER 79RY LOA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.11/23KV_LOA | 11/23KV 饋線復閉失敗 | OTHER | [5 empty] | 726 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | StaDev | 所內設施 |  | OilLeak1 |  |  | Status | 洩油池水位警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0869 |  |  | 1-36-05 |  |  | Locate Empty | A/N | OW1蓄油池水位警報1 WPF |  |  | B3/D03_A1 | [8 empty] | 南濱DS.洩油池警報(1) | 洩油池水位警報(1) | OTHER | [5 empty] | 727 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | StaDev | 所內設施 |  | OilLeak2 |  |  | Status | 洩油池水位警報2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0870 |  |  | 1-36-06 |  |  | Locate Empty | A/N | OW2蓄油池水位警報2 WPA |  |  | B3/D03_A1 | [8 empty] | 南濱DS.洩油池警報(2) | 洩油池水位警報(2) | OTHER | [5 empty] | 728 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0871 |  |  | 1-36-07 |  |  | 通訊室 | A/N | 通訊充電機故障 |  |  | B3/D03_A1 | [8 empty] | 南濱DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | [5 empty] | 729 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0872 |  |  | 1-36-08 |  |  | 通訊室 | A/N | ACFA (通訊設備AC故障) |  |  | B3/D03_A1 | [8 empty] | 南濱DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | [5 empty] | 730 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | StaDev | 所內設施 |  | R_Temp |  |  | Status | 溫度警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0875 |  |  | 1-36-11 |  |  | 通訊室 | A/N | 通信室溫控警報 |  |  | B3/D03_A1 | [8 empty] | 南濱DS.通信機房溫度 | 通信機房溫度警報 | OTHER | [5 empty] | 731 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | ComPoint |  |  | 25PFA |  |  | Status | 同步校核電驛電源 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0876 |  |  | 1-36-12 |  |  | 25RY | A/N | 25PFA 同步校核裝置電源 |  |  | B3/D03_A1 | [8 empty] | 南濱DS.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER | [5 empty] | 732 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | ComPoint |  |  | 25TA |  |  | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0877 |  |  | 1-36-13 |  |  | 25RY | A/N | 25TA 同步校核裝置超時 |  |  | B3/D03_A1 | [8 empty] | 南濱DS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | [5 empty] | 733 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | StaDev | 所內設施 |  | Water1 |  |  | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0878 |  |  | 1-36-14 |  |  | 地下室 | A/N | 地下室水位第一段警報 |  |  | B3/D03_A1 | [8 empty] | 南濱DS.水位警報(1) | 地下室水位警報(1) | OTHER | [5 empty] | 734 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | StaDev | 所內設施 |  | Water2 |  |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0879 |  |  | 1-36-15 |  |  | 地下室 | A/N | 地下室水位第二段警報 |  |  | B3/D03_A1 | [8 empty] | 南濱DS.水位警報(2) | 地下室水位警報(2) | OTHER | [5 empty] | 735 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | StaDev | 所內設施 |  | Water3 |  |  | Status | 地下室淹水3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0880 |  |  | 1-37-00 |  |  | 電纜涵洞 | A/N | 電纜涵洞水位第一段及第二段警報 |  |  | B3/D03_A1 | [8 empty] | 南濱DS.水位警報(3) | 電纜涵洞水位警報 | OTHER | [5 empty] | 736 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0881 |  |  | 1-37-01 |  |  | OSCF | A/N | 161KV示波器缺紙或故障警報OSCF |  |  | B3/D03_A1 | [8 empty] | 南濱DS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | [5 empty] | 737 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱～安瀚線(1530) |  | RYFA2 |  | B3 | Status | 第2具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0882 |  |  | 1-37-02 |  |  | 1530 | A/N | 南濱安瀚線1530 2RYFA故障 |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1530_287LA | 南濱安瀚線(1530) 2RY/DC故障 | OTHER | [5 empty] | 738 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱～安瀚線(1530) |  | 87CFA2 |  |  | Status | 第2具87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0883 |  |  | 1-37-03 |  |  | 1530 | A/N | 南濱安瀚線1530 287CFA故障 |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1530_2RAOA | 南濱安瀚線(1530) 287L通訊故障 | OTHER | [5 empty] | 739 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱～凸版線(1540) |  | RYFA2 |  | B3 | Status | 第2具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0884 |  |  | 1-37-04 |  |  | 1540 | A/N | 南濱凸版線1540 2RYFA故障 |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1540_287LA | 南濱凸版線(1540) 2RY/DC故障 | OTHER | [5 empty] | 740 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱～凸版線(1540) |  | 87CFA2 |  |  | Status | 第2具87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0885 |  |  | 1-37-05 |  |  | 1540 | A/N | 南濱凸版線1540 287CFA故障 |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1540_2RAOA | 南濱凸版線(1540) 287L通訊故障 | OTHER | [5 empty] | 741 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱～安瀚線(1530) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0886 |  |  | 1-37-06 |  |  | 1530 | USE/LOCK | 南濱安瀚線(1530) 287S |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1530_87UL2 | 安瀚線(1530) 第二套 87RY U/L | LINE161 | [5 empty] | 742 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱～凸版線(1540) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0887 |  |  | 1-37-07 |  |  | 1540 | USE/LOCK | 南濱凸版線(1540) 287S |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1540_87UL2 | 凸版線(1540) 第二套 87RY U/L | LINE161 | [5 empty] | 743 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 0 |  | StaDev | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0888 |  |  | 1-37-08 |  |  | Power Meter | A/N | Power Meter 故障警報 PMA |  |  | ELEM/D03_A1 | [8 empty] | 南濱DS.PMA | 電力量測表計故障 | OTHER | [5 empty] | 744 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | ComPoint |  |  | GRZ100 |  |  | Status | 電驛GRZ100閉鎖 | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0889 |  |  | 1-37-09 |  |  | BVS盤 | LOCK/USE | 本所各GRZ100 Ry U/L |  |  | B3/D03_A1 | [8 empty] | 南濱DS.BVS_RY | BVS GRZ100 RY U/L | OTHER | [5 empty] | 745 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | LOCK/USE | USE
D03 | 南濱DS |  |  | 2DTR | #2DTR |  | 87UL2 |  |  | Status | 第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0890 |  |  | 1-37-10 |  |  | NO.2 D.TR. | USE/LOCK | NO.2 D.TR. 287S |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#2DTR_287S | #2DTR 287RY U/L | OTHER | [5 empty] | 746 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS |  |  | 2DTR | #2DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0891 |  |  | 1-37-11 |  |  | NO.2 D.TR. | USE/LOCK | NO.2 D.TR. 51ZS |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#2DTR_51ZS | #2DTR 51Z U/L | OTHER | [5 empty] | 747 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS |  |  | 2DTR | #2DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0892 |  |  | 1-37-12 |  |  | NO.2 D.TR. | A/N | NO.2 D.TR. 86(50/50N/51Z/87/96) RY |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#2DTR_86RY | #2DTR 86(50/50N/51Z/87/96)RY | OTHER | [5 empty] | 748 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS |  |  | 2DTR | #2DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0893 |  |  | 1-37-13 |  |  | NO.2 D.TR. | A/N | NO.2 D.TR. RYFA 數位電驛故障 |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#2DTR_RYFA | #2DTR 數位電驛故障 | OTHER | [5 empty] | 749 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS |  |  | 2ADTR | #2DTR(A)(2ADTR) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0894 |  |  | 1-37-14 |  |  | M2A | USE/LOCK | 330(M2A) 81S |  |  | B1/D03_A1 | [8 empty] | 南濱DS.330_81RY | 330(M2A) 81RY U/L | OTHER | [5 empty] | 750 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Normal | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS |  |  | 2BDTR | #2DTR(B)(2BDTR) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0895 |  |  | 1-37-15 |  |  | M2B | USE/LOCK | 340(M2B) 81S |  |  | B1/D03_A1 | [8 empty] | 南濱DS.340_81RY | 340(M2B) 81RY U/L | OTHER | [5 empty] | 751 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Normal | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 1024 |  |  | 2-30-00 |  |  | SC-1A | A/M | #1SC 210 Q-CTL A/M |  |  | B3/D03_A1 | [8 empty] | 南濱DS.210_A/M | 11KV #1SC 乏控器 A/M | SC | [5 empty] | 752 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D03 | 南濱DS | 11 | 11kV | K311 | 濱11線(K311) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1026 |  |  | 2-30-02 |  |  | F1 | USE/LOCK | 濱11線 K311 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K311_79UL | 11KV濱11線(K311) 79RY U/L | FEEDER | [5 empty] | 753 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K311 | 濱11線(K311) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1027 |  |  | 2-30-03 |  |  | F1 | USE/LOCK | 濱11線 K311 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K311_LCO_TAP | 11KV濱11線(K311) LCO TAP | FEEDER | [5 empty] | 754 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K312 | 濱12線(K312) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1028 |  |  | 2-30-04 |  |  | F2 | USE/LOCK | 濱12線 K312 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K312_79UL | 11KV濱12線(K312) 79RY U/L | FEEDER | [5 empty] | 755 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K312 | 濱12線(K312) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1029 |  |  | 2-30-05 |  |  | F2 | USE/LOCK | 濱12線 K312 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K312_LCO_TAP | 11KV濱12線(K312) LCO TAP | FEEDER | [5 empty] | 756 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K313 | 濱13線(K313) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1030 |  |  | 2-30-06 |  |  | F3 | USE/LOCK | 濱13線 K313 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K313_79UL | 11KV濱13線(K313) 79RY U/L | FEEDER | [5 empty] | 757 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K313 | 濱13線(K313) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1031 |  |  | 2-30-07 |  |  | F3 | USE/LOCK | 濱13線 K313 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K313_LCO_TAP | 11KV濱13線(K313) LCO TAP | FEEDER | [5 empty] | 758 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K314 | 濱14線(K314) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1032 |  |  | 2-30-08 |  |  | F4 | USE/LOCK | 濱14線 K314 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K314_79UL | 11KV濱14線(K314) 79RY U/L | FEEDER | [5 empty] | 759 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K314 | 濱14線(K314) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1033 |  |  | 2-30-09 |  |  | F4 | USE/LOCK | 濱14線 K314 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K314_LCO_TAP | 11KV濱14線(K314) LCO TAP | FEEDER | [5 empty] | 760 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K315 | 濱15線(K315) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1034 |  |  | 2-30-10 |  |  | F5 | USE/LOCK | 濱15線 K315 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K315_79UL | 11KV濱15線(K315) 79RY U/L | FEEDER | [5 empty] | 761 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K315 | 濱15線(K315) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1035 |  |  | 2-30-11 |  |  | F5 | USE/LOCK | 濱15線 K315 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K315_LCO_TAP | 11KV濱15線(K315) LCO TAP | FEEDER | [5 empty] | 762 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 1036 |  |  | 2-30-12 |  |  | SC-1B | A/M | #2SC 220 Q-CTL A/M |  |  | B3/D03_A1 | [8 empty] | 南濱DS.220_A/M | 11KV #2SC 乏控器 A/M | SC | [5 empty] | 763 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D03 | 南濱DS | 11 | 11kV | K316 | 濱16線(K316) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1038 |  |  | 2-30-14 |  |  | F6 | USE/LOCK | 濱16線 K316 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K316_79UL | 11KV濱16線(K316) 79RY U/L | FEEDER | [5 empty] | 764 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K316 | 濱16線(K316) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1039 |  |  | 2-30-15 |  |  | F6 | USE/LOCK | 濱16線 K316 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K316_LCO_TAP | 11KV濱16線(K316) LCO TAP | FEEDER | [5 empty] | 765 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K317 | 濱17線(K317) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1040 |  |  | 2-31-00 |  |  | F7 | USE/LOCK | 濱17線 K317 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K317_79UL | 11KV濱17線(K317) 79RY U/L | FEEDER | [5 empty] | 766 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K317 | 濱17線(K317) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1041 |  |  | 2-31-01 |  |  | F7 | USE/LOCK | 濱17線 K317 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K317_LCO_TAP | 11KV濱17線(K317) LCO TAP | FEEDER | [5 empty] | 767 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K318 | 濱18線(K318) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1042 |  |  | 2-31-02 |  |  | F8 | USE/LOCK | 濱18線 K318 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K318_79UL | 11KV濱18線(K318) 79RY U/L | FEEDER | [5 empty] | 768 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K318 | 濱18線(K318) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1043 |  |  | 2-31-03 |  |  | F8 | USE/LOCK | 濱18線 K318 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K318_LCO_TAP | 11KV濱18線(K318) LCO TAP | FEEDER | [5 empty] | 769 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K319 | 濱19線(K319) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1044 |  |  | 2-31-04 |  |  | F9 | USE/LOCK | 濱19線 K319 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K319_79UL | 11KV濱19線(K319) 79RY U/L | FEEDER | [5 empty] | 770 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K319 | 濱19線(K319) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1045 |  |  | 2-31-05 |  |  | F9 | USE/LOCK | 濱19線 K319 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K319_LCO_TAP | 11KV濱19線(K319) LCO TAP | FEEDER | [5 empty] | 771 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K320 | 濱20線(K320) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1046 |  |  | 2-31-06 |  |  | F10 | USE/LOCK | 濱20線 K320 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K320_79UL | 11KV濱20線(K320) 79RY U/L | FEEDER | [5 empty] | 772 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K320 | 濱20線(K320) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1047 |  |  | 2-31-07 |  |  | F10 | USE/LOCK | 濱20線 K320 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K320_LCO_TAP | 11KV濱20線(K320) LCO TAP | FEEDER | [5 empty] | 773 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | 230 | #3SC(230) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 1048 |  |  | 2-31-08 |  |  | SC-2A | A/M | #2ASC Q-CTL A/M |  |  | B3/D03_A1 | [8 empty] | 南濱DS.230_A/M | 11KV #3SC 乏控器 A/M | SC | [5 empty] | 774 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D03 | 南濱DS | 11 | 11kV | K321 | 濱21線(K321) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1050 |  |  | 2-31-10 |  |  | F11 | USE/LOCK | 濱21線 K321 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K321_79UL | 11KV濱21線(K321) 79RY U/L | FEEDER | [5 empty] | 775 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K321 | 濱21線(K321) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1051 |  |  | 2-31-11 |  |  | F11 | USE/LOCK | 濱21線 K321 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K321_LCO_TAP | 11KV濱21線(K321) LCO TAP | FEEDER | [5 empty] | 776 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K322 | 濱22線(K322) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1052 |  |  | 2-31-12 |  |  | F12 | USE/LOCK | 濱22線 K322 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K322_79UL | 11KV濱22線(K322) 79RY U/L | FEEDER | [5 empty] | 777 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K322 | 濱22線(K322) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1053 |  |  | 2-31-13 |  |  | F12 | USE/LOCK | 濱22線 K322 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K322_LCO_TAP | 11KV濱22線(K322) LCO TAP | FEEDER | [5 empty] | 778 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K323 | 濱23線(K323) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1054 |  |  | 2-31-14 |  |  | F13 | USE/LOCK | 濱23線 K323 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K323_79UL | 11KV濱23線(K323) 79RY U/L | FEEDER | [5 empty] | 779 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K323 | 濱23線(K323) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1055 |  |  | 2-31-15 |  |  | F13 | USE/LOCK | 濱23線 K323 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K323_LCO_TAP | 11KV濱23線(K323) LCO TAP | FEEDER | [5 empty] | 780 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K324 | 濱24線(K324) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1056 |  |  | 2-32-00 |  |  | F14 | USE/LOCK | 濱24線 K324 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K324_79UL | 11KV濱24線(K324) 79RY U/L | FEEDER | [5 empty] | 781 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K324 | 濱24線(K324) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1057 |  |  | 2-32-01 |  |  | F14 | USE/LOCK | 濱24線 K324 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K324_LCO_TAP | 11KV濱24線(K324) LCO TAP | FEEDER | [5 empty] | 782 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K325 | 濱25線(K325) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1058 |  |  | 2-32-02 |  |  | F15 | USE/LOCK | 濱25線 K325 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K325_79UL | 11KV濱25線(K325) 79RY U/L | FEEDER | [5 empty] | 783 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K325 | 濱25線(K325) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1059 |  |  | 2-32-03 |  |  | F15 | USE/LOCK | 濱25線 K325 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K325_LCO_TAP | 11KV濱25線(K325) LCO TAP | FEEDER | [5 empty] | 784 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | 240 | #4SC(240) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 1060 |  |  | 2-32-04 |  |  | SC-2B | A/M | #2BSC Q-CTL A/M |  |  | B3/D03_A1 | [8 empty] | 南濱DS.240_A/M | 11KV #4SC 乏控器 A/M | SC | [5 empty] | 785 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D03 | 南濱DS | 11 | 11kV | K326 | 濱26線(K326) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1062 |  |  | 2-32-06 |  |  | F16 | USE/LOCK | 濱26線 K326 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K326_79UL | 11KV濱26線(K326) 79RY U/L | FEEDER | [5 empty] | 786 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K326 | 濱26線(K326) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1063 |  |  | 2-32-07 |  |  | F16 | USE/LOCK | 濱26線 K326 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K326_LCO_TAP | 11KV濱26線(K326) LCO TAP | FEEDER | [5 empty] | 787 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K327 | 濱27線(K327) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1064 |  |  | 2-32-08 |  |  | F17 | USE/LOCK | 濱27線 K327 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K327_79UL | 11KV濱27線(K327) 79RY U/L | FEEDER | [5 empty] | 788 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K327 | 濱27線(K327) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1065 |  |  | 2-32-09 |  |  | F17 | USE/LOCK | 濱27線 K327 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K327_LCO_TAP | 11KV濱27線(K327) LCO TAP | FEEDER | [5 empty] | 789 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K328 | 濱28線(K328) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1066 |  |  | 2-32-10 |  |  | F18 | USE/LOCK | 濱28線 K328 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K328_79UL | 11KV濱28線(K328) 79RY U/L | FEEDER | [5 empty] | 790 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K328 | 濱28線(K328) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1067 |  |  | 2-32-11 |  |  | F18 | USE/LOCK | 濱28線 K328 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K328_LCO_TAP | 11KV濱28線(K328) LCO TAP | FEEDER | [5 empty] | 791 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K329 | 濱29線(K329) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1068 |  |  | 2-32-12 |  |  | F19 | USE/LOCK | 濱29線 K329 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K329_79UL | 11KV濱29線(K329) 79RY U/L | FEEDER | [5 empty] | 792 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K329 | 濱29線(K329) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1069 |  |  | 2-32-13 |  |  | F19 | USE/LOCK | 濱29線 K329 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K329_LCO_TAP | 11KV濱29線(K329) LCO TAP | FEEDER | [5 empty] | 793 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K330 | 濱30線(K330) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1070 |  |  | 2-32-14 |  |  | F20 | USE/LOCK | 濱30線 K330 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K330_79UL | 11KV濱30線(K330) 79RY U/L | FEEDER | [5 empty] | 794 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K330 | 濱30線(K330) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1071 |  |  | 2-32-15 |  |  | F20 | USE/LOCK | 濱30線 K330 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K330_LCO_TAP | 11KV濱30線(K330) LCO TAP | FEEDER | [5 empty] | 795 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 22 | 22kV | 250 | #5SC(250) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 1072 |  |  | 2-33-00 |  |  | SC-3A | A/M | #5SC 250 Q-CTL A/M |  |  | B3/D03_A1 | [8 empty] | 南濱DS.250_A/M | 23KV #5SC 乏控器 A/M | SC | [5 empty] | 796 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D03 | 南濱DS | 22 | 22kV | K361 | 濱61線(K361) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1073 |  |  | 2-33-01 |  |  | F21 | USE/LOCK | 濱61線 K361 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K361_79UL | 23KV濱61線(K361) 79RY U/L | FEEDER | [5 empty] | 797 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 22 | 22kV | K361 | 濱61線(K361) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1074 |  |  | 2-33-02 |  |  | F21 | USE/LOCK | 濱61線 K361 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K361_LCO_TAP | 23KV濱61線(K361) LCO TAP | FEEDER | [5 empty] | 798 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 22 | 22kV | K362 | 濱62線(K362) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1075 |  |  | 2-33-03 |  |  | F22 | USE/LOCK | 濱62線 K362 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K362_79UL | 23KV濱62線(K362) 79RY U/L | FEEDER | [5 empty] | 799 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 22 | 22kV | K362 | 濱62線(K362) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1076 |  |  | 2-33-04 |  |  | F22 | USE/LOCK | 濱62線 K362 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K362_LCO_TAP | 23KV濱62線(K362) LCO TAP | FEEDER | [5 empty] | 800 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 22 | 22kV | K363 | 濱63線(K363) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1077 |  |  | 2-33-05 |  |  | F23 | USE/LOCK | 濱63線 K363 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K363_79UL | 23KV濱63線(K363) 79RY U/L | FEEDER | [5 empty] | 801 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 22 | 22kV | K363 | 濱63線(K363) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1078 |  |  | 2-33-06 |  |  | F23 | USE/LOCK | 濱63線 K363 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K363_LCO_TAP | 23KV濱63線(K363) LCO TAP | FEEDER | [5 empty] | 802 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 22 | 22kV | K364 | 濱64線(K364) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1079 |  |  | 2-33-07 |  |  | F24 | USE/LOCK | 濱64線 K364 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K364_79UL | 23KV濱64線(K364) 79RY U/L | FEEDER | [5 empty] | 803 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 22 | 22kV | K364 | 濱64線(K364) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1080 |  |  | 2-33-08 |  |  | F24 | USE/LOCK | 濱64線 K364 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K364_LCO_TAP | 23KV濱64線(K364) LCO TAP | FEEDER | [5 empty] | 804 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 22 | 22kV | K365 | 濱65線(K365) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1081 |  |  | 2-33-09 |  |  | F25 | USE/LOCK | 濱65線 K365 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K365_79UL | 23KV濱65線(K365) 79RY U/L | FEEDER | [5 empty] | 805 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 22 | 22kV | K365 | 濱65線(K365) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1082 |  |  | 2-33-10 |  |  | F25 | USE/LOCK | 濱65線 K365 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K365_LCO_TAP | 23KV濱65線(K365) LCO TAP | FEEDER | [5 empty] | 806 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 22 | 22kV | K366 | 濱66線(K366) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1083 |  |  | 2-33-11 |  |  | F26 | USE/LOCK | 濱66線 K366 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K366_79UL | 23KV濱66線(K366) 79RY U/L | FEEDER | [5 empty] | 807 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 22 | 22kV | K366 | 濱66線(K366) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1084 |  |  | 2-33-12 |  |  | F26 | USE/LOCK | 濱66線 K366 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K366_LCO_TAP | 23KV濱66線(K366) LCO TAP | FEEDER | [5 empty] | 808 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 22 | 22kV | K367 | 濱67線(K367) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1085 |  |  | 2-33-13 |  |  | F27 | USE/LOCK | 濱67線 K367 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K367_79UL | 23KV濱67線(K367) 79RY U/L | FEEDER | [5 empty] | 809 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 22 | 22kV | K367 | 濱67線(K367) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1086 |  |  | 2-33-14 |  |  | F27 | USE/LOCK | 濱67線 K367 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K367_LCO_TAP | 23KV濱67線(K367) LCO TAP | FEEDER | [5 empty] | 810 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 22 | 22kV | K368 | 濱68線(K368) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1087 |  |  | 2-33-15 |  |  | F28 | USE/LOCK | 濱68線 K368 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K368_79UL | 23KV濱68線(K368) 79RY U/L | FEEDER | [5 empty] | 811 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 22 | 22kV | K368 | 濱68線(K368) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1088 |  |  | 2-34-00 |  |  | F28 | USE/LOCK | 濱68線 K368 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K368_LCO_TAP | 23KV濱68線(K368) LCO TAP | FEEDER | [5 empty] | 812 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 22 | 22kV | 260 | #6SC(260) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 1089 |  |  | 2-34-01 |  |  | SC-3B | A/M | #6SC 260 Q-CTL A/M |  |  | B3/D03_A1 | [8 empty] | 南濱DS.260_A/M | 23KV #6SC 乏控器 A/M | SC | [5 empty] | 813 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D03 | 南濱DS | 22 | 22kV | 270 | #7SC(270) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 1090 |  |  | 2-34-02 |  |  | SC-4A | A/M | #7SC 270 Q-CTL A/M |  |  | B3/D03_A1 | [8 empty] | 南濱DS.270_A/M | 23KV #7SC 乏控器 A/M | SC | [5 empty] | 814 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D03 | 南濱DS | 22 | 22kV | K371 | 濱71線(K371) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1091 |  |  | 2-34-03 |  |  | F29 | USE/LOCK | 濱71線 K371 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K371_79UL | 23KV濱71線(K371) 79RY U/L | FEEDER | [5 empty] | 815 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 22 | 22kV | K371 | 濱71線(K371) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1092 |  |  | 2-34-04 |  |  | F29 | USE/LOCK | 濱71線 K371 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K371_LCO_TAP | 23KV濱71線(K371) LCO TAP | FEEDER | [5 empty] | 816 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 22 | 22kV | K372 | 濱72線(K372) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1093 |  |  | 2-34-05 |  |  | F30 | USE/LOCK | 濱72線 K372 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K372_79UL | 23KV濱72線(K372) 79RY U/L | FEEDER | [5 empty] | 817 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 22 | 22kV | K372 | 濱72線(K372) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1094 |  |  | 2-34-06 |  |  | F30 | USE/LOCK | 濱72線 K372 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K372_LCO_TAP | 23KV濱72線(K372) LCO TAP | FEEDER | [5 empty] | 818 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 22 | 22kV | K373 | 濱73線(K373) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1095 |  |  | 2-34-07 |  |  | F31 | USE/LOCK | 濱73線 K373 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K373_79UL | 23KV濱73線(K373) 79RY U/L | FEEDER | [5 empty] | 819 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 22 | 22kV | K373 | 濱73線(K373) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1096 |  |  | 2-34-08 |  |  | F31 | USE/LOCK | 濱73線 K373 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K373_LCO_TAP | 23KV濱73線(K373) LCO TAP | FEEDER | [5 empty] | 820 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 22 | 22kV | K374 | 濱74線(K374) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1097 |  |  | 2-34-09 |  |  | F32 | USE/LOCK | 濱74線 K374 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K374_79UL | 23KV濱74線(K374) 79RY U/L | FEEDER | [5 empty] | 821 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 22 | 22kV | K374 | 濱74線(K374) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1098 |  |  | 2-34-10 |  |  | F32 | USE/LOCK | 濱74線 K374 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K374_LCO_TAP | 23KV濱74線(K374) LCO TAP | FEEDER | [5 empty] | 822 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 22 | 22kV | K375 | 濱75線(K375) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1099 |  |  | 2-34-11 |  |  | F33 | USE/LOCK | 濱75線 K375 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K375_79UL | 23KV濱75線(K375) 79RY U/L | FEEDER | [5 empty] | 823 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 22 | 22kV | K375 | 濱75線(K375) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1100 |  |  | 2-34-12 |  |  | F33 | USE/LOCK | 濱75線 K375 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K375_LCO_TAP | 23KV濱75線(K375) LCO TAP | FEEDER | [5 empty] | 824 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 22 | 22kV | K376 | 濱76線(K376) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1101 |  |  | 2-34-13 |  |  | F34 | USE/LOCK | 濱76線 K376 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K376_79UL | 23KV濱76線(K376) 79RY U/L | FEEDER | [5 empty] | 825 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 22 | 22kV | K376 | 濱76線(K376) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1102 |  |  | 2-34-14 |  |  | F34 | USE/LOCK | 濱76線 K376 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K376_LCO_TAP | 23KV濱76線(K376) LCO TAP | FEEDER | [5 empty] | 826 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 22 | 22kV | K377 | 濱77線(K377) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1103 |  |  | 2-34-15 |  |  | F35 | USE/LOCK | 濱77線 K377 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K377_79UL | 23KV濱77線(K377) 79RY U/L | FEEDER | [5 empty] | 827 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 22 | 22kV | K377 | 濱77線(K377) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1104 |  |  | 2-35-00 |  |  | F35 | USE/LOCK | 濱77線 K377 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K377_LCO_TAP | 23KV濱77線(K377) LCO TAP | FEEDER | [5 empty] | 828 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 22 | 22kV | K378 | 濱78線(K378) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1105 |  |  | 2-35-01 |  |  | F36 | USE/LOCK | 濱78線 K378 79 RY 79S |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K378_79UL | 23KV濱78線(K378) 79RY U/L | FEEDER | [5 empty] | 829 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D03 | 南濱DS | 22 | 22kV | K378 | 濱78線(K378) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1106 |  |  | 2-35-02 |  |  | F36 | USE/LOCK | 濱78線 K378 51N TAP 51NS |  |  | B2/D03_D1 | [8 empty] | 南濱DS.K378_LCO_TAP | 23KV濱78線(K378) LCO TAP | FEEDER | [5 empty] | 830 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D03 | 南濱DS | 22 | 22kV | 280 | #8SC(280) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 1107 |  |  | 2-35-03 |  |  | SC-4B | A/M | #8SC 280 Q-CTL A/M |  |  | B3/D03_A1 | [8 empty] | 南濱DS.280_A/M | 23KV #8SC 乏控器 A/M | SC | [5 empty] | 831 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D03 | 南濱DS | 0 |  | StaDev | 所內設施 |  | GEN | 緊急發電機運轉 |  | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1108 |  |  | 2-35-04 |  |  | Locate Empty | ON/OFF | 緊急發電機運轉 |  |  | B3/D03_A1 | [8 empty] | 南濱DS.GEN | 緊急發電機運轉 | OTHER | [5 empty] | 832 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ON/OFF | OFF
D03 | 南濱DS | 161 | 161kV | StaDev | BUS |  | BUS_RYFA |  |  | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1109 |  |  | 2-35-05 |  |  | 161kV BUS | A/N | 161KV BUS數位電驛故障 |  |  | B2/D03_A1 | [8 empty] | 南濱DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | [5 empty] | 833 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | StaDev | BUS |  | 12B_CTFA | 161KV BUS 87RY CT 迴路故障 |  | Status | #1#2 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1110 |  |  | 2-35-06 |  |  | 161kV BUS | A/N | 161KV BUS 87RY CT 迴路故障 |  |  | B2/D03_A1 | [8 empty] | 南濱DS.161KV_BUS_CTFA | 161KV BUS 87RY CT回路故障 | OTHER | [5 empty] | 834 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | ComPoint |  |  | OLTC_A |  |  | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1111 |  |  | 2-35-07 |  |  | OLTC | OLTCA | OLTC 15分鐘內連動3次警報 |  |  | B3/D03_A1 | [8 empty] | 南濱DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | [5 empty] | 835 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS |  |  | 1DTR | #1DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1120 |  |  | 2-36-00 |  |  | Locate Empty |  | NO.1 D.TR.撲氣電驛(1) 196B1 |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | [5 empty] | 836 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS |  |  | 1DTR | #1DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1121 |  |  | 2-36-01 |  |  | Locate Empty |  | NO.1 D.TR.撲氣電驛(2) 196B2 |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | [5 empty] | 837 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS |  |  | 1DTR | #1DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1122 |  |  | 2-36-02 |  |  | Locate Empty |  | NO.1 D.TR.放壓裝置 196D |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#1DTR_96D | #1DTR 96D RY | MTR | [5 empty] | 838 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS |  |  | 1DTR | #1DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1123 |  |  | 2-36-03 |  |  | Locate Empty |  | NO.1 D.TR.衝擊油壓 196P |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#1DTR_96P | #1DTR 96P RY | MTR | [5 empty] | 839 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS |  |  | 1DTR | #1DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1124 |  |  | 2-36-04 |  |  | Locate Empty |  | NO.1 D.TR. ULTC 163Q |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#1DTR_63Q | #1DTR 63Q RY | MTR | [5 empty] | 840 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS |  |  | 2DTR | #2DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1125 |  |  | 2-36-05 |  |  | Locate Empty |  | NO.2 D.TR.撲氣電驛(1) 296B1 |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | [5 empty] | 841 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS |  |  | 2DTR | #2DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1126 |  |  | 2-36-06 |  |  | Locate Empty |  | NO.2 D.TR.撲氣電驛(2) 296B2 |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | [5 empty] | 842 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS |  |  | 2DTR | #2DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1127 |  |  | 2-36-07 |  |  | Locate Empty |  | NO.2 D.TR.放壓裝置 296D |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#2DTR_96D | #2DTR 96D RY | MTR | [5 empty] | 843 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS |  |  | 2DTR | #2DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1128 |  |  | 2-36-08 |  |  | Locate Empty |  | NO.2 D.TR.衝擊油壓 296P |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#2DTR_96P | #2DTR 96P RY | MTR | [5 empty] | 844 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS |  |  | 2DTR | #2DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1129 |  |  | 2-36-09 |  |  | Locate Empty |  | NO.2 D.TR. ULTC 263Q |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#2DTR_63Q | #2DTR 63Q RY | MTR | [5 empty] | 845 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS |  |  | 3DTR | #3DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1130 |  |  | 2-36-10 |  |  | Locate Empty |  | NO.3 D.TR.撲氣電驛(1) 396B1 |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#3DTR_96B1 | #3DTR 96B1 RY | MTR | [5 empty] | 846 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS |  |  | 3DTR | #3DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1131 |  |  | 2-36-11 |  |  | Locate Empty |  | NO.3 D.TR.撲氣電驛(2) 396B2 |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#3DTR_96B2 | #3DTR 96B2 RY | MTR | [5 empty] | 847 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS |  |  | 3DTR | #3DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1132 |  |  | 2-36-12 |  |  | Locate Empty |  | NO.3 D.TR.放壓裝置 396D |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#3DTR_96D | #3DTR 96D RY | MTR | [5 empty] | 848 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS |  |  | 3DTR | #3DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1133 |  |  | 2-36-13 |  |  | Locate Empty |  | NO.3 D.TR.衝擊油壓 396P |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#3DTR_96P | #3DTR 96P RY | MTR | [5 empty] | 849 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS |  |  | 3DTR | #3DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1134 |  |  | 2-36-14 |  |  | Locate Empty |  | NO.3 D.TR. ULTC 363Q |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#3DTR_63Q | #3DTR 63Q RY | MTR | [5 empty] | 850 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS |  |  | 4DTR | #4DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1135 |  |  | 2-36-15 |  |  | Locate Empty |  | NO.4 D.TR.撲氣電驛(1) 496B1 |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#4DTR_96B1 | #4DTR 96B1 RY | MTR | [5 empty] | 851 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS |  |  | 4DTR | #4DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1136 |  |  | 2-37-00 |  |  | Locate Empty |  | NO.4 D.TR.撲氣電驛(2) 496B2 |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#4DTR_96B2 | #4DTR 96B2 RY | MTR | [5 empty] | 852 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS |  |  | 4DTR | #4DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1137 |  |  | 2-37-01 |  |  | Locate Empty |  | NO.4 D.TR.放壓裝置 496D |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#4DTR_96D | #4DTR 96D RY | MTR | [5 empty] | 853 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS |  |  | 4DTR | #4DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1138 |  |  | 2-37-02 |  |  | Locate Empty |  | NO.4 D.TR.衝擊油壓 496P |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#4DTR_96P | #4DTR 96P RY | MTR | [5 empty] | 854 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS |  |  | 4DTR | #4DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1139 |  |  | 2-37-03 |  |  | Locate Empty |  | NO.4 D.TR. ULTC 463Q |  |  | B1/D03_A1 | [8 empty] | 南濱DS.#4DTR_63Q | #4DTR 63Q RY | MTR | [5 empty] | 855 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1510 | 安南～南濱一路(1510) |  | DS1 | 1511 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0896 | 641 |  | 1-38-00 | 1-38-01 |  | 1511 | ON | 安南南濱一路(1511) DS-AS |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1511_DS | 1511(安南南濱一路) DS | LINE161 | [5 empty] | 856 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 161 | 161kV | 1510 | 安南～南濱一路(1510) |  | DS2 | 1512 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0898 | 643 |  | 1-38-02 | 1-38-03 |  | 1512 | ON | 安南南濱一路 (1512) DS-AS |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1512_DS | 1512(安南南濱一路) DS | LINE161 | [5 empty] | 857 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D03 | 南濱DS | 161 | 161kV | 1510 | 安南～南濱一路(1510) |  | DS3 | 1513 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0900 | 645 |  | 1-38-04 | 1-38-05 |  | 1513 | ON | 安南南濱一路 (1513) DS-AS |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1513_DS | 1513(安南南濱一路) DS | LINE161 | [5 empty] | 858 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 161 | 161kV | 1510 | 安南～南濱一路(1510) |  | ES3 | 1513E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0902 | 647 |  | 1-38-06 | 1-38-07 |  | 1513E | ON | 安南南濱一路 (1513E) ES-AS |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1513E_ES | 1513E(安南南濱一路) ES | LINE161 | [5 empty] | 859 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D03 | 南濱DS | 161 | 161kV | 1520 | 安南～南濱二路(1520) |  | DS1 | 1521 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0904 | 649 |  | 1-38-08 | 1-38-09 |  | 1521 | ON | 安南南濱二路 (1521) DS-AS |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1521_DS | 1521(安南南濱二路) DS | LINE161 | [5 empty] | 860 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D03 | 南濱DS | 161 | 161kV | 1520 | 安南～南濱二路(1520) |  | DS2 | 1522 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0906 | 651 |  | 1-38-10 | 1-38-11 |  | 1522 | ON | 安南南濱二路 (1522) DS-AS |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1522_DS | 1522(安南南濱二路) DS | LINE161 | [5 empty] | 861 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 161 | 161kV | 1520 | 安南～南濱二路(1520) |  | DS3 | 1523 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0908 | 653 |  | 1-38-12 | 1-38-13 |  | 1523 | ON | 安南南濱二路 (1523) DS-AS |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1523_DS | 1523(安南南濱二路) DS | LINE161 | [5 empty] | 862 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 161 | 161kV | 1520 | 安南～南濱二路(1520) |  | ES3 | 1523E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0910 | 655 |  | 1-38-14 | 1-38-15 |  | 1523E | ON | 安南南濱二路 (1523E) ES-AS |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1523E_ES | 1523E(安南南濱二路) ES | LINE161 | [5 empty] | 863 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱～安瀚線(1530) |  | DS1 | 1531 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0912 | 657 |  | 1-39-00 | 1-39-01 |  | 1531 | ON | 南濱安瀚線 (1531) DS-AS |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1531_DS | 1531(南濱安瀚線) DS | LINE161 | [5 empty] | 864 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱～安瀚線(1530) |  | DS2 | 1532 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0914 | 659 |  | 1-39-02 | 1-39-03 |  | 1532 | ON | 南濱安瀚線 (1532) DS-AS |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1532_DS | 1532(南濱安瀚線) DS | LINE161 | [5 empty] | 865 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱～安瀚線(1530) |  | DS3 | 1533 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0916 | 661 |  | 1-39-04 | 1-39-05 |  | 1533 | ON | 南濱安瀚線 (1533) DS-AS |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1533_DS | 1533(南濱安瀚線) DS | LINE161 | [5 empty] | 866 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱～安瀚線(1530) |  | ES3 | 1533E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0918 | 663 |  | 1-39-06 | 1-39-07 |  | 1533E | ON | 南濱安瀚線 (1533E) ES-AS |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1533E_ES | 1533E(南濱安瀚線) ES | LINE161 | [5 empty] | 867 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱～凸版線(1540) |  | DS1 | 1541 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0920 | 665 |  | 1-39-08 | 1-39-09 |  | 1541 | ON | 南濱凸版線 (1541) DS-AS |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1541_DS | 1541(南濱凸版線) DS | LINE161 | [5 empty] | 868 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱～凸版線(1540) |  | DS2 | 1542 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0922 | 667 |  | 1-39-10 | 1-39-11 |  | 1542 | ON | 南濱凸版線 (1542) DS-AS |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1542_DS | 1542(南濱凸版線) DS | LINE161 | [5 empty] | 869 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱～凸版線(1540) |  | DS3 | 1543 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0924 | 669 |  | 1-39-12 | 1-39-13 |  | 1543 | ON | 南濱凸版線 (1543) DS-AS |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1543_DS | 1543(南濱凸版線) DS | LINE161 | [5 empty] | 870 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱～凸版線(1540) |  | ES3 | 1543E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0926 | 671 |  | 1-39-14 | 1-39-15 |  | 1543E | ON | 南濱凸版線 (1543E) ES-AS |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1543E_ES | 1543E(南濱凸版線) ES | LINE161 | [5 empty] | 871 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D03 | 南濱DS | 161 | 161kV | 1550 | 南濱～鹿耳紅線(1550) |  | DS1 | 1551 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0928 | 673 |  | 1-3A-00 | 1-3A-01 |  | 1551 | ON | 南濱鹿耳紅線 (1551) DS-AS |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1551_DS | 1551(南濱鹿耳紅線) DS | LINE161 | [5 empty] | 872 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 161 | 161kV | 1550 | 南濱～鹿耳紅線(1550) |  | DS2 | 1552 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0930 | 675 |  | 1-3A-02 | 1-3A-03 |  | 1552 | ON | 南濱鹿耳紅線 (1552) DS-AS |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1552_DS | 1552(南濱鹿耳紅線) DS | LINE161 | [5 empty] | 873 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D03 | 南濱DS | 161 | 161kV | 1550 | 南濱～鹿耳紅線(1550) |  | DS3 | 1553 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0932 | 677 |  | 1-3A-04 | 1-3A-05 |  | 1553 | ON | 南濱鹿耳紅線 (1553) DS-AS |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1553_DS | 1553(南濱鹿耳紅線) DS | LINE161 | [5 empty] | 874 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 161 | 161kV | 1550 | 南濱～鹿耳紅線(1550) |  | ES3 | 1553E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0934 | 679 |  | 1-3A-06 | 1-3A-07 |  | 1553E | ON | 南濱鹿耳紅線 (1553E) ES-AS |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1553E_ES | 1553E(南濱鹿耳紅線) ES | LINE161 | [5 empty] | 875 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D03 | 南濱DS | 161 | 161kV | 1560 | 南濱～鹿耳白線(1560) |  | DS1 | 1561 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0936 | 681 |  | 1-3A-08 | 1-3A-09 |  | 1561 | ON | 南濱鹿耳白線 (1561) DS-AS |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1561_DS | 1561(南濱鹿耳白線) DS | LINE161 | [5 empty] | 876 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D03 | 南濱DS | 161 | 161kV | 1560 | 南濱～鹿耳白線(1560) |  | DS2 | 1562 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0938 | 683 |  | 1-3A-10 | 1-3A-11 |  | 1562 | ON | 南濱鹿耳白線 (1562) DS-AS |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1562_DS | 1562(南濱鹿耳白線) DS | LINE161 | [5 empty] | 877 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 161 | 161kV | 1560 | 南濱～鹿耳白線(1560) |  | DS3 | 1563 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0940 | 685 |  | 1-3A-12 | 1-3A-13 |  | 1563 | ON | 南濱鹿耳白線 (1563) DS-AS |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1563_DS | 1563(南濱鹿耳白線) DS | LINE161 | [5 empty] | 878 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 161 | 161kV | 1560 | 南濱～鹿耳白線(1560) |  | ES3 | 1563E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0942 | 687 |  | 1-3A-14 | 1-3A-15 |  | 1563E | ON | 南濱鹿耳白線 (1563E) ES-AS |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1563E_ES | 1563E(南濱鹿耳白線) ES | LINE161 | [5 empty] | 879 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D03 | 南濱DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0976 | 721 |  | 1-3D-00 | 1-3D-01 |  | 1501 | ON | 161 TIE (1501) DS-AS |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1501_DS | 1501(TIE) DS | TIE | [5 empty] | 880 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0978 | 723 |  | 1-3D-02 | 1-3D-03 |  | 1502 | ON | 161 TIE (1502) DS-AS |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1502_DS | 1502(TIE) DS | TIE | [5 empty] | 881 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0980 | 725 |  | 1-3D-04 | 1-3D-05 |  | 1751 | ON | NO.1 DTR(1751) DS-AS |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1751_DS | 1751(#1DTR) DS | MTR | [5 empty] | 882 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0982 | 727 |  | 1-3D-06 | 1-3D-07 |  | 1752 | ON | NO.1 DTR(1752) DS-AS |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1752_DS | 1752(#1DTR) DS | MTR | [5 empty] | 883 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D03 | 南濱DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0984 | 729 |  | 1-3D-08 | 1-3D-09 |  | 1761 | ON | NO.2 DTR(1761) DS-AS |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1761_DS | 1761(#2DTR) DS | MTR | [5 empty] | 884 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D03 | 南濱DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0986 | 731 |  | 1-3D-10 | 1-3D-11 |  | 1762 | ON | NO.2 DTR(1762) DS-AS |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1762_DS | 1762(#2DTR) DS | MTR | [5 empty] | 885 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0988 | 733 |  | 1-3D-12 | 1-3D-13 |  | 1771 | ON | NO.3 DTR(1771) DS-AS |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1771_DS | 1771(#3DTR) DS | MTR | [5 empty] | 886 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0990 | 735 |  | 1-3D-14 | 1-3D-15 |  | 1772 | ON | NO.3 DTR(1772) DS-AS |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1772_DS | 1772(#3DTR) DS | MTR | [5 empty] | 887 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D03 | 南濱DS | 161 | 161kV | 1780 | #4DTR(1780) |  | DS1 | 1781 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0992 | 737 |  | 1-3E-00 | 1-3E-01 |  | 1781 | ON | NO.4 DTR(1781) DS-AS |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1781_DS | 1781(#4DTR) DS | MTR | [5 empty] | 888 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D03 | 南濱DS | 161 | 161kV | 1780 | #4DTR(1780) |  | DS2 | 1782 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0994 | 739 |  | 1-3E-02 | 1-3E-03 |  | 1782 | ON | NO.4 DTR(1782) DS-AS |  |  | B2/D03_A1 | [8 empty] | 南濱DS.1782_DS | 1782(#4DTR) DS | MTR | [5 empty] | 889 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 11 | 11kV | LBS210 | #1SC(210) |  | LBS |  |  | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/210 | C/1SC(B) |  |  | 0996 | 741 |  | 1-3E-04 | 1-3E-05 |  | SC1A | ON | #1SC 210 LBS LBS-AS |  |  | B3/D03_A1 | [8 empty] | 南濱DS.210_LBS | 210(11KV #1SC) LBS | SC | [5 empty] | 890 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 11 | 11kV | LBS220 | #2SC(220) |  | LBS |  |  | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/220 | C/2SC(B) |  |  | 0998 | 743 |  | 1-3E-06 | 1-3E-07 |  | SC1B | ON | #2SC 220 LBS LBS-AS |  |  | B3/D03_A1 | [8 empty] | 南濱DS.220_LBS | 220(11KV #2SC) LBS | SC | [5 empty] | 891 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 11 | 11kV | LBS230 | #1SC(230) |  | LBS |  |  | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/230 | C/3SC(B) |  |  | 1000 | 1001 | [9 empty] | B3/D03_A1 | [8 empty] | 南濱DS.230_LBS | 230(11KV #3SC) LBS | SC | [5 empty] | 892 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 11 | 11kV | LBS240 | #2SC(220) |  | LBS |  |  | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/240 | C/4SC(B) |  |  | 1002 | 1003 | [9 empty] | B3/D03_A1 | [8 empty] | 南濱DS.240_LBS | 240(11KV #4SC) LBS | SC | [5 empty] | 893 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS |  |  | 1DTR | #1DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0105 | [10 empty] | B1/D03_A1 | [16 empty] | 894 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D03 | 南濱DS |  |  | 3DTR | #3DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0106 | [10 empty] | B1/D03_A1 | [16 empty] | 895 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D03 | 南濱DS |  |  | 4DTR | #4DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0107 | [10 empty] | B1/D03_A1 | [16 empty] | 896 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D03 | 南濱DS |  |  | 1DTR | #1DTR |  | 87UL2 |  |  | Status | 第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1140 | [10 empty] | B1/D03_A1 | [16 empty] | 897 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D03 | 南濱DS |  |  | 3DTR | #3DTR |  | 87UL2 |  |  | Status | 第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1143 | [10 empty] | B1/D03_A1 | [16 empty] | 898 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D03 | 南濱DS |  |  | 4DTR | #4DTR |  | 87UL2 |  |  | Status | 第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1146 | [10 empty] | B1/D03_A1 | [16 empty] | 899 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D03 | 南濱DS |  |  | 1DTR | #1DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1141 | [10 empty] | B1/D03_A1 | [16 empty] | 900 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D03 | 南濱DS |  |  | 3DTR | #3DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1144 | [10 empty] | B1/D03_A1 | [16 empty] | 901 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D03 | 南濱DS |  |  | 4DTR | #4DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1147 | [10 empty] | B1/D03_A1 | [16 empty] | 902 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D03 | 南濱DS |  |  | 1DTR | #1DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1142 | [10 empty] | B1/D03_A1 | [16 empty] | 903 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D03 | 南濱DS |  |  | 3DTR | #3DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1145 | [10 empty] | B1/D03_A1 | [16 empty] | 904 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D03 | 南濱DS |  |  | 4DTR | #4DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1148 | [10 empty] | B1/D03_A1 | [16 empty] | 905 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
D03 | 南濱DS | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/D03_A1 | [12 empty] | 南濱DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: D03/161/1BUS/V; OPRD2: D03/161/2BUS/V
D03 | 南濱DS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/D03_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: D03/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
D03 | 南濱DS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/D03_A1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_6 | OPRD1: D03/161/1510/MW; OPRD2: D03/161/1520/MW; OPRD3: D03/161/1530/MW; OPRD4: D03/161/1540/MW; OPRD5: D03/161/1550/MW; OPRD6: D03/161/1560/MW
D03 | 南濱DS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/D03_A1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: D03/0/CalcPoint/OPRN2_MW
D03 | 南濱DS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/D03_A1 | [17 empty] | none
D03 | 南濱DS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/D03_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: D03/0/CalcPoint/OPRN1; OPRD2: D03/0/CalcPoint/OPRN2; OPRD3: D03/0/CalcPoint/PRFL_UL
D03 | 南濱DS |  |  | 1DTR | 1DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D03_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D03/11/310/I_R; OPRD2: D03/11/320/I_R
D03 | 南濱DS |  |  | 1DTR | 1DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D03_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D03/11/310/I_S; OPRD2: D03/11/320/I_S
D03 | 南濱DS |  |  | 1DTR | 1DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D03_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D03/11/310/I_T; OPRD2: D03/11/320/I_T
D03 | 南濱DS |  |  | 2DTR | 2DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D03_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D03/11/330/I_R; OPRD2: D03/11/340/I_R
D03 | 南濱DS |  |  | 2DTR | 2DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D03_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D03/11/330/I_S; OPRD2: D03/11/340/I_S
D03 | 南濱DS |  |  | 2DTR | 2DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D03_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D03/11/330/I_T; OPRD2: D03/11/340/I_T
D03 | 南濱DS | 161 | 161kV | 1510 | 安南～南濱一路(1510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D03_A1 | [12 empty] | 南濱DS.1510_AMP | 安南南濱一路 AMP | LINE161 | AMP_CAL | C20R1328 | amp_cal | OPRD1: D03/161/1510/MW; OPRD2: D03/161/1510/MVAR; OPRD3: D03/0/CalcPoint/Vbs4
D03 | 南濱DS | 161 | 161kV | 1520 | 安南～南濱二路(1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D03_A1 | [12 empty] | 南濱DS.1520_AMP | 安南南濱二路 AMP | LINE161 | AMP_CAL | C20R1930 | amp_cal | OPRD1: D03/161/1520/MW; OPRD2: D03/161/1520/MVAR; OPRD3: D03/0/CalcPoint/Vbs4
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱～安瀚線(1530) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D03_A1 | [12 empty] | 南濱DS.1530_AMP | 南濱安瀚線 AMP | LINE161 | AMP_CAL | C20R0964 | amp_cal | OPRD1: D03/161/1530/MW; OPRD2: D03/161/1530/MVAR; OPRD3: D03/0/CalcPoint/Vbs4
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱～凸版線(1540) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D03_A1 | [12 empty] | 南濱DS.1540_AMP | 南濱凸版線 AMP | LINE161 | AMP_CAL | C20R0964 | amp_cal | OPRD1: D03/161/1540/MW; OPRD2: D03/161/1540/MVAR; OPRD3: D03/0/CalcPoint/Vbs4
D03 | 南濱DS | 161 | 161kV | 1550 | 南濱～鹿耳紅線(1550) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D03_A1 | [12 empty] | 南濱DS.1550_AMP | 南濱鹿耳紅線 AMP | LINE161 | AMP_CAL | C20R1930 | amp_cal | OPRD1: D03/161/1550/MW; OPRD2: D03/161/1550/MVAR; OPRD3: D03/0/CalcPoint/Vbs4
D03 | 南濱DS | 161 | 161kV | 1560 | 南濱～鹿耳白線(1560) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D03_A1 | [12 empty] | 南濱DS.1560_AMP | 南濱鹿耳白線 AMP | LINE161 | AMP_CAL | C20R1930 | amp_cal | OPRD1: D03/161/1560/MW; OPRD2: D03/161/1560/MVAR; OPRD3: D03/0/CalcPoint/Vbs4
D03 | 南濱DS | 11 | 11kV | 1ABUS | #1ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D03_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D03/11/1ABUS/V
D03 | 南濱DS | 11 | 11kV | 1BBUS | #1BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D03_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D03/11/1BBUS/V
D03 | 南濱DS | 11 | 11kV | 2ABUS | #2ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D03_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D03/11/2ABUS/V
D03 | 南濱DS | 11 | 11kV | 2BBUS | #2BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D03_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D03/11/2BBUS/V
D03 | 南濱DS | 22 | 22kV | 3BUS | #3BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D03_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D03/22/3BUS/V
D03 | 南濱DS | 22 | 22kV | 4BUS | #4BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D03_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D03/22/4BUS/V
D03 | 南濱DS |  |  | 1DTR(A) | #1DTR(A) |  | TR_PERM | [9 empty] | B1/D03_A1 | [12 empty] | 南濱DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D03//1DTR(A)/SupLocal; OPRD2: D03//1DTR(A)/Tap Chan
D03 | 南濱DS |  |  | 1DTR(B) | #1DTR(B) |  | TR_PERM | [9 empty] | B1/D03_A1 | [12 empty] | 南濱DS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D03//1DTR(B)/SupLocal; OPRD2: D03//1DTR(B)/Tap Chan
D03 | 南濱DS |  |  | 2DTR(A) | #2DTR(A) |  | TR_PERM | [9 empty] | B1/D03_A1 | [12 empty] | 南濱DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D03//2DTR(A)/SupLocal; OPRD2: D03//2DTR(A)/Tap Chan
D03 | 南濱DS |  |  | 2DTR(B) | #2DTR(B) |  | TR_PERM | [9 empty] | B1/D03_A1 | [12 empty] | 南濱DS.#2DTR(B)_PERM | #2DTR(B) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D03//2DTR(B)/SupLocal; OPRD2: D03//2DTR(B)/Tap Chan
D03 | 南濱DS |  |  | 3DTR | #3DTR |  | TR_PERM | [9 empty] | B1/D03_A1 | [12 empty] | 南濱DS.#3DTR_PERM | #3DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D03//3DTR/SupLocal; OPRD2: D03//3DTR/Tap Chan
D03 | 南濱DS |  |  | 4DTR | #4DTR |  | TR_PERM | [9 empty] | B1/D03_A1 | [12 empty] | 南濱DS.#4DTR_PERM | #4DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D03//4DTR/SupLocal; OPRD2: D03//4DTR/Tap Chan
D03 | 南濱DS | 11 | 11kV | K311 | 濱11線(K311) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/11/1ABUS/V; OPRD2: D03/11/K311/I_R; OPRD3: D03/11/K311/I_S; OPRD4: D03/11/K311/I_T
D03 | 南濱DS | 11 | 11kV | K312 | 濱12線(K312) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/11/1ABUS/V; OPRD2: D03/11/K312/I_R; OPRD3: D03/11/K312/I_S; OPRD4: D03/11/K312/I_T
D03 | 南濱DS | 11 | 11kV | K313 | 濱13線(K313) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/11/1ABUS/V; OPRD2: D03/11/K313/I_R; OPRD3: D03/11/K313/I_S; OPRD4: D03/11/K313/I_T
D03 | 南濱DS | 11 | 11kV | K314 | 濱14線(K314) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/11/1ABUS/V; OPRD2: D03/11/K314/I_R; OPRD3: D03/11/K314/I_S; OPRD4: D03/11/K314/I_T
D03 | 南濱DS | 11 | 11kV | K315 | 濱15線(K315) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/11/1ABUS/V; OPRD2: D03/11/K315/I_R; OPRD3: D03/11/K315/I_S; OPRD4: D03/11/K315/I_T
D03 | 南濱DS | 11 | 11kV | K316 | 濱16線(K316) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/11/1BBUS/V; OPRD2: D03/11/K316/I_R; OPRD3: D03/11/K316/I_S; OPRD4: D03/11/K316/I_T
D03 | 南濱DS | 11 | 11kV | K317 | 濱17線(K317) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/11/1BBUS/V; OPRD2: D03/11/K317/I_R; OPRD3: D03/11/K317/I_S; OPRD4: D03/11/K317/I_T
D03 | 南濱DS | 11 | 11kV | K318 | 濱18線(K318) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/11/1BBUS/V; OPRD2: D03/11/K318/I_R; OPRD3: D03/11/K318/I_S; OPRD4: D03/11/K318/I_T
D03 | 南濱DS | 11 | 11kV | K319 | 濱19線(K319) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/11/1BBUS/V; OPRD2: D03/11/K319/I_R; OPRD3: D03/11/K319/I_S; OPRD4: D03/11/K319/I_T
D03 | 南濱DS | 11 | 11kV | K320 | 濱20線(K320) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/11/1BBUS/V; OPRD2: D03/11/K320/I_R; OPRD3: D03/11/K320/I_S; OPRD4: D03/11/K320/I_T
D03 | 南濱DS | 11 | 11kV | K321 | 濱21線(K321) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/11/2ABUS/V; OPRD2: D03/11/K321/I_R; OPRD3: D03/11/K321/I_S; OPRD4: D03/11/K321/I_T
D03 | 南濱DS | 11 | 11kV | K322 | 濱22線(K322) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/11/2ABUS/V; OPRD2: D03/11/K322/I_R; OPRD3: D03/11/K322/I_S; OPRD4: D03/11/K322/I_T
D03 | 南濱DS | 11 | 11kV | K323 | 濱23線(K323) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/11/2ABUS/V; OPRD2: D03/11/K323/I_R; OPRD3: D03/11/K323/I_S; OPRD4: D03/11/K323/I_T
D03 | 南濱DS | 11 | 11kV | K324 | 濱24線(K324) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/11/2ABUS/V; OPRD2: D03/11/K324/I_R; OPRD3: D03/11/K324/I_S; OPRD4: D03/11/K324/I_T
D03 | 南濱DS | 11 | 11kV | K325 | 濱25線(K325) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/11/2ABUS/V; OPRD2: D03/11/K325/I_R; OPRD3: D03/11/K325/I_S; OPRD4: D03/11/K325/I_T
D03 | 南濱DS | 11 | 11kV | K326 | 濱26線(K326) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/11/2BBUS/V; OPRD2: D03/11/K326/I_R; OPRD3: D03/11/K326/I_S; OPRD4: D03/11/K326/I_T
D03 | 南濱DS | 11 | 11kV | K327 | 濱27線(K327) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/11/2BBUS/V; OPRD2: D03/11/K327/I_R; OPRD3: D03/11/K327/I_S; OPRD4: D03/11/K327/I_T
D03 | 南濱DS | 11 | 11kV | K328 | 濱28線(K328) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/11/2BBUS/V; OPRD2: D03/11/K328/I_R; OPRD3: D03/11/K328/I_S; OPRD4: D03/11/K328/I_T
D03 | 南濱DS | 11 | 11kV | K329 | 濱29線(K329) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/11/2BBUS/V; OPRD2: D03/11/K329/I_R; OPRD3: D03/11/K329/I_S; OPRD4: D03/11/K329/I_T
D03 | 南濱DS | 11 | 11kV | K330 | 濱30線(K330) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/11/2BBUS/V; OPRD2: D03/11/K330/I_R; OPRD3: D03/11/K330/I_S; OPRD4: D03/11/K330/I_T
D03 | 南濱DS | 22 | 22kV | K361 | 濱61線(K361) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/22/3BUS/V; OPRD2: D03/22/K361/I_R; OPRD3: D03/22/K361/I_S; OPRD4: D03/22/K361/I_T
D03 | 南濱DS | 22 | 22kV | K362 | 濱62線(K362) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/22/3BUS/V; OPRD2: D03/22/K362/I_R; OPRD3: D03/22/K362/I_S; OPRD4: D03/22/K362/I_T
D03 | 南濱DS | 22 | 22kV | K363 | 濱63線(K363) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/22/3BUS/V; OPRD2: D03/22/K363/I_R; OPRD3: D03/22/K363/I_S; OPRD4: D03/22/K363/I_T
D03 | 南濱DS | 22 | 22kV | K364 | 濱64線(K364) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/22/3BUS/V; OPRD2: D03/22/K364/I_R; OPRD3: D03/22/K364/I_S; OPRD4: D03/22/K364/I_T
D03 | 南濱DS | 22 | 22kV | K365 | 濱65線(K365) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/22/3BUS/V; OPRD2: D03/22/K365/I_R; OPRD3: D03/22/K365/I_S; OPRD4: D03/22/K365/I_T
D03 | 南濱DS | 22 | 22kV | K366 | 濱66線(K366) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/22/3BUS/V; OPRD2: D03/22/K366/I_R; OPRD3: D03/22/K366/I_S; OPRD4: D03/22/K366/I_T
D03 | 南濱DS | 22 | 22kV | K367 | 濱67線(K367) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/22/3BUS/V; OPRD2: D03/22/K367/I_R; OPRD3: D03/22/K367/I_S; OPRD4: D03/22/K367/I_T
D03 | 南濱DS | 22 | 22kV | K368 | 濱68線(K368) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/22/3BUS/V; OPRD2: D03/22/K368/I_R; OPRD3: D03/22/K368/I_S; OPRD4: D03/22/K368/I_T
D03 | 南濱DS | 22 | 22kV | K371 | 濱71線(K371) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/22/4BUS/V; OPRD2: D03/22/K371/I_R; OPRD3: D03/22/K371/I_S; OPRD4: D03/22/K371/I_T
D03 | 南濱DS | 22 | 22kV | K372 | 濱72線(K372) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/22/4BUS/V; OPRD2: D03/22/K372/I_R; OPRD3: D03/22/K372/I_S; OPRD4: D03/22/K372/I_T
D03 | 南濱DS | 22 | 22kV | K373 | 濱73線(K373) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/22/4BUS/V; OPRD2: D03/22/K373/I_R; OPRD3: D03/22/K373/I_S; OPRD4: D03/22/K373/I_T
D03 | 南濱DS | 22 | 22kV | K374 | 濱74線(K374) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/22/4BUS/V; OPRD2: D03/22/K374/I_R; OPRD3: D03/22/K374/I_S; OPRD4: D03/22/K374/I_T
D03 | 南濱DS | 22 | 22kV | K375 | 濱75線(K375) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/22/4BUS/V; OPRD2: D03/22/K375/I_R; OPRD3: D03/22/K375/I_S; OPRD4: D03/22/K375/I_T
D03 | 南濱DS | 22 | 22kV | K376 | 濱76線(K376) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/22/4BUS/V; OPRD2: D03/22/K376/I_R; OPRD3: D03/22/K376/I_S; OPRD4: D03/22/K376/I_T
D03 | 南濱DS | 22 | 22kV | K377 | 濱77線(K377) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/22/4BUS/V; OPRD2: D03/22/K377/I_R; OPRD3: D03/22/K377/I_S; OPRD4: D03/22/K377/I_T
D03 | 南濱DS | 22 | 22kV | K378 | 濱78線(K378) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D03/22/4BUS/V; OPRD2: D03/22/K378/I_R; OPRD3: D03/22/K378/I_S; OPRD4: D03/22/K378/I_T
D03 | 南濱DS | 11 | 11kV | K311 | 濱11線(K311) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/11/K311/kVA; OPRD2: D03/11/K311/KVAR
D03 | 南濱DS | 11 | 11kV | K312 | 濱12線(K312) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/11/K312/kVA; OPRD2: D03/11/K312/KVAR
D03 | 南濱DS | 11 | 11kV | K313 | 濱13線(K313) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/11/K313/kVA; OPRD2: D03/11/K313/KVAR
D03 | 南濱DS | 11 | 11kV | K314 | 濱14線(K314) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/11/K314/kVA; OPRD2: D03/11/K314/KVAR
D03 | 南濱DS | 11 | 11kV | K315 | 濱15線(K315) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/11/K315/kVA; OPRD2: D03/11/K315/KVAR
D03 | 南濱DS | 11 | 11kV | K316 | 濱16線(K316) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/11/K316/kVA; OPRD2: D03/11/K316/KVAR
D03 | 南濱DS | 11 | 11kV | K317 | 濱17線(K317) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/11/K317/kVA; OPRD2: D03/11/K317/KVAR
D03 | 南濱DS | 11 | 11kV | K318 | 濱18線(K318) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/11/K318/kVA; OPRD2: D03/11/K318/KVAR
D03 | 南濱DS | 11 | 11kV | K319 | 濱19線(K319) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/11/K319/kVA; OPRD2: D03/11/K319/KVAR
D03 | 南濱DS | 11 | 11kV | K320 | 濱20線(K320) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/11/K320/kVA; OPRD2: D03/11/K320/KVAR
D03 | 南濱DS | 11 | 11kV | K321 | 濱21線(K321) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/11/K321/kVA; OPRD2: D03/11/K321/KVAR
D03 | 南濱DS | 11 | 11kV | K322 | 濱22線(K322) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/11/K322/kVA; OPRD2: D03/11/K322/KVAR
D03 | 南濱DS | 11 | 11kV | K323 | 濱23線(K323) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/11/K323/kVA; OPRD2: D03/11/K323/KVAR
D03 | 南濱DS | 11 | 11kV | K324 | 濱24線(K324) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/11/K324/kVA; OPRD2: D03/11/K324/KVAR
D03 | 南濱DS | 11 | 11kV | K325 | 濱25線(K325) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/11/K325/kVA; OPRD2: D03/11/K325/KVAR
D03 | 南濱DS | 11 | 11kV | K326 | 濱26線(K326) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/11/K326/kVA; OPRD2: D03/11/K326/KVAR
D03 | 南濱DS | 11 | 11kV | K327 | 濱27線(K327) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/11/K327/kVA; OPRD2: D03/11/K327/KVAR
D03 | 南濱DS | 11 | 11kV | K328 | 濱28線(K328) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/11/K328/kVA; OPRD2: D03/11/K328/KVAR
D03 | 南濱DS | 11 | 11kV | K329 | 濱29線(K329) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/11/K329/kVA; OPRD2: D03/11/K329/KVAR
D03 | 南濱DS | 11 | 11kV | K330 | 濱30線(K330) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/11/K330/kVA; OPRD2: D03/11/K330/KVAR
D03 | 南濱DS | 22 | 22kV | K361 | 濱61線(K361) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/22/K361/kVA; OPRD2: D03/22/K361/KVAR
D03 | 南濱DS | 22 | 22kV | K362 | 濱62線(K362) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/22/K362/kVA; OPRD2: D03/22/K362/KVAR
D03 | 南濱DS | 22 | 22kV | K363 | 濱63線(K363) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/22/K363/kVA; OPRD2: D03/22/K363/KVAR
D03 | 南濱DS | 22 | 22kV | K364 | 濱64線(K364) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/22/K364/kVA; OPRD2: D03/22/K364/KVAR
D03 | 南濱DS | 22 | 22kV | K365 | 濱65線(K365) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/22/K365/kVA; OPRD2: D03/22/K365/KVAR
D03 | 南濱DS | 22 | 22kV | K366 | 濱66線(K366) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/22/K366/kVA; OPRD2: D03/22/K366/KVAR
D03 | 南濱DS | 22 | 22kV | K367 | 濱67線(K367) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/22/K367/kVA; OPRD2: D03/22/K367/KVAR
D03 | 南濱DS | 22 | 22kV | K368 | 濱68線(K368) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/22/K368/kVA; OPRD2: D03/22/K368/KVAR
D03 | 南濱DS | 22 | 22kV | K371 | 濱71線(K371) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/22/K371/kVA; OPRD2: D03/22/K371/KVAR
D03 | 南濱DS | 22 | 22kV | K372 | 濱72線(K372) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/22/K372/kVA; OPRD2: D03/22/K372/KVAR
D03 | 南濱DS | 22 | 22kV | K373 | 濱73線(K373) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/22/K373/kVA; OPRD2: D03/22/K373/KVAR
D03 | 南濱DS | 22 | 22kV | K374 | 濱74線(K374) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/22/K374/kVA; OPRD2: D03/22/K374/KVAR
D03 | 南濱DS | 22 | 22kV | K375 | 濱75線(K375) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/22/K375/kVA; OPRD2: D03/22/K375/KVAR
D03 | 南濱DS | 22 | 22kV | K376 | 濱76線(K376) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/22/K376/kVA; OPRD2: D03/22/K376/KVAR
D03 | 南濱DS | 22 | 22kV | K377 | 濱77線(K377) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/22/K377/kVA; OPRD2: D03/22/K377/KVAR
D03 | 南濱DS | 22 | 22kV | K378 | 濱78線(K378) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D03_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D03/22/K378/kVA; OPRD2: D03/22/K378/KVAR
D03 | 南濱DS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D03_A1 | [12 empty] | 南濱DS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D03/11/210/CB; OPRD2: 6.9; OPRD3: 0
D03 | 南濱DS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D03_A1 | [12 empty] | 南濱DS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D03/11/220/CB; OPRD2: 6.9; OPRD3: 0
D03 | 南濱DS | 11 | 11kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D03_A1 | [12 empty] | 南濱DS.230_SC_MVAR | 11KV#3SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D03/11/230/CB; OPRD2: 6.9; OPRD3: 0
D03 | 南濱DS | 11 | 11kV | 240 | #4SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D03_A1 | [12 empty] | 南濱DS.240_SC_MVAR | 11KV#4SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D03/11/240/CB; OPRD2: 6.9; OPRD3: 0
D03 | 南濱DS | 22 | 22kV | 250 | #5SC(250) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D03_A1 | [12 empty] | 南濱DS.250_SC_MVAR | 23KV#5SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D03/22/250/CB; OPRD2: 13.8; OPRD3: 0
D03 | 南濱DS | 22 | 22kV | 260 | #6SC(260) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D03_A1 | [12 empty] | 南濱DS.260_SC_MVAR | 23KV#6SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D03/22/260/CB; OPRD2: 13.8; OPRD3: 0
D03 | 南濱DS | 22 | 22kV | 270 | #7SC(270) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D03_A1 | [12 empty] | 南濱DS.270_SC_MVAR | 23KV#7SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D03/22/270/CB; OPRD2: 13.8; OPRD3: 0
D03 | 南濱DS | 22 | 22kV | 280 | #8SC(280) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D03_A1 | [12 empty] | 南濱DS.280_SC_MVAR | 23KV#8SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D03/22/280/CB; OPRD2: 13.8; OPRD3: 0
D03 | 南濱DS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/D03_A1 | [12 empty] | 南濱DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_18 |  | com_alarm_54 | D03//1DTR/96B1 | D03//1DTR/GDA | D03//1DTR/96B2 | D03//1DTR/63Q | D03//1DTR/96D | D03//1DTR/PHA | D03//1DTR/87A | D03//1DTR/TRA | D03//1DTR/51ZA | D03//1DTR/96PA | D03//2DTR/96B2 | D03//2DTR/GDA | D03//2DTR/TRA | D03//2DTR/96B1 | D03//2DTR/PHA | D03//2DTR/96D | D03//2DTR/63Q | D03//2DTR/87A | D03//2DTR/51ZA | D03//2DTR/96PA | D03//3DTR/96D | D03//3DTR/63Q | D03//3DTR/TRA | D03//3DTR/96B1 | D03//3DTR/96B2 | D03//3DTR/51ZA | D03//3DTR/PHA | D03//3DTR/GDA | D03//3DTR/87A | D03//3DTR/96PA | D03//4DTR/96B1 | D03//4DTR/TRA | D03//4DTR/96B2 | D03//4DTR/87A | D03//4DTR/96D | D03//4DTR/63Q | D03//4DTR/96PA | D03//4DTR/GDA | D03//4DTR/PHA | D03//4DTR/51ZA | D03/11/310/GDA | D03/11/310/PHA | D03/11/320/GDA | D03/11/320/PHA | D03/11/330/GDA | D03/11/330/PHA | D03/11/340/GDA | D03/11/340/PHA | D03/161/1BUS/87A | D03/161/2BUS/87A
D03 | 南濱DS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/D03_A1 | [12 empty] | 南濱DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | STATION_FAULT_4 |  | com_alarm_4 | OPRD1: D03//1DTR/TRF; OPRD2: D03//2DTR(A)/TRF; OPRD3: D03//3DTR/TRF; OPRD4: D03//4DTR/TRF
D03 | 南濱DS | 161 | 161kV | 1750_D1 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D03_D1 | [17 empty] | lamp2CC | OPRD1: D03/161/1750/CB
D03 | 南濱DS | 11 | 11kV | 310_D1 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D03_D1 | [17 empty] | lamp2CC | OPRD1: D03/11/310/CB
D03 | 南濱DS | 11 | 11kV | 320_D1 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D03_D1 | [17 empty] | lamp2CC | OPRD1: D03/11/320/CB
D03 | 南濱DS | 161 | 161kV | 1760_D1 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D03_D1 | [17 empty] | lamp2CC | OPRD1: D03/161/1760/CB
D03 | 南濱DS | 11 | 11kV | 330_D1 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D03_D1 | [17 empty] | lamp2CC | OPRD1: D03/11/330/CB
D03 | 南濱DS | 11 | 11kV | 330_D1 | #2DTR(A)(330) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/D03_D1 | [17 empty] | lamp2CC | OPRD1: D03/11/330/81A
D03 | 南濱DS | 11 | 11kV | 340_D1 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D03_D1 | [17 empty] | lamp2CC | OPRD1: D03/11/340/CB
D03 | 南濱DS | 11 | 11kV | 340_D1 | #2DTR(B)(340) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/D03_D1 | [17 empty] | lamp2CC | OPRD1: D03/11/340/81A
D03 | 南濱DS | 161 | 161kV | 1770_D1 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D03_D1 | [17 empty] | lamp2CC | OPRD1: D03/161/1770/CB
D03 | 南濱DS | 22 | 22kV | 350_D1 | #3DTR(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D03_D1 | [17 empty] | lamp2CC | OPRD1: D03/22/350/CB
D03 | 南濱DS | 161 | 161kV | 1780_D1 | #4DTR(1780) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D03_D1 | [17 empty] | lamp2CC | OPRD1: D03/161/1780/CB
D03 | 南濱DS | 22 | 22kV | 370_D1 | #4DTR(370) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D03_D1 | [17 empty] | lamp2CC | OPRD1: D03/22/370/CB
D03 | 南濱DS | 0 |  | RTU_D1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/D03_D1 | [17 empty] | lamp2CC | OPRD1: D03/0/RTU/RTU_R_L
D03 | 南濱DS | 0 |  | StaDev_D1 | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/D03_D1 | [17 empty] | lamp2CC | OPRD1: D03/0/StaDev/STUV
D03 | 南濱DS | 0 |  | StaDev_D1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D03_D1 | [17 empty] | lamp2CC | OPRD1: D03/0/StaDev/DCA
D03 | 南濱DS | 0 |  | StaDev_D1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D03_D1 | [17 empty] | lamp2CC | OPRD1: D03/0/StaDev/DCE
D03 | 南濱DS | 0 |  | StaDev_D1 | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D03_D1 | [17 empty] | lamp2CC | OPRD1: D03/0/StaDev/PMA

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D03 | 南濱DS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 南濱DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | D03/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
D03 | 南濱DS | 161 | 161kV | 1510 | 安南南濱一路(1510) |  | I | [25 empty] | ADCS_S | [8 empty] | 南濱DS.1510_AMP | 安南南濱一路 AMP | LINE161 | D03/161/1510/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C20R1328 | 1195.199951 | 1195.199951 | 1328.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D03 | 南濱DS | 161 | 161kV | 1520 | 安南南濱二路(1520) |  | I | [25 empty] | ADCS_S | [8 empty] | 南濱DS.1520_AMP | 安南南濱二路 AMP | LINE161 | D03/161/1520/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C20R1930 | 1737.800049 | 1737.800049 | 1930.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱安瀚線(1530) |  | I | [25 empty] | ADCS_S | [8 empty] | 南濱DS.1530_AMP | 南濱安瀚線 AMP | LINE161 | D03/161/1530/I |  | AMP_CAL |  |  | 5 | CalcAIPoint | [21 empty] | C20R0964 | 867.599976 | 867.599976 | 964.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱凸版線(1540) |  | I | [25 empty] | ADCS_S | [8 empty] | 南濱DS.1540_AMP | 南濱凸版線 AMP | LINE161 | D03/161/1540/I |  | AMP_CAL |  |  | 6 | CalcAIPoint | [21 empty] | C20R0964 | 867.599976 | 867.599976 | 964.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱11線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱11線KVA | 11KV濱11線KVA | FEEDER |  |  | KVA_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱11線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱11線KW | 11KV濱11線KW | FEEDER |  |  | KW_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱12線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱12線KVA | 11KV濱12線KVA | FEEDER |  |  | KVA_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱12線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱12線KW | 11KV濱12線KW | FEEDER |  |  | KW_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱13線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱13線KVA | 11KV濱13線KVA | FEEDER |  |  | KVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱13線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱13線KW | 11KV濱13線KW | FEEDER |  |  | KW_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱14線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱14線KVA | 11KV濱14線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱14線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱14線KW | 11KV濱14線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱15線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱15線KVA | 11KV濱15線KVA | FEEDER |  |  | KVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱15線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱15線KW | 11KV濱15線KW | FEEDER |  |  | KW_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱16線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱16線KVA | 11KV濱16線KVA | FEEDER |  |  | KVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱16線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱16線KW | 11KV濱16線KW | FEEDER |  |  | KW_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱17線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱17線KVA | 11KV濱17線KVA | FEEDER |  |  | KVA_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱17線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱17線KW | 11KV濱17線KW | FEEDER |  |  | KW_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱18線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱18線KVA | 11KV濱18線KVA | FEEDER |  |  | KVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱18線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱18線KW | 11KV濱18線KW | FEEDER |  |  | KW_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱19線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱19線KVA | 11KV濱19線KVA | FEEDER |  |  | KVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱19線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱19線KW | 11KV濱19線KW | FEEDER |  |  | KW_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱20線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱20線KVA | 11KV濱20線KVA | FEEDER |  |  | KVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱20線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱20線KW | 11KV濱20線KW | FEEDER |  |  | KW_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱61線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱61線KVA | 23KV濱61線KVA | FEEDER |  |  | KVA_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱61線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱61線KW | 23KV濱61線KW | FEEDER |  |  | KW_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱62線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱62線KVA | 23KV濱62線KVA | FEEDER |  |  | KVA_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱62線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱62線KW | 23KV濱62線KW | FEEDER |  |  | KW_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱63線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱63線KVA | 23KV濱63線KVA | FEEDER |  |  | KVA_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱63線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱63線KW | 23KV濱63線KW | FEEDER |  |  | KW_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱64線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱64線KVA | 23KV濱64線KVA | FEEDER |  |  | KVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱64線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱64線KW | 23KV濱64線KW | FEEDER |  |  | KW_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱65線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱65線KVA | 23KV濱65線KVA | FEEDER |  |  | KVA_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱65線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱65線KW | 23KV濱65線KW | FEEDER |  |  | KW_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱66線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱66線KVA | 23KV濱66線KVA | FEEDER |  |  | KVA_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱66線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱66線KW | 23KV濱66線KW | FEEDER |  |  | KW_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱67線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱67線KVA | 23KV濱67線KVA | FEEDER |  |  | KVA_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱67線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱67線KW | 23KV濱67線KW | FEEDER |  |  | KW_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱68線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱68線KVA | 23KV濱68線KVA | FEEDER |  |  | KVA_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱68線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱68線KW | 23KV濱68線KW | FEEDER |  |  | KW_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱71線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱71線KVA | 23KV濱71線KVA | FEEDER |  |  | KVA_CAL |  |  | 43 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱71線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱71線KW | 23KV濱71線KW | FEEDER |  |  | KW_CAL |  |  | 44 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱72線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱72線KVA | 23KV濱72線KVA | FEEDER |  |  | KVA_CAL |  |  | 45 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱72線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱72線KW | 23KV濱72線KW | FEEDER |  |  | KW_CAL |  |  | 46 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱73線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱73線KVA | 23KV濱73線KVA | FEEDER |  |  | KVA_CAL |  |  | 47 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱73線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱73線KW | 23KV濱73線KW | FEEDER |  |  | KW_CAL |  |  | 48 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱74線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱74線KVA | 23KV濱74線KVA | FEEDER |  |  | KVA_CAL |  |  | 49 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱74線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱74線KW | 23KV濱74線KW | FEEDER |  |  | KW_CAL |  |  | 50 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱75線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱75線KVA | 23KV濱75線KVA | FEEDER |  |  | KVA_CAL |  |  | 51 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱75線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱75線KW | 23KV濱75線KW | FEEDER |  |  | KW_CAL |  |  | 52 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱76線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱76線KVA | 23KV濱76線KVA | FEEDER |  |  | KVA_CAL |  |  | 53 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱76線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱76線KW | 23KV濱76線KW | FEEDER |  |  | KW_CAL |  |  | 54 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱77線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱77線KVA | 23KV濱77線KVA | FEEDER |  |  | KVA_CAL |  |  | 55 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱77線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱77線KW | 23KV濱77線KW | FEEDER |  |  | KW_CAL |  |  | 56 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱78線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱78線KVA | 23KV濱78線KVA | FEEDER |  |  | KVA_CAL |  |  | 57 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱78線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱78線KW | 23KV濱78線KW | FEEDER |  |  | KW_CAL |  |  | 58 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 南濱DS.#1DTR(A)_MVA | #1DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 59 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D03 | 南濱DS | 0 |  | 1DTR(A) | #1DTR(A) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 南濱DS.#1DTR(A)_LOAD | #1DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 60 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D03 | 南濱DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PF | [25 empty] | ADCS_S | [8 empty] | 南濱DS.#1DTR(A)_PF | #1DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 61 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D03 | 南濱DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 南濱DS.#1DTR(B)_MVA | #1DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 62 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D03 | 南濱DS | 0 |  | 1DTR(B) | #1DTR(B) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 南濱DS.#1DTR(B)_LOAD | #1DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 63 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D03 | 南濱DS | 0 |  | 1DTR(B) | #1DTR(B) |  | PF | [25 empty] | ADCS_S | [8 empty] | 南濱DS.#1DTR(B)_PF | #1DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 64 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D03 | 南濱DS | 0 |  | 3DTR | #3DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 南濱DS.#3DTR_MVA | #3DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 65 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D03 | 南濱DS | 0 |  | 3DTR | #3DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 南濱DS.#3DTR_LOAD | #3DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 66 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D03 | 南濱DS | 0 |  | 3DTR | #3DTR |  | PF | [25 empty] | ADCS_S | [8 empty] | 南濱DS.#3DTR_PF | #3DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 67 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D03 | 南濱DS | 0 |  | 4DTR | #4DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 南濱DS.#4DTR_MVA | #4DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 68 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D03 | 南濱DS | 0 |  | 4DTR | #4DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 南濱DS.#4DTR_LOAD | #4DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 69 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D03 | 南濱DS | 0 |  | 4DTR | #4DTR |  | PF | [25 empty] | ADCS_S | [8 empty] | 南濱DS.#4DTR_PF | #4DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 70 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D03 | 南濱DS | 0 |  | 1DTR | #1DTR |  | MW | [25 empty] | ADCS_S | [8 empty] | 南濱DS.#1DTR_MW | #1DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 71 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  | 1DTR | #1DTR |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 南濱DS.#1DTR_MVAR | #1DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 72 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  | 1DTR | #1DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 南濱DS.#1DTR_MVA | #1DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 73 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D03 | 南濱DS | 0 |  | 1DTR | #1DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 南濱DS.#1DTR_LOAD | #1DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 74 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D03 | 南濱DS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 南濱DS.210_SC_MVAR | 11KV#1SC MVAR | SC | D03/11/210/MVAR |  | SC_LBS_11 |  |  | 75 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 11 | 11kV | 220_SC | #2SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 南濱DS.220_SC_MVAR | 11KV#2SC MVAR | SC | D03/11/220/MVAR |  | SC_LBS_11 |  |  | 76 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 22 | 22kV | 250_SC | #5SC | 9 | MVAR | [25 empty] | ADCS_S | [8 empty] | 南濱DS.250_SC_MVAR | 23KV#5SC MVAR | SC | D03/22/250/MVAR |  | SC_CAL_23 |  |  | 77 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 22 | 22kV | 260_SC | #6SC | 9 | MVAR | [25 empty] | ADCS_S | [8 empty] | 南濱DS.260_SC_MVAR | 23KV#6SC MVAR | SC | D03/22/260/MVAR |  | SC_CAL_23 |  |  | 78 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 22 | 22kV | 270_SC | #7SC | 9 | MVAR | [25 empty] | ADCS_S | [8 empty] | 南濱DS.270_SC_MVAR | 23KV#7SC MVAR | SC | D03/22/270/MVAR |  | SC_CAL_23 |  |  | 79 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 22 | 22kV | 280_SC | #8SC | 9 | MVAR | [25 empty] | ADCS_S | [8 empty] | 南濱DS.280_SC_MVAR | 23KV#8SC MVAR | SC | D03/22/280/MVAR |  | SC_CAL_23 |  |  | 80 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  | TRTOT | 南濱主變瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 南濱DS.TRTOT_MW | 南濱主變瞬時供電量 MW |  |  |  | TOTAL_PQ_CAL_4 |  |  | 81 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  | TRTOT | 南濱主變瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 南濱DS.TRTOT_MVAR | 南濱主變瞬時供電量 MVAR |  |  |  | TOTAL_PQ_CAL_4 |  |  | 82 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  | TEN_DAYS11 | (1530+1540 MW) |  | MW | [25 empty] | CDCS | [8 empty] | 南濱DS.TEN_DAYS11_MW | (1530+1540 MW) |  |  |  | MTR_PQ_CAL |  |  | 83 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 161 | 161kV | 1550 | 南濱鹿耳紅線(1550) |  | I | [25 empty] | ADCS_S | [8 empty] | 南濱DS.1550_AMP | 南濱鹿耳紅線 AMP | LINE161 | D03/161/1550/I |  | AMP_CAL |  |  | 84 | CalcAIPoint | [21 empty] | C20R1930 | 1737.800049 | 1737.800049 | 1930.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D03 | 南濱DS | 161 | 161kV | 1560 | 南濱鹿耳白線(1560) |  | I | [25 empty] | ADCS_S | [8 empty] | 南濱DS.1560_AMP | 南濱鹿耳白線 AMP | LINE161 | D03/161/1560/I |  | AMP_CAL |  |  | 85 | CalcAIPoint | [21 empty] | C20R1930 | 1737.800049 | 1737.800049 | 1930.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱21線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱21線KVA | 11KV濱21線KVA | FEEDER |  |  | KVA_CAL |  |  | 86 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱21線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱21線KW | 11KV濱21線KW | FEEDER |  |  | KW_CAL |  |  | 87 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱22線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱22線KVA | 11KV濱22線KVA | FEEDER |  |  | KVA_CAL |  |  | 88 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱22線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱22線KW | 11KV濱22線KW | FEEDER |  |  | KW_CAL |  |  | 89 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱23線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱23線KVA | 11KV濱23線KVA | FEEDER |  |  | KVA_CAL |  |  | 90 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱23線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱23線KW | 11KV濱23線KW | FEEDER |  |  | KW_CAL |  |  | 91 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱24線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱24線KVA | 11KV濱24線KVA | FEEDER |  |  | KVA_CAL |  |  | 92 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱24線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱24線KW | 11KV濱24線KW | FEEDER |  |  | KW_CAL |  |  | 93 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱25線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱25線KVA | 11KV濱25線KVA | FEEDER |  |  | KVA_CAL |  |  | 94 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱25線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱25線KW | 11KV濱25線KW | FEEDER |  |  | KW_CAL |  |  | 95 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱26線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱26線KVA | 11KV濱26線KVA | FEEDER |  |  | KVA_CAL |  |  | 96 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱26線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱26線KW | 11KV濱26線KW | FEEDER |  |  | KW_CAL |  |  | 97 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱27線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱27線KVA | 11KV濱27線KVA | FEEDER |  |  | KVA_CAL |  |  | 98 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱27線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱27線KW | 11KV濱27線KW | FEEDER |  |  | KW_CAL |  |  | 99 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱28線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱28線KVA | 11KV濱28線KVA | FEEDER |  |  | KVA_CAL |  |  | 100 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱28線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱28線KW | 11KV濱28線KW | FEEDER |  |  | KW_CAL |  |  | 101 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱29線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱29線KVA | 11KV濱29線KVA | FEEDER |  |  | KVA_CAL |  |  | 102 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱29線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱29線KW | 11KV濱29線KW | FEEDER |  |  | KW_CAL |  |  | 103 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱30線KVA | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱30線KVA | 11KV濱30線KVA | FEEDER |  |  | KVA_CAL |  |  | 104 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  |  |  |  | 濱30線KW | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.濱30線KW | 11KV濱30線KW | FEEDER |  |  | KW_CAL |  |  | 105 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 南濱DS.#2DTR(A)_MVA | #2DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 106 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D03 | 南濱DS | 0 |  | 2DTR(A) | #2DTR(A) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 南濱DS.#2DTR(A)_LOAD | #2DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 107 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D03 | 南濱DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PF | [25 empty] | ADCS_S | [8 empty] | 南濱DS.#2DTR(A)_PF | #2DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 108 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D03 | 南濱DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 南濱DS.#2DTR(B)_MVA | #2DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 109 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D03 | 南濱DS | 0 |  | 2DTR(B) | #2DTR(B) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 南濱DS.#2DTR(B)_LOAD | #2DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 110 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D03 | 南濱DS | 0 |  | 2DTR(B) | #2DTR(B) |  | PF | [25 empty] | ADCS_S | [8 empty] | 南濱DS.#2DTR(B)_PF | #2DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 111 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D03 | 南濱DS | 0 |  | 2DTR | #2DTR |  | MW | [25 empty] | ADCS_S | [8 empty] | 南濱DS.#2DTR_MW | #2DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 112 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  | 2DTR | #2DTR |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 南濱DS.#2DTR_MVAR | #2DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 113 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  | 2DTR | #2DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 南濱DS.#2DTR_MVA | #2DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 114 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D03 | 南濱DS | 0 |  | 2DTR | #2DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 南濱DS.#2DTR_LOAD | #2DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 115 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D03 | 南濱DS | 11 | 11kV | 230_SC | #3SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 南濱DS.230_SC_MVAR | 11KV#3SC MVAR | SC | D03/11/230/MVAR |  | SC_LBS_11 |  |  | 116 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 11 | 11kV | 240_SC | #4SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 南濱DS.240_SC_MVAR | 11KV#4SC MVAR | SC | D03/11/240/MVAR |  | SC_LBS_11 |  |  | 117 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  | 100_CB | 100(100_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.100_CB_4 | 100 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 118 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 300_CB | 300(300_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.300_CB_4 | 300 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 119 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 1750_CB | #1DTR(1750_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.1750_CB_4 | 1750(#1DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 120 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 310_CB | #1DTR(310_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.310_CB_4 | 310(#1DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 121 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 320_CB | #1DTR(320_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.320_CB_4 | 320(#1DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 122 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 1770_CB | #3DTR(1770_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.1770_CB_4 | 1770(#3DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 123 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 350_CB | #3DTR(350_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.350_CB_4 | 350(#3DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 124 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 1780_CB | #4DTR(1780_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.1780_CB_4 | 1780(#4DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 125 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 370_CB | #4DTR(370_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.370_CB_4 | 370(#4DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 126 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | 210_CB | #1SC(210_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.210_CB_4 | 210(11KV #1SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 127 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | 220_CB | #2SC(220_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.220_CB_4 | 220(11KV #2SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 128 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | 250_CB | #5SC(250_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.250_CB_4 | 250(23KV #5SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 129 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | 260_CB | #6SC(260_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.260_CB_4 | 260(23KV #6SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 130 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | 270_CB | #7SC(270_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.270_CB_4 | 270(23KV #7SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 131 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | 280_CB | #8SC(280_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.280_CB_4 | 280(23KV #8SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 132 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | 11__CBA | 11/斷路器重故障(11__CBA) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.11/23KV_CBA_4 | 11/23KV斷路器重故障 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 133 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | 11__CBF | 11/斷路器輕故障(11__CBF) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.11/23KV_CBF_4 | 11/23KV斷路器輕故障 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 134 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | RTU_S_L | RTU |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.RTU_S/L_4 | RTU SUPY/LOCAL (D4) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 135 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D03 | 南濱DS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_S | [8 empty] | 南濱DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | D03/0/CalcPoint/SUBA |  | STATION_FAULT_18 |  |  | 136 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 變電所輕故障點燈 | 變電所輕故障點燈 |  | SUBF | [25 empty] | ADCS_S | [8 empty] | 南濱DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | D03/0/CalcPoint/SUBF |  | STATION_FAULT_4 |  |  | 137 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.變電所重故障_4 | 變電所重故障點燈 (D4) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 138 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.變電所輕故障_4 | 變電所輕故障點燈 (D4) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 139 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1510_AMP | 安南南濱一路 | [27 empty] | ADCS_S | [8 empty] | 南濱DS.1510_AMP_A | 安南南濱一路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 140 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D03 | 南濱DS | 161 | 161kV | 1520_AMP | 安南南濱二路 | [27 empty] | ADCS_S | [8 empty] | 南濱DS.1520_AMP_A | 安南南濱二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 141 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D03 | 南濱DS | 161 | 161kV | 1530_AMP | 南濱安瀚線 | [27 empty] | ADCS_S | [8 empty] | 南濱DS.1530_AMP_A | 南濱安瀚線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 142 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D03 | 南濱DS | 161 | 161kV | 1540_AMP | 南濱凸版線 | [27 empty] | ADCS_S | [8 empty] | 南濱DS.1540_AMP_A | 南濱凸版線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 143 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D03 | 南濱DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PERM | [25 empty] | ADCS_S | [8 empty] | 南濱DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | D03//1DTR(A)/TR_PERM |  | DTR_PERM |  |  | 144 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D03 | 南濱DS | 0 |  | 1DTR(B) | #1DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 南濱DS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | D03//1DTR(B)/TR_PERM |  | DTR_PERM |  |  | 145 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D03 | 南濱DS | 0 |  | 3DTR | #3DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 南濱DS.#3DTR_PERM | #3DTR TAP PERMISSION POINT | MTR | D03//3DTR/TR_PERM |  | DTR_PERM |  |  | 146 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D03 | 南濱DS | 0 |  | 4DTR | #4DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 南濱DS.#4DTR_PERM | #4DTR TAP PERMISSION POINT | MTR | D03//4DTR/TR_PERM |  | DTR_PERM |  |  | 147 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D03 | 南濱DS | 0 |  | 1DTR_MVA | #1DTR | [27 empty] | ADCS_S | [8 empty] | 南濱DS.#1DTR_MVA_A | #1DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 148 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D03 | 南濱DS | 0 |  | 1DTR_MVA | #1DTR(A) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.#1DTR_MVA_4 | #1DTR(A) MVA 點燈 (D4) | MTR |  |  | MAP_SET |  |  | 149 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D03 | 南濱DS | 0 |  | 1DTR_MVA | #1DTR(B) |  | 5 | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.#1DTR_MVA_5 | #1DTR(B) MVA 點燈 (D4) | MTR |  |  | MAP_SET |  |  | 150 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D03 | 南濱DS | 0 |  | 3DTR_MVA | #3DTR | [27 empty] | ADCS_S | [8 empty] | 南濱DS.#3DTR_MVA_A | #3DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 151 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D03 | 南濱DS | 0 |  | 3DTR_MVA | #3DTR |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.#3DTR_MVA_4 | #3DTR MVA 點燈 (D4) | MTR |  |  | AD_LAMP_DD_2 |  |  | 152 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D03 | 南濱DS | 0 |  | 4DTR_MVA | #4DTR | [27 empty] | ADCS_S | [8 empty] | 南濱DS.#4DTR_MVA_A | #4DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 153 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D03 | 南濱DS | 0 |  | 4DTR_MVA | #4DTR |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.#4DTR_MVA_4 | #4DTR MVA 點燈 (D4) | MTR |  |  | AD_LAMP_DD_2 |  |  | 154 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D03 | 南濱DS | 0 |  | 1760_CB | #2DTR(1760_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.1760_CB_4 | 1760(#2DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 155 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_S | [8 empty] | 南濱DS.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_DS |  |  | 156 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1550_AMP | 南濱鹿耳紅線 | [27 empty] | ADCS_S | [8 empty] | 南濱DS.1550_AMP_A | 南濱鹿耳紅線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 157 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D03 | 南濱DS | 161 | 161kV | 1560_AMP | 南濱鹿耳白線 | [27 empty] | ADCS_S | [8 empty] | 南濱DS.1560_AMP_A | 南濱鹿耳白線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 158 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D03 | 南濱DS | 0 |  | 1ABUS | #1ABUS |  | 11KV#1ABUSC | [25 empty] | CDCS | [8 empty] | 南濱DS.11KV#1ABUSC | #1ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 159 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D03 | 南濱DS | 0 |  | 1BBUS | #1BBUS |  | 11KV#1BBUSC | [25 empty] | CDCS | [8 empty] | 南濱DS.11KV#1BBUSC | #1BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 160 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D03 | 南濱DS | 0 |  | 3BUS | #3BUS |  | 23KV#3BUSC | [25 empty] | CDCS | [8 empty] | 南濱DS.23KV#3BUSC | #3BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 161 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D03 | 南濱DS | 0 |  | 4BUS | #4BUS |  | 23KV#4BUSC | [25 empty] | CDCS | [8 empty] | 南濱DS.23KV#4BUSC | #4BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 162 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D03 | 南濱DS | 0 |  | TAP_OVER | TAP |  | SET | [25 empty] | ADCS_S | [8 empty] | 南濱DS.TAP_OVER_SET | TAP OVER HI/LO ALARM | MTR |  |  | 5000_CB_T6 |  |  | 163 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D03 | 南濱DS | 0 |  | BUS_OVER | BUS |  | SET | [25 empty] | ADCS_S | [8 empty] | 南濱DS.BUS_OVER_SET | BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B6 |  |  | 164 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D03 | 南濱DS | 0 |  | 5000 | 虛擬5000 |  | CB動作 | [25 empty] | ADCS_S | [8 empty] | 南濱DS.5000_CB動作 | 虛擬5000 CB動作,請查明原因處理 | MTR |  |  | 5000_CB_M |  |  | 165 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 200_CB | 200(200_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.200_CB_4 | 200 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 166 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 11 | 11kV | 230_CB | #3SC(230_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.230_CB_4 | 230(11KV #3SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 167 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | 240_CB | #4SC(240_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.240_CB_4 | 240(11KV #4SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 168 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PERM | [25 empty] | ADCS_S | [8 empty] | 南濱DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | D03//2DTR(A)/TR_PERM |  | DTR_PERM |  |  | 169 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D03 | 南濱DS | 0 |  | 2DTR(B) | #2DTR(B) |  | PERM | [25 empty] | ADCS_S | [8 empty] | 南濱DS.#2DTR(B)_PERM | #2DTR(B) TAP PERMISSION POINT | MTR | D03//2DTR(B)/TR_PERM |  | DTR_PERM |  |  | 170 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D03 | 南濱DS | 0 |  | 2DTR_MVA | #2DTR | [27 empty] | ADCS_S | [8 empty] | 南濱DS.#2DTR_MVA_A | #2DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 171 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D03 | 南濱DS | 0 |  | 2DTR_MVA | #2DTR |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 南濱DS.#2DTR_MVA_4 | #2DTR MVA 點燈 (D4) | MTR |  |  | AD_LAMP_DD_2 |  |  | 172 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D03 | 南濱DS | 0 |  | 2ABUS | #2ABUS |  | 11KV#2ABUSC | [25 empty] | CDCS | [8 empty] | 南濱DS.11KV#2ABUSC | #2ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 173 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D03 | 南濱DS | 0 |  | 2BBUS | #2BBUS |  | 11KV#2BBUSC | [25 empty] | CDCS | [8 empty] | 南濱DS.11KV#2BBUSC | #2BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 174 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D03 | 南濱DS | 0 |  | 注意OLTC | 注意OLTC |  | BUS電壓異常 | [25 empty] | ADCS_S | [8 empty] | 南濱DS.BUS電壓異常 | 注意OLTC Tap位置,並將RPDC閉鎖 | OTHER |  |  | STATION_FAULT_2 |  |  | 175 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | D03/0/RTU/ADCH1 |  |  |  | CDC | 176 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | D03/0/RTU/ADCH2 |  |  |  | CDC | 177 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | D03/0/RTU/ADCH3 |  |  |  | CDC | 178 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | AI | AI |  | ADCH4 | [17 empty] | 2-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | D03/0/RTU/ADCH4 |  |  |  | CDC | 179 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | AI | AI |  | ADCH5 | [17 empty] | 3-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.AI_ADCH5 | AI 90%參考點 ADCH5 | OTHER | D03/0/RTU/ADCH5 |  |  |  | CDC | 180 | GENERICAIPoint | DS043_L3 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | D03/0/RTU/ADCL1 |  |  |  | CDC | 181 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | D03/0/RTU/ADCL2 |  |  |  | CDC | 182 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | D03/0/RTU/ADCL3 |  |  |  | CDC | 183 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | AI | AI |  | ADCL4 | [17 empty] | 2-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | D03/0/RTU/ADCL4 |  |  |  | CDC | 184 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | AI | AI |  | ADCL5 | [17 empty] | 3-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.AI_ADCL5 | AI 10%參考點 ADCL5 | OTHER | D03/0/RTU/ADCL5 |  |  |  | CDC | 185 | GENERICAIPoint | DS043_L3 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 161 | 161kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | D03/161/1BUS/V |  |  |  | CDC | 186 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D03 | 南濱DS | 161 | 161kV | 2BUS | #2BUS |  | V | [17 empty] | 1-83 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | D03/161/2BUS/V |  |  |  | CDC | 187 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D03 | 南濱DS | 11 | 11kV | 1ABUS | #1ABUS |  | V | [17 empty] | 1-AE | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.11KV#1ABUS_KV | 11KV #1ABUS KV | BUS | D03/11/1ABUS/V |  |  |  | CDC | 188 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D03 | 南濱DS | 11 | 11kV | 1BBUS | #1BBUS |  | V | [17 empty] | 1-D2 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.11KV#1BBUS_KV | 11KV #1BBUS KV | BUS | D03/11/1BBUS/V |  |  |  | CDC | 189 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D03 | 南濱DS | 22 | 22kV | 3BUS | #3BUS |  | V | [17 empty] | 2-B4 | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.23KV#3BUS_KV | 23KV #3BUS KV | BUS | D03/22/3BUS/V |  |  |  | CDC | 190 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D03 | 南濱DS | 22 | 22kV | 4BUS | #4BUS |  | V | [17 empty] | 2-E4 | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.23KV#4BUS_KV | 23KV #4BUS KV | BUS | D03/22/4BUS/V |  |  |  | CDC | 191 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D03 | 南濱DS | 161 | 161kV | 1510 | 安南南濱一路(1510) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.1510_MW | 安南南濱一路 MW | LINE161 | D03/161/1510/MW |  |  |  | CDC | 192 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D03 | 南濱DS | 161 | 161kV | 1510 | 安南南濱一路(1510) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.1510_MVAR | 安南南濱一路 MVAR | LINE161 | D03/161/1510/MVAR |  |  |  | CDC | 193 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D03 | 南濱DS | 161 | 161kV | 1520 | 安南南濱二路(1520) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.1520_MW | 安南南濱二路 MW | LINE161 | D03/161/1520/MW |  |  |  | CDC | 194 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D03 | 南濱DS | 161 | 161kV | 1520 | 安南南濱二路(1520) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.1520_MVAR | 安南南濱二路 MVAR | LINE161 | D03/161/1520/MVAR |  |  |  | CDC | 195 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱安瀚線(1530) |  | MW | [17 empty] | 1-88 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.1530_MW | 南濱安瀚線 MW | LINE161 | D03/161/1530/MW |  |  |  | CDC | 196 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱安瀚線(1530) |  | MVAR | [17 empty] | 1-89 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.1530_MVAR | 南濱安瀚線 MVAR | LINE161 | D03/161/1530/MVAR |  |  |  | CDC | 197 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱凸版線(1540) |  | MW | [17 empty] | 1-8A | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.1540_MW | 南濱凸版線 MW | LINE161 | D03/161/1540/MW |  |  |  | CDC | 198 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱凸版線(1540) |  | MVAR | [17 empty] | 1-8B | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.1540_MVAR | 南濱凸版線 MVAR | LINE161 | D03/161/1540/MVAR |  |  |  | CDC | 199 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱11線 | 濱11線 |  | 濱11線KVAR | [17 empty] | 1-AF | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱11線KVAR | 11KV濱11線 KVAR | FEEDER | D03/11/K311/KVAR |  |  |  | CDC | 200 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱11線 | 濱11線 |  | 濱11線A1 | [17 empty] | 1-B0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱11線A1 | 11KV濱11線 R相AMP | FEEDER | D03/11/K311/I_R |  |  |  | CDC | 201 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱11線 | 濱11線 |  | 濱11線A2 | [17 empty] | 1-B1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱11線A2 | 11KV濱11線 S相AMP | FEEDER | D03/11/K311/I_S |  |  |  | CDC | 202 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱11線 | 濱11線 |  | 濱11線A3 | [17 empty] | 1-B2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱11線A3 | 11KV濱11線 T相AMP | FEEDER | D03/11/K311/I_T |  |  |  | CDC | 203 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱11線 | 濱11線 |  | 濱11線A0 | [17 empty] | 1-B3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱11線A0 | 11KV濱11線 N相AMP | FEEDER | D03/11/K311/I_N |  |  |  | CDC | 204 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱12線 | 濱12線 |  | 濱12線KVAR | [17 empty] | 1-B4 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱12線KVAR | 11KV濱12線 KVAR | FEEDER | D03/11/K312/KVAR |  |  |  | CDC | 205 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱12線 | 濱12線 |  | 濱12線A1 | [17 empty] | 1-B5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱12線A1 | 11KV濱12線 R相AMP | FEEDER | D03/11/K312/I_R |  |  |  | CDC | 206 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱12線 | 濱12線 |  | 濱12線A2 | [17 empty] | 1-B6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱12線A2 | 11KV濱12線 S相AMP | FEEDER | D03/11/K312/I_S |  |  |  | CDC | 207 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱12線 | 濱12線 |  | 濱12線A3 | [17 empty] | 1-B7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱12線A3 | 11KV濱12線 T相AMP | FEEDER | D03/11/K312/I_T |  |  |  | CDC | 208 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱12線 | 濱12線 |  | 濱12線A0 | [17 empty] | 1-B8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱12線A0 | 11KV濱12線 N相AMP | FEEDER | D03/11/K312/I_N |  |  |  | CDC | 209 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱13線 | 濱13線 |  | 濱13線KVAR | [17 empty] | 1-B9 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱13線KVAR | 11KV濱13線 KVAR | FEEDER | D03/11/K313/KVAR |  |  |  | CDC | 210 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱13線 | 濱13線 |  | 濱13線A1 | [17 empty] | 1-BA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱13線A1 | 11KV濱13線 R相AMP | FEEDER | D03/11/K313/I_R |  |  |  | CDC | 211 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱13線 | 濱13線 |  | 濱13線A2 | [17 empty] | 1-BB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱13線A2 | 11KV濱13線 S相AMP | FEEDER | D03/11/K313/I_S |  |  |  | CDC | 212 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱13線 | 濱13線 |  | 濱13線A3 | [17 empty] | 1-BC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱13線A3 | 11KV濱13線 T相AMP | FEEDER | D03/11/K313/I_T |  |  |  | CDC | 213 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱13線 | 濱13線 |  | 濱13線A0 | [17 empty] | 1-BD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱13線A0 | 11KV濱13線 N相AMP | FEEDER | D03/11/K313/I_N |  |  |  | CDC | 214 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱14線 | 濱14線 |  | 濱14線KVAR | [17 empty] | 1-BE | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱14線KVAR | 11KV濱14線 KVAR | FEEDER | D03/11/K314/KVAR |  |  |  | CDC | 215 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱14線 | 濱14線 |  | 濱14線A1 | [17 empty] | 1-BF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱14線A1 | 11KV濱14線 R相AMP | FEEDER | D03/11/K314/I_R |  |  |  | CDC | 216 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱14線 | 濱14線 |  | 濱14線A2 | [17 empty] | 1-C2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱14線A2 | 11KV濱14線 S相AMP | FEEDER | D03/11/K314/I_S |  |  |  | CDC | 217 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱14線 | 濱14線 |  | 濱14線A3 | [17 empty] | 1-C3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱14線A3 | 11KV濱14線 T相AMP | FEEDER | D03/11/K314/I_T |  |  |  | CDC | 218 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱14線 | 濱14線 |  | 濱14線A0 | [17 empty] | 1-C4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱14線A0 | 11KV濱14線 N相AMP | FEEDER | D03/11/K314/I_N |  |  |  | CDC | 219 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱15線 | 濱15線 |  | 濱15線KVAR | [17 empty] | 1-C5 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱15線KVAR | 11KV濱15線 KVAR | FEEDER | D03/11/K315/KVAR |  |  |  | CDC | 220 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱15線 | 濱15線 |  | 濱15線A1 | [17 empty] | 1-C6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱15線A1 | 11KV濱15線 R相AMP | FEEDER | D03/11/K315/I_R |  |  |  | CDC | 221 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱15線 | 濱15線 |  | 濱15線A2 | [17 empty] | 1-C7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱15線A2 | 11KV濱15線 S相AMP | FEEDER | D03/11/K315/I_S |  |  |  | CDC | 222 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱15線 | 濱15線 |  | 濱15線A3 | [17 empty] | 1-C8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱15線A3 | 11KV濱15線 T相AMP | FEEDER | D03/11/K315/I_T |  |  |  | CDC | 223 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱15線 | 濱15線 |  | 濱15線A0 | [17 empty] | 1-C9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱15線A0 | 11KV濱15線 N相AMP | FEEDER | D03/11/K315/I_N |  |  |  | CDC | 224 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱16線 | 濱16線 |  | 濱16線KVAR | [17 empty] | 1-D3 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱16線KVAR | 11KV濱16線 KVAR | FEEDER | D03/11/K316/KVAR |  |  |  | CDC | 225 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱16線 | 濱16線 |  | 濱16線A1 | [17 empty] | 1-D4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱16線A1 | 11KV濱16線 R相AMP | FEEDER | D03/11/K316/I_R |  |  |  | CDC | 226 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱16線 | 濱16線 |  | 濱16線A2 | [17 empty] | 1-D5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱16線A2 | 11KV濱16線 S相AMP | FEEDER | D03/11/K316/I_S |  |  |  | CDC | 227 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱16線 | 濱16線 |  | 濱16線A3 | [17 empty] | 1-D6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱16線A3 | 11KV濱16線 T相AMP | FEEDER | D03/11/K316/I_T |  |  |  | CDC | 228 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱16線 | 濱16線 |  | 濱16線A0 | [17 empty] | 1-D7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱16線A0 | 11KV濱16線 N相AMP | FEEDER | D03/11/K316/I_N |  |  |  | CDC | 229 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱17線 | 濱17線 |  | 濱17線KVAR | [17 empty] | 1-D8 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱17線KVAR | 11KV濱17線 KVAR | FEEDER | D03/11/K317/KVAR |  |  |  | CDC | 230 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱17線 | 濱17線 |  | 濱17線A1 | [17 empty] | 1-D9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱17線A1 | 11KV濱17線 R相AMP | FEEDER | D03/11/K317/I_R |  |  |  | CDC | 231 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱17線 | 濱17線 |  | 濱17線A2 | [17 empty] | 1-DA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱17線A2 | 11KV濱17線 S相AMP | FEEDER | D03/11/K317/I_S |  |  |  | CDC | 232 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱17線 | 濱17線 |  | 濱17線A3 | [17 empty] | 1-DB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱17線A3 | 11KV濱17線 T相AMP | FEEDER | D03/11/K317/I_T |  |  |  | CDC | 233 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱17線 | 濱17線 |  | 濱17線A0 | [17 empty] | 1-DC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱17線A0 | 11KV濱17線 N相AMP | FEEDER | D03/11/K317/I_N |  |  |  | CDC | 234 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱18線 | 濱18線 |  | 濱18線KVAR | [17 empty] | 1-DD | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱18線KVAR | 11KV濱18線 KVAR | FEEDER | D03/11/K318/KVAR |  |  |  | CDC | 235 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱18線 | 濱18線 |  | 濱18線A1 | [17 empty] | 1-DE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱18線A1 | 11KV濱18線 R相AMP | FEEDER | D03/11/K318/I_R |  |  |  | CDC | 236 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱18線 | 濱18線 |  | 濱18線A2 | [17 empty] | 1-DF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱18線A2 | 11KV濱18線 S相AMP | FEEDER | D03/11/K318/I_S |  |  |  | CDC | 237 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱18線 | 濱18線 |  | 濱18線A3 | [17 empty] | 1-E0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱18線A3 | 11KV濱18線 T相AMP | FEEDER | D03/11/K318/I_T |  |  |  | CDC | 238 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱18線 | 濱18線 |  | 濱18線A0 | [17 empty] | 1-E1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱18線A0 | 11KV濱18線 N相AMP | FEEDER | D03/11/K318/I_N |  |  |  | CDC | 239 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱19線 | 濱19線 |  | 濱19線KVAR | [17 empty] | 1-E2 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱19線KVAR | 11KV濱19線 KVAR | FEEDER | D03/11/K319/KVAR |  |  |  | CDC | 240 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱19線 | 濱19線 |  | 濱19線A1 | [17 empty] | 1-E3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱19線A1 | 11KV濱19線 R相AMP | FEEDER | D03/11/K319/I_R |  |  |  | CDC | 241 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱19線 | 濱19線 |  | 濱19線A2 | [17 empty] | 1-E4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱19線A2 | 11KV濱19線 S相AMP | FEEDER | D03/11/K319/I_S |  |  |  | CDC | 242 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱19線 | 濱19線 |  | 濱19線A3 | [17 empty] | 1-E5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱19線A3 | 11KV濱19線 T相AMP | FEEDER | D03/11/K319/I_T |  |  |  | CDC | 243 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱19線 | 濱19線 |  | 濱19線A0 | [17 empty] | 1-E6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱19線A0 | 11KV濱19線 N相AMP | FEEDER | D03/11/K319/I_N |  |  |  | CDC | 244 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱20線 | 濱20線 |  | 濱20線KVAR | [17 empty] | 1-E7 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱20線KVAR | 11KV濱20線 KVAR | FEEDER | D03/11/K320/KVAR |  |  |  | CDC | 245 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱20線 | 濱20線 |  | 濱20線A1 | [17 empty] | 1-E8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱20線A1 | 11KV濱20線 R相AMP | FEEDER | D03/11/K320/I_R |  |  |  | CDC | 246 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱20線 | 濱20線 |  | 濱20線A2 | [17 empty] | 1-E9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱20線A2 | 11KV濱20線 S相AMP | FEEDER | D03/11/K320/I_S |  |  |  | CDC | 247 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱20線 | 濱20線 |  | 濱20線A3 | [17 empty] | 1-EA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱20線A3 | 11KV濱20線 T相AMP | FEEDER | D03/11/K320/I_T |  |  |  | CDC | 248 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱20線 | 濱20線 |  | 濱20線A0 | [17 empty] | 1-EB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱20線A0 | 11KV濱20線 N相AMP | FEEDER | D03/11/K320/I_N |  |  |  | CDC | 249 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱61線 | 濱61線 |  | 濱61線KVAR | [17 empty] | 2-B5 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱61線KVAR | 23KV濱61線 KVAR | FEEDER | D03/22/K361/KVAR |  |  |  | CDC | 250 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱61線 | 濱61線 |  | 濱61線A1 | [17 empty] | 2-B6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱61線A1 | 23KV濱61線 R相AMP | FEEDER | D03/22/K361/I_R |  |  |  | CDC | 251 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱61線 | 濱61線 |  | 濱61線A2 | [17 empty] | 2-B7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱61線A2 | 23KV濱61線 S相AMP | FEEDER | D03/22/K361/I_S |  |  |  | CDC | 252 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱61線 | 濱61線 |  | 濱61線A3 | [17 empty] | 2-B8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱61線A3 | 23KV濱61線 T相AMP | FEEDER | D03/22/K361/I_T |  |  |  | CDC | 253 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱61線 | 濱61線 |  | 濱61線A0 | [17 empty] | 2-B9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱61線A0 | 23KV濱61線 N相AMP | FEEDER | D03/22/K361/I_N |  |  |  | CDC | 254 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱62線 | 濱62線 |  | 濱62線KVAR | [17 empty] | 2-BA | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱62線KVAR | 23KV濱62線 KVAR | FEEDER | D03/22/K362/KVAR |  |  |  | CDC | 255 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱62線 | 濱62線 |  | 濱62線A1 | [17 empty] | 2-BB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱62線A1 | 23KV濱62線 R相AMP | FEEDER | D03/22/K362/I_R |  |  |  | CDC | 256 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱62線 | 濱62線 |  | 濱62線A2 | [17 empty] | 2-BC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱62線A2 | 23KV濱62線 S相AMP | FEEDER | D03/22/K362/I_S |  |  |  | CDC | 257 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱62線 | 濱62線 |  | 濱62線A3 | [17 empty] | 2-BD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱62線A3 | 23KV濱62線 T相AMP | FEEDER | D03/22/K362/I_T |  |  |  | CDC | 258 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱62線 | 濱62線 |  | 濱62線A0 | [17 empty] | 2-BE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱62線A0 | 23KV濱62線 N相AMP | FEEDER | D03/22/K362/I_N |  |  |  | CDC | 259 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱63線 | 濱63線 |  | 濱63線KVAR | [17 empty] | 2-BF | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱63線KVAR | 23KV濱63線 KVAR | FEEDER | D03/22/K363/KVAR |  |  |  | CDC | 260 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱63線 | 濱63線 |  | 濱63線A1 | [17 empty] | 2-C2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱63線A1 | 23KV濱63線 R相AMP | FEEDER | D03/22/K363/I_R |  |  |  | CDC | 261 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱63線 | 濱63線 |  | 濱63線A2 | [17 empty] | 2-C3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱63線A2 | 23KV濱63線 S相AMP | FEEDER | D03/22/K363/I_S |  |  |  | CDC | 262 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱63線 | 濱63線 |  | 濱63線A3 | [17 empty] | 2-C4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱63線A3 | 23KV濱63線 T相AMP | FEEDER | D03/22/K363/I_T |  |  |  | CDC | 263 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱63線 | 濱63線 |  | 濱63線A0 | [17 empty] | 2-C5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱63線A0 | 23KV濱63線 N相AMP | FEEDER | D03/22/K363/I_N |  |  |  | CDC | 264 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱64線 | 濱64線 |  | 濱64線KVAR | [17 empty] | 2-C6 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱64線KVAR | 23KV濱64線 KVAR | FEEDER | D03/22/K364/KVAR |  |  |  | CDC | 265 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱64線 | 濱64線 |  | 濱64線A1 | [17 empty] | 2-C7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱64線A1 | 23KV濱64線 R相AMP | FEEDER | D03/22/K364/I_R |  |  |  | CDC | 266 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱64線 | 濱64線 |  | 濱64線A2 | [17 empty] | 2-C8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱64線A2 | 23KV濱64線 S相AMP | FEEDER | D03/22/K364/I_S |  |  |  | CDC | 267 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱64線 | 濱64線 |  | 濱64線A3 | [17 empty] | 2-C9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱64線A3 | 23KV濱64線 T相AMP | FEEDER | D03/22/K364/I_T |  |  |  | CDC | 268 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱64線 | 濱64線 |  | 濱64線A0 | [17 empty] | 2-CA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱64線A0 | 23KV濱64線 N相AMP | FEEDER | D03/22/K364/I_N |  |  |  | CDC | 269 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱65線 | 濱65線 |  | 濱65線KVAR | [17 empty] | 2-CB | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱65線KVAR | 23KV濱65線 KVAR | FEEDER | D03/22/K365/KVAR |  |  |  | CDC | 270 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱65線 | 濱65線 |  | 濱65線A1 | [17 empty] | 2-CC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱65線A1 | 23KV濱65線 R相AMP | FEEDER | D03/22/K365/I_R |  |  |  | CDC | 271 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱65線 | 濱65線 |  | 濱65線A2 | [17 empty] | 2-CD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱65線A2 | 23KV濱65線 S相AMP | FEEDER | D03/22/K365/I_S |  |  |  | CDC | 272 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱65線 | 濱65線 |  | 濱65線A3 | [17 empty] | 2-CE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱65線A3 | 23KV濱65線 T相AMP | FEEDER | D03/22/K365/I_T |  |  |  | CDC | 273 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱65線 | 濱65線 |  | 濱65線A0 | [17 empty] | 2-CF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱65線A0 | 23KV濱65線 N相AMP | FEEDER | D03/22/K365/I_N |  |  |  | CDC | 274 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱66線 | 濱66線 |  | 濱66線KVAR | [17 empty] | 2-D0 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱66線KVAR | 23KV濱66線 KVAR | FEEDER | D03/22/K366/KVAR |  |  |  | CDC | 275 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱66線 | 濱66線 |  | 濱66線A1 | [17 empty] | 2-D1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱66線A1 | 23KV濱66線 R相AMP | FEEDER | D03/22/K366/I_R |  |  |  | CDC | 276 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱66線 | 濱66線 |  | 濱66線A2 | [17 empty] | 2-D2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱66線A2 | 23KV濱66線 S相AMP | FEEDER | D03/22/K366/I_S |  |  |  | CDC | 277 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱66線 | 濱66線 |  | 濱66線A3 | [17 empty] | 2-D3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱66線A3 | 23KV濱66線 T相AMP | FEEDER | D03/22/K366/I_T |  |  |  | CDC | 278 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱66線 | 濱66線 |  | 濱66線A0 | [17 empty] | 2-D4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱66線A0 | 23KV濱66線 N相AMP | FEEDER | D03/22/K366/I_N |  |  |  | CDC | 279 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱67線 | 濱67線 |  | 濱67線KVAR | [17 empty] | 2-D5 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱67線KVAR | 23KV濱67線 KVAR | FEEDER | D03/22/K367/KVAR |  |  |  | CDC | 280 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱67線 | 濱67線 |  | 濱67線A1 | [17 empty] | 2-D6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱67線A1 | 23KV濱67線 R相AMP | FEEDER | D03/22/K367/I_R |  |  |  | CDC | 281 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱67線 | 濱67線 |  | 濱67線A2 | [17 empty] | 2-D7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱67線A2 | 23KV濱67線 S相AMP | FEEDER | D03/22/K367/I_S |  |  |  | CDC | 282 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱67線 | 濱67線 |  | 濱67線A3 | [17 empty] | 2-D8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱67線A3 | 23KV濱67線 T相AMP | FEEDER | D03/22/K367/I_T |  |  |  | CDC | 283 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱67線 | 濱67線 |  | 濱67線A0 | [17 empty] | 2-D9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱67線A0 | 23KV濱67線 N相AMP | FEEDER | D03/22/K367/I_N |  |  |  | CDC | 284 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱68線 | 濱68線 |  | 濱68線KVAR | [17 empty] | 2-DA | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱68線KVAR | 23KV濱68線 KVAR | FEEDER | D03/22/K368/KVAR |  |  |  | CDC | 285 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱68線 | 濱68線 |  | 濱68線A1 | [17 empty] | 2-DB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱68線A1 | 23KV濱68線 R相AMP | FEEDER | D03/22/K368/I_R |  |  |  | CDC | 286 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱68線 | 濱68線 |  | 濱68線A2 | [17 empty] | 2-DC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱68線A2 | 23KV濱68線 S相AMP | FEEDER | D03/22/K368/I_S |  |  |  | CDC | 287 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱68線 | 濱68線 |  | 濱68線A3 | [17 empty] | 2-DD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱68線A3 | 23KV濱68線 T相AMP | FEEDER | D03/22/K368/I_T |  |  |  | CDC | 288 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱68線 | 濱68線 |  | 濱68線A0 | [17 empty] | 2-DE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱68線A0 | 23KV濱68線 N相AMP | FEEDER | D03/22/K368/I_N |  |  |  | CDC | 289 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱71線 | 濱71線 |  | 濱71線KVAR | [17 empty] | 2-E5 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱71線KVAR | 23KV濱71線 KVAR | FEEDER | D03/22/K371/KVAR |  |  |  | CDC | 290 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱71線 | 濱71線 |  | 濱71線A1 | [17 empty] | 2-E6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱71線A1 | 23KV濱71線 R相AMP | FEEDER | D03/22/K371/I_R |  |  |  | CDC | 291 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱71線 | 濱71線 |  | 濱71線A2 | [17 empty] | 2-E7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱71線A2 | 23KV濱71線 S相AMP | FEEDER | D03/22/K371/I_S |  |  |  | CDC | 292 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱71線 | 濱71線 |  | 濱71線A3 | [17 empty] | 2-E8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱71線A3 | 23KV濱71線 T相AMP | FEEDER | D03/22/K371/I_T |  |  |  | CDC | 293 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱71線 | 濱71線 |  | 濱71線A0 | [17 empty] | 2-E9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱71線A0 | 23KV濱71線 N相AMP | FEEDER | D03/22/K371/I_N |  |  |  | CDC | 294 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱72線 | 濱72線 |  | 濱72線KVAR | [17 empty] | 2-EA | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱72線KVAR | 23KV濱72線 KVAR | FEEDER | D03/22/K372/KVAR |  |  |  | CDC | 295 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱72線 | 濱72線 |  | 濱72線A1 | [17 empty] | 2-EB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱72線A1 | 23KV濱72線 R相AMP | FEEDER | D03/22/K372/I_R |  |  |  | CDC | 296 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱72線 | 濱72線 |  | 濱72線A2 | [17 empty] | 2-EC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱72線A2 | 23KV濱72線 S相AMP | FEEDER | D03/22/K372/I_S |  |  |  | CDC | 297 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱72線 | 濱72線 |  | 濱72線A3 | [17 empty] | 2-ED | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱72線A3 | 23KV濱72線 T相AMP | FEEDER | D03/22/K372/I_T |  |  |  | CDC | 298 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱72線 | 濱72線 |  | 濱72線A0 | [17 empty] | 2-EE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱72線A0 | 23KV濱72線 N相AMP | FEEDER | D03/22/K372/I_N |  |  |  | CDC | 299 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱73線 | 濱73線 |  | 濱73線KVAR | [17 empty] | 2-EF | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱73線KVAR | 23KV濱73線 KVAR | FEEDER | D03/22/K373/KVAR |  |  |  | CDC | 300 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱73線 | 濱73線 |  | 濱73線A1 | [17 empty] | 2-F0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱73線A1 | 23KV濱73線 R相AMP | FEEDER | D03/22/K373/I_R |  |  |  | CDC | 301 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱73線 | 濱73線 |  | 濱73線A2 | [17 empty] | 2-F1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱73線A2 | 23KV濱73線 S相AMP | FEEDER | D03/22/K373/I_S |  |  |  | CDC | 302 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱73線 | 濱73線 |  | 濱73線A3 | [17 empty] | 2-F2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱73線A3 | 23KV濱73線 T相AMP | FEEDER | D03/22/K373/I_T |  |  |  | CDC | 303 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱73線 | 濱73線 |  | 濱73線A0 | [17 empty] | 2-F3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱73線A0 | 23KV濱73線 N相AMP | FEEDER | D03/22/K373/I_N |  |  |  | CDC | 304 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱74線 | 濱74線 |  | 濱74線KVAR | [17 empty] | 2-F4 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱74線KVAR | 23KV濱74線 KVAR | FEEDER | D03/22/K374/KVAR |  |  |  | CDC | 305 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱74線 | 濱74線 |  | 濱74線A1 | [17 empty] | 2-F5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱74線A1 | 23KV濱74線 R相AMP | FEEDER | D03/22/K374/I_R |  |  |  | CDC | 306 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱74線 | 濱74線 |  | 濱74線A2 | [17 empty] | 2-F6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱74線A2 | 23KV濱74線 S相AMP | FEEDER | D03/22/K374/I_S |  |  |  | CDC | 307 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱74線 | 濱74線 |  | 濱74線A3 | [17 empty] | 2-F7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱74線A3 | 23KV濱74線 T相AMP | FEEDER | D03/22/K374/I_T |  |  |  | CDC | 308 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱74線 | 濱74線 |  | 濱74線A0 | [17 empty] | 2-F8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱74線A0 | 23KV濱74線 N相AMP | FEEDER | D03/22/K374/I_N |  |  |  | CDC | 309 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱75線 | 濱75線 |  | 濱75線KVAR | [17 empty] | 2-F9 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱75線KVAR | 23KV濱75線 KVAR | FEEDER | D03/22/K375/KVAR |  |  |  | CDC | 310 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱75線 | 濱75線 |  | 濱75線A1 | [17 empty] | 2-FA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱75線A1 | 23KV濱75線 R相AMP | FEEDER | D03/22/K375/I_R |  |  |  | CDC | 311 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱75線 | 濱75線 |  | 濱75線A2 | [17 empty] | 2-FB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱75線A2 | 23KV濱75線 S相AMP | FEEDER | D03/22/K375/I_S |  |  |  | CDC | 312 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱75線 | 濱75線 |  | 濱75線A3 | [17 empty] | 2-FC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱75線A3 | 23KV濱75線 T相AMP | FEEDER | D03/22/K375/I_T |  |  |  | CDC | 313 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱75線 | 濱75線 |  | 濱75線A0 | [17 empty] | 2-FD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱75線A0 | 23KV濱75線 N相AMP | FEEDER | D03/22/K375/I_N |  |  |  | CDC | 314 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱76線 | 濱76線 |  | 濱76線KVAR | [17 empty] | 2-FE | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱76線KVAR | 23KV濱76線 KVAR | FEEDER | D03/22/K376/KVAR |  |  |  | CDC | 315 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱76線 | 濱76線 |  | 濱76線A1 | [17 empty] | 2-FF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱76線A1 | 23KV濱76線 R相AMP | FEEDER | D03/22/K376/I_R |  |  |  | CDC | 316 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱76線 | 濱76線 |  | 濱76線A2 | [17 empty] | 3-82 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱76線A2 | 23KV濱76線 S相AMP | FEEDER | D03/22/K376/I_S |  |  |  | CDC | 317 | GENERICAIPoint | DS043_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱76線 | 濱76線 |  | 濱76線A3 | [17 empty] | 3-83 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱76線A3 | 23KV濱76線 T相AMP | FEEDER | D03/22/K376/I_T |  |  |  | CDC | 318 | GENERICAIPoint | DS043_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱76線 | 濱76線 |  | 濱76線A0 | [17 empty] | 3-84 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱76線A0 | 23KV濱76線 N相AMP | FEEDER | D03/22/K376/I_N |  |  |  | CDC | 319 | GENERICAIPoint | DS043_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱77線 | 濱77線 |  | 濱77線KVAR | [17 empty] | 3-85 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱77線KVAR | 23KV濱77線 KVAR | FEEDER | D03/22/K377/KVAR |  |  |  | CDC | 320 | GENERICAIPoint | DS043_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱77線 | 濱77線 |  | 濱77線A1 | [17 empty] | 3-86 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱77線A1 | 23KV濱77線 R相AMP | FEEDER | D03/22/K377/I_R |  |  |  | CDC | 321 | GENERICAIPoint | DS043_L3 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱77線 | 濱77線 |  | 濱77線A2 | [17 empty] | 3-87 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱77線A2 | 23KV濱77線 S相AMP | FEEDER | D03/22/K377/I_S |  |  |  | CDC | 322 | GENERICAIPoint | DS043_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱77線 | 濱77線 |  | 濱77線A3 | [17 empty] | 3-88 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱77線A3 | 23KV濱77線 T相AMP | FEEDER | D03/22/K377/I_T |  |  |  | CDC | 323 | GENERICAIPoint | DS043_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱77線 | 濱77線 |  | 濱77線A0 | [17 empty] | 3-89 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱77線A0 | 23KV濱77線 N相AMP | FEEDER | D03/22/K377/I_N |  |  |  | CDC | 324 | GENERICAIPoint | DS043_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱78線 | 濱78線 |  | 濱78線KVAR | [17 empty] | 3-8A | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱78線KVAR | 23KV濱78線 KVAR | FEEDER | D03/22/K378/KVAR |  |  |  | CDC | 325 | GENERICAIPoint | DS043_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱78線 | 濱78線 |  | 濱78線A1 | [17 empty] | 3-8B | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱78線A1 | 23KV濱78線 R相AMP | FEEDER | D03/22/K378/I_R |  |  |  | CDC | 326 | GENERICAIPoint | DS043_L3 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱78線 | 濱78線 |  | 濱78線A2 | [17 empty] | 3-8C | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱78線A2 | 23KV濱78線 S相AMP | FEEDER | D03/22/K378/I_S |  |  |  | CDC | 327 | GENERICAIPoint | DS043_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱78線 | 濱78線 |  | 濱78線A3 | [17 empty] | 3-8D | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱78線A3 | 23KV濱78線 T相AMP | FEEDER | D03/22/K378/I_T |  |  |  | CDC | 328 | GENERICAIPoint | DS043_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | 濱78線 | 濱78線 |  | 濱78線A0 | [17 empty] | 3-8E | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱78線A0 | 23KV濱78線 N相AMP | FEEDER | D03/22/K378/I_N |  |  |  | CDC | 329 | GENERICAIPoint | DS043_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | 1500TIE | 1500TIE |  | I | [17 empty] | 1-98 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.1500TIE_AMP | 1500TIE AMP | TIE | D03/161/1500/I_R |  |  |  | CDC | 330 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | _100 | 100 |  | I_R | [17 empty] | 1-CA | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.11KV_100_A1 | 11KV 100 R相AMP | TIE | D03/11/100/I_R |  |  |  | CDC | 331 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | _100 | 100 |  | I_S | [17 empty] | 1-CB | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.11KV_100_A2 | 11KV 100 S相AMP | TIE | D03/11/100/I_S |  |  |  | CDC | 332 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | _100 | 100 |  | I_T | [17 empty] | 1-CC | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.11KV_100_A3 | 11KV 100 T相AMP | TIE | D03/11/100/I_T |  |  |  | CDC | 333 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | _200 | 200 |  | I_R | [17 empty] | 2-AC | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.11KV_200_A1 | 11KV 200 R相AMP | TIE | D03/11/200/I_R |  |  |  | CDC | 334 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | _200 | 200 |  | I_S | [17 empty] | 2-AD | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.11KV_200_A2 | 11KV 200 S相AMP | TIE | D03/11/200/I_S |  |  |  | CDC | 335 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | _200 | 200 |  | I_T | [17 empty] | 2-AE | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.11KV_200_A3 | 11KV 200 T相AMP | TIE | D03/11/200/I_T |  |  |  | CDC | 336 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | _300 | 300 |  | I_R | [17 empty] | 3-8F | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.23KV_300_A1 | 23KV 300 R相AMP | TIE | D03/22/300/I_R |  |  |  | CDC | 337 | GENERICAIPoint | DS043_L3 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | _300 | 300 |  | I_S | [17 empty] | 3-90 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.23KV_300_A2 | 23KV 300 S相AMP | TIE | D03/22/300/I_S |  |  |  | CDC | 338 | GENERICAIPoint | DS043_L3 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 22 | 22kV | _300 | 300 |  | I_T | [17 empty] | 3-91 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.23KV_300_A3 | 23KV 300 T相AMP | TIE | D03/22/300/I_T |  |  |  | CDC | 339 | GENERICAIPoint | DS043_L3 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MW | [17 empty] | 1-A9 | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | D03/11/310/KW |  |  |  | CDC | 340 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D03 | 南濱DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVAR | [17 empty] | 1-AA | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | D03/11/310/KVAR |  |  |  | CDC | 341 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D03 | 南濱DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_R | [17 empty] | 1-AB | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | D03/11/310/I_R |  |  |  | CDC | 342 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_S | [17 empty] | 1-AC | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | D03/11/310/I_S |  |  |  | CDC | 343 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_T | [17 empty] | 1-AD | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | D03/11/310/I_T |  |  |  | CDC | 344 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | 1DTR | #1DTR |  | OilTemp | [17 empty] | 1-99 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#1DTR_OIL | #1DTR 油溫 | MTR | D03//1DTR/OilTemp |  |  |  | CDC | 345 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D03 | 南濱DS | 0 |  | 1DTR(A) | #1DTR(A) |  | CoilTemp | [17 empty] | 1-9A | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | D03//1DTR(A)/CoilTemp |  |  |  | CDC | 346 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D03 | 南濱DS | 0 |  | 1DTR(A) | #1DTR(A) |  | TapPosMv | [17 empty] | 1-9C |  | 1-39 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 南濱DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | D03//1DTR(A)/TapPosMv |  |  |  | CDC | 347 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D03 | 南濱DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MW | [17 empty] | 1-CD | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | D03/11/320/KW |  |  |  | CDC | 348 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D03 | 南濱DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVAR | [17 empty] | 1-CE | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | D03/11/320/KVAR |  |  |  | CDC | 349 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D03 | 南濱DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_R | [17 empty] | 1-CF | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | D03/11/320/I_R |  |  |  | CDC | 350 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_S | [17 empty] | 1-D0 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | D03/11/320/I_S |  |  |  | CDC | 351 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_T | [17 empty] | 1-D1 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | D03/11/320/I_T |  |  |  | CDC | 352 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | 1DTR(B) | #1DTR(B) |  | CoilTemp | [17 empty] | 1-9B | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | D03//1DTR(B)/CoilTemp |  |  |  | CDC | 353 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D03 | 南濱DS | 0 |  | 1DTR(B) | #1DTR(B) |  | TapPosMv | [17 empty] | 1-9D |  | 1-3B |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 南濱DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | D03//1DTR(B)/TapPosMv |  |  |  | CDC | 354 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D03 | 南濱DS | 0 |  | 3DTR | #3DTR二次側 |  | MW | [17 empty] | 2-AF | [5 empty] | MW_-108_108(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#3DTR_MW | #3DTR二次側 MW | MTR | D03/22/350/KW |  |  |  | CDC | 355 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D03 | 南濱DS | 0 |  | 3DTR | #3DTR二次側 |  | MVAR | [17 empty] | 2-B0 | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#3DTR_MVAR | #3DTR二次側 MVAR | MTR | D03/22/350/KVAR |  |  |  | CDC | 356 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D03 | 南濱DS | 0 |  | 3DTR | #3DTR二次側 |  | I_R | [17 empty] | 2-B1 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#3DTR_A1 | #3DTR二次側 R相AMP | MTR | D03/22/350/I_R |  |  |  | CDC | 357 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | 3DTR | #3DTR二次側 |  | I_S | [17 empty] | 2-B2 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#3DTR_A2 | #3DTR二次側 S相AMP | MTR | D03/22/350/I_S |  |  |  | CDC | 358 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | 3DTR | #3DTR二次側 |  | I_T | [17 empty] | 2-B3 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#3DTR_A3 | #3DTR二次側 T相AMP | MTR | D03/22/350/I_T |  |  |  | CDC | 359 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | 3DTR | #3DTR |  | OilTemp | [17 empty] | 1-A3 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#3DTR_OIL | #3DTR 油溫 | MTR | D03//3DTR/OilTemp |  |  |  | CDC | 360 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D03 | 南濱DS | 0 |  | 3DTR | #3DTR |  | CoilTemp | [17 empty] | 1-A4 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#3DTR_COIL | #3DTR 線溫 | MTR | D03//3DTR/CoilTemp |  |  |  | CDC | 361 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D03 | 南濱DS | 0 |  | 3DTR | #3DTR |  | TapPosMv | [17 empty] | 1-A5 |  | 1-41 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 南濱DS.#3DTR_TAP | #3DTR OLTC TAP | MTR | D03//3DTR/TapPosMv |  |  |  | CDC | 362 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D03 | 南濱DS | 0 |  | 4DTR | #4DTR二次側 |  | MW | [17 empty] | 2-DF | [5 empty] | MW_-108_108(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#4DTR_MW | #4DTR二次側 MW | MTR | D03/22/370/KW |  |  |  | CDC | 363 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D03 | 南濱DS | 0 |  | 4DTR | #4DTR二次側 |  | MVAR | [17 empty] | 2-E0 | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#4DTR_MVAR | #4DTR二次側 MVAR | MTR | D03/22/370/KVAR |  |  |  | CDC | 364 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D03 | 南濱DS | 0 |  | 4DTR | #4DTR二次側 |  | I_R | [17 empty] | 2-E1 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#4DTR_A1 | #4DTR二次側 R相AMP | MTR | D03/22/370/I_R |  |  |  | CDC | 365 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | 4DTR | #4DTR二次側 |  | I_S | [17 empty] | 2-E2 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#4DTR_A2 | #4DTR二次側 S相AMP | MTR | D03/22/370/I_S |  |  |  | CDC | 366 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | 4DTR | #4DTR二次側 |  | I_T | [17 empty] | 2-E3 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#4DTR_A3 | #4DTR二次側 T相AMP | MTR | D03/22/370/I_T |  |  |  | CDC | 367 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | 4DTR | #4DTR |  | OilTemp | [17 empty] | 1-A6 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#4DTR_OIL | #4DTR 油溫 | MTR | D03//4DTR/OilTemp |  |  |  | CDC | 368 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D03 | 南濱DS | 0 |  | 4DTR | #4DTR |  | CoilTemp | [17 empty] | 1-A7 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#4DTR_COIL | #4DTR 線溫 | MTR | D03//4DTR/CoilTemp |  |  |  | CDC | 369 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D03 | 南濱DS | 0 |  | 4DTR | #4DTR |  | TapPosMv | [17 empty] | 1-A8 |  | 1-43 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 南濱DS.#4DTR_TAP | #4DTR OLTC TAP | MTR | D03//4DTR/TapPosMv |  |  |  | CDC | 370 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D03 | 南濱DS | 0 |  |  |  |  | DCV_N | [17 empty] | 1-97 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.直流N電源電壓 | 直流N電源電壓 | OTHER | D03/0/StaDev/DCV_N |  |  |  | CDC | 371 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D03 | 南濱DS | 0 |  |  |  |  | DCV_P | [17 empty] | 1-96 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.直流P電源電壓 | 直流P電源電壓 | OTHER | D03/0/StaDev/DCV_P |  |  |  | CDC | 372 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D03 | 南濱DS | 161 | 161kV | 1550 | 南濱鹿耳紅線(1550) |  | MW | [17 empty] | 1-8C | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.1550_MW | 南濱鹿耳紅線 MW | LINE161 | D03/161/1550/MW |  |  |  | CDC | 373 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D03 | 南濱DS | 161 | 161kV | 1550 | 南濱鹿耳紅線(1550) |  | MVAR | [17 empty] | 1-8D | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.1550_MVAR | 南濱鹿耳紅線 MVAR | LINE161 | D03/161/1550/MVAR |  |  |  | CDC | 374 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D03 | 南濱DS | 161 | 161kV | 1560 | 南濱鹿耳白線(1560) |  | MW | [17 empty] | 1-8E | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.1560_MW | 南濱鹿耳白線 MW | LINE161 | D03/161/1560/MW |  |  |  | CDC | 375 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D03 | 南濱DS | 161 | 161kV | 1560 | 南濱鹿耳白線(1560) |  | MVAR | [17 empty] | 1-8F | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.1560_MVAR | 南濱鹿耳白線 MVAR | LINE161 | D03/161/1560/MVAR |  |  |  | CDC | 376 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 2ABUS | #2ABUS |  | V | [17 empty] | 1-F1 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS | D03/11/2ABUS/V |  |  |  | CDC | 377 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D03 | 南濱DS | 11 | 11kV | 2BBUS | #2BBUS |  | V | [17 empty] | 2-92 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.11KV#2BBUS_KV | 11KV #2BBUS KV | BUS | D03/11/2BBUS/V |  |  |  | CDC | 378 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D03 | 南濱DS | 11 | 11kV | 濱21線 | 濱21線 |  | 濱21線KVAR | [17 empty] | 1-F2 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱21線KVAR | 11KV濱21線 KVAR | FEEDER | D03/11/K321/KVAR |  |  |  | CDC | 379 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱21線 | 濱21線 |  | 濱21線A1 | [17 empty] | 1-F3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱21線A1 | 11KV濱21線 R相AMP | FEEDER | D03/11/K321/I_R |  |  |  | CDC | 380 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱21線 | 濱21線 |  | 濱21線A2 | [17 empty] | 1-F4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱21線A2 | 11KV濱21線 S相AMP | FEEDER | D03/11/K321/I_S |  |  |  | CDC | 381 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱21線 | 濱21線 |  | 濱21線A3 | [17 empty] | 1-F5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱21線A3 | 11KV濱21線 T相AMP | FEEDER | D03/11/K321/I_T |  |  |  | CDC | 382 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱21線 | 濱21線 |  | 濱21線A0 | [17 empty] | 1-F6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱21線A0 | 11KV濱21線 N相AMP | FEEDER | D03/11/K321/I_N |  |  |  | CDC | 383 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱22線 | 濱22線 |  | 濱22線KVAR | [17 empty] | 1-F7 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱22線KVAR | 11KV濱22線 KVAR | FEEDER | D03/11/K322/KVAR |  |  |  | CDC | 384 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱22線 | 濱22線 |  | 濱22線A1 | [17 empty] | 1-F8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱22線A1 | 11KV濱22線 R相AMP | FEEDER | D03/11/K322/I_R |  |  |  | CDC | 385 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱22線 | 濱22線 |  | 濱22線A2 | [17 empty] | 1-F9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱22線A2 | 11KV濱22線 S相AMP | FEEDER | D03/11/K322/I_S |  |  |  | CDC | 386 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱22線 | 濱22線 |  | 濱22線A3 | [17 empty] | 1-FA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱22線A3 | 11KV濱22線 T相AMP | FEEDER | D03/11/K322/I_T |  |  |  | CDC | 387 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱22線 | 濱22線 |  | 濱22線A0 | [17 empty] | 1-FB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱22線A0 | 11KV濱22線 N相AMP | FEEDER | D03/11/K322/I_N |  |  |  | CDC | 388 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱23線 | 濱23線 |  | 濱23線KVAR | [17 empty] | 1-FC | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱23線KVAR | 11KV濱23線 KVAR | FEEDER | D03/11/K323/KVAR |  |  |  | CDC | 389 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱23線 | 濱23線 |  | 濱23線A1 | [17 empty] | 1-FD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱23線A1 | 11KV濱23線 R相AMP | FEEDER | D03/11/K323/I_R |  |  |  | CDC | 390 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱23線 | 濱23線 |  | 濱23線A2 | [17 empty] | 1-FE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱23線A2 | 11KV濱23線 S相AMP | FEEDER | D03/11/K323/I_S |  |  |  | CDC | 391 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱23線 | 濱23線 |  | 濱23線A3 | [17 empty] | 1-FF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱23線A3 | 11KV濱23線 T相AMP | FEEDER | D03/11/K323/I_T |  |  |  | CDC | 392 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱23線 | 濱23線 |  | 濱23線A0 | [17 empty] | 2-82 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱23線A0 | 11KV濱23線 N相AMP | FEEDER | D03/11/K323/I_N |  |  |  | CDC | 393 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱24線 | 濱24線 |  | 濱24線KVAR | [17 empty] | 2-83 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱24線KVAR | 11KV濱24線 KVAR | FEEDER | D03/11/K324/KVAR |  |  |  | CDC | 394 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱24線 | 濱24線 |  | 濱24線A1 | [17 empty] | 2-84 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱24線A1 | 11KV濱24線 R相AMP | FEEDER | D03/11/K324/I_R |  |  |  | CDC | 395 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱24線 | 濱24線 |  | 濱24線A2 | [17 empty] | 2-85 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱24線A2 | 11KV濱24線 S相AMP | FEEDER | D03/11/K324/I_S |  |  |  | CDC | 396 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱24線 | 濱24線 |  | 濱24線A3 | [17 empty] | 2-86 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱24線A3 | 11KV濱24線 T相AMP | FEEDER | D03/11/K324/I_T |  |  |  | CDC | 397 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱24線 | 濱24線 |  | 濱24線A0 | [17 empty] | 2-87 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱24線A0 | 11KV濱24線 N相AMP | FEEDER | D03/11/K324/I_N |  |  |  | CDC | 398 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱25線 | 濱25線 |  | 濱25線KVAR | [17 empty] | 2-88 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱25線KVAR | 11KV濱25線 KVAR | FEEDER | D03/11/K325/KVAR |  |  |  | CDC | 399 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱25線 | 濱25線 |  | 濱25線A1 | [17 empty] | 2-89 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱25線A1 | 11KV濱25線 R相AMP | FEEDER | D03/11/K325/I_R |  |  |  | CDC | 400 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱25線 | 濱25線 |  | 濱25線A2 | [17 empty] | 2-8A | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱25線A2 | 11KV濱25線 S相AMP | FEEDER | D03/11/K325/I_S |  |  |  | CDC | 401 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱25線 | 濱25線 |  | 濱25線A3 | [17 empty] | 2-8B | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱25線A3 | 11KV濱25線 T相AMP | FEEDER | D03/11/K325/I_T |  |  |  | CDC | 402 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱25線 | 濱25線 |  | 濱25線A0 | [17 empty] | 2-8C | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱25線A0 | 11KV濱25線 N相AMP | FEEDER | D03/11/K325/I_N |  |  |  | CDC | 403 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱26線 | 濱26線 |  | 濱26線KVAR | [17 empty] | 2-93 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱26線KVAR | 11KV濱26線 KVAR | FEEDER | D03/11/K326/KVAR |  |  |  | CDC | 404 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱26線 | 濱26線 |  | 濱26線A1 | [17 empty] | 2-94 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱26線A1 | 11KV濱26線 R相AMP | FEEDER | D03/11/K326/I_R |  |  |  | CDC | 405 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱26線 | 濱26線 |  | 濱26線A2 | [17 empty] | 2-95 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱26線A2 | 11KV濱26線 S相AMP | FEEDER | D03/11/K326/I_S |  |  |  | CDC | 406 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱26線 | 濱26線 |  | 濱26線A3 | [17 empty] | 2-96 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱26線A3 | 11KV濱26線 T相AMP | FEEDER | D03/11/K326/I_T |  |  |  | CDC | 407 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱26線 | 濱26線 |  | 濱26線A0 | [17 empty] | 2-97 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱26線A0 | 11KV濱26線 N相AMP | FEEDER | D03/11/K326/I_N |  |  |  | CDC | 408 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱27線 | 濱27線 |  | 濱27線KVAR | [17 empty] | 2-98 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱27線KVAR | 11KV濱27線 KVAR | FEEDER | D03/11/K327/KVAR |  |  |  | CDC | 409 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱27線 | 濱27線 |  | 濱27線A1 | [17 empty] | 2-99 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱27線A1 | 11KV濱27線 R相AMP | FEEDER | D03/11/K327/I_R |  |  |  | CDC | 410 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱27線 | 濱27線 |  | 濱27線A2 | [17 empty] | 2-9A | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱27線A2 | 11KV濱27線 S相AMP | FEEDER | D03/11/K327/I_S |  |  |  | CDC | 411 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱27線 | 濱27線 |  | 濱27線A3 | [17 empty] | 2-9B | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱27線A3 | 11KV濱27線 T相AMP | FEEDER | D03/11/K327/I_T |  |  |  | CDC | 412 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱27線 | 濱27線 |  | 濱27線A0 | [17 empty] | 2-9C | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱27線A0 | 11KV濱27線 N相AMP | FEEDER | D03/11/K327/I_N |  |  |  | CDC | 413 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱28線 | 濱28線 |  | 濱28線KVAR | [17 empty] | 2-9D | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱28線KVAR | 11KV濱28線 KVAR | FEEDER | D03/11/K328/KVAR |  |  |  | CDC | 414 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱28線 | 濱28線 |  | 濱28線A1 | [17 empty] | 2-9E | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱28線A1 | 11KV濱28線 R相AMP | FEEDER | D03/11/K328/I_R |  |  |  | CDC | 415 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱28線 | 濱28線 |  | 濱28線A2 | [17 empty] | 2-9F | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱28線A2 | 11KV濱28線 S相AMP | FEEDER | D03/11/K328/I_S |  |  |  | CDC | 416 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱28線 | 濱28線 |  | 濱28線A3 | [17 empty] | 2-A0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱28線A3 | 11KV濱28線 T相AMP | FEEDER | D03/11/K328/I_T |  |  |  | CDC | 417 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱28線 | 濱28線 |  | 濱28線A0 | [17 empty] | 2-A1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱28線A0 | 11KV濱28線 N相AMP | FEEDER | D03/11/K328/I_N |  |  |  | CDC | 418 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱29線 | 濱29線 |  | 濱29線KVAR | [17 empty] | 2-A2 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱29線KVAR | 11KV濱29線 KVAR | FEEDER | D03/11/K329/KVAR |  |  |  | CDC | 419 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱29線 | 濱29線 |  | 濱29線A1 | [17 empty] | 2-A3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱29線A1 | 11KV濱29線 R相AMP | FEEDER | D03/11/K329/I_R |  |  |  | CDC | 420 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱29線 | 濱29線 |  | 濱29線A2 | [17 empty] | 2-A4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱29線A2 | 11KV濱29線 S相AMP | FEEDER | D03/11/K329/I_S |  |  |  | CDC | 421 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱29線 | 濱29線 |  | 濱29線A3 | [17 empty] | 2-A5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱29線A3 | 11KV濱29線 T相AMP | FEEDER | D03/11/K329/I_T |  |  |  | CDC | 422 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱29線 | 濱29線 |  | 濱29線A0 | [17 empty] | 2-A6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱29線A0 | 11KV濱29線 N相AMP | FEEDER | D03/11/K329/I_N |  |  |  | CDC | 423 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱30線 | 濱30線 |  | 濱30線KVAR | [17 empty] | 2-A7 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱30線KVAR | 11KV濱30線 KVAR | FEEDER | D03/11/K330/KVAR |  |  |  | CDC | 424 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱30線 | 濱30線 |  | 濱30線A1 | [17 empty] | 2-A8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱30線A1 | 11KV濱30線 R相AMP | FEEDER | D03/11/K330/I_R |  |  |  | CDC | 425 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱30線 | 濱30線 |  | 濱30線A2 | [17 empty] | 2-A9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱30線A2 | 11KV濱30線 S相AMP | FEEDER | D03/11/K330/I_S |  |  |  | CDC | 426 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱30線 | 濱30線 |  | 濱30線A3 | [17 empty] | 2-AA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱30線A3 | 11KV濱30線 T相AMP | FEEDER | D03/11/K330/I_T |  |  |  | CDC | 427 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 濱30線 | 濱30線 |  | 濱30線A0 | [17 empty] | 2-AB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.濱30線A0 | 11KV濱30線 N相AMP | FEEDER | D03/11/K330/I_N |  |  |  | CDC | 428 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MW | [17 empty] | 1-EC | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | D03/11/330/KW |  |  |  | CDC | 429 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D03 | 南濱DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVAR | [17 empty] | 1-ED | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | D03/11/330/KVAR |  |  |  | CDC | 430 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D03 | 南濱DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_R | [17 empty] | 1-EE | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | D03/11/330/I_R |  |  |  | CDC | 431 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_S | [17 empty] | 1-EF | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | D03/11/330/I_S |  |  |  | CDC | 432 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_T | [17 empty] | 1-F0 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | D03/11/330/I_T |  |  |  | CDC | 433 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | 2DTR | #2DTR |  | OilTemp | [17 empty] | 1-9E | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#2DTR_OIL | #2DTR 油溫 | MTR | D03//2DTR/OilTemp |  |  |  | CDC | 434 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D03 | 南濱DS | 0 |  | 2DTR(A) | #2DTR(A) |  | CoilTemp | [17 empty] | 1-9F | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | D03//2DTR(A)/CoilTemp |  |  |  | CDC | 435 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D03 | 南濱DS | 0 |  | 2DTR(A) | #2DTR(A) |  | TapPosMv | [17 empty] | 1-A1 |  | 1-3D |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 南濱DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | D03//2DTR(A)/TapPosMv |  |  |  | CDC | 436 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D03 | 南濱DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MW | [17 empty] | 2-8D | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | D03/11/340/KW |  |  |  | CDC | 437 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D03 | 南濱DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVAR | [17 empty] | 2-8E | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | D03/11/340/KVAR |  |  |  | CDC | 438 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D03 | 南濱DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_R | [17 empty] | 2-8F | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | D03/11/340/I_R |  |  |  | CDC | 439 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_S | [17 empty] | 2-90 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | D03/11/340/I_S |  |  |  | CDC | 440 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_T | [17 empty] | 2-91 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | D03/11/340/I_T |  |  |  | CDC | 441 | GENERICAIPoint | DS043_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 0 |  | 2DTR(B) | #2DTR(B) |  | CoilTemp | [17 empty] | 1-A0 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 南濱DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | D03//2DTR(B)/CoilTemp |  |  |  | CDC | 442 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D03 | 南濱DS | 0 |  | 2DTR(B) | #2DTR(B) |  | TapPosMv | [17 empty] | 1-A2 |  | 1-3F |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 南濱DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | D03//2DTR(B)/TapPosMv |  |  |  | CDC | 443 | GENERICAIPoint | DS043_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D03 | 南濱DS | 11 | 11kV | 開陽成大(K312) | 開陽成大(K312) |  | 開陽成大KVAR | [17 empty] | 3-99 | [5 empty] | KVAR_-6000_6000(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.開陽成大KVAR | 11KV開陽成大(K312) KVAR | FEEDER |  |  |  |  | CDC | 444 | GENERICAIPoint | DS043_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 3.600000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 開陽成大(K312) | 開陽成大(K312) |  | 開陽成大A1 | [17 empty] | 3-9A | [5 empty] | A_-200_200(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.開陽成大A1 | 11KV開陽成大(K312) R相AMP | FEEDER |  |  |  |  | CDC | 445 | GENERICAIPoint | DS043_L3 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 開陽成大(K312) | 開陽成大(K312) |  | 開陽成大A2 | [17 empty] | 3-9B | [5 empty] | A_-200_200(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.開陽成大A2 | 11KV開陽成大(K312) S相AMP | FEEDER |  |  |  |  | CDC | 446 | GENERICAIPoint | DS043_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 開陽成大(K312) | 開陽成大(K312) |  | 開陽成大A3 | [17 empty] | 3-9C | [5 empty] | A_-200_200(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.開陽成大A3 | 11KV開陽成大(K312) T相AMP | FEEDER |  |  |  |  | CDC | 447 | GENERICAIPoint | DS043_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D03 | 南濱DS | 11 | 11kV | 開陽成大 | 開陽成大(K312) |  | KV1 | [17 empty] | 3-9D | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.開陽成大_KV1 | 11KV開陽成大(K312) R相KV | OTHER |  |  |  |  | CDC | 448 | GENERICAIPoint | DS043_L3 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D03 | 南濱DS | 11 | 11kV | 開陽成大 | 開陽成大(K312) |  | KV2 | [17 empty] | 3-9E | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.開陽成大_KV2 | 11KV開陽成大(K312) S相KV | OTHER |  |  |  |  | CDC | 449 | GENERICAIPoint | DS043_L3 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D03 | 南濱DS | 11 | 11kV | 開陽成大 | 開陽成大(K312) |  | KV3 | [17 empty] | 3-9F | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.開陽成大_KV3 | 11KV開陽成大(K312) T相KV | OTHER |  |  |  |  | CDC | 450 | GENERICAIPoint | DS043_L3 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D03 | 南濱DS | 11 | 11kV | 開陽成大 | 開陽成大(K312) |  | KW | [17 empty] | 3-98 | [5 empty] | KW_-6000_6000(-2000_2000) |  | DDCS4_1 | [8 empty] | 南濱DS.開陽成大_KW | 11KV開陽成大(K312) KW | OTHER |  |  |  |  | CDC | 451 | GENERICAIPoint | DS043_L3 | CDC2_AI |  | AI | [17 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 2.700000 | 0.010000
D03 | 南濱DS | 161 | 161kV | 1510 | 安南南濱一路(1510) |  | PHA | [17 empty] | 1-00-03 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.1510_PHA | 安南南濱一路(1510) 相間RY | LINE161 | D03/161/1510/PHA |  |  |  | CDC | 452 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1510 | 安南南濱一路(1510) |  | GDA | [17 empty] | 1-00-04 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.1510_GDA | 安南南濱一路(1510) 接地RY | LINE161 | D03/161/1510/GDA |  |  |  | CDC | 453 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1510 | 安南南濱一路(1510) |  | 87A | [17 empty] | 1-00-01 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.1510_87A | 安南南濱一路(1510) 87RY | LINE161 | D03/161/1510/87A |  |  |  | CDC | 454 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1510 | 安南南濱一路(1510) |  | 87UL | [17 empty] | 1-30-02 |  | 1-24 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1510_87UL | 安南南濱一路(1510) 87RY U/L | LINE161 | D03/161/1510/87UL |  |  |  | CDC | 455 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1510 | 安南南濱一路(1510) |  | CB | [17 empty] | 1-00-00 |  | 1-01 | [5 empty] | 161KV_S | [8 empty] | 南濱DS.1510_CB | 1510(安南南濱一路) CB | LINE161 | D03/161/1510/CB |  |  |  | CDC | 456 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 161 | 161kV | 1510 | 安南南濱一路(1510) |  | 79UL | [17 empty] | 1-30-03 |  | 1-25 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1510_79UL | 安南南濱一路(1510) 79RY U/L | LINE161 | D03/161/1510/79UL |  |  |  | CDC | 457 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1510 | 安南南濱一路(1510) |  | DS1 | 1511 | [16 empty] | 1-38-00 | 1-38-01 | 1-44 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1511_DS | 1511(安南南濱一路) DS | LINE161 | D03/161/1510/DS1 |  |  |  | CDC | 458 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 161 | 161kV | 1510 | 安南南濱一路(1510) |  | DS2 | 1512 | [16 empty] | 1-38-02 | 1-38-03 | 1-45 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1512_DS | 1512(安南南濱一路) DS | LINE161 | D03/161/1510/DS2 |  |  |  | CDC | 459 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D03 | 南濱DS | 161 | 161kV | 1510 | 安南南濱一路(1510) |  | DS3 | 1513 | [16 empty] | 1-38-04 | 1-38-05 | 1-46 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1513_DS | 1513(安南南濱一路) DS | LINE161 | D03/161/1510/DS3 |  |  |  | CDC | 460 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 161 | 161kV | 1510 | 安南南濱一路(1510) |  | E3 | 1513E | [16 empty] | 1-38-06 | 1-38-07 | 1-47 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1513E_ES | 1513E(安南南濱一路) ES | LINE161 | D03/161/1510/ES3 |  |  |  | CDC | 461 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D03 | 南濱DS | 161 | 161kV | 1520 | 安南南濱二路(1520) |  | PHA | [17 empty] | 1-01-00 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.1520_PHA | 安南南濱二路(1520) 相間RY | LINE161 | D03/161/1520/PHA |  |  |  | CDC | 462 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1520 | 安南南濱二路(1520) |  | GDA | [17 empty] | 1-01-01 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.1520_GDA | 安南南濱二路(1520) 接地RY | LINE161 | D03/161/1520/GDA |  |  |  | CDC | 463 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1520 | 安南南濱二路(1520) |  | 87A | [17 empty] | 1-00-06 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.1520_87A | 安南南濱二路(1520) 87RY | LINE161 | D03/161/1520/87A |  |  |  | CDC | 464 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1520 | 安南南濱二路(1520) |  | 87UL | [17 empty] | 1-30-04 |  | 1-26 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1520_87UL | 安南南濱二路(1520) 87RY U/L | LINE161 | D03/161/1520/87UL |  |  |  | CDC | 465 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1520 | 安南南濱二路(1520) |  | CB | [17 empty] | 1-00-05 |  | 1-02 | [5 empty] | 161KV_S | [8 empty] | 南濱DS.1520_CB | 1520(安南南濱二路) CB | LINE161 | D03/161/1520/CB |  |  |  | CDC | 466 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 161 | 161kV | 1520 | 安南南濱二路(1520) |  | 79UL | [17 empty] | 1-30-05 |  | 1-27 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1520_79UL | 安南南濱二路(1520) 79RY U/L | LINE161 | D03/161/1520/79UL |  |  |  | CDC | 467 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1520 | 安南南濱二路(1520) |  | DS1 | 1521 | [16 empty] | 1-38-08 | 1-38-09 | 1-48 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1521_DS | 1521(安南南濱二路) DS | LINE161 | D03/161/1520/DS1 |  |  |  | CDC | 468 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D03 | 南濱DS | 161 | 161kV | 1520 | 安南南濱二路(1520) |  | DS2 | 1522 | [16 empty] | 1-38-10 | 1-38-11 | 1-49 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1522_DS | 1522(安南南濱二路) DS | LINE161 | D03/161/1520/DS2 |  |  |  | CDC | 469 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 161 | 161kV | 1520 | 安南南濱二路(1520) |  | DS3 | 1523 | [16 empty] | 1-38-12 | 1-38-13 | 1-4A | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1523_DS | 1523(安南南濱二路) DS | LINE161 | D03/161/1520/DS3 |  |  |  | CDC | 470 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 161 | 161kV | 1520 | 安南南濱二路(1520) |  | E3 | 1523E | [16 empty] | 1-38-14 | 1-38-15 | 1-4B | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1523E_ES | 1523E(安南南濱二路) ES | LINE161 | D03/161/1520/ES3 |  |  |  | CDC | 471 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱安瀚線(1530) |  | PHA | [17 empty] | 1-01-05 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.1530_PHA | 南濱安瀚線(1530) 相間RY | LINE161 | D03/161/1530/PHA |  |  |  | CDC | 472 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱安瀚線(1530) |  | GDA | [17 empty] | 1-01-06 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.1530_GDA | 南濱安瀚線(1530) 接地RY | LINE161 | D03/161/1530/GDA |  |  |  | CDC | 473 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱安瀚線(1530) |  | CB | [17 empty] | 1-01-02 |  | 1-03 | [5 empty] | 161KV_S | [8 empty] | 南濱DS.1530_CB | 1530(南濱安瀚線) CB | LINE161 | D03/161/1530/CB |  |  |  | CDC | 474 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱安瀚線(1530) |  | 79UL | [17 empty] | 1-30-07 |  | 1-29 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1530_79UL | 南濱安瀚線(1530) 79RY U/L | LINE161 | D03/161/1530/79UL |  |  |  | CDC | 475 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱安瀚線(1530) |  | DS1 | 1531 | [16 empty] | 1-39-00 | 1-39-01 | 1-4C | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1531_DS | 1531(南濱安瀚線) DS | LINE161 | D03/161/1530/DS1 |  |  |  | CDC | 476 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱安瀚線(1530) |  | DS2 | 1532 | [16 empty] | 1-39-02 | 1-39-03 | 1-4D | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1532_DS | 1532(南濱安瀚線) DS | LINE161 | D03/161/1530/DS2 |  |  |  | CDC | 477 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱安瀚線(1530) |  | DS3 | 1533 | [16 empty] | 1-39-04 | 1-39-05 | 1-4E | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1533_DS | 1533(南濱安瀚線) DS | LINE161 | D03/161/1530/DS3 |  |  |  | CDC | 478 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱安瀚線(1530) |  | E3 | 1533E | [16 empty] | 1-39-06 | 1-39-07 | 1-4F | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1533E_ES | 1533E(南濱安瀚線) ES | LINE161 | D03/161/1530/ES3 |  |  |  | CDC | 479 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱凸版線(1540) |  | PHA | [17 empty] | 1-02-02 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.1540_PHA | 南濱凸版線(1540) 相間RY | LINE161 | D03/161/1540/PHA |  |  |  | CDC | 480 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱凸版線(1540) |  | GDA | [17 empty] | 1-02-03 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.1540_GDA | 南濱凸版線(1540) 接地RY | LINE161 | D03/161/1540/GDA |  |  |  | CDC | 481 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱凸版線(1540) |  | CB | [17 empty] | 1-01-07 |  | 1-04 | [5 empty] | 161KV_S | [8 empty] | 南濱DS.1540_CB | 1540(南濱凸版線) CB | LINE161 | D03/161/1540/CB |  |  |  | CDC | 482 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱凸版線(1540) |  | 79UL | [17 empty] | 1-30-09 |  | 1-2B | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1540_79UL | 南濱凸版線(1540) 79RY U/L | LINE161 | D03/161/1540/79UL |  |  |  | CDC | 483 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱凸版線(1540) |  | DS1 | 1541 | [16 empty] | 1-39-08 | 1-39-09 | 1-50 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1541_DS | 1541(南濱凸版線) DS | LINE161 | D03/161/1540/DS1 |  |  |  | CDC | 484 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱凸版線(1540) |  | DS2 | 1542 | [16 empty] | 1-39-10 | 1-39-11 | 1-51 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1542_DS | 1542(南濱凸版線) DS | LINE161 | D03/161/1540/DS2 |  |  |  | CDC | 485 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱凸版線(1540) |  | DS3 | 1543 | [16 empty] | 1-39-12 | 1-39-13 | 1-52 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1543_DS | 1543(南濱凸版線) DS | LINE161 | D03/161/1540/DS3 |  |  |  | CDC | 486 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱凸版線(1540) |  | E3 | 1543E | [16 empty] | 1-39-14 | 1-39-15 | 1-53 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1543E_ES | 1543E(南濱凸版線) ES | LINE161 | D03/161/1540/ES3 |  |  |  | CDC | 487 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D03 | 南濱DS | 11 | 11kV | K311 | 濱11線(K311) |  | PHA | [17 empty] | 1-14-04 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K311_PHA | 11KV濱11線(K311) 相間RY | FEEDER | D03/11/K311/PHA |  |  |  | CDC | 488 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K311 | 濱11線(K311) |  | GDA | [17 empty] | 1-14-05 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K311_GDA | 11KV濱11線(K311) 接地RY | FEEDER | D03/11/K311/GDA |  |  |  | CDC | 489 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K311 | 濱11線(K311) 79RY |  | 79UL | [17 empty] | 2-30-02 |  | 2-25 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K311_79UL | 11KV濱11線(K311) 79RY U/L | FEEDER | D03/11/K311/79UL |  |  |  | CDC | 490 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K311_LCO | 濱11線(K311) LCO |  | TapPosMv | [17 empty] | 2-30-03 |  | 2-26 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K311_LCO_TAP | 11KV濱11線(K311) LCO TAP | FEEDER | D03/11/K311/50_51NUL |  |  |  | CDC | 491 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K311 | K3(11KV濱11線) |  | CB | [17 empty] | 1-14-03 |  | 1-12 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K311_CB | K311(11KV濱11線) CB | FEEDER | D03/11/K311/CB |  |  |  | CDC | 492 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K312 | 濱12線(K312) |  | PHA | [17 empty] | 1-14-07 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K312_PHA | 11KV濱12線(K312) 相間RY | FEEDER | D03/11/K312/PHA |  |  |  | CDC | 493 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K312 | 濱12線(K312) |  | GDA | [17 empty] | 1-15-00 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K312_GDA | 11KV濱12線(K312) 接地RY | FEEDER | D03/11/K312/GDA |  |  |  | CDC | 494 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K312 | 濱12線(K312) 79RY |  | 79UL | [17 empty] | 2-30-04 |  | 2-27 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K312_79UL | 11KV濱12線(K312) 79RY U/L | FEEDER | D03/11/K312/79UL |  |  |  | CDC | 495 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K312_LCO | 濱12線(K312) LCO |  | TapPosMv | [17 empty] | 2-30-05 |  | 2-28 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K312_LCO_TAP | 11KV濱12線(K312) LCO TAP | FEEDER | D03/11/K312/50_51NUL |  |  |  | CDC | 496 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K312 | K312(11KV濱12線) |  | CB | [17 empty] | 1-14-06 |  | 1-13 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K312_CB | K312(11KV濱12線) CB | FEEDER | D03/11/K312/CB |  |  |  | CDC | 497 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K313 | 濱13線(K313) |  | PHA | [17 empty] | 1-15-02 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K313_PHA | 11KV濱13線(K313) 相間RY | FEEDER | D03/11/K313/PHA |  |  |  | CDC | 498 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K313 | 濱13線(K313) |  | GDA | [17 empty] | 1-15-03 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K313_GDA | 11KV濱13線(K313) 接地RY | FEEDER | D03/11/K313/GDA |  |  |  | CDC | 499 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K313 | 濱13線(K313) 79RY |  | 79UL | [17 empty] | 2-30-06 |  | 2-29 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K313_79UL | 11KV濱13線(K313) 79RY U/L | FEEDER | D03/11/K313/79UL |  |  |  | CDC | 500 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K313_LCO | 濱13線(K313) LCO |  | TapPosMv | [17 empty] | 2-30-07 |  | 2-2A | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K313_LCO_TAP | 11KV濱13線(K313) LCO TAP | FEEDER | D03/11/K313/50_51NUL |  |  |  | CDC | 501 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K313 | K313(11KV濱13線) |  | CB | [17 empty] | 1-15-01 |  | 1-14 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K313_CB | K313(11KV濱13線) CB | FEEDER | D03/11/K313/CB |  |  |  | CDC | 502 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K314 | 濱14線(K314) |  | PHA | [17 empty] | 1-15-05 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K314_PHA | 11KV濱14線(K314) 相間RY | FEEDER | D03/11/K314/PHA |  |  |  | CDC | 503 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K314 | 濱14線(K314) |  | GDA | [17 empty] | 1-15-06 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K314_GDA | 11KV濱14線(K314) 接地RY | FEEDER | D03/11/K314/GDA |  |  |  | CDC | 504 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K314 | 濱14線(K314) 79RY |  | 79UL | [17 empty] | 2-30-08 |  | 2-2B | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K314_79UL | 11KV濱14線(K314) 79RY U/L | FEEDER | D03/11/K314/79UL |  |  |  | CDC | 505 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K314_LCO | 濱14線(K314) LCO |  | TapPosMv | [17 empty] | 2-30-09 |  | 2-2C | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K314_LCO_TAP | 11KV濱14線(K314) LCO TAP | FEEDER | D03/11/K314/50_51NUL |  |  |  | CDC | 506 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K314 | K314(11KV濱14線) |  | CB | [17 empty] | 1-15-04 |  | 1-15 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K314_CB | K314(11KV濱14線) CB | FEEDER | D03/11/K314/CB |  |  |  | CDC | 507 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K315 | 濱15線(K315) |  | PHA | [17 empty] | 1-16-00 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K315_PHA | 11KV濱15線(K315) 相間RY | FEEDER | D03/11/K315/PHA |  |  |  | CDC | 508 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K315 | 濱15線(K315) |  | GDA | [17 empty] | 1-16-01 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K315_GDA | 11KV濱15線(K315) 接地RY | FEEDER | D03/11/K315/GDA |  |  |  | CDC | 509 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K315 | 濱15線(K315) 79RY |  | 79UL | [17 empty] | 2-30-10 |  | 2-2D | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K315_79UL | 11KV濱15線(K315) 79RY U/L | FEEDER | D03/11/K315/79UL |  |  |  | CDC | 510 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K315_LCO | 濱15線(K315) LCO |  | TapPosMv | [17 empty] | 2-30-11 |  | 2-2E | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K315_LCO_TAP | 11KV濱15線(K315) LCO TAP | FEEDER | D03/11/K315/50_51NUL |  |  |  | CDC | 511 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K315 | K315(11KV濱15線) |  | CB | [17 empty] | 1-15-07 |  | 1-16 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K315_CB | K315(11KV濱15線) CB | FEEDER | D03/11/K315/CB |  |  |  | CDC | 512 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K316 | 濱16線(K316) |  | PHA | [17 empty] | 1-17-04 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K316_PHA | 11KV濱16線(K316) 相間RY | FEEDER | D03/11/K316/PHA |  |  |  | CDC | 513 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K316 | 濱16線(K316) |  | GDA | [17 empty] | 1-17-05 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K316_GDA | 11KV濱16線(K316) 接地RY | FEEDER | D03/11/K316/GDA |  |  |  | CDC | 514 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K316 | 濱16線(K316) 79RY |  | 79UL | [17 empty] | 2-30-14 |  | 2-31 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K316_79UL | 11KV濱16線(K316) 79RY U/L | FEEDER | D03/11/K316/79UL |  |  |  | CDC | 515 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K316_LCO | 濱16線(K316) LCO |  | TapPosMv | [17 empty] | 2-30-15 |  | 2-32 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K316_LCO_TAP | 11KV濱16線(K316) LCO TAP | FEEDER | D03/11/K316/50_51NUL |  |  |  | CDC | 516 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K316 | K316(11KV濱16線) |  | CB | [17 empty] | 1-17-03 |  | 1-1B | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K316_CB | K316(11KV濱16線) CB | FEEDER | D03/11/K316/CB |  |  |  | CDC | 517 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K317 | 濱17線(K317) |  | PHA | [17 empty] | 1-17-07 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K317_PHA | 11KV濱17線(K317) 相間RY | FEEDER | D03/11/K317/PHA |  |  |  | CDC | 518 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K317 | 濱17線(K317) |  | GDA | [17 empty] | 1-18-00 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K317_GDA | 11KV濱17線(K317) 接地RY | FEEDER | D03/11/K317/GDA |  |  |  | CDC | 519 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K317 | 濱17線(K317) 79RY |  | 79UL | [17 empty] | 2-31-00 |  | 2-33 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K317_79UL | 11KV濱17線(K317) 79RY U/L | FEEDER | D03/11/K317/79UL |  |  |  | CDC | 520 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K317_LCO | 濱17線(K317) LCO |  | TapPosMv | [17 empty] | 2-31-01 |  | 2-34 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K317_LCO_TAP | 11KV濱17線(K317) LCO TAP | FEEDER | D03/11/K317/50_51NUL |  |  |  | CDC | 521 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K317 | K317(11KV濱17線) |  | CB | [17 empty] | 1-17-06 |  | 1-1C | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K317_CB | K317(11KV濱17線) CB | FEEDER | D03/11/K317/CB |  |  |  | CDC | 522 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K318 | 濱18線(K318) |  | PHA | [17 empty] | 1-18-02 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K318_PHA | 11KV濱18線(K318) 相間RY | FEEDER | D03/11/K318/PHA |  |  |  | CDC | 523 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K318 | 濱18線(K318) |  | GDA | [17 empty] | 1-18-03 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K318_GDA | 11KV濱18線(K318) 接地RY | FEEDER | D03/11/K318/GDA |  |  |  | CDC | 524 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K318 | 濱18線(K318) 79RY |  | 79UL | [17 empty] | 2-31-02 |  | 2-35 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K318_79UL | 11KV濱18線(K318) 79RY U/L | FEEDER | D03/11/K318/79UL |  |  |  | CDC | 525 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K318_LCO | 濱18線(K318) LCO |  | TapPosMv | [17 empty] | 2-31-03 |  | 2-36 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K318_LCO_TAP | 11KV濱18線(K318) LCO TAP | FEEDER | D03/11/K318/50_51NUL |  |  |  | CDC | 526 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K318 | K318(11KV濱18線) |  | CB | [17 empty] | 1-18-01 |  | 1-1D | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K318_CB | K318(11KV濱18線) CB | FEEDER | D03/11/K318/CB |  |  |  | CDC | 527 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K319 | 濱19線(K319) |  | PHA | [17 empty] | 1-18-05 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K319_PHA | 11KV濱19線(K319) 相間RY | FEEDER | D03/11/K319/PHA |  |  |  | CDC | 528 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K319 | 濱19線(K319) |  | GDA | [17 empty] | 1-18-06 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K319_GDA | 11KV濱19線(K319) 接地RY | FEEDER | D03/11/K319/GDA |  |  |  | CDC | 529 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K319 | 濱19線(K319) 79RY |  | 79UL | [17 empty] | 2-31-04 |  | 2-37 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K319_79UL | 11KV濱19線(K319) 79RY U/L | FEEDER | D03/11/K319/79UL |  |  |  | CDC | 530 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K319_LCO | 濱19線(K319) LCO |  | TapPosMv | [17 empty] | 2-31-05 |  | 2-38 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K319_LCO_TAP | 11KV濱19線(K319) LCO TAP | FEEDER | D03/11/K319/50_51NUL |  |  |  | CDC | 531 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K319 | K319(11KV濱19線) |  | CB | [17 empty] | 1-18-04 |  | 1-1E | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K319_CB | K319(11KV濱19線) CB | FEEDER | D03/11/K319/CB |  |  |  | CDC | 532 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K320 | 濱20線(K320) |  | PHA | [17 empty] | 1-19-00 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K320_PHA | 11KV濱20線(K320) 相間RY | FEEDER | D03/11/K320/PHA |  |  |  | CDC | 533 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K320 | 濱20線(K320) |  | GDA | [17 empty] | 1-19-01 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K320_GDA | 11KV濱20線(K320) 接地RY | FEEDER | D03/11/K320/GDA |  |  |  | CDC | 534 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K320 | 濱20線(K320) 79RY |  | 79UL | [17 empty] | 2-31-06 |  | 2-39 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K320_79UL | 11KV濱20線(K320) 79RY U/L | FEEDER | D03/11/K320/79UL |  |  |  | CDC | 535 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K320_LCO | 濱20線(K320) LCO |  | TapPosMv | [17 empty] | 2-31-07 |  | 2-3A | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K320_LCO_TAP | 11KV濱20線(K320) LCO TAP | FEEDER | D03/11/K320/50_51NUL |  |  |  | CDC | 536 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K320 | K320(11KV濱20線) |  | CB | [17 empty] | 1-18-07 |  | 1-1F | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K320_CB | K320(11KV濱20線) CB | FEEDER | D03/11/K320/CB |  |  |  | CDC | 537 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K361 | 濱61線(K361) |  | PHA | [17 empty] | 2-05-03 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K361_PHA | 23KV濱61線(K361) 相間RY | FEEDER | D03/22/K361/PHA |  |  |  | CDC | 538 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K361 | 濱61線(K361) |  | GDA | [17 empty] | 2-05-04 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K361_GDA | 23KV濱61線(K361) 接地RY | FEEDER | D03/22/K361/GDA |  |  |  | CDC | 539 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K361 | 濱61線(K361) 79RY |  | 79UL | [17 empty] | 2-33-01 |  | 2-54 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K361_79UL | 23KV濱61線(K361) 79RY U/L | FEEDER | D03/22/K361/79UL |  |  |  | CDC | 540 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 22 | 22kV | K361_LCO | 濱61線(K361) LCO |  | TapPosMv | [17 empty] | 2-33-02 |  | 2-55 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K361_LCO_TAP | 23KV濱61線(K361) LCO TAP | FEEDER | D03/22/K361/50_51NUL |  |  |  | CDC | 541 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 22 | 22kV | K361 | K361(23KV濱61線) |  | CB | [17 empty] | 2-05-02 |  | 2-0E | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K361_CB | K361(23KV濱61線) CB | FEEDER | D03/22/K361/CB |  |  |  | CDC | 542 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K362 | 濱62線(K362) |  | PHA | [17 empty] | 2-05-06 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K362_PHA | 23KV濱62線(K362) 相間RY | FEEDER | D03/22/K362/PHA |  |  |  | CDC | 543 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K362 | 濱62線(K362) |  | GDA | [17 empty] | 2-05-07 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K362_GDA | 23KV濱62線(K362) 接地RY | FEEDER | D03/22/K362/GDA |  |  |  | CDC | 544 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K362 | 濱62線(K362) 79RY |  | 79UL | [17 empty] | 2-33-03 |  | 2-56 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K362_79UL | 23KV濱62線(K362) 79RY U/L | FEEDER | D03/22/K362/79UL |  |  |  | CDC | 545 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 22 | 22kV | K362_LCO | 濱62線(K362) LCO |  | TapPosMv | [17 empty] | 2-33-04 |  | 2-57 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K362_LCO_TAP | 23KV濱62線(K362) LCO TAP | FEEDER | D03/22/K362/50_51NUL |  |  |  | CDC | 546 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 22 | 22kV | K362 | K362(23KV濱62線) |  | CB | [17 empty] | 2-05-05 |  | 2-0F | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K362_CB | K362(23KV濱62線) CB | FEEDER | D03/22/K362/CB |  |  |  | CDC | 547 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K363 | 濱63線(K363) |  | PHA | [17 empty] | 2-06-01 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K363_PHA | 23KV濱63線(K363) 相間RY | FEEDER | D03/22/K363/PHA |  |  |  | CDC | 548 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K363 | 濱63線(K363) |  | GDA | [17 empty] | 2-06-02 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K363_GDA | 23KV濱63線(K363) 接地RY | FEEDER | D03/22/K363/GDA |  |  |  | CDC | 549 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K363 | 濱63線(K363) 79RY |  | 79UL | [17 empty] | 2-33-05 |  | 2-58 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K363_79UL | 23KV濱63線(K363) 79RY U/L | FEEDER | D03/22/K363/79UL |  |  |  | CDC | 550 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 22 | 22kV | K363_LCO | 濱63線(K363) LCO |  | TapPosMv | [17 empty] | 2-33-06 |  | 2-59 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K363_LCO_TAP | 23KV濱63線(K363) LCO TAP | FEEDER | D03/22/K363/50_51NUL |  |  |  | CDC | 551 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 22 | 22kV | K363 | K363(23KV濱63線) |  | CB | [17 empty] | 2-06-00 |  | 2-10 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K363_CB | K363(23KV濱63線) CB | FEEDER | D03/22/K363/CB |  |  |  | CDC | 552 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K364 | 濱64線(K364) |  | PHA | [17 empty] | 2-06-04 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K364_PHA | 23KV濱64線(K364) 相間RY | FEEDER | D03/22/K364/PHA |  |  |  | CDC | 553 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K364 | 濱64線(K364) |  | GDA | [17 empty] | 2-06-05 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K364_GDA | 23KV濱64線(K364) 接地RY | FEEDER | D03/22/K364/GDA |  |  |  | CDC | 554 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K364 | 濱64線(K364) 79RY |  | 79UL | [17 empty] | 2-33-07 |  | 2-5A | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K364_79UL | 23KV濱64線(K364) 79RY U/L | FEEDER | D03/22/K364/79UL |  |  |  | CDC | 555 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 22 | 22kV | K364_LCO | 濱64線(K364) LCO |  | TapPosMv | [17 empty] | 2-33-08 |  | 2-5B | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K364_LCO_TAP | 23KV濱64線(K364) LCO TAP | FEEDER | D03/22/K364/50_51NUL |  |  |  | CDC | 556 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 22 | 22kV | K364 | K364(23KV濱64線) |  | CB | [17 empty] | 2-06-03 |  | 2-11 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K364_CB | K364(23KV濱64線) CB | FEEDER | D03/22/K364/CB |  |  |  | CDC | 557 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K365 | 濱65線(K365) |  | PHA | [17 empty] | 2-06-07 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K365_PHA | 23KV濱65線(K365) 相間RY | FEEDER | D03/22/K365/PHA |  |  |  | CDC | 558 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K365 | 濱65線(K365) |  | GDA | [17 empty] | 2-07-00 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K365_GDA | 23KV濱65線(K365) 接地RY | FEEDER | D03/22/K365/GDA |  |  |  | CDC | 559 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K365 | 濱65線(K365) 79RY |  | 79UL | [17 empty] | 2-33-09 |  | 2-5C | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K365_79UL | 23KV濱65線(K365) 79RY U/L | FEEDER | D03/22/K365/79UL |  |  |  | CDC | 560 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 22 | 22kV | K365_LCO | 濱65線(K365) LCO |  | TapPosMv | [17 empty] | 2-33-10 |  | 2-5D | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K365_LCO_TAP | 23KV濱65線(K365) LCO TAP | FEEDER | D03/22/K365/50_51NUL |  |  |  | CDC | 561 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 22 | 22kV | K365 | K365(23KV濱65線) |  | CB | [17 empty] | 2-06-06 |  | 2-12 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K365_CB | K365(23KV濱65線) CB | FEEDER | D03/22/K365/CB |  |  |  | CDC | 562 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K366 | 濱66線(K366) |  | PHA | [17 empty] | 2-07-02 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K366_PHA | 23KV濱66線(K366) 相間RY | FEEDER | D03/22/K366/PHA |  |  |  | CDC | 563 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K366 | 濱66線(K366) |  | GDA | [17 empty] | 2-07-03 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K366_GDA | 23KV濱66線(K366) 接地RY | FEEDER | D03/22/K366/GDA |  |  |  | CDC | 564 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K366 | 濱66線(K366) 79RY |  | 79UL | [17 empty] | 2-33-11 |  | 2-5E | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K366_79UL | 23KV濱66線(K366) 79RY U/L | FEEDER | D03/22/K366/79UL |  |  |  | CDC | 565 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 22 | 22kV | K366_LCO | 濱66線(K366) LCO |  | TapPosMv | [17 empty] | 2-33-12 |  | 2-5F | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K366_LCO_TAP | 23KV濱66線(K366) LCO TAP | FEEDER | D03/22/K366/50_51NUL |  |  |  | CDC | 566 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 22 | 22kV | K366 | K366(23KV濱66線) |  | CB | [17 empty] | 2-07-01 |  | 2-13 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K366_CB | K366(23KV濱66線) CB | FEEDER | D03/22/K366/CB |  |  |  | CDC | 567 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K367 | 濱67線(K367) |  | PHA | [17 empty] | 2-07-05 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K367_PHA | 23KV濱67線(K367) 相間RY | FEEDER | D03/22/K367/PHA |  |  |  | CDC | 568 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K367 | 濱67線(K367) |  | GDA | [17 empty] | 2-07-06 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K367_GDA | 23KV濱67線(K367) 接地RY | FEEDER | D03/22/K367/GDA |  |  |  | CDC | 569 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K367 | 濱67線(K367) 79RY |  | 79UL | [17 empty] | 2-33-13 |  | 2-60 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K367_79UL | 23KV濱67線(K367) 79RY U/L | FEEDER | D03/22/K367/79UL |  |  |  | CDC | 570 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 22 | 22kV | K367_LCO | 濱67線(K367) LCO |  | TapPosMv | [17 empty] | 2-33-14 |  | 2-61 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K367_LCO_TAP | 23KV濱67線(K367) LCO TAP | FEEDER | D03/22/K367/50_51NUL |  |  |  | CDC | 571 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 22 | 22kV | K367 | K367(23KV濱67線) |  | CB | [17 empty] | 2-07-04 |  | 2-14 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K367_CB | K367(23KV濱67線) CB | FEEDER | D03/22/K367/CB |  |  |  | CDC | 572 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K368 | 濱68線(K368) |  | PHA | [17 empty] | 2-08-00 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K368_PHA | 23KV濱68線(K368) 相間RY | FEEDER | D03/22/K368/PHA |  |  |  | CDC | 573 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K368 | 濱68線(K368) |  | GDA | [17 empty] | 2-08-01 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K368_GDA | 23KV濱68線(K368) 接地RY | FEEDER | D03/22/K368/GDA |  |  |  | CDC | 574 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K368 | 濱68線(K368) 79RY |  | 79UL | [17 empty] | 2-33-15 |  | 2-62 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K368_79UL | 23KV濱68線(K368) 79RY U/L | FEEDER | D03/22/K368/79UL |  |  |  | CDC | 575 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 22 | 22kV | K368_LCO | 濱68線(K368) LCO |  | TapPosMv | [17 empty] | 2-34-00 |  | 2-63 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K368_LCO_TAP | 23KV濱68線(K368) LCO TAP | FEEDER | D03/22/K368/50_51NUL |  |  |  | CDC | 576 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 22 | 22kV | K368 | K368(23KV濱68線) |  | CB | [17 empty] | 2-07-07 |  | 2-15 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K368_CB | K368(23KV濱68線) CB | FEEDER | D03/22/K368/CB |  |  |  | CDC | 577 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K371 | 濱71線(K371) |  | PHA | [17 empty] | 2-09-04 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K371_PHA | 23KV濱71線(K371) 相間RY | FEEDER | D03/22/K371/PHA |  |  |  | CDC | 578 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K371 | 濱71線(K371) |  | GDA | [17 empty] | 2-09-05 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K371_GDA | 23KV濱71線(K371) 接地RY | FEEDER | D03/22/K371/GDA |  |  |  | CDC | 579 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K371 | 濱71線(K371) 79RY |  | 79UL | [17 empty] | 2-34-03 |  | 2-66 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K371_79UL | 23KV濱71線(K371) 79RY U/L | FEEDER | D03/22/K371/79UL |  |  |  | CDC | 580 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 22 | 22kV | K371_LCO | 濱71線(K371) LCO |  | TapPosMv | [17 empty] | 2-34-04 |  | 2-67 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K371_LCO_TAP | 23KV濱71線(K371) LCO TAP | FEEDER | D03/22/K371/50_51NUL |  |  |  | CDC | 581 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 22 | 22kV | K371 | K371(23KV濱71線) |  | CB | [17 empty] | 2-09-03 |  | 2-19 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K371_CB | K371(23KV濱71線) CB | FEEDER | D03/22/K371/CB |  |  |  | CDC | 582 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K372 | 濱72線(K372) |  | PHA | [17 empty] | 2-09-07 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K372_PHA | 23KV濱72線(K372) 相間RY | FEEDER | D03/22/K372/PHA |  |  |  | CDC | 583 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K372 | 濱72線(K372) |  | GDA | [17 empty] | 2-0A-00 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K372_GDA | 23KV濱72線(K372) 接地RY | FEEDER | D03/22/K372/GDA |  |  |  | CDC | 584 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K372 | 濱72線(K372) 79RY |  | 79UL | [17 empty] | 2-34-05 |  | 2-68 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K372_79UL | 23KV濱72線(K372) 79RY U/L | FEEDER | D03/22/K372/79UL |  |  |  | CDC | 585 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 22 | 22kV | K372_LCO | 濱72線(K372) LCO |  | TapPosMv | [17 empty] | 2-34-06 |  | 2-69 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K372_LCO_TAP | 23KV濱72線(K372) LCO TAP | FEEDER | D03/22/K372/50_51NUL |  |  |  | CDC | 586 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 22 | 22kV | K372 | K372(23KV濱72線) |  | CB | [17 empty] | 2-09-06 |  | 2-1A | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K372_CB | K372(23KV濱72線) CB | FEEDER | D03/22/K372/CB |  |  |  | CDC | 587 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K373 | 濱73線(K373) |  | PHA | [17 empty] | 2-0A-02 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K373_PHA | 23KV濱73線(K373) 相間RY | FEEDER | D03/22/K373/PHA |  |  |  | CDC | 588 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K373 | 濱73線(K373) |  | GDA | [17 empty] | 2-0A-03 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K373_GDA | 23KV濱73線(K373) 接地RY | FEEDER | D03/22/K373/GDA |  |  |  | CDC | 589 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K373 | 濱73線(K373) 79RY |  | 79UL | [17 empty] | 2-34-07 |  | 2-6A | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K373_79UL | 23KV濱73線(K373) 79RY U/L | FEEDER | D03/22/K373/79UL |  |  |  | CDC | 590 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 22 | 22kV | K373_LCO | 濱73線(K373) LCO |  | TapPosMv | [17 empty] | 2-34-08 |  | 2-6B | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K373_LCO_TAP | 23KV濱73線(K373) LCO TAP | FEEDER | D03/22/K373/50_51NUL |  |  |  | CDC | 591 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 22 | 22kV | K373 | K373(23KV濱73線) |  | CB | [17 empty] | 2-0A-01 |  | 2-1B | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K373_CB | K373(23KV濱73線) CB | FEEDER | D03/22/K373/CB |  |  |  | CDC | 592 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K374 | 濱74線(K374) |  | PHA | [17 empty] | 2-0A-05 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K374_PHA | 23KV濱74線(K374) 相間RY | FEEDER | D03/22/K374/PHA |  |  |  | CDC | 593 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K374 | 濱74線(K374) |  | GDA | [17 empty] | 2-0A-06 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K374_GDA | 23KV濱74線(K374) 接地RY | FEEDER | D03/22/K374/GDA |  |  |  | CDC | 594 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K374 | 濱74線(K374) 79RY |  | 79UL | [17 empty] | 2-34-09 |  | 2-6C | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K374_79UL | 23KV濱74線(K374) 79RY U/L | FEEDER | D03/22/K374/79UL |  |  |  | CDC | 595 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 22 | 22kV | K374_LCO | 濱74線(K374) LCO |  | TapPosMv | [17 empty] | 2-34-10 |  | 2-6D | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K374_LCO_TAP | 23KV濱74線(K374) LCO TAP | FEEDER | D03/22/K374/50_51NUL |  |  |  | CDC | 596 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 22 | 22kV | K374 | K374(23KV濱74線) |  | CB | [17 empty] | 2-0A-04 |  | 2-1C | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K374_CB | K374(23KV濱74線) CB | FEEDER | D03/22/K374/CB |  |  |  | CDC | 597 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K375 | 濱75線(K375) |  | PHA | [17 empty] | 2-0B-00 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K375_PHA | 23KV濱75線(K375) 相間RY | FEEDER | D03/22/K375/PHA |  |  |  | CDC | 598 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K375 | 濱75線(K375) |  | GDA | [17 empty] | 2-0B-01 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K375_GDA | 23KV濱75線(K375) 接地RY | FEEDER | D03/22/K375/GDA |  |  |  | CDC | 599 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K375 | 濱75線(K375) 79RY |  | 79UL | [17 empty] | 2-34-11 |  | 2-6E | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K375_79UL | 23KV濱75線(K375) 79RY U/L | FEEDER | D03/22/K375/79UL |  |  |  | CDC | 600 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 22 | 22kV | K375_LCO | 濱75線(K375) LCO |  | TapPosMv | [17 empty] | 2-34-12 |  | 2-6F | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K375_LCO_TAP | 23KV濱75線(K375) LCO TAP | FEEDER | D03/22/K375/50_51NUL |  |  |  | CDC | 601 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 22 | 22kV | K375 | K375(23KV濱75線) |  | CB | [17 empty] | 2-0A-07 |  | 2-1D | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K375_CB | K375(23KV濱75線) CB | FEEDER | D03/22/K375/CB |  |  |  | CDC | 602 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K376 | 濱76線(K376) |  | PHA | [17 empty] | 2-0B-03 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K376_PHA | 23KV濱76線(K376) 相間RY | FEEDER | D03/22/K376/PHA |  |  |  | CDC | 603 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K376 | 濱76線(K376) |  | GDA | [17 empty] | 2-0B-04 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K376_GDA | 23KV濱76線(K376) 接地RY | FEEDER | D03/22/K376/GDA |  |  |  | CDC | 604 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K376 | 濱76線(K376) 79RY |  | 79UL | [17 empty] | 2-34-13 |  | 2-70 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K376_79UL | 23KV濱76線(K376) 79RY U/L | FEEDER | D03/22/K376/79UL |  |  |  | CDC | 605 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 22 | 22kV | K376_LCO | 濱76線(K376) LCO |  | TapPosMv | [17 empty] | 2-34-14 |  | 2-71 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K376_LCO_TAP | 23KV濱76線(K376) LCO TAP | FEEDER | D03/22/K376/50_51NUL |  |  |  | CDC | 606 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 22 | 22kV | K376 | K376(23KV濱76線) |  | CB | [17 empty] | 2-0B-02 |  | 2-1E | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K376_CB | K376(23KV濱76線) CB | FEEDER | D03/22/K376/CB |  |  |  | CDC | 607 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K377 | 濱77線(K377) |  | PHA | [17 empty] | 2-0B-06 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K377_PHA | 23KV濱77線(K377) 相間RY | FEEDER | D03/22/K377/PHA |  |  |  | CDC | 608 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K377 | 濱77線(K377) |  | GDA | [17 empty] | 2-0B-07 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K377_GDA | 23KV濱77線(K377) 接地RY | FEEDER | D03/22/K377/GDA |  |  |  | CDC | 609 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K377 | 濱77線(K377) 79RY |  | 79UL | [17 empty] | 2-34-15 |  | 2-72 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K377_79UL | 23KV濱77線(K377) 79RY U/L | FEEDER | D03/22/K377/79UL |  |  |  | CDC | 610 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 22 | 22kV | K377_LCO | 濱77線(K377) LCO |  | TapPosMv | [17 empty] | 2-35-00 |  | 2-73 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K377_LCO_TAP | 23KV濱77線(K377) LCO TAP | FEEDER | D03/22/K377/50_51NUL |  |  |  | CDC | 611 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 22 | 22kV | K377 | K377(23KV濱77線) |  | CB | [17 empty] | 2-0B-05 |  | 2-1F | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K377_CB | K377(23KV濱77線) CB | FEEDER | D03/22/K377/CB |  |  |  | CDC | 612 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | K378 | 濱78線(K378) |  | PHA | [17 empty] | 2-0C-01 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K378_PHA | 23KV濱78線(K378) 相間RY | FEEDER | D03/22/K378/PHA |  |  |  | CDC | 613 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K378 | 濱78線(K378) |  | GDA | [17 empty] | 2-0C-02 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K378_GDA | 23KV濱78線(K378) 接地RY | FEEDER | D03/22/K378/GDA |  |  |  | CDC | 614 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | K378 | 濱78線(K378) 79RY |  | 79UL | [17 empty] | 2-35-01 |  | 2-74 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K378_79UL | 23KV濱78線(K378) 79RY U/L | FEEDER | D03/22/K378/79UL |  |  |  | CDC | 615 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 22 | 22kV | K378_LCO | 濱78線(K378) LCO |  | TapPosMv | [17 empty] | 2-35-02 |  | 2-75 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K378_LCO_TAP | 23KV濱78線(K378) LCO TAP | FEEDER | D03/22/K378/50_51NUL |  |  |  | CDC | 616 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 22 | 22kV | K378 | K378(23KV濱78線) |  | CB | [17 empty] | 2-0C-00 |  | 2-20 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K378_CB | K378(23KV濱78線) CB | FEEDER | D03/22/K378/CB |  |  |  | CDC | 617 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 100 | TIE(100) |  | CB | [17 empty] | 1-16-02 |  | 1-17 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.100_CB | 100(TIE) CB | TIE | D03/11/100/CB |  |  |  | CDC | 618 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 100 | TIE(100) |  | 51A | [17 empty] | 1-16-03 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.100_51A | 11KV TIE(100) 51RY | TIE | D03/11/100/SCA |  |  |  | CDC | 619 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 100 | TIE(100) |  | 51NA | [17 empty] | 1-16-04 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.100_51NA | 11KV TIE(100) 51N RY | TIE | D03/11/100/UVA |  |  |  | CDC | 620 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [17 empty] | 1-06-02 |  | 1-0B | [5 empty] | 161KV_S | [8 empty] | 南濱DS.1500_CB | 1500(TIE) CB | TIE | D03/161/1500/CB |  |  |  | CDC | 621 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 1500 | TIE(1500) |  | 50A | [17 empty] | 1-06-03 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.1500_50A | 161KV TIE(1500) 50RY | TIE | D03/161/1500/50A |  |  |  | CDC | 622 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [16 empty] | 1-3D-00 | 1-3D-01 | 1-6C | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1501_DS | 1501(TIE) DS | TIE | D03/161/1500/DS1 |  |  |  | CDC | 623 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [16 empty] | 1-3D-02 | 1-3D-03 | 1-6D | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1502_DS | 1502(TIE) DS | TIE | D03/161/1500/DS2 |  |  |  | CDC | 624 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 0 |  | 300 | TIE(300) |  | CB | [17 empty] | 2-08-05 |  | 2-17 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.300_CB | 300(TIE) CB | TIE | D03/22/300/CB |  |  |  | CDC | 625 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 300 | TIE(300) |  | 51A | [17 empty] | 2-08-06 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.300_51A | 23KV TIE(300) 51RY | TIE | D03/22/300/PHA |  |  |  | CDC | 626 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 300 | TIE(300) |  | 51NA | [17 empty] | 2-08-07 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.300_51NA | 23KV TIE(300) 51N RY | TIE | D03/22/300/GDA |  |  |  | CDC | 627 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 390 | #1SSTR(390) |  | CB | [17 empty] | 1-16-05 |  | 1-18 | [5 empty] | 161KV_S | [8 empty] | 南濱DS.390_CB | 390(#1SSTR) CB | OTHER | D03/11/390/CB |  |  |  | CDC | 628 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 1SSTR | #1SSTR |  | 51A | [17 empty] | 1-16-06 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.#1SSTR_51A | #1SSTR 51RY | OTHER | D03/11/390/PHA |  |  |  | CDC | 629 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 1SSTR | #1SSTR |  | 51NA | [17 empty] | 1-16-07 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | D03/11/390/GDA |  |  |  | CDC | 630 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 490 | #2SSTR(490) |  | CB | [17 empty] | 2-0C-06 |  | 2-22 | [5 empty] | 161KV_S | [8 empty] | 南濱DS.490_CB | 490(#2SSTR) CB | OTHER | D03/22/490/CB |  |  |  | CDC | 631 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 2SSTR | #2SSTR |  | 51A | [17 empty] | 2-0C-07 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.#2SSTR_51A | #2SSTR 51RY | OTHER | D03/22/490/PHA |  |  |  | CDC | 632 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 2SSTR | #2SSTR |  | 51NA | [17 empty] | 2-0D-00 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | D03/22/490/GDA |  |  |  | CDC | 633 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB | [17 empty] | 1-07-00 |  | 1-0C | [5 empty] | 161KV_S | [8 empty] | 南濱DS.1750_CB | 1750(#1DTR) CB | MTR | D03/161/1750/CB |  |  |  | CDC | 634 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 310 | #1DTR(310) |  | CB | [17 empty] | 1-07-06 |  | 1-10 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.310_CB | 310(#1DTR) CB | MTR | D03/11/310/CB |  |  |  | CDC | 635 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 320 | #1DTR(320) |  | CB | [17 empty] | 1-08-02 |  | 1-19 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.320_CB | 320(#1DTR) CB | MTR | D03/11/320/CB |  |  |  | CDC | 636 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 1DTR | #1DTR |  | 51A | [17 empty] | 1-07-04 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.#1DTR_51A | #1DTR 51RY | MTR | D03//1DTR/PHA |  |  |  | CDC | 637 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 1DTR | #1DTR |  | 51NA | [17 empty] | 1-07-05 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.#1DTR_51NA | #1DTR 51N RY | MTR | D03//1DTR/GDA |  |  |  | CDC | 638 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 1DTR | #1DTR |  | 51ZA | [17 empty] | 1-07-03 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | D03//1DTR/51ZA |  |  |  | CDC | 639 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 1DTR | #1DTR |  | 87A | [17 empty] | 1-07-01 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.#1DTR_87A | #1DTR 87RY | MTR | D03//1DTR/87A |  |  |  | CDC | 640 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 310 | #1DTR(310) |  | 51A | [17 empty] | 1-07-07 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.310_51A | #1DTR二次側(310) 51RY | MTR | D03/11/310/51A |  |  |  | CDC | 641 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 320 | #1DTR(320) |  | 51A | [17 empty] | 1-08-03 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.320_51A | #1DTR二次側(320) 51RY | MTR | D03/11/320/51A |  |  |  | CDC | 642 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 1DTR | #1DTR |  | 96PA | [17 empty] | 1-07-02 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | D03//1DTR/96PA |  |  |  | CDC | 643 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 1DTR | #1DTR |  | 96D | [17 empty] | 2-36-02 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#1DTR_96D | #1DTR 96D RY | MTR | D03//1DTR/96D |  |  |  | CDC | 644 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 1DTR | #1DTR |  | 96P | [17 empty] | 2-36-03 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#1DTR_96P | #1DTR 96P RY | MTR | D03//1DTR/96P |  |  |  | CDC | 645 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 1DTR | #1DTR |  | 63Q | [17 empty] | 2-36-04 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#1DTR_63Q | #1DTR 63Q RY | MTR | D03//1DTR/63Q |  |  |  | CDC | 646 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 1DTR | #1DTR |  | 96B1 | [17 empty] | 2-36-00 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | D03//1DTR/96B1 |  |  |  | CDC | 647 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 1DTR | #1DTR |  | 96B2 | [17 empty] | 2-36-01 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | D03//1DTR/96B2 |  |  |  | CDC | 648 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 1DTR | #1DTR |  | TRA | [17 empty] | 1-31-11 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#1DTR_TRA | #1DTR 重故障 | MTR | D03//1DTR/TRA |  |  |  | CDC | 649 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 1DTR | #1DTR |  | TRF | [17 empty] | 1-31-12 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#1DTR_TRF | #1DTR 輕故障 | MTR | D03//1DTR/TRF |  |  |  | CDC | 650 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 1DTR(A) | #1DTR(A) |  | SupLocal | [17 empty] | 1-31-09 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | D03//1DTR(A)/SupLocal |  |  |  | CDC | 651 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D03 | 南濱DS | 0 |  | 1DTR(A) | #1DTR(A) |  | A_M | [17 empty] | 1-31-10 |  | 1-38 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | D03//1DTR(A)/Tap Chan |  |  |  | CDC | 652 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D03 | 南濱DS | 0 |  | 1DTR(B) | #1DTR(B) |  | SupLocal | [17 empty] | 1-31-13 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | D03//1DTR(B)/SupLocal |  |  |  | CDC | 653 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D03 | 南濱DS | 0 |  | 1DTR(B) | #1DTR(B) |  | A_M | [17 empty] | 1-31-14 |  | 1-3A | [5 empty] | ADCS_S | [8 empty] | 南濱DS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | D03//1DTR(B)/Tap Chan |  |  |  | CDC | 654 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D03 | 南濱DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 | [16 empty] | 1-3D-04 | 1-3D-05 | 1-6E | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1751_DS | 1751(#1DTR) DS | MTR | D03/161/1750/DS1 |  |  |  | CDC | 655 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 | [16 empty] | 1-3D-06 | 1-3D-07 | 1-6F | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1752_DS | 1752(#1DTR) DS | MTR | D03/161/1750/DS2 |  |  |  | CDC | 656 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D03 | 南濱DS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB | [17 empty] | 1-0A-04 |  | 1-0E | [5 empty] | 161KV_S | [8 empty] | 南濱DS.1770_CB | 1770(#3DTR) CB | MTR | D03/161/1770/CB |  |  |  | CDC | 657 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 350 | #3DTR(350) |  | CB | [17 empty] | 1-0B-02 |  | 1-22 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.350_CB | 350(#3DTR) CB | MTR | D03/22/350/CB |  |  |  | CDC | 658 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 3DTR | #3DTR |  | 51A | [17 empty] | 1-0B-00 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.#3DTR_51A | #3DTR 51RY | MTR | D03//3DTR/PHA |  |  |  | CDC | 659 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 3DTR | #3DTR |  | 51NA | [17 empty] | 1-0B-01 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.#3DTR_51NA | #3DTR 51N RY | MTR | D03//3DTR/GDA |  |  |  | CDC | 660 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 3DTR | #3DTR |  | 51ZA | [17 empty] | 1-0A-07 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.#3DTR_51ZA | #3DTR 51Z RY | MTR | D03//3DTR/51ZA |  |  |  | CDC | 661 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 3DTR | #3DTR |  | 87A | [17 empty] | 1-0A-05 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.#3DTR_87A | #3DTR 87RY | MTR | D03//3DTR/87A |  |  |  | CDC | 662 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 350 | #3DTR(350) |  | 51A | [17 empty] | 1-0B-03 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.350_51A | #3DTR二次側(350) 51RY | MTR | D03/22/350/51A |  |  |  | CDC | 663 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 3DTR | #3DTR |  | 96PA | [17 empty] | 1-0A-06 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.#3DTR_96PA | #3DTR 機械保護動作 | MTR | D03//3DTR/96PA |  |  |  | CDC | 664 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 3DTR | #3DTR |  | 96D | [17 empty] | 2-36-12 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#3DTR_96D | #3DTR 96D RY | MTR | D03//3DTR/96D |  |  |  | CDC | 665 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 3DTR | #3DTR |  | 96P | [17 empty] | 2-36-13 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#3DTR_96P | #3DTR 96P RY | MTR | D03//3DTR/96P |  |  |  | CDC | 666 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 3DTR | #3DTR |  | 63Q | [17 empty] | 2-36-14 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#3DTR_63Q | #3DTR 63Q RY | MTR | D03//3DTR/63Q |  |  |  | CDC | 667 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 3DTR | #3DTR |  | 96B1 | [17 empty] | 2-36-10 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#3DTR_96B1 | #3DTR 96B1 RY | MTR | D03//3DTR/96B1 |  |  |  | CDC | 668 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 3DTR | #3DTR |  | 96B2 | [17 empty] | 2-36-11 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#3DTR_96B2 | #3DTR 96B2 RY | MTR | D03//3DTR/96B2 |  |  |  | CDC | 669 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 3DTR | #3DTR |  | TRA | [17 empty] | 1-32-09 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#3DTR_TRA | #3DTR 重故障 | MTR | D03//3DTR/TRA |  |  |  | CDC | 670 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 3DTR | #3DTR |  | TRF | [17 empty] | 1-32-10 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#3DTR_TRF | #3DTR 輕故障 | MTR | D03//3DTR/TRF |  |  |  | CDC | 671 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 3DTR | #3DTR |  | SupLocal | [17 empty] | 1-32-07 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#3DTR_S/L | #3DTR OLTC S/L | MTR | D03//3DTR/SupLocal |  |  |  | CDC | 672 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D03 | 南濱DS | 0 |  | 3DTR | #3DTR |  | A_M | [17 empty] | 1-32-08 |  | 1-40 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.#3DTR_A/M | #3DTR OLTC A/M | MTR | D03//3DTR/Tap Chan |  |  |  | CDC | 673 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D03 | 南濱DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 | [16 empty] | 1-3D-12 | 1-3D-13 | 1-72 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1771_DS | 1771(#3DTR) DS | MTR | D03/161/1770/DS1 |  |  |  | CDC | 674 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 | [16 empty] | 1-3D-14 | 1-3D-15 | 1-73 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1772_DS | 1772(#3DTR) DS | MTR | D03/161/1770/DS2 |  |  |  | CDC | 675 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D03 | 南濱DS | 161 | 161kV | 1780 | #4DTR(1780) |  | CB | [17 empty] | 1-0B-06 |  | 1-0F | [5 empty] | 161KV_S | [8 empty] | 南濱DS.1780_CB | 1780(#4DTR) CB | MTR | D03/161/1780/CB |  |  |  | CDC | 676 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 370 | #4DTR(370) |  | CB | [17 empty] | 1-0C-04 |  | 1-23 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.370_CB | 370(#4DTR) CB | MTR | D03/22/370/CB |  |  |  | CDC | 677 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 4DTR | #4DTR |  | 51A | [17 empty] | 1-0C-02 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.#4DTR_51A | #4DTR 51RY | MTR | D03//4DTR/PHA |  |  |  | CDC | 678 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 4DTR | #4DTR |  | 51NA | [17 empty] | 1-0C-03 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.#4DTR_51NA | #4DTR 51N RY | MTR | D03//4DTR/GDA |  |  |  | CDC | 679 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 4DTR | #4DTR |  | 51ZA | [17 empty] | 1-0C-01 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.#4DTR_51ZA | #4DTR 51Z RY | MTR | D03//4DTR/51ZA |  |  |  | CDC | 680 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 4DTR | #4DTR |  | 87A | [17 empty] | 1-0B-07 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.#4DTR_87A | #4DTR 87RY | MTR | D03//4DTR/87A |  |  |  | CDC | 681 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 370 | #4DTR(370) |  | 51A | [17 empty] | 1-0C-05 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.370_51A | #4DTR二次側(370) 51RY | MTR | D03/22/370/51A |  |  |  | CDC | 682 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 4DTR | #4DTR |  | 96PA | [17 empty] | 1-0C-00 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.#4DTR_96PA | #4DTR 機械保護動作 | MTR | D03//4DTR/96PA |  |  |  | CDC | 683 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 4DTR | #4DTR |  | 96D | [17 empty] | 2-37-01 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#4DTR_96D | #4DTR 96D RY | MTR | D03//4DTR/96D |  |  |  | CDC | 684 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 4DTR | #4DTR |  | 96P | [17 empty] | 2-37-02 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#4DTR_96P | #4DTR 96P RY | MTR | D03//4DTR/96P |  |  |  | CDC | 685 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 4DTR | #4DTR |  | 63Q | [17 empty] | 2-37-03 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#4DTR_63Q | #4DTR 63Q RY | MTR | D03//4DTR/63Q |  |  |  | CDC | 686 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 4DTR | #4DTR |  | 96B1 | [17 empty] | 2-36-15 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#4DTR_96B1 | #4DTR 96B1 RY | MTR | D03//4DTR/96B1 |  |  |  | CDC | 687 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 4DTR | #4DTR |  | 96B2 | [17 empty] | 2-37-00 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#4DTR_96B2 | #4DTR 96B2 RY | MTR | D03//4DTR/96B2 |  |  |  | CDC | 688 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 4DTR | #4DTR |  | TRA | [17 empty] | 1-32-14 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#4DTR_TRA | #4DTR 重故障 | MTR | D03//4DTR/TRA |  |  |  | CDC | 689 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 4DTR | #4DTR |  | TRF | [17 empty] | 1-32-15 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#4DTR_TRF | #4DTR 輕故障 | MTR | D03//4DTR/TRF |  |  |  | CDC | 690 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 4DTR | #4DTR |  | SupLocal | [17 empty] | 1-32-12 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#4DTR_S/L | #4DTR OLTC S/L | MTR | D03//4DTR/SupLocal |  |  |  | CDC | 691 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D03 | 南濱DS | 0 |  | 4DTR | #4DTR |  | A_M | [17 empty] | 1-32-13 |  | 1-42 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.#4DTR_A/M | #4DTR OLTC A/M | MTR | D03//4DTR/Tap Chan |  |  |  | CDC | 692 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D03 | 南濱DS | 161 | 161kV | 1780 | #4DTR(1780) |  | DS1 | 1781 | [16 empty] | 1-3E-00 | 1-3E-01 | 1-74 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1781_DS | 1781(#4DTR) DS | MTR | D03/161/1780/DS1 |  |  |  | CDC | 693 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D03 | 南濱DS | 161 | 161kV | 1780 | #4DTR(1780) |  | DS2 | 1782 | [16 empty] | 1-3E-02 | 1-3E-03 | 1-75 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1782_DS | 1782(#4DTR) DS | MTR | D03/161/1780/DS2 |  |  |  | CDC | 694 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-14-00 |  | 1-11 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.210_CB | 210(11KV #1SC) CB | SC | D03/11/210/CB |  |  |  | CDC | 695 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M | [17 empty] | 2-30-00 |  | 2-23 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.210_A/M | 11KV #1SC 乏控器 A/M | SC | D03/11/210/SC_A_M |  |  |  | CDC | 696 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D03 | 南濱DS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-14-01 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.210_SCA | 11KV #1SC 51,51N RY | SC | D03/11/210/SCA |  |  |  | CDC | 697 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-14-02 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | D03/11/210/UVA |  |  |  | CDC | 698 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 210 | #1SC(210) |  | LBS | [17 empty] | 1-3E-04 | 1-3E-05 | 1-76 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.210_LBS | 210(11KV #1SC) LBS | SC | D03/11/210/LBS |  |  |  | CDC | 699 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 11 | 11kV | 210_LBS | #1SC |  | SC_A_M | [17 empty] | 2-30-01 |  | 2-24 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.210_LBS_A/M | 11KV #1SC LBS 乏控器 A/M | SC |  |  |  |  | CDC | 700 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D03 | 南濱DS | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 1-17-00 |  | 1-1A | [5 empty] | ADCS_S | [8 empty] | 南濱DS.220_CB | 220(11KV #2SC) CB | SC | D03/11/220/CB |  |  |  | CDC | 701 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M | [17 empty] | 2-30-12 |  | 2-2F | [5 empty] | ADCS_S | [8 empty] | 南濱DS.220_A/M | 11KV #2SC 乏控器 A/M | SC | D03/11/220/SC_A_M |  |  |  | CDC | 702 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D03 | 南濱DS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 1-17-01 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.220_SCA | 11KV #2SC 51,51N RY | SC | D03/11/220/SCA |  |  |  | CDC | 703 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 1-17-02 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | D03/11/220/UVA |  |  |  | CDC | 704 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 220 | #2SC(220) |  | LBS | [17 empty] | 1-3E-06 | 1-3E-07 | 1-77 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.220_LBS | 220(11KV #2SC) LBS | SC | D03/11/220/LBS |  |  |  | CDC | 705 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 11 | 11kV | 220_LBS | #2SC |  | SC_A_M | [17 empty] | 2-30-13 |  | 2-30 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.220_LBS_A/M | 11KV #2SC LBS 乏控器 A/M | SC |  |  |  |  | CDC | 706 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D03 | 南濱DS | 22 | 22kV | 250 | #5SC(250) |  | CB | [17 empty] | 2-04-07 |  | 2-0D | [5 empty] | ADCS_S | [8 empty] | 南濱DS.250_CB | 250(23KV #5SC) CB | SC | D03/22/250/CB |  |  |  | CDC | 707 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | 250 | #5SC(250) |  | SC_A_M | [17 empty] | 2-33-00 |  | 2-53 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.250_A/M | 23KV #5SC 乏控器 A/M | SC | D03/22/250/SC_A_M |  |  |  | CDC | 708 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D03 | 南濱DS | 22 | 22kV | 250 | #5SC(250) |  | SCA | [17 empty] | 2-05-00 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.250_SCA | 23KV #5SC 51,51N RY | SC | D03/22/250/SCA |  |  |  | CDC | 709 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | 250 | #5SC(250) |  | UVA | [17 empty] | 2-05-01 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.250_UVA | 23KV #5SC 27RY(欠壓) | SC | D03/22/250/UVA |  |  |  | CDC | 710 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | 260 | #6SC(260) |  | CB | [17 empty] | 2-08-02 |  | 2-16 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.260_CB | 260(23KV #6SC) CB | SC | D03/22/260/CB |  |  |  | CDC | 711 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | 260 | #6SC(260) |  | SC_A_M | [17 empty] | 2-34-01 |  | 2-64 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.260_A/M | 23KV #6SC 乏控器 A/M | SC | D03/22/260/SC_A_M |  |  |  | CDC | 712 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D03 | 南濱DS | 22 | 22kV | 260 | #6SC(260) |  | SCA | [17 empty] | 2-08-03 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.260_SCA | 23KV #6SC 51,51N RY | SC | D03/22/260/SCA |  |  |  | CDC | 713 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | 260 | #6SC(260) |  | UVA | [17 empty] | 2-08-04 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.260_UVA | 23KV #6SC 27RY(欠壓) | SC | D03/22/260/UVA |  |  |  | CDC | 714 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | 270 | #7SC(270) |  | CB | [17 empty] | 2-09-00 |  | 2-18 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.270_CB | 270(23KV #7SC) CB | SC | D03/22/270/CB |  |  |  | CDC | 715 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | 270 | #7SC(270) |  | SC_A_M | [17 empty] | 2-34-02 |  | 2-65 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.270_A/M | 23KV #7SC 乏控器 A/M | SC | D03/22/270/SC_A_M |  |  |  | CDC | 716 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D03 | 南濱DS | 22 | 22kV | 270 | #7SC(270) |  | SCA | [17 empty] | 2-09-01 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.270_SCA | 23KV #7SC 51,51N RY | SC | D03/22/270/SCA |  |  |  | CDC | 717 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | 270 | #7SC(270) |  | UVA | [17 empty] | 2-09-02 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.270_UVA | 23KV #7SC 27RY(欠壓) | SC | D03/22/270/UVA |  |  |  | CDC | 718 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | 280 | #8SC(280) |  | CB | [17 empty] | 2-0C-03 |  | 2-21 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.280_CB | 280(23KV #8SC) CB | SC | D03/22/280/CB |  |  |  | CDC | 719 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 22 | 22kV | 280 | #8SC(280) |  | SC_A_M | [17 empty] | 2-35-03 |  | 2-76 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.280_A/M | 23KV #8SC 乏控器 A/M | SC | D03/22/280/SC_A_M |  |  |  | CDC | 720 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D03 | 南濱DS | 22 | 22kV | 280 | #8SC(280) |  | SCA | [17 empty] | 2-0C-04 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.280_SCA | 23KV #8SC 51,51N RY | SC | D03/22/280/SCA |  |  |  | CDC | 721 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | 280 | #8SC(280) |  | UVA | [17 empty] | 2-0C-05 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.280_UVA | 23KV #8SC 27RY(欠壓) | SC | D03/22/280/UVA |  |  |  | CDC | 722 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1611BUS | #1BUS |  | VUA | [17 empty] | 1-35-10 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | D03/161/1BUS/BUS_VUA |  |  |  | CDC | 723 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1611BUS | #1BUS |  | 87A | [17 empty] | 1-06-04 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | D03/161/1BUS/87A |  |  |  | CDC | 724 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1611BUS | #1BUS |  | 87UL | [17 empty] | 1-31-06 |  | 1-7E | [5 empty] | ADCS_S | [8 empty] | 南濱DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | D03/161/1BUS/87UL |  |  |  | CDC | 725 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1612BUS | #2BUS |  | VUA | [17 empty] | 1-35-11 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | D03/161/2BUS/BUS_VUA |  |  |  | CDC | 726 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1612BUS | #2BUS |  | 87A | [17 empty] | 1-06-05 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | D03/161/2BUS/87A |  |  |  | CDC | 727 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1612BUS | #2BUS |  | 87UL | [17 empty] | 1-31-07 |  | 1-7F | [5 empty] | ADCS_S | [8 empty] | 南濱DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | D03/161/2BUS/87UL |  |  |  | CDC | 728 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 22 | 22kV | 11_ | 11/ |  | CBA | [17 empty] | 1-36-02 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | D03/0/ComPoint/FDR_CBA |  |  |  | CDC | 729 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | 11_ | 11/ |  | CBF | [17 empty] | 1-36-03 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | D03/0/ComPoint/FDR_CBF |  |  |  | CDC | 730 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV |  |  |  | CBA | [17 empty] | 1-35-06 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.161KV_CBA | 161KV斷路器重故障 | OTHER | D03/161/ComPoint/CBA |  |  |  | CDC | 731 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV |  |  |  | CBF | [17 empty] | 1-35-07 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | D03/161/ComPoint/CBF |  |  |  | CDC | 732 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV |  |  |  | OSCA | [17 empty] | 1-06-07 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.161KV_OSCA | 161KV示波器啟動警報 | OTHER | D03/161/ComPoint/OSCA |  |  |  | CDC | 733 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | LINE | LINE |  | RCA | [17 empty] | 1-06-06 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | D03/161/ComPoint/RCA |  |  |  | CDC | 734 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV |  |  |  | COMT | [17 empty] | 1-35-14 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.161空壓機COMT | 161KV空壓機運轉超時警報 | OTHER | D03/0/ComPoint/COMT |  |  |  | CDC | 735 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | _SC | 23/ SC |  | 60A | [17 empty] | 1-35-15 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.23KV_SC_60A | 23/11KV SC 60A | OTHER | D03/0/ComPoint/60A |  |  |  | CDC | 736 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.RTU_S/L | RTU SUPY/LOCAL | OTHER | D03/0/RTU/RTU_R_L |  |  |  | CDC | 737 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D03 | 南濱DS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.TEST_CB | TEST CB | OTHER | D03/0/RTU/Test_CB |  |  |  | CDC | 738 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  |  |  |  | Fire1 | [17 empty] | 1-34-04 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | D03/0/StaDev/Fire1 |  |  |  | CDC | 739 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  |  |  |  | Fire2 | [17 empty] | 1-34-05 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.火災警報(2) | 火災警報(2) | OTHER | D03/0/StaDev/Fire2 |  |  |  | CDC | 740 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  |  |  |  | Fire3 | [17 empty] | 1-34-06 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.火災警報(3) | 火災警報(3) | OTHER | D03/0/StaDev/Fire3 |  |  |  | CDC | 741 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  |  |  |  | Fire4 | [17 empty] | 1-34-07 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.火災警報(4) | 火災警報(4) | OTHER | D03/0/StaDev/Fire4 |  |  |  | CDC | 742 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  |  |  |  | 火災警報(5) | [17 empty] | 1-34-08 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.火災警報(5) | 火災警報(5) | OTHER | D03/0/StaDev/Fire5 |  |  |  | CDC | 743 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  |  |  |  | OPA | [17 empty] | 1-35-02 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | D03/0/ComPoint/OPA |  |  |  | CDC | 744 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  |  |  |  | 25PFA | [17 empty] | 1-36-12 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER | D03/0/ComPoint/25PFA |  |  |  | CDC | 745 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  |  |  |  | 25TA | [17 empty] | 1-36-13 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | D03/0/ComPoint/25TA |  |  |  | CDC | 746 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  |  |  |  | SUBA | [17 empty] | 1-36-01 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.其他重故障 | 變電所內其他重故障 | OTHER | D03/0/StaDev/PSF |  |  |  | CDC | 747 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  |  |  |  | SUBF | [17 empty] | 1-36-00 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.其他輕故障 | 變電所內其他輕故障 | OTHER | D03/0/StaDev/PSA |  |  |  | CDC | 748 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  |  |  |  | ACB1 | [17 empty] | 1-35-03 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | D03/0/StaDev/ACB1 |  |  |  | CDC | 749 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
D03 | 南濱DS | 0 |  |  |  |  | ACB2 | [17 empty] | 1-35-04 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | D03/0/StaDev/ACB2 |  |  |  | CDC | 750 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
D03 | 南濱DS | 0 |  |  |  |  | ACBA | [17 empty] | 1-35-09 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.所內電源ACBA | 所內電源故障警報 | OTHER | D03/0/StaDev/ACBA |  |  |  | CDC | 751 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  |  |  |  | STUV | [17 empty] | 1-35-05 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | D03/0/StaDev/STUV |  |  |  | CDC | 752 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-35-12 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | D03/0/StaDev/CHG1 |  |  |  | CDC | 753 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  |  |  |  | DCA | [17 empty] | 1-35-08 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.直流電源DCA | 直流電源故障警報 | OTHER | D03/0/StaDev/DCA |  |  |  | CDC | 754 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  |  |  |  | DCE | [17 empty] | 1-35-13 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.直流電源DCE | 直流電源接地故障警報 | OTHER | D03/0/StaDev/DCE |  |  |  | CDC | 755 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-36-07 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | D03/0/StaDev/CHG2 |  |  |  | CDC | 756 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  |  |  |  | CommACF | [17 empty] | 1-36-08 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | D03/0/StaDev/CommACF |  |  |  | CDC | 757 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  |  |  |  | Burglar1 | [17 empty] | 1-34-11 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.無人化防盜(1) | 無人化防盜(1)保全警報 | OTHER | D03/0/StaDev/Door3 |  |  |  | CDC | 758 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  |  |  |  | Burglar2 | [17 empty] | 1-34-12 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.無人化防盜(2) | 無人化防盜(2) | OTHER | D03/0/StaDev/Door4 |  |  |  | CDC | 759 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  |  |  |  | Burglar3 | [17 empty] | 1-34-13 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.無人化防盜(3) | 無人化防盜(3) | OTHER | D03/0/StaDev/Door5 |  |  |  | CDC | 760 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  |  |  |  | Door1 | [17 empty] | 1-34-09 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.無人化門禁(1) | 無人化門禁(1)1樓門禁警報 | OTHER | D03/0/StaDev/Door1 |  |  |  | CDC | 761 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  |  |  |  | Door2 | [17 empty] | 1-34-10 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.無人化門禁(2) | 無人化門禁(2)控制室門禁警報 | OTHER | D03/0/StaDev/Door2 |  |  |  | CDC | 762 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 1510 | 安南南濱一路(1510) |  | 87LA | [17 empty] | 1-33-00 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.1510_87LA | 安南南濱一路(1510) RY/DC故障 | OTHER | D03/161/1510/RYFA |  |  |  | CDC | 763 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 1510 | 安南南濱一路(1510) |  | RAOA | [17 empty] | 1-33-01 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.1510_RAOA | 安南南濱一路(1510) 87L通訊故障 | OTHER | D03/161/1510/85CFA |  |  |  | CDC | 764 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 1520 | 安南南濱二路(1520) |  | 87LA | [17 empty] | 1-33-02 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.1520_87LA | 安南南濱二路(1520) RY/DC故障 | OTHER | D03/161/1520/RYFA |  |  |  | CDC | 765 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 1520 | 安南南濱二路(1520) |  | RAOA | [17 empty] | 1-33-03 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.1520_RAOA | 安南南濱二路(1520) 87L通訊故障 | OTHER | D03/161/1520/85CFA |  |  |  | CDC | 766 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 310 | #1DTR(310) |  | GDA | [17 empty] | 1-08-01 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.310_GDA | 310開關箱IED RY GDA | OTHER | D03/11/310/GDA |  |  |  | CDC | 767 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 310 | #1DTR(310) |  | PHA2 | [17 empty] | 1-08-00 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.310_PHA2 | 310開關箱IED RY PHA | OTHER | D03/11/310/PHA |  |  |  | CDC | 768 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 320 | #1DTR(320) |  | GDA | [17 empty] | 1-08-05 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.320_GDA | 320開關箱IED RY GDA | OTHER | D03/11/320/GDA |  |  |  | CDC | 769 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 320 | #1DTR(320) |  | PHA2 | [17 empty] | 1-08-04 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.320_PHA2 | 320開關箱IED RY PHA | OTHER | D03/11/320/PHA |  |  |  | CDC | 770 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 350 | #3DTR(350) |  | GDA | [17 empty] | 1-0B-05 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.350_GDA | 350開關箱IED RY GDA | OTHER | D03/22/350/GDA |  |  |  | CDC | 771 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 350 | #3DTR(350) |  | PHA2 | [17 empty] | 1-0B-04 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.350_PHA2 | 350開關箱IED RY PHA | OTHER | D03/22/350/PHA |  |  |  | CDC | 772 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  |  |  |  | 水位警報(1) | [17 empty] | 1-36-14 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.水位警報(1) | 地下室水位警報(1) | OTHER | D03/0/StaDev/Water1 |  |  |  | CDC | 773 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  |  |  |  | 水位警報(2) | [17 empty] | 1-36-15 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.水位警報(2) | 地下室水位警報(2) | OTHER | D03/0/StaDev/Water2 |  |  |  | CDC | 774 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  |  |  |  | 空調機故障 | [17 empty] | 1-35-00 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.空調機故障 | 空調機故障或電源跳脫 | OTHER | D03/0/StaDev/AIRCON |  |  |  | CDC | 775 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | NORMAL/FAULT | NORMAL
D03 | 南濱DS | 0 |  |  |  |  | OilLeak1 | [17 empty] | 1-36-05 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.洩油池警報(1) | 洩油池水位警報(1) | OTHER | D03/0/StaDev/OilLeak1 |  |  |  | CDC | 776 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  |  |  |  | OilLeak2 | [17 empty] | 1-36-06 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.洩油池警報(2) | 洩油池水位警報(2) | OTHER | D03/0/StaDev/OilLeak2 |  |  |  | CDC | 777 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB | [17 empty] | 1-08-06 |  | 1-0D | [5 empty] | 161KV_S | [8 empty] | 南濱DS.1760_CB | 1760(#2DTR) CB | MTR | D03/161/1760/CB |  |  |  | CDC | 778 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 | [16 empty] | 1-3D-08 | 1-3D-09 | 1-70 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1761_DS | 1761(#2DTR) DS | MTR | D03/161/1760/DS1 |  |  |  | CDC | 779 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D03 | 南濱DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 | [16 empty] | 1-3D-10 | 1-3D-11 | 1-71 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1762_DS | 1762(#2DTR) DS | MTR | D03/161/1760/DS2 |  |  |  | CDC | 780 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 0 |  | 370 | #4DTR(370) |  | GDA | [17 empty] | 1-0C-07 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.370_GDA | 370開關箱IED RY GDA | OTHER | D03/22/370/GDA |  |  |  | CDC | 781 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 370 | #4DTR(370) |  | PHA2 | [17 empty] | 1-0C-06 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.370_PHA2 | 370開關箱IED RY PHA | OTHER | D03/22/370/PHA |  |  |  | CDC | 782 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  |  |  |  | 水位警報(3) | [17 empty] | 1-37-00 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.水位警報(3) | 電纜涵洞水位警報 | OTHER | D03/0/StaDev/Water3 |  |  |  | CDC | 783 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 1500TIE | 1500 |  | 50SA | [17 empty] | 1-35-01 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | D03/161/BUS/50SA |  |  |  | CDC | 784 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | TEST/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱安瀚線(1530) |  | 87A1 | [17 empty] | 1-01-03 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.1530_87A1 | 南濱安瀚線(1530) 第一套 87RY | LINE161 | D03/161/1530/87A1 |  |  |  | CDC | 785 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱安瀚線(1530) |  | 87A2 | [17 empty] | 1-01-04 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.1530_87A2 | 南濱安瀚線(1530) 第二套 87RY | LINE161 | D03/161/1530/87A2 |  |  |  | CDC | 786 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱安瀚線(1530) |  | 1_87UL1 | [17 empty] | 1-30-06 |  | 1-28 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1530_87UL1 | 安瀚線(1530) 第一套 87RY U/L | LINE161 | D03/161/1530/1_87UL1 |  |  |  | CDC | 787 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱安瀚線(1530) |  | 1_87UL2 | [17 empty] | 1-37-06 |  | 1-7C | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1530_87UL2 | 安瀚線(1530) 第二套 87RY U/L | LINE161 | D03/161/1530/1_87UL2 |  |  |  | CDC | 788 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱凸版線(1540) |  | 87A1 | [17 empty] | 1-02-00 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.1540_87A1 | 南濱凸版線(1540) 第一套 87RY | LINE161 | D03/161/1540/87A1 |  |  |  | CDC | 789 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱凸版線(1540) |  | 87A2 | [17 empty] | 1-02-01 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.1540_87A2 | 南濱凸版線(1540) 第二套 87RY | LINE161 | D03/161/1540/87A2 |  |  |  | CDC | 790 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱凸版線(1540) |  | 1_87UL1 | [17 empty] | 1-30-08 |  | 1-2A | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1540_87UL1 | 凸版線(1540) 第一套 87RY U/L | LINE161 | D03/161/1540/1_87UL1 |  |  |  | CDC | 791 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱凸版線(1540) |  | 1_87UL2 | [17 empty] | 1-37-07 |  | 1-7D | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1540_87UL2 | 凸版線(1540) 第二套 87RY U/L | LINE161 | D03/161/1540/1_87UL2 |  |  |  | CDC | 792 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 0 |  | 1530 | 南濱安瀚線(1530) |  | 187LA | [17 empty] | 1-33-04 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.1530_187LA | 南濱安瀚線(1530) 1RY/DC故障 | OTHER | D03/161/1530/RYFA1 |  |  |  | CDC | 793 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 1530 | 南濱安瀚線(1530) |  | 1RAOA | [17 empty] | 1-33-05 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.1530_1RAOA | 南濱安瀚線(1530) 187L通訊故障 | OTHER | D03/161/1530/87CFA1 |  |  |  | CDC | 794 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 1530 | 南濱安瀚線(1530) |  | 287LA | [17 empty] | 1-37-02 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.1530_287LA | 南濱安瀚線(1530) 2RY/DC故障 | OTHER | D03/161/1530/RYFA2 |  |  |  | CDC | 795 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 1530 | 南濱安瀚線(1530) |  | 2RAOA | [17 empty] | 1-37-03 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.1530_2RAOA | 南濱安瀚線(1530) 287L通訊故障 | OTHER | D03/161/1530/87CFA2 |  |  |  | CDC | 796 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 1540 | 南濱凸版線(1540) |  | 187LA | [17 empty] | 1-33-06 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.1540_187LA | 南濱凸版線(1540) 1RY/DC故障 | OTHER | D03/161/1540/RYFA1 |  |  |  | CDC | 797 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 1540 | 南濱凸版線(1540) |  | 1RAOA | [17 empty] | 1-33-07 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.1540_1RAOA | 南濱凸版線(1540) 187L通訊故障 | OTHER | D03/161/1540/87CFA1 |  |  |  | CDC | 798 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 1540 | 南濱凸版線(1540) |  | 287LA | [17 empty] | 1-37-04 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.1540_287LA | 南濱凸版線(1540) 2RY/DC故障 | OTHER | D03/161/1540/RYFA2 |  |  |  | CDC | 799 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 1540 | 南濱凸版線(1540) |  | 2RAOA | [17 empty] | 1-37-05 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.1540_2RAOA | 南濱凸版線(1540) 287L通訊故障 | OTHER | D03/161/1540/87CFA2 |  |  |  | CDC | 800 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  |  |  |  | 通信機房溫度 | [17 empty] | 1-36-11 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.通信機房溫度 | 通信機房溫度警報 | OTHER | D03/0/StaDev/R_Temp |  |  |  | CDC | 801 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV |  |  |  | OSCF | [17 empty] | 1-37-01 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | D03/161/ComPoint/OSCF |  |  |  | CDC | 802 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  |  |  |  | PMA | [17 empty] | 1-37-08 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.PMA | 電力量測表計故障 | OTHER | D03/0/StaDev/PMA |  |  |  | CDC | 803 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1550 | 南濱鹿耳紅線(1550) |  | PHA | [17 empty] | 1-02-07 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.1550_PHA | 南濱鹿耳紅線(1550) 相間RY | LINE161 | D03/161/1550/PHA |  |  |  | CDC | 804 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1550 | 南濱鹿耳紅線(1550) |  | GDA | [17 empty] | 1-03-00 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.1550_GDA | 南濱鹿耳紅線(1550) 接地RY | LINE161 | D03/161/1550/GDA |  |  |  | CDC | 805 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1550 | 南濱鹿耳紅線(1550) |  | 87A | [17 empty] | 1-02-05 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.1550_87A | 南濱鹿耳紅線(1550) 87RY | LINE161 | D03/161/1550/87A |  |  |  | CDC | 806 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1550 | 南濱鹿耳紅線(1550) |  | 87UL | [17 empty] | 1-30-10 |  | 1-2C | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1550_87UL | 南濱鹿耳紅線(1550) 87RY U/L | LINE161 | D03/161/1550/87UL |  |  |  | CDC | 807 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1550 | 南濱鹿耳紅線(1550) |  | CB | [17 empty] | 1-02-04 |  | 1-05 | [5 empty] | 161KV_S | [8 empty] | 南濱DS.1550_CB | 1550(南濱鹿耳紅線) CB | LINE161 | D03/161/1550/CB |  |  |  | CDC | 808 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 161 | 161kV | 1550 | 南濱鹿耳紅線(1550) |  | 79UL | [17 empty] | 1-30-11 |  | 1-2D | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1550_79UL | 南濱鹿耳紅線(1550) 79RY U/L | LINE161 | D03/161/1550/79UL |  |  |  | CDC | 809 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1550 | 南濱鹿耳紅線(1550) |  | DS1 | 1551 | [16 empty] | 1-3A-00 | 1-3A-01 | 1-54 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1551_DS | 1551(南濱鹿耳紅線) DS | LINE161 | D03/161/1550/DS1 |  |  |  | CDC | 810 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 161 | 161kV | 1550 | 南濱鹿耳紅線(1550) |  | DS2 | 1552 | [16 empty] | 1-3A-02 | 1-3A-03 | 1-55 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1552_DS | 1552(南濱鹿耳紅線) DS | LINE161 | D03/161/1550/DS2 |  |  |  | CDC | 811 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D03 | 南濱DS | 161 | 161kV | 1550 | 南濱鹿耳紅線(1550) |  | DS3 | 1553 | [16 empty] | 1-3A-04 | 1-3A-05 | 1-56 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1553_DS | 1553(南濱鹿耳紅線) DS | LINE161 | D03/161/1550/DS3 |  |  |  | CDC | 812 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 161 | 161kV | 1550 | 南濱鹿耳紅線(1550) |  | E3 | 1553E | [16 empty] | 1-3A-06 | 1-3A-07 | 1-57 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1553E_ES | 1553E(南濱鹿耳紅線) ES | LINE161 | D03/161/1550/ES3 |  |  |  | CDC | 813 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D03 | 南濱DS | 161 | 161kV | 1560 | 南濱鹿耳白線(1560) |  | PHA | [17 empty] | 1-03-04 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.1560_PHA | 南濱鹿耳白線(1560) 相間RY | LINE161 | D03/161/1560/PHA |  |  |  | CDC | 814 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1560 | 南濱鹿耳白線(1560) |  | GDA | [17 empty] | 1-03-05 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.1560_GDA | 南濱鹿耳白線(1560) 接地RY | LINE161 | D03/161/1560/GDA |  |  |  | CDC | 815 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1560 | 南濱鹿耳白線(1560) |  | 87A | [17 empty] | 1-03-02 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.1560_87A | 南濱鹿耳白線(1560) 87RY | LINE161 | D03/161/1560/87A |  |  |  | CDC | 816 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1560 | 南濱鹿耳白線(1560) |  | 87UL | [17 empty] | 1-30-12 |  | 1-2E | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1560_87UL | 南濱鹿耳白線(1560) 87RY U/L | LINE161 | D03/161/1560/87UL |  |  |  | CDC | 817 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1560 | 南濱鹿耳白線(1560) |  | CB | [17 empty] | 1-03-01 |  | 1-06 | [5 empty] | 161KV_S | [8 empty] | 南濱DS.1560_CB | 1560(南濱鹿耳白線) CB | LINE161 | D03/161/1560/CB |  |  |  | CDC | 818 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 161 | 161kV | 1560 | 南濱鹿耳白線(1560) |  | 79UL | [17 empty] | 1-30-13 |  | 1-2F | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1560_79UL | 南濱鹿耳白線(1560) 79RY U/L | LINE161 | D03/161/1560/79UL |  |  |  | CDC | 819 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1560 | 南濱鹿耳白線(1560) |  | DS1 | 1561 | [16 empty] | 1-3A-08 | 1-3A-09 | 1-58 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1561_DS | 1561(南濱鹿耳白線) DS | LINE161 | D03/161/1560/DS1 |  |  |  | CDC | 820 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D03 | 南濱DS | 161 | 161kV | 1560 | 南濱鹿耳白線(1560) |  | DS2 | 1562 | [16 empty] | 1-3A-10 | 1-3A-11 | 1-59 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1562_DS | 1562(南濱鹿耳白線) DS | LINE161 | D03/161/1560/DS2 |  |  |  | CDC | 821 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 161 | 161kV | 1560 | 南濱鹿耳白線(1560) |  | DS3 | 1563 | [16 empty] | 1-3A-12 | 1-3A-13 | 1-5A | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1563_DS | 1563(南濱鹿耳白線) DS | LINE161 | D03/161/1560/DS3 |  |  |  | CDC | 822 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 161 | 161kV | 1560 | 南濱鹿耳白線(1560) |  | E3 | 1563E | [16 empty] | 1-3A-14 | 1-3A-15 | 1-5B | [5 empty] | ADCS_S | [8 empty] | 南濱DS.1563E_ES | 1563E(南濱鹿耳白線) ES | LINE161 | D03/161/1560/ES3 |  |  |  | CDC | 823 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D03 | 南濱DS | 0 |  | 1550 | 南濱鹿耳紅線(1550) |  | 87CFA | [17 empty] | 1-33-08 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.1550_87CFA | 南濱鹿耳紅線(1550)87RY通訊故障 | OTHER | D03/161/1550/87CFA |  |  |  | CDC | 824 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 1550 | 南濱鹿耳紅線(1550) |  | RYFA | [17 empty] | 1-33-09 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.1550_RYFA | 南濱鹿耳紅線(1550)數位電驛故障 | OTHER | D03/161/1550/RYFA |  |  |  | CDC | 825 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 1560 | 南濱鹿耳白線(1560) |  | 87CFA | [17 empty] | 1-33-10 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.1560_87CFA | 南濱鹿耳白線(1560)87RY通訊故障 | OTHER | D03/161/1560/87CFA |  |  |  | CDC | 826 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 1560 | 南濱鹿耳白線(1560) |  | RYFA | [17 empty] | 1-33-11 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.1560_RYFA | 南濱鹿耳白線(1560)數位電驛故障 | OTHER | D03/161/1560/RYFA |  |  |  | CDC | 827 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | BVS | BVS |  | RY | [17 empty] | 1-37-09 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.BVS_RY | BVS GRZ100 RY U/L | OTHER | D03/0/ComPoint/GRZ100 |  |  |  | CDC | 828 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | LOCK/USE | USE
D03 | 南濱DS | 11 | 11kV | K321 | 濱21線(K321) |  | PHA | [17 empty] | 2-00-04 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K321_PHA | 11KV濱21線(K321) 相間RY | FEEDER | D03/11/K321/PHA |  |  |  | CDC | 829 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K321 | 濱21線(K321) |  | GDA | [17 empty] | 2-00-05 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K321_GDA | 11KV濱21線(K321) 接地RY | FEEDER | D03/11/K321/GDA |  |  |  | CDC | 830 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K321 | 濱21線(K321) 79RY |  | 79UL | [17 empty] | 2-31-10 |  | 2-3D | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K321_79UL | 11KV濱21線(K321) 79RY U/L | FEEDER | D03/11/K321/79UL |  |  |  | CDC | 831 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K321_LCO | 濱21線(K321) LCO |  | TapPosMv | [17 empty] | 2-31-11 |  | 2-3E | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K321_LCO_TAP | 11KV濱21線(K321) LCO TAP | FEEDER | D03/11/K321/50_51NUL |  |  |  | CDC | 832 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K321 | K321(11KV濱21線) |  | CB | [17 empty] | 2-00-03 |  | 2-01 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K321_CB | K321(11KV濱21線) CB | FEEDER | D03/11/K321/CB |  |  |  | CDC | 833 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K322 | 濱22線(K322) |  | PHA | [17 empty] | 2-00-07 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K322_PHA | 11KV濱22線(K322) 相間RY | FEEDER | D03/11/K322/PHA |  |  |  | CDC | 834 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K322 | 濱22線(K322) |  | GDA | [17 empty] | 2-01-00 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K322_GDA | 11KV濱22線(K322) 接地RY | FEEDER | D03/11/K322/GDA |  |  |  | CDC | 835 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K322 | 濱22線(K322) 79RY |  | 79UL | [17 empty] | 2-31-12 |  | 2-3F | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K322_79UL | 11KV濱22線(K322) 79RY U/L | FEEDER | D03/11/K322/79UL |  |  |  | CDC | 836 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K322_LCO | 濱22線(K322) LCO |  | TapPosMv | [17 empty] | 2-31-13 |  | 2-40 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K322_LCO_TAP | 11KV濱22線(K322) LCO TAP | FEEDER | D03/11/K322/50_51NUL |  |  |  | CDC | 837 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K322 | K322(11KV濱22線) |  | CB | [17 empty] | 2-00-06 |  | 2-02 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K322_CB | K322(11KV濱22線) CB | FEEDER | D03/11/K322/CB |  |  |  | CDC | 838 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K323 | 濱23線(K323) |  | PHA | [17 empty] | 2-01-02 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K323_PHA | 11KV濱23線(K323) 相間RY | FEEDER | D03/11/K323/PHA |  |  |  | CDC | 839 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K323 | 濱23線(K323) |  | GDA | [17 empty] | 2-01-03 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K323_GDA | 11KV濱23線(K323) 接地RY | FEEDER | D03/11/K323/GDA |  |  |  | CDC | 840 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K323 | 濱23線(K323) 79RY |  | 79UL | [17 empty] | 2-31-14 |  | 2-41 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K323_79UL | 11KV濱23線(K323) 79RY U/L | FEEDER | D03/11/K323/79UL |  |  |  | CDC | 841 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K323_LCO | 濱23線(K323) LCO |  | TapPosMv | [17 empty] | 2-31-15 |  | 2-42 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K323_LCO_TAP | 11KV濱23線(K323) LCO TAP | FEEDER | D03/11/K323/50_51NUL |  |  |  | CDC | 842 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K323 | K323(11KV濱23線) |  | CB | [17 empty] | 2-01-01 |  | 2-03 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K323_CB | K323(11KV濱23線) CB | FEEDER | D03/11/K323/CB |  |  |  | CDC | 843 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K324 | 濱24線(K324) |  | PHA | [17 empty] | 2-01-05 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K324_PHA | 11KV濱24線(K324) 相間RY | FEEDER | D03/11/K324/PHA |  |  |  | CDC | 844 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K324 | 濱24線(K324) |  | GDA | [17 empty] | 2-01-06 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K324_GDA | 11KV濱24線(K324) 接地RY | FEEDER | D03/11/K324/GDA |  |  |  | CDC | 845 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K324 | 濱24線(K324) 79RY |  | 79UL | [17 empty] | 2-32-00 |  | 2-43 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K324_79UL | 11KV濱24線(K324) 79RY U/L | FEEDER | D03/11/K324/79UL |  |  |  | CDC | 846 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K324_LCO | 濱24線(K324) LCO |  | TapPosMv | [17 empty] | 2-32-01 |  | 2-44 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K324_LCO_TAP | 11KV濱24線(K324) LCO TAP | FEEDER | D03/11/K324/50_51NUL |  |  |  | CDC | 847 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K324 | K324(11KV濱24線) |  | CB | [17 empty] | 2-01-04 |  | 2-04 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K324_CB | K324(11KV濱24線) CB | FEEDER | D03/11/K324/CB |  |  |  | CDC | 848 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K325 | 濱25線(K325) |  | PHA | [17 empty] | 2-02-00 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K325_PHA | 11KV濱25線(K325) 相間RY | FEEDER | D03/11/K325/PHA |  |  |  | CDC | 849 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K325 | 濱25線(K325) |  | GDA | [17 empty] | 2-02-01 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K325_GDA | 11KV濱25線(K325) 接地RY | FEEDER | D03/11/K325/GDA |  |  |  | CDC | 850 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K325 | 濱25線(K325) 79RY |  | 79UL | [17 empty] | 2-32-02 |  | 2-45 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K325_79UL | 11KV濱25線(K325) 79RY U/L | FEEDER | D03/11/K325/79UL |  |  |  | CDC | 851 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K325_LCO | 濱25線(K325) LCO |  | TapPosMv | [17 empty] | 2-32-03 |  | 2-46 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K325_LCO_TAP | 11KV濱25線(K325) LCO TAP | FEEDER | D03/11/K325/50_51NUL |  |  |  | CDC | 852 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K325 | K325(11KV濱25線) |  | CB | [17 empty] | 2-01-07 |  | 2-05 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K325_CB | K325(11KV濱25線) CB | FEEDER | D03/11/K325/CB |  |  |  | CDC | 853 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K326 | 濱26線(K326) |  | PHA | [17 empty] | 2-02-06 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K326_PHA | 11KV濱26線(K326) 相間RY | FEEDER | D03/11/K326/PHA |  |  |  | CDC | 854 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K326 | 濱26線(K326) |  | GDA | [17 empty] | 2-02-07 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K326_GDA | 11KV濱26線(K326) 接地RY | FEEDER | D03/11/K326/GDA |  |  |  | CDC | 855 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K326 | 濱26線(K326) 79RY |  | 79UL | [17 empty] | 2-32-06 |  | 2-49 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K326_79UL | 11KV濱26線(K326) 79RY U/L | FEEDER | D03/11/K326/79UL |  |  |  | CDC | 856 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K326_LCO | 濱26線(K326) LCO |  | TapPosMv | [17 empty] | 2-32-07 |  | 2-4A | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K326_LCO_TAP | 11KV濱26線(K326) LCO TAP | FEEDER | D03/11/K326/50_51NUL |  |  |  | CDC | 857 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K326 | K326(11KV濱26線) |  | CB | [17 empty] | 2-02-05 |  | 2-08 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K326_CB | K326(11KV濱26線) CB | FEEDER | D03/11/K326/CB |  |  |  | CDC | 858 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K327 | 濱27線(K327) |  | PHA | [17 empty] | 2-03-01 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K327_PHA | 11KV濱27線(K327) 相間RY | FEEDER | D03/11/K327/PHA |  |  |  | CDC | 859 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K327 | 濱27線(K327) |  | GDA | [17 empty] | 2-03-02 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K327_GDA | 11KV濱27線(K327) 接地RY | FEEDER | D03/11/K327/GDA |  |  |  | CDC | 860 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K327 | 濱27線(K327) 79RY |  | 79UL | [17 empty] | 2-32-08 |  | 2-4B | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K327_79UL | 11KV濱27線(K327) 79RY U/L | FEEDER | D03/11/K327/79UL |  |  |  | CDC | 861 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K327_LCO | 濱27線(K327) LCO |  | TapPosMv | [17 empty] | 2-32-09 |  | 2-4C | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K327_LCO_TAP | 11KV濱27線(K327) LCO TAP | FEEDER | D03/11/K327/50_51NUL |  |  |  | CDC | 862 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K327 | K327(11KV濱27線) |  | CB | [17 empty] | 2-03-00 |  | 2-09 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K327_CB | K327(11KV濱27線) CB | FEEDER | D03/11/K327/CB |  |  |  | CDC | 863 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K328 | 濱28線(K328) |  | PHA | [17 empty] | 2-03-04 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K328_PHA | 11KV濱28線(K328) 相間RY | FEEDER | D03/11/K328/PHA |  |  |  | CDC | 864 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K328 | 濱28線(K328) |  | GDA | [17 empty] | 2-03-05 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K328_GDA | 11KV濱28線(K328) 接地RY | FEEDER | D03/11/K328/GDA |  |  |  | CDC | 865 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K328 | 濱28線(K328) 79RY |  | 79UL | [17 empty] | 2-32-10 |  | 2-4D | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K328_79UL | 11KV濱28線(K328) 79RY U/L | FEEDER | D03/11/K328/79UL |  |  |  | CDC | 866 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K328_LCO | 濱28線(K328) LCO |  | TapPosMv | [17 empty] | 2-32-11 |  | 2-4E | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K328_LCO_TAP | 11KV濱28線(K328) LCO TAP | FEEDER | D03/11/K328/50_51NUL |  |  |  | CDC | 867 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K328 | K328(11KV濱28線) |  | CB | [17 empty] | 2-03-03 |  | 2-0A | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K328_CB | K328(11KV濱28線) CB | FEEDER | D03/11/K328/CB |  |  |  | CDC | 868 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K329 | 濱29線(K329) |  | PHA | [17 empty] | 2-03-07 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K329_PHA | 11KV濱29線(K329) 相間RY | FEEDER | D03/11/K329/PHA |  |  |  | CDC | 869 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K329 | 濱29線(K329) |  | GDA | [17 empty] | 2-04-00 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K329_GDA | 11KV濱29線(K329) 接地RY | FEEDER | D03/11/K329/GDA |  |  |  | CDC | 870 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K329 | 濱29線(K329) 79RY |  | 79UL | [17 empty] | 2-32-12 |  | 2-4F | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K329_79UL | 11KV濱29線(K329) 79RY U/L | FEEDER | D03/11/K329/79UL |  |  |  | CDC | 871 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K329_LCO | 濱29線(K329) LCO |  | TapPosMv | [17 empty] | 2-32-13 |  | 2-50 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K329_LCO_TAP | 11KV濱29線(K329) LCO TAP | FEEDER | D03/11/K329/50_51NUL |  |  |  | CDC | 872 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K329 | K329(11KV濱29線) |  | CB | [17 empty] | 2-03-06 |  | 2-0B | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K329_CB | K329(11KV濱29線) CB | FEEDER | D03/11/K329/CB |  |  |  | CDC | 873 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | K330 | 濱30線(K330) |  | PHA | [17 empty] | 2-04-02 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K330_PHA | 11KV濱30線(K330) 相間RY | FEEDER | D03/11/K330/PHA |  |  |  | CDC | 874 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K330 | 濱30線(K330) |  | GDA | [17 empty] | 2-04-03 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.K330_GDA | 11KV濱30線(K330) 接地RY | FEEDER | D03/11/K330/GDA |  |  |  | CDC | 875 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | K330 | 濱30線(K330) 79RY |  | 79UL | [17 empty] | 2-32-14 |  | 2-51 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K330_79UL | 11KV濱30線(K330) 79RY U/L | FEEDER | D03/11/K330/79UL |  |  |  | CDC | 876 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 11 | 11kV | K330_LCO | 濱30線(K330) LCO |  | TapPosMv | [17 empty] | 2-32-15 |  | 2-52 | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K330_LCO_TAP | 11KV濱30線(K330) LCO TAP | FEEDER | D03/11/K330/50_51NUL |  |  |  | CDC | 877 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D03 | 南濱DS | 11 | 11kV | K330 | K330(11KV濱30線) |  | CB | [17 empty] | 2-04-01 |  | 2-0C | [5 empty] | DDCS4_1 | [8 empty] | 南濱DS.K330_CB | K330(11KV濱30線) CB | FEEDER | D03/11/K330/CB |  |  |  | CDC | 878 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 200 | TIE(200) |  | CB | [17 empty] | 2-04-04 |  | 2-06 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.200_CB | 200(TIE) CB | TIE | D03/11/200/CB |  |  |  | CDC | 879 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 200 | TIE(200) |  | 51A | [17 empty] | 2-04-05 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.200_51A | 11KV TIE(200) 51RY | TIE | D03/11/200/PHA |  |  |  | CDC | 880 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 200 | TIE(200) |  | 51NA | [17 empty] | 2-04-06 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.200_51NA | 11KV TIE(200) 51N RY | TIE | D03/11/200/GDA |  |  |  | CDC | 881 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 330 | #2DTR(330) |  | CB | [17 empty] | 1-09-04 |  | 1-20 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.330_CB | 330(#2DTR) CB | MTR | D03/11/330/CB |  |  |  | CDC | 882 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 2DTR | #2DTR |  | 51ZA | [17 empty] | 1-09-01 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | D03//2DTR/51ZA |  |  |  | CDC | 883 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 2DTR | #2DTR |  | 87A | [17 empty] | 1-08-07 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.#2DTR_87A | #2DTR 87RY | MTR | D03//2DTR/87A |  |  |  | CDC | 884 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 2DTR | #2DTR |  | 96PA | [17 empty] | 1-09-00 | [7 empty] | 161KV_S | [8 empty] | 南濱DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | D03//2DTR/96PA |  |  |  | CDC | 885 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 2DTR | #2DTR |  | 96D | [17 empty] | 2-36-07 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#2DTR_96D | #2DTR 96D RY | MTR | D03//2DTR/96D |  |  |  | CDC | 886 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 2DTR | #2DTR |  | 96P | [17 empty] | 2-36-08 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#2DTR_96P | #2DTR 96P RY | MTR | D03//2DTR/96P |  |  |  | CDC | 887 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 2DTR | #2DTR |  | 63Q | [17 empty] | 2-36-09 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#2DTR_63Q | #2DTR 63Q RY | MTR | D03//2DTR/63Q |  |  |  | CDC | 888 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 2DTR | #2DTR |  | 96B1 | [17 empty] | 2-36-05 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | D03//2DTR/96B1 |  |  |  | CDC | 889 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 2DTR | #2DTR |  | 96B2 | [17 empty] | 2-36-06 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | D03//2DTR/96B2 |  |  |  | CDC | 890 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 2DTR | #2DTR |  | TRA | [17 empty] | 1-32-02 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#2DTR_TRA | #2DTR 重故障 | MTR | D03//2DTR/TRA |  |  |  | CDC | 891 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 2DTR | #2DTR |  | TRF | [17 empty] | 1-32-03 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#2DTR_TRF | #2DTR 輕故障 | MTR | D03//2DTR(A)/TRF |  |  |  | CDC | 892 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 2DTR(A) | #2DTR(A) |  | SupLocal | [17 empty] | 1-32-00 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | D03//2DTR(A)/SupLocal |  |  |  | CDC | 893 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D03 | 南濱DS | 0 |  | 2DTR(A) | #2DTR(A) |  | A_M | [17 empty] | 1-32-01 |  | 1-3C | [5 empty] | ADCS_S | [8 empty] | 南濱DS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | D03//2DTR(A)/Tap Chan |  |  |  | CDC | 894 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D03 | 南濱DS | 0 |  | 2DTR(B) | #2DTR(B) |  | SupLocal | [17 empty] | 1-32-04 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | D03//2DTR(B)/SupLocal |  |  |  | CDC | 895 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D03 | 南濱DS | 0 |  | 2DTR(B) | #2DTR(B) |  | A_M | [17 empty] | 1-32-05 |  | 1-3E | [5 empty] | ADCS_S | [8 empty] | 南濱DS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | D03//2DTR(B)/Tap Chan |  |  |  | CDC | 896 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D03 | 南濱DS | 11 | 11kV | 230 | #3SC(230) |  | CB | [17 empty] | 2-00-00 |  | 2-00 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.230_CB | 230(11KV #3SC) CB | SC | D03/11/230/CB |  |  |  | CDC | 897 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | 230 | #3SC(230) |  | SC_A_M | [17 empty] | 2-31-08 |  | 2-3B | [5 empty] | ADCS_S | [8 empty] | 南濱DS.230_A/M | 11KV #3SC 乏控器 A/M | SC | D03/11/230/SC_A_M |  |  |  | CDC | 898 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D03 | 南濱DS | 11 | 11kV | 230 | #3SC(230) |  | SCA | [17 empty] | 2-00-01 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.230_SCA | 11KV #3SC 51,51N RY | SC | D03/11/230/SCA |  |  |  | CDC | 899 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 230 | #3SC(230) |  | UVA | [17 empty] | 2-00-02 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | D03/11/230/UVA |  |  |  | CDC | 900 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 240 | #4SC(240) |  | CB | [17 empty] | 2-02-02 |  | 2-07 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.240_CB | 240(11KV #4SC) CB | SC | D03/11/240/CB |  |  |  | CDC | 901 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | 240 | #4SC(240) |  | SC_A_M | [17 empty] | 2-32-04 |  | 2-47 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.240_A/M | 11KV #4SC 乏控器 A/M | SC | D03/11/240/SC_A_M |  |  |  | CDC | 902 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D03 | 南濱DS | 11 | 11kV | 240 | #4SC(240) |  | SCA | [17 empty] | 2-02-03 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.240_SCA | 11KV #4SC 51,51N RY | SC | D03/11/240/SCA |  |  |  | CDC | 903 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 240 | #4SC(240) |  | UVA | [17 empty] | 2-02-04 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.240_UVA | 11KV #4SC 27RY(欠壓) | SC | D03/11/240/UVA |  |  |  | CDC | 904 | GENERICDIPoint | DS043_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 81RY | 330 |  | A/S(1) | [17 empty] | 1-09-05 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.81RY_A/S(1) | 330 81RY A/S | OTHER | D03/11/330/81A |  |  |  | CDC | 905 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
D03 | 南濱DS | 0 |  | 81RY | 340 |  | A/S(2) | [17 empty] | 1-0A-01 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.81RY_A/S(2) | 340 81RY A/S | OTHER | D03/11/340/81A |  |  |  | CDC | 906 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
D03 | 南濱DS | 0 |  | 2DTR | #2DTR |  | 87UL1 | [17 empty] | 1-31-15 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#2DTR_187S | #2DTR 187RY U/L | OTHER | D03//2DTR/87UL1 |  |  |  | CDC | 907 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 0 |  | 2DTR | #2DTR |  | 87UL2 | [17 empty] | 1-37-10 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#2DTR_287S | #2DTR 287RY U/L | OTHER | D03//2DTR/87UL2 |  |  |  | CDC | 908 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 0 |  | 2DTR | #2DTR |  | 51Z_UL | [17 empty] | 1-37-11 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#2DTR_51ZS | #2DTR 51Z U/L | OTHER | D03//2DTR/51Z_UL |  |  |  | CDC | 909 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 0 |  | 2DTR | #2DTR |  | 86RY | [17 empty] | 1-37-12 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#2DTR_86RY | #2DTR 86(50/50N/51Z/87/96)RY | OTHER | D03//2DTR/DTR_86A |  |  |  | CDC | 910 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 2DTR | #2DTR |  | RYFA | [17 empty] | 1-37-13 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#2DTR_RYFA | #2DTR 數位電驛故障 | OTHER | D03//2DTR/RYFA |  |  |  | CDC | 911 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 330 | #2DTR(330) |  | 81A | [17 empty] | 1-37-14 |  | 2-77 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.330_81RY | 330(M2A) 81RY U/L | OTHER | D03//2ADTR/81A |  |  |  | CDC | 912 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 0 |  | 330 | #2DTR(330) |  | GDA | [17 empty] | 1-09-07 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.330_GDA | 330開關箱IED RY GDA | OTHER | D03/11/330/GDA |  |  |  | CDC | 913 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 330 | #2DTR(330) |  | PHA2 | [17 empty] | 1-09-06 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.330_PHA2 | 330開關箱IED RY PHA | OTHER | D03/11/330/PHA |  |  |  | CDC | 914 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 340 | M2B(340) |  | 81A | [17 empty] | 1-37-15 |  | 2-78 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.340_81RY | 340(M2B) 81RY U/L | OTHER | D03//2BDTR/81A |  |  |  | CDC | 915 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 0 |  | 340 | 340開關箱IED |  | GDA | [17 empty] | 1-0A-03 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.340_GDA | 340開關箱IED RY GDA | OTHER | D03/11/340/GDA |  |  |  | CDC | 916 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 340 | 340開關箱IED |  | PHA2 | [17 empty] | 1-0A-02 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.340_PHA2 | 340開關箱IED RY PHA | OTHER | D03/11/340/PHA |  |  |  | CDC | 917 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 340 | #2DTR(340) |  | CB | [17 empty] | 1-0A-00 |  | 1-21 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.340_CB | 340(#2DTR) CB | MTR | D03/11/340/CB |  |  |  | CDC | 918 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | 230 | #3SC(230) |  | LBS | [17 empty] | 1-3E-08 | 1-3E-09 | 1-78 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.230_LBS | 230(11KV #3SC) LBS | SC | D03/11/230/LBS |  |  |  | CDC | 919 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 11 | 11kV | 230_LBS | #3SC |  | SC_A_M | [17 empty] | 2-31-09 |  | 2-3C | [5 empty] | ADCS_S | [8 empty] | 南濱DS.230_LBS_A/M | 11KV #3SC LBS 乏控器 A/M | SC |  |  |  |  | CDC | 920 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D03 | 南濱DS | 11 | 11kV | 240 | #4SC(240) |  | LBS | [17 empty] | 1-3E-10 | 1-3E-11 | 1-79 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.240_LBS | 240(11KV #4SC) LBS | SC | D03/11/240/LBS |  |  |  | CDC | 921 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 11 | 11kV | 240_LBS | #4SC |  | SC_A_M | [17 empty] | 2-32-05 |  | 2-48 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.240_LBS_A/M | 11KV #4SC LBS 乏控器 A/M | SC |  |  |  |  | CDC | 922 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D03 | 南濱DS | 0 |  | 2DTR | 2DTR |  | GDA | [17 empty] | 1-09-03 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#2DTR_GDA | 2DTR GDA | OTHER | D03//2DTR/GDA |  |  |  | CDC | 923 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | 2DTR | 2DTR |  | PHA | [17 empty] | 1-09-02 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.#2DTR_PHA | 2DTR PHA | OTHER | D03//2DTR/PHA |  |  |  | CDC | 924 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 0 |  |  |  |  | GEN | [17 empty] | 2-35-04 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.GEN | 緊急發電機運轉 | OTHER | D03/0/StaDev/1A5Other |  |  |  | CDC | 925 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D03 | 南濱DS | 161 | 161kV | _BUS | BUS |  | 87CTFA | [17 empty] | 2-35-06 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.161KV_BUS_CTFA | 161KV BUS 87RY CT回路故障 | OTHER | D03/161/BUS/12B_CTFA |  |  |  | CDC | 926 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | _BUS | BUS |  | RYFA | [17 empty] | 2-35-05 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | D03/161/BUS/BUS_RYFA |  |  |  | CDC | 927 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 0 |  | OLTC | OLTC |  | OLTCA | [17 empty] | 2-35-07 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | D03/0/ComPoint/OLTC_A |  |  |  | CDC | 928 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1611DTR | #1DTR |  | DTR_86A | [17 empty] | 1-0D-01 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.161#1DTR_86A | 161KV #1DTR 86RY | OTHER |  |  |  |  | CDC | 929 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1611DTR | #1DTR |  | 187UL | [17 empty] | 1-31-08 |  | 2-79 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.161#1DTR_187UL | 161KV #1DTR 187RY U/L | OTHER | D03//1DTR/87UL1 |  |  |  | CDC | 930 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1611DTR | #1DTR |  | 287UL | [17 empty] | 2-37-04 |  | 2-7A | [5 empty] | ADCS_S | [8 empty] | 南濱DS.161#1DTR_287UL | 161KV #1DTR 287RY U/L | OTHER |  |  |  |  | CDC | 931 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1611DTR | #1DTR |  | 51Z_UL | [17 empty] | 2-37-05 |  | 2-7B | [5 empty] | ADCS_S | [8 empty] | 南濱DS.161#1DTR_51ZUL | 161KV #1DTR 51ZRY U/L | OTHER |  |  |  |  | CDC | 932 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1611DTR | #1DTR |  | RYFA | [17 empty] | 2-37-06 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.161#1DTR_RYFA | 161KV #1DTR RYFA | OTHER |  |  |  |  | CDC | 933 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1613DTR | #3DTR |  | DTR_86A | [17 empty] | 1-0D-02 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.161#3DTR_86A | 161KV #3DTR 86RY | OTHER |  |  |  |  | CDC | 934 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1613DTR | #3DTR |  | 187UL | [17 empty] | 1-32-06 |  | 2-7C | [5 empty] | ADCS_S | [8 empty] | 南濱DS.161#3DTR_187UL | 161KV #3DTR 187RY U/L | OTHER | D03//3DTR/87UL1 |  |  |  | CDC | 935 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1613DTR | #3DTR |  | 287UL | [17 empty] | 2-37-07 |  | 2-7D | [5 empty] | ADCS_S | [8 empty] | 南濱DS.161#3DTR_287UL | 161KV #3DTR 287RY U/L | OTHER |  |  |  |  | CDC | 936 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1613DTR | #3DTR |  | 51Z_UL | [17 empty] | 2-37-08 |  | 2-7E | [5 empty] | ADCS_S | [8 empty] | 南濱DS.161#3DTR_51ZUL | 161KV #3DTR 51ZRY U/L | OTHER |  |  |  |  | CDC | 937 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1613DTR | #3DTR |  | RYFA | [17 empty] | 2-37-09 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.161#3DTR_RYFA | 161KV #3DTR RYFA | OTHER |  |  |  |  | CDC | 938 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1614DTR | #4DTR |  | DTR_86A | [17 empty] | 1-0D-03 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.161#4DTR_86A | 161KV #4DTR 86RY | OTHER |  |  |  |  | CDC | 939 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D03 | 南濱DS | 161 | 161kV | 1614DTR | #4DTR |  | 187UL | [17 empty] | 1-32-11 |  | 2-7F | [5 empty] | ADCS_S | [8 empty] | 南濱DS.161#4DTR_187UL | 161KV #4DTR 187RY U/L | OTHER | D03//4DTR/87UL1 |  |  |  | CDC | 940 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1614DTR | #4DTR |  | 287UL | [17 empty] | 2-37-10 |  | 3-00 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.161#4DTR_287UL | 161KV #4DTR 287RY U/L | OTHER |  |  |  |  | CDC | 941 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1614DTR | #4DTR |  | 51Z_UL | [17 empty] | 2-37-11 |  | 3-01 | [5 empty] | ADCS_S | [8 empty] | 南濱DS.161#4DTR_51ZUL | 161KV #4DTR 51ZRY U/L | OTHER |  |  |  |  | CDC | 942 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D03 | 南濱DS | 161 | 161kV | 1614DTR | #4DTR |  | RYFA | [17 empty] | 2-37-12 | [7 empty] | ADCS_S | [8 empty] | 南濱DS.161#4DTR_RYFA | 161KV #4DTR RYFA | OTHER |  |  |  |  | CDC | 943 | GENERICDIPoint | DS043_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 22 | 22kV | 11_ | 11/ |  | LOA | [17 empty] | 1-36-04 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.11/23KV_LOA | 11/23KV 饋線復閉失敗 | OTHER | D03/0/ComPoint/LOA |  |  |  | CDC | 944 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 開陽成大 | 開陽成大(K312) |  | 59V0 | [17 empty] | 1-1A-02 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.開陽成大_59V0 | 11KV開陽成大(K312) 59V0 | OTHER |  |  |  |  | CDC | 945 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 開陽成大 | 開陽成大(K312) |  | 81A | [17 empty] | 1-1A-05 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.開陽成大_81A | 11KV開陽成大(K312) 81A | OTHER |  |  |  |  | CDC | 946 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 開陽成大 | 開陽成大(K312) |  | CFA | [17 empty] | 1-3F-07 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.開陽成大_CFA | 11KV開陽成大(K312) 通訊故障 | OTHER |  |  |  |  | CDC | 947 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 開陽成大 | 開陽成大(K312) |  | DS1 | 開陽成大 | [16 empty] | 1-3F-00 | 1-3F-01 | [6 empty] | DDCS4_1 | [8 empty] | 南濱DS.開陽成大_DS | 11KV開陽成大(K312) DS | OTHER |  |  |  |  | CDC | 948 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 11 | 11kV | 開陽成大 | 開陽成大(K312) |  | GDA | [17 empty] | 1-1A-04 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.開陽成大_GDA | 11KV開陽成大(K312) GDA | OTHER |  |  |  |  | CDC | 949 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 開陽成大 | 開陽成大(K312) |  | PHA | [17 empty] | 1-1A-03 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.開陽成大_PHA | 11KV開陽成大(K312) PHA | OTHER |  |  |  |  | CDC | 950 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 開陽成大 | 開陽成大(K312) |  | PTDS | [17 empty] | 1-3F-02 | 1-3F-03 | [6 empty] | DDCS4_1 | [8 empty] | 南濱DS.開陽成大_PTDS | 11KV開陽成大(K312) PTDS | OTHER |  |  |  |  | CDC | 951 | GENERICDIPoint | DS043_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D03 | 南濱DS | 11 | 11kV | 開陽成大 | 開陽成大(K312) |  | RYFA | [17 empty] | 1-1A-01 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.開陽成大_RYA | 11KV開陽成大(K312) 27/59A | OTHER |  |  |  |  | CDC | 952 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D03 | 南濱DS | 11 | 11kV | 開陽成大_ | 開陽成大(K312) |  | CB | [17 empty] | 1-1A-00 | [7 empty] | DDCS4_1 | [8 empty] | 南濱DS.開陽成大__CB | 11KV開陽成大(K312) CB | OTHER |  |  |  |  | CDC | 953 | GENERICDIPoint | DS043_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 南濱DS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 954 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 11 | 11kV | 220_SC | #2SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 南濱DS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 955 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 22 | 22kV | 250_SC | #5SC | 9 | CAP | [25 empty] | ADCS_S | [8 empty] | 南濱DS.250_SC_CAP | 23KV#5SC 容量 | SC | [5 empty] | 956 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 22 | 22kV | 260_SC | #6SC | 9 | CAP | [25 empty] | ADCS_S | [8 empty] | 南濱DS.260_SC_CAP | 23KV#6SC 容量 | SC | [5 empty] | 957 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 22 | 22kV | 270_SC | #7SC | 9 | CAP | [25 empty] | ADCS_S | [8 empty] | 南濱DS.270_SC_CAP | 23KV#7SC 容量 | SC | [5 empty] | 958 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 22 | 22kV | 280_SC | #8SC | 9 | CAP | [25 empty] | ADCS_S | [8 empty] | 南濱DS.280_SC_CAP | 23KV#8SC 容量 | SC | [5 empty] | 959 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 0 |  | TRD | 南濱DS |  | 161 | [25 empty] | TRAIN_AD | [8 empty] | 南濱DS.TRD_161 | 南濱DS NT #1ADTR 11KV_Hi_Limit | [6 empty] | 960 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D03 | 南濱DS | 0 |  | TRD | 南濱DS |  | 162 | [25 empty] | TRAIN_AD | [8 empty] | 南濱DS.TRD_162 | 南濱DS NT #1ADTR 11KV_Lo_Limit | [6 empty] | 961 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D03 | 南濱DS | 0 |  | TRD | 南濱DS |  | 163 | [25 empty] | TRAIN_AD | [8 empty] | 南濱DS.TRD_163 | 南濱DS NT #1BDTR 11KV_Hi_Limit | [6 empty] | 962 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D03 | 南濱DS | 0 |  | TRD | 南濱DS |  | 164 | [25 empty] | TRAIN_AD | [8 empty] | 南濱DS.TRD_164 | 南濱DS NT #1BDTR 11KV_Lo_Limit | [6 empty] | 963 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D03 | 南濱DS | 0 |  | TRD | 南濱DS |  | 165 | [25 empty] | TRAIN_AD | [8 empty] | 南濱DS.TRD_165 | 南濱DS NT #3DTR 23KV_Hi_Limit | [6 empty] | 964 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D03 | 南濱DS | 0 |  | TRD | 南濱DS |  | 166 | [25 empty] | TRAIN_AD | [8 empty] | 南濱DS.TRD_166 | 南濱DS NT #3DTR 23KV_Lo_Limit | [6 empty] | 965 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D03 | 南濱DS | 0 |  | TRD | 南濱DS |  | 167 | [25 empty] | TRAIN_AD | [8 empty] | 南濱DS.TRD_167 | 南濱DS NT #4DTR 23KV_Hi_Limit | [6 empty] | 966 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D03 | 南濱DS | 0 |  | TRD | 南濱DS |  | 168 | [25 empty] | TRAIN_AD | [8 empty] | 南濱DS.TRD_168 | 南濱DS NT #4DTR 23KV_Lo_Limit | [6 empty] | 967 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D03 | 南濱DS | 11 | 11kV | 230_SC | #3SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 南濱DS.230_SC_CAP | 11KV#3SC 容量 | SC | [5 empty] | 968 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 11 | 11kV | 240_SC | #4SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 南濱DS.240_SC_CAP | 11KV#4SC 容量 | SC | [5 empty] | 969 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D03 | 南濱DS | 161 | 161kV | 1510 | 安南南濱一路(1510) |  | LE0 | 1510LE | [24 empty] | ADCS_S | [8 empty] | 南濱DS.1510LE | 1510LE (非取樣點) | LINE161 | D03/161/1510/LE0 |  |  |  |  | 970 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1510 | 安南南濱一路(1510) |  | BE0 | 1510BE | [24 empty] | ADCS_S | [8 empty] | 南濱DS.1510BE | 1510BE (非取樣點) | LINE161 | D03/161/1510/BE0 |  |  |  |  | 971 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1520 | 安南南濱二路(1520) |  | LE0 | 1520LE | [24 empty] | ADCS_S | [8 empty] | 南濱DS.1520LE | 1520LE (非取樣點) | LINE161 | D03/161/1520/LE0 |  |  |  |  | 972 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1520 | 安南南濱二路(1520) |  | BE0 | 1520BE | [24 empty] | ADCS_S | [8 empty] | 南濱DS.1520BE | 1520BE (非取樣點) | LINE161 | D03/161/1520/BE0 |  |  |  |  | 973 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱安瀚線(1530) |  | LE0 | 1530LE | [24 empty] | ADCS_S | [8 empty] | 南濱DS.1530LE | 1530LE (非取樣點) | LINE161 | D03/161/1530/LE0 |  |  |  |  | 974 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1530 | 南濱安瀚線(1530) |  | BE0 | 1530BE | [24 empty] | ADCS_S | [8 empty] | 南濱DS.1530BE | 1530BE (非取樣點) | LINE161 | D03/161/1530/BE0 |  |  |  |  | 975 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱凸版線(1540) |  | LE0 | 1540LE | [24 empty] | ADCS_S | [8 empty] | 南濱DS.1540LE | 1540LE (非取樣點) | LINE161 | D03/161/1540/LE0 |  |  |  |  | 976 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1540 | 南濱凸版線(1540) |  | BE0 | 1540BE | [24 empty] | ADCS_S | [8 empty] | 南濱DS.1540BE | 1540BE (非取樣點) | LINE161 | D03/161/1540/BE0 |  |  |  |  | 977 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K311 | K311_DS |  | DS1 | K311_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K311_DS | K311_DS (非取樣點) | FEEDER | D03/11/K311/DS |  |  |  |  | 978 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K311 | K311_ES |  | LE0 | K311_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K311_ES | K311_ES (非取樣點) | FEEDER | D03/11/K311/ES |  |  |  |  | 979 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K312 | K312_DS |  | DS1 | K312_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K312_DS | K312_DS (非取樣點) | FEEDER | D03/11/K312/DS |  |  |  |  | 980 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K312 | K312_ES |  | LE0 | K312_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K312_ES | K312_ES (非取樣點) | FEEDER | D03/11/K312/ES |  |  |  |  | 981 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K313 | K313_DS |  | DS1 | K313_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K313_DS | K313_DS (非取樣點) | FEEDER | D03/11/K313/DS |  |  |  |  | 982 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K313 | K313_ES |  | LE0 | K313_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K313_ES | K313_ES (非取樣點) | FEEDER | D03/11/K313/ES |  |  |  |  | 983 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K314 | K314_DS |  | DS1 | K314_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K314_DS | K314_DS (非取樣點) | FEEDER | D03/11/K314/DS |  |  |  |  | 984 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K314 | K314_ES |  | LE0 | K314_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K314_ES | K314_ES (非取樣點) | FEEDER | D03/11/K314/ES |  |  |  |  | 985 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K315 | K315_DS |  | DS1 | K315_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K315_DS | K315_DS (非取樣點) | FEEDER | D03/11/K315/DS |  |  |  |  | 986 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K315 | K315_ES |  | LE0 | K315_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K315_ES | K315_ES (非取樣點) | FEEDER | D03/11/K315/ES |  |  |  |  | 987 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K316 | K316_DS |  | DS1 | K316_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K316_DS | K316_DS (非取樣點) | FEEDER | D03/11/K316/DS |  |  |  |  | 988 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K316 | K316_ES |  | LE0 | K316_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K316_ES | K316_ES (非取樣點) | FEEDER | D03/11/K316/ES |  |  |  |  | 989 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K317 | K317_DS |  | DS1 | K317_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K317_DS | K317_DS (非取樣點) | FEEDER | D03/11/K317/DS |  |  |  |  | 990 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K317 | K317_ES |  | LE0 | K317_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K317_ES | K317_ES (非取樣點) | FEEDER | D03/11/K317/ES |  |  |  |  | 991 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K318 | K318_DS |  | DS1 | K318_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K318_DS | K318_DS (非取樣點) | FEEDER | D03/11/K318/DS |  |  |  |  | 992 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K318 | K318_ES |  | LE0 | K318_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K318_ES | K318_ES (非取樣點) | FEEDER | D03/11/K318/ES |  |  |  |  | 993 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K319 | K319_DS |  | DS1 | K319_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K319_DS | K319_DS (非取樣點) | FEEDER | D03/11/K319/DS |  |  |  |  | 994 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K319 | K319_ES |  | LE0 | K319_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K319_ES | K319_ES (非取樣點) | FEEDER | D03/11/K319/ES |  |  |  |  | 995 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K320 | K320_DS |  | DS1 | K320_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K320_DS | K320_DS (非取樣點) | FEEDER | D03/11/K320/DS |  |  |  |  | 996 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K320 | K320_ES |  | LE0 | K320_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K320_ES | K320_ES (非取樣點) | FEEDER | D03/11/K320/ES |  |  |  |  | 997 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K361 | K361_DS |  | DS1 | K361_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K361_DS | K361_DS (非取樣點) | FEEDER | D03/22/K361/DS |  |  |  |  | 998 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K361 | K361_ES |  | LE0 | K361_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K361_ES | K361_ES (非取樣點) | FEEDER | D03/22/K361/ES |  |  |  |  | 999 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K362 | K362_DS |  | DS1 | K362_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K362_DS | K362_DS (非取樣點) | FEEDER | D03/22/K362/DS |  |  |  |  | 1000 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K362 | K362_ES |  | LE0 | K362_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K362_ES | K362_ES (非取樣點) | FEEDER | D03/22/K362/ES |  |  |  |  | 1001 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K363 | K363_DS |  | DS1 | K363_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K363_DS | K363_DS (非取樣點) | FEEDER | D03/22/K363/DS |  |  |  |  | 1002 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K363 | K363_ES |  | LE0 | K363_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K363_ES | K363_ES (非取樣點) | FEEDER | D03/22/K363/ES |  |  |  |  | 1003 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K364 | K364_DS |  | DS1 | K364_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K364_DS | K364_DS (非取樣點) | FEEDER | D03/22/K364/DS |  |  |  |  | 1004 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K364 | K364_ES |  | LE0 | K364_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K364_ES | K364_ES (非取樣點) | FEEDER | D03/22/K364/ES |  |  |  |  | 1005 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K365 | K365_DS |  | DS1 | K365_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K365_DS | K365_DS (非取樣點) | FEEDER | D03/22/K365/DS |  |  |  |  | 1006 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K365 | K365_ES |  | LE0 | K365_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K365_ES | K365_ES (非取樣點) | FEEDER | D03/22/K365/ES |  |  |  |  | 1007 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K366 | K366_DS |  | DS1 | K366_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K366_DS | K366_DS (非取樣點) | FEEDER | D03/22/K366/DS |  |  |  |  | 1008 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K366 | K366_ES |  | LE0 | K366_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K366_ES | K366_ES (非取樣點) | FEEDER | D03/22/K366/ES |  |  |  |  | 1009 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K367 | K367_DS |  | DS1 | K367_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K367_DS | K367_DS (非取樣點) | FEEDER | D03/22/K367/DS |  |  |  |  | 1010 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K367 | K367_ES |  | LE0 | K367_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K367_ES | K367_ES (非取樣點) | FEEDER | D03/22/K367/ES |  |  |  |  | 1011 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K368 | K368_DS |  | DS1 | K368_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K368_DS | K368_DS (非取樣點) | FEEDER | D03/22/K368/DS |  |  |  |  | 1012 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K368 | K368_ES |  | LE0 | K368_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K368_ES | K368_ES (非取樣點) | FEEDER | D03/22/K368/ES |  |  |  |  | 1013 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K371 | K371_DS |  | DS1 | K371_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K371_DS | K371_DS (非取樣點) | FEEDER | D03/22/K371/DS |  |  |  |  | 1014 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K371 | K371_ES |  | LE0 | K371_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K371_ES | K371_ES (非取樣點) | FEEDER | D03/22/K371/ES |  |  |  |  | 1015 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K372 | K372_DS |  | DS1 | K372_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K372_DS | K372_DS (非取樣點) | FEEDER | D03/22/K372/DS |  |  |  |  | 1016 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K372 | K372_ES |  | LE0 | K372_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K372_ES | K372_ES (非取樣點) | FEEDER | D03/22/K372/ES |  |  |  |  | 1017 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K373 | K373_DS |  | DS1 | K373_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K373_DS | K373_DS (非取樣點) | FEEDER | D03/22/K373/DS |  |  |  |  | 1018 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K373 | K373_ES |  | LE0 | K373_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K373_ES | K373_ES (非取樣點) | FEEDER | D03/22/K373/ES |  |  |  |  | 1019 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K374 | K374_DS |  | DS1 | K374_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K374_DS | K374_DS (非取樣點) | FEEDER | D03/22/K374/DS |  |  |  |  | 1020 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K374 | K374_ES |  | LE0 | K374_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K374_ES | K374_ES (非取樣點) | FEEDER | D03/22/K374/ES |  |  |  |  | 1021 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K375 | K375_DS |  | DS1 | K375_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K375_DS | K375_DS (非取樣點) | FEEDER | D03/22/K375/DS |  |  |  |  | 1022 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K375 | K375_ES |  | LE0 | K375_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K375_ES | K375_ES (非取樣點) | FEEDER | D03/22/K375/ES |  |  |  |  | 1023 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K376 | K376_DS |  | DS1 | K376_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K376_DS | K376_DS (非取樣點) | FEEDER | D03/22/K376/DS |  |  |  |  | 1024 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K376 | K376_ES |  | LE0 | K376_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K376_ES | K376_ES (非取樣點) | FEEDER | D03/22/K376/ES |  |  |  |  | 1025 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K377 | K377_DS |  | DS1 | K377_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K377_DS | K377_DS (非取樣點) | FEEDER | D03/22/K377/DS |  |  |  |  | 1026 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K377 | K377_ES |  | LE0 | K377_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K377_ES | K377_ES (非取樣點) | FEEDER | D03/22/K377/ES |  |  |  |  | 1027 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K378 | K378_DS |  | DS1 | K378_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K378_DS | K378_DS (非取樣點) | FEEDER | D03/22/K378/DS |  |  |  |  | 1028 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K378 | K378_ES |  | LE0 | K378_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K378_ES | K378_ES (非取樣點) | FEEDER | D03/22/K378/ES |  |  |  |  | 1029 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 101 | 101 |  | 101 | 101 | [24 empty] | ADCS_S | [8 empty] | 南濱DS.101 | 101 (非取樣點) | TIE | D03/11/100/D1 |  |  |  |  | 1030 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 102 | 102 |  | 102 | 102 | [24 empty] | ADCS_S | [8 empty] | 南濱DS.102 | 102 (非取樣點) | TIE | D03/11/100/D2 |  |  |  |  | 1031 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [24 empty] | ADCS_S | [8 empty] | 南濱DS.1501E | 1501E (非取樣點) | TIE | D03/161/1500/E1 |  |  |  |  | 1032 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [24 empty] | ADCS_S | [8 empty] | 南濱DS.1502E | 1502E (非取樣點) | TIE | D03/161/1500/E2 |  |  |  |  | 1033 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 301 | 301 |  | 301 | 301 | [24 empty] | ADCS_S | [8 empty] | 南濱DS.301 | 301 (非取樣點) | TIE | D03/22/300/D1 |  |  |  |  | 1034 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 302 | 302 |  | 302 | 302 | [24 empty] | ADCS_S | [8 empty] | 南濱DS.302 | 302 (非取樣點) | TIE | D03/22/300/D2 |  |  |  |  | 1035 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 391 | 391 |  | 391 | 391 | [24 empty] | ADCS_S | [8 empty] | 南濱DS.391 | 391 (非取樣點) | OTHER | D03/11/390/D1 |  |  |  |  | 1036 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 391E | 391E |  | 391E | 391E | [24 empty] | ADCS_S | [8 empty] | 南濱DS.391E | 391E (非取樣點) | OTHER | D03/11/390/E1 |  |  |  |  | 1037 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 491 | 491 |  | 491 | 491 | [24 empty] | ADCS_S | [8 empty] | 南濱DS.491 | 491 (非取樣點) | OTHER | D03/22/490/D1 |  |  |  |  | 1038 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 491E | 491E |  | 491E | 491E | [24 empty] | ADCS_S | [8 empty] | 南濱DS.491E | 491E (非取樣點) | OTHER | D03/22/490/E1 |  |  |  |  | 1039 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | 1750TE | [24 empty] | ADCS_S | [8 empty] | 南濱DS.1750TE | 1750TE (非取樣點) | MTR | D03/161/1750/TE0 |  |  |  |  | 1040 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | 1750BE | [24 empty] | ADCS_S | [8 empty] | 南濱DS.1750BE | 1750BE (非取樣點) | MTR | D03/161/1750/BE0 |  |  |  |  | 1041 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 311 | 311 |  | 311 | 311 | [24 empty] | ADCS_S | [8 empty] | 南濱DS.311 | 311 (非取樣點) | MTR | D03/11/310/D1 |  |  |  |  | 1042 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 310 | #1DTR(310) |  | E1 | 311E | [24 empty] | ADCS_S | [8 empty] | 南濱DS.311E | 311E (非取樣點) | MTR | D03/11/310/E1 |  |  |  |  | 1043 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 321 | 321 |  | 321 | 321 | [24 empty] | ADCS_S | [8 empty] | 南濱DS.321 | 321 (非取樣點) | MTR | D03/11/320/D1 |  |  |  |  | 1044 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 320 | #1DTR(320) |  | E1 | 321E | [24 empty] | ADCS_S | [8 empty] | 南濱DS.321E | 321E (非取樣點) | MTR | D03/11/320/E1 |  |  |  |  | 1045 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | 1770TE | [24 empty] | ADCS_S | [8 empty] | 南濱DS.1770TE | 1770TE (非取樣點) | MTR | D03/161/1770/TE0 |  |  |  |  | 1046 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | 1770BE | [24 empty] | ADCS_S | [8 empty] | 南濱DS.1770BE | 1770BE (非取樣點) | MTR | D03/161/1770/BE0 |  |  |  |  | 1047 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 351 | 351 |  | 351 | 351 | [24 empty] | ADCS_S | [8 empty] | 南濱DS.351 | 351 (非取樣點) | MTR | D03/22/350/D1 |  |  |  |  | 1048 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 350 | #3DTR(350) |  | E1 | 351E | [24 empty] | ADCS_S | [8 empty] | 南濱DS.351E | 351E (非取樣點) | MTR | D03/22/350/E1 |  |  |  |  | 1049 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1780 | #4DTR(1780) |  | TE0 | 1780TE | [24 empty] | ADCS_S | [8 empty] | 南濱DS.1780TE | 1780TE (非取樣點) | MTR | D03/161/1780/TE0 |  |  |  |  | 1050 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1780 | #4DTR(1780) |  | BE0 | 1780BE | [24 empty] | ADCS_S | [8 empty] | 南濱DS.1780BE | 1780BE (非取樣點) | MTR | D03/161/1780/BE0 |  |  |  |  | 1051 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 371 | 371 |  | 371 | 371 | [24 empty] | ADCS_S | [8 empty] | 南濱DS.371 | 371 (非取樣點) | MTR | D03/22/370/D1 |  |  |  |  | 1052 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 370 | #4DTR(370) |  | E1 | 371E | [24 empty] | ADCS_S | [8 empty] | 南濱DS.371E | 371E (非取樣點) | MTR | D03/22/370/E1 |  |  |  |  | 1053 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 211E | 211E |  | 211E | 211E | [24 empty] | ADCS_S | [8 empty] | 南濱DS.211E | 211E (非取樣點) | SC | D03/11/210/E1 |  |  |  |  | 1054 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 210 | #1SC(210) |  | SC10 | 210SC1 | [24 empty] | ADCS_S | [8 empty] | 南濱DS.210SC1_ES | 210SC1_ES (非取樣點) | SC | [5 empty] | 1055 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 211 | 211 |  | 211 | 211 | [24 empty] | ADCS_S | [8 empty] | 南濱DS.211 | 211 (非取樣點) | SC | D03/11/210/D1 |  |  |  |  | 1056 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 210 | #1SC(210) |  | SC20 | 210SC2 | [24 empty] | ADCS_S | [8 empty] | 南濱DS.210SC2_ES | 210SC2_ES (非取樣點) | SC | [5 empty] | 1057 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 221E | 221E |  | 221E | 221E | [24 empty] | ADCS_S | [8 empty] | 南濱DS.221E | 221E (非取樣點) | SC | D03/11/220/E1 |  |  |  |  | 1058 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 220 | #2SC(220) |  | SC10 | 220SC1 | [24 empty] | ADCS_S | [8 empty] | 南濱DS.220SC1_ES | 220SC1_ES (非取樣點) | SC | [5 empty] | 1059 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 221 | 221 |  | 221 | 221 | [24 empty] | ADCS_S | [8 empty] | 南濱DS.221 | 221 (非取樣點) | SC | D03/11/220/D1 |  |  |  |  | 1060 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 220 | #2SC(220) |  | SC20 | 220SC2 | [24 empty] | ADCS_S | [8 empty] | 南濱DS.220SC2_ES | 220SC2_ES (非取樣點) | SC | [5 empty] | 1061 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 251E | 251E |  | 251E | 251E | [24 empty] | ADCS_S | [8 empty] | 南濱DS.251E | 251E (非取樣點) | SC | D03/22/250/E1 |  |  |  |  | 1062 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 250 | #5SC(250) |  | SC0 | 250SC | [24 empty] | ADCS_S | [8 empty] | 南濱DS.250SC_ES | 250SC_ES (非取樣點) | SC | [5 empty] | 1063 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 251 | 251 |  | 251 | 251 | [24 empty] | ADCS_S | [8 empty] | 南濱DS.251 | 251 (非取樣點) | SC | D03/22/250/D1 |  |  |  |  | 1064 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 261E | 261E |  | 261E | 261E | [24 empty] | ADCS_S | [8 empty] | 南濱DS.261E | 261E (非取樣點) | SC | D03/22/260/E1 |  |  |  |  | 1065 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 260 | #6SC(260) |  | SC0 | 260SC | [24 empty] | ADCS_S | [8 empty] | 南濱DS.260SC_ES | 260SC_ES (非取樣點) | SC | [5 empty] | 1066 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 261 | 261 |  | 261 | 261 | [24 empty] | ADCS_S | [8 empty] | 南濱DS.261 | 261 (非取樣點) | SC | D03/22/260/D1 |  |  |  |  | 1067 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 271E | 271E |  | 271E | 271E | [24 empty] | ADCS_S | [8 empty] | 南濱DS.271E | 271E (非取樣點) | SC | D03/22/270/E1 |  |  |  |  | 1068 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 270 | #7SC(270) |  | SC0 | 270SC | [24 empty] | ADCS_S | [8 empty] | 南濱DS.270SC_ES | 270SC_ES (非取樣點) | SC | [5 empty] | 1069 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 271 | 271 |  | 271 | 271 | [24 empty] | ADCS_S | [8 empty] | 南濱DS.271 | 271 (非取樣點) | SC | D03/22/270/D1 |  |  |  |  | 1070 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 281E | 281E |  | 281E | 281E | [24 empty] | ADCS_S | [8 empty] | 南濱DS.281E | 281E (非取樣點) | SC | D03/22/280/E1 |  |  |  |  | 1071 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 280 | #8SC(280) |  | SC0 | 280SC | [24 empty] | ADCS_S | [8 empty] | 南濱DS.280SC_ES | 280SC_ES (非取樣點) | SC | [5 empty] | 1072 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 281 | 281 |  | 281 | 281 | [24 empty] | ADCS_S | [8 empty] | 南濱DS.281 | 281 (非取樣點) | SC | D03/22/280/D1 |  |  |  |  | 1073 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 15B1E | 15B1E |  | BE1 | 15B1E | [24 empty] | ADCS_S | [8 empty] | 南濱DS.15B1E | 15B1E (非取樣點) | BUS | D03/161/161B1E/BE1 |  |  |  |  | 1074 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 15B2E | 15B2E |  | BE2 | 15B2E | [24 empty] | ADCS_S | [8 empty] | 南濱DS.15B2E | 15B2E (非取樣點) | BUS | D03/161/161B2E/BE2 |  |  |  |  | 1075 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | ADCS_S | [8 empty] | 南濱DS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 1076 | NotelDIPoint | [38 empty] | START/STOP | STOP
D03 | 南濱DS | 0 |  |  |  |  | 101E | 101E | [24 empty] | ADCS_S | [8 empty] | 南濱DS.101E | 101E(非取樣點) | OTHER | D03/11/100/E1 |  |  |  |  | 1077 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  |  |  |  | 301E | 301E | [24 empty] | ADCS_S | [8 empty] | 南濱DS.301E | 301E(非取樣點) | OTHER | D03/22/300/E1 |  |  |  |  | 1078 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  |  |  |  | 302E | 302E | [24 empty] | ADCS_S | [8 empty] | 南濱DS.302E | 302E(非取樣點) | OTHER | D03/22/300/E2 |  |  |  |  | 1079 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | 1760TE | [24 empty] | ADCS_S | [8 empty] | 南濱DS.1760TE | 1760TE (非取樣點) | MTR | D03/161/1760/TE0 |  |  |  |  | 1080 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | 1760BE | [24 empty] | ADCS_S | [8 empty] | 南濱DS.1760BE | 1760BE (非取樣點) | MTR | D03/161/1760/BE0 |  |  |  |  | 1081 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | BUTTON1 | BUTTON1 |  | ON | [25 empty] | ADCS_S | [8 empty] | 南濱DS.BUTTON1_ON | 南濱DS按鈕全停測試(1) | [6 empty] | 1082 | NotelDIPoint | [38 empty] | RUNNING/STOPPED | STOPPED
D03 | 南濱DS | 0 |  | BUTTON2 | BUTTON2 |  | ON | [25 empty] | ADCS_S | [8 empty] | 南濱DS.BUTTON2_ON | 南濱DS按鈕全停測試(2) | [6 empty] | 1083 | NotelDIPoint | [38 empty] | RUNNING/STOPPED | STOPPED
D03 | 南濱DS | 161 | 161kV | 1550 | 南濱鹿耳紅線(1550) |  | LE0 | 1550LE | [24 empty] | ADCS_S | [8 empty] | 南濱DS.1550LE | 1550LE (非取樣點) | LINE161 | D03/161/1550/LE0 |  |  |  |  | 1084 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1550 | 南濱鹿耳紅線(1550) |  | BE0 | 1550BE | [24 empty] | ADCS_S | [8 empty] | 南濱DS.1550BE | 1550BE (非取樣點) | LINE161 | D03/161/1550/BE0 |  |  |  |  | 1085 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1560 | 南濱鹿耳白線(1560) |  | LE0 | 1560LE | [24 empty] | ADCS_S | [8 empty] | 南濱DS.1560LE | 1560LE (非取樣點) | LINE161 | D03/161/1560/LE0 |  |  |  |  | 1086 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 161 | 161kV | 1560 | 南濱鹿耳白線(1560) |  | BE0 | 1560BE | [24 empty] | ADCS_S | [8 empty] | 南濱DS.1560BE | 1560BE (非取樣點) | LINE161 | D03/161/1560/BE0 |  |  |  |  | 1087 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K321 | K321_DS |  | DS1 | K321_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K321_DS | K321_DS (非取樣點) | FEEDER | D03/11/K321/DS |  |  |  |  | 1088 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K321 | K321_ES |  | LE0 | K321_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K321_ES | K321_ES (非取樣點) | FEEDER | D03/11/K321/ES |  |  |  |  | 1089 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K322 | K322_DS |  | DS1 | K322_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K322_DS | K322_DS (非取樣點) | FEEDER | D03/11/K322/DS |  |  |  |  | 1090 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K322 | K322_ES |  | LE0 | K322_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K322_ES | K322_ES (非取樣點) | FEEDER | D03/11/K322/ES |  |  |  |  | 1091 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K323 | K323_DS |  | DS1 | K323_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K323_DS | K323_DS (非取樣點) | FEEDER | D03/11/K323/DS |  |  |  |  | 1092 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K323 | K323_ES |  | LE0 | K323_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K323_ES | K323_ES (非取樣點) | FEEDER | D03/11/K323/ES |  |  |  |  | 1093 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K324 | K324_DS |  | DS1 | K324_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K324_DS | K324_DS (非取樣點) | FEEDER | D03/11/K324/DS |  |  |  |  | 1094 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K324 | K324_ES |  | LE0 | K324_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K324_ES | K324_ES (非取樣點) | FEEDER | D03/11/K324/ES |  |  |  |  | 1095 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K325 | K325_DS |  | DS1 | K325_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K325_DS | K325_DS (非取樣點) | FEEDER | D03/11/K325/DS |  |  |  |  | 1096 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K325 | K325_ES |  | LE0 | K325_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K325_ES | K325_ES (非取樣點) | FEEDER | D03/11/K325/ES |  |  |  |  | 1097 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K326 | K326_DS |  | DS1 | K326_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K326_DS | K326_DS (非取樣點) | FEEDER | D03/11/K326/DS |  |  |  |  | 1098 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K326 | K326_ES |  | LE0 | K326_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K326_ES | K326_ES (非取樣點) | FEEDER | D03/11/K326/ES |  |  |  |  | 1099 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K327 | K327_DS |  | DS1 | K327_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K327_DS | K327_DS (非取樣點) | FEEDER | D03/11/K327/DS |  |  |  |  | 1100 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K327 | K327_ES |  | LE0 | K327_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K327_ES | K327_ES (非取樣點) | FEEDER | D03/11/K327/ES |  |  |  |  | 1101 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K328 | K328_DS |  | DS1 | K328_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K328_DS | K328_DS (非取樣點) | FEEDER | D03/11/K328/DS |  |  |  |  | 1102 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K328 | K328_ES |  | LE0 | K328_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K328_ES | K328_ES (非取樣點) | FEEDER | D03/11/K328/ES |  |  |  |  | 1103 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K329 | K329_DS |  | DS1 | K329_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K329_DS | K329_DS (非取樣點) | FEEDER | D03/11/K329/DS |  |  |  |  | 1104 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K329 | K329_ES |  | LE0 | K329_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K329_ES | K329_ES (非取樣點) | FEEDER | D03/11/K329/ES |  |  |  |  | 1105 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | K330 | K330_DS |  | DS1 | K330_DS | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K330_DS | K330_DS (非取樣點) | FEEDER | D03/11/K330/DS |  |  |  |  | 1106 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | K330 | K330_ES |  | LE0 | K330_ES | [24 empty] | DDCS4_1 | [8 empty] | 南濱DS.K330_ES | K330_ES (非取樣點) | FEEDER | D03/11/K330/ES |  |  |  |  | 1107 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 201 | 201 |  | 201 | 201 | [24 empty] | ADCS_S | [8 empty] | 南濱DS.201 | 201 (非取樣點) | TIE | D03/11/200/D1 |  |  |  |  | 1108 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 202 | 202 |  | 202 | 202 | [24 empty] | ADCS_S | [8 empty] | 南濱DS.202 | 202 (非取樣點) | TIE | D03/11/200/D2 |  |  |  |  | 1109 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 331 | 331 |  | 331 | 331 | [24 empty] | ADCS_S | [8 empty] | 南濱DS.331 | 331 (非取樣點) | MTR | D03/11/330/D1 |  |  |  |  | 1110 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 330 | #2DTR(330) |  | E1 | 331E | [24 empty] | ADCS_S | [8 empty] | 南濱DS.331E | 331E (非取樣點) | MTR | D03/11/330/E1 |  |  |  |  | 1111 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 341 | 341 |  | 341 | 341 | [24 empty] | ADCS_S | [8 empty] | 南濱DS.341 | 341 (非取樣點) | MTR | D03/11/340/D1 |  |  |  |  | 1112 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 340 | #2DTR(340) |  | E1 | 341E | [24 empty] | ADCS_S | [8 empty] | 南濱DS.341E | 341E (非取樣點) | MTR | D03/11/340/E1 |  |  |  |  | 1113 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 231E | 231E |  | 231E | 231E | [24 empty] | ADCS_S | [8 empty] | 南濱DS.231E | 231E (非取樣點) | SC | D03/11/230/E1 |  |  |  |  | 1114 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 230 | #3SC(230) |  | SC10 | 230SC1 | [24 empty] | ADCS_S | [8 empty] | 南濱DS.230SC1_ES | 230SC1_ES (非取樣點) | SC | [5 empty] | 1115 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 231 | 231 |  | 231 | 231 | [24 empty] | ADCS_S | [8 empty] | 南濱DS.231 | 231 (非取樣點) | SC | D03/11/230/D1 |  |  |  |  | 1116 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 241E | 241E |  | 241E | 241E | [24 empty] | ADCS_S | [8 empty] | 南濱DS.241E | 241E (非取樣點) | SC | D03/11/240/E1 |  |  |  |  | 1117 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 240 | #4SC(240) |  | SC10 | 240SC1 | [24 empty] | ADCS_S | [8 empty] | 南濱DS.240SC1_ES | 240SC1_ES (非取樣點) | SC | [5 empty] | 1118 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 241 | 241 |  | 241 | 241 | [24 empty] | ADCS_S | [8 empty] | 南濱DS.241 | 241 (非取樣點) | SC | D03/11/240/D1 |  |  |  |  | 1119 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 230 | #3SC(230) |  | SC20 | 230SC2 | [24 empty] | ADCS_S | [8 empty] | 南濱DS.230SC2_ES | 230SC2_ES (非取樣點) | SC | [5 empty] | 1120 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 240 | #4SC(240) |  | SC20 | 240SC2 | [24 empty] | ADCS_S | [8 empty] | 南濱DS.240SC2_ES | 240SC2_ES (非取樣點) | SC | [5 empty] | 1121 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  |  |  |  | 102E | 102E | [24 empty] | ADCS_S | [8 empty] | 南濱DS.102E | 102E(非取樣點) | OTHER | D03/11/100/E2 |  |  |  |  | 1122 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  |  |  |  | 201E | 201E | [24 empty] | ADCS_S | [8 empty] | 南濱DS.201E | 201E(非取樣點) | OTHER | D03/11/200/E1 |  |  |  |  | 1123 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  |  |  |  | 202E | 202E | [24 empty] | ADCS_S | [8 empty] | 南濱DS.202E | 202E(非取樣點) | OTHER | D03/11/200/E2 |  |  |  |  | 1124 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 2ABUS | 2ABUS |  | PTD | 2ABUS_PTD | [24 empty] | ADCS_S | [8 empty] | 南濱DS.2ABUS_PTD | #2ABUS_PTD(非取樣點) | OTHER | [5 empty] | 1125 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 2ABUS | 2ABUS |  | PTE | 2ABUS_PTE | [24 empty] | ADCS_S | [8 empty] | 南濱DS.2ABUS_PTE | #2ABUS_PTE(非取樣點) | OTHER | [5 empty] | 1126 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 2BBUS | 2BBUS |  | PTD | 2BBUS_PTD | [24 empty] | ADCS_S | [8 empty] | 南濱DS.2BBUS_PTD | #2BBUS_PTD(非取樣點) | OTHER | [5 empty] | 1127 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D03 | 南濱DS | 0 |  | 2BBUS | 2BBUS |  | PTE | 2BBUS_PTE | [24 empty] | ADCS_S | [8 empty] | 南濱DS.2BBUS_PTE | #2BBUS_PTE(非取樣點) | OTHER | [5 empty] | 1128 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 1A | #1A |  | BE | #1A_BE | [24 empty] | ADCS_S | [8 empty] | 南濱DS.#1A_BE | #1A BE(非取樣點) | OTHER | [5 empty] | 1129 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 1B | #1B |  | BE | #1B_BE | [24 empty] | ADCS_S | [8 empty] | 南濱DS.#1B_BE | #1B BE(非取樣點) | OTHER | [5 empty] | 1130 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 2A | #2A |  | BE | #2A_BE | [24 empty] | ADCS_S | [8 empty] | 南濱DS.#2A_BE | #2A BE(非取樣點) | OTHER | [5 empty] | 1131 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 2B | #2B |  | BE | #2B_BE | [24 empty] | ADCS_S | [8 empty] | 南濱DS.#2B_BE | #2B BE(非取樣點) | OTHER | [5 empty] | 1132 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 3 | #3 |  | BE | #3_BE | [24 empty] | ADCS_S | [8 empty] | 南濱DS.#3_BE | #3 BE(非取樣點) | OTHER | [5 empty] | 1133 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D03 | 南濱DS | 0 |  | 4 | #4 |  | BE | #4_BE | [24 empty] | ADCS_S | [8 empty] | 南濱DS.#4_BE | #4 BE(非取樣點) | OTHER | [5 empty] | 1134 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo