## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D04 | 豐華DS | 11 | 11kV | 1ABUS | #1ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0051 |  |  | 1-B3 |  |  | PT-1A | KV | #1A PT R相電壓 | kV_-9_9(-2000_2000) | aaa | B3/D04_A1 | [8 empty] | 豐華DS.11KV#1ABUS_KV | 11KV #1ABUS KV | BUS | [5 empty] | 173 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D04 | 豐華DS | 11 | 11kV | 1BBUS | #1BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0084 |  |  | 1-D4 |  |  | PT-1B | KV | #1B PT R相電壓 | kV_-9_9(-2000_2000) | baa | B3/D04_A1 | [8 empty] | 豐華DS.11KV#1BBUS_KV | 11KV #1BBUS KV | BUS | [5 empty] | 206 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D04 | 豐華DS | 161 | 161kV | 1BUS | #1BUS |  | V |  | B3 | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 161KV #1BUS | KV | 161KV #1BUS 電壓 | kV_-210_210(-2000_2000) | aaa | B2/D04_A1 | [8 empty] | 豐華DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | [5 empty] | 130 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D04 | 豐華DS | 161 | 161kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | NO.1 BUS | A/N | 161KV NO.1 BUS 87B1A |  |  | B2/D04_A1 | [8 empty] | 豐華DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | [5 empty] | 400 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0859 |  |  | 1-35-11 |  |  | Locate Empty | A/N | 161KV NO.1 BUS欠壓 VUA1 |  |  | B2/D04_A1 | [8 empty] | 豐華DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | [5 empty] | 644 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0873 |  |  | 1-36-09 |  |  | Locate Empty | 87B1S | 161KV #1BUS 87RY U/L |  |  | B2/D04_A1 | [8 empty] | 豐華DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | [5 empty] | 657 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | 15B1E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aaaz | B2/D04_A1 | [8 empty] | 豐華DS.15B1E | 15B1E (非取樣點) | BUS | [5 empty] | 126 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS |  |  | 1DTR | #1DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | NO.1 DTR. | ℃ | NO.1 DTR. 油溫 | OIL_-120_120(-2000_2000) |  | B1/D04_A1 | [8 empty] | 豐華DS.#1DTR_OIL | #1DTR 油溫 | MTR | [5 empty] | 155 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D04 | 豐華DS |  |  | 1DTR | #1DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0059 |  |  | 1-07-03 |  |  | #1DTR | A/N | NO.1 DTR 87A 87A |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#1DTR_87A | #1DTR 87RY | MTR | [5 empty] | 406 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS |  |  | 1DTR | #1DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0060 |  |  | 1-07-04 |  |  | #1DTR | A/N | NO.1 DTR 機械保護動作(96PA) |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | [5 empty] | 407 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS |  |  | 1DTR | #1DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0061 |  |  | 1-07-05 |  |  | #1DTR | A/N | NO.1 DTR 51ZA 51ZA |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | [5 empty] | 408 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS |  |  | 1DTR | #1DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0062 |  |  | 1-07-06 |  |  | #1DTR | PHA | NO.1 DTR PHA PHA |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#1DTR_51A | #1DTR 51RY | MTR | [5 empty] | 409 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS |  |  | 1DTR | #1DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0063 |  |  | 1-07-07 |  |  | #1DTR | GDA | NO.1 DTR GDA GDA |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#1DTR_51NA | #1DTR 51N RY | MTR | [5 empty] | 410 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS |  |  | 1DTR | #1DTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0794 |  |  | 1-31-10 |  |  | Locate Empty | USE/LOCK | NO.1 D.TR. 187S |  |  | B1/D04_A1 | [8 empty] | 豐華DS.161#1DTR_187UL | 161KV #1DTR 187RY U/L | OTHER | [5 empty] | 593 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS |  |  | 1DTR | #1DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0799 |  |  | 1-31-15 |  |  | Locate Empty | A/N | NO.1 D.TR.撲氣電驛(1) 196B1 |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | [5 empty] | 598 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS |  |  | 1DTR | #1DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0800 |  |  | 1-32-00 |  |  | Locate Empty | A/N | NO.1 D.TR.撲氣電驛(2) 196B2 |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | [5 empty] | 599 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS |  |  | 1DTR | #1DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0801 |  |  | 1-32-01 |  |  | Locate Empty | A/N | NO.1 D.TR.放壓裝置 196D |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#1DTR_96D | #1DTR 96D RY | MTR | [5 empty] | 600 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS |  |  | 1DTR | #1DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0802 |  |  | 1-32-02 |  |  | Locate Empty | A/N | NO.1 D.TR.衝擊油壓 196P |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#1DTR_96P | #1DTR 96P RY | MTR | [5 empty] | 601 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS |  |  | 1DTR | #1DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0803 |  |  | 1-32-03 |  |  | Locate Empty | A/N | NO.1 D.TR. ULTC 163Q |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#1DTR_63Q | #1DTR 63Q RY | MTR | [5 empty] | 602 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS |  |  | 1DTR | #1DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0804 |  |  | 1-32-04 |  |  | Locate Empty | A/N | NO.1 D.TR.輕故障 1TRF |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#1DTR_TRF | #1DTR 輕故障 | MTR | [5 empty] | 603 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS |  |  | 1DTR | #1DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0805 |  |  | 1-32-05 |  |  | Locate Empty | A/N | NO.1 D.TR.重故障 1TRA |  | a | B1/D04_A1 | [8 empty] | 豐華DS.#1DTR_TRA | #1DTR 重故障 | MTR | [5 empty] | 604 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS |  |  | 1DTR | #1DTR |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0917 |  |  | 1-39-05 |  |  | Locate Empty |  |  |  |  | B1/D04_A1 | [8 empty] | 豐華DS.161#1DTR_287UL | 161KV #1DTR 287RY U/L | OTHER | [5 empty] | 698 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS |  |  | 1DTR | #1DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0918 |  |  | 1-39-06 |  |  | Locate Empty |  |  |  |  | B1/D04_A1 | [8 empty] | 豐華DS.161#1DTR_51ZUL | 161KV #1DTR 51ZRY U/L | OTHER | [5 empty] | 699 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS |  |  | 1DTR | #1DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0919 |  |  | 1-39-07 |  |  | Locate Empty |  |  |  |  | B1/D04_A1 | [8 empty] | 豐華DS.161#1DTR_RYFA | 161KV #1DTR RYFA | OTHER | [5 empty] | 700 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS |  |  | 1DTR | #1DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0116 | [10 empty] | B1/D04_A1 | [16 empty] | 826 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1750TE | 1750TE (非取樣點) | MTR | [5 empty] | 28 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1750BE | 1750BE (非取樣點) | MTR | [5 empty] | 29 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/1DTR |  | 0058 |  |  | 1-07-02 |  |  | #1DTR | ON/OFF | NO.1 1750 CB 52AS |  | aabb | ELEM/D04_A1 | [8 empty] | 豐華DS.1750_CB | 1750(#1DTR) CB | MTR | [5 empty] | 405 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1044 | 1045 |  | 2-31-04 | 2-31-05 |  | Locate Empty | ON | NO.1 DTR(1751) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1751_DS | 1751(#1DTR) DS | MTR | [5 empty] | 749 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1046 | 1047 |  | 2-31-06 | 2-31-07 |  | Locate Empty | ON | NO.1 DTR(1752) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1752_DS | 1752(#1DTR) DS | MTR | [5 empty] | 750 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS |  |  | 1DTR(A) | #1DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | NO.1 DTR.A | ℃ | NO.1 DTR.A 線溫 | COIL_-120_120(-2000_2000) |  | B1/D04_A1 | [8 empty] | 豐華DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | [5 empty] | 156 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D04 | 豐華DS |  |  | 1DTR(A) | #1DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | NO.1 DTR.A | 升/降 | NO.1 DTR.A TAP | TAP_-8.5_8.5(0_2000) |  | B1/D04_A1 | [8 empty] | 豐華DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | [5 empty] | 158 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D04 | 豐華DS |  |  | 1DTR(A) | #1DTR(A) |  | SupLocal |  | B3 | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0795 |  |  | 1-31-11 |  |  | Locate Empty | 遙控/現場 | NO.1 D.TR. S/L (A) 143R1S3 |  | c | B1/D04_A1 | [8 empty] | 豐華DS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | [5 empty] | 594 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D04 | 豐華DS |  |  | 1DTR(A) | #1DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0796 |  |  | 1-31-12 |  |  | Locate Empty | OLTC A/M | NO.1 D.TR. A/M (A) 1AX-S1 |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | [5 empty] | 595 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D04 | 豐華DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | D1 | 311(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D04_A1 | [8 empty] | 豐華DS.311 | 311 (非取樣點) | MTR | [5 empty] | 30 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | E1 | 311E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D04_A1 | [8 empty] | 豐華DS.311E | 311E (非取樣點) | MTR | [5 empty] | 31 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | D1A | MW | D1A 310 瓦 | MW_-54_54(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | [5 empty] | 168 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | D1A | MVAR | D1A 310 乏 | MVAR_-36_36(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | [5 empty] | 169 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | D1A | A | D1A 310 R相電流 | A_-3000_3000(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | [5 empty] | 170 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | D1A | A | D1A 310 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | [5 empty] | 171 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | D1A | A | D1A 310 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | [5 empty] | 172 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0064 |  |  | 1-08-00 |  |  | D1A | PHA | D1A 310 (51-3φ)PHA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.310_51A | #1DTR二次側(310) 51RY | MTR | [5 empty] | 411 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | T/1DTR(A) |  |  | 0066 |  |  | 1-08-02 |  |  | D1A | ON/OFF | D1A 310 CB 52AS |  | aaba | ELEM/D04_A1 | [8 empty] | 豐華DS.310_CB | 310(#1DTR) CB | MTR | [5 empty] | 413 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0067 |  |  | 1-08-03 |  |  | D1A | PHA | D1A 310 PHA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.310_PHA2 | 310開關箱IED RY PHA | OTHER | [5 empty] | 414 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 |  |  | 1-08-04 |  |  | D1A | GDA | D1A 310 GDA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.310_GDA | 310開關箱IED RY GDA | OTHER | [5 empty] | 415 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS |  |  | 1DTR(B) | #1DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | NO.1 DTR.B | ℃ | NO.1 DTR.B 線溫 | COIL_-120_120(-2000_2000) |  | B1/D04_A1 | [8 empty] | 豐華DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | [5 empty] | 157 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D04 | 豐華DS |  |  | 1DTR(B) | #1DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | NO.1 DTR.B | 升/降 | NO.1 DTR.B TAP | TAP_-8.5_8.5(0_2000) |  | B1/D04_A1 | [8 empty] | 豐華DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | [5 empty] | 159 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D04 | 豐華DS |  |  | 1DTR(B) | #1DTR(B) |  | SupLocal |  | B3 | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0797 |  |  | 1-31-13 |  |  | Locate Empty | 遙控/現場 | NO.1 D.TR. S/L (B) 143R2S3 |  | b | B1/D04_A1 | [8 empty] | 豐華DS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | [5 empty] | 596 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D04 | 豐華DS |  |  | 1DTR(B) | #1DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0798 |  |  | 1-31-14 |  |  | Locate Empty | OLTC A/M | NO.1 D.TR. A/M (B) 1AX-S2 |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | [5 empty] | 597 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D04 | 豐華DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | D1 | 321(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D04_A1 | [8 empty] | 豐華DS.321 | 321 (非取樣點) | MTR | [5 empty] | 32 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | E1 | 321E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D04_A1 | [8 empty] | 豐華DS.321E | 321E (非取樣點) | MTR | [5 empty] | 33 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | D1B | MW | D1B 320 瓦 | MW_-54_54(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | [5 empty] | 201 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | D1B | MVAR | D1B 320 乏 | MVAR_-36_36(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | [5 empty] | 202 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | D1B | A | D1B 320 R相電流 | A_-3000_3000(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | [5 empty] | 203 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | D1B | A | D1B 320 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | [5 empty] | 204 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | D1B | A | D1B 320 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | [5 empty] | 205 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0065 |  |  | 1-08-01 |  |  | D1B | PHA | D1B 320 (51-3φ)PHA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.320_51A | #1DTR二次側(320) 51RY | MTR | [5 empty] | 412 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | T/1DTR(B) |  |  | 0069 |  |  | 1-08-05 |  |  | D1B | ON/OFF | D1B 320 CB 52AS |  | baaa | ELEM/D04_A1 | [8 empty] | 豐華DS.320_CB | 320(#1DTR) CB | MTR | [5 empty] | 416 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0070 |  |  | 1-08-06 |  |  | D1B | PHA | D1B 320 PHA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.320_PHA2 | 320開關箱IED RY PHA | OTHER | [5 empty] | 417 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0071 |  |  | 1-08-07 |  |  | D1B | GDA | D1B 320 GDA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.320_GDA | 320開關箱IED RY GDA | OTHER | [5 empty] | 418 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | 210 | #1SC(210) |  | E1 | 211E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D04_A1 | [8 empty] | 豐華DS.211E | 211E (非取樣點) | SC | [5 empty] | 56 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | 210 | #1SC(210) |  | D1 | 211(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D04_A1 | [8 empty] | 豐華DS.211 | 211 (非取樣點) | SC | [5 empty] | 57 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | 210 | #1SC(210) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | A/LBS210^C/1SC(A) |  |  | 0143 |  |  | 1-11-07 |  |  | #1SC | ON/OFF | #1SC 210 CB 52AS |  | aacb | B3/D04_A1 | [8 empty] | 豐華DS.210_CB | 210(11KV #1SC) CB | SC | [5 empty] | 468 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0144 |  |  | 1-12-00 |  |  | #1SC | SCA | #1SC 210 CB RY SCA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.210_SCA | 11KV #1SC 51,51N RY | SC | [5 empty] | 469 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0145 |  |  | 1-12-01 |  |  | #1SC | UVA | #1SC 210 CB RY UVA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | [5 empty] | 470 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1950 | #1SHR(1950) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | R/1SHR |  | 0042 |  |  | 1-05-02 |  |  | Line11 | ON/OFF | 1SHR(1950)CB 52AS |  | aaqb | B2/D04_A1 | [16 empty] | 394 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 161 | 161kV | 1950 | #1SHR(1950) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_A1 | [16 empty] | 22 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 161 | 161kV | 1950 | #1SHR(1950) |  | RE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_A1 | [16 empty] | 23 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 11 | 11kV | 390 | #1SSTR(390) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | T/1SSTR |  |  | 0146 |  |  | 1-12-02 |  |  | #1 SSTR | ON/OFF | #1SSTR 390 CB 52AS |  | aaab | B3/D04_A1 | [8 empty] | 豐華DS.390_CB | 390(#1SSTR) CB | OTHER | [5 empty] | 471 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 161 | 161kV | 1950 | #1SHR(1950) |  | DS1 | 1951 | ADD | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1032 | 1033 | [9 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1961_DS | 1961(161KV #2SHR) DS | OTHER | [5 empty] | 829 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1950 | #1SHR(1950) |  | DS2 | 1952 | ADD | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1034 | 1035 | [9 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1962_DS | 1962(161KV #2SHR) DS | OTHER | [5 empty] | 830 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 11 | 11kV | 390 | #1SSTR(390) |  | D1 | 391(非取樣點) | B3 | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D04_A1 | [8 empty] | 豐華DS.391 | 391 (非取樣點) | OTHER | [5 empty] | 58 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | 390 | #1SSTR(390) |  | E1 | 391E(非取樣點) | B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D04_A1 | [8 empty] | 豐華DS.391E | 391E (非取樣點) | OTHER | [5 empty] | 59 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | 2ABUS | #2ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0115 |  |  | 1-F3 |  |  | PT-2A | KV | #2A PT R相電壓 | kV_-9_9(-2000_2000) | aba | B3/D04_A1 | [8 empty] | 豐華DS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS | [5 empty] | 237 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D04 | 豐華DS | 11 | 11kV | 390 | #1SSTR(390) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0147 |  |  | 1-12-03 |  |  | #1 SSTR | PHA | #1SSTR 390 RY PHA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.#1SSTR_51A | #1SSTR 51RY | OTHER | [5 empty] | 472 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | 390 | #1SSTR(390) |  | GDA |  | B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0148 |  |  | 1-12-04 |  |  | #1 SSTR | GDA | #1SSTR 390 RY GDA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | [5 empty] | 473 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | 2BBUS | #2BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0151 |  |  | 2-97 |  |  | PT-2B | KV | #2B PT R相電壓 | kV_-9_9(-2000_2000) | bba | B3/D04_A1 | [8 empty] | 豐華DS.11KV#2BBUS_KV | 11KV #2BBUS KV | BUS | [5 empty] | 273 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D04 | 豐華DS | 161 | 161kV | 2BUS | #2BUS |  | V |  | B3 | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0003 |  |  | 1-83 |  |  | 161KV #2BUS | KV | 161KV #2BUS 電壓 | kV_-210_210(-2000_2000) | aab | B2/D04_A1 | [8 empty] | 豐華DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | [5 empty] | 131 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D04 | 豐華DS | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | 15B2E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/2Bus | [13 empty] | aaaz | B2/D04_A1 | [8 empty] | 豐華DS.15B2E | 15B2E (非取樣點) | BUS | [5 empty] | 127 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0053 |  |  | 1-06-05 |  |  | NO.2 BUS | A/N | 161KV NO.2 BUS 87B2A |  |  | B2/D04_A1 | [8 empty] | 豐華DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | [5 empty] | 401 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0860 |  |  | 1-35-12 |  |  | Locate Empty | A/N | 161KV NO.2 BUS欠壓 VUA2 |  |  | B2/D04_A1 | [8 empty] | 豐華DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | [5 empty] | 645 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0874 |  |  | 1-36-10 |  |  | Locate Empty | 87B2S | 161KV #2BUS 87RY U/L |  |  | B2/D04_A1 | [8 empty] | 豐華DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | [5 empty] | 658 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS |  |  | 2DTR | #2DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0817 |  |  | 1-33-01 |  |  | Locate Empty | A/N | NO.2 D.TR.重故障 2TRA |  | a | B1/D04_A1 | [8 empty] | 豐華DS.#2DTR_TRA | #2DTR 重故障 | MTR | [5 empty] | 616 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS |  |  | 2DTR | #2DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | NO.2 DTR. | ℃ | NO.2 DTR. 油溫 | OIL_-120_120(-2000_2000) |  | B1/D04_A1 | [8 empty] | 豐華DS.#2DTR_OIL | #2DTR 油溫 | MTR | [5 empty] | 160 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D04 | 豐華DS |  |  | 2DTR | #2DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0073 |  |  | 1-09-01 |  |  | #2DTR | A/N | NO.2 DTR 87A 87A |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#2DTR_87A | #2DTR 87RY | MTR | [5 empty] | 420 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS |  |  | 2DTR | #2DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-09-02 |  |  | #2DTR | A/N | NO.2 DTR 機械保護動作(96PA) |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | [5 empty] | 421 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS |  |  | 2DTR | #2DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0075 |  |  | 1-09-03 |  |  | #2DTR | A/N | NO.2 DTR 51ZA 51ZA |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | [5 empty] | 422 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS |  |  | 2DTR | #2DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0076 |  |  | 1-09-04 |  |  | #2DTR | PHA | NO.2 DTR PHA PHA |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#2DTR_51A | #2DTR 51RY | MTR | [5 empty] | 423 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS |  |  | 2DTR | #2DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0077 |  |  | 1-09-05 |  |  | #2DTR | GDA | NO.2 DTR GDA GDA |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#2DTR_51NA | #2DTR 51N RY | MTR | [5 empty] | 424 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS |  |  | 2DTR | #2DTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0806 |  |  | 1-32-06 |  |  | Locate Empty | USE/LOCK | NO.2 D.TR. 287S |  |  | B1/D04_A1 | [8 empty] | 豐華DS.161#2DTR_187UL | 161KV #2DTR 187RY U/L | OTHER | [5 empty] | 605 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS |  |  | 2DTR | #2DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0811 |  |  | 1-32-11 |  |  | Locate Empty | A/N | NO.2 D.TR.撲氣電驛(1) 296B1 |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | [5 empty] | 610 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS |  |  | 2DTR | #2DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0812 |  |  | 1-32-12 |  |  | Locate Empty | A/N | NO.2 D.TR.撲氣電驛(2) 296B2 |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | [5 empty] | 611 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS |  |  | 2DTR | #2DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0813 |  |  | 1-32-13 |  |  | Locate Empty | A/N | NO.2 D.TR.放壓裝置 296D |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#2DTR_96D | #2DTR 96D RY | MTR | [5 empty] | 612 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS |  |  | 2DTR | #2DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0814 |  |  | 1-32-14 |  |  | Locate Empty | A/N | NO.2 D.TR.衝擊油壓 296P |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#2DTR_96P | #2DTR 96P RY | MTR | [5 empty] | 613 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS |  |  | 2DTR | #2DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0815 |  |  | 1-32-15 |  |  | Locate Empty | A/N | NO.2 D.TR. ULTC 263Q |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#2DTR_63Q | #2DTR 63Q RY | MTR | [5 empty] | 614 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS |  |  | 2DTR | #2DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0816 |  |  | 1-33-00 |  |  | Locate Empty | A/N | NO.2 D.TR.輕故障 2TRF |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#2DTR_TRF | #2DTR 輕故障 | MTR | [5 empty] | 615 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2DTR |  | 0072 |  |  | 1-09-00 |  |  | #2DTR | ON/OFF | NO.2 1760 CB 52AS |  | aaeb | ELEM/D04_A1 | [8 empty] | 豐華DS.1760_CB | 1760(#2DTR) CB | MTR | [5 empty] | 419 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS |  |  | 2DTR | #2DTR |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0920 |  |  | 1-39-08 |  |  | Locate Empty |  |  |  |  | B1/D04_A1 | [8 empty] | 豐華DS.161#2DTR_287UL | 161KV #2DTR 287RY U/L | OTHER | [5 empty] | 701 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS |  |  | 2DTR | #2DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0921 |  |  | 1-39-09 |  |  | Locate Empty |  |  |  |  | B1/D04_A1 | [8 empty] | 豐華DS.161#2DTR_51ZUL | 161KV #2DTR 51ZRY U/L | OTHER | [5 empty] | 702 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS |  |  | 2DTR | #2DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0922 |  |  | 1-39-10 |  |  | Locate Empty |  |  |  |  | B1/D04_A1 | [8 empty] | 豐華DS.161#2DTR_RYFA | 161KV #2DTR RYFA | OTHER | [5 empty] | 703 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS |  |  | 2DTR | #2DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0117 | [10 empty] | B1/D04_A1 | [16 empty] | 827 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1760TE | 1760TE (非取樣點) | MTR | [5 empty] | 34 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1760BE | 1760BE (非取樣點) | MTR | [5 empty] | 35 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | T/2DTR(A) |  |  | 0080 |  |  | 1-0A-00 |  |  | D2A | ON/OFF | D2A 330 CB 52AS |  | abba | ELEM/D04_A1 | [8 empty] | 豐華DS.330_CB | 330(#2DTR) CB | MTR | [5 empty] | 427 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1048 | 1049 |  | 2-31-08 | 2-31-09 |  | Locate Empty | ON | NO.2 DTR(1761) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1761_DS | 1761(#2DTR) DS | MTR | [5 empty] | 751 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1050 | 1051 |  | 2-31-10 | 2-31-11 |  | Locate Empty | ON | NO.2 DTR(1762) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1762_DS | 1762(#2DTR) DS | MTR | [5 empty] | 752 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS |  |  | 2DTR(A) | #2DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | NO.2 DTR.A | ℃ | NO.2 DTR.A 線溫 | COIL_-120_120(-2000_2000) |  | B1/D04_A1 | [8 empty] | 豐華DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | [5 empty] | 161 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D04 | 豐華DS |  |  | 2DTR(A) | #2DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | NO.2 DTR.A | 升/降 | NO.2 DTR.A TAP | TAP_-8.5_8.5(0_2000) |  | B1/D04_A1 | [8 empty] | 豐華DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | [5 empty] | 163 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D04 | 豐華DS |  |  | 2DTR(A) | #2DTR(A) |  | SupLocal |  | B3 | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0807 |  |  | 1-32-07 |  |  | Locate Empty | 遙控/現場 | NO.2 D.TR. S/L (A) 243R1S3 |  | c | B1/D04_A1 | [8 empty] | 豐華DS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | [5 empty] | 606 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D04 | 豐華DS |  |  | 2DTR(A) | #2DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0808 |  |  | 1-32-08 |  |  | Locate Empty | OLTC A/M | NO.2 D.TR. A/M (A) 2AX-S1 |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | [5 empty] | 607 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D04 | 豐華DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | D1 | 331(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D04_A1 | [8 empty] | 豐華DS.331 | 331 (非取樣點) | MTR | [5 empty] | 36 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | E1 | 331E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D04_A1 | [8 empty] | 豐華DS.331E | 331E (非取樣點) | MTR | [5 empty] | 37 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | D2A | MW | D2A 330 瓦 | MW_-54_54(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | [5 empty] | 232 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | D2A | MVAR | D2A 330 乏 | MVAR_-36_36(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | [5 empty] | 233 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | D2A | A | D2A 330 R 相電流 | A_-3000_3000(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | [5 empty] | 234 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | D2A | A | D2A 330 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | [5 empty] | 235 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | D2A | A | D2A 330 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | [5 empty] | 236 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0078 |  |  | 1-09-06 |  |  | D2A | PHA | D2A 330 (51-3φ)PHA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.330_51A | #2DTR二次側(330) 51RY | MTR | [5 empty] | 425 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | T/2DTR(B) |  |  | 0083 |  |  | 1-0A-03 |  |  | D2B | ON/OFF | D2B 340 CB 52AS |  | bbca | ELEM/D04_A1 | [8 empty] | 豐華DS.340_CB | 340(#2DTR) CB | MTR | [5 empty] | 430 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0081 |  |  | 1-0A-01 |  |  | D2A | PHA | D2A 330 PHA PHA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.330_PHA2 | 330開關箱IED RY PHA | OTHER | [5 empty] | 428 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0082 |  |  | 1-0A-02 |  |  | D2A | GDA | D2A 330 GDA GDA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.330_GDA | 330開關箱IED RY GDA | OTHER | [5 empty] | 429 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS |  |  | 2DTR(B) | #2DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | NO.2 DTR.B | ℃ | NO.2 DTR.B 線溫 | COIL_-120_120(-2000_2000) |  | B1/D04_A1 | [8 empty] | 豐華DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | [5 empty] | 162 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D04 | 豐華DS |  |  | 2DTR(B) | #2DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | NO.2 DTR.B | 升/降 | NO.2 DTR.B TAP | TAP_-8.5_8.5(0_2000) |  | B1/D04_A1 | [8 empty] | 豐華DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | [5 empty] | 164 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D04 | 豐華DS |  |  | 2DTR(B) | #2DTR(B) |  | SupLocal |  | B3 | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0809 |  |  | 1-32-09 |  |  | Locate Empty | 遙控/現場 | NO.2 D.TR. S/L (B) 243R2S3 |  | b | B1/D04_A1 | [8 empty] | 豐華DS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | [5 empty] | 608 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D04 | 豐華DS |  |  | 2DTR(B) | #2DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0810 |  |  | 1-32-10 |  |  | Locate Empty | OLTC A/M | NO.2 D.TR. A/M (B) 2AX-S2 |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | [5 empty] | 609 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D04 | 豐華DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | D1 | 341(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D04_A1 | [8 empty] | 豐華DS.341 | 341 (非取樣點) | MTR | [5 empty] | 38 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | E1 | 341E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D04_A1 | [8 empty] | 豐華DS.341E | 341E (非取樣點) | MTR | [5 empty] | 39 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0146 |  |  | 2-92 |  |  | D2B | MW | D2B 340 瓦 | MW_-54_54(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | [5 empty] | 268 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0147 |  |  | 2-93 |  |  | D2B | MVAR | D2B 340 乏 | MVAR_-36_36(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | [5 empty] | 269 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0148 |  |  | 2-94 |  |  | D2B | A | D2B 340 R 相電流 | A_-3000_3000(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | [5 empty] | 270 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0149 |  |  | 2-95 |  |  | D2B | A | D2B 340 S 相電流 | A_-3000_3000(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | [5 empty] | 271 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0150 |  |  | 2-96 |  |  | D2B | A | D2B 340 T 相電流 | A_-3000_3000(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | [5 empty] | 272 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0079 |  |  | 1-09-07 |  |  | D2B | PHA | D2B 340 (51-3φ)PHA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.340_51A | #2DTR二次側(340) 51RY | MTR | [5 empty] | 426 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | 220 | #2SC(220) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | A/LBS220^C/2SC(A) |  |  | 0164 |  |  | 1-14-04 |  |  | #2SC | ON/OFF | #2SC 220 CB 52AS |  | babb | B3/D04_A1 | [8 empty] | 豐華DS.220_CB | 220(11KV #2SC) CB | SC | [5 empty] | 489 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0084 |  |  | 1-0A-04 |  |  | D2B | PHA | D2B 340 PHA PHA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.340_PHA2 | 340開關箱IED RY PHA | OTHER | [5 empty] | 431 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0085 |  |  | 1-0A-05 |  |  | D2B | GDA | D2B 340 GDA GDA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.340_GDA | 340開關箱IED RY GDA | OTHER | [5 empty] | 432 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | 220 | #2SC(220) |  | E1 | 221E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D04_A1 | [8 empty] | 豐華DS.221E | 221E (非取樣點) | SC | [5 empty] | 70 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | 220 | #2SC(220) |  | D1 | 221(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D04_A1 | [8 empty] | 豐華DS.221 | 221 (非取樣點) | SC | [5 empty] | 71 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 161 | 161kV | 1960 | #2SHR(1960) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | R/2SHR |  | 0046 |  |  | 1-05-06 |  |  | Line12 | ON/OFF | 2SHR(1960)CB 52AS |  | aarb | B2/D04_A1 | [8 empty] | 豐華DS.1960_CB | 1960(161KV #2SHR) CB | OTHER | [5 empty] | 395 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0165 |  |  | 1-14-05 |  |  | #2SC | SCA | #2SC 220 CB RY SCA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.220_SCA | 11KV #2SC 51,51N RY | SC | [5 empty] | 490 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0166 |  |  | 1-14-06 |  |  | #2SC | UVA | #2SC 220 CB RY UVA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | [5 empty] | 491 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | 490 | #2SSTR(490) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | T/2SSTR |  |  | 0330 |  |  | 2-09-02 |  |  | #2 SSTR | ON/OFF | #2SSTR 490 CB 52AS |  | bbbb | B3/D04_A1 | [8 empty] | 豐華DS.490_CB | 490(#2SSTR) CB | OTHER | [5 empty] | 534 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 161 | 161kV | 1960 | #2SHR(1960) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1960BE | 1960BE(非取樣點) | OTHER | [5 empty] | 24 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1960 | #2SHR(1960) |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0128 |  |  | 1-C0 |  |  | Locate Empty | ℃ | 2SHR(1960)線溫 | COIL_-120_120(-2000_2000) | [10 empty] | 豐華DS.161#2SHR_COIL | 161KV #2SHR 線溫 | OTHER | [5 empty] | 250 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D04 | 豐華DS | 161 | 161kV | 1960 | #2SHR(1960) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0129 |  |  | 1-C1 |  |  | Locate Empty | ℃ | 2SHR(1960)油溫 | OIL_-120_120(-2000_2000) | [10 empty] | 豐華DS.161#2SHR_OIL | 161KV #2SHR 油溫 | OTHER | [5 empty] | 251 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D04 | 豐華DS | 161 | 161kV | 1960 | #2SHR(1960) |  | RE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1960RE | 1960RE(非取樣點) | OTHER | [5 empty] | 25 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 22 | 22kV | 3BUS | #3BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0185 |  |  | 2-B9 |  |  | PT-3 | KV | #3 PT R相電壓 | kV_-18_18(-2000_2000) | aca | B3/D04_A1 | [8 empty] | 豐華DS.23KV#3BUS_KV | 23KV #3BUS KV | BUS | [5 empty] | 307 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D04 | 豐華DS | 161 | 161kV | 1960 | #2SHR(1960) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0047 |  |  | 1-05-07 |  |  | Line12 | 85A | 2SHR(1960)RY 87A |  |  | B2/D04_A1 | [8 empty] | 豐華DS.161#2SHR_87A | 161KV #2SHR 87RY | OTHER | [5 empty] | 396 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1960 | #2SHR(1960) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0049 |  |  | 1-06-01 |  |  | Line12 | GDA | 2SHR(1960)RY 51A |  |  | B2/D04_A1 | [8 empty] | 豐華DS.161#2SHR_51A | 161KV #2SHR 51RY | OTHER | [5 empty] | 397 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1960 | #2SHR(1960) |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0898 |  |  | 1-38-02 |  |  | L12 |  | 2SHR RY 故障 12RYFA |  |  | B2/D04_A1 | [8 empty] | 豐華DS.161_2SHR_RYFA | 161KV 2SHR(1960)數位電驛故障 | OTHER | [5 empty] | 681 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1960 | #2SHR(1960) |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0048 | [10 empty] | B2/D04_A1 | [16 empty] | 817 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 161 | 161kV | 1960 | #2SHR(1960) |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1236 | [10 empty] | B2/D04_A1 | [16 empty] | 818 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 161 | 161kV | 1960 | #2SHR(1960) |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1237 | [10 empty] | B2/D04_A1 | [16 empty] | 819 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 161 | 161kV | 1960 | #2SHR(1960) |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1234 | [10 empty] | B2/D04_A1 | [16 empty] | 820 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 161 | 161kV | 1960 | #2SHR(1960) |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1235 | [10 empty] | B2/D04_A1 | [16 empty] | 821 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 161 | 161kV | 1960 | #2SHR(1960) |  | 51_UL |  |  | Status | 51RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1227 | [10 empty] | B2/D04_A1 | [16 empty] | 822 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 161 | 161kV | 1960 | #2SHR(1960) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1226 | [10 empty] | B2/D04_A1 | [16 empty] | 823 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 161 | 161kV | 1960 | #2SHR(1960) |  | SHRA |  |  | Status | 電抗器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1239 | [10 empty] | B2/D04_A1 | [16 empty] | 824 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 161 | 161kV | 1960 | #2SHR(1960) |  | SHRF |  |  | Status | 電抗器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1238 | [10 empty] | B2/D04_A1 | [16 empty] | 825 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 161 | 161kV | 1960 | #2SHR(1960) |  | DS1 | 1961 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1032 | 1033 | [9 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1961_DS | 1961(161KV #2SHR) DS | OTHER | [5 empty] | 829 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1960 | #2SHR(1960) |  | DS2 | 1962 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1034 | 1035 | [9 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1962_DS | 1962(161KV #2SHR) DS | OTHER | [5 empty] | 830 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 11 | 11kV | 490 | #2SSTR(490) |  | D1 | 491(非取樣點) | B3 | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D04_A1 | [8 empty] | 豐華DS.491 | 491 (非取樣點) | OTHER | [5 empty] | 104 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | 490 | #2SSTR(490) |  | E1 | 491E(非取樣點) | B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D04_A1 | [8 empty] | 豐華DS.491E | 491E (非取樣點) | OTHER | [5 empty] | 105 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS |  |  | 3DTR | #3DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR |  |  |  |  | 0827 |  |  | 1-33-11 |  |  | Locate Empty | A/N | NO.3 D.TR.重故障 3TRA |  | a | B1/D04_A1 | [8 empty] | 豐華DS.#3DTR_TRA | #3DTR 重故障 | MTR | [5 empty] | 626 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | 490 | #2SSTR(490) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0331 |  |  | 2-09-03 |  |  | #2 SSTR | PHA | #2SSTR 490 RY PHA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.#2SSTR_51A | #2SSTR 51RY | OTHER | [5 empty] | 535 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | 490 | #2SSTR(490) |  | GDA |  | B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0332 |  |  | 2-09-04 |  |  | #2 SSTR | GDA | #2SSTR 490 RY GDA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | [5 empty] | 536 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/3DTR |  | 0086 |  |  | 1-0A-06 |  |  | #3DTR | ON/OFF | NO.3 1770 CB 52AS |  | aakb | ELEM/D04_A1 | [8 empty] | 豐華DS.1770_CB | 1770(#3DTR) CB | MTR | [5 empty] | 433 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS |  |  | 3DTR | #3DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | NO.3 DTR. | ℃ | NO.3 DTR. 油溫 | OIL_-120_120(-2000_2000) |  | B1/D04_A1 | [8 empty] | 豐華DS.#3DTR_OIL | #3DTR 油溫 | MTR | [5 empty] | 165 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D04 | 豐華DS |  |  | 3DTR | #3DTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | NO.3 DTR. | ℃ | NO.3 DTR. 線溫 | COIL_-120_120(-2000_2000) |  | B1/D04_A1 | [8 empty] | 豐華DS.#3DTR_COIL | #3DTR 線溫 | MTR | [5 empty] | 166 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D04 | 豐華DS |  |  | 3DTR | #3DTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | NO.3 DTR. | 升/降 | NO.3 DTR. TAP | TAP_-8.5_8.5(0_2000) |  | B1/D04_A1 | [8 empty] | 豐華DS.#3DTR_TAP | #3DTR OLTC TAP | MTR | [5 empty] | 167 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D04 | 豐華DS |  |  | 3DTR | #3DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0087 |  |  | 1-0A-07 |  |  | #3DTR | A/N | NO.3 DTR 87A 87A |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#3DTR_87A | #3DTR 87RY | MTR | [5 empty] | 434 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS |  |  | 3DTR | #3DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0088 |  |  | 1-0B-00 |  |  | #3DTR | A/N | NO.3 DTR 機械保護動作(96PA) |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#3DTR_96PA | #3DTR 機械保護動作 | MTR | [5 empty] | 435 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS |  |  | 3DTR | #3DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0089 |  |  | 1-0B-01 |  |  | #3DTR | A/N | NO.3 DTR 51ZA 51ZA |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#3DTR_51ZA | #3DTR 51Z RY | MTR | [5 empty] | 436 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS |  |  | 3DTR | #3DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0090 |  |  | 1-0B-02 |  |  | #3DTR | PHA | NO.3 DTR PHA PHA |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#3DTR_51A | #3DTR 51RY | MTR | [5 empty] | 437 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS |  |  | 3DTR | #3DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0091 |  |  | 1-0B-03 |  |  | #3DTR | GDA | NO.3 DTR GDA GDA |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#3DTR_51NA | #3DTR 51N RY | MTR | [5 empty] | 438 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS |  |  | 3DTR | #3DTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0818 |  |  | 1-33-02 |  |  | Locate Empty | USE/LOCK | NO.3 D.TR. 387S |  |  | B1/D04_A1 | [8 empty] | 豐華DS.161#3DTR_187UL | 161KV #3DTR 187RY U/L | OTHER | [5 empty] | 617 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS |  |  | 3DTR | #3DTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0819 |  |  | 1-33-03 |  |  | Locate Empty | 遙控/現場 | NO.3 D.TR. S/L 343R1S3 |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#3DTR_S/L | #3DTR OLTC S/L | MTR | [5 empty] | 618 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D04 | 豐華DS |  |  | 3DTR | #3DTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0820 |  |  | 1-33-04 |  |  | Locate Empty | OLTC A/M | NO.3 D.TR. A/M 3AX-S |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#3DTR_A/M | #3DTR OLTC A/M | MTR | [5 empty] | 619 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D04 | 豐華DS |  |  | 3DTR | #3DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0821 |  |  | 1-33-05 |  |  | Locate Empty | A/N | NO.3 D.TR.撲氣電驛(1) 396B1 |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#3DTR_96B1 | #3DTR 96B1 RY | MTR | [5 empty] | 620 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS |  |  | 3DTR | #3DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0822 |  |  | 1-33-06 |  |  | Locate Empty | A/N | NO.3 D.TR.撲氣電驛(2) 396B2 |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#3DTR_96B2 | #3DTR 96B2 RY | MTR | [5 empty] | 621 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS |  |  | 3DTR | #3DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0823 |  |  | 1-33-07 |  |  | Locate Empty | A/N | NO.3 D.TR.放壓裝置 396D |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#3DTR_96D | #3DTR 96D RY | MTR | [5 empty] | 622 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS |  |  | 3DTR | #3DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0824 |  |  | 1-33-08 |  |  | Locate Empty | A/N | NO.3 D.TR.衝擊油壓 396P |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#3DTR_96P | #3DTR 96P RY | MTR | [5 empty] | 623 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS |  |  | 3DTR | #3DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0825 |  |  | 1-33-09 |  |  | Locate Empty | A/N | NO.3 D.TR. ULTC 363Q |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#3DTR_63Q | #3DTR 63Q RY | MTR | [5 empty] | 624 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS |  |  | 3DTR | #3DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0826 |  |  | 1-33-10 |  |  | Locate Empty | A/N | NO.3 D.TR.輕故障 3TRF |  |  | B1/D04_A1 | [8 empty] | 豐華DS.#3DTR_TRF | #3DTR 輕故障 | MTR | [5 empty] | 625 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | 350 | #3DTR(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3Bus | T/3DTR |  |  | 0093 |  |  | 1-0B-05 |  |  | D3 | ON/OFF | D3 350 CB 52AS |  | acaa | ELEM/D04_A1 | [8 empty] | 豐華DS.350_CB | 350(#3DTR) CB | MTR | [5 empty] | 440 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS |  |  | 3DTR | #3DTR |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0923 |  |  | 1-39-11 |  |  | Locate Empty |  |  |  |  | B1/D04_A1 | [8 empty] | 豐華DS.161#3DTR_287UL | 161KV #3DTR 287RY U/L | OTHER | [5 empty] | 704 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS |  |  | 3DTR | #3DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0924 |  |  | 1-39-12 |  |  | Locate Empty |  |  |  |  | B1/D04_A1 | [8 empty] | 豐華DS.161#3DTR_51ZUL | 161KV #3DTR 51ZRY U/L | OTHER | [5 empty] | 705 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS |  |  | 3DTR | #3DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0925 |  |  | 1-39-13 |  |  | Locate Empty |  |  |  |  | B1/D04_A1 | [8 empty] | 豐華DS.161#3DTR_RYFA | 161KV #3DTR RYFA | OTHER | [5 empty] | 706 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS |  |  | 3DTR | #3DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0118 | [10 empty] | B1/D04_A1 | [16 empty] | 828 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1770TE | 1770TE (非取樣點) | MTR | [5 empty] | 40 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1770BE | 1770BE (非取樣點) | MTR | [5 empty] | 41 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | 230 | #3SC(230) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | A/LBS230^C/3SC(A) |  |  | 0303 |  |  | 2-05-07 |  |  | #3SC | ON/OFF | #3SC 230 CB 52AS |  | abcb | B3/D04_A1 | [8 empty] | 豐華DS.230_CB | 230(11KV #3SC) CB | SC | [5 empty] | 507 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1052 | 1053 |  | 2-31-12 | 2-31-13 |  | Locate Empty | ON | NO.3 DTR(1771) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1771_DS | 1771(#3DTR) DS | MTR | [5 empty] | 753 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1054 | 1055 |  | 2-31-14 | 2-31-15 |  | Locate Empty | ON | NO.3 DTR(1772) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1772_DS | 1772(#3DTR) DS | MTR | [5 empty] | 754 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 22 | 22kV | 350 | #3DTR(350) |  | D1 | 351(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D04_A1 | [8 empty] | 豐華DS.351 | 351 (非取樣點) | MTR | [5 empty] | 42 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 22 | 22kV | 350 | #3DTR(350) |  | E1 | 351E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D04_A1 | [8 empty] | 豐華DS.351E | 351E (非取樣點) | MTR | [5 empty] | 43 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 22 | 22kV | 350 | #3DTR(350) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0180 |  |  | 2-B4 |  |  | D3 | MW | D3 350 瓦 | MW_-108_108(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.#3DTR_MW | #3DTR二次側 MW | MTR | [5 empty] | 302 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.216 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 350 | #3DTR(350) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0181 |  |  | 2-B5 |  |  | D3 | MVAR | D3 350 乏 | MVAR_-72_72(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.#3DTR_MVAR | #3DTR二次側 MVAR | MTR | [5 empty] | 303 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 350 | #3DTR(350) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0182 |  |  | 2-B6 |  |  | D3 | A | D3 350 R 相電流 | A_-3000_3000(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.#3DTR_A1 | #3DTR二次側 R相AMP | MTR | [5 empty] | 304 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 350 | #3DTR(350) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0183 |  |  | 2-B7 |  |  | D3 | A | D3 350 S 相電流 | A_-3000_3000(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.#3DTR_A2 | #3DTR二次側 S相AMP | MTR | [5 empty] | 305 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 350 | #3DTR(350) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0184 |  |  | 2-B8 |  |  | D3 | A | D3 350T 相電流 | A_-3000_3000(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.#3DTR_A3 | #3DTR二次側 T相AMP | MTR | [5 empty] | 306 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 350 | #3DTR(350) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0092 |  |  | 1-0B-04 |  |  | D3 | PHA | D3 350 (51-3φ)PHA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.350_51A | #3DTR二次側(350) 51RY | MTR | [5 empty] | 439 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1780 | #4DTR(1780) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/4DTR |  | 0096 |  |  | 1-0C-00 |  |  | #4DTR | ON/OFF | NO.4 1780 CB 52AS |  | aanb | ELEM/D04_A1 | [8 empty] | 豐華DS.1780_CB | 1780(#4DTR) CB | MTR | [5 empty] | 443 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 22 | 22kV | 350 | #3DTR(350) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0094 |  |  | 1-0B-06 |  |  | D3 | PHA | D3 350 PHA PHA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.350_PHA2 | 350開關箱IED RY PHA | OTHER | [5 empty] | 441 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | 350 | #3DTR(350) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0095 |  |  | 1-0B-07 |  |  | D3 | GDA | D3 350 GDA GDA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.350_GDA | 350開關箱IED RY GDA | OTHER | [5 empty] | 442 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | 230 | #3SC(230) |  | E1 | 231E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D04_A1 | [8 empty] | 豐華DS.231E | 231E (非取樣點) | SC | [5 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | 230 | #3SC(230) |  | D1 | 231(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D04_A1 | [8 empty] | 豐華DS.231 | 231 (非取樣點) | SC | [5 empty] | 83 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | 240 | #4SC(240) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | A/LBS240^C/4SC(A) |  |  | 0324 |  |  | 2-08-04 |  |  | #4SC | ON/OFF | #4SC 240 CB 52AS |  | bbdb | B3/D04_A1 | [8 empty] | 豐華DS.240_CB | 240(11KV #4SC) CB | SC | [5 empty] | 528 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | 230 | #3SC(230) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0304 |  |  | 2-06-00 |  |  | #3SC | SCA | #3SC 230 RY SCA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.230_SCA | 11KV #3SC 51,51N RY | SC | [5 empty] | 508 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | 230 | #3SC(230) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0305 |  |  | 2-06-01 |  |  | #3SC | UVA | #3SC 230 RY UVA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | [5 empty] | 509 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | 250 | #5SC(250) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3Bus | C/5SC |  |  | 0345 |  |  | 2-0B-01 |  |  | #5SC | ON/OFF | #5SC 250 CB 52AS |  | acbb | B3/D04_A1 | [8 empty] | 豐華DS.250_CB | 250(23KV #5SC) CB | SC | [5 empty] | 549 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 161 | 161kV | 1780 | #4DTR(1780) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1780TE | 1780TE (非取樣點) | MTR | [5 empty] | 44 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1780 | #4DTR(1780) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1780BE | 1780BE (非取樣點) | MTR | [5 empty] | 45 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 22 | 22kV | 260 | #6SC(260) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3Bus | C/6SC |  |  | 0360 |  |  | 2-0D-00 |  |  | #6SC | ON/OFF | #6SC 260 CB 52AS |  | aclb | B3/D04_A1 | [8 empty] | 豐華DS.260_CB | 260(23KV #6SC) CB | SC | [5 empty] | 564 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 161 | 161kV | 1780 | #4DTR(1780) |  | DS1 | 1781 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1056 | 1057 |  | 2-32-00 | 2-32-01 |  | Locate Empty | ON | NO.4 DTR(1781) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1781_DS | 1781(#4DTR) DS | MTR | [5 empty] | 755 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1780 | #4DTR(1780) |  | DS2 | 1782 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1058 | 1059 |  | 2-32-02 | 2-32-03 |  | Locate Empty | ON | NO.4 DTR(1782) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1782_DS | 1782(#4DTR) DS | MTR | [5 empty] | 756 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 11 | 11kV | 240 | #4SC(240) |  | E1 | 241E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D04_A1 | [8 empty] | 豐華DS.241E | 241E (非取樣點) | SC | [5 empty] | 98 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | 240 | #4SC(240) |  | D1 | 241(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D04_A1 | [8 empty] | 豐華DS.241 | 241 (非取樣點) | SC | [5 empty] | 99 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | 100 | TIE(100) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/2ABus | B/1ABus |  |  | 0306 |  |  | 2-06-02 |  |  | TIE-2A | ON/OFF | TIE-2A 100 CB 52AS |  | abab | B3/D04_A1 | [8 empty] | 豐華DS.100_CB | 100(TIE) CB | TIE | [5 empty] | 510 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | 240 | #4SC(240) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0325 |  |  | 2-08-05 |  |  | #4SC | SCA | #4SC 240 RY SCA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.240_SCA | 11KV #4SC 51,51N RY | SC | [5 empty] | 529 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | 240 | #4SC(240) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0326 |  |  | 2-08-06 |  |  | #4SC | UVA | #4SC 240 RY UVA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.240_UVA | 11KV #4SC 27RY(欠壓) | SC | [5 empty] | 530 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0050 |  |  | 1-06-02 |  |  | 161KV TIE | ON/OFF | TIE(1500)CB 52AS |  | aafz | B2/D04_A1 | [8 empty] | 豐華DS.1500_CB | 1500(TIE) CB | TIE | [5 empty] | 398 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 22 | 22kV | 250 | #5SC(250) |  | E1 | 251E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D04_A1 | [8 empty] | 豐華DS.251E | 251E (非取樣點) | SC | [5 empty] | 114 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 22 | 22kV | 250 | #5SC(250) |  | D1 | 251(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D04_A1 | [8 empty] | 豐華DS.251 | 251 (非取樣點) | SC | [5 empty] | 115 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | 200 | TIE(200) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/2BBus | B/1BBus |  |  | 0327 |  |  | 2-08-07 |  |  | TIE-2B | ON/OFF | TIE-2B 200 CB 52AS |  | bbab | B3/D04_A1 | [8 empty] | 豐華DS.200_CB | 200(TIE) CB | TIE | [5 empty] | 531 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 22 | 22kV | 250 | #5SC(250) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0346 |  |  | 2-0B-02 |  |  | #5SC | SCA | #5SC 250 RY SCA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.250_SCA | 23KV #5SC 51,51N RY | SC | [5 empty] | 550 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | 250 | #5SC(250) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0347 |  |  | 2-0B-03 |  |  | #5SC | UVA | #5SC 250 RY UVA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.250_UVA | 23KV #5SC 27RY(欠壓) | SC | [5 empty] | 551 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | 260 | #6SC(260) |  | E1 | 261E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D04_A1 | [8 empty] | 豐華DS.261E | 261E (非取樣點) | SC | [5 empty] | 124 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 22 | 22kV | 260 | #6SC(260) |  | D1 | 261(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D04_A1 | [8 empty] | 豐華DS.261 | 261 (非取樣點) | SC | [5 empty] | 125 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 161 | 161kV | 1550 | 三竹～豐華一路(1550) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D02D041/T2 |  | 0018 |  |  | 1-02-02 |  |  | L5 | ON/OFF | 三竹豐華一路(1550)CB 52AS |  | aaia | B2/D04_A1 | [8 empty] | 豐華DS.1550_CB | 1550(三竹豐華一路) CB | LINE161 | [5 empty] | 370 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 22 | 22kV | 260 | #6SC(260) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0361 |  |  | 2-0D-01 |  |  | #6SC | SCA | #6SC 260 RY SCA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.260_SCA | 23KV #6SC 51,51N RY | SC | [5 empty] | 565 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | 260 | #6SC(260) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0362 |  |  | 2-0D-02 |  |  | #6SC | UVA | #6SC 260 RY UVA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.260_UVA | 23KV #6SC 27RY(欠壓) | SC | [5 empty] | 566 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | RTU | RTU |  | ADCL1 |  |  | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.AI_ADCL1 | AI10%參考點 ADCL1 | OTHER | [5 empty] | 128 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 0 |  | RTU | RTU |  | ADCH1 |  |  | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.1 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.AI_ADCH1 | AI90%參考點 ADCH1 | OTHER | [5 empty] | 129 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 0 |  | RTU | RTU |  | ADCL2 |  |  | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1- |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.4 AI Card) |  |  |  |  | B3/D04_A1 | [12 empty] | CDC_Mon1_DPC |  |  |  | 186 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 0 |  | RTU | RTU |  | ADCH2 |  |  | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1- |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.4 AI Card) |  |  |  |  | B3/D04_A1 | [12 empty] | CDC_Mon1_DPC |  |  |  | 187 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 0 |  | RTU | RTU |  | ADCL4 |  |  | MvMoment | No4 AI參考點 10% |  | Y |  | AI | [6 empty] | 0192 |  |  | 2-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.4 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.AI_ADCL4 | AI10%參考點 ADCL4 | OTHER | [5 empty] | 314 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 0 |  | RTU | RTU |  | ADCH4 |  |  | MvMoment | No4 AI參考點 90% |  | Y |  | AI | [6 empty] | 0193 |  |  | 2-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.4 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.AI_ADCH4 | AI90%參考點 ADCH4 | OTHER | [5 empty] | 315 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 0 |  | RTU | RTU |  | ADCL5 |  |  | MvMoment | No5 AI參考點 10% |  | Y |  | AI | [6 empty] | 0256 |  |  | 3-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.5 AI Card) |  |  |  |  | B3/D04_A1 | [16 empty] | 350 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 0 |  | RTU | RTU |  | ADCH5 |  |  | MvMoment | No5 AI參考點 90% |  | Y |  | AI | [6 empty] | 0257 |  |  | 3-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.5 AI Card) |  |  |  |  | B3/D04_A1 | [16 empty] | 351 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 0 |  | RTU | RTU |  | RTU_MCT |  |  | Status | RTU Master Ry | Open/Close | Y | E | DI-SP | [6 empty] | 0114 |  |  | 1-0E-02 |  |  | 161RTU | MCT_ SOE | RTU Master Ry SOE |  |  | B3/D04_A1 | [16 empty] | 451 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 0 |  | RTU | RTU |  | RTUA |  |  | Status | RTU故障警報 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0115 |  |  | 1-0E-03 |  |  | RTU | RTUA | RTU發生異常 |  |  | B3/D04_A1 | [8 empty] | 豐華DS.RTUA | RTU發生異常 | OTHER | [5 empty] | 452 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0768 |  |  | 1-30-00 |  |  | Test CB | ON/OFF | TEST C.B. |  |  | ELEM/ALL | [8 empty] | 豐華DS.TEST_CB | TEST CB | OTHER | [5 empty] | 569 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | RTU | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0769 |  |  | 1-30-01 |  |  | Locate Empty | L/R | LOCAL/REMOTE STATUS |  |  | ELEM/D04_A1 | [8 empty] | 豐華DS.RTU_S/L | RTU SUPY/LOCAL | OTHER | [5 empty] | 570 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
D04 | 豐華DS | 11 | 11kV | 100 | TIE(100) |  | D1 | 101(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D04_A1 | [8 empty] | 豐華DS.101 | 101 (非取樣點) | TIE | [5 empty] | 84 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | 100 | TIE(100) |  | D2 | 102(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D04_A1 | [8 empty] | 豐華DS.102 | 102 (非取樣點) | TIE | [5 empty] | 85 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | 100 | TIE(100) |  | E1 | 101E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D04_A1 | [8 empty] | 豐華DS.101E | 101E(非取樣點) | OTHER | [5 empty] | 86 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | 100 | TIE(100) |  | E2 | 102E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D04_A1 | [8 empty] | 豐華DS.102E | 102E(非取樣點) | OTHER | [5 empty] | 87 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | 100 | TIE(100) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0143 |  |  | 2-8F |  |  | TIE-2A | A | TIE-2A 100 R 相電流 | A_-2000_2000(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.11KV_100_A1 | 11KV 100 R相AMP | TIE | [5 empty] | 265 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 100 | TIE(100) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0144 |  |  | 2-90 |  |  | TIE-2A | A | TIE-2A 100 S 相電流 | A_-2000_2000(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.11KV_100_A2 | 11KV 100 S相AMP | TIE | [5 empty] | 266 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 100 | TIE(100) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0145 |  |  | 2-91 |  |  | TIE-2A | A | TIE-2A 100 T 相電流 | A_-2000_2000(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.11KV_100_A3 | 11KV 100 T相AMP | TIE | [5 empty] | 267 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1560 | 三竹～豐華二路(1560) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D02D042/T2 |  | 0022 |  |  | 1-02-06 |  |  | L6 | ON/OFF | 三竹豐華二路(1560)CB 52AS |  | aaja | B2/D04_A1 | [8 empty] | 豐華DS.1560_CB | 1560(三竹豐華二路) CB | LINE161 | [5 empty] | 374 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | 100 | TIE(100) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0307 |  |  | 2-06-03 |  |  | TIE-2A | PHA | TIE-2A 100 RY PHA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.100_51A | 11KV TIE(100) 51RY | TIE | [5 empty] | 511 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | 100 | TIE(100) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0308 |  |  | 2-06-04 |  |  | TIE-2A | GDA | TIE-2A 100 RY GDA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.100_51NA | 11KV TIE(100) 51N RY | TIE | [5 empty] | 512 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1501E | 1501E (非取樣點) | TIE | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1502E | 1502E (非取樣點) | TIE | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1500 | TIE(1500) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | 161KV TIE | A | (1500) R相電流 | A_-2000_2000(-2000_2000) |  | B2/D04_A1 | [8 empty] | 豐華DS.1500TIE_AMP | 1500TIE AMP | TIE | [5 empty] | 154 |  |  |  |  | AI | [5 empty] | C20R1600 | 1520 | 1600 | 1760 | 1968 | 2.27 | -1520 | -1600 | -1760 | -1968 | 1 | 0.01 | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1570 | 安南～王行、豐華線(1570) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D04TN15R/T2 |  | 0026 |  |  | 1-03-02 |  |  | L7 | ON/OFF | 山上安南豐華紅線(1570)CB 52AS |  | aala | B2/D04_A1 | [8 empty] | 豐華DS.1570_CB | 1570(山上安南紅線) CB | LINE161 | [5 empty] | 378 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0051 |  |  | 1-06-03 |  |  | 161KV TIE | A/N | TIE(1500)RY 50A |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1500_50A | 161KV TIE(1500) 50RY | TIE | [5 empty] | 399 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0875 |  |  | 1-36-11 |  |  | 161KV TIE | 測試/正常 | 161KV TIE (1500)50RY 測試/正常 |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | [5 empty] | 659 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Test | Test | 1 |  |  | TEST/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1040 | 1041 |  | 2-31-00 | 2-31-01 |  | Locate Empty | ON | 161KV TIE (1501) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1501_DS | 1501(TIE) DS | TIE | [5 empty] | 747 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1042 | 1043 |  | 2-31-02 | 2-31-03 |  | Locate Empty | ON | 161KV TIE (1502) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1502_DS | 1502(TIE) DS | TIE | [5 empty] | 748 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 11 | 11kV | 200 | TIE(200) |  | D1 | 201(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D04_A1 | [8 empty] | 豐華DS.201 | 201 (非取樣點) | TIE | [5 empty] | 100 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | 200 | TIE(200) |  | D2 | 202(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D04_A1 | [8 empty] | 豐華DS.202 | 202 (非取樣點) | TIE | [5 empty] | 101 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | 200 | TIE(200) |  | E1 | 201E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D04_A1 | [8 empty] | 豐華DS.201E | 201E(非取樣點) | OTHER | [5 empty] | 102 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | 200 | TIE(200) |  | E2 | 202E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D04_A1 | [8 empty] | 豐華DS.202E | 202E(非取樣點) | OTHER | [5 empty] | 103 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | 200 | TIE(200) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0177 |  |  | 2-B1 |  |  | TIE-2B | A | TIE-2B 200 R 相電流 | A_-2000_2000(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.11KV_200_A1 | 11KV 200 R相AMP | TIE | [5 empty] | 299 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 200 | TIE(200) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0178 |  |  | 2-B2 |  |  | TIE-2B | A | TIE-2B 200 S 相電流 | A_-2000_2000(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.11KV_200_A2 | 11KV 200 S相AMP | TIE | [5 empty] | 300 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 200 | TIE(200) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0179 |  |  | 2-B3 |  |  | TIE-2B | A | TIE-2B 200 T 相電流 | A_-2000_2000(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.11KV_200_A3 | 11KV 200 T相AMP | TIE | [5 empty] | 301 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1520 | 南科～豐華白線(1520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/E01D04W/T2 |  | 0004 |  |  | 1-00-04 |  |  | L2 | ON/OFF | 南科豐華白線 1520 CB 52AS |  | aada | B2/D04_A1 | [8 empty] | 豐華DS.1520_CB | 1520(南科豐華白線) CB | LINE161 | [5 empty] | 356 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | 200 | TIE(200) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0328 |  |  | 2-09-00 |  |  | TIE-2B | PHA | TIE-2B 200 RY PHA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.200_51A | 11KV TIE(200) 51RY | TIE | [5 empty] | 532 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | 200 | TIE(200) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0329 |  |  | 2-09-01 |  |  | TIE-2B | GDA | TIE-2B 200 RY GDA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.200_51NA | 11KV TIE(200) 51N RY | TIE | [5 empty] | 533 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1550 | 三竹～豐華一路(1550) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1550LE | 1550LE (非取樣點) | LINE161 | [5 empty] | 10 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1550 | 三竹～豐華一路(1550) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1550BE | 1550BE (非取樣點) | LINE161 | [5 empty] | 11 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1550 | 三竹～豐華一路(1550) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0012 |  |  | 1-8C |  |  | L5 | MW | 三竹豐華一路 (1550)瓦 | MW_-560_560(-2000_2000) |  | B2/D04_A1 | [8 empty] | 豐華DS.1550_MW | 三竹豐華一路 MW | LINE161 | [5 empty] | 140 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1550 | 三竹～豐華一路(1550) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0013 |  |  | 1-8D |  |  | L5 | MVAR | 三竹豐華一路 (1550)乏 | MVAR_-560_560(-2000_2000) |  | B2/D04_A1 | [8 empty] | 豐華DS.1550_MVAR | 三竹豐華一路 MVAR | LINE161 | [5 empty] | 141 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1510 | 南科～豐華紅線(1510) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/E01D04R/T2 |  | 0000 |  |  | 1-00-00 |  |  | L1 | ON/OFF | 南科豐華紅線 1510 CB 52AS |  | aaca | B2/D04_A1 | [8 empty] | 豐華DS.1510_CB | 1510(南科豐華紅線) CB | LINE161 | [5 empty] | 352 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 161 | 161kV | 1550 | 三竹～豐華一路(1550) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0019 |  |  | 1-02-03 |  |  | L5 | 87A | 三竹豐華一路(1550)RY 87A |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1550_87A | 三竹豐華一路(1550) 87RY | LINE161 | [5 empty] | 371 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1550 | 三竹～豐華一路(1550) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0020 |  |  | 1-02-04 |  |  | L5 | PHA | 三竹豐華一路(1550)RY PHA |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1550_PHA | 三竹豐華一路(1550) 相間RY | LINE161 | [5 empty] | 372 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1550 | 三竹～豐華一路(1550) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-05 |  |  | L5 | GDA | 三竹豐華一路(1550)RY GDA |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1550_GDA | 三竹豐華一路(1550) 接地RY | LINE161 | [5 empty] | 373 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1550 | 三竹～豐華一路(1550) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0778 |  |  | 1-30-10 |  |  | L5 | USE/LOCK | 三竹豐華一路(1550)87RY 87S |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1550_87UL | 三竹豐華一路(1550) 87RY U/L | LINE161 | [5 empty] | 579 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1550 | 三竹～豐華一路(1550) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0779 |  |  | 1-30-11 |  |  | L5 | USE/LOCK | 三竹豐華一路(1550)79RY 79S |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1550_79UL | 三竹豐華一路(1550) 79RY U/L | LINE161 | [5 empty] | 580 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1550 | 三竹～豐華一路(1550) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0884 |  |  | 1-37-04 |  |  | L5 |  | 三竹豐華一路 1550 587L CFA |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1550_87LCFA | 三竹豐華一路(1550) 87L通訊故障 | OTHER | [5 empty] | 668 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1550 | 三竹～豐華一路(1550) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0885 |  |  | 1-37-05 |  |  | L5 |  | 三竹豐華一路 1550 RY故障 587LA |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1550_87LA | 三竹豐華一路(1550)數位電驛故障 | OTHER | [5 empty] | 669 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1550 | 三竹～豐華一路(1550) |  | DS1 | 1551 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0976 | 977 |  | 1-3D-00 | 1-3D-01 |  | L5 | ON | 三竹豐華一路 (1551) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1551_DS | 1551(三竹豐華一路) DS | LINE161 | [5 empty] | 723 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1550 | 三竹～豐華一路(1550) |  | DS2 | 1552 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0978 | 979 |  | 1-3D-02 | 1-3D-03 |  | L5 | ON | 三竹豐華一路 (1552) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1552_DS | 1552(三竹豐華一路) DS | LINE161 | [5 empty] | 724 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1550 | 三竹～豐華一路(1550) |  | DS3 | 1553 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0980 | 981 |  | 1-3D-04 | 1-3D-05 |  | L5 | ON | 三竹豐華一路 (1553) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1553_DS | 1553(三竹豐華一路) DS | LINE161 | [5 empty] | 725 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1550 | 三竹～豐華一路(1550) |  | ES3 | 1553E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0982 | 983 |  | 1-3D-06 | 1-3D-07 |  | L5 | ON | 三竹豐華一路 (1553E) ES-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1553E_ES | 1553E(三竹豐華一路) ES | LINE161 | [5 empty] | 726 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1560 | 三竹～豐華二路(1560) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1560LE | 1560LE (非取樣點) | LINE161 | [5 empty] | 12 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1560 | 三竹～豐華二路(1560) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1560BE | 1560BE (非取樣點) | LINE161 | [5 empty] | 13 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1560 | 三竹～豐華二路(1560) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0014 |  |  | 1-8E |  |  | L6 | MW | 三竹豐華二路 (1560)瓦 | MW_-560_560(-2000_2000) |  | B2/D04_A1 | [8 empty] | 豐華DS.1560_MW | 三竹豐華二路 MW | LINE161 | [5 empty] | 142 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1560 | 三竹～豐華二路(1560) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0015 |  |  | 1-8F |  |  | L6 | MVAR | 三竹豐華二路 (1560)乏 | MVAR_-560_560(-2000_2000) |  | B2/D04_A1 | [8 empty] | 豐華DS.1560_MVAR | 三竹豐華二路 MVAR | LINE161 | [5 empty] | 143 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K811 | 豐11線 (K811) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/K811/T1 |  |  | 0128 |  |  | 1-10-00 |  |  | F1 | ON/OFF | 豐11線 K811 CB 52AS |  | aadb | B2/D04_D1 | [8 empty] | 豐華DS.K811_CB | K811(11KV豐11線) CB | FEEDER | [5 empty] | 453 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 161 | 161kV | 1560 | 三竹～豐華二路(1560) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0023 |  |  | 1-02-07 |  |  | L6 | 87A | 三竹豐華二路(1560)RY 87A |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1560_87A | 三竹豐華二路(1560) 87RY | LINE161 | [5 empty] | 375 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1560 | 三竹～豐華二路(1560) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0024 |  |  | 1-03-00 |  |  | L6 | PHA | 三竹豐華二路(1560)RY PHA |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1560_PHA | 三竹豐華二路(1560) 相間RY | LINE161 | [5 empty] | 376 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1560 | 三竹～豐華二路(1560) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0025 |  |  | 1-03-01 |  |  | L6 | GDA | 三竹豐華二路(1560)RY GDA |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1560_GDA | 三竹豐華二路(1560) 接地RY | LINE161 | [5 empty] | 377 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1560 | 三竹～豐華二路(1560) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0780 |  |  | 1-30-12 |  |  | L6 | USE/LOCK | 三竹豐華二路(1560)87RY 87S |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1560_87UL | 三竹豐華二路(1560) 87RY U/L | LINE161 | [5 empty] | 581 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1560 | 三竹～豐華二路(1560) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0781 |  |  | 1-30-13 |  |  | L6 | USE/LOCK | 三竹豐華二路(1560)79RY 79S |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1560_79UL | 三竹豐華二路(1560) 79RY U/L | LINE161 | [5 empty] | 582 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1560 | 三竹～豐華二路(1560) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0886 |  |  | 1-37-06 |  |  | L6 |  | 三竹豐華二路 1560 687L CFA |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1560_87LCFA | 三竹豐華二路(1560) 87L通訊故障 | OTHER | [5 empty] | 670 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1560 | 三竹～豐華二路(1560) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0887 |  |  | 1-37-07 |  |  | L6 |  | 三竹豐華二路 1560 RY故障 687LA |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1560_87LA | 三竹豐華二路(1560)數位電驛故障 | OTHER | [5 empty] | 671 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1560 | 三竹～豐華二路(1560) |  | DS1 | 1561 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0984 | 985 |  | 1-3D-08 | 1-3D-09 |  | L6 | ON | 三竹豐華二路 (1561) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1561_DS | 1561(三竹豐華二路) DS | LINE161 | [5 empty] | 727 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1560 | 三竹～豐華二路(1560) |  | DS2 | 1562 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0986 | 987 |  | 1-3D-10 | 1-3D-11 |  | L6 | ON | 三竹豐華二路 (1562) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1562_DS | 1562(三竹豐華二路) DS | LINE161 | [5 empty] | 728 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1560 | 三竹～豐華二路(1560) |  | DS3 | 1563 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0988 | 989 |  | 1-3D-12 | 1-3D-13 |  | L6 | ON | 三竹豐華二路 (1563) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1563_DS | 1563(三竹豐華二路) DS | LINE161 | [5 empty] | 729 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1560 | 三竹～豐華二路(1560) |  | ES3 | 1563E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0990 | 991 |  | 1-3D-14 | 1-3D-15 |  | L6 | ON | 三竹豐華二路 (1563E) ES-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1563E_ES | 1563E(三竹豐華二路) ES | LINE161 | [5 empty] | 730 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1570 | 安南～王行、豐華線(1570) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1570LE | 1570LE (非取樣點) | LINE161 | [5 empty] | 14 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1570 | 安南～王行、豐華線(1570) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1570BE | 1570BE (非取樣點) | LINE161 | [5 empty] | 15 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1570 | 安南～王行、豐華線(1570) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0016 |  |  | 1-90 |  |  | L7 | MW | 山上安南豐華紅線 (1570)瓦 | MW_-560_560(-2000_2000) |  | B2/D04_A1 | [8 empty] | 豐華DS.1570_MW | 山上安南紅線 MW | LINE161 | [5 empty] | 144 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1570 | 安南～王行、豐華線(1570) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0017 |  |  | 1-91 |  |  | L7 | MVAR | 山上安南豐華紅線 (1570)乏 | MVAR_-560_560(-2000_2000) |  | B2/D04_A1 | [8 empty] | 豐華DS.1570_MVAR | 山上安南紅線 MVAR | LINE161 | [5 empty] | 145 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K812 | 豐12線 (K812) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/K812/T1 |  |  | 0131 |  |  | 1-10-03 |  |  | F2 | ON/OFF | 豐12線 K812 CB 52AS |  | aaeb | B2/D04_D1 | [8 empty] | 豐華DS.K812_CB | K812(11KV豐12線) CB | FEEDER | [5 empty] | 456 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 161 | 161kV | 1570 | 安南～王行、豐華線(1570) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0027 |  |  | 1-03-03 |  |  | L7 | 87A1 | 山上安南豐華紅線(1570)RY 87A1 |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1570_87A1 | 山上安南紅線(1570) #1 87RY | LINE161 | [5 empty] | 379 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1570 | 安南～王行、豐華線(1570) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0028 |  |  | 1-03-04 |  |  | L7 | PHA | 山上安南豐華紅線(1570)RY PHA |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1570_PHA | 山上安南紅線(1570) 相間RY | LINE161 | [5 empty] | 380 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1570 | 安南～王行、豐華線(1570) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0029 |  |  | 1-03-05 |  |  | L7 | GDA | 山上安南豐華紅線(1570)RY GDA |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1570_GDA | 山上安南紅線(1570) 接地RY | LINE161 | [5 empty] | 381 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1570 | 安南～王行、豐華線(1570) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0109 |  |  | 1-0D-05 |  |  | L7 | 87A2 | 山上安南豐華紅線(1570)RY 87A2 |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1570_87A2 | 山上安南紅線(1570) #2 87RY | LINE161 | [5 empty] | 447 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1570 | 安南～王行、豐華線(1570) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0782 |  |  | 1-30-14 |  |  | L7 | USE/LOCK | 山上安南豐華紅線(1570)#1 87RY 87S |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1570_87UL1 | 山上安南紅線(1570) #1 87RY U/L | LINE161 | [5 empty] | 583 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1570 | 安南～王行、豐華線(1570) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0783 |  |  | 1-30-15 |  |  | L7 | USE/LOCK | 山上安南豐華紅線(1570)79RY 79S |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1570_79UL | 山上安南紅線(1570) 79RY U/L | LINE161 | [5 empty] | 584 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1570 | 安南～王行、豐華線(1570) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0888 |  |  | 1-37-08 |  |  | L7 | A/N | 山上安南豐華紅線 1570 87CFA(87RY通訊故障) |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1570_87CFA | 山上安南紅線(1570)87RY通訊故障 | OTHER | [5 empty] | 672 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1570 | 安南～王行、豐華線(1570) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0889 |  |  | 1-37-09 |  |  | L7 | A/N | 山上安南豐華紅線 1570 RYFA(電驛故障) |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1570_RYFA | 山上安南紅線(1570)數位電驛故障 | OTHER | [5 empty] | 673 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1570 | 安南～王行、豐華線(1570) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0913 |  |  | 1-39-01 |  |  | L7 | USE/LOCK | 山上安南豐華紅線(1570) #2 87RY 87S |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1570_87UL2 | 山上安南紅線(1570) #2 87RY U/L | LINE161 | [5 empty] | 694 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1570 | 安南～王行、豐華線(1570) |  | DS1 | 1571 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0992 | 993 |  | 1-3E-00 | 1-3E-01 |  | L7 | ON | 山上安南豐華紅線 (1571) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1571_DS | 1571(山上安南紅線) DS | LINE161 | [5 empty] | 731 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1570 | 安南～王行、豐華線(1570) |  | DS2 | 1572 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0994 | 995 |  | 1-3E-02 | 1-3E-03 |  | L7 | ON | 山上安南豐華紅線 (1572) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1572_DS | 1572(山上安南紅線) DS | LINE161 | [5 empty] | 732 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1570 | 安南～王行、豐華線(1570) |  | DS3 | 1573 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0996 | 997 |  | 1-3E-04 | 1-3E-05 |  | L7 | ON | 山上安南豐華紅線 (1573) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1573_DS | 1573(山上安南紅線) DS | LINE161 | [5 empty] | 733 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1570 | 安南～王行、豐華線(1570) |  | ES3 | 1573E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0998 | 999 |  | 1-3E-06 | 1-3E-07 |  | L7 | ON | 山上安南豐華紅線 (1573E) ES-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1573E_ES | 1573E(山上安南紅線) ES | LINE161 | [5 empty] | 734 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 0 |  | StaDev | 所內設施 |  | DCV_P |  |  | MvMoment | 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | DCV | 65 | DC-P電壓 | kV_-150_150(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.直流P電源電壓 | 直流P電源電壓 | OTHER | [5 empty] | 152 |  |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 | 0.01 | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D04 | 豐華DS | 0 |  | StaDev | 所內設施 |  | DCV_N |  |  | MvMoment | 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0027 |  |  | 1-9B |  |  | DCV | -65 | DC-N電壓 | kV_-150_150(-2000_2000) |  | B3/D04_A1 | [8 empty] | 豐華DS.直流N電源電壓 | 直流N電源電壓 | OTHER | [5 empty] | 153 |  |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 | 0.01 | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D04 | 豐華DS | 0 |  | StaDev | 所內設施 |  | Fire1 | 受信總機 |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0838 |  |  | 1-34-06 |  |  | 火災警報(1) | A/N | 火災警報(1)受信總機 |  |  | B3/D04_A1 | [8 empty] | 豐華DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | [5 empty] | 627 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | StaDev | 所內設施 |  | Fire2 | 建物-所內電源室 |  | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0839 |  |  | 1-34-07 |  |  | 火災警報(2) | A/N | 火災警報(2)建物-所內電源室 |  |  | B3/D04_A1 | [8 empty] | 豐華DS.火災警報(2) | 火災警報(2)建物-所內電源室 | OTHER | [5 empty] | 628 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | StaDev | 所內設施 |  | Fire3 | 消防通風閘門 |  | Status | 火災警報3 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0840 |  |  | 1-34-08 |  |  | 火災警報(3) | A/N | 火災警報(3)消防通風閘門 |  |  | B3/D04_A1 | [8 empty] | 豐華DS.火災警報(3) | 火災警報(3)消防通風閘門 | OTHER | [5 empty] | 629 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | StaDev | 所內設施 |  | Door1 | 1樓門禁警報 |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0843 |  |  | 1-34-11 |  |  | Locate Empty | A/N | 無人化門禁(一) 1樓門禁警報 |  |  | B3/D04_A1 | [8 empty] | 豐華DS.無人化門禁(1) | 無人化門禁(1)建築物大門 | OTHER | [5 empty] | 630 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | StaDev | 所內設施 |  | Door2 | 控制室門禁警報 |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0844 |  |  | 1-34-12 |  |  | Locate Empty | A/N | 無人化門禁(二) 控制室門禁警報 |  |  | B3/D04_A1 | [8 empty] | 豐華DS.無人化門禁(2) | 無人化門禁(2)控制室大門 | OTHER | [5 empty] | 631 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | StaDev | 所內設施 |  | Door3 | 保全警報 |  | Status | 無人化門禁3 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0845 |  |  | 1-34-13 |  |  | Locate Empty | A/N | 無人化門禁(三) 保全警報 |  |  | B3/D04_A1 | [8 empty] | 豐華DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | [5 empty] | 632 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | StaDev | 所內設施 |  | Lights1 | FLA |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0848 |  |  | 1-35-00 |  |  | Locate Empty | ON/OFF | 無人化開關場照明(A) FLA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.開關場照明(A) | 開關場照明(A) | OTHER | [5 empty] | 633 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
D04 | 豐華DS | 0 |  | StaDev | 所內設施 |  | Lights2 | FLB |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0849 |  |  | 1-35-01 |  |  | Locate Empty | ON/OFF | 無人化開關場照明(B) FLB |  |  | B3/D04_A1 | [8 empty] | 豐華DS.開關場照明(B) | 開關場照明(B) | OTHER | [5 empty] | 634 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
D04 | 豐華DS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0850 |  |  | 1-35-02 |  |  | Locate Empty | ON/OFF | 所內電源ACB1 |  |  | B3/D04_A1 | [8 empty] | 豐華DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | [5 empty] | 635 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D04 | 豐華DS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0851 |  |  | 1-35-03 |  |  | Locate Empty | ON/OFF | 所內電源ACB2 |  |  | B3/D04_A1 | [8 empty] | 豐華DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | [5 empty] | 636 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D04 | 豐華DS | 0 |  | StaDev | 所內設施 |  | ACBT |  |  | Status | 所內電源ACB TIE | Close/Open | Y | 3 | DI-SP | [6 empty] | 0852 |  |  | 1-35-04 |  |  | Locate Empty | ON/OFF | 所內電源ACB TIE |  |  | B3/D04_A1 | [8 empty] | 豐華DS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | [5 empty] | 637 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ON/OFF | OFF
D04 | 豐華DS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0854 |  |  | 1-35-06 |  |  | Locate Empty | A/N | 所內欠壓警報 STUV |  |  | ELEM/D04_A1 | [8 empty] | 豐華DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | [5 empty] | 639 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0857 |  |  | 1-35-09 |  |  | Locate Empty | A/N | NFB跳脫警報 DCA |  |  | ELEM/D04_A1 | [8 empty] | 豐華DS.直流電源DCA | 直流電源故障警報 | OTHER | [5 empty] | 642 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0858 |  |  | 1-35-10 |  |  | Locate Empty | A/N | ACB警報 ACBA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.所內電源ACBA | 所內電源故障警報 | OTHER | [5 empty] | 643 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0861 |  |  | 1-35-13 |  |  | Locate Empty | A/N | 充電機警報 CHG1 |  |  | B3/D04_A1 | [8 empty] | 豐華DS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | [5 empty] | 646 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0862 |  |  | 1-35-14 |  |  | Locate Empty | A/N | DC接地警報 DCE |  |  | ELEM/D04_A1 | [8 empty] | 豐華DS.直流電源DCE | 直流電源接地故障警報 | OTHER | [5 empty] | 647 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | StaDev | 所內設施 |  | Water1 |  |  | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0864 |  |  | 1-36-00 |  |  | Locate Empty | A/N | 地下室水位警報(1) UW1 |  |  | B3/D04_A1 | [8 empty] | 豐華DS.水位警報(1) | 地下室水位警報(1) | OTHER | [5 empty] | 649 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | StaDev | 所內設施 |  | Water2 |  |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0865 |  |  | 1-36-01 |  |  | Locate Empty | A/N | 地下室水位警報(2) UW2 |  |  | B3/D04_A1 | [8 empty] | 豐華DS.水位警報(2) | 地下室水位警報(2) | OTHER | [5 empty] | 650 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | StaDev | 所內設施 |  | OilLeak1 |  |  | Status | 洩油池水位警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0870 |  |  | 1-36-06 |  |  | Locate Empty | A/N | OW1蓄油池水位警報1 WPF |  |  | B3/D04_A1 | [8 empty] | 豐華DS.洩油池警報(1) | 洩油池水位警報(1) | OTHER | [5 empty] | 655 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | StaDev | 所內設施 |  | OilLeak2 |  |  | Status | 洩油池水位警報2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0871 |  |  | 1-36-07 |  |  | Locate Empty | A/N | OW2蓄油池水位警報2 WPA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.洩油池警報(2) | 洩油池水位警報(2) | OTHER | [5 empty] | 656 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | StaDev | 所內設施 |  | GEN | 緊急發電機運轉 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0899 |  |  | 1-38-03 |  |  | L12 | ON/OFF | 緊急發電機運轉 |  |  | B3/D04_A1 | [8 empty] | 豐華DS.GEN | 緊急發電機運轉 | OTHER | [5 empty] | 682 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ON/OFF | OFF
D04 | 豐華DS | 0 |  | StaDev | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0900 |  |  | 1-38-04 |  |  | Locate Empty | A/N | 其他輕故障 PSF |  |  | B3/D04_A1 | [8 empty] | 豐華DS.其他輕故障 | 變電所內其他輕故障 | OTHER | [5 empty] | 683 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | StaDev | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0901 |  |  | 1-38-05 |  |  | Locate Empty | A/N | 其他重故障 PSA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.其他重故障 | 變電所內其他重故障 | OTHER | [5 empty] | 684 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0902 |  |  | 1-38-06 |  |  | 通訊室 | A/N | 通訊充電機故障 CHG2 |  |  | B3/D04_A1 | [8 empty] | 豐華DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | [5 empty] | 685 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0903 |  |  | 1-38-07 |  |  | 通訊室 | A/N | 通訊設備AC故障 ACFA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | [5 empty] | 686 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | StaDev | 所內設施 |  | R_Temp1 | 通訊室或控制室 |  | Status | 溫度警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0906 |  |  | 1-38-10 |  |  | 通訊室 | A/N | 通訊室或控制室溫度警報 |  |  | B3/D04_A1 | [8 empty] | 豐華DS.通信機房溫度 | 通訊室或控制室溫度警報 | OTHER | [5 empty] | 687 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | StaDev | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0908 |  |  | 1-38-12 |  |  | Power Meter | A/N | Power Meter 故障警報 PMA |  |  | ELEM/D04_A1 | [8 empty] | 豐華DS.PMA | 電力量測表計故障 | OTHER | [5 empty] | 689 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | StaDev | 所內設施 |  | Fire4 |  |  | Status | 火災警報4 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0841 | [10 empty] | B3/D04_A1 | [16 empty] | 831 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 0 |  | StaDev | 所內設施 |  | Door4 |  |  | Status | 無人化門禁4 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0846 | [10 empty] | B3/D04_A1 | [16 empty] | 832 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 0 |  | StaDev | 所內設施 |  | Fire5 |  |  | Status | 火災警報5 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0842 | [10 empty] | B3/D04_A1 | [16 empty] | 833 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 0 |  | StaDev | 所內設施 |  | Door5 |  |  | Status | 無人化門禁5 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0847 | [10 empty] | B3/D04_A1 | [16 empty] | 834 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 161 | 161kV | 1520 | 南科～豐華白線(1520) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1520LE | 1520LE (非取樣點) | LINE161 | [5 empty] | 4 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1520 | 南科～豐華白線(1520) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1520BE | 1520BE (非取樣點) | LINE161 | [5 empty] | 5 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1520 | 南科～豐華白線(1520) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | L2 | MW | 南科豐華白線 1520 瓦 | MW_-560_560(-2000_2000) |  | B2/D04_A1 | [8 empty] | 豐華DS.1520_MW | 南科豐華白線 MW | LINE161 | [5 empty] | 134 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1520 | 南科～豐華白線(1520) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | L2 | MVAR | 南科豐華白線 1520 乏 | MVAR_-560_560(-2000_2000) |  | B2/D04_A1 | [8 empty] | 豐華DS.1520_MVAR | 南科豐華白線 MVAR | LINE161 | [5 empty] | 135 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K813 | 豐13線 (K813) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/K813/T1 |  |  | 0134 |  |  | 1-10-06 |  |  | F3 | ON/OFF | 豐13線 K813 CB 52AS |  | aafb | B2/D04_D1 | [8 empty] | 豐華DS.K813_CB | K813(11KV豐13線) CB | FEEDER | [5 empty] | 459 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 161 | 161kV | 1520 | 南科～豐華白線(1520) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0005 |  |  | 1-00-05 |  |  | L2 | 87A1 | 南科豐華白線 1520 CB 87A1 |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1520_87A1 | 南科豐華白線(1520)87RY1 | OTHER | [5 empty] | 357 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1520 | 南科～豐華白線(1520) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | L2 | PHA | 南科豐華白線 1520 CB PHA |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1520_PHA | 南科豐華白線(1520) 相間RY | LINE161 | [5 empty] | 358 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1520 | 南科～豐華白線(1520) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-07 |  |  | L2 | GDA | 南科豐華白線 1520 CB GDA |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1520_GDA | 南科豐華白線(1520) 接地RY | LINE161 | [5 empty] | 359 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1520 | 南科～豐華白線(1520) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0108 |  |  | 1-0D-04 |  |  | Locate Empty | 87A2 | 南科豐華白線 1520 CB 87A2 |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1520_87A2 | 南科豐華白線(1520)87RY2 | OTHER | [5 empty] | 446 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1520 | 南科～豐華白線(1520) |  | DTTA |  |  | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0113 |  |  | 1-0E-01 |  |  | Locate Empty | DTTA | 南科豐華白線 (1520 ) 遠方遙跳 |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1520_DTTA | 南科豐華白線(1520)遠方遙跳 | OTHER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1520 | 南科～豐華白線(1520) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0772 |  |  | 1-30-04 |  |  | L2 | USE/LOCK | 南科豐華白線(1520)87RY1 U/L |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1520_87RY1UL | 南科豐華白線(1520)87RY1 U/L | OTHER | [5 empty] | 573 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1520 | 南科～豐華白線(1520) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0773 |  |  | 1-30-05 |  |  | L2 | USE/LOCK | 南科豐華白線(1520)79RY 79S |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1520_79UL | 南科豐華白線(1520) 79RY U/L | LINE161 | [5 empty] | 574 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1520 | 南科～豐華白線(1520) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0878 |  |  | 1-36-14 |  |  | L2 | A/N | 南科豐華白線1520 87CFA(87RY通訊故障) |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1520_87CFA | 南科豐華白線(1520)87RY通訊故障 | OTHER | [5 empty] | 662 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1520 | 南科～豐華白線(1520) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0879 |  |  | 1-36-15 |  |  | L2 | A/N | 南科豐華白線1520 RYFA(數位電驛故障) |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1520_RYFA | 南科豐華白線(1520)數位電驛故障 | OTHER | [5 empty] | 663 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1520 | 南科～豐華白線(1520) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0912 |  |  | 1-39-00 |  |  | Locate Empty | USE/LOCK | 南科豐華白線(1520)87RY2 U/L |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1520_87RY2UL | 南科豐華白線(1520)87RY2 U/L | OTHER | [5 empty] | 693 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1520 | 南科～豐華白線(1520) |  | DS1 | 1521 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0952 | 953 |  | 1-3B-08 | 1-3B-09 |  | L2 | ON | 南科豐華白線 (1521) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1521_DS | 1521(南科豐華白線) DS | LINE161 | [5 empty] | 711 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1520 | 南科～豐華白線(1520) |  | DS2 | 1522 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0954 | 955 |  | 1-3B-10 | 1-3B-11 |  | L2 | ON | 南科豐華白線 (1522) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1522_DS | 1522(南科豐華白線) DS | LINE161 | [5 empty] | 712 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1520 | 南科～豐華白線(1520) |  | DS3 | 1523 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0956 | 957 |  | 1-3B-12 | 1-3B-13 |  | L2 | ON | 南科豐華白線 (1523) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1523_DS | 1523(南科豐華白線) DS | LINE161 | [5 empty] | 713 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1520 | 南科～豐華白線(1520) |  | ES3 | 1523E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0958 | 959 |  | 1-3B-14 | 1-3B-15 |  | L2 | ON | 南科豐華白線 (1523E) ES-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1523E_ES | 1523E(南科豐華白線) ES | LINE161 | [5 empty] | 714 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1510 | 南科～豐華紅線(1510) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 2 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1510 | 南科～豐華紅線(1510) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1510BE | 1510BE (非取樣點) | LINE161 | [5 empty] | 3 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1510 | 南科～豐華紅線(1510) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | L1 | MW | 南科豐華紅線 1510 瓦 | MW_-560_560(-2000_2000) |  | B2/D04_A1 | [8 empty] | 豐華DS.1510_MW | 南科豐華紅線 MW | LINE161 | [5 empty] | 132 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1510 | 南科～豐華紅線(1510) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | L1 | MVAR | 南科豐華紅線 1510 乏 | MVAR_-560_560(-2000_2000) |  | B2/D04_A1 | [8 empty] | 豐華DS.1510_MVAR | 南科豐華紅線 MVAR | LINE161 | [5 empty] | 133 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K814 | 豐14線 (K814) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/K814/T1 |  |  | 0137 |  |  | 1-11-01 |  |  | F4 | ON/OFF | 豐14線 K814 CB 52AS |  | aahb | B2/D04_D1 | [8 empty] | 豐華DS.K814_CB | K814(11KV豐14線) CB | FEEDER | [5 empty] | 462 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 161 | 161kV | 1510 | 南科～豐華紅線(1510) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0001 |  |  | 1-00-01 |  |  | L1 | 87A | 南科豐華紅線 1510 CB 87A |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1510_87A | 南科豐華紅線(1510) 87RY | LINE161 | [5 empty] | 353 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1510 | 南科～豐華紅線(1510) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0002 |  |  | 1-00-02 |  |  | L1 | PHA | 南科豐華紅線 1510 CB PHA |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1510_PHA | 南科豐華紅線(1510) 相間RY | LINE161 | [5 empty] | 354 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1510 | 南科～豐華紅線(1510) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | L1 | GDA | 南科豐華紅線 1510 CB GDA |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1510_GDA | 南科豐華紅線(1510) 接地RY | LINE161 | [5 empty] | 355 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1510 | 南科～豐華紅線(1510) |  | DTTA |  |  | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0112 |  |  | 1-0E-00 |  |  | L1 | RY | 南科豐華紅線(1510)RY DTTA |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1510_DTTA | 南科豐華紅線(1510) 遠方遙跳 | OTHER | [5 empty] | 449 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1510 | 南科～豐華紅線(1510) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0770 |  |  | 1-30-02 |  |  | L1 | USE/LOCK | 南科豐華紅線(1510)87RY 87S |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1510_87UL | 南科豐華紅線(1510) 87RY U/L | LINE161 | [5 empty] | 571 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1510 | 南科～豐華紅線(1510) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0771 |  |  | 1-30-03 |  |  | L1 | USE/LOCK | 南科豐華紅線(1510)79RY 79S |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1510_79UL | 南科豐華紅線(1510) 79RY U/L | LINE161 | [5 empty] | 572 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1510 | 南科～豐華紅線(1510) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0876 |  |  | 1-36-12 |  |  | L1 | A/N | 南科豐華紅線1510 187L CFA |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1510_87LCFA | 南科豐華紅線(1510) 87L通訊故障 | OTHER | [5 empty] | 660 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1510 | 南科～豐華紅線(1510) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0877 |  |  | 1-36-13 |  |  | L1 | A/N | 南科豐華紅線1510 187LA |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1510_87LA | 南科豐華紅線(1510)數位電驛故障 | OTHER | [5 empty] | 661 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1510 | 南科～豐華紅線(1510) |  | DS1 | 1511 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0944 | 945 |  | 1-3B-00 | 1-3B-01 |  | L1 | ON | 南科豐華紅線 (1511) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1511_DS | 1511(南科豐華紅線) DS | LINE161 | [5 empty] | 707 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1510 | 南科～豐華紅線(1510) |  | DS2 | 1512 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0946 | 947 |  | 1-3B-02 | 1-3B-03 |  | L1 | ON | 南科豐華紅線 (1512) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1512_DS | 1512(南科豐華紅線) DS | LINE161 | [5 empty] | 708 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1510 | 南科～豐華紅線(1510) |  | DS3 | 1513 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0948 | 949 |  | 1-3B-04 | 1-3B-05 |  | L1 | ON | 南科豐華紅線 (1513) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1513_DS | 1513(南科豐華紅線) DS | LINE161 | [5 empty] | 709 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1510 | 南科～豐華紅線(1510) |  | ES3 | 1513E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0950 | 951 |  | 1-3B-06 | 1-3B-07 |  | L1 | ON | 南科豐華紅線 (1513E) ES-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1513E_ES | 1513E(南科豐華紅線) ES | LINE161 | [5 empty] | 710 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 11 | 11kV | K811 | 豐11線 (K811) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K811_DS | K811_DS (非取樣點) | FEEDER | [5 empty] | 46 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K811 | 豐11線 (K811) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K811_ES | K811_ES (非取樣點) | FEEDER | [5 empty] | 47 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | K811 | 豐11線 (K811) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | F1 | KVAR | 豐11線 K811 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐11線KVAR | 11KV豐11線 KVAR | FEEDER | [5 empty] | 174 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K811 | 豐11線 (K811) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | F1 | A | 豐11線 K811 R相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐11線A1 | 11KV豐11線 R相AMP | FEEDER | [5 empty] | 175 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K811 | 豐11線 (K811) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | F1 | A | 豐11線 K811 S相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐11線A2 | 11KV豐11線 S相AMP | FEEDER | [5 empty] | 176 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K811 | 豐11線 (K811) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | F1 | A | 豐11線 K811 T相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐11線A3 | 11KV豐11線 T相AMP | FEEDER | [5 empty] | 177 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K811 | 豐11線 (K811) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | F1 | A | 豐11線 K811 N相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐11線A0 | 11KV豐11線 N相AMP | FEEDER | [5 empty] | 178 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K815 | 豐15線 (K815) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/K815/T1 |  |  | 0140 |  |  | 1-11-04 |  |  | F5 | ON/OFF | 豐15線 K815 CB 52AS |  | aaib | B2/D04_D1 | [8 empty] | 豐華DS.K815_CB | K815(11KV豐15線) CB | FEEDER | [5 empty] | 465 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K811 | 豐11線 (K811) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0129 |  |  | 1-10-01 |  |  | F1 | PHA | 豐11線 K811 RY PHA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K811_PHA | 11KV豐11線(K811) 相間RY | FEEDER | [5 empty] | 454 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K811 | 豐11線 (K811) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-10-02 |  |  | F1 | GDA | 豐11線 K811 RY GDA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K811_GDA | 11KV豐11線(K811) 接地RY | FEEDER | [5 empty] | 455 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K811 | 豐11線 (K811) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1152 | [10 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K811_79UL | 11KV豐11線(K811) 79RY U/L | FEEDER | [5 empty] | 761 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K811 | 豐11線 (K811) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1153 | [10 empty] | B2/D04_D1 | [16 empty] | 789 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 11 | 11kV | K812 | 豐12線 (K812) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K812_DS | K812_DS (非取樣點) | FEEDER | [5 empty] | 48 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K812 | 豐12線 (K812) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K812_ES | K812_ES (非取樣點) | FEEDER | [5 empty] | 49 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | K812 | 豐12線 (K812) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | F2 | KVAR | 豐12線 K812 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐12線KVAR | 11KV豐12線 KVAR | FEEDER | [5 empty] | 179 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K812 | 豐12線 (K812) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | F2 | A | 豐12線 K812 R相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐12線A1 | 11KV豐12線 R相AMP | FEEDER | [5 empty] | 180 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K812 | 豐12線 (K812) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | F2 | A | 豐12線 K812 S 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐12線A2 | 11KV豐12線 S相AMP | FEEDER | [5 empty] | 181 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K812 | 豐12線 (K812) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0060 |  |  | 1-BC |  |  | F2 | A | 豐12線 K812 T 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐12線A3 | 11KV豐12線 T相AMP | FEEDER | [5 empty] | 182 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K812 | 豐12線 (K812) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | F2 | A | 豐12線 K812 N 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐12線A0 | 11KV豐12線 N相AMP | FEEDER | [5 empty] | 183 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K821 | 豐21線 (K821) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/K821/T1 |  |  | 0149 |  |  | 1-12-05 |  |  | F6 | ON/OFF | 豐21線 K821 CB 52AS |  | bacb | B2/D04_D1 | [8 empty] | 豐華DS.K821_CB | K821(11KV豐21線) CB | FEEDER | [5 empty] | 474 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K812 | 豐12線 (K812) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0132 |  |  | 1-10-04 |  |  | F2 | PHA | 豐12線 K812 RY PHA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K812_PHA | 11KV豐12線(K812) 相間RY | FEEDER | [5 empty] | 457 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K812 | 豐12線 (K812) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0133 |  |  | 1-10-05 |  |  | F2 | GDA | 豐12線 K812 RY GDA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K812_GDA | 11KV豐12線(K812) 接地RY | FEEDER | [5 empty] | 458 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K812 | 豐12線 (K812) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1154 | [10 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K812_79UL | 11KV豐12線(K812) 79RY U/L | FEEDER | [5 empty] | 762 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K812 | 豐12線 (K812) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1155 | [10 empty] | B2/D04_D1 | [16 empty] | 790 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 11 | 11kV | K813 | 豐13線 (K813) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K813_DS | K813_DS (非取樣點) | FEEDER | [5 empty] | 50 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K813 | 豐13線 (K813) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K813_ES | K813_ES (非取樣點) | FEEDER | [5 empty] | 51 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | K813 | 豐13線 (K813) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | F3 | KVAR | 豐13線 K813 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐13線KVAR | 11KV豐13線 KVAR | FEEDER | [5 empty] | 184 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K813 | 豐13線 (K813) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0063 |  |  | 1-BF |  |  | F3 | A | 豐13線 K813 R相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐13線A1 | 11KV豐13線 R相AMP | FEEDER | [5 empty] | 185 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K813 | 豐13線 (K813) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | F3 | A | 豐13線 K813 S 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐13線A2 | 11KV豐13線 S相AMP | FEEDER | [5 empty] | 188 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K813 | 豐13線 (K813) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | F3 | A | 豐13線 K813 T 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐13線A3 | 11KV豐13線 T相AMP | FEEDER | [5 empty] | 189 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K813 | 豐13線 (K813) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | F3 | A | 豐13線 K813 N 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐13線A0 | 11KV豐13線 N相AMP | FEEDER | [5 empty] | 190 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K822 | 豐22線 (K822) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/K822/T1 |  |  | 0152 |  |  | 1-13-00 |  |  | F7 | ON/OFF | 豐22線 K822 CB 52AS |  | badb | B2/D04_D1 | [8 empty] | 豐華DS.K822_CB | K822(11KV豐22線) CB | FEEDER | [5 empty] | 477 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K813 | 豐13線 (K813) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0135 |  |  | 1-10-07 |  |  | F3 | PHA | 豐13線 K813 RY PHA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K813_PHA | 11KV豐13線(K813) 相間RY | FEEDER | [5 empty] | 460 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K813 | 豐13線 (K813) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0136 |  |  | 1-11-00 |  |  | F3 | GDA | 豐13線 K813 RY GDA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K813_GDA | 11KV豐13線(K813) 接地RY | FEEDER | [5 empty] | 461 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K813 | 豐13線 (K813) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1156 | [10 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K813_79UL | 11KV豐13線(K813) 79RY U/L | FEEDER | [5 empty] | 763 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K813 | 豐13線 (K813) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1157 | [10 empty] | B2/D04_D1 | [16 empty] | 791 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 11 | 11kV | K814 | 豐14線 (K814) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K814_DS | K814_DS (非取樣點) | FEEDER | [5 empty] | 52 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K814 | 豐14線 (K814) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K814_ES | K814_ES (非取樣點) | FEEDER | [5 empty] | 53 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | K814 | 豐14線 (K814) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | F4 | KVAR | 豐14線 K814 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐14線KVAR | 11KV豐14線 KVAR | FEEDER | [5 empty] | 191 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K814 | 豐14線 (K814) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | F4 | A | 豐14線 K814 R 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐14線A1 | 11KV豐14線 R相AMP | FEEDER | [5 empty] | 192 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K814 | 豐14線 (K814) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | F4 | A | 豐14線 K814 S 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐14線A2 | 11KV豐14線 S相AMP | FEEDER | [5 empty] | 193 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K814 | 豐14線 (K814) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | F4 | A | 豐14線 K814 T 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐14線A3 | 11KV豐14線 T相AMP | FEEDER | [5 empty] | 194 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K814 | 豐14線 (K814) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | F4 | A | 豐14線 K814 N 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐14線A0 | 11KV豐14線 N相AMP | FEEDER | [5 empty] | 195 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K823 | 豐23線 (K823) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/K823/T1 |  |  | 0155 |  |  | 1-13-03 |  |  | F8 | ON/OFF | 豐23線 K823 CB 52AS |  | baeb | B2/D04_D1 | [8 empty] | 豐華DS.K823_CB | K823(11KV豐23線) CB | FEEDER | [5 empty] | 480 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K814 | 豐14線 (K814) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0138 |  |  | 1-11-02 |  |  | F4 | PHA | 豐14線 K814 RY PHA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K814_PHA | 11KV豐14線(K814) 相間RY | FEEDER | [5 empty] | 463 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K814 | 豐14線 (K814) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0139 |  |  | 1-11-03 |  |  | F4 | GDA | 豐14線 K814 RY GDA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K814_GDA | 11KV豐14線(K814) 接地RY | FEEDER | [5 empty] | 464 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K814 | 豐14線 (K814) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1158 | [10 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K814_79UL | 11KV豐14線(K814) 79RY U/L | FEEDER | [5 empty] | 764 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K814 | 豐14線 (K814) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1159 | [10 empty] | B2/D04_D1 | [16 empty] | 792 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 11 | 11kV | K815 | 豐15線 (K815) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K815_DS | K815_DS (非取樣點) | FEEDER | [5 empty] | 54 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K815 | 豐15線 (K815) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K815_ES | K815_ES (非取樣點) | FEEDER | [5 empty] | 55 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | K815 | 豐15線 (K815) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | F5 | KVAR | 豐15線 K815 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐15線KVAR | 11KV豐15線 KVAR | FEEDER | [5 empty] | 196 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K815 | 豐15線 (K815) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | F5 | A | 豐15線 K815 R 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐15線A1 | 11KV豐15線 R相AMP | FEEDER | [5 empty] | 197 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K815 | 豐15線 (K815) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | F5 | A | 豐15線 K815 S 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐15線A2 | 11KV豐15線 S相AMP | FEEDER | [5 empty] | 198 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K815 | 豐15線 (K815) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | F5 | A | 豐15線 K815 T 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐15線A3 | 11KV豐15線 T相AMP | FEEDER | [5 empty] | 199 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K815 | 豐15線 (K815) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | F5 | A | 豐15線 K815 N相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐15線A0 | 11KV豐15線 N相AMP | FEEDER | [5 empty] | 200 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K824 | 豐24線 (K824) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/K824/T1 |  |  | 0158 |  |  | 1-13-06 |  |  | F9 | ON/OFF | 豐24線 K824 CB 52AS |  | bagb | B2/D04_D1 | [8 empty] | 豐華DS.K824_CB | K824(11KV豐24線) CB | FEEDER | [5 empty] | 483 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K815 | 豐15線 (K815) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0141 |  |  | 1-11-05 |  |  | F5 | PHA | 豐15線 K815 RY PHA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K815_PHA | 11KV豐15線(K815) 相間RY | FEEDER | [5 empty] | 466 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K815 | 豐15線 (K815) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0142 |  |  | 1-11-06 |  |  | F5 | GDA | 豐15線 K815 RY GDA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K815_GDA | 11KV豐15線(K815) 接地RY | FEEDER | [5 empty] | 467 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K815 | 豐15線 (K815) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1160 | [10 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K815_79UL | 11KV豐15線(K815) 79RY U/L | FEEDER | [5 empty] | 765 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K815 | 豐15線 (K815) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1161 | [10 empty] | B2/D04_D1 | [16 empty] | 793 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 11 | 11kV | K821 | 豐21線 (K821) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K821_DS | K821_DS (非取樣點) | FEEDER | [5 empty] | 60 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K821 | 豐21線 (K821) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K821_ES | K821_ES (非取樣點) | FEEDER | [5 empty] | 61 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | K821 | 豐21線 (K821) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | F6 | KVAR | 豐21線 K821 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐21線KVAR | 11KV豐21線 KVAR | FEEDER | [5 empty] | 207 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K821 | 豐21線 (K821) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | F6 | A | 豐21線 K821 R 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐21線A1 | 11KV豐21線 R相AMP | FEEDER | [5 empty] | 208 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K821 | 豐21線 (K821) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | F6 | A | 豐21線 K821 S相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐21線A2 | 11KV豐21線 S相AMP | FEEDER | [5 empty] | 209 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K821 | 豐21線 (K821) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | F6 | A | 豐21線 K821 T相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐21線A3 | 11KV豐21線 T相AMP | FEEDER | [5 empty] | 210 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K821 | 豐21線 (K821) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | F6 | A | 豐21線 K821 N相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐21線A0 | 11KV豐21線 N相AMP | FEEDER | [5 empty] | 211 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K825 | 豐25線 (K825) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/K825/T1 |  |  | 0161 |  |  | 1-14-01 |  |  | F10 | ON/OFF | 豐25線 K825 CB 52AS |  | bahb | B2/D04_D1 | [8 empty] | 豐華DS.K825_CB | K825(11KV豐25線) CB | FEEDER | [5 empty] | 486 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K821 | 豐21線 (K821) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0150 |  |  | 1-12-06 |  |  | F6 | PHA | 豐21線 K821 RY PHA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K821_PHA | 11KV豐21線(K821) 相間RY | FEEDER | [5 empty] | 475 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K821 | 豐21線 (K821) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0151 |  |  | 1-12-07 |  |  | F6 | GDA | 豐21線 K821 RY GDA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K821_GDA | 11KV豐21線(K821) 接地RY | FEEDER | [5 empty] | 476 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K821 | 豐21線 (K821) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1162 | [10 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K821_79UL | 11KV豐21線(K821) 79RY U/L | FEEDER | [5 empty] | 766 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K821 | 豐21線 (K821) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1163 | [10 empty] | B2/D04_D1 | [16 empty] | 794 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 11 | 11kV | K822 | 豐22線 (K822) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K822_DS | K822_DS (非取樣點) | FEEDER | [5 empty] | 62 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K822 | 豐22線 (K822) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K822_ES | K822_ES (非取樣點) | FEEDER | [5 empty] | 63 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | K822 | 豐22線 (K822) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | F7 | KVAR | 豐22線 K822 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐22線KVAR | 11KV豐22線 KVAR | FEEDER | [5 empty] | 212 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K822 | 豐22線 (K822) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | F7 | A | 豐22線 K822 R相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐22線A1 | 11KV豐22線 R相AMP | FEEDER | [5 empty] | 213 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K822 | 豐22線 (K822) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | F7 | A | 豐22線 K822 S相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐22線A2 | 11KV豐22線 S相AMP | FEEDER | [5 empty] | 214 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K822 | 豐22線 (K822) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | F7 | A | 豐22線 K822 T相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐22線A3 | 11KV豐22線 T相AMP | FEEDER | [5 empty] | 215 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K822 | 豐22線 (K822) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | F7 | A | 豐22線 K822 N相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐22線A0 | 11KV豐22線 N相AMP | FEEDER | [5 empty] | 216 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K831 | 豐31線(K831) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/K831/T1 |  |  | 0288 |  |  | 2-04-00 |  |  | F11 | ON/OFF | 豐31線 K831 CB 52AS |  | abdb | B2/D04_D1 | [8 empty] | 豐華DS.K831_CB | K831(11KV豐31線) CB | FEEDER | [5 empty] | 492 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K822 | 豐22線 (K822) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0153 |  |  | 1-13-01 |  |  | F7 | PHA | 豐22線 K822 RY PHA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K822_PHA | 11KV豐22線(K822) 相間RY | FEEDER | [5 empty] | 478 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K822 | 豐22線 (K822) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0154 |  |  | 1-13-02 |  |  | F7 | GDA | 豐22線 K822 RY GDA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K822_GDA | 11KV豐22線(K822) 接地RY | FEEDER | [5 empty] | 479 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K822 | 豐22線 (K822) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1164 | [10 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K822_79UL | 11KV豐22線(K822) 79RY U/L | FEEDER | [5 empty] | 767 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K822 | 豐22線 (K822) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1165 | [10 empty] | B2/D04_D1 | [16 empty] | 795 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 11 | 11kV | K823 | 豐23線 (K823) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K823_DS | K823_DS (非取樣點) | FEEDER | [5 empty] | 64 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K823 | 豐23線 (K823) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K823_ES | K823_ES (非取樣點) | FEEDER | [5 empty] | 65 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | K823 | 豐23線 (K823) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | F8 | KVAR | 豐23線 K823 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐23線KVAR | 11KV豐23線 KVAR | FEEDER | [5 empty] | 217 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K823 | 豐23線 (K823) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | F8 | A | 豐23線 K823 R相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐23線A1 | 11KV豐23線 R相AMP | FEEDER | [5 empty] | 218 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K823 | 豐23線 (K823) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | F8 | A | 豐23線 K823 S相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐23線A2 | 11KV豐23線 S相AMP | FEEDER | [5 empty] | 219 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K823 | 豐23線 (K823) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0098 |  |  | 1-E2 |  |  | F8 | A | 豐23線 K823 T相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐23線A3 | 11KV豐23線 T相AMP | FEEDER | [5 empty] | 220 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K823 | 豐23線 (K823) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | F8 | A | 豐23線 K823 N相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐23線A0 | 11KV豐23線 N相AMP | FEEDER | [5 empty] | 221 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K832 | 豐32線(K832) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/K832/T1 |  |  | 0291 |  |  | 2-04-03 |  |  | F12 | ON/OFF | 豐32線 K832 CB 52AS |  | abeb | B2/D04_D1 | [8 empty] | 豐華DS.K832_CB | K832(11KV豐32線) CB | FEEDER | [5 empty] | 495 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K823 | 豐23線 (K823) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0156 |  |  | 1-13-04 |  |  | F8 | PHA | 豐23線 K823 RY PHA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K823_PHA | 11KV豐23線(K823) 相間RY | FEEDER | [5 empty] | 481 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K823 | 豐23線 (K823) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0157 |  |  | 1-13-05 |  |  | F8 | GDA | 豐23線 K823 RY GDA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K823_GDA | 11KV豐23線(K823) 接地RY | FEEDER | [5 empty] | 482 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K823 | 豐23線 (K823) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1166 | [10 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K823_79UL | 11KV豐23線(K823) 79RY U/L | FEEDER | [5 empty] | 768 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K823 | 豐23線 (K823) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1167 | [10 empty] | B2/D04_D1 | [16 empty] | 796 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 11 | 11kV | K824 | 豐24線 (K824) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K824_DS | K824_DS (非取樣點) | FEEDER | [5 empty] | 66 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K824 | 豐24線 (K824) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K824_ES | K824_ES (非取樣點) | FEEDER | [5 empty] | 67 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | K824 | 豐24線 (K824) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | F9 | KVAR | 豐24線 K824 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐24線KVAR | 11KV豐24線 KVAR | FEEDER | [5 empty] | 222 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K824 | 豐24線 (K824) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0101 |  |  | 1-E5 |  |  | F9 | A | 豐24線 K824 R相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐24線A1 | 11KV豐24線 R相AMP | FEEDER | [5 empty] | 223 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K824 | 豐24線 (K824) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | F9 | A | 豐24線 K824 S 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐24線A2 | 11KV豐24線 S相AMP | FEEDER | [5 empty] | 224 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K824 | 豐24線 (K824) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | F9 | A | 豐24線 K824 T相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐24線A3 | 11KV豐24線 T相AMP | FEEDER | [5 empty] | 225 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K824 | 豐24線 (K824) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | F9 | A | 豐24線 K824 N相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐24線A0 | 11KV豐24線 N相AMP | FEEDER | [5 empty] | 226 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K833 | 豐33線(K833) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/K833/T1 |  |  | 0294 |  |  | 2-04-06 |  |  | F13 | ON/OFF | 豐33線 K833 CB 52AS |  | abgb | B2/D04_D1 | [8 empty] | 豐華DS.K833_CB | K833(11KV豐33線) CB | FEEDER | [5 empty] | 498 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K824 | 豐24線 (K824) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0159 |  |  | 1-13-07 |  |  | F9 | PHA | 豐24線 K824 RY PHA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K824_PHA | 11KV豐24線(K824) 相間RY | FEEDER | [5 empty] | 484 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K824 | 豐24線 (K824) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0160 |  |  | 1-14-00 |  |  | F9 | GDA | 豐24線 K824 RY GDA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K824_GDA | 11KV豐24線(K824) 接地RY | FEEDER | [5 empty] | 485 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K824 | 豐24線 (K824) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1168 | [10 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K824_79UL | 11KV豐24線(K824) 79RY U/L | FEEDER | [5 empty] | 769 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K824 | 豐24線 (K824) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1169 | [10 empty] | B2/D04_D1 | [16 empty] | 797 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 11 | 11kV | K825 | 豐25線 (K825) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K825_DS | K825_DS (非取樣點) | FEEDER | [5 empty] | 68 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K825 | 豐25線 (K825) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K825_ES | K825_ES (非取樣點) | FEEDER | [5 empty] | 69 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | K825 | 豐25線 (K825) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | F10 | KVAR | 豐25線 K825 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐25線KVAR | 11KV豐25線 KVAR | FEEDER | [5 empty] | 227 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K825 | 豐25線 (K825) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | F10 | A | 豐25線 K825 R相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐25線A1 | 11KV豐25線 R相AMP | FEEDER | [5 empty] | 228 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K825 | 豐25線 (K825) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | F10 | A | 豐25線 K825 S 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐25線A2 | 11KV豐25線 S相AMP | FEEDER | [5 empty] | 229 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K825 | 豐25線 (K825) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | F10 | A | 豐25線 K825 T相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐25線A3 | 11KV豐25線 T相AMP | FEEDER | [5 empty] | 230 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K825 | 豐25線 (K825) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | F10 | A | 豐25線 K825 N相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐25線A0 | 11KV豐25線 N相AMP | FEEDER | [5 empty] | 231 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K834 | 豐34線(K834) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/K834/T1 |  |  | 0297 |  |  | 2-05-01 |  |  | F14 | ON/OFF | 豐34線 K834 CB 52AS |  | abhb | B2/D04_D1 | [8 empty] | 豐華DS.K834_CB | K834(11KV豐34線) CB | FEEDER | [5 empty] | 501 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K825 | 豐25線 (K825) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0162 |  |  | 1-14-02 |  |  | F10 | PHA | 豐25線 K825 RY PHA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K825_PHA | 11KV豐25線(K825) 相間RY | FEEDER | [5 empty] | 487 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K825 | 豐25線 (K825) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0163 |  |  | 1-14-03 |  |  | F10 | GDA | 豐25線 K825 RY GDA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K825_GDA | 11KV豐25線(K825) 接地RY | FEEDER | [5 empty] | 488 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K825 | 豐25線 (K825) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1170 | [10 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K825_79UL | 11KV豐25線(K825) 79RY U/L | FEEDER | [5 empty] | 770 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K825 | 豐25線 (K825) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1171 | [10 empty] | B2/D04_D1 | [16 empty] | 798 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 11 | 11kV | K831 | 豐31線(K831) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K831_DS | K831_DS (非取樣點) | FEEDER | [5 empty] | 72 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K831 | 豐31線(K831) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K831_ES | K831_ES (非取樣點) | FEEDER | [5 empty] | 73 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | K831 | 豐31線(K831) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | F11 | KVAR | 豐31線 K831 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐31線KVAR | 11KV豐31線 KVAR | FEEDER | [5 empty] | 238 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K831 | 豐31線(K831) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | F11 | A | 豐31線 K831 R 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐31線A1 | 11KV豐31線 R相AMP | FEEDER | [5 empty] | 239 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K831 | 豐31線(K831) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | F11 | A | 豐31線 K831 S相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐31線A2 | 11KV豐31線 S相AMP | FEEDER | [5 empty] | 240 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K831 | 豐31線(K831) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | F11 | A | 豐31線 K831 T相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐31線A3 | 11KV豐31線 T相AMP | FEEDER | [5 empty] | 241 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K831 | 豐31線(K831) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | F11 | A | 豐31線 K831 N相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐31線A0 | 11KV豐31線 N相AMP | FEEDER | [5 empty] | 242 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K835 | 豐35線(K835) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/K835/T1 |  |  | 0300 |  |  | 2-05-04 |  |  | F15 | ON/OFF | 豐35線 K835 CB 52AS |  | abib | B2/D04_D1 | [8 empty] | 豐華DS.K835_CB | K835(11KV豐35線) CB | FEEDER | [5 empty] | 504 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K831 | 豐31線(K831) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0289 |  |  | 2-04-01 |  |  | F11 | PHA | 豐31線 K831 RY PHA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K831_PHA | 11KV豐31線(K831) 相間RY | FEEDER | [5 empty] | 493 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K831 | 豐31線(K831) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0290 |  |  | 2-04-02 |  |  | F11 | GDA | 豐31線 K831 RY GDA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K831_GDA | 11KV豐31線(K831) 接地RY | FEEDER | [5 empty] | 494 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K831 | 豐31線(K831) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1172 | [10 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K831_79UL | 11KV豐31線(K831) 79RY U/L | FEEDER | [5 empty] | 771 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K831 | 豐31線(K831) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1173 | [10 empty] | B2/D04_D1 | [16 empty] | 799 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 11 | 11kV | K832 | 豐32線(K832) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K832_DS | K832_DS (非取樣點) | FEEDER | [5 empty] | 74 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K832 | 豐32線(K832) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K832_ES | K832_ES (非取樣點) | FEEDER | [5 empty] | 75 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | K832 | 豐32線(K832) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | F12 | KVAR | 豐32線 K832 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐32線KVAR | 11KV豐32線 KVAR | FEEDER | [5 empty] | 243 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K832 | 豐32線(K832) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | F12 | A | 豐32線 K832 R相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐32線A1 | 11KV豐32線 R相AMP | FEEDER | [5 empty] | 244 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K832 | 豐32線(K832) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | F12 | A | 豐32線 K832 S相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐32線A2 | 11KV豐32線 S相AMP | FEEDER | [5 empty] | 245 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K832 | 豐32線(K832) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | F12 | A | 豐32線 K832 T相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐32線A3 | 11KV豐32線 T相AMP | FEEDER | [5 empty] | 246 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K832 | 豐32線(K832) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | F12 | A | 豐32線 K832 N相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐32線A0 | 11KV豐32線 N相AMP | FEEDER | [5 empty] | 247 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K841 | 豐41線(K841) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/K841/T1 |  |  | 0309 |  |  | 2-06-05 |  |  | F16 | ON/OFF | 豐41線 K841 CB 52AS |  | bbeb | B2/D04_D1 | [8 empty] | 豐華DS.K841_CB | K841(11KV豐41線) CB | FEEDER | [5 empty] | 513 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K832 | 豐32線(K832) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0292 |  |  | 2-04-04 |  |  | F12 | PHA | 豐32線 K832 RY PHA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K832_PHA | 11KV豐32線(K832) 相間RY | FEEDER | [5 empty] | 496 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K832 | 豐32線(K832) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0293 |  |  | 2-04-05 |  |  | F12 | GDA | 豐32線 K832 RY GDA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K832_GDA | 11KV豐32線(K832) 接地RY | FEEDER | [5 empty] | 497 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K832 | 豐32線(K832) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1174 | [10 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K832_79UL | 11KV豐32線(K832) 79RY U/L | FEEDER | [5 empty] | 772 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K832 | 豐32線(K832) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1175 | [10 empty] | B2/D04_D1 | [16 empty] | 800 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 11 | 11kV | K833 | 豐33線(K833) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K833_DS | K833_DS (非取樣點) | FEEDER | [5 empty] | 76 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K833 | 豐33線(K833) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K833_ES | K833_ES (非取樣點) | FEEDER | [5 empty] | 77 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | K833 | 豐33線(K833) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | F13 | KVAR | 豐33線 K833 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐33線KVAR | 11KV豐33線 KVAR | FEEDER | [5 empty] | 248 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K833 | 豐33線(K833) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | F13 | A | 豐33線 K833 R 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐33線A1 | 11KV豐33線 R相AMP | FEEDER | [5 empty] | 249 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K833 | 豐33線(K833) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | F13 | A | 豐33線 K833 S 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐33線A2 | 11KV豐33線 S相AMP | FEEDER | [5 empty] | 252 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K833 | 豐33線(K833) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | F13 | A | 豐33線 K833 T相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐33線A3 | 11KV豐33線 T相AMP | FEEDER | [5 empty] | 253 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K833 | 豐33線(K833) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | F13 | A | 豐33線 K833 N相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐33線A0 | 11KV豐33線 N相AMP | FEEDER | [5 empty] | 254 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K842 | 豐42線(K842) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/K842/T1 |  |  | 0312 |  |  | 2-07-00 |  |  | F17 | ON/OFF | 豐42線 K842 CB 52AS |  | bbfb | B2/D04_D1 | [8 empty] | 豐華DS.K842_CB | K842(11KV豐42線) CB | FEEDER | [5 empty] | 516 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K833 | 豐33線(K833) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0295 |  |  | 2-04-07 |  |  | F13 | PHA | 豐33線 K833 RY PHA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K833_PHA | 11KV豐33線(K833) 相間RY | FEEDER | [5 empty] | 499 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K833 | 豐33線(K833) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0296 |  |  | 2-05-00 |  |  | F13 | GDA | 豐33線 K833 RY GDA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K833_GDA | 11KV豐33線(K833) 接地RY | FEEDER | [5 empty] | 500 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K833 | 豐33線(K833) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1176 | [10 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K833_79UL | 11KV豐33線(K833) 79RY U/L | FEEDER | [5 empty] | 773 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K833 | 豐33線(K833) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1177 | [10 empty] | B2/D04_D1 | [16 empty] | 801 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 11 | 11kV | K834 | 豐34線(K834) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K834_DS | K834_DS (非取樣點) | FEEDER | [5 empty] | 78 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K834 | 豐34線(K834) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K834_ES | K834_ES (非取樣點) | FEEDER | [5 empty] | 79 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | K834 | 豐34線(K834) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0133 |  |  | 2-85 |  |  | F14 | KVAR | 豐34線 K834 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐34線KVAR | 11KV豐34線 KVAR | FEEDER | [5 empty] | 255 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K834 | 豐34線(K834) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | F14 | A | 豐34線 K834 R 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐34線A1 | 11KV豐34線 R相AMP | FEEDER | [5 empty] | 256 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K834 | 豐34線(K834) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0135 |  |  | 2-87 |  |  | F14 | A | 豐34線 K834 S 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐34線A2 | 11KV豐34線 S相AMP | FEEDER | [5 empty] | 257 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K834 | 豐34線(K834) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0136 |  |  | 2-88 |  |  | F14 | A | 豐34線 K834 T 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐34線A3 | 11KV豐34線 T相AMP | FEEDER | [5 empty] | 258 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K834 | 豐34線(K834) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0137 |  |  | 2-89 |  |  | F14 | A | 豐34線 K834 N相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐34線A0 | 11KV豐34線 N相AMP | FEEDER | [5 empty] | 259 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K843 | 豐43線(K843) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/K843/T1 |  |  | 0315 |  |  | 2-07-03 |  |  | F18 | ON/OFF | 豐43線 K843 CB 52AS |  | bbgb | B2/D04_D1 | [8 empty] | 豐華DS.K843_CB | K843(11KV豐43線) CB | FEEDER | [5 empty] | 519 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K834 | 豐34線(K834) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0298 |  |  | 2-05-02 |  |  | F14 | PHA | 豐34線 K834 RY PHA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K834_PHA | 11KV豐34線(K834) 相間RY | FEEDER | [5 empty] | 502 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K834 | 豐34線(K834) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0299 |  |  | 2-05-03 |  |  | F14 | GDA | 豐34線 K834 RY GDA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K834_GDA | 11KV豐34線(K834) 接地RY | FEEDER | [5 empty] | 503 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K834 | 豐34線(K834) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1178 | [10 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K834_79UL | 11KV豐34線(K834) 79RY U/L | FEEDER | [5 empty] | 774 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K834 | 豐34線(K834) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1179 | [10 empty] | B2/D04_D1 | [16 empty] | 802 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 11 | 11kV | K835 | 豐35線(K835) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K835_DS | K835_DS (非取樣點) | FEEDER | [5 empty] | 80 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K835 | 豐35線(K835) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K835_ES | K835_ES (非取樣點) | FEEDER | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | K835 | 豐35線(K835) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0138 |  |  | 2-8A |  |  | F15 | KVAR | 豐35線 K835 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐35線KVAR | 11KV豐35線 KVAR | FEEDER | [5 empty] | 260 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K835 | 豐35線(K835) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0139 |  |  | 2-8B |  |  | F15 | A | 豐35線 K835 R 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐35線A1 | 11KV豐35線 R相AMP | FEEDER | [5 empty] | 261 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K835 | 豐35線(K835) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0140 |  |  | 2-8C |  |  | F15 | A | 豐35線 K835 S 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐35線A2 | 11KV豐35線 S相AMP | FEEDER | [5 empty] | 262 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K835 | 豐35線(K835) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0141 |  |  | 2-8D |  |  | F15 | A | 豐35線 K835 T 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐35線A3 | 11KV豐35線 T相AMP | FEEDER | [5 empty] | 263 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K835 | 豐35線(K835) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0142 |  |  | 2-8E |  |  | F15 | A | 豐35線 K835 N相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐35線A0 | 11KV豐35線 N相AMP | FEEDER | [5 empty] | 264 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K844 | 豐44線(K844) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/K844/T1 |  |  | 0318 |  |  | 2-07-06 |  |  | F19 | ON/OFF | 豐44線 K844 CB 52AS |  | bbib | B2/D04_D1 | [8 empty] | 豐華DS.K844_CB | K844(11KV豐44線) CB | FEEDER | [5 empty] | 522 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K835 | 豐35線(K835) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0301 |  |  | 2-05-05 |  |  | F15 | PHA | 豐35線 K835 RY PHA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K835_PHA | 11KV豐35線(K835) 相間RY | FEEDER | [5 empty] | 505 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K835 | 豐35線(K835) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0302 |  |  | 2-05-06 |  |  | F15 | GDA | 豐35線 K835 RY GDA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K835_GDA | 11KV豐35線(K835) 接地RY | FEEDER | [5 empty] | 506 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K835 | 豐35線(K835) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1180 | [10 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K835_79UL | 11KV豐35線(K835) 79RY U/L | FEEDER | [5 empty] | 775 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K835 | 豐35線(K835) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1181 | [10 empty] | B2/D04_D1 | [16 empty] | 803 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 11 | 11kV | K841 | 豐41線(K841) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K841_DS | K841_DS (非取樣點) | FEEDER | [5 empty] | 88 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K841 | 豐41線(K841) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K841_ES | K841_ES (非取樣點) | FEEDER | [5 empty] | 89 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | K841 | 豐41線(K841) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0152 |  |  | 2-98 |  |  | F16 | KVAR | 豐41線 K841 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐41線KVAR | 11KV豐41線 KVAR | FEEDER | [5 empty] | 274 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K841 | 豐41線(K841) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0153 |  |  | 2-99 |  |  | F16 | A | 豐41線 K841 R 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐41線A1 | 11KV豐41線 R相AMP | FEEDER | [5 empty] | 275 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K841 | 豐41線(K841) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0154 |  |  | 2-9A |  |  | F16 | A | 豐41線 K841 S 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐41線A2 | 11KV豐41線 S相AMP | FEEDER | [5 empty] | 276 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K841 | 豐41線(K841) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0155 |  |  | 2-9B |  |  | F16 | A | 豐41線 K841 T 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐41線A3 | 11KV豐41線 T相AMP | FEEDER | [5 empty] | 277 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K841 | 豐41線(K841) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0156 |  |  | 2-9C |  |  | F16 | A | 豐41線 K841 N相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐41線A0 | 11KV豐41線 N相AMP | FEEDER | [5 empty] | 278 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K845 | 豐45線(K845) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/K845/T1 |  |  | 0321 |  |  | 2-08-01 |  |  | F20 | ON/OFF | 豐45線 K845 CB 52AS |  | bbjb | B2/D04_D1 | [8 empty] | 豐華DS.K845_CB | K845(11KV豐45線) CB | FEEDER | [5 empty] | 525 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K841 | 豐41線(K841) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0310 |  |  | 2-06-06 |  |  | F16 | PHA | 豐41線 K841 RY PHA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K841_PHA | 11KV豐41線(K841) 相間RY | FEEDER | [5 empty] | 514 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K841 | 豐41線(K841) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0311 |  |  | 2-06-07 |  |  | F16 | GDA | 豐41線 K841 RY GDA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K841_GDA | 11KV豐41線(K841) 接地RY | FEEDER | [5 empty] | 515 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K841 | 豐41線(K841) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1182 | [10 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K841_79UL | 11KV豐41線(K841) 79RY U/L | FEEDER | [5 empty] | 776 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K841 | 豐41線(K841) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1183 | [10 empty] | B2/D04_D1 | [16 empty] | 804 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 11 | 11kV | K842 | 豐42線(K842) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K842_DS | K842_DS (非取樣點) | FEEDER | [5 empty] | 90 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K842 | 豐42線(K842) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K842_ES | K842_ES (非取樣點) | FEEDER | [5 empty] | 91 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | K842 | 豐42線(K842) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0157 |  |  | 2-9D |  |  | F17 | KVAR | 豐42線 K842 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐42線KVAR | 11KV豐42線 KVAR | FEEDER | [5 empty] | 279 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K842 | 豐42線(K842) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0158 |  |  | 2-9E |  |  | F17 | A | 豐42線 K842 R 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐42線A1 | 11KV豐42線 R相AMP | FEEDER | [5 empty] | 280 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K842 | 豐42線(K842) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0159 |  |  | 2-9F |  |  | F17 | A | 豐42線 K842 S 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐42線A2 | 11KV豐42線 S相AMP | FEEDER | [5 empty] | 281 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K842 | 豐42線(K842) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0160 |  |  | 2-A0 |  |  | F17 | A | 豐42線 K842 T 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐42線A3 | 11KV豐42線 T相AMP | FEEDER | [5 empty] | 282 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K842 | 豐42線(K842) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0161 |  |  | 2-A1 |  |  | F17 | A | 豐42線 K842 N相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐42線A0 | 11KV豐42線 N相AMP | FEEDER | [5 empty] | 283 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K861 | 豐61線(K861) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/K861/T1 |  |  | 0333 |  |  | 2-09-05 |  |  | F21 | ON/OFF | 豐61線 K861 CB 52AS |  | accb | B2/D04_D1 | [8 empty] | 豐華DS.K861_CB | K861(23KV豐61線) CB | FEEDER | [5 empty] | 537 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K842 | 豐42線(K842) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0313 |  |  | 2-07-01 |  |  | F17 | PHA | 豐42線 K842 RY PHA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K842_PHA | 11KV豐42線(K842) 相間RY | FEEDER | [5 empty] | 517 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K842 | 豐42線(K842) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0314 |  |  | 2-07-02 |  |  | F17 | GDA | 豐42線 K842 RY GDA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K842_GDA | 11KV豐42線(K842) 接地RY | FEEDER | [5 empty] | 518 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K842 | 豐42線(K842) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1184 | [10 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K842_79UL | 11KV豐42線(K842) 79RY U/L | FEEDER | [5 empty] | 777 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K842 | 豐42線(K842) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1185 | [10 empty] | B2/D04_D1 | [16 empty] | 805 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 11 | 11kV | K843 | 豐43線(K843) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K843_DS | K843_DS (非取樣點) | FEEDER | [5 empty] | 92 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K843 | 豐43線(K843) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K843_ES | K843_ES (非取樣點) | FEEDER | [5 empty] | 93 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | K843 | 豐43線(K843) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0162 |  |  | 2-A2 |  |  | F18 | KVAR | 豐43線 K843 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐43線KVAR | 11KV豐43線 KVAR | FEEDER | [5 empty] | 284 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K843 | 豐43線(K843) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0163 |  |  | 2-A3 |  |  | F18 | A | 豐43線 K843 R 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐43線A1 | 11KV豐43線 R相AMP | FEEDER | [5 empty] | 285 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K843 | 豐43線(K843) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0164 |  |  | 2-A4 |  |  | F18 | A | 豐43線 K843 S 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐43線A2 | 11KV豐43線 S相AMP | FEEDER | [5 empty] | 286 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K843 | 豐43線(K843) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0165 |  |  | 2-A5 |  |  | F18 | A | 豐43線 K843 T 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐43線A3 | 11KV豐43線 T相AMP | FEEDER | [5 empty] | 287 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K843 | 豐43線(K843) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0166 |  |  | 2-A6 |  |  | F18 | A | 豐43線 K843 N相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐43線A0 | 11KV豐43線 N相AMP | FEEDER | [5 empty] | 288 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K862 | 豐62線(K862) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/K862/T1 |  |  | 0336 |  |  | 2-0A-00 |  |  | F22 | ON/OFF | 豐62線 K862 CB 52AS |  | aceb | B2/D04_D1 | [8 empty] | 豐華DS.K862_CB | K862(23KV豐62線) CB | FEEDER | [5 empty] | 540 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K843 | 豐43線(K843) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0316 |  |  | 2-07-04 |  |  | F18 | PHA | 豐43線 K843 RY PHA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K843_PHA | 11KV豐43線(K843) 相間RY | FEEDER | [5 empty] | 520 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K843 | 豐43線(K843) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0317 |  |  | 2-07-05 |  |  | F18 | GDA | 豐43線 K843 RY GDA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K843_GDA | 11KV豐43線(K843) 接地RY | FEEDER | [5 empty] | 521 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K843 | 豐43線(K843) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1186 | [10 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K843_79UL | 11KV豐43線(K843) 79RY U/L | FEEDER | [5 empty] | 778 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K843 | 豐43線(K843) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1187 | [10 empty] | B2/D04_D1 | [16 empty] | 806 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 11 | 11kV | K844 | 豐44線(K844) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K844_DS | K844_DS (非取樣點) | FEEDER | [5 empty] | 94 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K844 | 豐44線(K844) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K844_ES | K844_ES (非取樣點) | FEEDER | [5 empty] | 95 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | K844 | 豐44線(K844) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0167 |  |  | 2-A7 |  |  | F19 | KVAR | 豐44線 K844 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐44線KVAR | 11KV豐44線 KVAR | FEEDER | [5 empty] | 289 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K844 | 豐44線(K844) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0168 |  |  | 2-A8 |  |  | F19 | A | 豐44線 K844 R 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐44線A1 | 11KV豐44線 R相AMP | FEEDER | [5 empty] | 290 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K844 | 豐44線(K844) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0169 |  |  | 2-A9 |  |  | F19 | A | 豐44線 K844 S 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐44線A2 | 11KV豐44線 S相AMP | FEEDER | [5 empty] | 291 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K844 | 豐44線(K844) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0170 |  |  | 2-AA |  |  | F19 | A | 豐44線 K844 T 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐44線A3 | 11KV豐44線 T相AMP | FEEDER | [5 empty] | 292 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K844 | 豐44線(K844) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0171 |  |  | 2-AB |  |  | F19 | A | 豐44線 K844 N相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐44線A0 | 11KV豐44線 N相AMP | FEEDER | [5 empty] | 293 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K863 | 豐63線(K863) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/K863/T1 |  |  | 0339 |  |  | 2-0A-03 |  |  | F23 | ON/OFF | 豐63線 K863 CB 52AS |  | acfb | B2/D04_D1 | [8 empty] | 豐華DS.K863_CB | K863(23KV豐63線) CB | FEEDER | [5 empty] | 543 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K844 | 豐44線(K844) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0319 |  |  | 2-07-07 |  |  | F19 | PHA | 豐44線 K844 RY PHA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K844_PHA | 11KV豐44線(K844) 相間RY | FEEDER | [5 empty] | 523 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K844 | 豐44線(K844) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0320 |  |  | 2-08-00 |  |  | F19 | GDA | 豐44線 K844 RY GDA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K844_GDA | 11KV豐44線(K844) 接地RY | FEEDER | [5 empty] | 524 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K844 | 豐44線(K844) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1188 | [10 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K844_79UL | 11KV豐44線(K844) 79RY U/L | FEEDER | [5 empty] | 779 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K844 | 豐44線(K844) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1189 | [10 empty] | B2/D04_D1 | [16 empty] | 807 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 11 | 11kV | K845 | 豐45線(K845) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K845_DS | K845_DS (非取樣點) | FEEDER | [5 empty] | 96 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K845 | 豐45線(K845) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K845_ES | K845_ES (非取樣點) | FEEDER | [5 empty] | 97 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 11 | 11kV | K845 | 豐45線(K845) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0172 |  |  | 2-AC |  |  | F20 | KVAR | 豐45線 K845 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐45線KVAR | 11KV豐45線 KVAR | FEEDER | [5 empty] | 294 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K845 | 豐45線(K845) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0173 |  |  | 2-AD |  |  | F20 | A | 豐45線 K845 R 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐45線A1 | 11KV豐45線 R相AMP | FEEDER | [5 empty] | 295 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K845 | 豐45線(K845) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0174 |  |  | 2-AE |  |  | F20 | A | 豐45線 K845 S 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐45線A2 | 11KV豐45線 S相AMP | FEEDER | [5 empty] | 296 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K845 | 豐45線(K845) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0175 |  |  | 2-AF |  |  | F20 | A | 豐45線 K845 T 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐45線A3 | 11KV豐45線 T相AMP | FEEDER | [5 empty] | 297 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | K845 | 豐45線(K845) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0176 |  |  | 2-B0 |  |  | F20 | A | 豐45線 K845 N相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐45線A0 | 11KV豐45線 N相AMP | FEEDER | [5 empty] | 298 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K864 | 豐64線(K864) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/K864/T1 |  |  | 0342 |  |  | 2-0A-06 |  |  | F24 | ON/OFF | 豐64線 K864 CB 52AS |  | acgb | B2/D04_D1 | [8 empty] | 豐華DS.K864_CB | K864(23KV豐64線) CB | FEEDER | [5 empty] | 546 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K845 | 豐45線(K845) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0322 |  |  | 2-08-02 |  |  | F20 | PHA | 豐45線 K845 RY PHA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K845_PHA | 11KV豐45線(K845) 相間RY | FEEDER | [5 empty] | 526 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K845 | 豐45線(K845) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0323 |  |  | 2-08-03 |  |  | F20 | GDA | 豐45線 K845 RY GDA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K845_GDA | 11KV豐45線(K845) 接地RY | FEEDER | [5 empty] | 527 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K845 | 豐45線(K845) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1190 | [10 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K845_79UL | 11KV豐45線(K845) 79RY U/L | FEEDER | [5 empty] | 780 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K845 | 豐45線(K845) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1191 | [10 empty] | B2/D04_D1 | [16 empty] | 808 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 22 | 22kV | K861 | 豐61線(K861) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K861_DS | K861_DS (非取樣點) | FEEDER | [5 empty] | 106 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 22 | 22kV | K861 | 豐61線(K861) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K861_ES | K861_ES (非取樣點) | FEEDER | [5 empty] | 107 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 22 | 22kV | K861 | 豐61線(K861) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0186 |  |  | 2-BA |  |  | F21 | A | 豐61線 K861 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐61線KVAR | 23KV豐61線 KVAR | FEEDER | [5 empty] | 308 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K861 | 豐61線(K861) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0187 |  |  | 2-BB |  |  | F21 | A | 豐61線 K861 R 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐61線A1 | 23KV豐61線 R相AMP | FEEDER | [5 empty] | 309 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K861 | 豐61線(K861) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0188 |  |  | 2-BC |  |  | F21 | A | 豐61線 K861 S 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐61線A2 | 23KV豐61線 S相AMP | FEEDER | [5 empty] | 310 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K861 | 豐61線(K861) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0189 |  |  | 2-BD |  |  | F21 | A | 豐61線 K861 T 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐61線A3 | 23KV豐61線 T相AMP | FEEDER | [5 empty] | 311 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K861 | 豐61線(K861) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0190 |  |  | 2-BE |  |  | F21 | A | 豐61線 K861 N相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐61線A0 | 23KV豐61線 N相AMP | FEEDER | [5 empty] | 312 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K865 | 豐65線(K865) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/K865/T1 |  |  | 0348 |  |  | 2-0B-04 |  |  | F25 | ON/OFF | 豐65線 K865 CB 52AS |  | achb | B2/D04_D1 | [8 empty] | 豐華DS.K865_CB | K865(23KV豐65線) CB | FEEDER | [5 empty] | 552 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 22 | 22kV | K861 | 豐61線(K861) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0334 |  |  | 2-09-06 |  |  | F21 | PHA | 豐61線 K861 RY PHA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K861_PHA | 23KV豐61線(K861) 相間RY | FEEDER | [5 empty] | 538 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | K861 | 豐61線(K861) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0335 |  |  | 2-09-07 |  |  | F21 | GDA | 豐61線 K861 RY GDA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K861_GDA | 23KV豐61線(K861) 接地RY | FEEDER | [5 empty] | 539 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | K861 | 豐61線(K861) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1192 | [10 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K861_79UL | 23KV豐61線(K861) 79RY U/L | FEEDER | [5 empty] | 781 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 22 | 22kV | K861 | 豐61線(K861) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1193 | [10 empty] | B2/D04_D1 | [16 empty] | 809 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 22 | 22kV | K862 | 豐62線(K862) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K862_DS | K862_DS (非取樣點) | FEEDER | [5 empty] | 108 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 22 | 22kV | K862 | 豐62線(K862) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K862_ES | K862_ES (非取樣點) | FEEDER | [5 empty] | 109 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 22 | 22kV | K862 | 豐62線(K862) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0191 |  |  | 2-BF |  |  | F22 | KVAR | 豐62線 K862 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐62線KVAR | 23KV豐62線 KVAR | FEEDER | [5 empty] | 313 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K862 | 豐62線(K862) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0194 |  |  | 2-C2 |  |  | F22 | A | 豐62線 K862 R 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐62線A1 | 23KV豐62線 R相AMP | FEEDER | [5 empty] | 316 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K862 | 豐62線(K862) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0195 |  |  | 2-C3 |  |  | F22 | A | 豐62線 K862 S 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐62線A2 | 23KV豐62線 S相AMP | FEEDER | [5 empty] | 317 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K862 | 豐62線(K862) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0196 |  |  | 2-C4 |  |  | F22 | A | 豐62線 K862 T 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐62線A3 | 23KV豐62線 T相AMP | FEEDER | [5 empty] | 318 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K862 | 豐62線(K862) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0197 |  |  | 2-C5 |  |  | F22 | A | 豐62線 K862 N相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐62線A0 | 23KV豐62線 N相AMP | FEEDER | [5 empty] | 319 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K866 | 豐66線(K866) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/K866/T1 |  |  | 0351 |  |  | 2-0B-07 |  |  | F26 | ON/OFF | 豐66線 K866 CB 52AS |  | acib | B2/D04_D1 | [8 empty] | 豐華DS.K866_CB | K866(23KV豐66線) CB | FEEDER | [5 empty] | 555 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 22 | 22kV | K862 | 豐62線(K862) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0337 |  |  | 2-0A-01 |  |  | F22 | PHA | 豐62線 K862 RY PHA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K862_PHA | 23KV豐62線(K862) 相間RY | FEEDER | [5 empty] | 541 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | K862 | 豐62線(K862) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0338 |  |  | 2-0A-02 |  |  | F22 | GDA | 豐62線 K862 RY GDA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K862_GDA | 23KV豐62線(K862) 接地RY | FEEDER | [5 empty] | 542 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | K862 | 豐62線(K862) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1194 | [10 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K862_79UL | 23KV豐62線(K862) 79RY U/L | FEEDER | [5 empty] | 782 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 22 | 22kV | K862 | 豐62線(K862) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1195 | [10 empty] | B2/D04_D1 | [16 empty] | 810 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 22 | 22kV | K863 | 豐63線(K863) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K863_DS | K863_DS (非取樣點) | FEEDER | [5 empty] | 110 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 22 | 22kV | K863 | 豐63線(K863) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K863_ES | K863_ES (非取樣點) | FEEDER | [5 empty] | 111 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 22 | 22kV | K863 | 豐63線(K863) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0198 |  |  | 2-C6 |  |  | F23 | KVAR | 豐63線 K863 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐63線KVAR | 23KV豐63線 KVAR | FEEDER | [5 empty] | 320 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K863 | 豐63線(K863) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0199 |  |  | 2-C7 |  |  | F23 | A | 豐63線 K863 R 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐63線A1 | 23KV豐63線 R相AMP | FEEDER | [5 empty] | 321 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K863 | 豐63線(K863) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0200 |  |  | 2-C8 |  |  | F23 | A | 豐63線 K863 S 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐63線A2 | 23KV豐63線 S相AMP | FEEDER | [5 empty] | 322 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K863 | 豐63線(K863) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0201 |  |  | 2-C9 |  |  | F23 | A | 豐63線 K863 T 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐63線A3 | 23KV豐63線 T相AMP | FEEDER | [5 empty] | 323 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K863 | 豐63線(K863) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0202 |  |  | 2-CA |  |  | F23 | A | 豐63線 K863 N相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐63線A0 | 23KV豐63線 N相AMP | FEEDER | [5 empty] | 324 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K867 | 豐67線(K867) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/K867/T1 |  |  | 0354 |  |  | 2-0C-02 |  |  | F27 | ON/OFF | 豐67線 K867 CB 52AS |  | acjb | B2/D04_D1 | [8 empty] | 豐華DS.K867_CB | K867(23KV豐67線) CB | FEEDER | [5 empty] | 558 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 22 | 22kV | K863 | 豐63線(K863) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0340 |  |  | 2-0A-04 |  |  | F23 | PHA | 豐63線 K863 RY PHA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K863_PHA | 23KV豐63線(K863) 相間RY | FEEDER | [5 empty] | 544 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | K863 | 豐63線(K863) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0341 |  |  | 2-0A-05 |  |  | F23 | GDA | 豐63線 K863 RY GDA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K863_GDA | 23KV豐63線(K863) 接地RY | FEEDER | [5 empty] | 545 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | K863 | 豐63線(K863) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1196 | [10 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K863_79UL | 23KV豐63線(K863) 79RY U/L | FEEDER | [5 empty] | 783 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 22 | 22kV | K863 | 豐63線(K863) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1197 | [10 empty] | B2/D04_D1 | [16 empty] | 811 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 22 | 22kV | K864 | 豐64線(K864) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K864_DS | K864_DS (非取樣點) | FEEDER | [5 empty] | 112 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 22 | 22kV | K864 | 豐64線(K864) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K864_ES | K864_ES (非取樣點) | FEEDER | [5 empty] | 113 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 22 | 22kV | K864 | 豐64線(K864) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0203 |  |  | 2-CB |  |  | F24 | KVAR | 豐64線 K864 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐64線KVAR | 23KV豐64線 KVAR | FEEDER | [5 empty] | 325 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K864 | 豐64線(K864) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0204 |  |  | 2-CC |  |  | F24 | A | 豐64線 K864 R 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐64線A1 | 23KV豐64線 R相AMP | FEEDER | [5 empty] | 326 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K864 | 豐64線(K864) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0205 |  |  | 2-CD |  |  | F24 | A | 豐64線 K864 S 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐64線A2 | 23KV豐64線 S相AMP | FEEDER | [5 empty] | 327 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K864 | 豐64線(K864) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0206 |  |  | 2-CE |  |  | F24 | A | 豐64線 K864 T 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐64線A3 | 23KV豐64線 T相AMP | FEEDER | [5 empty] | 328 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K864 | 豐64線(K864) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0207 |  |  | 2-CF |  |  | F24 | A | 豐64線 K864 N相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐64線A0 | 23KV豐64線 N相AMP | FEEDER | [5 empty] | 329 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K868 | 豐68線(K868) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/K868/T1 |  |  | 0357 |  |  | 2-0C-05 |  |  | F28 | ON/OFF | 豐68線 K868 CB 52AS |  | ackb | B2/D04_D1 | [8 empty] | 豐華DS.K868_CB | K868(23KV豐68線) CB | FEEDER | [5 empty] | 561 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 22 | 22kV | K864 | 豐64線(K864) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0343 |  |  | 2-0A-07 |  |  | F24 | PHA | 豐64線 K864 RY PHA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K864_PHA | 23KV豐64線(K864) 相間RY | FEEDER | [5 empty] | 547 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | K864 | 豐64線(K864) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0344 |  |  | 2-0B-00 |  |  | F24 | GDA | 豐64線 K864 RY GDA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K864_GDA | 23KV豐64線(K864) 接地RY | FEEDER | [5 empty] | 548 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | K864 | 豐64線(K864) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1198 | [10 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K864_79UL | 23KV豐64線(K864) 79RY U/L | FEEDER | [5 empty] | 784 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 22 | 22kV | K864 | 豐64線(K864) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1199 | [10 empty] | B2/D04_D1 | [16 empty] | 812 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 22 | 22kV | K865 | 豐65線(K865) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K865_DS | K865_DS (非取樣點) | FEEDER | [5 empty] | 116 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 22 | 22kV | K865 | 豐65線(K865) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K865_ES | K865_ES (非取樣點) | FEEDER | [5 empty] | 117 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 22 | 22kV | K865 | 豐65線(K865) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0208 |  |  | 2-D0 |  |  | F25 | KVAR | 豐65線 K865 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐65線KVAR | 23KV豐65線 KVAR | FEEDER | [5 empty] | 330 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K865 | 豐65線(K865) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0209 |  |  | 2-D1 |  |  | F25 | A | 豐65線 K865 R 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐65線A1 | 23KV豐65線 R相AMP | FEEDER | [5 empty] | 331 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K865 | 豐65線(K865) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0210 |  |  | 2-D2 |  |  | F25 | A | 豐65線 K865 S 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐65線A2 | 23KV豐65線 S相AMP | FEEDER | [5 empty] | 332 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K865 | 豐65線(K865) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0211 |  |  | 2-D3 |  |  | F25 | A | 豐65線 K865 T 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐65線A3 | 23KV豐65線 T相AMP | FEEDER | [5 empty] | 333 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K865 | 豐65線(K865) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0212 |  |  | 2-D4 |  |  | F25 | A | 豐65線 K865 N相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐65線A0 | 23KV豐65線 N相AMP | FEEDER | [5 empty] | 334 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1530 | 豐華～奇晶一線(1530) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D04C11/T1 |  | 0008 |  |  | 1-01-00 |  |  | L3 | ON/OFF | 豐華奇晶一線(1530)CB 52AS |  | aaga | B2/D04_A1 | [8 empty] | 豐華DS.1530_CB | 1530(豐華奇晶一線) CB | LINE161 | [5 empty] | 360 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 22 | 22kV | K865 | 豐65線(K865) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0349 |  |  | 2-0B-05 |  |  | F25 | PHA | 豐65線 K865 RY PHA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K865_PHA | 23KV豐65線(K865) 相間RY | FEEDER | [5 empty] | 553 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | K865 | 豐65線(K865) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0350 |  |  | 2-0B-06 |  |  | F25 | GDA | 豐65線 K865 RY GDA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K865_GDA | 23KV豐65線(K865) 接地RY | FEEDER | [5 empty] | 554 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | K865 | 豐65線(K865) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1200 | [10 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K865_79UL | 23KV豐65線(K865) 79RY U/L | FEEDER | [5 empty] | 785 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 22 | 22kV | K865 | 豐65線(K865) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1201 | [10 empty] | B2/D04_D1 | [16 empty] | 813 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 22 | 22kV | K866 | 豐66線(K866) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K866_DS | K866_DS (非取樣點) | FEEDER | [5 empty] | 118 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 22 | 22kV | K866 | 豐66線(K866) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K866_ES | K866_ES (非取樣點) | FEEDER | [5 empty] | 119 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 22 | 22kV | K866 | 豐66線(K866) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0213 |  |  | 2-D5 |  |  | F26 | KVAR | 豐66線 K866 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐66線KVAR | 23KV豐66線 KVAR | FEEDER | [5 empty] | 335 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K866 | 豐66線(K866) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0214 |  |  | 2-D6 |  |  | F26 | A | 豐66線 K866 R 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐66線A1 | 23KV豐66線 R相AMP | FEEDER | [5 empty] | 336 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K866 | 豐66線(K866) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0215 |  |  | 2-D7 |  |  | F26 | A | 豐66線 K866 S 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐66線A2 | 23KV豐66線 S相AMP | FEEDER | [5 empty] | 337 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K866 | 豐66線(K866) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0216 |  |  | 2-D8 |  |  | F26 | A | 豐66線 K866 T 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐66線A3 | 23KV豐66線 T相AMP | FEEDER | [5 empty] | 338 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K866 | 豐66線(K866) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0217 |  |  | 2-D9 |  |  | F26 | A | 豐66線 K866 N相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐66線A0 | 23KV豐66線 N相AMP | FEEDER | [5 empty] | 339 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1540 | 豐華～奇晶四線(1540) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D04C15/T1 |  | 0013 |  |  | 1-01-05 |  |  | L4 | ON/OFF | 豐華奇晶四線(1540)CB 52AS |  | aaha | B2/D04_A1 | [8 empty] | 豐華DS.1540_CB | 1540(豐華奇晶四線) CB | LINE161 | [5 empty] | 365 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 22 | 22kV | K866 | 豐66線(K866) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0352 |  |  | 2-0C-00 |  |  | F26 | PHA | 豐66線 K866 RY PHA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K866_PHA | 23KV豐66線(K866) 相間RY | FEEDER | [5 empty] | 556 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | K866 | 豐66線(K866) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0353 |  |  | 2-0C-01 |  |  | F26 | GDA | 豐66線 K866 RY GDA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K866_GDA | 23KV豐66線(K866) 接地RY | FEEDER | [5 empty] | 557 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | K866 | 豐66線(K866) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1202 | [10 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K866_79UL | 23KV豐66線(K866) 79RY U/L | FEEDER | [5 empty] | 786 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 22 | 22kV | K866 | 豐66線(K866) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1203 | [10 empty] | B2/D04_D1 | [16 empty] | 814 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 22 | 22kV | K867 | 豐67線(K867) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K867_DS | K867_DS (非取樣點) | FEEDER | [5 empty] | 120 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 22 | 22kV | K867 | 豐67線(K867) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K867_ES | K867_ES (非取樣點) | FEEDER | [5 empty] | 121 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 22 | 22kV | K867 | 豐67線(K867) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0218 |  |  | 2-DA |  |  | F27 | KVAR | 豐67線 K867 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐67線KVAR | 23KV豐67線 KVAR | FEEDER | [5 empty] | 340 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K867 | 豐67線(K867) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0219 |  |  | 2-DB |  |  | F27 | A | 豐67線 K867 R 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐67線A1 | 23KV豐67線 R相AMP | FEEDER | [5 empty] | 341 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K867 | 豐67線(K867) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0220 |  |  | 2-DC |  |  | F27 | A | 豐67線 K867 S 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐67線A2 | 23KV豐67線 S相AMP | FEEDER | [5 empty] | 342 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K867 | 豐67線(K867) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0221 |  |  | 2-DD |  |  | F27 | A | 豐67線 K867 T 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐67線A3 | 23KV豐67線 T相AMP | FEEDER | [5 empty] | 343 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K867 | 豐67線(K867) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0222 |  |  | 2-DE |  |  | F27 | A | 豐67線 K867 N相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐67線A0 | 23KV豐67線 N相AMP | FEEDER | [5 empty] | 344 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華~聯電五一路(1610) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D04C191/T1 |  | 0034 |  |  | 1-04-02 |  |  | Line9 | ON/OFF | 豐華聯電五一路 (1610)CB 52AS |  | aaoa | B2/D04_A1 | [8 empty] | 豐華DS.1610_CB | 1610(豐華聯電五一路) CB | LINE161 | [5 empty] | 386 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 22 | 22kV | K867 | 豐67線(K867) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0355 |  |  | 2-0C-03 |  |  | F27 | PHA | 豐67線 K867 RY PHA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K867_PHA | 23KV豐67線(K867) 相間RY | FEEDER | [5 empty] | 559 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | K867 | 豐67線(K867) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0356 |  |  | 2-0C-04 |  |  | F27 | GDA | 豐67線 K867 RY GDA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K867_GDA | 23KV豐67線(K867) 接地RY | FEEDER | [5 empty] | 560 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | K867 | 豐67線(K867) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1204 | [10 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K867_79UL | 23KV豐67線(K867) 79RY U/L | FEEDER | [5 empty] | 787 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 22 | 22kV | K867 | 豐67線(K867) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1205 | [10 empty] | B2/D04_D1 | [16 empty] | 815 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 22 | 22kV | K868 | 豐68線(K868) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K868_DS | K868_DS (非取樣點) | FEEDER | [5 empty] | 122 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 22 | 22kV | K868 | 豐68線(K868) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K868_ES | K868_ES (非取樣點) | FEEDER | [5 empty] | 123 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 22 | 22kV | K868 | 豐68線(K868) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0223 |  |  | 2-DF |  |  | F28 | KVAR | 豐68線 K868 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐68線KVAR | 23KV豐68線 KVAR | FEEDER | [5 empty] | 345 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K868 | 豐68線(K868) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0224 |  |  | 2-E0 |  |  | F28 | A | 豐68線 K868 R 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐68線A1 | 23KV豐68線 R相AMP | FEEDER | [5 empty] | 346 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K868 | 豐68線(K868) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0225 |  |  | 2-E1 |  |  | F28 | A | 豐68線 K868 S 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐68線A2 | 23KV豐68線 S相AMP | FEEDER | [5 empty] | 347 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K868 | 豐68線(K868) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0226 |  |  | 2-E2 |  |  | F28 |  | 豐68線 K868 T 相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐68線A3 | 23KV豐68線 T相AMP | FEEDER | [5 empty] | 348 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | K868 | 豐68線(K868) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0227 |  |  | 2-E3 |  |  | F28 | A | 豐68線 K868 N相電流 | A_-600_600(-2000_2000) |  | B2/D04_D1 | [8 empty] | 豐華DS.豐68線A0 | 23KV豐68線 N相AMP | FEEDER | [5 empty] | 349 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華~聯電五二路(1620) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D04C192/T1 |  | 0038 |  |  | 1-04-06 |  |  | Line10 | ON/OFF | 豐華聯電五二路 (1620)CB 52AS |  | aapa | B2/D04_A1 | [8 empty] | 豐華DS.1620_CB | 1620(豐華聯電五二路) CB | LINE161 | [5 empty] | 390 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 22 | 22kV | K868 | 豐68線(K868) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0358 |  |  | 2-0C-06 |  |  | F28 | PHA | 豐68線 K868 RY PHA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K868_PHA | 23KV豐68線(K868) 相間RY | FEEDER | [5 empty] | 562 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | K868 | 豐68線(K868) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0359 |  |  | 2-0C-07 |  |  | F28 | GDA | 豐68線 K868 RY GDA |  |  | B2/D04_D1 | [8 empty] | 豐華DS.K868_GDA | 23KV豐68線(K868) 接地RY | FEEDER | [5 empty] | 563 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | K868 | 豐68線(K868) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1206 | [10 empty] | B2/D04_D1 | [8 empty] | 豐華DS.K868_79UL | 23KV豐68線(K868) 79RY U/L | FEEDER | [5 empty] | 788 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 22 | 22kV | K868 | 豐68線(K868) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1207 | [10 empty] | B2/D04_D1 | [16 empty] | 816 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D04 | 豐華DS | 161 | 161kV | 1530 | 豐華～奇晶一線(1530) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1530LE | 1530LE (非取樣點) | LINE161 | [5 empty] | 6 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1530 | 豐華～奇晶一線(1530) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1530BE | 1530BE (非取樣點) | LINE161 | [5 empty] | 7 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1530 | 豐華～奇晶一線(1530) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | L3 | MW | 豐華奇晶一線 (1530)瓦 | MW_-560_560(-2000_2000) |  | B2/D04_A1 | [8 empty] | 豐華DS.1530_MW | 豐華奇晶一線 MW | LINE161 | [5 empty] | 136 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1530 | 豐華～奇晶一線(1530) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | L3 | MVAR | 豐華奇晶一線 (1530)乏 | MVAR_-560_560(-2000_2000) |  | B2/D04_A1 | [8 empty] | 豐華DS.1530_MVAR | 豐華奇晶一線 MVAR | LINE161 | [5 empty] | 137 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1580 | 鹽行～王行、豐華線(1580) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D04TN16W/T2 |  | 0030 |  |  | 1-03-06 |  |  | L8 | ON/OFF | 山上鹽行豐華白線(1580)CB 52AS |  | aama | B2/D04_A1 | [8 empty] | 豐華DS.1580_CB | 1580(山上鹽行白線) CB | LINE161 | [5 empty] | 382 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 161 | 161kV | 1530 | 豐華～奇晶一線(1530) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | L3 | 87LA1 | 豐華奇晶一線(1530)RY 87LA1 |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1530_87A1 | 豐華奇晶一線(1530)#1 87RY | OTHER | [5 empty] | 361 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1530 | 豐華～奇晶一線(1530) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0010 |  |  | 1-01-02 |  |  | L3 | 87LA2 | 豐華奇晶一線(1530)RY 87LA2 |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1530_87A2 | 豐華奇晶一線(1530)#2 87RY | OTHER | [5 empty] | 362 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1530 | 豐華～奇晶一線(1530) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-03 |  |  | L3 | PHA | 豐華奇晶一線(1530)RY PHA |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1530_PHA | 豐華奇晶一線(1530) 相間RY | LINE161 | [5 empty] | 363 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1530 | 豐華～奇晶一線(1530) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0012 |  |  | 1-01-04 |  |  | L3 | GDA | 豐華奇晶一線(1530)RY GDA |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1530_GDA | 豐華奇晶一線(1530) 接地RY | LINE161 | [5 empty] | 364 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1530 | 豐華～奇晶一線(1530) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0774 |  |  | 1-30-06 |  |  | L3 | USE/LOCK | 豐華奇晶一線(1530)#1 87RY U/L 87UL1 |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1530_87UL1 | 豐華奇晶一線(1530)#1 87RY U/L | OTHER | [5 empty] | 575 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1530 | 豐華～奇晶一線(1530) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0775 |  |  | 1-30-07 |  |  | L3 | USE/LOCK | 豐華奇晶一線(1530)79RY U/L 79S |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1530_79UL | 豐華奇晶一線(1530) 79RY U/L | LINE161 | [5 empty] | 576 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1530 | 豐華～奇晶一線(1530) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0880 |  |  | 1-37-00 |  |  | L3 | 87CFA | 豐華奇晶一線 1530 87CFA(87RY通訊故障) |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1530_87CFA | 豐華奇晶一線(1530)87RY通訊故障 | OTHER | [5 empty] | 664 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1530 | 豐華～奇晶一線(1530) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0881 |  |  | 1-37-01 |  |  | L3 | RYFA | 豐華奇晶一線 1530 RYFA(數位電驛故障) |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1530_RYFA | 豐華奇晶一線(1530)數位電驛故障 | OTHER | [5 empty] | 665 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1530 | 豐華～奇晶一線(1530) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0916 |  |  | 1-39-04 |  |  | L3 | USE/LOCK | 豐華奇晶一線(1530)#2 87RY U/L 87UL2 |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1530_87UL2 | 豐華奇晶一線(1530)#2 87RY U/L | OTHER | [5 empty] | 697 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1530 | 豐華～奇晶一線(1530) |  | DS1 | 1531 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0960 | 961 |  | 1-3C-00 | 1-3C-01 |  | L3 | ON | 豐華奇晶一線 (1531) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1531_DS | 1531(豐華奇晶一線) DS | LINE161 | [5 empty] | 715 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1530 | 豐華～奇晶一線(1530) |  | DS2 | 1532 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0962 | 963 |  | 1-3C-02 | 1-3C-03 |  | L3 | ON | 豐華奇晶一線 (1532) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1532_DS | 1532(豐華奇晶一線) DS | LINE161 | [5 empty] | 716 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1530 | 豐華～奇晶一線(1530) |  | DS3 | 1533 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0964 | 965 |  | 1-3C-04 | 1-3C-05 |  | L3 | ON | 豐華奇晶一線 (1533) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1533_DS | 1533(豐華奇晶一線) DS | LINE161 | [5 empty] | 717 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1530 | 豐華～奇晶一線(1530) |  | ES3 | 1533E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0966 | 967 |  | 1-3C-06 | 1-3C-07 |  | L3 | ON | 豐華奇晶一線 (1533E) ES-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1533E_ES | 1533E(豐華奇晶一線) ES | LINE161 | [5 empty] | 718 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1540 | 豐華～奇晶四線(1540) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1540LE | 1540LE (非取樣點) | LINE161 | [5 empty] | 8 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1540 | 豐華～奇晶四線(1540) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1540BE | 1540BE (非取樣點) | LINE161 | [5 empty] | 9 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1540 | 豐華～奇晶四線(1540) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | L4 | MW | 豐華奇晶四線 (1540)瓦 | MW_-560_560(-2000_2000) |  | B2/D04_A1 | [8 empty] | 豐華DS.1540_MW | 豐華奇晶四線 MW | LINE161 | [5 empty] | 138 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1540 | 豐華～奇晶四線(1540) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | L4 | MVAR | 豐華奇晶四線 (1540)乏 | MVAR_-560_560(-2000_2000) |  | B2/D04_A1 | [8 empty] | 豐華DS.1540_MVAR | 豐華奇晶四線 MVAR | LINE161 | [5 empty] | 139 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 11 | 11kV | LBS210 | #1SC(210) |  | LBS |  | Element | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/210 | C/1SC(B) |  |  | 1060 | 1061 |  | 2-32-04 | 2-32-05 |  | #1SC | ON | #1SC 210 LBS LBS-AS |  |  | B3/D04_A1 | [8 empty] | 豐華DS.210_LBS | 210(11KV #1SC) LBS | SC | [5 empty] | 757 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1540 | 豐華～奇晶四線(1540) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-06 |  |  | L4 | 87LA1 | 豐華奇晶四線(1540)RY 87LA1 |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1540_87A1 | 豐華奇晶四線(1540) #1 87RY | OTHER | [5 empty] | 366 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1540 | 豐華～奇晶四線(1540) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0015 |  |  | 1-01-07 |  |  | L4 | 87LA2 | 豐華奇晶四線(1540)RY 87LA2 |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1540_87A2 | 豐華奇晶四線(1540) #2 87RY | OTHER | [5 empty] | 367 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1540 | 豐華～奇晶四線(1540) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-02-00 |  |  | L4 | PHA | 豐華奇晶四線(1540)RY PHA |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1540_PHA | 豐華奇晶四線(1540) 相間RY | LINE161 | [5 empty] | 368 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1540 | 豐華～奇晶四線(1540) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0017 |  |  | 1-02-01 |  |  | L4 | GDA | 豐華奇晶四線(1540)RY GDA |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1540_GDA | 豐華奇晶四線(1540) 接地RY | LINE161 | [5 empty] | 369 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1540 | 豐華～奇晶四線(1540) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0776 |  |  | 1-30-08 |  |  | L4 | USE/LOCK | 豐華奇晶四線(1540)#1 87RY U/L 87UL1 |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1540_87UL1 | 豐華奇晶四線(1540)#1 87RY U/L | OTHER | [5 empty] | 577 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1540 | 豐華～奇晶四線(1540) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0777 |  |  | 1-30-09 |  |  | L4 | USE/LOCK | 豐華奇晶四線(1540)79RY U/L 79S |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1540_79UL | 豐華奇晶四線(1540) 79RY U/L | LINE161 | [5 empty] | 578 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1540 | 豐華～奇晶四線(1540) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0882 |  |  | 1-37-02 |  |  | L4 | 87CFA | 豐華奇晶四線 1540 87CFA(87RY通訊故障) |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1540_87CFA | 豐華奇晶四線(1540)87RY通訊故障 | OTHER | [5 empty] | 666 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1540 | 豐華～奇晶四線(1540) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0883 |  |  | 1-37-03 |  |  | L4 | RYFA | 豐華奇晶四線 1540 RYFA(數位電驛故障) |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1540_RYFA | 豐華奇晶四線(1540)數位電驛故障 | OTHER | [5 empty] | 667 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1540 | 豐華～奇晶四線(1540) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0915 |  |  | 1-39-03 |  |  | L4 | USE/LOCK | 豐華奇晶四線(1540)#2 87RY U/L 87UL2 |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1540_87UL2 | 豐華奇晶四線(1540)#2 87RY U/L | OTHER | [5 empty] | 696 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1540 | 豐華～奇晶四線(1540) |  | DS1 | 1541 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0968 | 969 |  | 1-3C-08 | 1-3C-09 |  | L4 | ON | 豐華奇晶四線 (1541) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1541_DS | 1541(豐華奇晶四線) DS | LINE161 | [5 empty] | 719 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1540 | 豐華～奇晶四線(1540) |  | DS2 | 1542 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0970 | 971 |  | 1-3C-10 | 1-3C-11 |  | L4 | ON | 豐華奇晶四線 (1542) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1542_DS | 1542(豐華奇晶四線) DS | LINE161 | [5 empty] | 720 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1540 | 豐華～奇晶四線(1540) |  | DS3 | 1543 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0972 | 973 |  | 1-3C-12 | 1-3C-13 |  | L4 | ON | 豐華奇晶四線 (1543) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1543_DS | 1543(豐華奇晶四線) DS | LINE161 | [5 empty] | 721 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1540 | 豐華～奇晶四線(1540) |  | ES3 | 1543E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0974 | 975 |  | 1-3C-14 | 1-3C-15 |  | L4 | ON | 豐華奇晶四線 (1543E) ES-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1543E_ES | 1543E(豐華奇晶四線) ES | LINE161 | [5 empty] | 722 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華~聯電五一路(1610) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1610LE | 1610LE (非取樣點) | LINE161 | [5 empty] | 18 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華~聯電五一路(1610) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1610BE | 1610BE (非取樣點) | LINE161 | [5 empty] | 19 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華~聯電五一路(1610) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | Line9 | MW | 豐華聯電五一路 (1610)瓦 | MW_-560_560(-2000_2000) |  | B2/D04_A1 | [8 empty] | 豐華DS.1610_MW | 豐華聯電五一路 MW | LINE161 | [5 empty] | 148 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華~聯電五一路(1610) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | Line9 | MVAR | 豐華聯電五一路 (1610)乏 | MVAR_-560_560(-2000_2000) |  | B2/D04_A1 | [8 empty] | 豐華DS.1610_MVAR | 豐華聯電五一路 MVAR | LINE161 | [5 empty] | 149 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 11 | 11kV | LBS220 | #2SC(220) |  | LBS |  | Element | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/220 | C/2SC(B) |  |  | 1062 | 1063 |  | 2-32-06 | 2-32-07 |  | #2SC | ON | #2SC 220 LBS LBS-AS |  |  | B3/D04_A1 | [8 empty] | 豐華DS.220_LBS | 220(11KV #2SC) LBS | SC | [5 empty] | 758 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華~聯電五一路(1610) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0035 |  |  | 1-04-03 |  |  | Line9 | 87A1 | 豐華聯電五一路 (1610)RY 87A1 |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1610_87A1 | 豐華聯電五一路(1610) #1 87RY | LINE161 | [5 empty] | 387 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華~聯電五一路(1610) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0036 |  |  | 1-04-04 |  |  | Line9 | PHA | 豐華聯電五一路 (1610)RY PHA |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1610_PHA | 豐華聯電五一路(1610) 相間RY | LINE161 | [5 empty] | 388 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華~聯電五一路(1610) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0037 |  |  | 1-04-05 |  |  | Line9 | GDA | 豐華聯電五一路 (1610)RY GDA |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1610_GDA | 豐華聯電五一路(1610) 接地RY | LINE161 | [5 empty] | 389 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華~聯電五一路(1610) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0106 |  |  | 1-0D-02 |  |  | Line9 | 87A2 | 豐華聯電五一路 (1610)RY 87A2 |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1610_87A2 | 豐華聯電五一路(1610) #2 87RY | LINE161 | [5 empty] | 444 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華~聯電五一路(1610) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0786 |  |  | 1-31-02 |  |  | Line9 | USE/LOCK | 豐華聯電五一路 (1610)#1 87RY U/L 87T1 |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1610_87UL1 | 豐華聯電五一路(1610)#1 87RY UL | LINE161 | [5 empty] | 587 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華~聯電五一路(1610) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0787 |  |  | 1-31-03 |  |  | Line9 | USE/LOCK | 豐華聯電五一路 (1610)#2 87RY U/L 87T2 |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1610_87UL2 | 豐華聯電五一路(1610)#2 87RY UL | LINE161 | [5 empty] | 588 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華~聯電五一路(1610) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0788 |  |  | 1-31-04 |  |  | Line9 | USE/LOCK | 豐華聯電五一路 (1610) 79RY 79S |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1610_79UL | 豐華聯電五一路(1610) 79RY U/L | LINE161 | [5 empty] | 589 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華~聯電五一路(1610) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0892 |  |  | 1-37-12 |  |  | L9 |  | 豐華聯電五一路 (1610) 87CFA(87RY通訊故障) |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1610_87CFA | 豐華聯電五一路(1610)通訊故障 | OTHER | [5 empty] | 676 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華~聯電五一路(1610) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0893 |  |  | 1-37-13 |  |  | L9 |  | 豐華聯電五一路 (1610) RYFA(數位電驛故障) |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1610_RYFA | 豐華聯電五一路(1610)電驛故障 | OTHER | [5 empty] | 677 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華~聯電五一路(1610) |  | DS1 | 1611 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1008 | 1009 |  | 1-3F-00 | 1-3F-01 |  | L9 | ON | 豐華聯電五一路 (1611) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1611_DS | 1611(豐華聯電五一路) DS | LINE161 | [5 empty] | 739 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華~聯電五一路(1610) |  | DS2 | 1612 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1010 | 1011 |  | 1-3F-02 | 1-3F-03 |  | L9 | ON | 豐華聯電五一路 (1612) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1612_DS | 1612(豐華聯電五一路) DS | LINE161 | [5 empty] | 740 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華~聯電五一路(1610) |  | DS3 | 1613 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1012 | 1013 |  | 1-3F-04 | 1-3F-05 |  | L9 | ON | 豐華聯電五一路 (1613) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1613_DS | 1613(豐華聯電五一路) DS | LINE161 | [5 empty] | 741 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華~聯電五一路(1610) |  | ES3 | 1613E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1014 | 1015 |  | 1-3F-06 | 1-3F-07 |  | L9 | ON | 豐華聯電五一路 (1613E) ES-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1613E_ES | 1613E(豐華聯電五一路) ES | LINE161 | [5 empty] | 742 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華~聯電五二路(1620) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1620LE | 1620LE (非取樣點) | LINE161 | [5 empty] | 20 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華~聯電五二路(1620) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1620BE | 1620BE (非取樣點) | LINE161 | [5 empty] | 21 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華~聯電五二路(1620) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | Line10 | MW | 豐華聯電五二路 (1620)瓦 | MW_-560_560(-2000_2000) |  | B2/D04_A1 | [8 empty] | 豐華DS.1620_MW | 豐華聯電五二路 MW | LINE161 | [5 empty] | 150 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華~聯電五二路(1620) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | Line10 | MVAR | 豐華聯電五二路 (1620)乏 | MVAR_-560_560(-2000_2000) |  | B2/D04_A1 | [8 empty] | 豐華DS.1620_MVAR | 豐華聯電五二路 MVAR | LINE161 | [5 empty] | 151 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 11 | 11kV | LBS230 | #3SC(230) |  | LBS |  | Element | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/230 | C/3SC(B) |  |  | 1064 | 1065 |  | 2-32-08 | 2-32-09 |  | #3SC | ON | #3SC 230 LBS LBS-AS |  |  | B3/D04_A1 | [8 empty] | 豐華DS.230_LBS | 230(11KV #3SC) LBS | SC | [5 empty] | 759 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華~聯電五二路(1620) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0039 |  |  | 1-04-07 |  |  | Line10 | 87A1 | 豐華聯電五二路 (1620)RY 87A1 |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1620_87A1 | 豐華聯電五二路(1620) #1 87RY | LINE161 | [5 empty] | 391 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華~聯電五二路(1620) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0040 |  |  | 1-05-00 |  |  | Line10 | PHA | 豐華聯電五二路 (1620)RY PHA |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1620_PHA | 豐華聯電五二路(1620) 相間RY | LINE161 | [5 empty] | 392 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華~聯電五二路(1620) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0041 |  |  | 1-05-01 |  |  | Line10 | GDA | 豐華聯電五二路 (1620)RY GDA |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1620_GDA | 豐華聯電五二路(1620) 接地RY | LINE161 | [5 empty] | 393 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華~聯電五二路(1620) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0107 |  |  | 1-0D-03 |  |  | Line10 | 87A2 | 豐華聯電五二路 (1620)RY 87A2 |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1620_87A2 | 豐華聯電五二路(1620) #2 87RY | LINE161 | [5 empty] | 445 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華~聯電五二路(1620) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0789 |  |  | 1-31-05 |  |  | Line10 | USE/LOCK | 豐華聯電五二路 (1620)#1 87RY U/L 87T1 |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1620_87UL1 | 豐華聯電五二路(1620)#1 87RY UL | LINE161 | [5 empty] | 590 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華~聯電五二路(1620) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0790 |  |  | 1-31-06 |  |  | Line10 | USE/LOCK | 豐華聯電五二路 (1620)#2 87RY U/L 87T2 |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1620_87UL2 | 豐華聯電五二路(1620)#2 87RY UL | LINE161 | [5 empty] | 591 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華~聯電五二路(1620) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0791 |  |  | 1-31-07 |  |  | Line10 | USE/LOCK | 豐華聯電五二路 (1620) 79RY 79S |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1620_79UL | 豐華聯電五二路(1620) 79RY U/L | LINE161 | [5 empty] | 592 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華~聯電五二路(1620) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0894 |  |  | 1-37-14 |  |  | L10 |  | 豐華聯電五二路 (1620) 87CFA(87RY通訊故障) |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1620_87CFA | 豐華聯電五二路(1620)通訊故障 | OTHER | [5 empty] | 678 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華~聯電五二路(1620) |  | RYFA |  | Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0895 |  |  | 1-37-15 |  |  | L10 |  | 豐華聯電五二路 (1620) RYFA(數位電驛故障) |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1620_RYFA | 豐華聯電五二路(1620)電驛故障 | OTHER | [5 empty] | 679 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華~聯電五二路(1620) |  | DS1 | 1621 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1016 | 1017 |  | 1-3F-08 | 1-3F-09 |  | L10 | ON | 豐華聯電五二路 (1621) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1621_DS | 1621(豐華聯電五二路) DS | LINE161 | [5 empty] | 743 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華~聯電五二路(1620) |  | DS2 | 1622 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1018 | 1019 |  | 1-3F-10 | 1-3F-11 |  | L10 | ON | 豐華聯電五二路 (1622) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1622_DS | 1622(豐華聯電五二路) DS | LINE161 | [5 empty] | 744 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華~聯電五二路(1620) |  | DS3 | 1623 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1020 | 1021 |  | 1-3F-12 | 1-3F-13 |  | L10 | ON | 豐華聯電五二路 (1623) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1623_DS | 1623(豐華聯電五二路) DS | LINE161 | [5 empty] | 745 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華~聯電五二路(1620) |  | ES3 | 1623E | B3 | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1022 | 1023 |  | 1-3F-14 | 1-3F-15 |  | L10 | ON | 豐華聯電五二路 (1623E) ES-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1623E_ES | 1623E(豐華聯電五二路) ES | LINE161 | [5 empty] | 746 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1580 | 鹽行～王行、豐華線(1580) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1580LE | 1580LE (非取樣點) | LINE161 | [5 empty] | 16 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1580 | 鹽行～王行、豐華線(1580) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D04_A1 | [8 empty] | 豐華DS.1580BE | 1580BE (非取樣點) | LINE161 | [5 empty] | 17 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1580 | 鹽行～王行、豐華線(1580) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | L8 | MW | 山上鹽行豐華白線 (1580)瓦 | MW_-560_560(-2000_2000) |  | B2/D04_A1 | [8 empty] | 豐華DS.1580_MW | 山上鹽行白線 MW | LINE161 | [5 empty] | 146 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1580 | 鹽行～王行、豐華線(1580) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | L8 | MVAR | 山上鹽行豐華白線 (1580)乏 | MVAR_-560_560(-2000_2000) |  | B2/D04_A1 | [8 empty] | 豐華DS.1580_MVAR | 山上鹽行白線 MVAR | LINE161 | [5 empty] | 147 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 11 | 11kV | LBS240 | #4SC(240) |  | LBS |  | Element | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/240 | C/4SC(B) |  |  | 1066 | 1067 |  | 2-32-10 | 2-32-11 |  | #4SC | ON | #4SC 240 LBS LBS-AS |  |  | B3/D04_A1 | [8 empty] | 豐華DS.240_LBS | 240(11KV #4SC) LBS | SC | [5 empty] | 760 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1580 | 鹽行～王行、豐華線(1580) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0031 |  |  | 1-03-07 |  |  | L8 | 87A1 | 山上鹽行豐華白線(1580)RY 87A1 |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1580_87A1 | 山上鹽行白線(1580) #1 87RY | LINE161 | [5 empty] | 383 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1580 | 鹽行～王行、豐華線(1580) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0032 |  |  | 1-04-00 |  |  | L8 | PHA | 山上鹽行豐華白線(1580)RY PHA |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1580_PHA | 山上鹽行白線(1580) 相間RY | LINE161 | [5 empty] | 384 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1580 | 鹽行～王行、豐華線(1580) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0033 |  |  | 1-04-01 |  |  | L8 | GDA | 山上鹽行豐華白線(1580)RY GDA |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1580_GDA | 山上鹽行白線(1580) 接地RY | LINE161 | [5 empty] | 385 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1580 | 鹽行～王行、豐華線(1580) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0110 |  |  | 1-0D-06 |  |  | L8 | 87A2 | 山上鹽行豐華白線(1580)RY 87A2 |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1580_87A2 | 山上鹽行白線(1580) #2 87RY | LINE161 | [5 empty] | 448 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1580 | 鹽行～王行、豐華線(1580) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0784 |  |  | 1-31-00 |  |  | L8 | USE/LOCK | 山上鹽行豐華白線(1580)#1 87RY 87S |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1580_87UL1 | 山上鹽行白線(1580) #1 87RY U/L | LINE161 | [5 empty] | 585 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1580 | 鹽行～王行、豐華線(1580) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0785 |  |  | 1-31-01 |  |  | L8 | USE/LOCK | 山上鹽行豐華白線(1580)79RY 79S |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1580_79UL | 山上鹽行白線(1580) 79RY U/L | LINE161 | [5 empty] | 586 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1580 | 鹽行～王行、豐華線(1580) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0890 |  |  | 1-37-10 |  |  | L8 | A/N | 山上鹽行豐華白線 1580 87CFA(87RY通訊故障) |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1580_87CFA | 山上鹽行白線(1580)87RY通訊故障 | OTHER | [5 empty] | 674 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1580 | 鹽行～王行、豐華線(1580) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0891 |  |  | 1-37-11 |  |  | L8 | A/N | 山上鹽行豐華白線 1580 RYFA(電驛故障) |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1580_RYFA | 山上鹽行白線(1580)數位電驛故障 | OTHER | [5 empty] | 675 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1580 | 鹽行～王行、豐華線(1580) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0914 |  |  | 1-39-02 |  |  | L8 | USE/LOCK | 山上鹽行豐華白線(1580)#2 87RY 87S |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1580_87UL2 | 山上鹽行白線(1580) #2 87RY U/L | LINE161 | [5 empty] | 695 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1580 | 鹽行～王行、豐華線(1580) |  | DS1 | 1581 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1000 | 1001 |  | 1-3E-08 | 1-3E-09 |  | L8 | ON | 山上鹽行豐華白線 (1581) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1581_DS | 1581(山上鹽行白線) DS | LINE161 | [5 empty] | 735 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1580 | 鹽行～王行、豐華線(1580) |  | DS2 | 1582 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1002 | 1003 |  | 1-3E-10 | 1-3E-11 |  | L8 | ON | 山上鹽行豐華白線 (1582) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1582_DS | 1582(山上鹽行白線) DS | LINE161 | [5 empty] | 736 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1580 | 鹽行～王行、豐華線(1580) |  | DS3 | 1583 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1004 | 1005 |  | 1-3E-12 | 1-3E-13 |  | L8 | ON | 山上鹽行豐華白線 (1583) DS-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1583_DS | 1583(山上鹽行白線) DS | LINE161 | [5 empty] | 737 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1580 | 鹽行～王行、豐華線(1580) |  | ES3 | 1583E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1006 | 1007 |  | 1-3E-14 | 1-3E-15 |  | L8 | ON | 山上鹽行豐華白線 (1583E) ES-AS |  |  | B2/D04_A1 | [8 empty] | 豐華DS.1583E_ES | 1583E(山上鹽行白線) ES | LINE161 | [5 empty] | 738 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0054 |  |  | 1-06-06 |  |  | Locate Empty | A/N | 161KV 79 RY RCA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | [5 empty] | 402 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0055 |  |  | 1-06-07 |  |  | OSCA | A/N | 161KV示波器啟動警報OSCA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.161KV_OSCA_1 | 161KV示波器啟動警報(1) | OTHER | [5 empty] | 403 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0056 |  |  | 1-07-00 |  |  | Locate Empty | 備用 | 161KV NO.2 O.S.C. OSC1A |  |  | B3/D04_A1 | [8 empty] | 豐華DS.161KV_OSCA_2 | 161KV示波器啟動警報(2) | OTHER | [5 empty] | 404 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | ComPoint |  |  | 25PFA |  |  | Status | 同步校核電驛電源 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0396 |  |  | 2-11-04 |  |  | 25RY | A/N | 同步校核裝置電源 25TA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | [5 empty] | 567 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | ComPoint |  |  | 25TA |  |  | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0397 |  |  | 2-11-05 |  |  | 25RY | A/N | 同步校核裝置超時 25PFA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER | [5 empty] | 568 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | ComPoint |  |  | OPA |  |  | Status | 充油電纜低壓警報 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0853 |  |  | 1-35-05 |  |  | Locate Empty | A/N | 充油電纜警報 OPA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | [5 empty] | 638 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0855 |  |  | 1-35-07 |  |  | Locate Empty | A/N | 161KV CB 重故障 CBA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.161KV_CBA | 161KV斷路器重故障 | OTHER | [5 empty] | 640 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0856 |  |  | 1-35-08 |  |  | Locate Empty | A/N | 161KV CB 輕故障 CBF |  |  | B3/D04_A1 | [8 empty] | 豐華DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | [5 empty] | 641 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | ComPoint |  |  | COMT |  |  | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0863 |  |  | 1-35-15 |  |  | Locate Empty | A/N | 161KV CB空壓機超時運轉 COMT |  |  | B3/D04_A1 | [8 empty] | 豐華DS.161空壓機COMT | 161KV空壓機運轉超時警報 | OTHER | [5 empty] | 648 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | ComPoint |  |  | FDR_60A |  |  | Status | 11/22kV電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0866 |  |  | 1-36-02 |  |  | Locate Empty | A/N | 23KV SC 60-RY 警報 60A |  |  | B3/D04_A1 | [8 empty] | 豐華DS.11KV_SC_60A | 23/11KV SC 60A | OTHER | [5 empty] | 651 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0867 |  |  | 1-36-03 |  |  | Locate Empty | A/N | 23KV CB重故障 CBA |  |  | ELEM/D04_A1 | [8 empty] | 豐華DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | [5 empty] | 652 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0868 |  |  | 1-36-04 |  |  | Locate Empty | A/N | 23KV CB輕故障 CBF |  |  | ELEM/D04_A1 | [8 empty] | 豐華DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | [5 empty] | 653 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | ComPoint |  |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0869 |  |  | 1-36-05 |  |  | Locate Empty | A/N | 23KV FEEDER 79RY LOA |  |  | B3/D04_A1 | [8 empty] | 豐華DS.11/23KV_LOA | 11/23KV饋線復閉失敗閉鎖 | OTHER | [5 empty] | 654 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | ComPoint |  |  | OLTC_A |  |  | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0897 |  |  | 1-38-01 |  |  | OLTC | OLTCA | OLTC 15分鐘內連動3次警報 |  |  | B3/D04_A1 | [8 empty] | 豐華DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | [5 empty] | 680 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0907 |  |  | 1-38-11 |  |  | OSCF | A/N | 161KV示波器缺紙或故障警報OSCF |  |  | B3/D04_A1 | [8 empty] | 豐華DS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | [5 empty] | 688 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | ComPoint |  |  | BUS_RYFA |  |  | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0909 |  |  | 1-38-13 |  |  | 161kV#1,2Bus | RYFA | 161kV#1,#2Bus 數位電驛故障 |  |  | B3/D04_A1 | [8 empty] | 豐華DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | [5 empty] | 690 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | ComPoint |  |  | 87CTFA | 87RY CT迴路故障 | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0910 |  |  | 1-38-14 |  |  | 161kV#1,2Bus | CTFA | 161kV#1,#2Bus 差流電驛CT迴路故障警報 |  |  | B3/D04_A1 | [8 empty] | 豐華DS.161KV_BUS_CTFA | 161KV BUS CT回路故障 | OTHER | [5 empty] | 691 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | ComPoint |  |  | GRZ100 |  |  | Status | 電驛GRZ100閉鎖 | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0911 |  |  | 1-38-15 |  |  | BVS盤 | LOCK/USE | 本所各GRZ100 Ry U/L |  |  | B3/D04_A1 | [8 empty] | 豐華DS.BVS_RY | BVS GRZ100 RY U/L | OTHER | [5 empty] | 692 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | LOCK/USE | USE

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
D04 | 豐華DS | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/D04_A1 | [12 empty] | 豐華DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: D04/161/1BUS/V; OPRD2: D04/161/2BUS/V
D04 | 豐華DS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/D04_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: D04/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
D04 | 豐華DS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/D04_A1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_10 | OPRD1: D04/161/1510/MW; OPRD2: D04/161/1520/MW; OPRD3: D04/161/1530/MW; OPRD4: D04/161/1540/MW; OPRD5: D04/161/1550/MW; OPRD6: D04/161/1560/MW; OPRD7: D04/161/1570/MW; OPRD8: D04/161/1580/MW; OPRD9: D04/161/1610/MW; OPRD10: D04/161/1620/MW
D04 | 豐華DS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/D04_A1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: D04/0/CalcPoint/OPRN2_MW
D04 | 豐華DS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/D04_A1 | [17 empty] | none
D04 | 豐華DS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/D04_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: D04/0/CalcPoint/OPRN1; OPRD2: D04/0/CalcPoint/OPRN2; OPRD3: D04/0/CalcPoint/PRFL_UL
D04 | 豐華DS |  |  | 1DTR | 1DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D04_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D04/11/310/I_R; OPRD2: D04/11/320/I_R
D04 | 豐華DS |  |  | 1DTR | 1DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D04_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D04/11/310/I_S; OPRD2: D04/11/320/I_S
D04 | 豐華DS |  |  | 1DTR | 1DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D04_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D04/11/310/I_T; OPRD2: D04/11/320/I_T
D04 | 豐華DS |  |  | 2DTR | 2DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D04_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D04/11/330/I_R; OPRD2: D04/11/340/I_R
D04 | 豐華DS |  |  | 2DTR | 2DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D04_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D04/11/330/I_S; OPRD2: D04/11/340/I_S
D04 | 豐華DS |  |  | 2DTR | 2DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D04_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D04/11/330/I_T; OPRD2: D04/11/340/I_T
D04 | 豐華DS | 161 | 161kV | 1510 | 南科～豐華紅線(1510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D04_A1 | [12 empty] | 豐華DS.1510_AMP | 南科豐華紅線 AMP | LINE161 | AMP_CAL | C20R1790 | amp_cal | OPRD1: D04/161/1510/MW; OPRD2: D04/161/1510/MVAR; OPRD3: D04/0/CalcPoint/Vbs4
D04 | 豐華DS | 161 | 161kV | 1520 | 南科～豐華白線(1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D04_A1 | [12 empty] | 豐華DS.1520_AMP | 南科豐華白線 AMP | LINE161 | AMP_CAL | C20R1790 | amp_cal | OPRD1: D04/161/1520/MW; OPRD2: D04/161/1520/MVAR; OPRD3: D04/0/CalcPoint/Vbs4
D04 | 豐華DS | 161 | 161kV | 1530 | 豐華～奇晶一線(1530) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D04_A1 | [12 empty] | 豐華DS.1530_AMP | 豐華奇晶一線 AMP | LINE161 | AMP_CAL | C20R0964 | amp_cal | OPRD1: D04/161/1530/MW; OPRD2: D04/161/1530/MVAR; OPRD3: D04/0/CalcPoint/Vbs4
D04 | 豐華DS | 161 | 161kV | 1540 | 豐華～奇晶四線(1540) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D04_A1 | [12 empty] | 豐華DS.1540_AMP | 豐華奇晶四線 AMP | LINE161 | AMP_CAL | C20R0964 | amp_cal | OPRD1: D04/161/1540/MW; OPRD2: D04/161/1540/MVAR; OPRD3: D04/0/CalcPoint/Vbs4
D04 | 豐華DS | 161 | 161kV | 1550 | 三竹～豐華一路(1550) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D04_A1 | [12 empty] | 豐華DS.1550_AMP | 三竹豐華一路 AMP | LINE161 | AMP_CAL | C20R1790 | amp_cal | OPRD1: D04/161/1550/MW; OPRD2: D04/161/1550/MVAR; OPRD3: D04/0/CalcPoint/Vbs4
D04 | 豐華DS | 161 | 161kV | 1560 | 三竹～豐華二路(1560) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D04_A1 | [12 empty] | 豐華DS.1560_AMP | 三竹豐華二路 AMP | LINE161 | AMP_CAL | C20R1790 | amp_cal | OPRD1: D04/161/1560/MW; OPRD2: D04/161/1560/MVAR; OPRD3: D04/0/CalcPoint/Vbs4
D04 | 豐華DS | 161 | 161kV | 1570 | 山上～安南、豐華紅線(1570) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D04_A1 | [12 empty] | 豐華DS.1570_AMP | 山上安南紅線 AMP | LINE161 | AMP_CAL | C20R1790 | amp_cal | OPRD1: D04/161/1570/MW; OPRD2: D04/161/1570/MVAR; OPRD3: D04/0/CalcPoint/Vbs4
D04 | 豐華DS | 161 | 161kV | 1580 | 山上～鹽行、豐華白線(1580) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D04_A1 | [12 empty] | 豐華DS.1580_AMP | 山上鹽行白線 AMP | LINE161 | AMP_CAL | C20R1790 | amp_cal | OPRD1: D04/161/1580/MW; OPRD2: D04/161/1580/MVAR; OPRD3: D04/0/CalcPoint/Vbs4
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華~聯電五一路(1610) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D04_A1 | [12 empty] | 豐華DS.1610_AMP | 豐華聯電五一路 AMP | LINE161 | AMP_CAL | C20R1228 | amp_cal | OPRD1: D04/161/1610/MW; OPRD2: D04/161/1610/MVAR; OPRD3: D04/0/CalcPoint/Vbs4
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華~聯電五二路(1620) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D04_A1 | [12 empty] | 豐華DS.1620_AMP | 豐華聯電五二路 AMP | LINE161 | AMP_CAL | C20R1228 | amp_cal | OPRD1: D04/161/1620/MW; OPRD2: D04/161/1620/MVAR; OPRD3: D04/0/CalcPoint/Vbs4
D04 | 豐華DS | 11 | 11kV | 1ABUS | #1ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D04_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D04/11/1ABUS/V
D04 | 豐華DS | 11 | 11kV | 1BBUS | #1BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D04_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D04/11/1BBUS/V
D04 | 豐華DS | 11 | 11kV | 2ABUS | #2ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D04_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D04/11/2ABUS/V
D04 | 豐華DS | 11 | 11kV | 2BBUS | #2BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D04_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D04/11/2BBUS/V
D04 | 豐華DS | 11 | 11kV | 3BUS | #3BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D04_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D04/11/3BUS/V
D04 | 豐華DS |  |  | 1DTR(A) | #1DTR(A) |  | TR_PERM | [9 empty] | B1/D04_A1 | [12 empty] | 豐華DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D04//1DTR(A)/SupLocal; OPRD2: D04//1DTR(A)/Tap Chan
D04 | 豐華DS |  |  | 1DTR(B) | #1DTR(B) |  | TR_PERM | [9 empty] | B1/D04_A1 | [12 empty] | 豐華DS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D04//1DTR(B)/SupLocal; OPRD2: D04//1DTR(B)/Tap Chan
D04 | 豐華DS |  |  | 2DTR(A) | #2DTR(A) |  | TR_PERM | [9 empty] | B1/D04_A1 | [12 empty] | 豐華DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D04//2DTR(A)/SupLocal; OPRD2: D04//2DTR(A)/Tap Chan
D04 | 豐華DS |  |  | 2DTR(B) | #2DTR(B) |  | TR_PERM | [9 empty] | B1/D04_A1 | [12 empty] | 豐華DS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D04//2DTR(B)/SupLocal; OPRD2: D04//2DTR(B)/Tap Chan
D04 | 豐華DS |  |  | 3DTR | #3DTR |  | TR_PERM | [9 empty] | B1/D04_A1 | [12 empty] | 豐華DS.#3DTR_PERM | #3DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D04//3DTR/SupLocal; OPRD2: D04//3DTR/Tap Chan
D04 | 豐華DS | 11 | 11kV | K811 | 豐11線 (K811) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D04/11/1ABUS/V; OPRD2: D04/11/K811/I_R; OPRD3: D04/11/K811/I_S; OPRD4: D04/11/K811/I_T
D04 | 豐華DS | 11 | 11kV | K812 | 豐12線 (K812) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D04/11/1ABUS/V; OPRD2: D04/11/K812/I_R; OPRD3: D04/11/K812/I_S; OPRD4: D04/11/K812/I_T
D04 | 豐華DS | 11 | 11kV | K813 | 豐13線 (K813) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D04/11/1ABUS/V; OPRD2: D04/11/K813/I_R; OPRD3: D04/11/K813/I_S; OPRD4: D04/11/K813/I_T
D04 | 豐華DS | 11 | 11kV | K814 | 豐14線 (K814) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D04/11/1ABUS/V; OPRD2: D04/11/K814/I_R; OPRD3: D04/11/K814/I_S; OPRD4: D04/11/K814/I_T
D04 | 豐華DS | 11 | 11kV | K815 | 豐15線 (K815) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D04/11/1ABUS/V; OPRD2: D04/11/K815/I_R; OPRD3: D04/11/K815/I_S; OPRD4: D04/11/K815/I_T
D04 | 豐華DS | 11 | 11kV | K821 | 豐21線 (K821) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D04/11/1BBUS/V; OPRD2: D04/11/K821/I_R; OPRD3: D04/11/K821/I_S; OPRD4: D04/11/K821/I_T
D04 | 豐華DS | 11 | 11kV | K822 | 豐22線 (K822) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D04/11/1BBUS/V; OPRD2: D04/11/K822/I_R; OPRD3: D04/11/K822/I_S; OPRD4: D04/11/K822/I_T
D04 | 豐華DS | 11 | 11kV | K823 | 豐23線 (K823) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D04/11/1BBUS/V; OPRD2: D04/11/K823/I_R; OPRD3: D04/11/K823/I_S; OPRD4: D04/11/K823/I_T
D04 | 豐華DS | 11 | 11kV | K824 | 豐24線 (K824) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D04/11/1BBUS/V; OPRD2: D04/11/K824/I_R; OPRD3: D04/11/K824/I_S; OPRD4: D04/11/K824/I_T
D04 | 豐華DS | 11 | 11kV | K825 | 豐25線 (K825) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D04/11/1BBUS/V; OPRD2: D04/11/K825/I_R; OPRD3: D04/11/K825/I_S; OPRD4: D04/11/K825/I_T
D04 | 豐華DS | 11 | 11kV | K831 | 豐31線(K831) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D04/11/2ABUS/V; OPRD2: D04/11/K831/I_R; OPRD3: D04/11/K831/I_S; OPRD4: D04/11/K831/I_T
D04 | 豐華DS | 11 | 11kV | K832 | 豐32線(K832) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D04/11/2ABUS/V; OPRD2: D04/11/K832/I_R; OPRD3: D04/11/K832/I_S; OPRD4: D04/11/K832/I_T
D04 | 豐華DS | 11 | 11kV | K833 | 豐33線(K833) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D04/11/2ABUS/V; OPRD2: D04/11/K833/I_R; OPRD3: D04/11/K833/I_S; OPRD4: D04/11/K833/I_T
D04 | 豐華DS | 11 | 11kV | K834 | 豐34線(K834) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D04/11/2ABUS/V; OPRD2: D04/11/K834/I_R; OPRD3: D04/11/K834/I_S; OPRD4: D04/11/K834/I_T
D04 | 豐華DS | 11 | 11kV | K835 | 豐35線(K835) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D04/11/2ABUS/V; OPRD2: D04/11/K835/I_R; OPRD3: D04/11/K835/I_S; OPRD4: D04/11/K835/I_T
D04 | 豐華DS | 11 | 11kV | K841 | 豐41線(K841) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D04/11/2BBUS/V; OPRD2: D04/11/K841/I_R; OPRD3: D04/11/K841/I_S; OPRD4: D04/11/K841/I_T
D04 | 豐華DS | 11 | 11kV | K842 | 豐42線(K842) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D04/11/2BBUS/V; OPRD2: D04/11/K842/I_R; OPRD3: D04/11/K842/I_S; OPRD4: D04/11/K842/I_T
D04 | 豐華DS | 11 | 11kV | K843 | 豐43線(K843) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D04/11/2BBUS/V; OPRD2: D04/11/K843/I_R; OPRD3: D04/11/K843/I_S; OPRD4: D04/11/K843/I_T
D04 | 豐華DS | 11 | 11kV | K844 | 豐44線(K844) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D04/11/2BBUS/V; OPRD2: D04/11/K844/I_R; OPRD3: D04/11/K844/I_S; OPRD4: D04/11/K844/I_T
D04 | 豐華DS | 11 | 11kV | K845 | 豐45線(K845) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D04/11/2BBUS/V; OPRD2: D04/11/K845/I_R; OPRD3: D04/11/K845/I_S; OPRD4: D04/11/K845/I_T
D04 | 豐華DS | 22 | 22kV | K861 | 豐61線(K861) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D04/22/K861/I_R; OPRD3: D04/22/K861/I_S; OPRD4: D04/22/K861/I_T
D04 | 豐華DS | 22 | 22kV | K862 | 豐62線(K862) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D04/22/K862/I_R; OPRD3: D04/22/K862/I_S; OPRD4: D04/22/K862/I_T
D04 | 豐華DS | 22 | 22kV | K863 | 豐63線(K863) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D04/22/K863/I_R; OPRD3: D04/22/K863/I_S; OPRD4: D04/22/K863/I_T
D04 | 豐華DS | 22 | 22kV | K864 | 豐64線(K864) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D04/22/K864/I_R; OPRD3: D04/22/K864/I_S; OPRD4: D04/22/K864/I_T
D04 | 豐華DS | 22 | 22kV | K865 | 豐65線(K865) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D04/22/K865/I_R; OPRD3: D04/22/K865/I_S; OPRD4: D04/22/K865/I_T
D04 | 豐華DS | 22 | 22kV | K866 | 豐66線(K866) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D04/22/K866/I_R; OPRD3: D04/22/K866/I_S; OPRD4: D04/22/K866/I_T
D04 | 豐華DS | 22 | 22kV | K867 | 豐67線(K867) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D04/22/K867/I_R; OPRD3: D04/22/K867/I_S; OPRD4: D04/22/K867/I_T
D04 | 豐華DS | 22 | 22kV | K868 | 豐68線(K868) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D04/22/K868/I_R; OPRD3: D04/22/K868/I_S; OPRD4: D04/22/K868/I_T
D04 | 豐華DS | 11 | 11kV | K811 | 豐11線 (K811) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D04/11/K811/kVA; OPRD2: D04/11/K811/KVAR
D04 | 豐華DS | 11 | 11kV | K812 | 豐12線 (K812) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D04/11/K812/kVA; OPRD2: D04/11/K812/KVAR
D04 | 豐華DS | 11 | 11kV | K813 | 豐13線 (K813) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D04/11/K813/kVA; OPRD2: D04/11/K813/KVAR
D04 | 豐華DS | 11 | 11kV | K814 | 豐14線 (K814) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D04/11/K814/kVA; OPRD2: D04/11/K814/KVAR
D04 | 豐華DS | 11 | 11kV | K815 | 豐15線 (K815) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D04/11/K815/kVA; OPRD2: D04/11/K815/KVAR
D04 | 豐華DS | 11 | 11kV | K821 | 豐21線 (K821) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D04/11/K821/kVA; OPRD2: D04/11/K821/KVAR
D04 | 豐華DS | 11 | 11kV | K822 | 豐22線 (K822) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D04/11/K822/kVA; OPRD2: D04/11/K822/KVAR
D04 | 豐華DS | 11 | 11kV | K823 | 豐23線 (K823) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D04/11/K823/kVA; OPRD2: D04/11/K823/KVAR
D04 | 豐華DS | 11 | 11kV | K824 | 豐24線 (K824) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D04/11/K824/kVA; OPRD2: D04/11/K824/KVAR
D04 | 豐華DS | 11 | 11kV | K825 | 豐25線 (K825) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D04/11/K825/kVA; OPRD2: D04/11/K825/KVAR
D04 | 豐華DS | 11 | 11kV | K831 | 豐31線(K831) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D04/11/K831/kVA; OPRD2: D04/11/K831/KVAR
D04 | 豐華DS | 11 | 11kV | K832 | 豐32線(K832) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D04/11/K832/kVA; OPRD2: D04/11/K832/KVAR
D04 | 豐華DS | 11 | 11kV | K833 | 豐33線(K833) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D04/11/K833/kVA; OPRD2: D04/11/K833/KVAR
D04 | 豐華DS | 11 | 11kV | K834 | 豐34線(K834) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D04/11/K834/kVA; OPRD2: D04/11/K834/KVAR
D04 | 豐華DS | 11 | 11kV | K835 | 豐35線(K835) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D04/11/K835/kVA; OPRD2: D04/11/K835/KVAR
D04 | 豐華DS | 11 | 11kV | K841 | 豐41線(K841) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D04/11/K841/kVA; OPRD2: D04/11/K841/KVAR
D04 | 豐華DS | 11 | 11kV | K842 | 豐42線(K842) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D04/11/K842/kVA; OPRD2: D04/11/K842/KVAR
D04 | 豐華DS | 11 | 11kV | K843 | 豐43線(K843) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D04/11/K843/kVA; OPRD2: D04/11/K843/KVAR
D04 | 豐華DS | 11 | 11kV | K844 | 豐44線(K844) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D04/11/K844/kVA; OPRD2: D04/11/K844/KVAR
D04 | 豐華DS | 11 | 11kV | K845 | 豐45線(K845) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D04/11/K845/kVA; OPRD2: D04/11/K845/KVAR
D04 | 豐華DS | 22 | 22kV | K861 | 豐61線(K861) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D04/22/K861/kVA; OPRD2: D04/22/K861/KVAR
D04 | 豐華DS | 22 | 22kV | K862 | 豐62線(K862) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D04/22/K862/kVA; OPRD2: D04/22/K862/KVAR
D04 | 豐華DS | 22 | 22kV | K863 | 豐63線(K863) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D04/22/K863/kVA; OPRD2: D04/22/K863/KVAR
D04 | 豐華DS | 22 | 22kV | K864 | 豐64線(K864) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D04/22/K864/kVA; OPRD2: D04/22/K864/KVAR
D04 | 豐華DS | 22 | 22kV | K865 | 豐65線(K865) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D04/22/K865/kVA; OPRD2: D04/22/K865/KVAR
D04 | 豐華DS | 22 | 22kV | K866 | 豐66線(K866) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D04/22/K866/kVA; OPRD2: D04/22/K866/KVAR
D04 | 豐華DS | 22 | 22kV | K867 | 豐67線(K867) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D04/22/K867/kVA; OPRD2: D04/22/K867/KVAR
D04 | 豐華DS | 22 | 22kV | K868 | 豐68線(K868) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D04_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D04/22/K868/kVA; OPRD2: D04/22/K868/KVAR
D04 | 豐華DS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D04_A1 | [12 empty] | 豐華DS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D04/11/210/CB; OPRD2: 6.9; OPRD3: 0
D04 | 豐華DS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D04_A1 | [12 empty] | 豐華DS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D04/11/220/CB; OPRD2: 6.9; OPRD3: 0
D04 | 豐華DS | 11 | 11kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D04_A1 | [12 empty] | 豐華DS.230_SC_MVAR | 11KV#3SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D04/11/230/CB; OPRD2: 6.9; OPRD3: 0
D04 | 豐華DS | 11 | 11kV | 240 | #4SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D04_A1 | [12 empty] | 豐華DS.240_SC_MVAR | 11KV#4SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D04/11/240/CB; OPRD2: 6.9; OPRD3: 0
D04 | 豐華DS | 22 | 22kV | 250 | #5SC(250) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D04_A1 | [12 empty] | 豐華DS.250_SC_MVAR | 23KV#5SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D04/22/250/CB; OPRD2: 13.8; OPRD3: 0
D04 | 豐華DS | 22 | 22kV | 260 | #6SC(260) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D04_A1 | [12 empty] | 豐華DS.260_SC_MVAR | 23KV#6SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D04/22/260/CB; OPRD2: 13.8; OPRD3: 0
D04 | 豐華DS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/D04_A1 | [12 empty] | 豐華DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_14 |  | com_alarm_42 | D04//1DTR/GDA | D04//1DTR/PHA | D04//1DTR/96D | D04//1DTR/TRA | D04//1DTR/63Q | D04//1DTR/96B2 | D04//1DTR/96B1 | D04//1DTR/87A | D04//1DTR/51ZA | D04//1DTR/96PA | D04//2DTR/63Q | D04//2DTR/GDA | D04//2DTR/96D | D04//2DTR/96B1 | D04//2DTR/96B2 | D04//2DTR/87A | D04//2DTR/TRA | D04//2DTR/96PA | D04//2DTR/PHA | D04//2DTR/51ZA | D04//3DTR/63Q | D04//3DTR/TRA | D04//3DTR/96D | D04//3DTR/96B1 | D04//3DTR/96B2 | D04//3DTR/51ZA | D04//3DTR/96PA | D04//3DTR/87A | D04//3DTR/PHA | D04//3DTR/GDA | D04/11/310/PHA | D04/11/310/GDA | D04/11/320/GDA | D04/11/320/PHA | D04/11/330/PHA | D04/11/330/GDA | D04/11/340/GDA | D04/11/340/PHA | D04/161/1BUS/87A | D04/161/2BUS/87A | D04/22/350/GDA | D04/22/350/PHA
D04 | 豐華DS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/D04_A1 | [12 empty] | 豐華DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | STATION_FAULT_3 |  | com_alarm_3 | OPRD1: D04//1DTR/TRF; OPRD2: D04//2DTR/TRF; OPRD3: D04//3DTR/TRF
D04 | 豐華DS | 161 | 161kV | 1750_D1 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D04_D1 | [17 empty] | lamp2CC | OPRD1: D04/161/1750/CB
D04 | 豐華DS | 11 | 11kV | 310_D1 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D04_D1 | [17 empty] | lamp2CC | OPRD1: D04/11/310/CB
D04 | 豐華DS | 11 | 11kV | 320_D1 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D04_D1 | [17 empty] | lamp2CC | OPRD1: D04/11/320/CB
D04 | 豐華DS | 161 | 161kV | 1760_D1 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D04_D1 | [17 empty] | lamp2CC | OPRD1: D04/161/1760/CB
D04 | 豐華DS | 11 | 11kV | 330_D1 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D04_D1 | [17 empty] | lamp2CC | OPRD1: D04/11/330/CB
D04 | 豐華DS | 11 | 11kV | 340_D1 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D04_D1 | [17 empty] | lamp2CC | OPRD1: D04/11/340/CB
D04 | 豐華DS | 161 | 161kV | 1770_D1 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D04_D1 | [17 empty] | lamp2CC | OPRD1: D04/161/1770/CB
D04 | 豐華DS | 22 | 22kV | 350_D1 | #3DTR(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D04_D1 | [17 empty] | lamp2CC | OPRD1: D04/22/350/CB
D04 | 豐華DS | 161 | 161kV | 1780_D1 | #4DTR(1780) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D04_D1 | [17 empty] | lamp2CC | OPRD1: D04/161/1780/CB
D04 | 豐華DS | 0 |  | RTU_D1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/D04_D1 | [17 empty] | lamp2CC | OPRD1: D04/0/RTU/RTU_R_L
D04 | 豐華DS | 0 |  | StaDev_D1 | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/D04_D1 | [17 empty] | lamp2CC | OPRD1: D04/0/StaDev/STUV
D04 | 豐華DS | 0 |  | StaDev_D1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D04_D1 | [17 empty] | lamp2CC | OPRD1: D04/0/StaDev/DCA
D04 | 豐華DS | 0 |  | StaDev_D1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D04_D1 | [17 empty] | lamp2CC | OPRD1: D04/0/StaDev/DCE
D04 | 豐華DS | 22 | 22kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D04_D1 | [17 empty] | lamp2CC | OPRD1: D04/22/ComPoint/CBA
D04 | 豐華DS | 22 | 22kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | ELEM/D04_D1 | [17 empty] | lamp2CC | OPRD1: D04/22/ComPoint/CBF
D04 | 豐華DS | 0 |  | StaDev_D1 | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D04_D1 | [17 empty] | lamp2CC | OPRD1: D04/0/StaDev/PMA

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D04 | 豐華DS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 豐華DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | D04/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
D04 | 豐華DS | 161 | 161kV | 1510 | 南科豐華紅線(1510) |  | I | [25 empty] | ADCS_S | [8 empty] | 豐華DS.1510_AMP | 南科豐華紅線 AMP | LINE161 | D04/161/1510/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D04 | 豐華DS | 161 | 161kV | 1520 | 南科豐華白線(1520) |  | I | [25 empty] | ADCS_S | [8 empty] | 豐華DS.1520_AMP | 南科豐華白線 AMP | LINE161 | D04/161/1520/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D04 | 豐華DS | 161 | 161kV | 1530 | 豐華奇晶一線(1530) |  | I | [25 empty] | ADCS_S | [8 empty] | 豐華DS.1530_AMP | 豐華奇晶一線 AMP | LINE161 | D04/161/1530/I |  | AMP_CAL |  |  | 5 | CalcAIPoint | [21 empty] | C20R0964 | 867.599976 | 867.599976 | 964.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D04 | 豐華DS | 161 | 161kV | 1540 | 豐華奇晶四線(1540) |  | I | [25 empty] | ADCS_S | [8 empty] | 豐華DS.1540_AMP | 豐華奇晶四線 AMP | LINE161 | D04/161/1540/I |  | AMP_CAL |  |  | 6 | CalcAIPoint | [21 empty] | C20R0964 | 867.599976 | 867.599976 | 964.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D04 | 豐華DS | 161 | 161kV | 1550 | 三竹豐華一路(1550) |  | I | [25 empty] | ADCS_S | [8 empty] | 豐華DS.1550_AMP | 三竹豐華一路 AMP | LINE161 | D04/161/1550/I |  | AMP_CAL |  |  | 7 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D04 | 豐華DS | 161 | 161kV | 1560 | 三竹豐華二路(1560) |  | I | [25 empty] | ADCS_S | [8 empty] | 豐華DS.1560_AMP | 三竹豐華二路 AMP | LINE161 | D04/161/1560/I |  | AMP_CAL |  |  | 8 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D04 | 豐華DS | 161 | 161kV | 1570 | 山上安南紅線(1570) |  | I | [25 empty] | ADCS_S | [8 empty] | 豐華DS.1570_AMP | 山上安南紅線 AMP | LINE161 | D04/161/1570/I |  | AMP_CAL |  |  | 9 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D04 | 豐華DS | 161 | 161kV | 1580 | 山上鹽行白線(1580) |  | I | [25 empty] | ADCS_S | [8 empty] | 豐華DS.1580_AMP | 山上鹽行白線 AMP | LINE161 | D04/161/1580/I |  | AMP_CAL |  |  | 10 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐11線KVA | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐11線KVA | 11KV豐11線KVA | FEEDER |  |  | KVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐11線KW | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐11線KW | 11KV豐11線KW | FEEDER |  |  | KW_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐12線KVA | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐12線KVA | 11KV豐12線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐12線KW | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐12線KW | 11KV豐12線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐13線KVA | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐13線KVA | 11KV豐13線KVA | FEEDER |  |  | KVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐13線KW | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐13線KW | 11KV豐13線KW | FEEDER |  |  | KW_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐14線KVA | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐14線KVA | 11KV豐14線KVA | FEEDER |  |  | KVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐14線KW | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐14線KW | 11KV豐14線KW | FEEDER |  |  | KW_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐15線KVA | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐15線KVA | 11KV豐15線KVA | FEEDER |  |  | KVA_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐15線KW | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐15線KW | 11KV豐15線KW | FEEDER |  |  | KW_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐21線KVA | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐21線KVA | 11KV豐21線KVA | FEEDER |  |  | KVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐21線KW | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐21線KW | 11KV豐21線KW | FEEDER |  |  | KW_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐22線KVA | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐22線KVA | 11KV豐22線KVA | FEEDER |  |  | KVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐22線KW | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐22線KW | 11KV豐22線KW | FEEDER |  |  | KW_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐23線KVA | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐23線KVA | 11KV豐23線KVA | FEEDER |  |  | KVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐23線KW | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐23線KW | 11KV豐23線KW | FEEDER |  |  | KW_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐24線KVA | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐24線KVA | 11KV豐24線KVA | FEEDER |  |  | KVA_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐24線KW | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐24線KW | 11KV豐24線KW | FEEDER |  |  | KW_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐25線KVA | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐25線KVA | 11KV豐25線KVA | FEEDER |  |  | KVA_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐25線KW | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐25線KW | 11KV豐25線KW | FEEDER |  |  | KW_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐31線KVA | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐31線KVA | 11KV豐31線KVA | FEEDER |  |  | KVA_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐31線KW | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐31線KW | 11KV豐31線KW | FEEDER |  |  | KW_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐32線KVA | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐32線KVA | 11KV豐32線KVA | FEEDER |  |  | KVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐32線KW | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐32線KW | 11KV豐32線KW | FEEDER |  |  | KW_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐33線KVA | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐33線KVA | 11KV豐33線KVA | FEEDER |  |  | KVA_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐33線KW | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐33線KW | 11KV豐33線KW | FEEDER |  |  | KW_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐34線KVA | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐34線KVA | 11KV豐34線KVA | FEEDER |  |  | KVA_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐34線KW | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐34線KW | 11KV豐34線KW | FEEDER |  |  | KW_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐35線KVA | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐35線KVA | 11KV豐35線KVA | FEEDER |  |  | KVA_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐35線KW | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐35線KW | 11KV豐35線KW | FEEDER |  |  | KW_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐41線KVA | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐41線KVA | 11KV豐41線KVA | FEEDER |  |  | KVA_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐41線KW | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐41線KW | 11KV豐41線KW | FEEDER |  |  | KW_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐42線KVA | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐42線KVA | 11KV豐42線KVA | FEEDER |  |  | KVA_CAL |  |  | 43 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐42線KW | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐42線KW | 11KV豐42線KW | FEEDER |  |  | KW_CAL |  |  | 44 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐43線KVA | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐43線KVA | 11KV豐43線KVA | FEEDER |  |  | KVA_CAL |  |  | 45 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐43線KW | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐43線KW | 11KV豐43線KW | FEEDER |  |  | KW_CAL |  |  | 46 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐44線KVA | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐44線KVA | 11KV豐44線KVA | FEEDER |  |  | KVA_CAL |  |  | 47 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐44線KW | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐44線KW | 11KV豐44線KW | FEEDER |  |  | KW_CAL |  |  | 48 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐45線KVA | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐45線KVA | 11KV豐45線KVA | FEEDER |  |  | KVA_CAL |  |  | 49 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐45線KW | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐45線KW | 11KV豐45線KW | FEEDER |  |  | KW_CAL |  |  | 50 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐61線KVA | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐61線KVA | 23KV豐61線KVA | FEEDER |  |  | KVA_CAL |  |  | 51 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐61線KW | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐61線KW | 23KV豐61線KW | FEEDER |  |  | KW_CAL |  |  | 52 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐62線KVA | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐62線KVA | 23KV豐62線KVA | FEEDER |  |  | KVA_CAL |  |  | 53 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐62線KW | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐62線KW | 23KV豐62線KW | FEEDER |  |  | KW_CAL |  |  | 54 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐63線KVA | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐63線KVA | 23KV豐63線KVA | FEEDER |  |  | KVA_CAL |  |  | 55 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐63線KW | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐63線KW | 23KV豐63線KW | FEEDER |  |  | KW_CAL |  |  | 56 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐64線KVA | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐64線KVA | 23KV豐64線KVA | FEEDER |  |  | KVA_CAL |  |  | 57 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐64線KW | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐64線KW | 23KV豐64線KW | FEEDER |  |  | KW_CAL |  |  | 58 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐65線KVA | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐65線KVA | 23KV豐65線KVA | FEEDER |  |  | KVA_CAL |  |  | 59 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐65線KW | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐65線KW | 23KV豐65線KW | FEEDER |  |  | KW_CAL |  |  | 60 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐66線KVA | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐66線KVA | 23KV豐66線KVA | FEEDER |  |  | KVA_CAL |  |  | 61 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐66線KW | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐66線KW | 23KV豐66線KW | FEEDER |  |  | KW_CAL |  |  | 62 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐67線KVA | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐67線KVA | 23KV豐67線KVA | FEEDER |  |  | KVA_CAL |  |  | 63 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐67線KW | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐67線KW | 23KV豐67線KW | FEEDER |  |  | KW_CAL |  |  | 64 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐68線KVA | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐68線KVA | 23KV豐68線KVA | FEEDER |  |  | KVA_CAL |  |  | 65 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  |  |  |  | 豐68線KW | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.豐68線KW | 23KV豐68線KW | FEEDER |  |  | KW_CAL |  |  | 66 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 豐華DS.#1DTR(A)_MVA | #1DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 67 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D04 | 豐華DS | 0 |  | 1DTR(A) | #1DTR(A) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 豐華DS.#1DTR(A)_LOAD | #1DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 68 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D04 | 豐華DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PF | [25 empty] | ADCS_S | [8 empty] | 豐華DS.#1DTR(A)_PF | #1DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 69 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D04 | 豐華DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 豐華DS.#1DTR(B)_MVA | #1DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 70 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D04 | 豐華DS | 0 |  | 1DTR(B) | #1DTR(B) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 豐華DS.#1DTR(B)_LOAD | #1DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 71 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D04 | 豐華DS | 0 |  | 1DTR(B) | #1DTR(B) |  | PF | [25 empty] | ADCS_S | [8 empty] | 豐華DS.#1DTR(B)_PF | #1DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 72 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D04 | 豐華DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 豐華DS.#2DTR(A)_MVA | #2DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 73 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D04 | 豐華DS | 0 |  | 2DTR(A) | #2DTR(A) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 豐華DS.#2DTR(A)_LOAD | #2DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 74 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D04 | 豐華DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PF | [25 empty] | ADCS_S | [8 empty] | 豐華DS.#2DTR(A)_PF | #2DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 75 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D04 | 豐華DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 豐華DS.#2DTR(B)_MVA | #2DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 76 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D04 | 豐華DS | 0 |  | 2DTR(B) | #2DTR(B) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 豐華DS.#2DTR(B)_LOAD | #2DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 77 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D04 | 豐華DS | 0 |  | 2DTR(B) | #2DTR(B) |  | PF | [25 empty] | ADCS_S | [8 empty] | 豐華DS.#2DTR(B)_PF | #2DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 78 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D04 | 豐華DS | 0 |  | 3DTR | #3DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 豐華DS.#3DTR_MVA | #3DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 79 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D04 | 豐華DS | 0 |  | 3DTR | #3DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 豐華DS.#3DTR_LOAD | #3DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 80 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D04 | 豐華DS | 0 |  | 3DTR | #3DTR |  | PF | [25 empty] | ADCS_S | [8 empty] | 豐華DS.#3DTR_PF | #3DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 81 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D04 | 豐華DS | 0 |  | 1DTR | #1DTR |  | MW | [25 empty] | ADCS_S | [8 empty] | 豐華DS.#1DTR_MW | #1DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 82 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  | 1DTR | #1DTR |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 豐華DS.#1DTR_MVAR | #1DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 83 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  | 1DTR | #1DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 豐華DS.#1DTR_MVA | #1DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 84 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D04 | 豐華DS | 0 |  | 1DTR | #1DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 豐華DS.#1DTR_LOAD | #1DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 85 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D04 | 豐華DS | 0 |  | 2DTR | #2DTR |  | MW | [25 empty] | ADCS_S | [8 empty] | 豐華DS.#2DTR_MW | #2DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 86 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  | 2DTR | #2DTR |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 豐華DS.#2DTR_MVAR | #2DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 87 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  | 2DTR | #2DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 豐華DS.#2DTR_MVA | #2DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 88 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D04 | 豐華DS | 0 |  | 2DTR | #2DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 豐華DS.#2DTR_LOAD | #2DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 89 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D04 | 豐華DS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 豐華DS.210_SC_MVAR | 11KV#1SC MVAR | SC | D04/11/210/MVAR |  | SC_LBS_11 |  |  | 90 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 11 | 11kV | 220_SC | #2SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 豐華DS.220_SC_MVAR | 11KV#2SC MVAR | SC | D04/11/220/MVAR |  | SC_LBS_11 |  |  | 91 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 11 | 11kV | 230_SC | #3SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 豐華DS.230_SC_MVAR | 11KV#3SC MVAR | SC | D04/11/230/MVAR |  | SC_LBS_11 |  |  | 92 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 11 | 11kV | 240_SC | #4SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 豐華DS.240_SC_MVAR | 11KV#4SC MVAR | SC | D04/11/240/MVAR |  | SC_LBS_11 |  |  | 93 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 22 | 22kV | 250_SC | #5SC | 9 | MVAR | [25 empty] | ADCS_S | [8 empty] | 豐華DS.250_SC_MVAR | 23KV#5SC MVAR | SC | D04/22/250/MVAR |  | SC_CAL_23 |  |  | 94 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 22 | 22kV | 260_SC | #6SC | 9 | MVAR | [25 empty] | ADCS_S | [8 empty] | 豐華DS.260_SC_MVAR | 23KV#6SC MVAR | SC | D04/22/260/MVAR |  | SC_CAL_23 |  |  | 95 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  | TRTOT | 豐華主變瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 豐華DS.TRTOT_MW | 豐華主變瞬時供電量 MW |  |  |  | TOTAL_PQ_CAL_3 |  |  | 96 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  | TRTOT | 豐華主變瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 豐華DS.TRTOT_MVAR | 豐華主變瞬時供電量 MVAR |  |  |  | TOTAL_PQ_CAL_3 |  |  | 97 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華聯電五一路(1610) |  | I | [25 empty] | ADCS_S | [8 empty] | 豐華DS.1610_AMP | 豐華聯電五一路 AMP | LINE161 | D04/161/1610/I |  | AMP_CAL |  |  | 98 | CalcAIPoint | [21 empty] | C20R1228 | 1105.000000 | 1105.000000 | 1228.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華聯電五二路(1620) |  | I | [25 empty] | ADCS_S | [8 empty] | 豐華DS.1620_AMP | 豐華聯電五二路 AMP | LINE161 | D04/161/1620/I |  | AMP_CAL |  |  | 99 | CalcAIPoint | [21 empty] | C20R1228 | 1105.000000 | 1105.000000 | 1228.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D04 | 豐華DS | 0 |  | TEN_DAYS09 | (1530+1540 MW) |  | MW | [25 empty] | CDCS | [8 empty] | 豐華DS.TEN_DAYS09_MW | (1530+1540 MW) |  |  |  | MTR_PQ_CAL |  |  | 100 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  | TEN_DAYS13 | (1610+1620 MW) |  | MW | [25 empty] | CDCS | [8 empty] | 豐華DS.TEN_DAYS13_MW | (1610+1620 MW) |  |  |  | MTR_PQ_CAL |  |  | 101 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 161 | 161kV | 1960_SHR | #2SHR |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 豐華DS.1960_SHR_MVAR | 161KV#2SHR MVAR | SC |  |  | SHR_CAL_324_5 |  |  | 102 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  | 100_CB | 100(100_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.100_CB_4 | 100 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 103 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | 200_CB | 200(200_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.200_CB_4 | 200 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 104 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | 1750_CB | #1DTR(1750_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.1750_CB_4 | 1750(#1DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 105 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 310_CB | #1DTR(310_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.310_CB_4 | 310(#1DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 106 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 320_CB | #1DTR(320_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.320_CB_4 | 320(#1DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 107 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 1760_CB | #2DTR(1760_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.1760_CB_4 | 1760(#2DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 108 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 330_CB | #2DTR(330_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.330_CB_4 | 330(#2DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 109 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 340_CB | #2DTR(340_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.340_CB_4 | 340(#2DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 110 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 1770_CB | #3DTR(1770_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.1770_CB_4 | 1770(#3DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 111 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 350_CB | #3DTR(350_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.350_CB_4 | 350(#3DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 112 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | 210_CB | #1SC(210_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.210_CB_4 | 210(11KV #1SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 113 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | 220_CB | #2SC(220_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.220_CB_4 | 220(11KV #2SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 114 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | 230_CB | #3SC(230_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.230_CB_4 | 230(11KV #3SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 115 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | 240_CB | #4SC(240_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.240_CB_4 | 240(11KV #4SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 116 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 22 | 22kV | 250_CB | #5SC(250_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.250_CB_4 | 250(23KV #5SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 117 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 22 | 22kV | 260_CB | #6SC(260_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.260_CB_4 | 260(23KV #6SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 118 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 22 | 22kV | 11__CBA | 11/斷路器重故障(11__CBA) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.11/23KV_CBA_4 | 11/23KV斷路器重故障 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 119 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | 11__CBF | 11/斷路器輕故障(11__CBF) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.11/23KV_CBF_4 | 11/23KV斷路器輕故障 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 120 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | RTU_S_L | RTU |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.RTU_S/L_4 | RTU SUPY/LOCAL (D4) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 121 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D04 | 豐華DS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_S | [8 empty] | 豐華DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | D04/0/CalcPoint/SUBA |  | STATION_FAULT_14 |  |  | 122 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 變電所輕故障點燈 | 變電所輕故障點燈 |  | SUBF | [25 empty] | ADCS_S | [8 empty] | 豐華DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | D04/0/CalcPoint/SUBF |  | STATION_FAULT_3 |  |  | 123 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.變電所重故障_4 | 變電所重故障點燈 (D4) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 124 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.變電所輕故障_4 | 變電所輕故障點燈 (D4) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 125 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1510_AMP | 南科豐華紅線 | [27 empty] | ADCS_S | [8 empty] | 豐華DS.1510_AMP_A | 南科豐華紅線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 126 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D04 | 豐華DS | 161 | 161kV | 1520_AMP | 南科豐華白線 | [27 empty] | ADCS_S | [8 empty] | 豐華DS.1520_AMP_A | 南科豐華白線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 127 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D04 | 豐華DS | 161 | 161kV | 1530_AMP | 豐華奇晶一線 | [27 empty] | ADCS_S | [8 empty] | 豐華DS.1530_AMP_A | 豐華奇晶一線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 128 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D04 | 豐華DS | 161 | 161kV | 1540_AMP | 豐華奇晶四線 | [27 empty] | ADCS_S | [8 empty] | 豐華DS.1540_AMP_A | 豐華奇晶四線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 129 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D04 | 豐華DS | 161 | 161kV | 1550_AMP | 三竹豐華一路 | [27 empty] | ADCS_S | [8 empty] | 豐華DS.1550_AMP_A | 三竹豐華一路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 130 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D04 | 豐華DS | 161 | 161kV | 1560_AMP | 三竹豐華二路 | [27 empty] | ADCS_S | [8 empty] | 豐華DS.1560_AMP_A | 三竹豐華二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 131 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D04 | 豐華DS | 161 | 161kV | 1570_AMP | 山上安南紅線 | [27 empty] | ADCS_S | [8 empty] | 豐華DS.1570_AMP_A | 山上安南紅線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 132 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D04 | 豐華DS | 161 | 161kV | 1580_AMP | 山上鹽行白線 | [27 empty] | ADCS_S | [8 empty] | 豐華DS.1580_AMP_A | 山上鹽行白線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 133 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D04 | 豐華DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PERM | [25 empty] | ADCS_S | [8 empty] | 豐華DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | D04//1DTR(A)/TR_PERM |  | DTR_PERM |  |  | 134 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D04 | 豐華DS | 0 |  | 1DTR(B) | #1DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 豐華DS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | D04//1DTR(B)/TR_PERM |  | DTR_PERM |  |  | 135 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D04 | 豐華DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PERM | [25 empty] | ADCS_S | [8 empty] | 豐華DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | D04//2DTR(A)/TR_PERM |  | DTR_PERM |  |  | 136 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D04 | 豐華DS | 0 |  | 2DTR(B) | #2DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 豐華DS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | D04//2DTR(B)/TR_PERM |  | DTR_PERM |  |  | 137 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D04 | 豐華DS | 0 |  | 3DTR | #3DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 豐華DS.#3DTR_PERM | #3DTR TAP PERMISSION POINT | MTR | D04//3DTR/TR_PERM |  | DTR_PERM |  |  | 138 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D04 | 豐華DS | 0 |  | 1DTR_MVA | #1DTR | [27 empty] | ADCS_S | [8 empty] | 豐華DS.#1DTR_MVA_A | #1DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 139 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D04 | 豐華DS | 0 |  | 1DTR_MVA | #1DTR(A) |  | 3 | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.#1DTR_MVA_3 | #1DTR(A) MVA 點燈 (D4) | MTR |  |  | MAP_SET |  |  | 140 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D04 | 豐華DS | 0 |  | 1DTR_MVA | #1DTR(B) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.#1DTR_MVA_4 | #1DTR(B) MVA 點燈 (D4) | MTR |  |  | MAP_SET |  |  | 141 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D04 | 豐華DS | 0 |  | 2DTR_MVA | #2DTR | [27 empty] | ADCS_S | [8 empty] | 豐華DS.#2DTR_MVA_A | #2DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 142 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D04 | 豐華DS | 0 |  | 2DTR_MVA | #2DTR(A) |  | 3 | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.#2DTR_MVA_3 | #2DTR(A) MVA 點燈 (D4) | MTR |  |  | MAP_SET |  |  | 143 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D04 | 豐華DS | 0 |  | 2DTR_MVA | #2DTR(B) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.#2DTR_MVA_4 | #2DTR(B) MVA 點燈 (D4) | MTR |  |  | MAP_SET |  |  | 144 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D04 | 豐華DS | 0 |  | 3DTR_MVA | #3DTR | [27 empty] | ADCS_S | [8 empty] | 豐華DS.#3DTR_MVA_A | #3DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 145 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D04 | 豐華DS | 0 |  | 3DTR_MVA | #3DTR |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 豐華DS.#3DTR_MVA_4 | #3DTR MVA 點燈 (D4) | MTR |  |  | AD_LAMP_DD_2 |  |  | 146 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D04 | 豐華DS | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_S | [8 empty] | 豐華DS.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_DS |  |  | 147 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1610_AMP | 豐華聯電五一路 | [27 empty] | ADCS_S | [8 empty] | 豐華DS.1610_AMP_A | 豐華聯電五一路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 148 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D04 | 豐華DS | 161 | 161kV | 1620_AMP | 豐華聯電五二路 | [27 empty] | ADCS_S | [8 empty] | 豐華DS.1620_AMP_A | 豐華聯電五二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 149 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D04 | 豐華DS | 0 |  | 1ABUS | #1ABUS |  | 11KV#1ABUSC | [25 empty] | CDCS | [8 empty] | 豐華DS.11KV#1ABUSC | #1ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 150 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D04 | 豐華DS | 0 |  | 1BBUS | #1BBUS |  | 11KV#1BBUSC | [25 empty] | CDCS | [8 empty] | 豐華DS.11KV#1BBUSC | #1BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 151 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D04 | 豐華DS | 0 |  | 2ABUS | #2ABUS |  | 11KV#2ABUSC | [25 empty] | CDCS | [8 empty] | 豐華DS.11KV#2ABUSC | #2ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 152 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D04 | 豐華DS | 0 |  | 2BBUS | #2BBUS |  | 11KV#2BBUSC | [25 empty] | CDCS | [8 empty] | 豐華DS.11KV#2BBUSC | #2BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 153 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D04 | 豐華DS | 0 |  | 3BUS | #3BUS |  | 23KV#3BUSC | [25 empty] | CDCS | [8 empty] | 豐華DS.23KV#3BUSC | #3BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 154 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D04 | 豐華DS | 0 |  | TAP_OVER | TAP |  | SET | [25 empty] | ADCS_S | [8 empty] | 豐華DS.TAP_OVER_SET | TAP OVER HI/LO ALARM | MTR |  |  | 5000_CB_T5 |  |  | 155 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D04 | 豐華DS | 0 |  | BUS_OVER | BUS |  | SET | [25 empty] | ADCS_S | [8 empty] | 豐華DS.BUS_OVER_SET | BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B5 |  |  | 156 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D04 | 豐華DS | 0 |  | 5000 | 虛擬5000 |  | CB動作 | [25 empty] | ADCS_S | [8 empty] | 豐華DS.5000_CB動作 | 虛擬5000 CB動作,請查明原因處理 | MTR |  |  | 5000_CB_M |  |  | 157 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 注意OLTC | 注意OLTC |  | BUS電壓異常 | [25 empty] | ADCS_S | [8 empty] | 豐華DS.BUS電壓異常 | 注意OLTC Tap位置,並將RPDC閉鎖 | OTHER |  |  | STATION_FAULT_3 |  |  | 158 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | D04/161/1BUS/V |  |  |  | CDC | 159 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D04 | 豐華DS | 161 | 161kV | 2BUS | #2BUS |  | V | [17 empty] | 1-83 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | D04/161/2BUS/V |  |  |  | CDC | 160 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D04 | 豐華DS | 11 | 11kV | 1ABUS | #1ABUS |  | V | [17 empty] | 1-B3 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.11KV#1ABUS_KV | 11KV #1ABUS KV | BUS | D04/11/1ABUS/V |  |  |  | CDC | 161 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D04 | 豐華DS | 11 | 11kV | 1BBUS | #1BBUS |  | V | [17 empty] | 1-D4 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.11KV#1BBUS_KV | 11KV #1BBUS KV | BUS | D04/11/1BBUS/V |  |  |  | CDC | 162 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D04 | 豐華DS | 11 | 11kV | 2ABUS | #2ABUS |  | V | [17 empty] | 1-F3 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS | D04/11/2ABUS/V |  |  |  | CDC | 163 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D04 | 豐華DS | 11 | 11kV | 2BBUS | #2BBUS |  | V | [17 empty] | 2-97 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.11KV#2BBUS_KV | 11KV #2BBUS KV | BUS | D04/11/2BBUS/V |  |  |  | CDC | 164 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D04 | 豐華DS | 22 | 22kV | 3BUS | #3BUS |  | V | [17 empty] | 2-B9 | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.23KV#3BUS_KV | 23KV #3BUS KV | BUS | D04/11/3BUS/V |  |  |  | CDC | 165 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D04 | 豐華DS | 161 | 161kV | 1510 | 南科豐華紅線(1510) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.1510_MW | 南科豐華紅線 MW | LINE161 | D04/161/1510/MW |  |  |  | CDC | 166 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1510 | 南科豐華紅線(1510) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.1510_MVAR | 南科豐華紅線 MVAR | LINE161 | D04/161/1510/MVAR |  |  |  | CDC | 167 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1520 | 南科豐華白線(1520) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.1520_MW | 南科豐華白線 MW | LINE161 | D04/161/1520/MW |  |  |  | CDC | 168 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1520 | 南科豐華白線(1520) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.1520_MVAR | 南科豐華白線 MVAR | LINE161 | D04/161/1520/MVAR |  |  |  | CDC | 169 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1530 | 豐華奇晶一線(1530) |  | MW | [17 empty] | 1-88 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.1530_MW | 豐華奇晶一線 MW | LINE161 | D04/161/1530/MW |  |  |  | CDC | 170 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1530 | 豐華奇晶一線(1530) |  | MVAR | [17 empty] | 1-89 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.1530_MVAR | 豐華奇晶一線 MVAR | LINE161 | D04/161/1530/MVAR |  |  |  | CDC | 171 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1540 | 豐華奇晶四線(1540) |  | MW | [17 empty] | 1-8A | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.1540_MW | 豐華奇晶四線 MW | LINE161 | D04/161/1540/MW |  |  |  | CDC | 172 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1540 | 豐華奇晶四線(1540) |  | MVAR | [17 empty] | 1-8B | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.1540_MVAR | 豐華奇晶四線 MVAR | LINE161 | D04/161/1540/MVAR |  |  |  | CDC | 173 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1550 | 三竹豐華一路(1550) |  | MW | [17 empty] | 1-8C | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.1550_MW | 三竹豐華一路 MW | LINE161 | D04/161/1550/MW |  |  |  | CDC | 174 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1550 | 三竹豐華一路(1550) |  | MVAR | [17 empty] | 1-8D | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.1550_MVAR | 三竹豐華一路 MVAR | LINE161 | D04/161/1550/MVAR |  |  |  | CDC | 175 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1560 | 三竹豐華二路(1560) |  | MW | [17 empty] | 1-8E | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.1560_MW | 三竹豐華二路 MW | LINE161 | D04/161/1560/MW |  |  |  | CDC | 176 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1560 | 三竹豐華二路(1560) |  | MVAR | [17 empty] | 1-8F | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.1560_MVAR | 三竹豐華二路 MVAR | LINE161 | D04/161/1560/MVAR |  |  |  | CDC | 177 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1570 | 山上安南紅線(1570) |  | MW | [17 empty] | 1-90 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.1570_MW | 山上安南紅線 MW | LINE161 | D04/161/1570/MW |  |  |  | CDC | 178 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1570 | 山上安南紅線(1570) |  | MVAR | [17 empty] | 1-91 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.1570_MVAR | 山上安南紅線 MVAR | LINE161 | D04/161/1570/MVAR |  |  |  | CDC | 179 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1580 | 山上鹽行白線(1580) |  | MW | [17 empty] | 1-92 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.1580_MW | 山上鹽行白線 MW | LINE161 | D04/161/1580/MW |  |  |  | CDC | 180 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1580 | 山上鹽行白線(1580) |  | MVAR | [17 empty] | 1-93 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.1580_MVAR | 山上鹽行白線 MVAR | LINE161 | D04/161/1580/MVAR |  |  |  | CDC | 181 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐11線 | 豐11線 |  | 豐11線KVAR | [17 empty] | 1-B4 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐11線KVAR | 11KV豐11線 KVAR | FEEDER | D04/11/K811/KVAR |  |  |  | CDC | 182 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐11線 | 豐11線 |  | 豐11線A1 | [17 empty] | 1-B5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐11線A1 | 11KV豐11線 R相AMP | FEEDER | D04/11/K811/I_R |  |  |  | CDC | 183 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐11線 | 豐11線 |  | 豐11線A2 | [17 empty] | 1-B6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐11線A2 | 11KV豐11線 S相AMP | FEEDER | D04/11/K811/I_S |  |  |  | CDC | 184 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐11線 | 豐11線 |  | 豐11線A3 | [17 empty] | 1-B7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐11線A3 | 11KV豐11線 T相AMP | FEEDER | D04/11/K811/I_T |  |  |  | CDC | 185 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐11線 | 豐11線 |  | 豐11線A0 | [17 empty] | 1-B8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐11線A0 | 11KV豐11線 N相AMP | FEEDER | D04/11/K811/I_N |  |  |  | CDC | 186 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐12線 | 豐12線 |  | 豐12線KVAR | [17 empty] | 1-B9 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐12線KVAR | 11KV豐12線 KVAR | FEEDER | D04/11/K812/KVAR |  |  |  | CDC | 187 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐12線 | 豐12線 |  | 豐12線A1 | [17 empty] | 1-BA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐12線A1 | 11KV豐12線 R相AMP | FEEDER | D04/11/K812/I_R |  |  |  | CDC | 188 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐12線 | 豐12線 |  | 豐12線A2 | [17 empty] | 1-BB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐12線A2 | 11KV豐12線 S相AMP | FEEDER | D04/11/K812/I_S |  |  |  | CDC | 189 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐12線 | 豐12線 |  | 豐12線A3 | [17 empty] | 1-BC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐12線A3 | 11KV豐12線 T相AMP | FEEDER | D04/11/K812/I_T |  |  |  | CDC | 190 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐12線 | 豐12線 |  | 豐12線A0 | [17 empty] | 1-BD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐12線A0 | 11KV豐12線 N相AMP | FEEDER | D04/11/K812/I_N |  |  |  | CDC | 191 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐13線 | 豐13線 |  | 豐13線KVAR | [17 empty] | 1-BE | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐13線KVAR | 11KV豐13線 KVAR | FEEDER | D04/11/K813/KVAR |  |  |  | CDC | 192 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐13線 | 豐13線 |  | 豐13線A1 | [17 empty] | 1-BF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐13線A1 | 11KV豐13線 R相AMP | FEEDER | D04/11/K813/I_R |  |  |  | CDC | 193 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐13線 | 豐13線 |  | 豐13線A2 | [17 empty] | 1-C2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐13線A2 | 11KV豐13線 S相AMP | FEEDER | D04/11/K813/I_S |  |  |  | CDC | 194 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐13線 | 豐13線 |  | 豐13線A3 | [17 empty] | 1-C3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐13線A3 | 11KV豐13線 T相AMP | FEEDER | D04/11/K813/I_T |  |  |  | CDC | 195 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐13線 | 豐13線 |  | 豐13線A0 | [17 empty] | 1-C4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐13線A0 | 11KV豐13線 N相AMP | FEEDER | D04/11/K813/I_N |  |  |  | CDC | 196 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐14線 | 豐14線 |  | 豐14線KVAR | [17 empty] | 1-C5 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐14線KVAR | 11KV豐14線 KVAR | FEEDER | D04/11/K814/KVAR |  |  |  | CDC | 197 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐14線 | 豐14線 |  | 豐14線A1 | [17 empty] | 1-C6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐14線A1 | 11KV豐14線 R相AMP | FEEDER | D04/11/K814/I_R |  |  |  | CDC | 198 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐14線 | 豐14線 |  | 豐14線A2 | [17 empty] | 1-C7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐14線A2 | 11KV豐14線 S相AMP | FEEDER | D04/11/K814/I_S |  |  |  | CDC | 199 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐14線 | 豐14線 |  | 豐14線A3 | [17 empty] | 1-C8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐14線A3 | 11KV豐14線 T相AMP | FEEDER | D04/11/K814/I_T |  |  |  | CDC | 200 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐14線 | 豐14線 |  | 豐14線A0 | [17 empty] | 1-C9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐14線A0 | 11KV豐14線 N相AMP | FEEDER | D04/11/K814/I_N |  |  |  | CDC | 201 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐15線 | 豐15線 |  | 豐15線KVAR | [17 empty] | 1-CA | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐15線KVAR | 11KV豐15線 KVAR | FEEDER | D04/11/K815/KVAR |  |  |  | CDC | 202 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐15線 | 豐15線 |  | 豐15線A1 | [17 empty] | 1-CB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐15線A1 | 11KV豐15線 R相AMP | FEEDER | D04/11/K815/I_R |  |  |  | CDC | 203 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐15線 | 豐15線 |  | 豐15線A2 | [17 empty] | 1-CC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐15線A2 | 11KV豐15線 S相AMP | FEEDER | D04/11/K815/I_S |  |  |  | CDC | 204 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐15線 | 豐15線 |  | 豐15線A3 | [17 empty] | 1-CD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐15線A3 | 11KV豐15線 T相AMP | FEEDER | D04/11/K815/I_T |  |  |  | CDC | 205 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐15線 | 豐15線 |  | 豐15線A0 | [17 empty] | 1-CE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐15線A0 | 11KV豐15線 N相AMP | FEEDER | D04/11/K815/I_N |  |  |  | CDC | 206 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐21線 | 豐21線 |  | 豐21線KVAR | [17 empty] | 1-D5 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐21線KVAR | 11KV豐21線 KVAR | FEEDER | D04/11/K821/KVAR |  |  |  | CDC | 207 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐21線 | 豐21線 |  | 豐21線A1 | [17 empty] | 1-D6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐21線A1 | 11KV豐21線 R相AMP | FEEDER | D04/11/K821/I_R |  |  |  | CDC | 208 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐21線 | 豐21線 |  | 豐21線A2 | [17 empty] | 1-D7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐21線A2 | 11KV豐21線 S相AMP | FEEDER | D04/11/K821/I_S |  |  |  | CDC | 209 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐21線 | 豐21線 |  | 豐21線A3 | [17 empty] | 1-D8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐21線A3 | 11KV豐21線 T相AMP | FEEDER | D04/11/K821/I_T |  |  |  | CDC | 210 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐21線 | 豐21線 |  | 豐21線A0 | [17 empty] | 1-D9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐21線A0 | 11KV豐21線 N相AMP | FEEDER | D04/11/K821/I_N |  |  |  | CDC | 211 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐22線 | 豐22線 |  | 豐22線KVAR | [17 empty] | 1-DA | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐22線KVAR | 11KV豐22線 KVAR | FEEDER | D04/11/K822/KVAR |  |  |  | CDC | 212 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐22線 | 豐22線 |  | 豐22線A1 | [17 empty] | 1-DB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐22線A1 | 11KV豐22線 R相AMP | FEEDER | D04/11/K822/I_R |  |  |  | CDC | 213 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐22線 | 豐22線 |  | 豐22線A2 | [17 empty] | 1-DC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐22線A2 | 11KV豐22線 S相AMP | FEEDER | D04/11/K822/I_S |  |  |  | CDC | 214 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐22線 | 豐22線 |  | 豐22線A3 | [17 empty] | 1-DD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐22線A3 | 11KV豐22線 T相AMP | FEEDER | D04/11/K822/I_T |  |  |  | CDC | 215 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐22線 | 豐22線 |  | 豐22線A0 | [17 empty] | 1-DE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐22線A0 | 11KV豐22線 N相AMP | FEEDER | D04/11/K822/I_N |  |  |  | CDC | 216 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐23線 | 豐23線 |  | 豐23線KVAR | [17 empty] | 1-DF | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐23線KVAR | 11KV豐23線 KVAR | FEEDER | D04/11/K823/KVAR |  |  |  | CDC | 217 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐23線 | 豐23線 |  | 豐23線A1 | [17 empty] | 1-E0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐23線A1 | 11KV豐23線 R相AMP | FEEDER | D04/11/K823/I_R |  |  |  | CDC | 218 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐23線 | 豐23線 |  | 豐23線A2 | [17 empty] | 1-E1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐23線A2 | 11KV豐23線 S相AMP | FEEDER | D04/11/K823/I_S |  |  |  | CDC | 219 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐23線 | 豐23線 |  | 豐23線A3 | [17 empty] | 1-E2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐23線A3 | 11KV豐23線 T相AMP | FEEDER | D04/11/K823/I_T |  |  |  | CDC | 220 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐23線 | 豐23線 |  | 豐23線A0 | [17 empty] | 1-E3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐23線A0 | 11KV豐23線 N相AMP | FEEDER | D04/11/K823/I_N |  |  |  | CDC | 221 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐24線 | 豐24線 |  | 豐24線KVAR | [17 empty] | 1-E4 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐24線KVAR | 11KV豐24線 KVAR | FEEDER | D04/11/K824/KVAR |  |  |  | CDC | 222 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐24線 | 豐24線 |  | 豐24線A1 | [17 empty] | 1-E5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐24線A1 | 11KV豐24線 R相AMP | FEEDER | D04/11/K824/I_R |  |  |  | CDC | 223 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐24線 | 豐24線 |  | 豐24線A2 | [17 empty] | 1-E6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐24線A2 | 11KV豐24線 S相AMP | FEEDER | D04/11/K824/I_S |  |  |  | CDC | 224 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐24線 | 豐24線 |  | 豐24線A3 | [17 empty] | 1-E7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐24線A3 | 11KV豐24線 T相AMP | FEEDER | D04/11/K824/I_T |  |  |  | CDC | 225 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐24線 | 豐24線 |  | 豐24線A0 | [17 empty] | 1-E8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐24線A0 | 11KV豐24線 N相AMP | FEEDER | D04/11/K824/I_N |  |  |  | CDC | 226 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐25線 | 豐25線 |  | 豐25線KVAR | [17 empty] | 1-E9 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐25線KVAR | 11KV豐25線 KVAR | FEEDER | D04/11/K825/KVAR |  |  |  | CDC | 227 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐25線 | 豐25線 |  | 豐25線A1 | [17 empty] | 1-EA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐25線A1 | 11KV豐25線 R相AMP | FEEDER | D04/11/K825/I_R |  |  |  | CDC | 228 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐25線 | 豐25線 |  | 豐25線A2 | [17 empty] | 1-EB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐25線A2 | 11KV豐25線 S相AMP | FEEDER | D04/11/K825/I_S |  |  |  | CDC | 229 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐25線 | 豐25線 |  | 豐25線A3 | [17 empty] | 1-EC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐25線A3 | 11KV豐25線 T相AMP | FEEDER | D04/11/K825/I_T |  |  |  | CDC | 230 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐25線 | 豐25線 |  | 豐25線A0 | [17 empty] | 1-ED | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐25線A0 | 11KV豐25線 N相AMP | FEEDER | D04/11/K825/I_N |  |  |  | CDC | 231 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐31線 | 豐31線 |  | 豐31線KVAR | [17 empty] | 1-F4 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐31線KVAR | 11KV豐31線 KVAR | FEEDER | D04/11/K831/KVAR |  |  |  | CDC | 232 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐31線 | 豐31線 |  | 豐31線A1 | [17 empty] | 1-F5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐31線A1 | 11KV豐31線 R相AMP | FEEDER | D04/11/K831/I_R |  |  |  | CDC | 233 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐31線 | 豐31線 |  | 豐31線A2 | [17 empty] | 1-F6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐31線A2 | 11KV豐31線 S相AMP | FEEDER | D04/11/K831/I_S |  |  |  | CDC | 234 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐31線 | 豐31線 |  | 豐31線A3 | [17 empty] | 1-F7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐31線A3 | 11KV豐31線 T相AMP | FEEDER | D04/11/K831/I_T |  |  |  | CDC | 235 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐31線 | 豐31線 |  | 豐31線A0 | [17 empty] | 1-F8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐31線A0 | 11KV豐31線 N相AMP | FEEDER | D04/11/K831/I_N |  |  |  | CDC | 236 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐32線 | 豐32線 |  | 豐32線KVAR | [17 empty] | 1-F9 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐32線KVAR | 11KV豐32線 KVAR | FEEDER | D04/11/K832/KVAR |  |  |  | CDC | 237 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐32線 | 豐32線 |  | 豐32線A1 | [17 empty] | 1-FA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐32線A1 | 11KV豐32線 R相AMP | FEEDER | D04/11/K832/I_R |  |  |  | CDC | 238 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐32線 | 豐32線 |  | 豐32線A2 | [17 empty] | 1-FB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐32線A2 | 11KV豐32線 S相AMP | FEEDER | D04/11/K832/I_S |  |  |  | CDC | 239 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐32線 | 豐32線 |  | 豐32線A3 | [17 empty] | 1-FC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐32線A3 | 11KV豐32線 T相AMP | FEEDER | D04/11/K832/I_T |  |  |  | CDC | 240 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐32線 | 豐32線 |  | 豐32線A0 | [17 empty] | 1-FD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐32線A0 | 11KV豐32線 N相AMP | FEEDER | D04/11/K832/I_N |  |  |  | CDC | 241 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐33線 | 豐33線 |  | 豐33線KVAR | [17 empty] | 1-FE | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐33線KVAR | 11KV豐33線 KVAR | FEEDER | D04/11/K833/KVAR |  |  |  | CDC | 242 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐33線 | 豐33線 |  | 豐33線A1 | [17 empty] | 1-FF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐33線A1 | 11KV豐33線 R相AMP | FEEDER | D04/11/K833/I_R |  |  |  | CDC | 243 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐33線 | 豐33線 |  | 豐33線A2 | [17 empty] | 2-82 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐33線A2 | 11KV豐33線 S相AMP | FEEDER | D04/11/K833/I_S |  |  |  | CDC | 244 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐33線 | 豐33線 |  | 豐33線A3 | [17 empty] | 2-83 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐33線A3 | 11KV豐33線 T相AMP | FEEDER | D04/11/K833/I_T |  |  |  | CDC | 245 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐33線 | 豐33線 |  | 豐33線A0 | [17 empty] | 2-84 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐33線A0 | 11KV豐33線 N相AMP | FEEDER | D04/11/K833/I_N |  |  |  | CDC | 246 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐34線 | 豐34線 |  | 豐34線KVAR | [17 empty] | 2-85 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐34線KVAR | 11KV豐34線 KVAR | FEEDER | D04/11/K834/KVAR |  |  |  | CDC | 247 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐34線 | 豐34線 |  | 豐34線A1 | [17 empty] | 2-86 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐34線A1 | 11KV豐34線 R相AMP | FEEDER | D04/11/K834/I_R |  |  |  | CDC | 248 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐34線 | 豐34線 |  | 豐34線A2 | [17 empty] | 2-87 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐34線A2 | 11KV豐34線 S相AMP | FEEDER | D04/11/K834/I_S |  |  |  | CDC | 249 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐34線 | 豐34線 |  | 豐34線A3 | [17 empty] | 2-88 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐34線A3 | 11KV豐34線 T相AMP | FEEDER | D04/11/K834/I_T |  |  |  | CDC | 250 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐34線 | 豐34線 |  | 豐34線A0 | [17 empty] | 2-89 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐34線A0 | 11KV豐34線 N相AMP | FEEDER | D04/11/K834/I_N |  |  |  | CDC | 251 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐35線 | 豐35線 |  | 豐35線KVAR | [17 empty] | 2-8A | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐35線KVAR | 11KV豐35線 KVAR | FEEDER | D04/11/K835/KVAR |  |  |  | CDC | 252 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐35線 | 豐35線 |  | 豐35線A1 | [17 empty] | 2-8B | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐35線A1 | 11KV豐35線 R相AMP | FEEDER | D04/11/K835/I_R |  |  |  | CDC | 253 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐35線 | 豐35線 |  | 豐35線A2 | [17 empty] | 2-8C | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐35線A2 | 11KV豐35線 S相AMP | FEEDER | D04/11/K835/I_S |  |  |  | CDC | 254 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐35線 | 豐35線 |  | 豐35線A3 | [17 empty] | 2-8D | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐35線A3 | 11KV豐35線 T相AMP | FEEDER | D04/11/K835/I_T |  |  |  | CDC | 255 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐35線 | 豐35線 |  | 豐35線A0 | [17 empty] | 2-8E | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐35線A0 | 11KV豐35線 N相AMP | FEEDER | D04/11/K835/I_N |  |  |  | CDC | 256 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐41線 | 豐41線 |  | 豐41線KVAR | [17 empty] | 2-98 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐41線KVAR | 11KV豐41線 KVAR | FEEDER | D04/11/K841/KVAR |  |  |  | CDC | 257 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐41線 | 豐41線 |  | 豐41線A1 | [17 empty] | 2-99 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐41線A1 | 11KV豐41線 R相AMP | FEEDER | D04/11/K841/I_R |  |  |  | CDC | 258 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐41線 | 豐41線 |  | 豐41線A2 | [17 empty] | 2-9A | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐41線A2 | 11KV豐41線 S相AMP | FEEDER | D04/11/K841/I_S |  |  |  | CDC | 259 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐41線 | 豐41線 |  | 豐41線A3 | [17 empty] | 2-9B | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐41線A3 | 11KV豐41線 T相AMP | FEEDER | D04/11/K841/I_T |  |  |  | CDC | 260 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐41線 | 豐41線 |  | 豐41線A0 | [17 empty] | 2-9C | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐41線A0 | 11KV豐41線 N相AMP | FEEDER | D04/11/K841/I_N |  |  |  | CDC | 261 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐42線 | 豐42線 |  | 豐42線KVAR | [17 empty] | 2-9D | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐42線KVAR | 11KV豐42線 KVAR | FEEDER | D04/11/K842/KVAR |  |  |  | CDC | 262 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐42線 | 豐42線 |  | 豐42線A1 | [17 empty] | 2-9E | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐42線A1 | 11KV豐42線 R相AMP | FEEDER | D04/11/K842/I_R |  |  |  | CDC | 263 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐42線 | 豐42線 |  | 豐42線A2 | [17 empty] | 2-9F | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐42線A2 | 11KV豐42線 S相AMP | FEEDER | D04/11/K842/I_S |  |  |  | CDC | 264 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐42線 | 豐42線 |  | 豐42線A3 | [17 empty] | 2-A0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐42線A3 | 11KV豐42線 T相AMP | FEEDER | D04/11/K842/I_T |  |  |  | CDC | 265 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐42線 | 豐42線 |  | 豐42線A0 | [17 empty] | 2-A1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐42線A0 | 11KV豐42線 N相AMP | FEEDER | D04/11/K842/I_N |  |  |  | CDC | 266 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐43線 | 豐43線 |  | 豐43線KVAR | [17 empty] | 2-A2 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐43線KVAR | 11KV豐43線 KVAR | FEEDER | D04/11/K843/KVAR |  |  |  | CDC | 267 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐43線 | 豐43線 |  | 豐43線A1 | [17 empty] | 2-A3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐43線A1 | 11KV豐43線 R相AMP | FEEDER | D04/11/K843/I_R |  |  |  | CDC | 268 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐43線 | 豐43線 |  | 豐43線A2 | [17 empty] | 2-A4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐43線A2 | 11KV豐43線 S相AMP | FEEDER | D04/11/K843/I_S |  |  |  | CDC | 269 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐43線 | 豐43線 |  | 豐43線A3 | [17 empty] | 2-A5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐43線A3 | 11KV豐43線 T相AMP | FEEDER | D04/11/K843/I_T |  |  |  | CDC | 270 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐43線 | 豐43線 |  | 豐43線A0 | [17 empty] | 2-A6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐43線A0 | 11KV豐43線 N相AMP | FEEDER | D04/11/K843/I_N |  |  |  | CDC | 271 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐44線 | 豐44線 |  | 豐44線KVAR | [17 empty] | 2-A7 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐44線KVAR | 11KV豐44線 KVAR | FEEDER | D04/11/K844/KVAR |  |  |  | CDC | 272 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐44線 | 豐44線 |  | 豐44線A1 | [17 empty] | 2-A8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐44線A1 | 11KV豐44線 R相AMP | FEEDER | D04/11/K844/I_R |  |  |  | CDC | 273 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐44線 | 豐44線 |  | 豐44線A2 | [17 empty] | 2-A9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐44線A2 | 11KV豐44線 S相AMP | FEEDER | D04/11/K844/I_S |  |  |  | CDC | 274 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐44線 | 豐44線 |  | 豐44線A3 | [17 empty] | 2-AA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐44線A3 | 11KV豐44線 T相AMP | FEEDER | D04/11/K844/I_T |  |  |  | CDC | 275 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐44線 | 豐44線 |  | 豐44線A0 | [17 empty] | 2-AB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐44線A0 | 11KV豐44線 N相AMP | FEEDER | D04/11/K844/I_N |  |  |  | CDC | 276 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐45線 | 豐45線 |  | 豐45線KVAR | [17 empty] | 2-AC | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐45線KVAR | 11KV豐45線 KVAR | FEEDER | D04/11/K845/KVAR |  |  |  | CDC | 277 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐45線 | 豐45線 |  | 豐45線A1 | [17 empty] | 2-AD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐45線A1 | 11KV豐45線 R相AMP | FEEDER | D04/11/K845/I_R |  |  |  | CDC | 278 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐45線 | 豐45線 |  | 豐45線A2 | [17 empty] | 2-AE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐45線A2 | 11KV豐45線 S相AMP | FEEDER | D04/11/K845/I_S |  |  |  | CDC | 279 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐45線 | 豐45線 |  | 豐45線A3 | [17 empty] | 2-AF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐45線A3 | 11KV豐45線 T相AMP | FEEDER | D04/11/K845/I_T |  |  |  | CDC | 280 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | 豐45線 | 豐45線 |  | 豐45線A0 | [17 empty] | 2-B0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐45線A0 | 11KV豐45線 N相AMP | FEEDER | D04/11/K845/I_N |  |  |  | CDC | 281 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐61線 | 豐61線 |  | 豐61線KVAR | [17 empty] | 2-BA | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐61線KVAR | 23KV豐61線 KVAR | FEEDER | D04/22/K861/KVAR |  |  |  | CDC | 282 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐61線 | 豐61線 |  | 豐61線A1 | [17 empty] | 2-BB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐61線A1 | 23KV豐61線 R相AMP | FEEDER | D04/22/K861/I_R |  |  |  | CDC | 283 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐61線 | 豐61線 |  | 豐61線A2 | [17 empty] | 2-BC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐61線A2 | 23KV豐61線 S相AMP | FEEDER | D04/22/K861/I_S |  |  |  | CDC | 284 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐61線 | 豐61線 |  | 豐61線A3 | [17 empty] | 2-BD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐61線A3 | 23KV豐61線 T相AMP | FEEDER | D04/22/K861/I_T |  |  |  | CDC | 285 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐61線 | 豐61線 |  | 豐61線A0 | [17 empty] | 2-BE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐61線A0 | 23KV豐61線 N相AMP | FEEDER | D04/22/K861/I_N |  |  |  | CDC | 286 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐62線 | 豐62線 |  | 豐62線KVAR | [17 empty] | 2-BF | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐62線KVAR | 23KV豐62線 KVAR | FEEDER | D04/22/K862/KVAR |  |  |  | CDC | 287 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐62線 | 豐62線 |  | 豐62線A1 | [17 empty] | 2-C2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐62線A1 | 23KV豐62線 R相AMP | FEEDER | D04/22/K862/I_R |  |  |  | CDC | 288 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐62線 | 豐62線 |  | 豐62線A2 | [17 empty] | 2-C3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐62線A2 | 23KV豐62線 S相AMP | FEEDER | D04/22/K862/I_S |  |  |  | CDC | 289 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐62線 | 豐62線 |  | 豐62線A3 | [17 empty] | 2-C4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐62線A3 | 23KV豐62線 T相AMP | FEEDER | D04/22/K862/I_T |  |  |  | CDC | 290 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐62線 | 豐62線 |  | 豐62線A0 | [17 empty] | 2-C5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐62線A0 | 23KV豐62線 N相AMP | FEEDER | D04/22/K862/I_N |  |  |  | CDC | 291 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐63線 | 豐63線 |  | 豐63線KVAR | [17 empty] | 2-C6 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐63線KVAR | 23KV豐63線 KVAR | FEEDER | D04/22/K863/KVAR |  |  |  | CDC | 292 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐63線 | 豐63線 |  | 豐63線A1 | [17 empty] | 2-C7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐63線A1 | 23KV豐63線 R相AMP | FEEDER | D04/22/K863/I_R |  |  |  | CDC | 293 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐63線 | 豐63線 |  | 豐63線A2 | [17 empty] | 2-C8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐63線A2 | 23KV豐63線 S相AMP | FEEDER | D04/22/K863/I_S |  |  |  | CDC | 294 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐63線 | 豐63線 |  | 豐63線A3 | [17 empty] | 2-C9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐63線A3 | 23KV豐63線 T相AMP | FEEDER | D04/22/K863/I_T |  |  |  | CDC | 295 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐63線 | 豐63線 |  | 豐63線A0 | [17 empty] | 2-CA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐63線A0 | 23KV豐63線 N相AMP | FEEDER | D04/22/K863/I_N |  |  |  | CDC | 296 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐64線 | 豐64線 |  | 豐64線KVAR | [17 empty] | 2-CB | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐64線KVAR | 23KV豐64線 KVAR | FEEDER | D04/22/K864/KVAR |  |  |  | CDC | 297 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐64線 | 豐64線 |  | 豐64線A1 | [17 empty] | 2-CC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐64線A1 | 23KV豐64線 R相AMP | FEEDER | D04/22/K864/I_R |  |  |  | CDC | 298 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐64線 | 豐64線 |  | 豐64線A2 | [17 empty] | 2-CD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐64線A2 | 23KV豐64線 S相AMP | FEEDER | D04/22/K864/I_S |  |  |  | CDC | 299 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐64線 | 豐64線 |  | 豐64線A3 | [17 empty] | 2-CE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐64線A3 | 23KV豐64線 T相AMP | FEEDER | D04/22/K864/I_T |  |  |  | CDC | 300 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐64線 | 豐64線 |  | 豐64線A0 | [17 empty] | 2-CF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐64線A0 | 23KV豐64線 N相AMP | FEEDER | D04/22/K864/I_N |  |  |  | CDC | 301 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐65線 | 豐65線 |  | 豐65線KVAR | [17 empty] | 2-D0 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐65線KVAR | 23KV豐65線 KVAR | FEEDER | D04/22/K865/KVAR |  |  |  | CDC | 302 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐65線 | 豐65線 |  | 豐65線A1 | [17 empty] | 2-D1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐65線A1 | 23KV豐65線 R相AMP | FEEDER | D04/22/K865/I_R |  |  |  | CDC | 303 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐65線 | 豐65線 |  | 豐65線A2 | [17 empty] | 2-D2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐65線A2 | 23KV豐65線 S相AMP | FEEDER | D04/22/K865/I_S |  |  |  | CDC | 304 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐65線 | 豐65線 |  | 豐65線A3 | [17 empty] | 2-D3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐65線A3 | 23KV豐65線 T相AMP | FEEDER | D04/22/K865/I_T |  |  |  | CDC | 305 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐65線 | 豐65線 |  | 豐65線A0 | [17 empty] | 2-D4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐65線A0 | 23KV豐65線 N相AMP | FEEDER | D04/22/K865/I_N |  |  |  | CDC | 306 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐66線 | 豐66線 |  | 豐66線KVAR | [17 empty] | 2-D5 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐66線KVAR | 23KV豐66線 KVAR | FEEDER | D04/22/K866/KVAR |  |  |  | CDC | 307 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐66線 | 豐66線 |  | 豐66線A1 | [17 empty] | 2-D6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐66線A1 | 23KV豐66線 R相AMP | FEEDER | D04/22/K866/I_R |  |  |  | CDC | 308 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐66線 | 豐66線 |  | 豐66線A2 | [17 empty] | 2-D7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐66線A2 | 23KV豐66線 S相AMP | FEEDER | D04/22/K866/I_S |  |  |  | CDC | 309 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐66線 | 豐66線 |  | 豐66線A3 | [17 empty] | 2-D8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐66線A3 | 23KV豐66線 T相AMP | FEEDER | D04/22/K866/I_T |  |  |  | CDC | 310 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐66線 | 豐66線 |  | 豐66線A0 | [17 empty] | 2-D9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐66線A0 | 23KV豐66線 N相AMP | FEEDER | D04/22/K866/I_N |  |  |  | CDC | 311 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐67線 | 豐67線 |  | 豐67線KVAR | [17 empty] | 2-DA | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐67線KVAR | 23KV豐67線 KVAR | FEEDER | D04/22/K867/KVAR |  |  |  | CDC | 312 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐67線 | 豐67線 |  | 豐67線A1 | [17 empty] | 2-DB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐67線A1 | 23KV豐67線 R相AMP | FEEDER | D04/22/K867/I_R |  |  |  | CDC | 313 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐67線 | 豐67線 |  | 豐67線A2 | [17 empty] | 2-DC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐67線A2 | 23KV豐67線 S相AMP | FEEDER | D04/22/K867/I_S |  |  |  | CDC | 314 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐67線 | 豐67線 |  | 豐67線A3 | [17 empty] | 2-DD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐67線A3 | 23KV豐67線 T相AMP | FEEDER | D04/22/K867/I_T |  |  |  | CDC | 315 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐67線 | 豐67線 |  | 豐67線A0 | [17 empty] | 2-DE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐67線A0 | 23KV豐67線 N相AMP | FEEDER | D04/22/K867/I_N |  |  |  | CDC | 316 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐68線 | 豐68線 |  | 豐68線KVAR | [17 empty] | 2-DF | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐68線KVAR | 23KV豐68線 KVAR | FEEDER | D04/22/K868/KVAR |  |  |  | CDC | 317 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐68線 | 豐68線 |  | 豐68線A1 | [17 empty] | 2-E0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐68線A1 | 23KV豐68線 R相AMP | FEEDER | D04/22/K868/I_R |  |  |  | CDC | 318 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐68線 | 豐68線 |  | 豐68線A2 | [17 empty] | 2-E1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐68線A2 | 23KV豐68線 S相AMP | FEEDER | D04/22/K868/I_S |  |  |  | CDC | 319 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐68線 | 豐68線 |  | 豐68線A3 | [17 empty] | 2-E2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐68線A3 | 23KV豐68線 T相AMP | FEEDER | D04/22/K868/I_T |  |  |  | CDC | 320 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 豐68線 | 豐68線 |  | 豐68線A0 | [17 empty] | 2-E3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.豐68線A0 | 23KV豐68線 N相AMP | FEEDER | D04/22/K868/I_N |  |  |  | CDC | 321 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 0 |  | 1500TIE | 1500TIE |  | I | [17 empty] | 1-9C | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.1500TIE_AMP | 1500TIE AMP | TIE | D04/161/1500/I_R |  |  |  | CDC | 322 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | _100 | 100 |  | I_R | [17 empty] | 2-8F | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.11KV_100_A1 | 11KV 100 R相AMP | TIE | D04/11/100/I_R |  |  |  | CDC | 323 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | _100 | 100 |  | I_S | [17 empty] | 2-90 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.11KV_100_A2 | 11KV 100 S相AMP | TIE | D04/11/100/I_S |  |  |  | CDC | 324 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | _100 | 100 |  | I_T | [17 empty] | 2-91 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.11KV_100_A3 | 11KV 100 T相AMP | TIE | D04/11/100/I_T |  |  |  | CDC | 325 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | _200 | 200 |  | I_R | [17 empty] | 2-B1 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.11KV_200_A1 | 11KV 200 R相AMP | TIE | D04/11/200/I_R |  |  |  | CDC | 326 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | _200 | 200 |  | I_S | [17 empty] | 2-B2 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.11KV_200_A2 | 11KV 200 S相AMP | TIE | D04/11/200/I_S |  |  |  | CDC | 327 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 11 | 11kV | _200 | 200 |  | I_T | [17 empty] | 2-B3 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.11KV_200_A3 | 11KV 200 T相AMP | TIE | D04/11/200/I_T |  |  |  | CDC | 328 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MW | [17 empty] | 1-AE | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | D04/11/310/KW |  |  |  | CDC | 329 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D04 | 豐華DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVAR | [17 empty] | 1-AF | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | D04/11/310/KVAR |  |  |  | CDC | 330 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D04 | 豐華DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_R | [17 empty] | 1-B0 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | D04/11/310/I_R |  |  |  | CDC | 331 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_S | [17 empty] | 1-B1 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | D04/11/310/I_S |  |  |  | CDC | 332 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_T | [17 empty] | 1-B2 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | D04/11/310/I_T |  |  |  | CDC | 333 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 0 |  | 1DTR | #1DTR |  | OilTemp | [17 empty] | 1-9D | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.#1DTR_OIL | #1DTR 油溫 | MTR | D04//1DTR/OilTemp |  |  |  | CDC | 334 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D04 | 豐華DS | 0 |  | 1DTR(A) | #1DTR(A) |  | CoilTemp | [17 empty] | 1-9E | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | D04//1DTR(A)/CoilTemp |  |  |  | CDC | 335 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D04 | 豐華DS | 0 |  | 1DTR(A) | #1DTR(A) |  | TapPosMv | [17 empty] | 1-A0 |  | 1-4B |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 豐華DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | D04//1DTR(A)/TapPosMv |  |  |  | CDC | 336 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D04 | 豐華DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MW | [17 empty] | 1-CF | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | D04/11/320/KW |  |  |  | CDC | 337 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D04 | 豐華DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVAR | [17 empty] | 1-D0 | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | D04/11/320/KVAR |  |  |  | CDC | 338 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D04 | 豐華DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_R | [17 empty] | 1-D1 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | D04/11/320/I_R |  |  |  | CDC | 339 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_S | [17 empty] | 1-D2 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | D04/11/320/I_S |  |  |  | CDC | 340 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_T | [17 empty] | 1-D3 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | D04/11/320/I_T |  |  |  | CDC | 341 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 0 |  | 1DTR(B) | #1DTR(B) |  | CoilTemp | [17 empty] | 1-9F | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | D04//1DTR(B)/CoilTemp |  |  |  | CDC | 342 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D04 | 豐華DS | 0 |  | 1DTR(B) | #1DTR(B) |  | TapPosMv | [17 empty] | 1-A1 |  | 1-4D |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 豐華DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | D04//1DTR(B)/TapPosMv |  |  |  | CDC | 343 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D04 | 豐華DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MW | [17 empty] | 1-EE | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | D04/11/330/KW |  |  |  | CDC | 344 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D04 | 豐華DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVAR | [17 empty] | 1-EF | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | D04/11/330/KVAR |  |  |  | CDC | 345 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D04 | 豐華DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_R | [17 empty] | 1-F0 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | D04/11/330/I_R |  |  |  | CDC | 346 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_S | [17 empty] | 1-F1 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | D04/11/330/I_S |  |  |  | CDC | 347 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_T | [17 empty] | 1-F2 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | D04/11/330/I_T |  |  |  | CDC | 348 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 0 |  | 2DTR | #2DTR |  | OilTemp | [17 empty] | 1-A2 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.#2DTR_OIL | #2DTR 油溫 | MTR | D04//2DTR/OilTemp |  |  |  | CDC | 349 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D04 | 豐華DS | 0 |  | 2DTR(A) | #2DTR(A) |  | CoilTemp | [17 empty] | 1-A3 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | D04//2DTR(A)/CoilTemp |  |  |  | CDC | 350 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D04 | 豐華DS | 0 |  | 2DTR(A) | #2DTR(A) |  | TapPosMv | [17 empty] | 1-A5 |  | 1-4F |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 豐華DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | D04//2DTR(A)/TapPosMv |  |  |  | CDC | 351 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D04 | 豐華DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MW | [17 empty] | 2-92 | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | D04/11/340/KW |  |  |  | CDC | 352 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D04 | 豐華DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVAR | [17 empty] | 2-93 | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | D04/11/340/KVAR |  |  |  | CDC | 353 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D04 | 豐華DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_R | [17 empty] | 2-94 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | D04/11/340/I_R |  |  |  | CDC | 354 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_S | [17 empty] | 2-95 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | D04/11/340/I_S |  |  |  | CDC | 355 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_T | [17 empty] | 2-96 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | D04/11/340/I_T |  |  |  | CDC | 356 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 0 |  | 2DTR(B) | #2DTR(B) |  | CoilTemp | [17 empty] | 1-A4 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | D04//2DTR(B)/CoilTemp |  |  |  | CDC | 357 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D04 | 豐華DS | 0 |  | 2DTR(B) | #2DTR(B) |  | TapPosMv | [17 empty] | 1-A6 |  | 1-51 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 豐華DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | D04//2DTR(B)/TapPosMv |  |  |  | CDC | 358 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D04 | 豐華DS | 0 |  | 3DTR | #3DTR二次側 |  | MW | [17 empty] | 2-B4 | [5 empty] | MW_-108_108(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.#3DTR_MW | #3DTR二次側 MW | MTR | D04/22/350/KW |  |  |  | CDC | 359 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D04 | 豐華DS | 0 |  | 3DTR | #3DTR二次側 |  | MVAR | [17 empty] | 2-B5 | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.#3DTR_MVAR | #3DTR二次側 MVAR | MTR | D04/22/350/KVAR |  |  |  | CDC | 360 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D04 | 豐華DS | 0 |  | 3DTR | #3DTR二次側 |  | I_R | [17 empty] | 2-B6 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.#3DTR_A1 | #3DTR二次側 R相AMP | MTR | D04/22/350/I_R |  |  |  | CDC | 361 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 0 |  | 3DTR | #3DTR二次側 |  | I_S | [17 empty] | 2-B7 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.#3DTR_A2 | #3DTR二次側 S相AMP | MTR | D04/22/350/I_S |  |  |  | CDC | 362 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 0 |  | 3DTR | #3DTR二次側 |  | I_T | [17 empty] | 2-B8 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.#3DTR_A3 | #3DTR二次側 T相AMP | MTR | D04/22/350/I_T |  |  |  | CDC | 363 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 0 |  | 3DTR | #3DTR |  | OilTemp | [17 empty] | 1-A7 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.#3DTR_OIL | #3DTR 油溫 | MTR | D04//3DTR/OilTemp |  |  |  | CDC | 364 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D04 | 豐華DS | 0 |  | 3DTR | #3DTR |  | CoilTemp | [17 empty] | 1-A8 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.#3DTR_COIL | #3DTR 線溫 | MTR | D04//3DTR/CoilTemp |  |  |  | CDC | 365 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D04 | 豐華DS | 0 |  | 3DTR | #3DTR |  | TapPosMv | [17 empty] | 1-A9 |  | 1-53 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 豐華DS.#3DTR_TAP | #3DTR OLTC TAP | MTR | D04//3DTR/TapPosMv |  |  |  | CDC | 366 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D04 | 豐華DS | 0 |  | AI | AI90%參考點 |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.AI_ADCH1 | AI90%參考點 ADCH1 | OTHER | D04/0/RTU/ADCH1 |  |  |  | CDC | 367 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 0 |  | AI | AI90%參考點 |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.AI_ADCH3 | AI90%參考點 ADCH3 | OTHER |  |  |  |  | CDC | 368 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 0 |  | AI | AI90%參考點 |  | ADCH4 | [17 empty] | 2-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.AI_ADCH4 | AI90%參考點 ADCH4 | OTHER | D04/0/RTU/ADCH4 |  |  |  | CDC | 369 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 0 |  | AI | AI10%參考點 |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.AI_ADCL1 | AI10%參考點 ADCL1 | OTHER | D04/0/RTU/ADCL1 |  |  |  | CDC | 370 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 0 |  | AI | AI10%參考點 |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.AI_ADCL3 | AI10%參考點 ADCL3 | OTHER |  |  |  |  | CDC | 371 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 0 |  | AI | AI10%參考點 |  | ADCL4 | [17 empty] | 2-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.AI_ADCL4 | AI10%參考點 ADCL4 | OTHER | D04/0/RTU/ADCL4 |  |  |  | CDC | 372 | GENERICAIPoint | DS052_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 0 |  |  |  |  | DCV_N | [17 empty] | 1-9B | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.直流N電源電壓 | 直流N電源電壓 | OTHER | D04/0/StaDev/DCV_N |  |  |  | CDC | 373 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D04 | 豐華DS | 0 |  |  |  |  | DCV_P | [17 empty] | 1-9A | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.直流P電源電壓 | 直流P電源電壓 | OTHER | D04/0/StaDev/DCV_P |  |  |  | CDC | 374 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華聯電五一路(1610) |  | MW | [17 empty] | 1-94 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.1610_MW | 豐華聯電五一路 MW | LINE161 | D04/161/1610/MW |  |  |  | CDC | 375 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華聯電五一路(1610) |  | MVAR | [17 empty] | 1-95 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.1610_MVAR | 豐華聯電五一路 MVAR | LINE161 | D04/161/1610/MVAR |  |  |  | CDC | 376 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華聯電五二路(1620) |  | MW | [17 empty] | 1-96 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.1620_MW | 豐華聯電五二路 MW | LINE161 | D04/161/1620/MW |  |  |  | CDC | 377 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華聯電五二路(1620) |  | MVAR | [17 empty] | 1-97 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.1620_MVAR | 豐華聯電五二路 MVAR | LINE161 | D04/161/1620/MVAR |  |  |  | CDC | 378 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1612SHR | #2SHR |  | CoilTemp | [17 empty] | 1-C0 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.161#2SHR_COIL | 161KV #2SHR 線溫 | OTHER | D04//2SHR/OilTemp |  |  |  | CDC | 379 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D04 | 豐華DS | 161 | 161kV | 1612SHR | #2SHR |  | OilTemp | [17 empty] | 1-C1 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 豐華DS.161#2SHR_OIL | 161KV #2SHR 油溫 | OTHER | D04//2SHR/CoilTemp |  |  |  | CDC | 380 | GENERICAIPoint | DS052_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D04 | 豐華DS | 22 | 22kV | 博碩群創 | 博碩群創 |  | 博碩群創KVAR | [17 empty] | 3-98 | [5 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.博碩群創KVAR | 23KV博碩群創 KVAR | FEEDER |  |  |  |  | CDC | 381 | GENERICAIPoint | DS052_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 博碩群創 | 博碩群創 |  | 博碩群創A1 | [17 empty] | 3-99 | [5 empty] | A_-300_300(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.博碩群創A1 | 23KV博碩群創 R相AMP | FEEDER |  |  |  |  | CDC | 382 | GENERICAIPoint | DS052_L3 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 博碩群創 | 博碩群創 |  | 博碩群創A2 | [17 empty] | 3-9A | [5 empty] | A_-300_300(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.博碩群創A2 | 23KV博碩群創 S相AMP | FEEDER |  |  |  |  | CDC | 383 | GENERICAIPoint | DS052_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 博碩群創 | 博碩群創 |  | 博碩群創A3 | [17 empty] | 3-9B | [5 empty] | A_-300_300(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.博碩群創A3 | 23KV博碩群創 T相AMP | FEEDER |  |  |  |  | CDC | 384 | GENERICAIPoint | DS052_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D04 | 豐華DS | 22 | 22kV | 博碩群創 | 博碩群創(K863) |  | KV1 | [17 empty] | 3-9C | [5 empty] | kV_-18_18(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.博碩群創_KV1 | 23KV博碩群創(K863) VR | OTHER |  |  |  |  | CDC | 385 | GENERICAIPoint | DS052_L3 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D04 | 豐華DS | 22 | 22kV | 博碩群創 | 博碩群創(K863) |  | KV2 | [17 empty] | 3-9D | [5 empty] | kV_-18_18(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.博碩群創_KV2 | 23KV博碩群創(K863) VS | OTHER |  |  |  |  | CDC | 386 | GENERICAIPoint | DS052_L3 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D04 | 豐華DS | 22 | 22kV | 博碩群創 | 博碩群創(K863) |  | KV3 | [17 empty] | 3-9E | [5 empty] | kV_-18_18(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.博碩群創_KV3 | 23KV博碩群創(K863) VT | OTHER |  |  |  |  | CDC | 387 | GENERICAIPoint | DS052_L3 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D04 | 豐華DS | 22 | 22kV | 博碩群創 | 博碩群創(K863) |  | KW | [17 empty] | 3-97 | [5 empty] | KW_-18000_18000(-2000_2000) |  | DDCS4_2 | [8 empty] | 豐華DS.博碩群創_KW | 23KV博碩群創(K863) KW | OTHER |  |  |  |  | CDC | 388 | GENERICAIPoint | DS052_L3 | CDC2_AI |  | AI | [17 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 3.600000 | 0.010000
D04 | 豐華DS | 161 | 161kV | 1510 | 南科豐華紅線(1510) |  | PHA | [17 empty] | 1-00-02 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.1510_PHA | 南科豐華紅線(1510) 相間RY | LINE161 | D04/161/1510/PHA |  |  |  | CDC | 389 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1510 | 南科豐華紅線(1510) |  | GDA | [17 empty] | 1-00-03 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.1510_GDA | 南科豐華紅線(1510) 接地RY | LINE161 | D04/161/1510/GDA |  |  |  | CDC | 390 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1510 | 南科豐華紅線(1510) |  | 87A | [17 empty] | 1-00-01 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.1510_87A | 南科豐華紅線(1510) 87RY | LINE161 | D04/161/1510/87A1 |  |  |  | CDC | 391 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1510 | 南科豐華紅線(1510) |  | 87UL | [17 empty] | 1-30-02 |  | 1-16 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1510_87UL | 南科豐華紅線(1510) 87RY U/L | LINE161 | D04/161/1510/87UL |  |  |  | CDC | 392 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1510 | 南科豐華紅線(1510) |  | CB | [17 empty] | 1-00-00 |  | 1-02 | [5 empty] | 161KV_S | [8 empty] | 豐華DS.1510_CB | 1510(南科豐華紅線) CB | LINE161 | D04/161/1510/CB |  |  |  | CDC | 393 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 161 | 161kV | 1510 | 南科豐華紅線(1510) |  | 79UL | [17 empty] | 1-30-03 |  | 1-17 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1510_79UL | 南科豐華紅線(1510) 79RY U/L | LINE161 | D04/161/1510/79UL |  |  |  | CDC | 394 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1510 | 南科豐華紅線(1510) |  | DS1 | 1511 | [16 empty] | 1-3B-00 | 1-3B-01 | 1-56 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1511_DS | 1511(南科豐華紅線) DS | LINE161 | D04/161/1510/DS1 |  |  |  | CDC | 395 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1510 | 南科豐華紅線(1510) |  | DS2 | 1512 | [16 empty] | 1-3B-02 | 1-3B-03 | 1-57 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1512_DS | 1512(南科豐華紅線) DS | LINE161 | D04/161/1510/DS2 |  |  |  | CDC | 396 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1510 | 南科豐華紅線(1510) |  | DS3 | 1513 | [16 empty] | 1-3B-04 | 1-3B-05 | 1-58 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1513_DS | 1513(南科豐華紅線) DS | LINE161 | D04/161/1510/DS3 |  |  |  | CDC | 397 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1510 | 南科豐華紅線(1510) |  | E3 | 1513E | [16 empty] | 1-3B-06 | 1-3B-07 | 1-59 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1513E_ES | 1513E(南科豐華紅線) ES | LINE161 | D04/161/1510/ES3 |  |  |  | CDC | 398 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1520 | 南科豐華白線(1520) |  | PHA | [17 empty] | 1-00-06 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.1520_PHA | 南科豐華白線(1520) 相間RY | LINE161 | D04/161/1520/PHA |  |  |  | CDC | 399 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1520 | 南科豐華白線(1520) |  | GDA | [17 empty] | 1-00-07 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.1520_GDA | 南科豐華白線(1520) 接地RY | LINE161 | D04/161/1520/GDA |  |  |  | CDC | 400 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1520 | 南科豐華白線(1520) |  | CB | [17 empty] | 1-00-04 |  | 1-03 | [5 empty] | 161KV_S | [8 empty] | 豐華DS.1520_CB | 1520(南科豐華白線) CB | LINE161 | D04/161/1520/CB |  |  |  | CDC | 401 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 161 | 161kV | 1520 | 南科豐華白線(1520) |  | 79UL | [17 empty] | 1-30-05 |  | 1-19 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1520_79UL | 南科豐華白線(1520) 79RY U/L | LINE161 | D04/161/1520/79UL |  |  |  | CDC | 402 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1520 | 南科豐華白線(1520) |  | DS1 | 1521 | [16 empty] | 1-3B-08 | 1-3B-09 | 1-5A | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1521_DS | 1521(南科豐華白線) DS | LINE161 | D04/161/1520/DS1 |  |  |  | CDC | 403 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1520 | 南科豐華白線(1520) |  | DS2 | 1522 | [16 empty] | 1-3B-10 | 1-3B-11 | 1-5B | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1522_DS | 1522(南科豐華白線) DS | LINE161 | D04/161/1520/DS2 |  |  |  | CDC | 404 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1520 | 南科豐華白線(1520) |  | DS3 | 1523 | [16 empty] | 1-3B-12 | 1-3B-13 | 1-5C | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1523_DS | 1523(南科豐華白線) DS | LINE161 | D04/161/1520/DS3 |  |  |  | CDC | 405 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1520 | 南科豐華白線(1520) |  | E3 | 1523E | [16 empty] | 1-3B-14 | 1-3B-15 | 1-5D | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1523E_ES | 1523E(南科豐華白線) ES | LINE161 | D04/161/1520/ES3 |  |  |  | CDC | 406 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1530 | 豐華奇晶一線(1530) |  | PHA | [17 empty] | 1-01-03 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.1530_PHA | 豐華奇晶一線(1530) 相間RY | LINE161 | D04/161/1530/PHA |  |  |  | CDC | 407 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1530 | 豐華奇晶一線(1530) |  | GDA | [17 empty] | 1-01-04 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.1530_GDA | 豐華奇晶一線(1530) 接地RY | LINE161 | D04/161/1530/GDA |  |  |  | CDC | 408 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1530 | 豐華奇晶一線(1530)#1 |  | 87A1 | [17 empty] | 1-01-01 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.1530_87A1 | 豐華奇晶一線(1530)#1 87RY | OTHER | D04/161/1530/87A1 |  |  |  | CDC | 409 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1530 | 豐華奇晶一線(1530)#2 |  | 87A2 | [17 empty] | 1-01-02 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.1530_87A2 | 豐華奇晶一線(1530)#2 87RY | OTHER | D04/161/1530/87A2 |  |  |  | CDC | 410 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1530 | 豐華奇晶一線(1530) |  | CB | [17 empty] | 1-01-00 |  | 1-04 | [5 empty] | 161KV_S | [8 empty] | 豐華DS.1530_CB | 1530(豐華奇晶一線) CB | LINE161 | D04/161/1530/CB |  |  |  | CDC | 411 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 161 | 161kV | 1530 | 豐華奇晶一線(1530) |  | 79UL | [17 empty] | 1-30-07 |  | 1-1B | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1530_79UL | 豐華奇晶一線(1530) 79RY U/L | LINE161 | D04/161/1530/79UL |  |  |  | CDC | 412 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1530 | 豐華奇晶一線(1530) |  | DS1 | 1531 | [16 empty] | 1-3C-00 | 1-3C-01 | 1-5E | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1531_DS | 1531(豐華奇晶一線) DS | LINE161 | D04/161/1530/DS1 |  |  |  | CDC | 413 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1530 | 豐華奇晶一線(1530) |  | DS2 | 1532 | [16 empty] | 1-3C-02 | 1-3C-03 | 1-5F | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1532_DS | 1532(豐華奇晶一線) DS | LINE161 | D04/161/1530/DS2 |  |  |  | CDC | 414 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1530 | 豐華奇晶一線(1530) |  | DS3 | 1533 | [16 empty] | 1-3C-04 | 1-3C-05 | 1-60 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1533_DS | 1533(豐華奇晶一線) DS | LINE161 | D04/161/1530/DS3 |  |  |  | CDC | 415 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1530 | 豐華奇晶一線(1530) |  | E3 | 1533E | [16 empty] | 1-3C-06 | 1-3C-07 | 1-61 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1533E_ES | 1533E(豐華奇晶一線) ES | LINE161 | D04/161/1530/ES3 |  |  |  | CDC | 416 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1540 | 豐華奇晶四線(1540) |  | PHA | [17 empty] | 1-02-00 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.1540_PHA | 豐華奇晶四線(1540) 相間RY | LINE161 | D04/161/1540/PHA |  |  |  | CDC | 417 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1540 | 豐華奇晶四線(1540) |  | GDA | [17 empty] | 1-02-01 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.1540_GDA | 豐華奇晶四線(1540) 接地RY | LINE161 | D04/161/1540/GDA |  |  |  | CDC | 418 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1540 | 豐華奇晶四線(1540) |  | 87A1 | [17 empty] | 1-01-06 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.1540_87A1 | 豐華奇晶四線(1540) #1 87RY | OTHER | D04/161/1540/87A1 |  |  |  | CDC | 419 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1540 | 豐華奇晶四線(1540) |  | 87A2 | [17 empty] | 1-01-07 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.1540_87A2 | 豐華奇晶四線(1540) #2 87RY | OTHER | D04/161/1540/87A2 |  |  |  | CDC | 420 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1540 | 豐華奇晶四線(1540) |  | CB | [17 empty] | 1-01-05 |  | 1-05 | [5 empty] | 161KV_S | [8 empty] | 豐華DS.1540_CB | 1540(豐華奇晶四線) CB | LINE161 | D04/161/1540/CB |  |  |  | CDC | 421 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 161 | 161kV | 1540 | 豐華奇晶四線(1540) |  | 79UL | [17 empty] | 1-30-09 |  | 1-1D | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1540_79UL | 豐華奇晶四線(1540) 79RY U/L | LINE161 | D04/161/1540/79UL |  |  |  | CDC | 422 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1540 | 豐華奇晶四線(1540) |  | DS1 | 1541 | [16 empty] | 1-3C-08 | 1-3C-09 | 1-62 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1541_DS | 1541(豐華奇晶四線) DS | LINE161 | D04/161/1540/DS1 |  |  |  | CDC | 423 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1540 | 豐華奇晶四線(1540) |  | DS2 | 1542 | [16 empty] | 1-3C-10 | 1-3C-11 | 1-63 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1542_DS | 1542(豐華奇晶四線) DS | LINE161 | D04/161/1540/DS2 |  |  |  | CDC | 424 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1540 | 豐華奇晶四線(1540) |  | DS3 | 1543 | [16 empty] | 1-3C-12 | 1-3C-13 | 1-64 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1543_DS | 1543(豐華奇晶四線) DS | LINE161 | D04/161/1540/DS3 |  |  |  | CDC | 425 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1540 | 豐華奇晶四線(1540) |  | E3 | 1543E | [16 empty] | 1-3C-14 | 1-3C-15 | 1-65 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1543E_ES | 1543E(豐華奇晶四線) ES | LINE161 | D04/161/1540/ES3 |  |  |  | CDC | 426 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1550 | 三竹豐華一路(1550) |  | PHA | [17 empty] | 1-02-04 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.1550_PHA | 三竹豐華一路(1550) 相間RY | LINE161 | D04/161/1550/PHA |  |  |  | CDC | 427 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1550 | 三竹豐華一路(1550) |  | GDA | [17 empty] | 1-02-05 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.1550_GDA | 三竹豐華一路(1550) 接地RY | LINE161 | D04/161/1550/GDA |  |  |  | CDC | 428 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1550 | 三竹豐華一路(1550) |  | 87A | [17 empty] | 1-02-03 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.1550_87A | 三竹豐華一路(1550) 87RY | LINE161 | D04/161/1550/87A |  |  |  | CDC | 429 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1550 | 三竹豐華一路(1550) |  | 87UL | [17 empty] | 1-30-10 |  | 1-1E | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1550_87UL | 三竹豐華一路(1550) 87RY U/L | LINE161 | D04/161/1550/87UL |  |  |  | CDC | 430 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1550 | 三竹豐華一路(1550) |  | CB | [17 empty] | 1-02-02 |  | 1-06 | [5 empty] | 161KV_S | [8 empty] | 豐華DS.1550_CB | 1550(三竹豐華一路) CB | LINE161 | D04/161/1550/CB |  |  |  | CDC | 431 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 161 | 161kV | 1550 | 三竹豐華一路(1550) |  | 79UL | [17 empty] | 1-30-11 |  | 1-1F | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1550_79UL | 三竹豐華一路(1550) 79RY U/L | LINE161 | D04/161/1550/79UL |  |  |  | CDC | 432 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1550 | 三竹豐華一路(1550) |  | DS1 | 1551 | [16 empty] | 1-3D-00 | 1-3D-01 | 1-66 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1551_DS | 1551(三竹豐華一路) DS | LINE161 | D04/161/1550/DS1 |  |  |  | CDC | 433 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1550 | 三竹豐華一路(1550) |  | DS2 | 1552 | [16 empty] | 1-3D-02 | 1-3D-03 | 1-67 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1552_DS | 1552(三竹豐華一路) DS | LINE161 | D04/161/1550/DS2 |  |  |  | CDC | 434 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1550 | 三竹豐華一路(1550) |  | DS3 | 1553 | [16 empty] | 1-3D-04 | 1-3D-05 | 1-68 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1553_DS | 1553(三竹豐華一路) DS | LINE161 | D04/161/1550/DS3 |  |  |  | CDC | 435 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1550 | 三竹豐華一路(1550) |  | E3 | 1553E | [16 empty] | 1-3D-06 | 1-3D-07 | 1-69 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1553E_ES | 1553E(三竹豐華一路) ES | LINE161 | D04/161/1550/ES3 |  |  |  | CDC | 436 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1560 | 三竹豐華二路(1560) |  | PHA | [17 empty] | 1-03-00 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.1560_PHA | 三竹豐華二路(1560) 相間RY | LINE161 | D04/161/1560/PHA |  |  |  | CDC | 437 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1560 | 三竹豐華二路(1560) |  | GDA | [17 empty] | 1-03-01 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.1560_GDA | 三竹豐華二路(1560) 接地RY | LINE161 | D04/161/1560/GDA |  |  |  | CDC | 438 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1560 | 三竹豐華二路(1560) |  | 87A | [17 empty] | 1-02-07 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.1560_87A | 三竹豐華二路(1560) 87RY | LINE161 | D04/161/1560/87A |  |  |  | CDC | 439 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1560 | 三竹豐華二路(1560) |  | 87UL | [17 empty] | 1-30-12 |  | 1-20 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1560_87UL | 三竹豐華二路(1560) 87RY U/L | LINE161 | D04/161/1560/87UL |  |  |  | CDC | 440 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1560 | 三竹豐華二路(1560) |  | CB | [17 empty] | 1-02-06 |  | 1-07 | [5 empty] | 161KV_S | [8 empty] | 豐華DS.1560_CB | 1560(三竹豐華二路) CB | LINE161 | D04/161/1560/CB |  |  |  | CDC | 441 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 161 | 161kV | 1560 | 三竹豐華二路(1560) |  | 79UL | [17 empty] | 1-30-13 |  | 1-21 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1560_79UL | 三竹豐華二路(1560) 79RY U/L | LINE161 | D04/161/1560/79UL |  |  |  | CDC | 442 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1560 | 三竹豐華二路(1560) |  | DS1 | 1561 | [16 empty] | 1-3D-08 | 1-3D-09 | 1-6A | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1561_DS | 1561(三竹豐華二路) DS | LINE161 | D04/161/1560/DS1 |  |  |  | CDC | 443 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1560 | 三竹豐華二路(1560) |  | DS2 | 1562 | [16 empty] | 1-3D-10 | 1-3D-11 | 1-6B | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1562_DS | 1562(三竹豐華二路) DS | LINE161 | D04/161/1560/DS2 |  |  |  | CDC | 444 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1560 | 三竹豐華二路(1560) |  | DS3 | 1563 | [16 empty] | 1-3D-12 | 1-3D-13 | 1-6C | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1563_DS | 1563(三竹豐華二路) DS | LINE161 | D04/161/1560/DS3 |  |  |  | CDC | 445 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1560 | 三竹豐華二路(1560) |  | E3 | 1563E | [16 empty] | 1-3D-14 | 1-3D-15 | 1-6D | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1563E_ES | 1563E(三竹豐華二路) ES | LINE161 | D04/161/1560/ES3 |  |  |  | CDC | 446 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1570 | 山上安南紅線(1570) |  | PHA | [17 empty] | 1-03-04 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.1570_PHA | 山上安南紅線(1570) 相間RY | LINE161 | D04/161/1570/PHA |  |  |  | CDC | 447 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1570 | 山上安南紅線(1570) |  | GDA | [17 empty] | 1-03-05 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.1570_GDA | 山上安南紅線(1570) 接地RY | LINE161 | D04/161/1570/GDA |  |  |  | CDC | 448 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1570 | 山上安南紅線(1570) |  | CB | [17 empty] | 1-03-02 |  | 1-08 | [5 empty] | 161KV_S | [8 empty] | 豐華DS.1570_CB | 1570(山上安南紅線) CB | LINE161 | D04/161/1570/CB |  |  |  | CDC | 449 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 161 | 161kV | 1570 | 山上安南紅線(1570) |  | 79UL | [17 empty] | 1-30-15 |  | 1-23 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1570_79UL | 山上安南紅線(1570) 79RY U/L | LINE161 | D04/161/1570/79UL |  |  |  | CDC | 450 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1570 | 山上安南紅線(1570) |  | DS1 | 1571 | [16 empty] | 1-3E-00 | 1-3E-01 | 1-6E | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1571_DS | 1571(山上安南紅線) DS | LINE161 | D04/161/1570/DS1 |  |  |  | CDC | 451 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1570 | 山上安南紅線(1570) |  | DS2 | 1572 | [16 empty] | 1-3E-02 | 1-3E-03 | 1-6F | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1572_DS | 1572(山上安南紅線) DS | LINE161 | D04/161/1570/DS2 |  |  |  | CDC | 452 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1570 | 山上安南紅線(1570) |  | DS3 | 1573 | [16 empty] | 1-3E-04 | 1-3E-05 | 1-70 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1573_DS | 1573(山上安南紅線) DS | LINE161 | D04/161/1570/DS3 |  |  |  | CDC | 453 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1570 | 山上安南紅線(1570) |  | E3 | 1573E | [16 empty] | 1-3E-06 | 1-3E-07 | 1-71 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1573E_ES | 1573E(山上安南紅線) ES | LINE161 | D04/161/1570/ES3 |  |  |  | CDC | 454 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1580 | 山上鹽行白線(1580) |  | PHA | [17 empty] | 1-04-00 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.1580_PHA | 山上鹽行白線(1580) 相間RY | LINE161 | D04/161/1580/PHA |  |  |  | CDC | 455 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1580 | 山上鹽行白線(1580) |  | GDA | [17 empty] | 1-04-01 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.1580_GDA | 山上鹽行白線(1580) 接地RY | LINE161 | D04/161/1580/GDA |  |  |  | CDC | 456 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1580 | 山上鹽行白線(1580) |  | CB | [17 empty] | 1-03-06 |  | 1-09 | [5 empty] | 161KV_S | [8 empty] | 豐華DS.1580_CB | 1580(山上鹽行白線) CB | LINE161 | D04/161/1580/CB |  |  |  | CDC | 457 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 161 | 161kV | 1580 | 山上鹽行白線(1580) |  | 79UL | [17 empty] | 1-31-01 |  | 1-25 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1580_79UL | 山上鹽行白線(1580) 79RY U/L | LINE161 | D04/161/1580/79UL |  |  |  | CDC | 458 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1580 | 山上鹽行白線(1580) |  | DS1 | 1581 | [16 empty] | 1-3E-08 | 1-3E-09 | 1-72 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1581_DS | 1581(山上鹽行白線) DS | LINE161 | D04/161/1580/DS1 |  |  |  | CDC | 459 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1580 | 山上鹽行白線(1580) |  | DS2 | 1582 | [16 empty] | 1-3E-10 | 1-3E-11 | 1-73 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1582_DS | 1582(山上鹽行白線) DS | LINE161 | D04/161/1580/DS2 |  |  |  | CDC | 460 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1580 | 山上鹽行白線(1580) |  | DS3 | 1583 | [16 empty] | 1-3E-12 | 1-3E-13 | 1-74 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1583_DS | 1583(山上鹽行白線) DS | LINE161 | D04/161/1580/DS3 |  |  |  | CDC | 461 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1580 | 山上鹽行白線(1580) |  | E3 | 1583E | [16 empty] | 1-3E-14 | 1-3E-15 | 1-75 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1583E_ES | 1583E(山上鹽行白線) ES | LINE161 | D04/161/1580/ES3 |  |  |  | CDC | 462 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 11 | 11kV | K811 | 豐11線(K811) |  | PHA | [17 empty] | 1-10-01 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K811_PHA | 11KV豐11線(K811) 相間RY | FEEDER | D04/11/K811/PHA |  |  |  | CDC | 463 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K811 | 豐11線(K811) |  | GDA | [17 empty] | 1-10-02 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K811_GDA | 11KV豐11線(K811) 接地RY | FEEDER | D04/11/K811/GDA |  |  |  | CDC | 464 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K811 | 豐11線(K811) 79RY |  | 79UL | [17 empty] | 2-38-00 |  | 2-3E | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K811_79UL | 11KV豐11線(K811) 79RY U/L | FEEDER | D04/11/K811/79UL |  |  |  | CDC | 465 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K811_LCO | 豐11線(K811) LCO |  | TapPosMv | [17 empty] | 2-38-01 |  | 2-3F | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K811_LCO_TAP | 11KV豐11線(K811) LCO TAP | FEEDER |  |  |  |  | CDC | 466 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D04 | 豐華DS | 11 | 11kV | K811 | K8(11KV豐11線) |  | CB | [17 empty] | 1-10-00 |  | 1-31 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K811_CB | K811(11KV豐11線) CB | FEEDER | D04/11/K811/CB |  |  |  | CDC | 467 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K812 | 豐12線(K812) |  | PHA | [17 empty] | 1-10-04 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K812_PHA | 11KV豐12線(K812) 相間RY | FEEDER | D04/11/K812/PHA |  |  |  | CDC | 468 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K812 | 豐12線(K812) |  | GDA | [17 empty] | 1-10-05 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K812_GDA | 11KV豐12線(K812) 接地RY | FEEDER | D04/11/K812/GDA |  |  |  | CDC | 469 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K812 | 豐12線(K812) 79RY |  | 79UL | [17 empty] | 2-38-02 |  | 2-40 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K812_79UL | 11KV豐12線(K812) 79RY U/L | FEEDER | D04/11/K812/79UL |  |  |  | CDC | 470 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K812_LCO | 豐12線(K812) LCO |  | TapPosMv | [17 empty] | 2-38-03 |  | 2-41 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K812_LCO_TAP | 11KV豐12線(K812) LCO TAP | FEEDER |  |  |  |  | CDC | 471 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D04 | 豐華DS | 11 | 11kV | K812 | K812(11KV豐12線) |  | CB | [17 empty] | 1-10-03 |  | 1-32 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K812_CB | K812(11KV豐12線) CB | FEEDER | D04/11/K812/CB |  |  |  | CDC | 472 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K813 | 豐13線(K813) |  | PHA | [17 empty] | 1-10-07 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K813_PHA | 11KV豐13線(K813) 相間RY | FEEDER | D04/11/K813/PHA |  |  |  | CDC | 473 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K813 | 豐13線(K813) |  | GDA | [17 empty] | 1-11-00 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K813_GDA | 11KV豐13線(K813) 接地RY | FEEDER | D04/11/K813/GDA |  |  |  | CDC | 474 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K813 | 豐13線(K813) 79RY |  | 79UL | [17 empty] | 2-38-04 |  | 2-42 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K813_79UL | 11KV豐13線(K813) 79RY U/L | FEEDER | D04/11/K813/79UL |  |  |  | CDC | 475 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K813_LCO | 豐13線(K813) LCO |  | TapPosMv | [17 empty] | 2-38-05 |  | 2-43 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K813_LCO_TAP | 11KV豐13線(K813) LCO TAP | FEEDER |  |  |  |  | CDC | 476 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D04 | 豐華DS | 11 | 11kV | K813 | K813(11KV豐13線) |  | CB | [17 empty] | 1-10-06 |  | 1-33 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K813_CB | K813(11KV豐13線) CB | FEEDER | D04/11/K813/CB |  |  |  | CDC | 477 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K814 | 豐14線(K814) |  | PHA | [17 empty] | 1-11-02 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K814_PHA | 11KV豐14線(K814) 相間RY | FEEDER | D04/11/K814/PHA |  |  |  | CDC | 478 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K814 | 豐14線(K814) |  | GDA | [17 empty] | 1-11-03 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K814_GDA | 11KV豐14線(K814) 接地RY | FEEDER | D04/11/K814/GDA |  |  |  | CDC | 479 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K814 | 豐14線(K814) 79RY |  | 79UL | [17 empty] | 2-38-06 |  | 2-44 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K814_79UL | 11KV豐14線(K814) 79RY U/L | FEEDER | D04/11/K814/79UL |  |  |  | CDC | 480 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K814_LCO | 豐14線(K814) LCO |  | TapPosMv | [17 empty] | 2-38-07 |  | 2-45 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K814_LCO_TAP | 11KV豐14線(K814) LCO TAP | FEEDER |  |  |  |  | CDC | 481 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D04 | 豐華DS | 11 | 11kV | K814 | K814(11KV豐14線) |  | CB | [17 empty] | 1-11-01 |  | 1-34 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K814_CB | K814(11KV豐14線) CB | FEEDER | D04/11/K814/CB |  |  |  | CDC | 482 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K815 | 豐15線(K815) |  | PHA | [17 empty] | 1-11-05 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K815_PHA | 11KV豐15線(K815) 相間RY | FEEDER | D04/11/K815/PHA |  |  |  | CDC | 483 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K815 | 豐15線(K815) |  | GDA | [17 empty] | 1-11-06 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K815_GDA | 11KV豐15線(K815) 接地RY | FEEDER | D04/11/K815/GDA |  |  |  | CDC | 484 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K815 | 豐15線(K815) 79RY |  | 79UL | [17 empty] | 2-38-08 |  | 2-46 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K815_79UL | 11KV豐15線(K815) 79RY U/L | FEEDER | D04/11/K815/79UL |  |  |  | CDC | 485 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K815_LCO | 豐15線(K815) LCO |  | TapPosMv | [17 empty] | 2-38-09 |  | 2-47 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K815_LCO_TAP | 11KV豐15線(K815) LCO TAP | FEEDER |  |  |  |  | CDC | 486 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D04 | 豐華DS | 11 | 11kV | K815 | K815(11KV豐15線) |  | CB | [17 empty] | 1-11-04 |  | 1-35 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K815_CB | K815(11KV豐15線) CB | FEEDER | D04/11/K815/CB |  |  |  | CDC | 487 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K821 | 豐21線(K821) |  | PHA | [17 empty] | 1-12-06 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K821_PHA | 11KV豐21線(K821) 相間RY | FEEDER | D04/11/K821/PHA |  |  |  | CDC | 488 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K821 | 豐21線(K821) |  | GDA | [17 empty] | 1-12-07 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K821_GDA | 11KV豐21線(K821) 接地RY | FEEDER | D04/11/K821/GDA |  |  |  | CDC | 489 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K821 | 豐21線(K821) 79RY |  | 79UL | [17 empty] | 2-38-10 |  | 2-48 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K821_79UL | 11KV豐21線(K821) 79RY U/L | FEEDER | D04/11/K821/79UL |  |  |  | CDC | 490 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K821_LCO | 豐21線(K821) LCO |  | TapPosMv | [17 empty] | 2-38-11 |  | 2-49 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K821_LCO_TAP | 11KV豐21線(K821) LCO TAP | FEEDER |  |  |  |  | CDC | 491 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D04 | 豐華DS | 11 | 11kV | K821 | K821(11KV豐21線) |  | CB | [17 empty] | 1-12-05 |  | 1-40 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K821_CB | K821(11KV豐21線) CB | FEEDER | D04/11/K821/CB |  |  |  | CDC | 492 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K822 | 豐22線(K822) |  | PHA | [17 empty] | 1-13-01 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K822_PHA | 11KV豐22線(K822) 相間RY | FEEDER | D04/11/K822/PHA |  |  |  | CDC | 493 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K822 | 豐22線(K822) |  | GDA | [17 empty] | 1-13-02 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K822_GDA | 11KV豐22線(K822) 接地RY | FEEDER | D04/11/K822/GDA |  |  |  | CDC | 494 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K822 | 豐22線(K822) 79RY |  | 79UL | [17 empty] | 2-38-12 |  | 2-4A | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K822_79UL | 11KV豐22線(K822) 79RY U/L | FEEDER | D04/11/K822/79UL |  |  |  | CDC | 495 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K822_LCO | 豐22線(K822) LCO |  | TapPosMv | [17 empty] | 2-38-13 |  | 2-4B | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K822_LCO_TAP | 11KV豐22線(K822) LCO TAP | FEEDER |  |  |  |  | CDC | 496 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D04 | 豐華DS | 11 | 11kV | K822 | K822(11KV豐22線) |  | CB | [17 empty] | 1-13-00 |  | 1-41 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K822_CB | K822(11KV豐22線) CB | FEEDER | D04/11/K822/CB |  |  |  | CDC | 497 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K823 | 豐23線(K823) |  | PHA | [17 empty] | 1-13-04 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K823_PHA | 11KV豐23線(K823) 相間RY | FEEDER | D04/11/K823/PHA |  |  |  | CDC | 498 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K823 | 豐23線(K823) |  | GDA | [17 empty] | 1-13-05 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K823_GDA | 11KV豐23線(K823) 接地RY | FEEDER | D04/11/K823/GDA |  |  |  | CDC | 499 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K823 | 豐23線(K823) 79RY |  | 79UL | [17 empty] | 2-38-14 |  | 2-4C | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K823_79UL | 11KV豐23線(K823) 79RY U/L | FEEDER | D04/11/K823/79UL |  |  |  | CDC | 500 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K823_LCO | 豐23線(K823) LCO |  | TapPosMv | [17 empty] | 2-38-15 |  | 2-4D | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K823_LCO_TAP | 11KV豐23線(K823) LCO TAP | FEEDER |  |  |  |  | CDC | 501 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D04 | 豐華DS | 11 | 11kV | K823 | K823(11KV豐23線) |  | CB | [17 empty] | 1-13-03 |  | 1-42 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K823_CB | K823(11KV豐23線) CB | FEEDER | D04/11/K823/CB |  |  |  | CDC | 502 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K824 | 豐24線(K824) |  | PHA | [17 empty] | 1-13-07 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K824_PHA | 11KV豐24線(K824) 相間RY | FEEDER | D04/11/K824/PHA |  |  |  | CDC | 503 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K824 | 豐24線(K824) |  | GDA | [17 empty] | 1-14-00 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K824_GDA | 11KV豐24線(K824) 接地RY | FEEDER | D04/11/K824/GDA |  |  |  | CDC | 504 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K824 | 豐24線(K824) 79RY |  | 79UL | [17 empty] | 2-39-00 |  | 2-4E | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K824_79UL | 11KV豐24線(K824) 79RY U/L | FEEDER | D04/11/K824/79UL |  |  |  | CDC | 505 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K824_LCO | 豐24線(K824) LCO |  | TapPosMv | [17 empty] | 2-39-01 |  | 2-4F | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K824_LCO_TAP | 11KV豐24線(K824) LCO TAP | FEEDER |  |  |  |  | CDC | 506 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D04 | 豐華DS | 11 | 11kV | K824 | K824(11KV豐24線) |  | CB | [17 empty] | 1-13-06 |  | 1-43 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K824_CB | K824(11KV豐24線) CB | FEEDER | D04/11/K824/CB |  |  |  | CDC | 507 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K825 | 豐25線(K825) |  | PHA | [17 empty] | 1-14-02 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K825_PHA | 11KV豐25線(K825) 相間RY | FEEDER | D04/11/K825/PHA |  |  |  | CDC | 508 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K825 | 豐25線(K825) |  | GDA | [17 empty] | 1-14-03 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K825_GDA | 11KV豐25線(K825) 接地RY | FEEDER | D04/11/K825/GDA |  |  |  | CDC | 509 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K825 | 豐25線(K825) 79RY |  | 79UL | [17 empty] | 2-39-02 |  | 2-50 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K825_79UL | 11KV豐25線(K825) 79RY U/L | FEEDER | D04/11/K825/79UL |  |  |  | CDC | 510 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K825_LCO | 豐25線(K825) LCO |  | TapPosMv | [17 empty] | 2-39-03 |  | 2-51 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K825_LCO_TAP | 11KV豐25線(K825) LCO TAP | FEEDER |  |  |  |  | CDC | 511 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D04 | 豐華DS | 11 | 11kV | K825 | K825(11KV豐25線) |  | CB | [17 empty] | 1-14-01 |  | 1-44 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K825_CB | K825(11KV豐25線) CB | FEEDER | D04/11/K825/CB |  |  |  | CDC | 512 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K831 | 豐31線(K831) |  | PHA | [17 empty] | 2-04-01 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K831_PHA | 11KV豐31線(K831) 相間RY | FEEDER | D04/11/K831/PHA |  |  |  | CDC | 513 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K831 | 豐31線(K831) |  | GDA | [17 empty] | 2-04-02 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K831_GDA | 11KV豐31線(K831) 接地RY | FEEDER | D04/11/K831/GDA |  |  |  | CDC | 514 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K831 | 豐31線(K831) 79RY |  | 79UL | [17 empty] | 2-39-04 |  | 2-52 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K831_79UL | 11KV豐31線(K831) 79RY U/L | FEEDER | D04/11/K831/79UL |  |  |  | CDC | 515 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K831_LCO | 豐31線(K831) LCO |  | TapPosMv | [17 empty] | 2-39-05 |  | 2-53 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K831_LCO_TAP | 11KV豐31線(K831) LCO TAP | FEEDER |  |  |  |  | CDC | 516 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D04 | 豐華DS | 11 | 11kV | K831 | K831(11KV豐31線) |  | CB | [17 empty] | 2-04-00 |  | 2-18 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K831_CB | K831(11KV豐31線) CB | FEEDER | D04/11/K831/CB |  |  |  | CDC | 517 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K832 | 豐32線(K832) |  | PHA | [17 empty] | 2-04-04 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K832_PHA | 11KV豐32線(K832) 相間RY | FEEDER | D04/11/K832/PHA |  |  |  | CDC | 518 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K832 | 豐32線(K832) |  | GDA | [17 empty] | 2-04-05 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K832_GDA | 11KV豐32線(K832) 接地RY | FEEDER | D04/11/K832/GDA |  |  |  | CDC | 519 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K832 | 豐32線(K832) 79RY |  | 79UL | [17 empty] | 2-39-06 |  | 2-54 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K832_79UL | 11KV豐32線(K832) 79RY U/L | FEEDER | D04/11/K832/79UL |  |  |  | CDC | 520 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K832_LCO | 豐32線(K832) LCO |  | TapPosMv | [17 empty] | 2-39-07 |  | 2-55 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K832_LCO_TAP | 11KV豐32線(K832) LCO TAP | FEEDER |  |  |  |  | CDC | 521 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D04 | 豐華DS | 11 | 11kV | K832 | K832(11KV豐32線) |  | CB | [17 empty] | 2-04-03 |  | 2-19 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K832_CB | K832(11KV豐32線) CB | FEEDER | D04/11/K832/CB |  |  |  | CDC | 522 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K833 | 豐33線(K833) |  | PHA | [17 empty] | 2-04-07 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K833_PHA | 11KV豐33線(K833) 相間RY | FEEDER | D04/11/K833/PHA |  |  |  | CDC | 523 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K833 | 豐33線(K833) |  | GDA | [17 empty] | 2-05-00 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K833_GDA | 11KV豐33線(K833) 接地RY | FEEDER | D04/11/K833/GDA |  |  |  | CDC | 524 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K833 | 豐33線(K833) 79RY |  | 79UL | [17 empty] | 2-39-08 |  | 2-56 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K833_79UL | 11KV豐33線(K833) 79RY U/L | FEEDER | D04/11/K833/79UL |  |  |  | CDC | 525 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K833_LCO | 豐33線(K833) LCO |  | TapPosMv | [17 empty] | 2-39-09 |  | 2-57 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K833_LCO_TAP | 11KV豐33線(K833) LCO TAP | FEEDER |  |  |  |  | CDC | 526 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D04 | 豐華DS | 11 | 11kV | K833 | K833(11KV豐33線) |  | CB | [17 empty] | 2-04-06 |  | 2-1A | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K833_CB | K833(11KV豐33線) CB | FEEDER | D04/11/K833/CB |  |  |  | CDC | 527 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K834 | 豐34線(K834) |  | PHA | [17 empty] | 2-05-02 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K834_PHA | 11KV豐34線(K834) 相間RY | FEEDER | D04/11/K834/PHA |  |  |  | CDC | 528 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K834 | 豐34線(K834) |  | GDA | [17 empty] | 2-05-03 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K834_GDA | 11KV豐34線(K834) 接地RY | FEEDER | D04/11/K834/GDA |  |  |  | CDC | 529 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K834 | 豐34線(K834) 79RY |  | 79UL | [17 empty] | 2-39-10 |  | 2-58 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K834_79UL | 11KV豐34線(K834) 79RY U/L | FEEDER | D04/11/K834/79UL |  |  |  | CDC | 530 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K834_LCO | 豐34線(K834) LCO |  | TapPosMv | [17 empty] | 2-39-11 |  | 2-59 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K834_LCO_TAP | 11KV豐34線(K834) LCO TAP | FEEDER |  |  |  |  | CDC | 531 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D04 | 豐華DS | 11 | 11kV | K834 | K834(11KV豐34線) |  | CB | [17 empty] | 2-05-01 |  | 2-1B | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K834_CB | K834(11KV豐34線) CB | FEEDER | D04/11/K834/CB |  |  |  | CDC | 532 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K835 | 豐35線(K835) |  | PHA | [17 empty] | 2-05-05 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K835_PHA | 11KV豐35線(K835) 相間RY | FEEDER | D04/11/K835/PHA |  |  |  | CDC | 533 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K835 | 豐35線(K835) |  | GDA | [17 empty] | 2-05-06 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K835_GDA | 11KV豐35線(K835) 接地RY | FEEDER | D04/11/K835/GDA |  |  |  | CDC | 534 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K835 | 豐35線(K835) 79RY |  | 79UL | [17 empty] | 2-39-12 |  | 2-5A | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K835_79UL | 11KV豐35線(K835) 79RY U/L | FEEDER | D04/11/K835/79UL |  |  |  | CDC | 535 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K835_LCO | 豐35線(K835) LCO |  | TapPosMv | [17 empty] | 2-39-13 |  | 2-5B | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K835_LCO_TAP | 11KV豐35線(K835) LCO TAP | FEEDER |  |  |  |  | CDC | 536 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D04 | 豐華DS | 11 | 11kV | K835 | K835(11KV豐35線) |  | CB | [17 empty] | 2-05-04 |  | 2-1C | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K835_CB | K835(11KV豐35線) CB | FEEDER | D04/11/K835/CB |  |  |  | CDC | 537 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K841 | 豐41線(K841) |  | PHA | [17 empty] | 2-06-06 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K841_PHA | 11KV豐41線(K841) 相間RY | FEEDER | D04/11/K841/PHA |  |  |  | CDC | 538 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K841 | 豐41線(K841) |  | GDA | [17 empty] | 2-06-07 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K841_GDA | 11KV豐41線(K841) 接地RY | FEEDER | D04/11/K841/GDA |  |  |  | CDC | 539 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K841 | 豐41線(K841) 79RY |  | 79UL | [17 empty] | 2-39-14 |  | 2-5C | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K841_79UL | 11KV豐41線(K841) 79RY U/L | FEEDER | D04/11/K841/79UL |  |  |  | CDC | 540 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K841_LCO | 豐41線(K841) LCO |  | TapPosMv | [17 empty] | 2-39-15 |  | 2-5D | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K841_LCO_TAP | 11KV豐41線(K841) LCO TAP | FEEDER |  |  |  |  | CDC | 541 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D04 | 豐華DS | 11 | 11kV | K841 | K841(11KV豐41線) |  | CB | [17 empty] | 2-06-05 |  | 2-20 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K841_CB | K841(11KV豐41線) CB | FEEDER | D04/11/K841/CB |  |  |  | CDC | 542 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K842 | 豐42線(K842) |  | PHA | [17 empty] | 2-07-01 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K842_PHA | 11KV豐42線(K842) 相間RY | FEEDER | D04/11/K842/PHA |  |  |  | CDC | 543 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K842 | 豐42線(K842) |  | GDA | [17 empty] | 2-07-02 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K842_GDA | 11KV豐42線(K842) 接地RY | FEEDER | D04/11/K842/GDA |  |  |  | CDC | 544 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K842 | 豐42線(K842) 79RY |  | 79UL | [17 empty] | 2-3A-00 |  | 2-5E | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K842_79UL | 11KV豐42線(K842) 79RY U/L | FEEDER | D04/11/K842/79UL |  |  |  | CDC | 545 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K842_LCO | 豐42線(K842) LCO |  | TapPosMv | [17 empty] | 2-3A-01 |  | 2-5F | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K842_LCO_TAP | 11KV豐42線(K842) LCO TAP | FEEDER |  |  |  |  | CDC | 546 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D04 | 豐華DS | 11 | 11kV | K842 | K842(11KV豐42線) |  | CB | [17 empty] | 2-07-00 |  | 2-21 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K842_CB | K842(11KV豐42線) CB | FEEDER | D04/11/K842/CB |  |  |  | CDC | 547 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K843 | 豐43線(K843) |  | PHA | [17 empty] | 2-07-04 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K843_PHA | 11KV豐43線(K843) 相間RY | FEEDER | D04/11/K843/PHA |  |  |  | CDC | 548 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K843 | 豐43線(K843) |  | GDA | [17 empty] | 2-07-05 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K843_GDA | 11KV豐43線(K843) 接地RY | FEEDER | D04/11/K843/GDA |  |  |  | CDC | 549 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K843 | 豐43線(K843) 79RY |  | 79UL | [17 empty] | 2-3A-02 |  | 2-60 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K843_79UL | 11KV豐43線(K843) 79RY U/L | FEEDER | D04/11/K843/79UL |  |  |  | CDC | 550 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K843_LCO | 豐43線(K843) LCO |  | TapPosMv | [17 empty] | 2-3A-03 |  | 2-61 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K843_LCO_TAP | 11KV豐43線(K843) LCO TAP | FEEDER |  |  |  |  | CDC | 551 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D04 | 豐華DS | 11 | 11kV | K843 | K843(11KV豐43線) |  | CB | [17 empty] | 2-07-03 |  | 2-22 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K843_CB | K843(11KV豐43線) CB | FEEDER | D04/11/K843/CB |  |  |  | CDC | 552 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K844 | 豐44線(K844) |  | PHA | [17 empty] | 2-07-07 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K844_PHA | 11KV豐44線(K844) 相間RY | FEEDER | D04/11/K844/PHA |  |  |  | CDC | 553 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K844 | 豐44線(K844) |  | GDA | [17 empty] | 2-08-00 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K844_GDA | 11KV豐44線(K844) 接地RY | FEEDER | D04/11/K844/GDA |  |  |  | CDC | 554 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K844 | 豐44線(K844) 79RY |  | 79UL | [17 empty] | 2-3A-04 |  | 2-62 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K844_79UL | 11KV豐44線(K844) 79RY U/L | FEEDER | D04/11/K844/79UL |  |  |  | CDC | 555 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K844_LCO | 豐44線(K844) LCO |  | TapPosMv | [17 empty] | 2-3A-05 |  | 2-63 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K844_LCO_TAP | 11KV豐44線(K844) LCO TAP | FEEDER |  |  |  |  | CDC | 556 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D04 | 豐華DS | 11 | 11kV | K844 | K844(11KV豐44線) |  | CB | [17 empty] | 2-07-06 |  | 2-23 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K844_CB | K844(11KV豐44線) CB | FEEDER | D04/11/K844/CB |  |  |  | CDC | 557 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | K845 | 豐45線(K845) |  | PHA | [17 empty] | 2-08-02 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K845_PHA | 11KV豐45線(K845) 相間RY | FEEDER | D04/11/K845/PHA |  |  |  | CDC | 558 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K845 | 豐45線(K845) |  | GDA | [17 empty] | 2-08-03 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K845_GDA | 11KV豐45線(K845) 接地RY | FEEDER | D04/11/K845/GDA |  |  |  | CDC | 559 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | K845 | 豐45線(K845) 79RY |  | 79UL | [17 empty] | 2-3A-06 |  | 2-64 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K845_79UL | 11KV豐45線(K845) 79RY U/L | FEEDER | D04/11/K845/79UL |  |  |  | CDC | 560 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 11 | 11kV | K845_LCO | 豐45線(K845) LCO |  | TapPosMv | [17 empty] | 2-3A-07 |  | 2-65 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K845_LCO_TAP | 11KV豐45線(K845) LCO TAP | FEEDER |  |  |  |  | CDC | 561 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D04 | 豐華DS | 11 | 11kV | K845 | K845(11KV豐45線) |  | CB | [17 empty] | 2-08-01 |  | 2-24 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K845_CB | K845(11KV豐45線) CB | FEEDER | D04/11/K845/CB |  |  |  | CDC | 562 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 22 | 22kV | K861 | 豐61線(K861) |  | PHA | [17 empty] | 2-09-06 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K861_PHA | 23KV豐61線(K861) 相間RY | FEEDER | D04/22/K861/PHA |  |  |  | CDC | 563 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | K861 | 豐61線(K861) |  | GDA | [17 empty] | 2-09-07 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K861_GDA | 23KV豐61線(K861) 接地RY | FEEDER | D04/22/K861/GDA |  |  |  | CDC | 564 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | K861 | 豐61線(K861) 79RY |  | 79UL | [17 empty] | 2-3A-08 |  | 2-66 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K861_79UL | 23KV豐61線(K861) 79RY U/L | FEEDER | D04/22/K861/79UL |  |  |  | CDC | 565 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 22 | 22kV | K861_LCO | 豐61線(K861) LCO |  | TapPosMv | [17 empty] | 2-3A-09 |  | 2-67 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K861_LCO_TAP | 23KV豐61線(K861) LCO TAP | FEEDER |  |  |  |  | CDC | 566 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D04 | 豐華DS | 22 | 22kV | K861 | K861(23KV豐61線) |  | CB | [17 empty] | 2-09-05 |  | 2-26 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K861_CB | K861(23KV豐61線) CB | FEEDER | D04/22/K861/CB |  |  |  | CDC | 567 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 22 | 22kV | K862 | 豐62線(K862) |  | PHA | [17 empty] | 2-0A-01 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K862_PHA | 23KV豐62線(K862) 相間RY | FEEDER | D04/22/K862/PHA |  |  |  | CDC | 568 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | K862 | 豐62線(K862) |  | GDA | [17 empty] | 2-0A-02 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K862_GDA | 23KV豐62線(K862) 接地RY | FEEDER | D04/22/K862/GDA |  |  |  | CDC | 569 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | K862 | 豐62線(K862) 79RY |  | 79UL | [17 empty] | 2-3A-10 |  | 2-68 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K862_79UL | 23KV豐62線(K862) 79RY U/L | FEEDER | D04/22/K862/79UL |  |  |  | CDC | 570 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 22 | 22kV | K862_LCO | 豐62線(K862) LCO |  | TapPosMv | [17 empty] | 2-3A-11 |  | 2-69 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K862_LCO_TAP | 23KV豐62線(K862) LCO TAP | FEEDER |  |  |  |  | CDC | 571 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D04 | 豐華DS | 22 | 22kV | K862 | K862(23KV豐62線) |  | CB | [17 empty] | 2-0A-00 |  | 2-27 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K862_CB | K862(23KV豐62線) CB | FEEDER | D04/22/K862/CB |  |  |  | CDC | 572 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 22 | 22kV | K863 | 豐63線(K863) |  | PHA | [17 empty] | 2-0A-04 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K863_PHA | 23KV豐63線(K863) 相間RY | FEEDER | D04/22/K863/PHA |  |  |  | CDC | 573 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | K863 | 豐63線(K863) |  | GDA | [17 empty] | 2-0A-05 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K863_GDA | 23KV豐63線(K863) 接地RY | FEEDER | D04/22/K863/GDA |  |  |  | CDC | 574 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | K863 | 豐63線(K863) 79RY |  | 79UL | [17 empty] | 2-3A-12 |  | 2-6A | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K863_79UL | 23KV豐63線(K863) 79RY U/L | FEEDER | D04/22/K863/79UL |  |  |  | CDC | 575 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 22 | 22kV | K863_LCO | 豐63線(K863) LCO |  | TapPosMv | [17 empty] | 2-3A-13 |  | 2-6B | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K863_LCO_TAP | 23KV豐63線(K863) LCO TAP | FEEDER |  |  |  |  | CDC | 576 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D04 | 豐華DS | 22 | 22kV | K863 | K863(23KV豐63線) |  | CB | [17 empty] | 2-0A-03 |  | 2-28 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K863_CB | K863(23KV豐63線) CB | FEEDER | D04/22/K863/CB |  |  |  | CDC | 577 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 22 | 22kV | K864 | 豐64線(K864) |  | PHA | [17 empty] | 2-0A-07 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K864_PHA | 23KV豐64線(K864) 相間RY | FEEDER | D04/22/K864/PHA |  |  |  | CDC | 578 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | K864 | 豐64線(K864) |  | GDA | [17 empty] | 2-0B-00 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K864_GDA | 23KV豐64線(K864) 接地RY | FEEDER | D04/22/K864/GDA |  |  |  | CDC | 579 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | K864 | 豐64線(K864) 79RY |  | 79UL | [17 empty] | 2-3A-14 |  | 2-6C | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K864_79UL | 23KV豐64線(K864) 79RY U/L | FEEDER | D04/22/K864/79UL |  |  |  | CDC | 580 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 22 | 22kV | K864_LCO | 豐64線(K864) LCO |  | TapPosMv | [17 empty] | 2-3A-15 |  | 2-6D | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K864_LCO_TAP | 23KV豐64線(K864) LCO TAP | FEEDER |  |  |  |  | CDC | 581 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D04 | 豐華DS | 22 | 22kV | K864 | K864(23KV豐64線) |  | CB | [17 empty] | 2-0A-06 |  | 2-29 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K864_CB | K864(23KV豐64線) CB | FEEDER | D04/22/K864/CB |  |  |  | CDC | 582 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 22 | 22kV | K865 | 豐65線(K865) |  | PHA | [17 empty] | 2-0B-05 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K865_PHA | 23KV豐65線(K865) 相間RY | FEEDER | D04/22/K865/PHA |  |  |  | CDC | 583 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | K865 | 豐65線(K865) |  | GDA | [17 empty] | 2-0B-06 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K865_GDA | 23KV豐65線(K865) 接地RY | FEEDER | D04/22/K865/GDA |  |  |  | CDC | 584 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | K865 | 豐65線(K865) 79RY |  | 79UL | [17 empty] | 2-3B-00 |  | 2-6E | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K865_79UL | 23KV豐65線(K865) 79RY U/L | FEEDER | D04/22/K865/79UL |  |  |  | CDC | 585 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 22 | 22kV | K865_LCO | 豐65線(K865) LCO |  | TapPosMv | [17 empty] | 2-3B-01 |  | 2-6F | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K865_LCO_TAP | 23KV豐65線(K865) LCO TAP | FEEDER |  |  |  |  | CDC | 586 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D04 | 豐華DS | 22 | 22kV | K865 | K865(23KV豐65線) |  | CB | [17 empty] | 2-0B-04 |  | 2-2A | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K865_CB | K865(23KV豐65線) CB | FEEDER | D04/22/K865/CB |  |  |  | CDC | 587 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 22 | 22kV | K866 | 豐66線(K866) |  | PHA | [17 empty] | 2-0C-00 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K866_PHA | 23KV豐66線(K866) 相間RY | FEEDER | D04/22/K866/PHA |  |  |  | CDC | 588 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | K866 | 豐66線(K866) |  | GDA | [17 empty] | 2-0C-01 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K866_GDA | 23KV豐66線(K866) 接地RY | FEEDER | D04/22/K866/GDA |  |  |  | CDC | 589 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | K866 | 豐66線(K866) 79RY |  | 79UL | [17 empty] | 2-3B-02 |  | 2-70 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K866_79UL | 23KV豐66線(K866) 79RY U/L | FEEDER | D04/22/K866/79UL |  |  |  | CDC | 590 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 22 | 22kV | K866_LCO | 豐66線(K866) LCO |  | TapPosMv | [17 empty] | 2-3B-03 |  | 2-71 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K866_LCO_TAP | 23KV豐66線(K866) LCO TAP | FEEDER |  |  |  |  | CDC | 591 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D04 | 豐華DS | 22 | 22kV | K866 | K866(23KV豐66線) |  | CB | [17 empty] | 2-0B-07 |  | 2-2B | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K866_CB | K866(23KV豐66線) CB | FEEDER | D04/22/K866/CB |  |  |  | CDC | 592 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 22 | 22kV | K867 | 豐67線(K867) |  | PHA | [17 empty] | 2-0C-03 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K867_PHA | 23KV豐67線(K867) 相間RY | FEEDER | D04/22/K867/PHA |  |  |  | CDC | 593 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | K867 | 豐67線(K867) |  | GDA | [17 empty] | 2-0C-04 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K867_GDA | 23KV豐67線(K867) 接地RY | FEEDER | D04/22/K867/GDA |  |  |  | CDC | 594 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | K867 | 豐67線(K867) 79RY |  | 79UL | [17 empty] | 2-3B-04 |  | 2-72 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K867_79UL | 23KV豐67線(K867) 79RY U/L | FEEDER | D04/22/K867/79UL |  |  |  | CDC | 595 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 22 | 22kV | K867_LCO | 豐67線(K867) LCO |  | TapPosMv | [17 empty] | 2-3B-05 |  | 2-73 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K867_LCO_TAP | 23KV豐67線(K867) LCO TAP | FEEDER |  |  |  |  | CDC | 596 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D04 | 豐華DS | 22 | 22kV | K867 | K867(23KV豐67線) |  | CB | [17 empty] | 2-0C-02 |  | 2-2C | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K867_CB | K867(23KV豐67線) CB | FEEDER | D04/22/K867/CB |  |  |  | CDC | 597 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 22 | 22kV | K868 | 豐68線(K868) |  | PHA | [17 empty] | 2-0C-06 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K868_PHA | 23KV豐68線(K868) 相間RY | FEEDER | D04/22/K868/PHA |  |  |  | CDC | 598 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | K868 | 豐68線(K868) |  | GDA | [17 empty] | 2-0C-07 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.K868_GDA | 23KV豐68線(K868) 接地RY | FEEDER | D04/22/K868/GDA |  |  |  | CDC | 599 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | K868 | 豐68線(K868) 79RY |  | 79UL | [17 empty] | 2-3B-06 |  | 2-74 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K868_79UL | 23KV豐68線(K868) 79RY U/L | FEEDER | D04/22/K868/79UL |  |  |  | CDC | 600 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 22 | 22kV | K868_LCO | 豐68線(K868) LCO |  | TapPosMv | [17 empty] | 2-3B-07 |  | 2-75 | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K868_LCO_TAP | 23KV豐68線(K868) LCO TAP | FEEDER |  |  |  |  | CDC | 601 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D04 | 豐華DS | 22 | 22kV | K868 | K868(23KV豐68線) |  | CB | [17 empty] | 2-0C-05 |  | 2-2D | [5 empty] | DDCS4_2 | [8 empty] | 豐華DS.K868_CB | K868(23KV豐68線) CB | FEEDER | D04/22/K868/CB |  |  |  | CDC | 602 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 100 | TIE(100) |  | CB | [17 empty] | 2-06-02 |  | 2-16 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.100_CB | 100(TIE) CB | TIE | D04/11/100/CB |  |  |  | CDC | 603 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | 100 | TIE(100) |  | 51A | [17 empty] | 2-06-03 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.100_51A | 11KV TIE(100) 51RY | TIE | D04/11/100/SCA |  |  |  | CDC | 604 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 100 | TIE(100) |  | 51NA | [17 empty] | 2-06-04 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.100_51NA | 11KV TIE(100) 51N RY | TIE | D04/11/100/UVA |  |  |  | CDC | 605 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [17 empty] | 1-06-02 |  | 1-0E | [5 empty] | 161KV_S | [8 empty] | 豐華DS.1500_CB | 1500(TIE) CB | TIE | D04/161/1500/CB |  |  |  | CDC | 606 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 1500 | TIE(1500) |  | 50A | [17 empty] | 1-06-03 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.1500_50A | 161KV TIE(1500) 50RY | TIE | D04/161/1500/50A |  |  |  | CDC | 607 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [16 empty] | 2-31-00 | 2-31-01 | 2-06 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1501_DS | 1501(TIE) DS | TIE | D04/161/1500/DS1 |  |  |  | CDC | 608 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [16 empty] | 2-31-02 | 2-31-03 | 2-07 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1502_DS | 1502(TIE) DS | TIE | D04/161/1500/DS2 |  |  |  | CDC | 609 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 0 |  | 200 | TIE(200) |  | CB | [17 empty] | 2-08-07 |  | 2-1D | [5 empty] | ADCS_S | [8 empty] | 豐華DS.200_CB | 200(TIE) CB | TIE | D04/11/200/CB |  |  |  | CDC | 610 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | 200 | TIE(200) |  | 51A | [17 empty] | 2-09-00 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.200_51A | 11KV TIE(200) 51RY | TIE | D04/11/200/PHA |  |  |  | CDC | 611 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 200 | TIE(200) |  | 51NA | [17 empty] | 2-09-01 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.200_51NA | 11KV TIE(200) 51N RY | TIE | D04/11/200/GDA |  |  |  | CDC | 612 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 390 | #1SSTR(390) |  | CB | [17 empty] | 1-12-02 |  | 1-2E | [5 empty] | 161KV_S | [8 empty] | 豐華DS.390_CB | 390(#1SSTR) CB | OTHER | D04/11/390/CB |  |  |  | CDC | 613 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 1SSTR | #1SSTR |  | 51A | [17 empty] | 1-12-03 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.#1SSTR_51A | #1SSTR 51RY | OTHER | D04/11/390/PHA |  |  |  | CDC | 614 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1SSTR | #1SSTR |  | 51NA | [17 empty] | 1-12-04 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | D04/11/390/GDA |  |  |  | CDC | 615 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 490 | #2SSTR(490) |  | CB | [17 empty] | 2-09-02 |  | 2-1E | [5 empty] | 161KV_S | [8 empty] | 豐華DS.490_CB | 490(#2SSTR) CB | OTHER | D04/11/490/CB |  |  |  | CDC | 616 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 2SSTR | #2SSTR |  | 51A | [17 empty] | 2-09-03 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.#2SSTR_51A | #2SSTR 51RY | OTHER | D04/11/490/PHA |  |  |  | CDC | 617 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 2SSTR | #2SSTR |  | 51NA | [17 empty] | 2-09-04 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | D04/11/490/GDA |  |  |  | CDC | 618 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB | [17 empty] | 1-07-02 |  | 1-0F | [5 empty] | 161KV_S | [8 empty] | 豐華DS.1750_CB | 1750(#1DTR) CB | MTR | D04/161/1750/CB |  |  |  | CDC | 619 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 310 | #1DTR(310) |  | CB | [17 empty] | 1-08-02 |  | 1-2F | [5 empty] | ADCS_S | [8 empty] | 豐華DS.310_CB | 310(#1DTR) CB | MTR | D04/11/310/CB |  |  |  | CDC | 620 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 320 | #1DTR(320) |  | CB | [17 empty] | 1-08-05 |  | 1-3E | [5 empty] | ADCS_S | [8 empty] | 豐華DS.320_CB | 320(#1DTR) CB | MTR | D04/11/320/CB |  |  |  | CDC | 621 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 1DTR | #1DTR |  | 51A | [17 empty] | 1-07-06 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.#1DTR_51A | #1DTR 51RY | MTR | D04//1DTR/PHA |  |  |  | CDC | 622 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1DTR | #1DTR |  | 51NA | [17 empty] | 1-07-07 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.#1DTR_51NA | #1DTR 51N RY | MTR | D04//1DTR/GDA |  |  |  | CDC | 623 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1DTR | #1DTR |  | 51ZA | [17 empty] | 1-07-05 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | D04//1DTR/51ZA |  |  |  | CDC | 624 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1DTR | #1DTR |  | 87A | [17 empty] | 1-07-03 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.#1DTR_87A | #1DTR 87RY | MTR | D04//1DTR/87A |  |  |  | CDC | 625 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 310 | #1DTR(310) |  | 51A | [17 empty] | 1-08-00 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.310_51A | #1DTR二次側(310) 51RY | MTR | D04/11/310/51A |  |  |  | CDC | 626 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 320 | #1DTR(320) |  | 51A | [17 empty] | 1-08-01 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.320_51A | #1DTR二次側(320) 51RY | MTR | D04/11/320/51A |  |  |  | CDC | 627 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1DTR | #1DTR |  | 96PA | [17 empty] | 1-07-04 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | D04//1DTR/96PA |  |  |  | CDC | 628 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1DTR | #1DTR |  | 96D | [17 empty] | 1-32-01 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.#1DTR_96D | #1DTR 96D RY | MTR | D04//1DTR/96D |  |  |  | CDC | 629 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1DTR | #1DTR |  | 96P | [17 empty] | 1-32-02 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.#1DTR_96P | #1DTR 96P RY | MTR | D04//1DTR/96P |  |  |  | CDC | 630 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1DTR | #1DTR |  | 63Q | [17 empty] | 1-32-03 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.#1DTR_63Q | #1DTR 63Q RY | MTR | D04//1DTR/63Q |  |  |  | CDC | 631 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1DTR | #1DTR |  | 96B1 | [17 empty] | 1-31-15 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | D04//1DTR/96B1 |  |  |  | CDC | 632 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1DTR | #1DTR |  | 96B2 | [17 empty] | 1-32-00 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | D04//1DTR/96B2 |  |  |  | CDC | 633 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1DTR | #1DTR |  | TRA | [17 empty] | 1-32-05 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.#1DTR_TRA | #1DTR 重故障 | MTR | D04//1DTR/TRA |  |  |  | CDC | 634 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1DTR | #1DTR |  | TRF | [17 empty] | 1-32-04 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.#1DTR_TRF | #1DTR 輕故障 | MTR | D04//1DTR/TRF |  |  |  | CDC | 635 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1DTR(A) | #1DTR(A) |  | SupLocal | [17 empty] | 1-31-11 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | D04//1DTR(A)/SupLocal |  |  |  | CDC | 636 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D04 | 豐華DS | 0 |  | 1DTR(A) | #1DTR(A) |  | A_M | [17 empty] | 1-31-12 |  | 1-4A | [5 empty] | ADCS_S | [8 empty] | 豐華DS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | D04//1DTR(A)/Tap Chan |  |  |  | CDC | 637 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D04 | 豐華DS | 0 |  | 1DTR(B) | #1DTR(B) |  | SupLocal | [17 empty] | 1-31-13 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | D04//1DTR(B)/SupLocal |  |  |  | CDC | 638 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D04 | 豐華DS | 0 |  | 1DTR(B) | #1DTR(B) |  | A_M | [17 empty] | 1-31-14 |  | 1-4C | [5 empty] | ADCS_S | [8 empty] | 豐華DS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | D04//1DTR(B)/Tap Chan |  |  |  | CDC | 639 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D04 | 豐華DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 | [16 empty] | 2-31-04 | 2-31-05 | 2-08 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1751_DS | 1751(#1DTR) DS | MTR | D04/161/1750/DS1 |  |  |  | CDC | 640 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 | [16 empty] | 2-31-06 | 2-31-07 | 2-09 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1752_DS | 1752(#1DTR) DS | MTR | D04/161/1750/DS2 |  |  |  | CDC | 641 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB | [17 empty] | 1-09-00 |  | 1-10 | [5 empty] | 161KV_S | [8 empty] | 豐華DS.1760_CB | 1760(#2DTR) CB | MTR | D04/161/1760/CB |  |  |  | CDC | 642 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 330 | #2DTR(330) |  | CB | [17 empty] | 1-0A-00 |  | 1-45 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.330_CB | 330(#2DTR) CB | MTR | D04/11/330/CB |  |  |  | CDC | 643 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 340 | #2DTR(340) |  | CB | [17 empty] | 1-0A-03 |  | 1-46 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.340_CB | 340(#2DTR) CB | MTR | D04/11/340/CB |  |  |  | CDC | 644 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 2DTR | #2DTR |  | 51A | [17 empty] | 1-09-04 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.#2DTR_51A | #2DTR 51RY | MTR | D04//2DTR/PHA |  |  |  | CDC | 645 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 2DTR | #2DTR |  | 51NA | [17 empty] | 1-09-05 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.#2DTR_51NA | #2DTR 51N RY | MTR | D04//2DTR/GDA |  |  |  | CDC | 646 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 2DTR | #2DTR |  | 51ZA | [17 empty] | 1-09-03 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | D04//2DTR/51ZA |  |  |  | CDC | 647 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 2DTR | #2DTR |  | 87A | [17 empty] | 1-09-01 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.#2DTR_87A | #2DTR 87RY | MTR | D04//2DTR/87A |  |  |  | CDC | 648 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 330 | #2DTR(330) |  | 51A | [17 empty] | 1-09-06 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.330_51A | #2DTR二次側(330) 51RY | MTR | D04/11/330/51A |  |  |  | CDC | 649 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 340 | #2DTR(340) |  | 51A | [17 empty] | 1-09-07 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.340_51A | #2DTR二次側(340) 51RY | MTR | D04/11/340/51A |  |  |  | CDC | 650 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 2DTR | #2DTR |  | 96PA | [17 empty] | 1-09-02 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | D04//2DTR/96PA |  |  |  | CDC | 651 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 2DTR | #2DTR |  | 96D | [17 empty] | 1-32-13 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.#2DTR_96D | #2DTR 96D RY | MTR | D04//2DTR/96D |  |  |  | CDC | 652 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 2DTR | #2DTR |  | 96P | [17 empty] | 1-32-14 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.#2DTR_96P | #2DTR 96P RY | MTR | D04//2DTR/96P |  |  |  | CDC | 653 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 2DTR | #2DTR |  | 63Q | [17 empty] | 1-32-15 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.#2DTR_63Q | #2DTR 63Q RY | MTR | D04//2DTR/63Q |  |  |  | CDC | 654 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 2DTR | #2DTR |  | 96B1 | [17 empty] | 1-32-11 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | D04//2DTR/96B1 |  |  |  | CDC | 655 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 2DTR | #2DTR |  | 96B2 | [17 empty] | 1-32-12 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | D04//2DTR/96B2 |  |  |  | CDC | 656 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 2DTR | #2DTR |  | TRA | [17 empty] | 1-33-01 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.#2DTR_TRA | #2DTR 重故障 | MTR | D04//2DTR/TRA |  |  |  | CDC | 657 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 2DTR | #2DTR |  | TRF | [17 empty] | 1-33-00 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.#2DTR_TRF | #2DTR 輕故障 | MTR | D04//2DTR/TRF |  |  |  | CDC | 658 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 2DTR(A) | #2DTR(A) |  | SupLocal | [17 empty] | 1-32-07 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | D04//2DTR(A)/SupLocal |  |  |  | CDC | 659 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D04 | 豐華DS | 0 |  | 2DTR(A) | #2DTR(A) |  | A_M | [17 empty] | 1-32-08 |  | 1-4E | [5 empty] | ADCS_S | [8 empty] | 豐華DS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | D04//2DTR(A)/Tap Chan |  |  |  | CDC | 660 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D04 | 豐華DS | 0 |  | 2DTR(B) | #2DTR(B) |  | SupLocal | [17 empty] | 1-32-09 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | D04//2DTR(B)/SupLocal |  |  |  | CDC | 661 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D04 | 豐華DS | 0 |  | 2DTR(B) | #2DTR(B) |  | A_M | [17 empty] | 1-32-10 |  | 1-50 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | D04//2DTR(B)/Tap Chan |  |  |  | CDC | 662 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D04 | 豐華DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 | [16 empty] | 2-31-08 | 2-31-09 | 2-0A | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1761_DS | 1761(#2DTR) DS | MTR | D04/161/1760/DS1 |  |  |  | CDC | 663 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 | [16 empty] | 2-31-10 | 2-31-11 | 2-0B | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1762_DS | 1762(#2DTR) DS | MTR | D04/161/1760/DS2 |  |  |  | CDC | 664 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB | [17 empty] | 1-0A-06 |  | 1-11 | [5 empty] | 161KV_S | [8 empty] | 豐華DS.1770_CB | 1770(#3DTR) CB | MTR | D04/161/1770/CB |  |  |  | CDC | 665 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 350 | #3DTR(350) |  | CB | [17 empty] | 1-0B-05 |  | 1-47 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.350_CB | 350(#3DTR) CB | MTR | D04/22/350/CB |  |  |  | CDC | 666 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 3DTR | #3DTR |  | 51A | [17 empty] | 1-0B-02 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.#3DTR_51A | #3DTR 51RY | MTR | D04//3DTR/PHA |  |  |  | CDC | 667 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 3DTR | #3DTR |  | 51NA | [17 empty] | 1-0B-03 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.#3DTR_51NA | #3DTR 51N RY | MTR | D04//3DTR/GDA |  |  |  | CDC | 668 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 3DTR | #3DTR |  | 51ZA | [17 empty] | 1-0B-01 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.#3DTR_51ZA | #3DTR 51Z RY | MTR | D04//3DTR/51ZA |  |  |  | CDC | 669 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 3DTR | #3DTR |  | 87A | [17 empty] | 1-0A-07 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.#3DTR_87A | #3DTR 87RY | MTR | D04//3DTR/87A |  |  |  | CDC | 670 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 350 | #3DTR(350) |  | 51A | [17 empty] | 1-0B-04 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.350_51A | #3DTR二次側(350) 51RY | MTR | D04/22/350/51A |  |  |  | CDC | 671 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 3DTR | #3DTR |  | 96PA | [17 empty] | 1-0B-00 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.#3DTR_96PA | #3DTR 機械保護動作 | MTR | D04//3DTR/96PA |  |  |  | CDC | 672 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 3DTR | #3DTR |  | 96D | [17 empty] | 1-33-07 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.#3DTR_96D | #3DTR 96D RY | MTR | D04//3DTR/96D |  |  |  | CDC | 673 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 3DTR | #3DTR |  | 96P | [17 empty] | 1-33-08 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.#3DTR_96P | #3DTR 96P RY | MTR | D04//3DTR/96P |  |  |  | CDC | 674 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 3DTR | #3DTR |  | 63Q | [17 empty] | 1-33-09 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.#3DTR_63Q | #3DTR 63Q RY | MTR | D04//3DTR/63Q |  |  |  | CDC | 675 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 3DTR | #3DTR |  | 96B1 | [17 empty] | 1-33-05 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.#3DTR_96B1 | #3DTR 96B1 RY | MTR | D04//3DTR/96B1 |  |  |  | CDC | 676 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 3DTR | #3DTR |  | 96B2 | [17 empty] | 1-33-06 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.#3DTR_96B2 | #3DTR 96B2 RY | MTR | D04//3DTR/96B2 |  |  |  | CDC | 677 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 3DTR | #3DTR |  | TRA | [17 empty] | 1-33-11 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.#3DTR_TRA | #3DTR 重故障 | MTR | D04//3DTR/TRA |  |  |  | CDC | 678 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 3DTR | #3DTR |  | TRF | [17 empty] | 1-33-10 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.#3DTR_TRF | #3DTR 輕故障 | MTR | D04//3DTR/TRF |  |  |  | CDC | 679 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 3DTR | #3DTR |  | SupLocal | [17 empty] | 1-33-03 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.#3DTR_S/L | #3DTR OLTC S/L | MTR | D04//3DTR/SupLocal |  |  |  | CDC | 680 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D04 | 豐華DS | 0 |  | 3DTR | #3DTR |  | A_M | [17 empty] | 1-33-04 |  | 1-52 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.#3DTR_A/M | #3DTR OLTC A/M | MTR | D04//3DTR/Tap Chan |  |  |  | CDC | 681 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D04 | 豐華DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 | [16 empty] | 2-31-12 | 2-31-13 | 2-0C | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1771_DS | 1771(#3DTR) DS | MTR | D04/161/1770/DS1 |  |  |  | CDC | 682 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 | [16 empty] | 2-31-14 | 2-31-15 | 2-0D | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1772_DS | 1772(#3DTR) DS | MTR | D04/161/1770/DS2 |  |  |  | CDC | 683 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-11-07 |  | 1-30 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.210_CB | 210(11KV #1SC) CB | SC | D04/11/210/CB |  |  |  | CDC | 684 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-12-00 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.210_SCA | 11KV #1SC 51,51N RY | SC | D04/11/210/SCA |  |  |  | CDC | 685 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-12-01 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | D04/11/210/UVA |  |  |  | CDC | 686 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | 210 | #1SC(210) |  | LBS | [17 empty] | 2-32-04 | 2-32-05 | 2-12 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.210_LBS | 210(11KV #1SC) LBS | SC | D04/22/210/LBS |  |  |  | CDC | 687 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 1-14-04 |  | 1-3F | [5 empty] | ADCS_S | [8 empty] | 豐華DS.220_CB | 220(11KV #2SC) CB | SC | D04/11/220/CB |  |  |  | CDC | 688 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 1-14-05 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.220_SCA | 11KV #2SC 51,51N RY | SC | D04/11/220/SCA |  |  |  | CDC | 689 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 1-14-06 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | D04/11/220/UVA |  |  |  | CDC | 690 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | 220 | #2SC(220) |  | LBS | [17 empty] | 2-32-06 | 2-32-07 | 2-13 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.220_LBS | 220(11KV #2SC) LBS | SC | D04/22/220/LBS |  |  |  | CDC | 691 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 11 | 11kV | 230 | #3SC(230) |  | CB | [17 empty] | 2-05-07 |  | 2-17 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.230_CB | 230(11KV #3SC) CB | SC | D04/11/230/CB |  |  |  | CDC | 692 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | 230 | #3SC(230) |  | SCA | [17 empty] | 2-06-00 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.230_SCA | 11KV #3SC 51,51N RY | SC | D04/11/230/SCA |  |  |  | CDC | 693 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | 230 | #3SC(230) |  | UVA | [17 empty] | 2-06-01 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | D04/11/230/UVA |  |  |  | CDC | 694 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | 230 | #3SC(230) |  | LBS | [17 empty] | 2-32-08 | 2-32-09 | 2-14 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.230_LBS | 230(11KV #3SC) LBS | SC | D04/22/230/LBS |  |  |  | CDC | 695 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 11 | 11kV | 240 | #4SC(240) |  | CB | [17 empty] | 2-08-04 |  | 2-1F | [5 empty] | ADCS_S | [8 empty] | 豐華DS.240_CB | 240(11KV #4SC) CB | SC | D04/11/240/CB |  |  |  | CDC | 696 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 11 | 11kV | 240 | #4SC(240) |  | SCA | [17 empty] | 2-08-05 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.240_SCA | 11KV #4SC 51,51N RY | SC | D04/11/240/SCA |  |  |  | CDC | 697 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | 240 | #4SC(240) |  | UVA | [17 empty] | 2-08-06 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.240_UVA | 11KV #4SC 27RY(欠壓) | SC | D04/11/240/UVA |  |  |  | CDC | 698 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | 240 | #4SC(240) |  | LBS | [17 empty] | 2-32-10 | 2-32-11 | 2-15 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.240_LBS | 240(11KV #4SC) LBS | SC | D04/22/240/LBS |  |  |  | CDC | 699 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 22 | 22kV | 250 | #5SC(250) |  | CB | [17 empty] | 2-0B-01 |  | 2-25 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.250_CB | 250(23KV #5SC) CB | SC | D04/22/250/CB |  |  |  | CDC | 700 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 22 | 22kV | 250 | #5SC(250) |  | SCA | [17 empty] | 2-0B-02 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.250_SCA | 23KV #5SC 51,51N RY | SC | D04/22/250/SCA |  |  |  | CDC | 701 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | 250 | #5SC(250) |  | UVA | [17 empty] | 2-0B-03 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.250_UVA | 23KV #5SC 27RY(欠壓) | SC | D04/22/250/UVA |  |  |  | CDC | 702 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | 260 | #6SC(260) |  | CB | [17 empty] | 2-0D-00 |  | 2-2E | [5 empty] | ADCS_S | [8 empty] | 豐華DS.260_CB | 260(23KV #6SC) CB | SC | D04/22/260/CB |  |  |  | CDC | 703 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 22 | 22kV | 260 | #6SC(260) |  | SCA | [17 empty] | 2-0D-01 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.260_SCA | 23KV #6SC 51,51N RY | SC | D04/22/260/SCA |  |  |  | CDC | 704 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | 260 | #6SC(260) |  | UVA | [17 empty] | 2-0D-02 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.260_UVA | 23KV #6SC 27RY(欠壓) | SC | D04/22/260/UVA |  |  |  | CDC | 705 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1611BUS | #1BUS |  | VUA | [17 empty] | 1-35-11 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | D04/161/1BUS/BUS_VUA |  |  |  | CDC | 706 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1611BUS | #1BUS |  | 87A | [17 empty] | 1-06-04 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | D04/161/1BUS/87A |  |  |  | CDC | 707 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1611BUS | #1BUS |  | 87UL | [17 empty] | 1-36-09 |  | 1-2C | [5 empty] | ADCS_S | [8 empty] | 豐華DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | D04/161/1BUS/87UL |  |  |  | CDC | 708 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1612BUS | #2BUS |  | VUA | [17 empty] | 1-35-12 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | D04/161/2BUS/BUS_VUA |  |  |  | CDC | 709 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1612BUS | #2BUS |  | 87A | [17 empty] | 1-06-05 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | D04/161/2BUS/87A |  |  |  | CDC | 710 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1612BUS | #2BUS |  | 87UL | [17 empty] | 1-36-10 |  | 1-2D | [5 empty] | ADCS_S | [8 empty] | 豐華DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | D04/161/2BUS/87UL |  |  |  | CDC | 711 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 22 | 22kV | 11_ | 11/ |  | CBA | [17 empty] | 1-36-03 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | D04/22/ComPoint/CBA |  |  |  | CDC | 712 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | 11_ | 11/ |  | CBF | [17 empty] | 1-36-04 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | D04/22/ComPoint/CBF |  |  |  | CDC | 713 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | _SC | 23/ SC |  | 60A | [17 empty] | 1-36-02 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.11KV_SC_60A | 23/11KV SC 60A | OTHER | D04/22/ComPoint/FDR_60A |  |  |  | CDC | 714 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV |  |  |  | CBA | [17 empty] | 1-35-07 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.161KV_CBA | 161KV斷路器重故障 | OTHER | D04/161/ComPoint/CBA |  |  |  | CDC | 715 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV |  |  |  | CBF | [17 empty] | 1-35-08 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | D04/161/ComPoint/CBF |  |  |  | CDC | 716 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | LINE | LINE |  | RCA | [17 empty] | 1-06-06 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | D04/161/ComPoint/RCA |  |  |  | CDC | 717 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV |  |  |  | COMT | [17 empty] | 1-35-15 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.161空壓機COMT | 161KV空壓機運轉超時警報 | OTHER | D04/161/ComPoint/COMT |  |  |  | CDC | 718 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.RTU_S/L | RTU SUPY/LOCAL | OTHER | D04/0/RTU/RTU_R_L |  |  |  | CDC | 719 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D04 | 豐華DS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.TEST_CB | TEST CB | OTHER | D04/0/RTU/Test_CB |  |  |  | CDC | 720 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  |  |  |  | Fire1 | [17 empty] | 1-34-06 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | D04/0/StaDev/Fire1 |  |  |  | CDC | 721 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  |  |  |  | Fire2 | [17 empty] | 1-34-07 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.火災警報(2) | 火災警報(2)建物-所內電源室 | OTHER | D04/0/StaDev/Fire2 |  |  |  | CDC | 722 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  |  |  |  | Fire3 | [17 empty] | 1-34-08 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.火災警報(3) | 火災警報(3)消防通風閘門 | OTHER | D04/0/StaDev/Fire3 |  |  |  | CDC | 723 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  |  |  |  | Fire4 | [17 empty] | 1-34-09 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.火災警報(4) | 火災警報(4) | OTHER |  |  |  |  | CDC | 724 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  |  |  |  | OPA | [17 empty] | 1-35-05 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | D04/0/ComPoint/OPA |  |  |  | CDC | 725 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  |  |  |  | 25PFA | [17 empty] | 2-11-05 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER | D04/0/ComPoint/25TA |  |  |  | CDC | 726 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  |  |  |  | 25TA | [17 empty] | 2-11-04 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | D04/0/ComPoint/25PFA |  |  |  | CDC | 727 | GENERICDIPoint | DS052_L2 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  |  |  |  | SUBA | [17 empty] | 1-38-05 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.其他重故障 | 變電所內其他重故障 | OTHER | D04/0/StaDev/PSA |  |  |  | CDC | 728 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  |  |  |  | SUBF | [17 empty] | 1-38-04 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.其他輕故障 | 變電所內其他輕故障 | OTHER | D04/0/StaDev/PSF |  |  |  | CDC | 729 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  |  |  |  | ACB1 | [17 empty] | 1-35-02 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | D04/0/StaDev/ACB1 |  |  |  | CDC | 730 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
D04 | 豐華DS | 0 |  |  |  |  | ACB2 | [17 empty] | 1-35-03 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | D04/0/StaDev/ACB2 |  |  |  | CDC | 731 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
D04 | 豐華DS | 0 |  |  |  |  | ACBA | [17 empty] | 1-35-10 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.所內電源ACBA | 所內電源故障警報 | OTHER | D04/0/StaDev/ACBA |  |  |  | CDC | 732 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 所內電源開關ACB | 所內電源開關ACB |  | ACBT | [17 empty] | 1-35-04 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | D04/0/StaDev/ACBT |  |  |  | CDC | 733 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D04 | 豐華DS | 0 |  |  |  |  | STUV | [17 empty] | 1-35-06 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | D04/0/StaDev/STUV |  |  |  | CDC | 734 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-35-13 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | D04/0/StaDev/CHG1 |  |  |  | CDC | 735 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  |  |  |  | DCA | [17 empty] | 1-35-09 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.直流電源DCA | 直流電源故障警報 | OTHER | D04/0/StaDev/DCA |  |  |  | CDC | 736 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  |  |  |  | DCE | [17 empty] | 1-35-14 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.直流電源DCE | 直流電源接地故障警報 | OTHER | D04/0/StaDev/DCE |  |  |  | CDC | 737 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-38-06 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | D04/0/StaDev/CHG2 |  |  |  | CDC | 738 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  |  |  |  | CommACF | [17 empty] | 1-38-07 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | D04/0/StaDev/CommACF |  |  |  | CDC | 739 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  |  |  |  | Door1 | [17 empty] | 1-34-11 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.無人化門禁(1) | 無人化門禁(1)建築物大門 | OTHER | D04/0/StaDev/Door1 |  |  |  | CDC | 740 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  |  |  |  | Door2 | [17 empty] | 1-34-12 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.無人化門禁(2) | 無人化門禁(2)控制室大門 | OTHER | D04/0/StaDev/Door2 |  |  |  | CDC | 741 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  |  |  |  | Lights1 | [17 empty] | 1-35-00 |  | 2-10 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.開關場照明(A) | 開關場照明(A) | OTHER | D04/0/StaDev/Lights1 |  |  |  | CDC | 742 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D04 | 豐華DS | 0 |  |  |  |  | Lights2 | [17 empty] | 1-35-01 |  | 2-11 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.開關場照明(B) | 開關場照明(B) | OTHER | D04/0/StaDev/Lights2 |  |  |  | CDC | 743 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D04 | 豐華DS | 0 |  | 1500TIE | 1500 |  | 50SA | [17 empty] | 1-36-11 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | D04/161/1500/50SA |  |  |  | CDC | 744 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | TEST/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1510 | 南科豐華紅線(1510) |  | 87LA | [17 empty] | 1-36-13 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.1510_87LA | 南科豐華紅線(1510)數位電驛故障 | OTHER | D04/161/1510/RYFA |  |  |  | CDC | 745 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1510 | 南科豐華紅線(1510) |  | 87LCFA | [17 empty] | 1-36-12 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.1510_87LCFA | 南科豐華紅線(1510) 87L通訊故障 | OTHER | D04/161/1510/87CFA |  |  |  | CDC | 746 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1510 | 南科豐華紅線(1510) |  | DTTA | [17 empty] | 1-0E-00 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.1510_DTTA | 南科豐華紅線(1510) 遠方遙跳 | OTHER | D04/161/1510/DTTA |  |  |  | CDC | 747 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1550 | 三竹豐華一路(1550) |  | 87LA | [17 empty] | 1-37-05 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.1550_87LA | 三竹豐華一路(1550)數位電驛故障 | OTHER | D04/161/1550/RYFA |  |  |  | CDC | 748 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1550 | 三竹豐華一路(1550) |  | 87LCFA | [17 empty] | 1-37-04 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.1550_87LCFA | 三竹豐華一路(1550) 87L通訊故障 | OTHER | D04/161/1550/87CFA |  |  |  | CDC | 749 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1560 | 三竹豐華二路(1560) |  | 87LA | [17 empty] | 1-37-07 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.1560_87LA | 三竹豐華二路(1560)數位電驛故障 | OTHER | D04/161/1560/RYFA |  |  |  | CDC | 750 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1560 | 三竹豐華二路(1560) |  | 87LCFA | [17 empty] | 1-37-06 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.1560_87LCFA | 三竹豐華二路(1560) 87L通訊故障 | OTHER | D04/161/1560/87CFA |  |  |  | CDC | 751 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | _OSCA | _OSCA |  | 1 | [17 empty] | 1-06-07 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.161KV_OSCA_1 | 161KV示波器啟動警報(1) | OTHER | D04/161/ComPoint/OSCA |  |  |  | CDC | 752 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | _OSCA | _OSCA | [19 empty] | 1-07-00 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.161KV_OSCA_2 | 161KV示波器啟動警報(2) | OTHER | D04/161/ComPoint/OSCA |  |  |  | CDC | 753 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 310 | #1DTR(310) |  | GDA | [17 empty] | 1-08-04 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.310_GDA | 310開關箱IED RY GDA | OTHER | D04/11/310/GDA |  |  |  | CDC | 754 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 310 | #1DTR(310) |  | PHA2 | [17 empty] | 1-08-03 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.310_PHA2 | 310開關箱IED RY PHA | OTHER | D04/11/310/PHA |  |  |  | CDC | 755 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 320 | #1DTR(320) |  | GDA | [17 empty] | 1-08-07 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.320_GDA | 320開關箱IED RY GDA | OTHER | D04/11/320/GDA |  |  |  | CDC | 756 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 320 | #1DTR(320) |  | PHA2 | [17 empty] | 1-08-06 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.320_PHA2 | 320開關箱IED RY PHA | OTHER | D04/11/320/PHA |  |  |  | CDC | 757 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 330 | #2DTR(330) |  | GDA | [17 empty] | 1-0A-02 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.330_GDA | 330開關箱IED RY GDA | OTHER | D04/11/330/GDA |  |  |  | CDC | 758 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 330 | #2DTR(330) |  | PHA2 | [17 empty] | 1-0A-01 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.330_PHA2 | 330開關箱IED RY PHA | OTHER | D04/11/330/PHA |  |  |  | CDC | 759 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 340 | #2DTR(340) |  | GDA | [17 empty] | 1-0A-05 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.340_GDA | 340開關箱IED RY GDA | OTHER | D04/11/340/GDA |  |  |  | CDC | 760 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 340 | #2DTR(340) |  | PHA2 | [17 empty] | 1-0A-04 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.340_PHA2 | 340開關箱IED RY PHA | OTHER | D04/11/340/PHA |  |  |  | CDC | 761 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 350 | #3DTR(350) |  | GDA | [17 empty] | 1-0B-07 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.350_GDA | 350開關箱IED RY GDA | OTHER | D04/22/350/GDA |  |  |  | CDC | 762 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 350 | #3DTR(350) |  | PHA2 | [17 empty] | 1-0B-06 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.350_PHA2 | 350開關箱IED RY PHA | OTHER | D04/22/350/PHA |  |  |  | CDC | 763 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  |  |  |  | 水位警報(1) | [17 empty] | 1-36-00 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.水位警報(1) | 地下室水位警報(1) | OTHER | D04/0/StaDev/Water1 |  |  |  | CDC | 764 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  |  |  |  | 水位警報(2) | [17 empty] | 1-36-01 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.水位警報(2) | 地下室水位警報(2) | OTHER | D04/0/StaDev/Water2 |  |  |  | CDC | 765 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  |  |  |  | 火災警報(5) | [17 empty] | 1-34-10 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.火災警報(5) | 火災警報(5) | OTHER |  |  |  |  | CDC | 766 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  |  |  |  | OilLeak1 | [17 empty] | 1-36-06 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.洩油池警報(1) | 洩油池水位警報(1) | OTHER | D04/0/StaDev/OilLeak1 |  |  |  | CDC | 767 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  |  |  |  | OilLeak2 | [17 empty] | 1-36-07 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.洩油池警報(2) | 洩油池水位警報(2) | OTHER | D04/0/StaDev/OilLeak2 |  |  |  | CDC | 768 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  |  |  |  | 通信機房溫度 | [17 empty] | 1-38-10 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.通信機房溫度 | 通訊室或控制室溫度警報 | OTHER | D04/0/StaDev/R_Temp1 |  |  |  | CDC | 769 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  |  |  |  | 無人化門禁(4) | [17 empty] | 1-34-14 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.無人化門禁(4) | 無人化門禁(4) | OTHER |  |  |  |  | CDC | 770 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  |  |  |  | 無人化門禁(5) | [17 empty] | 1-34-15 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.無人化門禁(5) | 無人化門禁(5) | OTHER |  |  |  |  | CDC | 771 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 161 | 161kV |  |  |  | OSCF | [17 empty] | 1-38-11 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | D04/161/ComPoint/OSCF |  |  |  | CDC | 772 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  |  |  |  | PMA | [17 empty] | 1-38-12 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.PMA | 電力量測表計故障 | OTHER | D04/0/StaDev/PMA |  |  |  | CDC | 773 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華聯電五一路(1610) |  | PHA | [17 empty] | 1-04-04 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.1610_PHA | 豐華聯電五一路(1610) 相間RY | LINE161 | D04/161/1610/PHA |  |  |  | CDC | 774 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華聯電五一路(1610) |  | GDA | [17 empty] | 1-04-05 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.1610_GDA | 豐華聯電五一路(1610) 接地RY | LINE161 | D04/161/1610/GDA |  |  |  | CDC | 775 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華聯電五一路(1610) |  | 87A1 | [17 empty] | 1-04-03 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.1610_87A1 | 豐華聯電五一路(1610) #1 87RY | LINE161 | D04/161/1610/87A1 |  |  |  | CDC | 776 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華聯電五一路(1610) |  | 87A2 | [17 empty] | 1-0D-02 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.1610_87A2 | 豐華聯電五一路(1610) #2 87RY | LINE161 | D04/161/1610/87A2 |  |  |  | CDC | 777 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華聯電五一路(1610) |  | CB | [17 empty] | 1-04-02 |  | 1-0A | [5 empty] | 161KV_S | [8 empty] | 豐華DS.1610_CB | 1610(豐華聯電五一路) CB | LINE161 | D04/161/1610/CB |  |  |  | CDC | 778 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華聯電五一路(1610) |  | 79UL | [17 empty] | 1-31-04 |  | 1-27 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1610_79UL | 豐華聯電五一路(1610) 79RY U/L | LINE161 | D04/161/1610/79UL |  |  |  | CDC | 779 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華聯電五一路(1610) |  | DS1 | 1611 | [16 empty] | 1-3F-00 | 1-3F-01 | 1-76 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1611_DS | 1611(豐華聯電五一路) DS | LINE161 | D04/161/1610/DS1 |  |  |  | CDC | 780 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華聯電五一路(1610) |  | DS2 | 1612 | [16 empty] | 1-3F-02 | 1-3F-03 | 1-77 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1612_DS | 1612(豐華聯電五一路) DS | LINE161 | D04/161/1610/DS2 |  |  |  | CDC | 781 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華聯電五一路(1610) |  | DS3 | 1613 | [16 empty] | 1-3F-04 | 1-3F-05 | 1-78 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1613_DS | 1613(豐華聯電五一路) DS | LINE161 | D04/161/1610/DS3 |  |  |  | CDC | 782 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華聯電五一路(1610) |  | E3 | 1613E | [16 empty] | 1-3F-06 | 1-3F-07 | 1-79 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1613E_ES | 1613E(豐華聯電五一路) ES | LINE161 | D04/161/1610/ES3 |  |  |  | CDC | 783 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華聯電五二路(1620) |  | PHA | [17 empty] | 1-05-00 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.1620_PHA | 豐華聯電五二路(1620) 相間RY | LINE161 | D04/161/1620/PHA |  |  |  | CDC | 784 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華聯電五二路(1620) |  | GDA | [17 empty] | 1-05-01 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.1620_GDA | 豐華聯電五二路(1620) 接地RY | LINE161 | D04/161/1620/GDA |  |  |  | CDC | 785 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華聯電五二路(1620) |  | 87A1 | [17 empty] | 1-04-07 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.1620_87A1 | 豐華聯電五二路(1620) #1 87RY | LINE161 | D04/161/1620/87A1 |  |  |  | CDC | 786 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華聯電五二路(1620) |  | 87A2 | [17 empty] | 1-0D-03 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.1620_87A2 | 豐華聯電五二路(1620) #2 87RY | LINE161 | D04/161/1620/87A2 |  |  |  | CDC | 787 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華聯電五二路(1620) |  | CB | [17 empty] | 1-04-06 |  | 1-0B | [5 empty] | 161KV_S | [8 empty] | 豐華DS.1620_CB | 1620(豐華聯電五二路) CB | LINE161 | D04/161/1620/CB |  |  |  | CDC | 788 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華聯電五二路(1620) |  | 79UL | [17 empty] | 1-31-07 |  | 1-29 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1620_79UL | 豐華聯電五二路(1620) 79RY U/L | LINE161 | D04/161/1620/79UL |  |  |  | CDC | 789 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華聯電五二路(1620) |  | DS2 | 1622 | [16 empty] | 1-3F-10 | 1-3F-11 | 1-7B | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1622_DS | 1622(豐華聯電五二路) DS | LINE161 | D04/161/1620/DS2 |  |  |  | CDC | 790 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華聯電五二路(1620) |  | DS3 | 1623 | [16 empty] | 1-3F-12 | 1-3F-13 | 1-7C | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1623_DS | 1623(豐華聯電五二路) DS | LINE161 | D04/161/1620/DS3 |  |  |  | CDC | 791 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華聯電五二路(1620) |  | E3 | 1623E | [16 empty] | 1-3F-14 | 1-3F-15 | 1-7D | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1623E_ES | 1623E(豐華聯電五二路) ES | LINE161 | D04/161/1620/ES3 |  |  |  | CDC | 792 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 0 |  | 1610 | 豐華聯電五一路(1610) |  | 87CFA | [17 empty] | 1-37-12 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.1610_87CFA | 豐華聯電五一路(1610)通訊故障 | OTHER | D04/161/1610/87CFA |  |  |  | CDC | 793 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1610 | 豐華聯電五一路(1610) |  | RYFA | [17 empty] | 1-37-13 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.1610_RYFA | 豐華聯電五一路(1610)電驛故障 | OTHER | D04/161/1610/RYFA |  |  |  | CDC | 794 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1620 | 豐華聯電五二路(1620) |  | 87CFA | [17 empty] | 1-37-14 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.1620_87CFA | 豐華聯電五二路(1620)通訊故障 | OTHER | D04/161/1620/87CFA |  |  |  | CDC | 795 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1620 | 豐華聯電五二路(1620) |  | RYFA | [17 empty] | 1-37-15 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.1620_RYFA | 豐華聯電五二路(1620)電驛故障 | OTHER | D04/161/1620/RYFA |  |  |  | CDC | 796 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華聯電五一路(1610) |  | 1_87UL1 | [17 empty] | 1-31-02 |  | 1-26 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1610_87UL1 | 豐華聯電五一路(1610)#1 87RY UL | LINE161 | D04/161/1610/1_87UL1 |  |  |  | CDC | 797 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華聯電五一路(1610) |  | 1_87UL2 | [17 empty] | 1-31-03 |  | 1-14 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1610_87UL2 | 豐華聯電五一路(1610)#2 87RY UL | LINE161 | D04/161/1610/1_87UL2 |  |  |  | CDC | 798 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華聯電五二路(1620) |  | 1_87UL1 | [17 empty] | 1-31-05 |  | 1-28 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1620_87UL1 | 豐華聯電五二路(1620)#1 87RY UL | LINE161 | D04/161/1620/1_87UL1 |  |  |  | CDC | 799 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華聯電五二路(1620) |  | 1_87UL2 | [17 empty] | 1-31-06 |  | 1-15 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1620_87UL2 | 豐華聯電五二路(1620)#2 87RY UL | LINE161 | D04/161/1620/1_87UL2 |  |  |  | CDC | 800 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華聯電五二路(1620) |  | DS1 | 1621 | [16 empty] | 1-3F-08 | 1-3F-09 | 1-7A | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1621_DS | 1621(豐華聯電五二路) DS | LINE161 | D04/161/1620/DS1 |  |  |  | CDC | 801 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1780 | #4DTR(1780) |  | CB | [17 empty] | 1-0C-00 |  | 1-12 | [5 empty] | 161KV_S | [8 empty] | 豐華DS.1780_CB | 1780(#4DTR) CB | MTR | D04/161/1780/CB |  |  |  | CDC | 802 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 161 | 161kV | 1780 | #4DTR(1780) |  | DS1 | 1781 | [16 empty] | 2-32-00 | 2-32-01 | 2-0E | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1781_DS | 1781(#4DTR) DS | MTR | D04/161/1780/DS1 |  |  |  | CDC | 803 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1780 | #4DTR(1780) |  | DS2 | 1782 | [16 empty] | 2-32-02 | 2-32-03 | 2-0F | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1782_DS | 1782(#4DTR) DS | MTR | D04/161/1780/DS2 |  |  |  | CDC | 804 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 0 |  |  |  |  | Burglar1 | [17 empty] | 1-34-13 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | D04/0/StaDev/Door3 |  |  |  | CDC | 805 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | 11_ | 11/ |  | LOA | [17 empty] | 1-36-05 | [7 empty] | DDCS4_2 | [8 empty] | 豐華DS.11/23KV_LOA | 11/23KV饋線復閉失敗閉鎖 | OTHER | D04/22/ComPoint/LOA |  |  |  | CDC | 806 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | _BUS | BUS |  | 87CTFA | [17 empty] | 1-38-14 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.161KV_BUS_CTFA | 161KV BUS CT回路故障 | OTHER | D04/161/ComPoint/2A5Other |  |  |  | CDC | 807 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | _BUS | BUS |  | RYFA | [17 empty] | 1-38-13 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | D04/161/ComPoint/BUS_RYFA |  |  |  | CDC | 808 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 2SHR | #2SHR |  | 161#2SHR96PA | [17 empty] | 1-06-00 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.161#2SHR96PA | 161KV #2SHR 機械保護動作 | OTHER |  |  |  |  | CDC | 809 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1612SHR | #2SHR |  | 51A | [17 empty] | 1-06-01 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.161#2SHR_51A | 161KV #2SHR 51RY | OTHER | D04/161/1960/51A |  |  |  | CDC | 810 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1612SHR | #2SHR |  | 51UL | [17 empty] | 2-3C-11 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.161#2SHR_51UL | 161KV #2SHR 51RY U/L | OTHER |  |  |  |  | CDC | 811 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1612SHR | #2SHR |  | 87A | [17 empty] | 1-05-07 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.161#2SHR_87A | 161KV #2SHR 87RY | OTHER | D04/161/1960/87A |  |  |  | CDC | 812 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1612SHR | #2SHR |  | 87UL | [17 empty] | 2-3C-10 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.161#2SHR_87UL | 161KV #2SHR 87RY U/L | OTHER |  |  |  |  | CDC | 813 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1612SHR | #2SHR |  | 96B1 | [17 empty] | 2-3D-02 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.161#2SHR_96B1 | 161KV #2SHR 96B1 RY | OTHER |  |  |  |  | CDC | 814 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1612SHR | #2SHR |  | 96B2 | [17 empty] | 2-3D-03 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.161#2SHR_96B2 | 161KV #2SHR 96B2 RY | OTHER |  |  |  |  | CDC | 815 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1612SHR | #2SHR |  | 96D | [17 empty] | 2-3D-04 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.161#2SHR_96D | 161KV #2SHR 96D RY | OTHER |  |  |  |  | CDC | 816 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1612SHR | #2SHR |  | 96P | [17 empty] | 2-3D-05 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.161#2SHR_96P | 161KV #2SHR 96P RY | OTHER |  |  |  |  | CDC | 817 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1612SHR | #2SHR |  | SHRA | [17 empty] | 2-3D-07 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.161#2SHR_SRA | 161KV #2SHR 重故障 | OTHER |  |  |  |  | CDC | 818 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1612SHR | #2SHR |  | SRF | [17 empty] | 2-3D-06 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.161#2SHR_SRF | 161KV #2SHR 輕故障 | OTHER |  |  |  |  | CDC | 819 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 161_2SHR | 161_2SHR |  | RYFA | [17 empty] | 1-38-02 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.161_2SHR_RYFA | 161KV 2SHR(1960)數位電驛故障 | OTHER | D04/161/2SHR/RYFA |  |  |  | CDC | 820 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1960 | #2SHR(1960) |  | CB | [17 empty] | 1-05-06 |  | 1-0D | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1960_CB | 1960(161KV #2SHR) CB | OTHER | D04/161/1960/CB |  |  |  | CDC | 821 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1960 | #2SHR(1960) |  | DS1 | 1961 | [16 empty] | 2-30-08 | 2-30-09 | 2-02 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1961_DS | 1961(161KV #2SHR) DS | OTHER | D04/161/1960/DS1 |  |  |  | CDC | 822 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D04 | 豐華DS | 161 | 161kV | 1960 | #2SHR(1960) |  | DS2 | 1962 | [16 empty] | 2-30-10 | 2-30-11 | 2-03 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1962_DS | 1962(161KV #2SHR) DS | OTHER | D04/161/1960/DS2 |  |  |  | CDC | 823 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 0 |  | BVS | BVS |  | RY | [17 empty] | 1-38-15 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.BVS_RY | BVS GRZ100 RY U/L | OTHER | D04/0/ComPoint/GRZ100 |  |  |  | CDC | 824 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | LOCK/USE | USE
D04 | 豐華DS | 0 |  | 1520 | 南科豐華白線(1520) |  | 87A1 | [17 empty] | 1-00-05 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.1520_87A1 | 南科豐華白線(1520)87RY1 | OTHER | D04/161/1520/87A1 |  |  |  | CDC | 825 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1520 | 南科豐華白線(1520) |  | 87A2 | [17 empty] | 1-0D-04 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.1520_87A2 | 南科豐華白線(1520)87RY2 | OTHER | D04/161/1520/87A2 |  |  |  | CDC | 826 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1520 | 南科豐華白線(1520) |  | 87CFA | [17 empty] | 1-36-14 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.1520_87CFA | 南科豐華白線(1520)87RY通訊故障 | OTHER | D04/161/1520/87CFA |  |  |  | CDC | 827 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1520 | 南科豐華白線(1520) |  | 87RY1UL | [17 empty] | 1-30-04 |  | 1-18 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1520_87RY1UL | 南科豐華白線(1520)87RY1 U/L | OTHER | D04/161/1520/87UL |  |  |  | CDC | 828 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 0 |  | 1520 | 南科豐華白線(1520) |  | 87RY2UL | [17 empty] | 1-39-00 |  | 1-13 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1520_87RY2UL | 南科豐華白線(1520)87RY2 U/L | OTHER | D04/161/1520/1_87UL2 |  |  |  | CDC | 829 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 0 |  | 1520 | 南科豐華白線(1520) |  | RYFA | [17 empty] | 1-36-15 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.1520_RYFA | 南科豐華白線(1520)數位電驛故障 | OTHER | D04/161/1520/RYFA |  |  |  | CDC | 830 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1570 | 山上安南紅線(1570) |  | 87A1 | [17 empty] | 1-03-03 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.1570_87A1 | 山上安南紅線(1570) #1 87RY | LINE161 | D04/161/1570/87A1 |  |  |  | CDC | 831 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1570 | 山上安南紅線(1570) |  | 87A2 | [17 empty] | 1-0D-05 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.1570_87A2 | 山上安南紅線(1570) #2 87RY | LINE161 | D04/161/1570/87A2 |  |  |  | CDC | 832 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1570 | 山上安南紅線(1570) |  | 1_87UL1 | [17 empty] | 1-30-14 |  | 1-22 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1570_87UL1 | 山上安南紅線(1570) #1 87RY U/L | LINE161 | D04/161/1570/87UL |  |  |  | CDC | 833 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1570 | 山上安南紅線(1570) |  | 1_87UL2 | [17 empty] | 1-39-01 |  | 1-2A | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1570_87UL2 | 山上安南紅線(1570) #2 87RY U/L | LINE161 | D04/161/1570/1_87UL2 |  |  |  | CDC | 834 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 0 |  | 1570 | 山上安南紅線(1570) |  | 87CFA | [17 empty] | 1-37-08 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.1570_87CFA | 山上安南紅線(1570)87RY通訊故障 | OTHER | D04/161/1570/87CFA |  |  |  | CDC | 835 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1570 | 山上安南紅線(1570) |  | RYFA | [17 empty] | 1-37-09 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.1570_RYFA | 山上安南紅線(1570)數位電驛故障 | OTHER | D04/161/1570/RYFA |  |  |  | CDC | 836 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1580 | 山上鹽行白線(1580) |  | 87A1 | [17 empty] | 1-03-07 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.1580_87A1 | 山上鹽行白線(1580) #1 87RY | LINE161 | D04/161/1580/87A1 |  |  |  | CDC | 837 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1580 | 山上鹽行白線(1580) |  | 87A2 | [17 empty] | 1-0D-06 | [7 empty] | 161KV_S | [8 empty] | 豐華DS.1580_87A2 | 山上鹽行白線(1580) #2 87RY | LINE161 | D04/161/1580/87A2 |  |  |  | CDC | 838 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1580 | 山上鹽行白線(1580) |  | 1_87UL1 | [17 empty] | 1-31-00 |  | 1-24 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1580_87UL1 | 山上鹽行白線(1580) #1 87RY U/L | LINE161 | D04/161/1580/87UL |  |  |  | CDC | 839 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1580 | 山上鹽行白線(1580) |  | 1_87UL2 | [17 empty] | 1-39-02 |  | 1-2B | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1580_87UL2 | 山上鹽行白線(1580) #2 87RY U/L | LINE161 | D04/161/1580/1_87UL2 |  |  |  | CDC | 840 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 0 |  | 1580 | 山上鹽行白線(1580) |  | 87CFA | [17 empty] | 1-37-10 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.1580_87CFA | 山上鹽行白線(1580)87RY通訊故障 | OTHER | D04/161/1580/87CFA |  |  |  | CDC | 841 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1580 | 山上鹽行白線(1580) |  | RYFA | [17 empty] | 1-37-11 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.1580_RYFA | 山上鹽行白線(1580)數位電驛故障 | OTHER | D04/161/1580/RYFA |  |  |  | CDC | 842 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1520 | 南科豐華白線(1520) |  | DTTA | [17 empty] | 1-0E-01 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.1520_DTTA | 南科豐華白線(1520)遠方遙跳 | OTHER | D04/161/1520/DTTA |  |  |  | CDC | 843 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 0 |  |  |  |  | GEN | [17 empty] | 1-38-03 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.GEN | 緊急發電機運轉 | OTHER | D04/0/StaDev/1A5Other |  |  |  | CDC | 844 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D04 | 豐華DS | 0 |  |  |  |  | RTUA | [17 empty] | 1-0E-03 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.RTUA | RTU發生異常 | OTHER | D04/0/RTU/RTUA |  |  |  | CDC | 845 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | OLTC | OLTC |  | OLTCA | [17 empty] | 1-38-01 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | D04/0/ComPoint/OLTC_A |  |  |  | CDC | 846 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1540 | 豐華奇晶四線(1540) |  | 87CFA | [17 empty] | 1-37-02 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.1540_87CFA | 豐華奇晶四線(1540)87RY通訊故障 | OTHER | D04/161/1540/87CFA |  |  |  | CDC | 847 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1540 | 豐華奇晶四線(1540) |  | 1_87UL1 | [17 empty] | 1-30-08 |  | 1-1C | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1540_87UL1 | 豐華奇晶四線(1540)#1 87RY U/L | OTHER | D04/161/1540/87UL |  |  |  | CDC | 848 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 0 |  | 1540 | 豐華奇晶四線(1540) |  | 1_87UL2 | [17 empty] | 1-39-03 |  | 1-36 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1540_87UL2 | 豐華奇晶四線(1540)#2 87RY U/L | OTHER | D04/161/1540/1_87UL2 |  |  |  | CDC | 849 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 0 |  | 1540 | 豐華奇晶四線(1540) |  | RYFA | [17 empty] | 1-37-03 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.1540_RYFA | 豐華奇晶四線(1540)數位電驛故障 | OTHER | D04/161/1540/RYFA |  |  |  | CDC | 850 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1530 | 豐華奇晶一線(1530) |  | 87CFA | [17 empty] | 1-37-00 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.1530_87CFA | 豐華奇晶一線(1530)87RY通訊故障 | OTHER | D04/161/1530/87CFA |  |  |  | CDC | 851 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 1530 | 豐華奇晶一線(1530) |  | 1_87UL1 | [17 empty] | 1-30-06 |  | 1-1A | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1530_87UL1 | 豐華奇晶一線(1530)#1 87RY U/L | OTHER | D04/161/1530/1_87UL1 |  |  |  | CDC | 852 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 0 |  | 1530 | 豐華奇晶一線(1530) |  | 1_87UL2 | [17 empty] | 1-39-04 |  | 1-37 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.1530_87UL2 | 豐華奇晶一線(1530)#2 87RY U/L | OTHER | D04/161/1530/1_87UL2 |  |  |  | CDC | 853 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 0 |  | 1530 | 豐華奇晶一線(1530) |  | RYFA | [17 empty] | 1-37-01 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.1530_RYFA | 豐華奇晶一線(1530)數位電驛故障 | OTHER | D04/161/1530/RYFA |  |  |  | CDC | 854 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1613DTR | #3DTR |  | DTR_86A | [17 empty] | 1-0E-06 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.161#3DTR_86A | 161KV #3DTR 86RY | OTHER |  |  |  |  | CDC | 855 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1613DTR | #3DTR |  | 187UL | [17 empty] | 1-33-02 |  | 3-0C | [5 empty] | ADCS_S | [8 empty] | 豐華DS.161#3DTR_187UL | 161KV #3DTR 187RY U/L | OTHER | D04//3DTR/1_87UL1 |  |  |  | CDC | 856 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1613DTR | #3DTR |  | 287UL | [17 empty] | 1-39-11 |  | 3-0D | [5 empty] | ADCS_S | [8 empty] | 豐華DS.161#3DTR_287UL | 161KV #3DTR 287RY U/L | OTHER | D04//3DTR/1_87UL2 |  |  |  | CDC | 857 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1613DTR | #3DTR |  | 51Z_UL | [17 empty] | 1-39-12 |  | 2-7E | [5 empty] | ADCS_S | [8 empty] | 豐華DS.161#3DTR_51ZUL | 161KV #3DTR 51ZRY U/L | OTHER | D04//3DTR/51Z_UL |  |  |  | CDC | 858 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1613DTR | #3DTR |  | RYFA | [17 empty] | 1-39-13 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.161#3DTR_RYFA | 161KV #3DTR RYFA | OTHER | D04//3DTR/RYFA |  |  |  | CDC | 859 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1612DTR | #2DTR |  | DTR_86A | [17 empty] | 1-0E-05 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.161#2DTR_86A | 161KV #2DTR 86RY | OTHER |  |  |  |  | CDC | 860 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1612DTR | #2DTR |  | 187UL | [17 empty] | 1-32-06 |  | 3-09 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.161#2DTR_187UL | 161KV #2DTR 187RY U/L | OTHER | D04//2DTR/1_87UL1 |  |  |  | CDC | 861 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1612DTR | #2DTR |  | 287UL | [17 empty] | 1-39-08 |  | 3-0A | [5 empty] | ADCS_S | [8 empty] | 豐華DS.161#2DTR_287UL | 161KV #2DTR 287RY U/L | OTHER | D04//2DTR/1_87UL2 |  |  |  | CDC | 862 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1612DTR | #2DTR |  | 51Z_UL | [17 empty] | 1-39-09 |  | 3-0B | [5 empty] | ADCS_S | [8 empty] | 豐華DS.161#2DTR_51ZUL | 161KV #2DTR 51ZRY U/L | OTHER | D04//2DTR/51Z_UL |  |  |  | CDC | 863 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1612DTR | #2DTR |  | RYFA | [17 empty] | 1-39-10 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.161#2DTR_RYFA | 161KV #2DTR RYFA | OTHER | D04//2DTR/RYFA |  |  |  | CDC | 864 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1611DTR | #1DTR |  | DTR_86A | [17 empty] | 1-0E-04 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.161#1DTR_86A | 161KV #1DTR 86RY | OTHER |  |  |  |  | CDC | 865 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D04 | 豐華DS | 161 | 161kV | 1611DTR | #1DTR |  | 187UL | [17 empty] | 1-31-10 |  | 3-06 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.161#1DTR_187UL | 161KV #1DTR 187RY U/L | OTHER | D04//1DTR/1_87UL1 |  |  |  | CDC | 866 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1611DTR | #1DTR |  | 287UL | [17 empty] | 1-39-05 |  | 3-07 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.161#1DTR_287UL | 161KV #1DTR 287RY U/L | OTHER | D04//1DTR/1_87UL2 |  |  |  | CDC | 867 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1611DTR | #1DTR |  | 51Z_UL | [17 empty] | 1-39-06 |  | 3-08 | [5 empty] | ADCS_S | [8 empty] | 豐華DS.161#1DTR_51ZUL | 161KV #1DTR 51ZRY U/L | OTHER | D04//1DTR/51Z_UL |  |  |  | CDC | 868 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D04 | 豐華DS | 161 | 161kV | 1611DTR | #1DTR |  | RYFA | [17 empty] | 1-39-07 | [7 empty] | ADCS_S | [8 empty] | 豐華DS.161#1DTR_RYFA | 161KV #1DTR RYFA | OTHER | D04//1DTR/RYFA |  |  |  | CDC | 869 | GENERICDIPoint | DS052_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  |  |  |  | 博碩群創59V0 | [17 empty] | 1-0F-02 | [7 empty] | DDCS4_1 | [8 empty] | 豐華DS.博碩群創59V0 | 23KV博碩群創(K863)59V0 | OTHER |  |  |  |  | CDC | 870 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 博碩群創 | 博碩群創 |  | 81A | [17 empty] | 1-0F-05 | [7 empty] | DDCS4_1 | [8 empty] | 豐華DS.博碩群創_81A | 23KV博碩群創(K863)81A | OTHER |  |  |  |  | CDC | 871 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | 博碩群創 | 博碩群創(K863) |  | CB | [17 empty] | 1-0F-00 | [7 empty] | DDCS4_1 | [8 empty] | 豐華DS.博碩群創_CB | 23KV博碩群創(K863) CB | OTHER |  |  |  |  | CDC | 872 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 博碩群創 | 博碩群創 |  | CFA | [17 empty] | 2-33-07 | [7 empty] | DDCS4_1 | [8 empty] | 豐華DS.博碩群創_CFA | 23KV博碩群創(K863)通訊警報 | OTHER |  |  |  |  | CDC | 873 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D04 | 豐華DS | 22 | 22kV | 博碩群創 | 博碩群創(K863) |  | DS1 | [17 empty] | 2-33-00 | 2-33-01 | [6 empty] | DDCS4_1 | [8 empty] | 豐華DS.博碩群創_DS1 | 23KV博碩群創(K863) DS1 | OTHER |  |  |  |  | CDC | 874 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 22 | 22kV | 博碩群創 | 博碩群創(K863) |  | DS2 | [17 empty] | 2-33-02 | 2-33-03 | [6 empty] | DDCS4_1 | [8 empty] | 豐華DS.博碩群創_DS2 | 23KV博碩群創(K863) DS2 | OTHER |  |  |  |  | CDC | 875 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 22 | 22kV | 博碩群創 | 博碩群創(K863) |  | LE0 | 博碩群創 | [16 empty] | 2-33-04 | 2-33-05 | [6 empty] | DDCS4_1 | [8 empty] | 豐華DS.博碩群創_ES | 23KV博碩群創(K863) ES | OTHER |  |  |  |  | CDC | 876 | GENERICDIPoint | DS052_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D04 | 豐華DS | 0 |  | 博碩群創 | 博碩群創 |  | GDA | [17 empty] | 1-0F-04 | [7 empty] | DDCS4_1 | [8 empty] | 豐華DS.博碩群創_GDA | 23KV博碩群創(K863)GDA | OTHER |  |  |  |  | CDC | 877 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 博碩群創 | 博碩群創 |  | PHA | [17 empty] | 1-0F-03 | [7 empty] | DDCS4_1 | [8 empty] | 豐華DS.博碩群創_PHA | 23KV博碩群創(K863)PHA | OTHER |  |  |  |  | CDC | 878 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 0 |  | 博碩群創 | 博碩群創 |  | RYFA | [17 empty] | 1-0F-01 | [7 empty] | DDCS4_1 | [8 empty] | 豐華DS.博碩群創_RYA | 23KV博碩群創(K863)27/59 | OTHER |  |  |  |  | CDC | 879 | GENERICDIPoint | DS052_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D04 | 豐華DS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 豐華DS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 880 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 11 | 11kV | 220_SC | #2SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 豐華DS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 881 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 11 | 11kV | 230_SC | #3SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 豐華DS.230_SC_CAP | 11KV#3SC 容量 | SC | [5 empty] | 882 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 11 | 11kV | 240_SC | #4SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 豐華DS.240_SC_CAP | 11KV#4SC 容量 | SC | [5 empty] | 883 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 22 | 22kV | 250_SC | #5SC | 9 | CAP | [25 empty] | ADCS_S | [8 empty] | 豐華DS.250_SC_CAP | 23KV#5SC 容量 | SC | [5 empty] | 884 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 22 | 22kV | 260_SC | #6SC | 9 | CAP | [25 empty] | ADCS_S | [8 empty] | 豐華DS.260_SC_CAP | 23KV#6SC 容量 | SC | [5 empty] | 885 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D04 | 豐華DS | 0 |  | TRD | 豐華DS |  | 185 | [25 empty] | TRAIN_AD | [8 empty] | 豐華DS.TRD_185 | 豐華DS NT #1ADTR 11KV_Hi_Limit | [6 empty] | 886 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D04 | 豐華DS | 0 |  | TRD | 豐華DS |  | 186 | [25 empty] | TRAIN_AD | [8 empty] | 豐華DS.TRD_186 | 豐華DS NT #1ADTR 11KV_Lo_Limit | [6 empty] | 887 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D04 | 豐華DS | 0 |  | TRD | 豐華DS |  | 187 | [25 empty] | TRAIN_AD | [8 empty] | 豐華DS.TRD_187 | 豐華DS NT #1BDTR 11KV_Hi_Limit | [6 empty] | 888 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D04 | 豐華DS | 0 |  | TRD | 豐華DS |  | 188 | [25 empty] | TRAIN_AD | [8 empty] | 豐華DS.TRD_188 | 豐華DS NT #1BDTR 11KV_Lo_Limit | [6 empty] | 889 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D04 | 豐華DS | 0 |  | TRD | 豐華DS |  | 189 | [25 empty] | TRAIN_AD | [8 empty] | 豐華DS.TRD_189 | 豐華DS NT #2ADTR 11KV_Hi_Limit | [6 empty] | 890 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D04 | 豐華DS | 0 |  | TRD | 豐華DS |  | 190 | [25 empty] | TRAIN_AD | [8 empty] | 豐華DS.TRD_190 | 豐華DS NT #2ADTR 11KV_Lo_Limit | [6 empty] | 891 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D04 | 豐華DS | 0 |  | TRD | 豐華DS |  | 191 | [25 empty] | TRAIN_AD | [8 empty] | 豐華DS.TRD_191 | 豐華DS NT #2BDTR 11KV_Hi_Limit | [6 empty] | 892 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D04 | 豐華DS | 0 |  | TRD | 豐華DS |  | 192 | [25 empty] | TRAIN_AD | [8 empty] | 豐華DS.TRD_192 | 豐華DS NT #2BDTR 11KV_Lo_Limit | [6 empty] | 893 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D04 | 豐華DS | 0 |  | TRD | 豐華DS |  | 193 | [25 empty] | TRAIN_AD | [8 empty] | 豐華DS.TRD_193 | 豐華DS NT #3DTR 23KV_Hi_Limit | [6 empty] | 894 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D04 | 豐華DS | 0 |  | TRD | 豐華DS |  | 194 | [25 empty] | TRAIN_AD | [8 empty] | 豐華DS.TRD_194 | 豐華DS NT #3DTR 23KV_Lo_Limit | [6 empty] | 895 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D04 | 豐華DS | 161 | 161kV | 1510 | 南科豐華紅線(1510) |  | LE0 | 1510LE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1510LE | 1510LE (非取樣點) | LINE161 | D04/161/1510/LE0 |  |  |  |  | 896 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1510 | 南科豐華紅線(1510) |  | BE0 | 1510BE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1510BE | 1510BE (非取樣點) | LINE161 | D04/161/1510/BE0 |  |  |  |  | 897 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1520 | 南科豐華白線(1520) |  | LE0 | 1520LE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1520LE | 1520LE (非取樣點) | LINE161 | D04/161/1520/LE0 |  |  |  |  | 898 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1520 | 南科豐華白線(1520) |  | BE0 | 1520BE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1520BE | 1520BE (非取樣點) | LINE161 | D04/161/1520/BE0 |  |  |  |  | 899 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1530 | 豐華奇晶一線(1530) |  | LE0 | 1530LE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1530LE | 1530LE (非取樣點) | LINE161 | D04/161/1530/LE0 |  |  |  |  | 900 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1530 | 豐華奇晶一線(1530) |  | BE0 | 1530BE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1530BE | 1530BE (非取樣點) | LINE161 | D04/161/1530/BE0 |  |  |  |  | 901 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1540 | 豐華奇晶四線(1540) |  | LE0 | 1540LE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1540LE | 1540LE (非取樣點) | LINE161 | D04/161/1540/LE0 |  |  |  |  | 902 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1540 | 豐華奇晶四線(1540) |  | BE0 | 1540BE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1540BE | 1540BE (非取樣點) | LINE161 | D04/161/1540/BE0 |  |  |  |  | 903 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1550 | 三竹豐華一路(1550) |  | LE0 | 1550LE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1550LE | 1550LE (非取樣點) | LINE161 | D04/161/1550/LE0 |  |  |  |  | 904 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1550 | 三竹豐華一路(1550) |  | BE0 | 1550BE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1550BE | 1550BE (非取樣點) | LINE161 | D04/161/1550/BE0 |  |  |  |  | 905 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1560 | 三竹豐華二路(1560) |  | LE0 | 1560LE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1560LE | 1560LE (非取樣點) | LINE161 | D04/161/1560/LE0 |  |  |  |  | 906 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1560 | 三竹豐華二路(1560) |  | BE0 | 1560BE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1560BE | 1560BE (非取樣點) | LINE161 | D04/161/1560/BE0 |  |  |  |  | 907 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1570 | 山上安南紅線(1570) |  | LE0 | 1570LE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1570LE | 1570LE (非取樣點) | LINE161 | D04/161/1570/LE0 |  |  |  |  | 908 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1570 | 山上安南紅線(1570) |  | BE0 | 1570BE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1570BE | 1570BE (非取樣點) | LINE161 | D04/161/1570/BE0 |  |  |  |  | 909 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1580 | 山上鹽行白線(1580) |  | LE0 | 1580LE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1580LE | 1580LE (非取樣點) | LINE161 | D04/161/1580/LE0 |  |  |  |  | 910 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1580 | 山上鹽行白線(1580) |  | BE0 | 1580BE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1580BE | 1580BE (非取樣點) | LINE161 | D04/161/1580/BE0 |  |  |  |  | 911 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | K811 | K811_DS |  | DS1 | K811_DS | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K811_DS | K811_DS (非取樣點) | FEEDER | D04/11/K811/DS |  |  |  |  | 912 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | K811 | K811_ES |  | LE0 | K811_ES | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K811_ES | K811_ES (非取樣點) | FEEDER | D04/11/K811/ES |  |  |  |  | 913 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | K812 | K812_DS |  | DS1 | K812_DS | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K812_DS | K812_DS (非取樣點) | FEEDER | D04/11/K812/DS |  |  |  |  | 914 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | K812 | K812_ES |  | LE0 | K812_ES | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K812_ES | K812_ES (非取樣點) | FEEDER | D04/11/K812/ES |  |  |  |  | 915 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | K813 | K813_DS |  | DS1 | K813_DS | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K813_DS | K813_DS (非取樣點) | FEEDER | D04/11/K813/DS |  |  |  |  | 916 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | K813 | K813_ES |  | LE0 | K813_ES | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K813_ES | K813_ES (非取樣點) | FEEDER | D04/11/K813/ES |  |  |  |  | 917 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | K814 | K814_DS |  | DS1 | K814_DS | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K814_DS | K814_DS (非取樣點) | FEEDER | D04/11/K814/DS |  |  |  |  | 918 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | K814 | K814_ES |  | LE0 | K814_ES | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K814_ES | K814_ES (非取樣點) | FEEDER | D04/11/K814/ES |  |  |  |  | 919 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | K815 | K815_DS |  | DS1 | K815_DS | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K815_DS | K815_DS (非取樣點) | FEEDER | D04/11/K815/DS |  |  |  |  | 920 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | K815 | K815_ES |  | LE0 | K815_ES | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K815_ES | K815_ES (非取樣點) | FEEDER | D04/11/K815/ES |  |  |  |  | 921 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | K821 | K821_DS |  | DS1 | K821_DS | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K821_DS | K821_DS (非取樣點) | FEEDER | D04/11/K821/DS |  |  |  |  | 922 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | K821 | K821_ES |  | LE0 | K821_ES | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K821_ES | K821_ES (非取樣點) | FEEDER | D04/11/K821/ES |  |  |  |  | 923 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | K822 | K822_DS |  | DS1 | K822_DS | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K822_DS | K822_DS (非取樣點) | FEEDER | D04/11/K822/DS |  |  |  |  | 924 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | K822 | K822_ES |  | LE0 | K822_ES | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K822_ES | K822_ES (非取樣點) | FEEDER | D04/11/K822/ES |  |  |  |  | 925 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | K823 | K823_DS |  | DS1 | K823_DS | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K823_DS | K823_DS (非取樣點) | FEEDER | D04/11/K823/DS |  |  |  |  | 926 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | K823 | K823_ES |  | LE0 | K823_ES | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K823_ES | K823_ES (非取樣點) | FEEDER | D04/11/K823/ES |  |  |  |  | 927 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | K824 | K824_DS |  | DS1 | K824_DS | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K824_DS | K824_DS (非取樣點) | FEEDER | D04/11/K824/DS |  |  |  |  | 928 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | K824 | K824_ES |  | LE0 | K824_ES | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K824_ES | K824_ES (非取樣點) | FEEDER | D04/11/K824/ES |  |  |  |  | 929 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | K825 | K825_DS |  | DS1 | K825_DS | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K825_DS | K825_DS (非取樣點) | FEEDER | D04/11/K825/DS |  |  |  |  | 930 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | K825 | K825_ES |  | LE0 | K825_ES | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K825_ES | K825_ES (非取樣點) | FEEDER | D04/11/K825/ES |  |  |  |  | 931 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | K831 | K831_DS |  | DS1 | K831_DS | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K831_DS | K831_DS (非取樣點) | FEEDER | D04/11/K831/DS |  |  |  |  | 932 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | K831 | K831_ES |  | LE0 | K831_ES | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K831_ES | K831_ES (非取樣點) | FEEDER | D04/11/K831/ES |  |  |  |  | 933 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | K832 | K832_DS |  | DS1 | K832_DS | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K832_DS | K832_DS (非取樣點) | FEEDER | D04/11/K832/DS |  |  |  |  | 934 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | K832 | K832_ES |  | LE0 | K832_ES | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K832_ES | K832_ES (非取樣點) | FEEDER | D04/11/K832/ES |  |  |  |  | 935 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | K833 | K833_DS |  | DS1 | K833_DS | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K833_DS | K833_DS (非取樣點) | FEEDER | D04/11/K833/DS |  |  |  |  | 936 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | K833 | K833_ES |  | LE0 | K833_ES | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K833_ES | K833_ES (非取樣點) | FEEDER | D04/11/K833/ES |  |  |  |  | 937 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | K834 | K834_DS |  | DS1 | K834_DS | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K834_DS | K834_DS (非取樣點) | FEEDER | D04/11/K834/DS |  |  |  |  | 938 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | K834 | K834_ES |  | LE0 | K834_ES | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K834_ES | K834_ES (非取樣點) | FEEDER | D04/11/K834/ES |  |  |  |  | 939 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | K835 | K835_DS |  | DS1 | K835_DS | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K835_DS | K835_DS (非取樣點) | FEEDER | D04/11/K835/DS |  |  |  |  | 940 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | K835 | K835_ES |  | LE0 | K835_ES | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K835_ES | K835_ES (非取樣點) | FEEDER | D04/11/K835/ES |  |  |  |  | 941 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | K841 | K841_DS |  | DS1 | K841_DS | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K841_DS | K841_DS (非取樣點) | FEEDER | D04/11/K841/DS |  |  |  |  | 942 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | K841 | K841_ES |  | LE0 | K841_ES | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K841_ES | K841_ES (非取樣點) | FEEDER | D04/11/K841/ES |  |  |  |  | 943 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | K842 | K842_DS |  | DS1 | K842_DS | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K842_DS | K842_DS (非取樣點) | FEEDER | D04/11/K842/DS |  |  |  |  | 944 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | K842 | K842_ES |  | LE0 | K842_ES | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K842_ES | K842_ES (非取樣點) | FEEDER | D04/11/K842/ES |  |  |  |  | 945 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | K843 | K843_DS |  | DS1 | K843_DS | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K843_DS | K843_DS (非取樣點) | FEEDER | D04/11/K843/DS |  |  |  |  | 946 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | K843 | K843_ES |  | LE0 | K843_ES | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K843_ES | K843_ES (非取樣點) | FEEDER | D04/11/K843/ES |  |  |  |  | 947 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | K844 | K844_DS |  | DS1 | K844_DS | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K844_DS | K844_DS (非取樣點) | FEEDER | D04/11/K844/DS |  |  |  |  | 948 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | K844 | K844_ES |  | LE0 | K844_ES | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K844_ES | K844_ES (非取樣點) | FEEDER | D04/11/K844/ES |  |  |  |  | 949 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | K845 | K845_DS |  | DS1 | K845_DS | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K845_DS | K845_DS (非取樣點) | FEEDER | D04/11/K845/DS |  |  |  |  | 950 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | K845 | K845_ES |  | LE0 | K845_ES | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K845_ES | K845_ES (非取樣點) | FEEDER | D04/11/K845/ES |  |  |  |  | 951 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | K861 | K861_DS |  | DS1 | K861_DS | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K861_DS | K861_DS (非取樣點) | FEEDER | D04/22/K861/DS |  |  |  |  | 952 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | K861 | K861_ES |  | LE0 | K861_ES | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K861_ES | K861_ES (非取樣點) | FEEDER | D04/22/K861/ES |  |  |  |  | 953 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | K862 | K862_DS |  | DS1 | K862_DS | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K862_DS | K862_DS (非取樣點) | FEEDER | D04/22/K862/DS |  |  |  |  | 954 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | K862 | K862_ES |  | LE0 | K862_ES | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K862_ES | K862_ES (非取樣點) | FEEDER | D04/22/K862/ES |  |  |  |  | 955 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | K863 | K863_DS |  | DS1 | K863_DS | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K863_DS | K863_DS (非取樣點) | FEEDER | D04/22/K863/DS |  |  |  |  | 956 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | K863 | K863_ES |  | LE0 | K863_ES | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K863_ES | K863_ES (非取樣點) | FEEDER | D04/22/K863/ES |  |  |  |  | 957 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | K864 | K864_DS |  | DS1 | K864_DS | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K864_DS | K864_DS (非取樣點) | FEEDER | D04/22/K864/DS |  |  |  |  | 958 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | K864 | K864_ES |  | LE0 | K864_ES | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K864_ES | K864_ES (非取樣點) | FEEDER | D04/22/K864/ES |  |  |  |  | 959 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | K865 | K865_DS |  | DS1 | K865_DS | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K865_DS | K865_DS (非取樣點) | FEEDER | D04/22/K865/DS |  |  |  |  | 960 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | K865 | K865_ES |  | LE0 | K865_ES | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K865_ES | K865_ES (非取樣點) | FEEDER | D04/22/K865/ES |  |  |  |  | 961 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | K866 | K866_DS |  | DS1 | K866_DS | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K866_DS | K866_DS (非取樣點) | FEEDER | D04/22/K866/DS |  |  |  |  | 962 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | K866 | K866_ES |  | LE0 | K866_ES | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K866_ES | K866_ES (非取樣點) | FEEDER | D04/22/K866/ES |  |  |  |  | 963 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | K867 | K867_DS |  | DS1 | K867_DS | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K867_DS | K867_DS (非取樣點) | FEEDER | D04/22/K867/DS |  |  |  |  | 964 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | K867 | K867_ES |  | LE0 | K867_ES | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K867_ES | K867_ES (非取樣點) | FEEDER | D04/22/K867/ES |  |  |  |  | 965 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | K868 | K868_DS |  | DS1 | K868_DS | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K868_DS | K868_DS (非取樣點) | FEEDER | D04/22/K868/DS |  |  |  |  | 966 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | K868 | K868_ES |  | LE0 | K868_ES | [24 empty] | DDCS4_2 | [8 empty] | 豐華DS.K868_ES | K868_ES (非取樣點) | FEEDER | D04/22/K868/ES |  |  |  |  | 967 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | 101 | 101 |  | 101 | 101 | [24 empty] | ADCS_S | [8 empty] | 豐華DS.101 | 101 (非取樣點) | TIE | D04/11/100/D1 |  |  |  |  | 968 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 102 | 102 |  | 102 | 102 | [24 empty] | ADCS_S | [8 empty] | 豐華DS.102 | 102 (非取樣點) | TIE | D04/11/100/D2 |  |  |  |  | 969 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1501E | 1501E (非取樣點) | TIE | D04/161/1500/E1 |  |  |  |  | 970 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1502E | 1502E (非取樣點) | TIE | D04/161/1500/E2 |  |  |  |  | 971 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | 201 | 201 |  | 201 | 201 | [24 empty] | ADCS_S | [8 empty] | 豐華DS.201 | 201 (非取樣點) | TIE | D04/11/200/D1 |  |  |  |  | 972 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 202 | 202 |  | 202 | 202 | [24 empty] | ADCS_S | [8 empty] | 豐華DS.202 | 202 (非取樣點) | TIE | D04/11/200/D2 |  |  |  |  | 973 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 391 | 391 |  | 391 | 391 | [24 empty] | ADCS_S | [8 empty] | 豐華DS.391 | 391 (非取樣點) | OTHER | D04/11/390/D1 |  |  |  |  | 974 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 391E | 391E |  | 391E | 391E | [24 empty] | ADCS_S | [8 empty] | 豐華DS.391E | 391E (非取樣點) | OTHER | D04/11/390/E1 |  |  |  |  | 975 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | 491 | 491 |  | 491 | 491 | [24 empty] | ADCS_S | [8 empty] | 豐華DS.491 | 491 (非取樣點) | OTHER | D04/11/490/D1 |  |  |  |  | 976 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 491E | 491E |  | 491E | 491E | [24 empty] | ADCS_S | [8 empty] | 豐華DS.491E | 491E (非取樣點) | OTHER | D04/11/490/E1 |  |  |  |  | 977 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | 1750TE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1750TE | 1750TE (非取樣點) | MTR | D04/161/1750/TE0 |  |  |  |  | 978 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | 1750BE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1750BE | 1750BE (非取樣點) | MTR | D04/161/1750/BE0 |  |  |  |  | 979 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | 311 | 311 |  | 311 | 311 | [24 empty] | ADCS_S | [8 empty] | 豐華DS.311 | 311 (非取樣點) | MTR | D04/11/310/D1 |  |  |  |  | 980 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 310 | #1DTR(310) |  | E1 | 311E | [24 empty] | ADCS_S | [8 empty] | 豐華DS.311E | 311E (非取樣點) | MTR | D04/11/310/E1 |  |  |  |  | 981 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | 321 | 321 |  | 321 | 321 | [24 empty] | ADCS_S | [8 empty] | 豐華DS.321 | 321 (非取樣點) | MTR | D04/11/320/D1 |  |  |  |  | 982 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 320 | #1DTR(320) |  | E1 | 321E | [24 empty] | ADCS_S | [8 empty] | 豐華DS.321E | 321E (非取樣點) | MTR | D04/11/320/E1 |  |  |  |  | 983 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | 1760TE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1760TE | 1760TE (非取樣點) | MTR | D04/161/1760/TE0 |  |  |  |  | 984 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | 1760BE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1760BE | 1760BE (非取樣點) | MTR | D04/161/1760/BE0 |  |  |  |  | 985 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | 331 | 331 |  | 331 | 331 | [24 empty] | ADCS_S | [8 empty] | 豐華DS.331 | 331 (非取樣點) | MTR | D04/11/330/D1 |  |  |  |  | 986 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 330 | #2DTR(330) |  | E1 | 331E | [24 empty] | ADCS_S | [8 empty] | 豐華DS.331E | 331E (非取樣點) | MTR | D04/11/330/E1 |  |  |  |  | 987 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | 341 | 341 |  | 341 | 341 | [24 empty] | ADCS_S | [8 empty] | 豐華DS.341 | 341 (非取樣點) | MTR | D04/11/340/D1 |  |  |  |  | 988 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 340 | #2DTR(340) |  | E1 | 341E | [24 empty] | ADCS_S | [8 empty] | 豐華DS.341E | 341E (非取樣點) | MTR | D04/11/340/E1 |  |  |  |  | 989 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | 1770TE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1770TE | 1770TE (非取樣點) | MTR | D04/161/1770/TE0 |  |  |  |  | 990 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | 1770BE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1770BE | 1770BE (非取樣點) | MTR | D04/161/1770/BE0 |  |  |  |  | 991 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | 351 | 351 |  | 351 | 351 | [24 empty] | ADCS_S | [8 empty] | 豐華DS.351 | 351 (非取樣點) | MTR | D04/22/350/D1 |  |  |  |  | 992 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 350 | #3DTR(350) |  | E1 | 351E | [24 empty] | ADCS_S | [8 empty] | 豐華DS.351E | 351E (非取樣點) | MTR | D04/22/350/E1 |  |  |  |  | 993 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | 211E | 211E |  | 211E | 211E | [24 empty] | ADCS_S | [8 empty] | 豐華DS.211E | 211E (非取樣點) | SC | D04/11/210/E1 |  |  |  |  | 994 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | 211 | 211 |  | 211 | 211 | [24 empty] | ADCS_S | [8 empty] | 豐華DS.211 | 211 (非取樣點) | SC | D04/11/210/D1 |  |  |  |  | 995 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 221E | 221E |  | 221E | 221E | [24 empty] | ADCS_S | [8 empty] | 豐華DS.221E | 221E (非取樣點) | SC | D04/11/220/E1 |  |  |  |  | 996 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | 221 | 221 |  | 221 | 221 | [24 empty] | ADCS_S | [8 empty] | 豐華DS.221 | 221 (非取樣點) | SC | D04/11/220/D1 |  |  |  |  | 997 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 231E | 231E |  | 231E | 231E | [24 empty] | ADCS_S | [8 empty] | 豐華DS.231E | 231E (非取樣點) | SC | D04/11/230/E1 |  |  |  |  | 998 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | 231 | 231 |  | 231 | 231 | [24 empty] | ADCS_S | [8 empty] | 豐華DS.231 | 231 (非取樣點) | SC | D04/11/230/D1 |  |  |  |  | 999 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 241E | 241E |  | 241E | 241E | [24 empty] | ADCS_S | [8 empty] | 豐華DS.241E | 241E (非取樣點) | SC | D04/11/240/E1 |  |  |  |  | 1000 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | 241 | 241 |  | 241 | 241 | [24 empty] | ADCS_S | [8 empty] | 豐華DS.241 | 241 (非取樣點) | SC | D04/11/240/D1 |  |  |  |  | 1001 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 251E | 251E |  | 251E | 251E | [24 empty] | ADCS_S | [8 empty] | 豐華DS.251E | 251E (非取樣點) | SC | D04/22/250/E1 |  |  |  |  | 1002 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | 251 | 251 |  | 251 | 251 | [24 empty] | ADCS_S | [8 empty] | 豐華DS.251 | 251 (非取樣點) | SC | D04/22/250/D1 |  |  |  |  | 1003 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 261E | 261E |  | 261E | 261E | [24 empty] | ADCS_S | [8 empty] | 豐華DS.261E | 261E (非取樣點) | SC | D04/22/260/E1 |  |  |  |  | 1004 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | 261 | 261 |  | 261 | 261 | [24 empty] | ADCS_S | [8 empty] | 豐華DS.261 | 261 (非取樣點) | SC | D04/22/260/D1 |  |  |  |  | 1005 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 15B1E | 15B1E |  | BE1 | 15B1E | [24 empty] | ADCS_S | [8 empty] | 豐華DS.15B1E | 15B1E (非取樣點) | BUS | D04/161/161B1E/BE1 |  |  |  |  | 1006 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | 15B2E | 15B2E |  | BE2 | 15B2E | [24 empty] | ADCS_S | [8 empty] | 豐華DS.15B2E | 15B2E (非取樣點) | BUS | D04/161/161B2E/BE2 |  |  |  |  | 1007 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 1008 | NotelDIPoint | [38 empty] | START/STOP | STOP
D04 | 豐華DS | 0 |  |  |  |  | 101E | 101E | [24 empty] | ADCS_S | [8 empty] | 豐華DS.101E | 101E(非取樣點) | OTHER | D04/11/100/E1 |  |  |  |  | 1009 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  |  |  |  | 102E | 102E | [24 empty] | ADCS_S | [8 empty] | 豐華DS.102E | 102E(非取樣點) | OTHER | D04/11/100/E2 |  |  |  |  | 1010 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  |  |  |  | 201E | 201E | [24 empty] | ADCS_S | [8 empty] | 豐華DS.201E | 201E(非取樣點) | OTHER | D04/11/200/E1 |  |  |  |  | 1011 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  |  |  |  | 202E | 202E | [24 empty] | ADCS_S | [8 empty] | 豐華DS.202E | 202E(非取樣點) | OTHER | D04/11/200/E2 |  |  |  |  | 1012 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華聯電五一路(1610) |  | LE0 | 1610LE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1610LE | 1610LE (非取樣點) | LINE161 | D04/161/1610/LE0 |  |  |  |  | 1013 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1610 | 豐華聯電五一路(1610) |  | BE0 | 1610BE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1610BE | 1610BE (非取樣點) | LINE161 | D04/161/1610/BE0 |  |  |  |  | 1014 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華聯電五二路(1620) |  | LE0 | 1620LE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1620LE | 1620LE (非取樣點) | LINE161 | D04/161/1620/LE0 |  |  |  |  | 1015 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1620 | 豐華聯電五二路(1620) |  | BE0 | 1620BE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1620BE | 1620BE (非取樣點) | LINE161 | D04/161/1620/BE0 |  |  |  |  | 1016 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1780 | #4DTR(1780) |  | TE0 | 1780TE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1780TE | 1780TE (非取樣點) | MTR | D04/161/1780/TE0 |  |  |  |  | 1017 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 161 | 161kV | 1780 | #4DTR(1780) |  | BE0 | 1780BE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1780BE | 1780BE (非取樣點) | MTR | D04/161/1780/BE0 |  |  |  |  | 1018 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | 1A | #1A |  | BE | #1A_BE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.#1A_BE | #1A BE(非取樣點) | OTHER | [5 empty] | 1019 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | 1B | #1B |  | BE | #1B_BE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.#1B_BE | #1B BE(非取樣點) | OTHER | [5 empty] | 1020 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | 2A | #2A |  | BE | #2A_BE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.#2A_BE | #2A BE(非取樣點) | OTHER | [5 empty] | 1021 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | 2B | #2B |  | BE | #2B_BE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.#2B_BE | #2B BE(非取樣點) | OTHER | [5 empty] | 1022 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | 3 | #3 |  | BE | #3_BE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.#3_BE | #3 BE(非取樣點) | OTHER | [5 empty] | 1023 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  |  |  |  | 1960BE | 1960BE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1960BE | 1960BE(非取樣點) | OTHER | D04/161/1960/BE0 |  |  |  |  | 1024 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  |  |  |  | 1960RE | 1960RE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1960RE | 1960RE(非取樣點) | OTHER | D04/161/1960/RE0 |  |  |  |  | 1025 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | 1ABUS | 1ABUS |  | PTD | 1ABUS_PTD | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1ABUS_PTD | #1ABUS_PTD(非取樣點) | OTHER | [5 empty] | 1026 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 1ABUS | 1ABUS |  | PTE | 1ABUS_PTE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1ABUS_PTE | #1ABUS_PTE(非取樣點) | OTHER | [5 empty] | 1027 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | 1BBUS | 1BBUS |  | PTD | 1BBUS_PTD | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1BBUS_PTD | #1BBUS_PTD(非取樣點) | OTHER | [5 empty] | 1028 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 1BBUS | 1BBUS |  | PTE | 1BBUS_PTE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.1BBUS_PTE | #1BBUS_PTE(非取樣點) | OTHER | [5 empty] | 1029 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | 2ABUS | 2ABUS |  | PTD | 2ABUS_PTD | [24 empty] | ADCS_S | [8 empty] | 豐華DS.2ABUS_PTD | #2ABUS_PTD(非取樣點) | OTHER | [5 empty] | 1030 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 2ABUS | 2ABUS |  | PTE | 2ABUS_PTE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.2ABUS_PTE | #2ABUS_PTE(非取樣點) | OTHER | [5 empty] | 1031 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | 2BBUS | 2BBUS |  | PTD | 2BBUS_PTD | [24 empty] | ADCS_S | [8 empty] | 豐華DS.2BBUS_PTD | #2BBUS_PTD(非取樣點) | OTHER | [5 empty] | 1032 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 2BBUS | 2BBUS |  | PTE | 2BBUS_PTE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.2BBUS_PTE | #2BBUS_PTE(非取樣點) | OTHER | [5 empty] | 1033 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D04 | 豐華DS | 0 |  | 3BUS | 3BUS |  | PTD | 3BUS_PTD | [24 empty] | ADCS_S | [8 empty] | 豐華DS.3BUS_PTD | #3BUS_PTD(非取樣點) | OTHER | [5 empty] | 1034 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D04 | 豐華DS | 0 |  | 3BUS | 3BUS |  | PTE | 3BUS_PTE | [24 empty] | ADCS_S | [8 empty] | 豐華DS.3BUS_PTE | #3BUS_PTE(非取樣點) | OTHER | [5 empty] | 1035 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo