## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D05 | 道爺DS | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_A1 | [8 empty] | 道爺DS.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 2 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_A1 | [8 empty] | 道爺DS.1510BE | 1510BE (非取樣點) | LINE161 | [5 empty] | 3 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_A1 | [8 empty] | 道爺DS.1520LE | 1520LE (非取樣點) | LINE161 | [5 empty] | 4 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_A1 | [8 empty] | 道爺DS.1520BE | 1520BE (非取樣點) | LINE161 | [5 empty] | 5 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1530 | 南科～道爺三路(1530) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_A1 | [8 empty] | 道爺DS.1530LE | 1530LE (非取樣點) | LINE161 | [5 empty] | 6 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1530 | 南科～道爺三路(1530) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_A1 | [8 empty] | 道爺DS.1530BE | 1530BE (非取樣點) | LINE161 | [5 empty] | 7 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1540 | 南科～道爺四路(1540) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_A1 | [8 empty] | 道爺DS.1540LE | 1540LE (非取樣點) | LINE161 | [5 empty] | 8 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1540 | 南科～道爺四路(1540) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_A1 | [8 empty] | 道爺DS.1540BE | 1540BE (非取樣點) | LINE161 | [5 empty] | 9 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺~奇晶七紅線(1550) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_A1 | [8 empty] | 道爺DS.1550LE | 1550LE (非取樣點) | LINE161 | [5 empty] | 10 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺~奇晶七紅線(1550) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_A1 | [8 empty] | 道爺DS.1550BE | 1550BE (非取樣點) | LINE161 | [5 empty] | 11 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺~奇晶七白線(1560) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_A1 | [8 empty] | 道爺DS.1560LE | 1560LE (非取樣點) | LINE161 | [5 empty] | 12 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺~奇晶七白線(1560) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_A1 | [8 empty] | 道爺DS.1560BE | 1560BE (非取樣點) | LINE161 | [5 empty] | 13 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺～奇晶六紅線(1570) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_A1 | [8 empty] | 道爺DS.1570LE | 1570LE (非取樣點) | LINE161 | [5 empty] | 14 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺～奇晶六紅線(1570) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_A1 | [8 empty] | 道爺DS.1570BE | 1570BE (非取樣點) | LINE161 | [5 empty] | 15 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺～奇晶六白線(1580) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_A1 | [8 empty] | 道爺DS.1580LE | 1580LE (非取樣點) | LINE161 | [5 empty] | 16 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺～奇晶六白線(1580) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_A1 | [8 empty] | 道爺DS.1580BE | 1580BE (非取樣點) | LINE161 | [5 empty] | 17 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1610 | 道爺~安南~新化線(1610) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_A1 | [8 empty] | 道爺DS.1610LE | 1610LE (非取樣點) | LINE161 | [5 empty] | 18 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1610 | 道爺~安南~新化線(1610) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_A1 | [8 empty] | 道爺DS.1610BE | 1610BE (非取樣點) | LINE161 | [5 empty] | 19 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1620 | 道爺~和順~新化線(1620) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_A1 | [8 empty] | 道爺DS.1620LE | 1620LE (非取樣點) | LINE161 | [5 empty] | 20 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1620 | 道爺~和順~新化線(1620) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_A1 | [8 empty] | 道爺DS.1620BE | 1620BE (非取樣點) | LINE161 | [5 empty] | 21 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_A1 | [8 empty] | 道爺DS.1501E | 1501E (非取樣點) | TIE | [5 empty] | 22 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_A1 | [8 empty] | 道爺DS.1502E | 1502E (非取樣點) | TIE | [5 empty] | 23 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1600 | TIE(1600) |  | E1 | 1601E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_A1 | [8 empty] | 道爺DS.1601E | 1601E (非取樣點) | TIE | [5 empty] | 24 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1600 | TIE(1600) |  | E2 | 1602E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_A1 | [8 empty] | 道爺DS.1602E | 1602E (非取樣點) | TIE | [5 empty] | 25 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1700 | TIE(1700) |  | E1 | 1701E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_A1 | [8 empty] | 道爺DS.1701E | 1701E (非取樣點) | TIE | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1700 | TIE(1700) |  | E2 | 1703E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_A1 | [8 empty] | 道爺DS.1703E | 1703E (非取樣點) | TIE | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1800 | TIE(1800) |  | E1 | 1802E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_A1 | [8 empty] | 道爺DS.1802E | 1802E (非取樣點) | TIE | [5 empty] | 28 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1800 | TIE(1800) |  | E2 | 1804E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_A1 | [8 empty] | 道爺DS.1804E | 1804E (非取樣點) | TIE | [5 empty] | 29 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_A1 | [8 empty] | 道爺DS.1760TE | 1760TE (非取樣點) | MTR | [5 empty] | 30 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_A1 | [8 empty] | 道爺DS.1760BE | 1760BE (非取樣點) | MTR | [5 empty] | 31 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | D1 | 331(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D05_A1 | [8 empty] | 道爺DS.331 | 331 (非取樣點) | MTR | [5 empty] | 32 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | E1 | 331E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D05_A1 | [8 empty] | 道爺DS.331E | 331E (非取樣點) | MTR | [5 empty] | 33 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | D1 | 341(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D05_A1 | [8 empty] | 道爺DS.341 | 341 (非取樣點) | MTR | [5 empty] | 34 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | E1 | 341E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D05_A1 | [8 empty] | 道爺DS.341E | 341E (非取樣點) | MTR | [5 empty] | 35 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_A1 | [8 empty] | 道爺DS.1770TE | 1770TE (非取樣點) | MTR | [5 empty] | 36 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_A1 | [8 empty] | 道爺DS.1770BE | 1770BE (非取樣點) | MTR | [5 empty] | 37 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | D1 | 351(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D05_A1 | [8 empty] | 道爺DS.351 | 351 (非取樣點) | MTR | [5 empty] | 38 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | E1 | 351E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D05_A1 | [8 empty] | 道爺DS.351E | 351E (非取樣點) | MTR | [5 empty] | 39 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | D1 | 361(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D05_A1 | [8 empty] | 道爺DS.361 | 361 (非取樣點) | MTR | [5 empty] | 40 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | E1 | 361E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D05_A1 | [8 empty] | 道爺DS.361E | 361E (非取樣點) | MTR | [5 empty] | 41 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 22 | 22kV | 200 | TIE(200) |  | E1 | 201E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D05_A1 | [8 empty] | 道爺DS.201E | 201E (非取樣點) | TIE | [5 empty] | 42 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 22 | 22kV | 200 | TIE(200) |  | E2 | 202E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D05_A1 | [8 empty] | 道爺DS.202E | 202E (非取樣點) | TIE | [5 empty] | 43 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 22 | 22kV | 200 | TIE(200) |  | D1 | 201(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D05_A1 | [8 empty] | 道爺DS.201 | 201 (非取樣點) | TIE | [5 empty] | 44 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 200 | TIE(200) |  | D2 | 202(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D05_A1 | [8 empty] | 道爺DS.202 | 202 (非取樣點) | TIE | [5 empty] | 45 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 230 | #3SC(230) |  | E1 | 231E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D05_A1 | [8 empty] | 道爺DS.231E | 231E (非取樣點) | SC | [5 empty] | 46 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 22 | 22kV | 230 | #3SC(230) |  | D1 | 231(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D05_A1 | [8 empty] | 道爺DS.231 | 231 (非取樣點) | SC | [5 empty] | 47 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K61 | 爺61線(4K61) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_D1 | [8 empty] | 道爺DS.4K61_DS | 4K61_DS (非取樣點) | FEEDER | [5 empty] | 48 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K61 | 爺61線(4K61) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D05_D1 | [8 empty] | 道爺DS.4K61_ES | 4K61_ES (非取樣點) | FEEDER | [5 empty] | 49 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 22 | 22kV | 4K62 | 爺62線(4K62) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_D1 | [8 empty] | 道爺DS.4K62_DS | 4K62_DS (非取樣點) | FEEDER | [5 empty] | 50 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K62 | 爺62線(4K62) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D05_D1 | [8 empty] | 道爺DS.4K62_ES | 4K62_ES (非取樣點) | FEEDER | [5 empty] | 51 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 22 | 22kV | 4K63 | 爺63線(4K63) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_D1 | [8 empty] | 道爺DS.4K63_DS | 4K63_DS (非取樣點) | FEEDER | [5 empty] | 52 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K63 | 爺63線(4K63) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D05_D1 | [8 empty] | 道爺DS.4K63_ES | 4K63_ES (非取樣點) | FEEDER | [5 empty] | 53 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 22 | 22kV | 4K64 | 爺64線(4K64) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_D1 | [8 empty] | 道爺DS.4K64_DS | 4K64_DS (非取樣點) | FEEDER | [5 empty] | 54 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K64 | 爺64線(4K64) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D05_D1 | [8 empty] | 道爺DS.4K64_ES | 4K64_ES (非取樣點) | FEEDER | [5 empty] | 55 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 22 | 22kV | 240 | #4SC(240) |  | E1 | 241E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D05_A1 | [8 empty] | 道爺DS.241E | 241E (非取樣點) | SC | [5 empty] | 56 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 22 | 22kV | 240 | #4SC(240) |  | D1 | 241(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D05_A1 | [8 empty] | 道爺DS.241 | 241 (非取樣點) | SC | [5 empty] | 57 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K65 | 爺65線(4K65) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_D1 | [8 empty] | 道爺DS.4K65_DS | 4K65_DS (非取樣點) | FEEDER | [5 empty] | 58 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K65 | 爺65線(4K65) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D05_D1 | [8 empty] | 道爺DS.4K65_ES | 4K65_ES (非取樣點) | FEEDER | [5 empty] | 59 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 22 | 22kV | 4K66 | 爺66線(4K66) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_D1 | [8 empty] | 道爺DS.4K66_DS | 4K66_DS (非取樣點) | FEEDER | [5 empty] | 60 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K66 | 爺66線(4K66) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D05_D1 | [8 empty] | 道爺DS.4K66_ES | 4K66_ES (非取樣點) | FEEDER | [5 empty] | 61 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 22 | 22kV | 4K67 | 爺67線(4K67) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_D1 | [8 empty] | 道爺DS.4K67_DS | 4K67_DS (非取樣點) | FEEDER | [5 empty] | 62 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K67 | 爺67線(4K67) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D05_D1 | [8 empty] | 道爺DS.4K67_ES | 4K67_ES (非取樣點) | FEEDER | [5 empty] | 63 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 22 | 22kV | 4K68 | 爺68線(4K68) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_D1 | [8 empty] | 道爺DS.4K68_DS | 4K68_DS (非取樣點) | FEEDER | [5 empty] | 64 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K68 | 爺68線(4K68) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D05_D1 | [8 empty] | 道爺DS.4K68_ES | 4K68_ES (非取樣點) | FEEDER | [5 empty] | 65 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 22 | 22kV | 390 | #1SSTR(390) |  | D1 | 391(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D05_A1 | [8 empty] | 道爺DS.391 | 391 (非取樣點) | OTHER | [5 empty] | 66 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 390 | #1SSTR(390) |  | E1 | 391E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D05_A1 | [8 empty] | 道爺DS.391E | 391E (非取樣點) | OTHER | [5 empty] | 67 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 22 | 22kV | 300 | TIE(300) |  | E1 | 301E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D05_A1 | [8 empty] | 道爺DS.301E | 301E (非取樣點) | TIE | [5 empty] | 68 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 22 | 22kV | 300 | TIE(300) |  | E2 | 302E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D05_A1 | [8 empty] | 道爺DS.302E | 302E (非取樣點) | TIE | [5 empty] | 69 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 22 | 22kV | 300 | TIE(300) |  | D1 | 301(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D05_A1 | [8 empty] | 道爺DS.301 | 301 (非取樣點) | TIE | [5 empty] | 70 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 300 | TIE(300) |  | D2 | 302(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D05_A1 | [8 empty] | 道爺DS.302 | 302 (非取樣點) | TIE | [5 empty] | 71 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 250 | #5SC(250) |  | E1 | 251E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D05_A1 | [8 empty] | 道爺DS.251E | 251E (非取樣點) | SC | [5 empty] | 72 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 22 | 22kV | 250 | #5SC(250) |  | D1 | 251(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D05_A1 | [8 empty] | 道爺DS.251 | 251 (非取樣點) | SC | [5 empty] | 73 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K71 | 爺71線(4K71) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_D1 | [8 empty] | 道爺DS.4K71_DS | 4K71_DS (非取樣點) | FEEDER | [5 empty] | 74 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K71 | 爺71線(4K71) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D05_D1 | [8 empty] | 道爺DS.4K71_ES | 4K71_ES (非取樣點) | FEEDER | [5 empty] | 75 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 22 | 22kV | 4K72 | 爺72線(4K72) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_D1 | [8 empty] | 道爺DS.4K72_DS | 4K72_DS (非取樣點) | FEEDER | [5 empty] | 76 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K72 | 爺72線(4K72) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D05_D1 | [8 empty] | 道爺DS.4K72_ES | 4K72_ES (非取樣點) | FEEDER | [5 empty] | 77 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 22 | 22kV | 4K73 | 爺73線(4K73) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_D1 | [8 empty] | 道爺DS.4K73_DS | 4K73_DS (非取樣點) | FEEDER | [5 empty] | 78 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K73 | 爺73線(4K73) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D05_D1 | [8 empty] | 道爺DS.4K73_ES | 4K73_ES (非取樣點) | FEEDER | [5 empty] | 79 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 22 | 22kV | 4K74 | 爺74線(4K74) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_D1 | [8 empty] | 道爺DS.4K74_DS | 4K74_DS (非取樣點) | FEEDER | [5 empty] | 80 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K74 | 爺74線(4K74) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D05_D1 | [8 empty] | 道爺DS.4K74_ES | 4K74_ES (非取樣點) | FEEDER | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 22 | 22kV | 260 | #6SC(260) |  | E1 | 261E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D05_A1 | [8 empty] | 道爺DS.261E | 261E (非取樣點) | SC | [5 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 22 | 22kV | 260 | #6SC(260) |  | D1 | 261(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D05_A1 | [8 empty] | 道爺DS.261 | 261 (非取樣點) | SC | [5 empty] | 83 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K75 | 爺75線(4K75) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_D1 | [8 empty] | 道爺DS.4K75_DS | 4K75_DS (非取樣點) | FEEDER | [5 empty] | 84 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K75 | 爺75線(4K75) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D05_D1 | [8 empty] | 道爺DS.4K75_ES | 4K75_ES (非取樣點) | FEEDER | [5 empty] | 85 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 22 | 22kV | 4K76 | 爺76線(4K76) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_D1 | [8 empty] | 道爺DS.4K76_DS | 4K76_DS (非取樣點) | FEEDER | [5 empty] | 86 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K76 | 爺76線(4K76) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D05_D1 | [8 empty] | 道爺DS.4K76_ES | 4K76_ES (非取樣點) | FEEDER | [5 empty] | 87 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 22 | 22kV | 4K77 | 爺77線(4K77) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_D1 | [8 empty] | 道爺DS.4K77_DS | 4K77_DS (非取樣點) | FEEDER | [5 empty] | 88 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K77 | 爺77線(4K77) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D05_D1 | [8 empty] | 道爺DS.4K77_ES | 4K77_ES (非取樣點) | FEEDER | [5 empty] | 89 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 22 | 22kV | 4K78 | 爺78線(4K78) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D05_D1 | [8 empty] | 道爺DS.4K78_DS | 4K78_DS (非取樣點) | FEEDER | [5 empty] | 90 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K78 | 爺78線(4K78) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D05_D1 | [8 empty] | 道爺DS.4K78_ES | 4K78_ES (非取樣點) | FEEDER | [5 empty] | 91 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 22 | 22kV | 490 | #2SSTR(490) |  | D1 | 491(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D05_A1 | [8 empty] | 道爺DS.491 | 491 (非取樣點) | OTHER | [5 empty] | 92 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 490 | #2SSTR(490) |  | E1 | 491E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D05_A1 | [8 empty] | 道爺DS.491E | 491E (非取樣點) | OTHER | [5 empty] | 93 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | 15B1E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2EthA1 | B/1Bus | [13 empty] | aajz | B2/D05_A1 | [8 empty] | 道爺DS.15B1E | 15B1E (非取樣點) | BUS | [5 empty] | 94 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | 15B2E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2EthA2 | B/2Bus | [13 empty] | aajz | B2/D05_A1 | [8 empty] | 道爺DS.15B2E | 15B2E (非取樣點) | BUS | [5 empty] | 95 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 161B3E | #3BUS(161B3E) |  | BE3 | 15B3E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2EthA3 | B/3Bus | [13 empty] | abez | B2/D05_A1 | [8 empty] | 道爺DS.15B3E | 15B3E (非取樣點) | BUS | [5 empty] | 96 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 161B4E | #4BUS(161B4E) |  | BE4 | 15B4E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2EthA4 | B/4Bus | [13 empty] | abez | B2/D05_A1 | [8 empty] | 道爺DS.15B4E | 15B4E (非取樣點) | BUS | [5 empty] | 97 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1BUS | #1BUS |  | V |  | B3 | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | Locate Empty | KV | 161KV #1BUS 電壓 | kV_-210_210(-2000_2000) | aaa | B2/D05_A1 | [8 empty] | 道爺DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | [5 empty] | 98 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D05 | 道爺DS | 161 | 161kV | 2BUS | #2BUS |  | V |  | B3 | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0003 |  |  | 1-83 |  |  | Locate Empty | KV | 161KV #2BUS 電壓 | kV_-210_210(-2000_2000) | aab | B2/D05_A1 | [8 empty] | 道爺DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | [5 empty] | 99 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D05 | 道爺DS | 161 | 161kV | 3BUS | #3BUS |  | V |  | B3 | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0004 |  |  | 1-84 |  |  | Locate Empty | KV | 161KV #3BUS 電壓 | kV_-210_210(-2000_2000) | aba | B2/D05_A1 | [8 empty] | 道爺DS.161KV#3BUS_KV | 161KV #3BUS KV | BUS | [5 empty] | 100 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D05 | 道爺DS | 161 | 161kV | 4BUS | #4BUS |  | V |  | B3 | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0005 |  |  | 1-85 |  |  | Locate Empty | KV | 161KV #4BUS 電壓 | kV_-210_210(-2000_2000) | abb | B2/D05_A1 | [8 empty] | 道爺DS.161KV#4BUS_KV | 161KV #4BUS KV | BUS | [5 empty] | 101 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D05 | 道爺DS | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | Locate Empty | MW | 1510 南科道爺一路MW | MW_-560_560(-2000_2000) |  | B2/D05_A1 | [8 empty] | 道爺DS.1510_MW | 南科道爺ㄧ路 MW | LINE161 | [5 empty] | 102 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | Locate Empty | MVAR | 1510 南科道爺一路MVAR | MVAR_-560_560(-2000_2000) |  | B2/D05_A1 | [8 empty] | 道爺DS.1510_MVAR | 南科道爺ㄧ路 MVAR | LINE161 | [5 empty] | 103 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | Locate Empty | MW | 1520 南科道爺二路MW | MW_-560_560(-2000_2000) |  | B2/D05_A1 | [8 empty] | 道爺DS.1520_MW | 南科道爺二路 MW | LINE161 | [5 empty] | 104 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | Locate Empty | MVAR | 1520 南科道爺二路MVAR | MVAR_-560_560(-2000_2000) |  | B2/D05_A1 | [8 empty] | 道爺DS.1520_MVAR | 南科道爺二路 MVAR | LINE161 | [5 empty] | 105 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1530 | 南科～道爺三路(1530) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | Locate Empty | MW | 1530 南科道爺三路MW | MW_-560_560(-2000_2000) |  | B2/D05_A1 | [8 empty] | 道爺DS.1530_MW | 南科道爺三路 MW | LINE161 | [5 empty] | 106 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1530 | 南科～道爺三路(1530) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | Locate Empty | MVAR | 1530 南科道爺三路MVAR | MVAR_-560_560(-2000_2000) |  | B2/D05_A1 | [8 empty] | 道爺DS.1530_MVAR | 南科道爺三路 MVAR | LINE161 | [5 empty] | 107 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1540 | 南科～道爺四路(1540) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0012 |  |  | 1-8C |  |  | Locate Empty | MW | 1540 南科道爺四路MW | MW_-560_560(-2000_2000) |  | B2/D05_A1 | [8 empty] | 道爺DS.1540_MW | 南科道爺四路 MW | LINE161 | [5 empty] | 108 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1540 | 南科～道爺四路(1540) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0013 |  |  | 1-8D |  |  | Locate Empty | MVAR | 1540 南科道爺四路MVAR | MVAR_-560_560(-2000_2000) |  | B2/D05_A1 | [8 empty] | 道爺DS.1540_MVAR | 南科道爺四路 MVAR | LINE161 | [5 empty] | 109 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺~奇晶七紅線(1550) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0014 |  |  | 1-8E |  |  | Locate Empty | MW | 1550 道爺奇晶七紅線MW | MW_-560_560(-2000_2000) |  | B2/D05_A1 | [8 empty] | 道爺DS.1550_MW | 道爺奇晶七紅線 MW | LINE161 | [5 empty] | 110 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺~奇晶七紅線(1550) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0015 |  |  | 1-8F |  |  | Locate Empty | MVAR | 1550 道爺奇晶七紅線MVAR | MVAR_-560_560(-2000_2000) |  | B2/D05_A1 | [8 empty] | 道爺DS.1550_MVAR | 道爺奇晶七紅線 MVAR | LINE161 | [5 empty] | 111 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺~奇晶七白線(1560) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0016 |  |  | 1-90 |  |  | Locate Empty | MW | 1560 道爺奇晶七白線MW | MW_-560_560(-2000_2000) |  | B2/D05_A1 | [8 empty] | 道爺DS.1560_MW | 道爺奇晶七白線 MW | LINE161 | [5 empty] | 112 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺~奇晶七白線(1560) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0017 |  |  | 1-91 |  |  | Locate Empty | MVAR | 1560 道爺奇晶七白線MVAR | MVAR_-560_560(-2000_2000) |  | B2/D05_A1 | [8 empty] | 道爺DS.1560_MVAR | 道爺奇晶七白線 MVAR | LINE161 | [5 empty] | 113 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺～奇晶六紅線(1570) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | Locate Empty | MW | 1570 道爺奇晶六線紅線MW | MW_-560_560(-2000_2000) |  | B2/D05_A1 | [8 empty] | 道爺DS.1570_MW | 道爺奇晶六紅線 MW | LINE161 | [5 empty] | 114 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺～奇晶六紅線(1570) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | Locate Empty | MVAR | 1570 道爺奇晶六線紅線MVAR | MVAR_-560_560(-2000_2000) |  | B2/D05_A1 | [8 empty] | 道爺DS.1570_MVAR | 道爺奇晶六紅線 MVAR | LINE161 | [5 empty] | 115 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺～奇晶六白線(1580) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | Locate Empty | MW | 1580 道爺奇晶六線白線MW | MW_-560_560(-2000_2000) |  | B2/D05_A1 | [8 empty] | 道爺DS.1580_MW | 道爺奇晶六白線 MW | LINE161 | [5 empty] | 116 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺～奇晶六白線(1580) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | Locate Empty | MVAR | 1580 道爺奇晶六線白線MVAR | MVAR_-560_560(-2000_2000) |  | B2/D05_A1 | [8 empty] | 道爺DS.1580_MVAR | 道爺奇晶六白線 MVAR | LINE161 | [5 empty] | 117 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1610 | 道爺~安南~新化線(1610) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | Locate Empty | MW | 1610 道爺安南新化線MW | MW_-560_560(-2000_2000) |  | B2/D05_A1 | [8 empty] | 道爺DS.1610_MW | 道爺安南新化線 MW | LINE161 | [5 empty] | 118 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1610 | 道爺~安南~新化線(1610) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | Locate Empty | MVAR | 1610 道爺安南新化線MVAR | MVAR_-560_560(-2000_2000) |  | B2/D05_A1 | [8 empty] | 道爺DS.1610_MVAR | 道爺安南新化線 MVAR | LINE161 | [5 empty] | 119 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1620 | 道爺~和順~新化線(1620) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0024 |  |  | 1-98 |  |  | Locate Empty | MW | 1620 道爺和順新化線MW | MW_-560_560(-2000_2000) |  | B2/D05_A1 | [8 empty] | 道爺DS.1620_MW | 道爺和順新化線 MW | LINE161 | [5 empty] | 120 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1620 | 道爺~和順~新化線(1620) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | Locate Empty | MVAR | 1620 道爺和順新化線MVAR | MVAR_-560_560(-2000_2000) |  | B2/D05_A1 | [8 empty] | 道爺DS.1620_MVAR | 道爺和順新化線 MVAR | LINE161 | [5 empty] | 121 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1500 | TIE(1500) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | Locate Empty | A | 1500 TIE R相電流 | A_-2000_2000(-2000_2000) |  | B2/D05_A1 | [8 empty] | 道爺DS.1500TIE_AMP | 1500TIE AMP | TIE | [5 empty] | 122 |  |  |  |  | AI | [5 empty] | C20R1600 | 1520 | 1600 | 1760 | 1968 | 2.27 | -1520 | -1600 | -1760 | -1968 | 1 | 0.01 | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1600 | TIE(1600) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0027 |  |  | 1-9B |  |  | Locate Empty | A | 1600 TIE R相電流 | A_-2000_2000(-2000_2000) |  | B2/D05_A1 | [8 empty] | 道爺DS.1600TIE_AMP | 1600TIE AMP | TIE | [5 empty] | 123 |  |  |  |  | AI | [5 empty] | C20R1600 | 1520 | 1600 | 1760 | 1968 | 2.27 | -1520 | -1600 | -1760 | -1968 | 1 | 0.01 | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1700 | TIE(1700) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | Locate Empty | A | 1700 SECTION1 R相電流 | A_-2000_2000(-2000_2000) |  | B2/D05_A1 | [8 empty] | 道爺DS.1700TIE_AMP | 1700TIE AMP | TIE | [5 empty] | 124 |  |  |  |  | AI | [5 empty] | C20R1600 | 1520 | 1600 | 1760 | 1968 | 2.27 | -1520 | -1600 | -1760 | -1968 | 1 | 0.01 | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1800 | TIE(1800) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | Locate Empty | A | 1800 SECTION2 R相電流 | A_-2000_2000(-2000_2000) |  | B2/D05_A1 | [8 empty] | 道爺DS.1800TIE_AMP | 1800TIE AMP | TIE | [5 empty] | 125 |  |  |  |  | AI | [5 empty] | C20R1600 | 1520 | 1600 | 1760 | 1968 | 2.27 | -1520 | -1600 | -1760 | -1968 | 1 | 0.01 | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | DCV_P |  |  | MvMoment | 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | Locate Empty | V | DC直流電壓 P | kV_-150_150(-2000_2000) |  | B3/D05_A1 | [8 empty] | 道爺DS.直流P電源電壓 | 直流P電源電壓 | OTHER | [5 empty] | 126 |  |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 | 0.01 | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | DCV_N |  |  | MvMoment | 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | Locate Empty | V | DC直流電壓 N | kV_-150_150(-2000_2000) |  | B3/D05_A1 | [8 empty] | 道爺DS.直流N電源電壓 | 直流N電源電壓 | OTHER | [5 empty] | 127 |  |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 | 0.01 | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D05 | 道爺DS |  |  | 2DTR | #2DTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | 1AI-CH1 |  | #2 DTR ULTC TAP指示量 | TAP_-8.5_8.5(0_2000) |  | B1/D05_A1 | [8 empty] | 道爺DS.#2DTR_TAP | #2DTR OLTC TAP | MTR | [5 empty] | 128 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D05 | 道爺DS |  |  | 2DTR | #2DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | 1AI-CH3 | ℃ | #2 DTR 油溫指示量 | OIL_-120_120(-2000_2000) |  | B1/D05_A1 | [8 empty] | 道爺DS.#2DTR_OIL | #2DTR 油溫 | MTR | [5 empty] | 129 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D05 | 道爺DS |  |  | 2DTR | #2DTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | 2AI-CH1 | ℃ | #2 DTR 線溫指示量 | COIL_-120_120(-2000_2000) |  | B1/D05_A1 | [8 empty] | 道爺DS.#2DTR_COIL | #2DTR 線溫 | MTR | [5 empty] | 130 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D05 | 道爺DS |  |  | 3DTR | #3DTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | 1AI-CH1 |  | #3 DTR ULTC TAP指示量 | TAP_-8.5_8.5(0_2000) |  | B1/D05_A1 | [8 empty] | 道爺DS.#3DTR_TAP | #3DTR OLTC TAP | MTR | [5 empty] | 131 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D05 | 道爺DS |  |  | 3DTR | #3DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | 1AI-CH3 | ℃ | #3 DTR 油溫指示量 | OIL_-120_120(-2000_2000) |  | B1/D05_A1 | [8 empty] | 道爺DS.#3DTR_OIL | #3DTR 油溫 | MTR | [5 empty] | 132 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D05 | 道爺DS |  |  | 3DTR | #3DTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | 2AI-CH1 | ℃ | #3 DTR 線溫指示量 | COIL_-120_120(-2000_2000) |  | B1/D05_A1 | [8 empty] | 道爺DS.#3DTR_COIL | #3DTR 線溫 | MTR | [5 empty] | 133 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D05 | 道爺DS | 22 | 22kV | 200 | TIE(200) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | Locate Empty | A | 200 R相電流量 | A_-2000_2000(-2000_2000) |  | B3/D05_A1 | [8 empty] | 道爺DS.23KV_200_A1 | 23KV 200 R相AMP | TIE | [5 empty] | 134 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 200 | TIE(200) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | Locate Empty | A | 200 S相電流量 | A_-2000_2000(-2000_2000) |  | B3/D05_A1 | [8 empty] | 道爺DS.23KV_200_A2 | 23KV 200 S相AMP | TIE | [5 empty] | 135 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 200 | TIE(200) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | Locate Empty | A | 200 T相電流量 | A_-2000_2000(-2000_2000) |  | B3/D05_A1 | [8 empty] | 道爺DS.23KV_200_A3 | 23KV 200 T相AMP | TIE | [5 empty] | 136 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 2ABUS | #2ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0108 |  |  | 1-EC |  |  | Locate Empty | KV | PT-2A BUS | kV_-18_18(-2000_2000) | aaa | B3/D05_A1 | [8 empty] | 道爺DS.23KV#2ABUS_KV | 23KV #2ABUS KV | BUS | [5 empty] | 137 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D05 | 道爺DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | Locate Empty | MW | 330 MW | MW_-108_108(-2000_2000) |  | B3/D05_A1 | [8 empty] | 道爺DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | [5 empty] | 138 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | Locate Empty | MVAR | 330 MVAR | MVAR_-72_72(-2000_2000) |  | B3/D05_A1 | [8 empty] | 道爺DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | [5 empty] | 139 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | Locate Empty | A | 330 R相電流 | A_-3000_3000(-2000_2000) |  | B3/D05_A1 | [8 empty] | 道爺DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | [5 empty] | 140 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | Locate Empty | A | 330 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D05_A1 | [8 empty] | 道爺DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | [5 empty] | 141 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | Locate Empty | A | 330 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D05_A1 | [8 empty] | 道爺DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | [5 empty] | 142 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K61 | 爺61線(4K61) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | Locate Empty | KVAR | 爺61線（4K61） KVAR | KVAR_-21600_21600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺61線KVAR | 23KV爺61線 KVAR | FEEDER | [5 empty] | 143 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K61 | 爺61線(4K61) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | Locate Empty | A | 爺61線（4K61） R相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺61線A1 | 23KV爺61線 R相AMP | FEEDER | [5 empty] | 144 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K61 | 爺61線(4K61) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | Locate Empty | A | 爺61線（4K61） S相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺61線A2 | 23KV爺61線 S相AMP | FEEDER | [5 empty] | 145 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K61 | 爺61線(4K61) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | Locate Empty | A | 爺61線（4K61） T相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺61線A3 | 23KV爺61線 T相AMP | FEEDER | [5 empty] | 146 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K61 | 爺61線(4K61) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | Locate Empty | A | 爺61線（4K61） N相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺61線A0 | 23KV爺61線 N相AMP | FEEDER | [5 empty] | 147 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K62 | 爺62線(4K62) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | Locate Empty | KVAR | 爺62線（4K62） KVAR | KVAR_-21600_21600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺62線KVAR | 23KV爺62線 KVAR | FEEDER | [5 empty] | 148 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K62 | 爺62線(4K62) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | Locate Empty | A | 爺62線（4K62） R相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺62線A1 | 23KV爺62線 R相AMP | FEEDER | [5 empty] | 149 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K62 | 爺62線(4K62) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | Locate Empty | A | 爺62線（4K62） S相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺62線A2 | 23KV爺62線 S相AMP | FEEDER | [5 empty] | 150 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K62 | 爺62線(4K62) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | Locate Empty | A | 爺62線（4K62） T相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺62線A3 | 23KV爺62線 T相AMP | FEEDER | [5 empty] | 151 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K62 | 爺62線(4K62) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | Locate Empty | A | 爺62線（4K62） N相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺62線A0 | 23KV爺62線 N相AMP | FEEDER | [5 empty] | 152 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K63 | 爺63線(4K63) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | Locate Empty | KVAR | 爺63線（4K63） KVAR | KVAR_-21600_21600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺63線KVAR | 23KV爺63線 KVAR | FEEDER | [5 empty] | 153 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K63 | 爺63線(4K63) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | Locate Empty | A | 爺63線（4K63） R相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺63線A1 | 23KV爺63線 R相AMP | FEEDER | [5 empty] | 154 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K63 | 爺63線(4K63) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | Locate Empty | A | 爺63線（4K63） S相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺63線A2 | 23KV爺63線 S相AMP | FEEDER | [5 empty] | 155 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K63 | 爺63線(4K63) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | Locate Empty | A | 爺63線（4K63） T相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺63線A3 | 23KV爺63線 T相AMP | FEEDER | [5 empty] | 156 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K63 | 爺63線(4K63) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | Locate Empty | A | 爺63線（4K63） N相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺63線A0 | 23KV爺63線 N相AMP | FEEDER | [5 empty] | 157 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K64 | 爺64線(4K64) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | Locate Empty | KVAR | 爺64線（4K64） KVAR | KVAR_-21600_21600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺64線KVAR | 23KV爺64線 KVAR | FEEDER | [5 empty] | 158 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K64 | 爺64線(4K64) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | Locate Empty | A | 爺64線（4K64） R相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺64線A1 | 23KV爺64線 R相AMP | FEEDER | [5 empty] | 159 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K64 | 爺64線(4K64) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0133 |  |  | 2-85 |  |  | Locate Empty | A | 爺64線（4K64） S相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺64線A2 | 23KV爺64線 S相AMP | FEEDER | [5 empty] | 160 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K64 | 爺64線(4K64) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | Locate Empty | A | 爺64線（4K64） T相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺64線A3 | 23KV爺64線 T相AMP | FEEDER | [5 empty] | 161 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K64 | 爺64線(4K64) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0135 |  |  | 2-87 |  |  | Locate Empty | A | 爺64線（4K64） N相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺64線A0 | 23KV爺64線 N相AMP | FEEDER | [5 empty] | 162 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 2BBUS | #2BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0136 |  |  | 2-88 |  |  | Locate Empty | KV | PT-2B BUS | kV_-18_18(-2000_2000) | baa | B3/D05_A1 | [8 empty] | 道爺DS.23KV#2BBUS_KV | 23KV #2BBUS KV | BUS | [5 empty] | 163 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D05 | 道爺DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0137 |  |  | 2-89 |  |  | Locate Empty | MW | 340 MW | MW_-108_108(-2000_2000) |  | B3/D05_A1 | [8 empty] | 道爺DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | [5 empty] | 164 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0138 |  |  | 2-8A |  |  | Locate Empty | MVAR | 340 MVAR | MVAR_-72_72(-2000_2000) |  | B3/D05_A1 | [8 empty] | 道爺DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | [5 empty] | 165 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0139 |  |  | 2-8B |  |  | Locate Empty | A | 340 R相電流 | A_-3000_3000(-2000_2000) |  | B3/D05_A1 | [8 empty] | 道爺DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | [5 empty] | 166 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0140 |  |  | 2-8C |  |  | Locate Empty | A | 340 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D05_A1 | [8 empty] | 道爺DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | [5 empty] | 167 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0141 |  |  | 2-8D |  |  | Locate Empty | A | 340 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D05_A1 | [8 empty] | 道爺DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | [5 empty] | 168 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K65 | 爺65線(4K65) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0142 |  |  | 2-8E |  |  | Locate Empty | KVAR | 爺65線（4K65） KVAR | KVAR_-21600_21600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺65線KVAR | 23KV爺65線 KVAR | FEEDER | [5 empty] | 169 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K65 | 爺65線(4K65) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0143 |  |  | 2-8F |  |  | Locate Empty | A | 爺65線（4K65） R相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺65線A1 | 23KV爺65線 R相AMP | FEEDER | [5 empty] | 170 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K65 | 爺65線(4K65) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0144 |  |  | 2-90 |  |  | Locate Empty | A | 爺65線（4K65） S相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺65線A2 | 23KV爺65線 S相AMP | FEEDER | [5 empty] | 171 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K65 | 爺65線(4K65) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0145 |  |  | 2-91 |  |  | Locate Empty | A | 爺65線（4K65） T相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺65線A3 | 23KV爺65線 T相AMP | FEEDER | [5 empty] | 172 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K65 | 爺65線(4K65) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0146 |  |  | 2-92 |  |  | Locate Empty | A | 爺65線（4K65） N相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺65線A0 | 23KV爺65線 N相AMP | FEEDER | [5 empty] | 173 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K66 | 爺66線(4K66) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0147 |  |  | 2-93 |  |  | Locate Empty | KVAR | 爺66線（4K66） KVAR | KVAR_-21600_21600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺66線KVAR | 23KV爺66線 KVAR | FEEDER | [5 empty] | 174 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K66 | 爺66線(4K66) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0148 |  |  | 2-94 |  |  | Locate Empty | A | 爺66線（4K66） R相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺66線A1 | 23KV爺66線 R相AMP | FEEDER | [5 empty] | 175 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K66 | 爺66線(4K66) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0149 |  |  | 2-95 |  |  | Locate Empty | A | 爺66線（4K66） S相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺66線A2 | 23KV爺66線 S相AMP | FEEDER | [5 empty] | 176 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K66 | 爺66線(4K66) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0150 |  |  | 2-96 |  |  | Locate Empty | A | 爺66線（4K66） T相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺66線A3 | 23KV爺66線 T相AMP | FEEDER | [5 empty] | 177 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K66 | 爺66線(4K66) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0151 |  |  | 2-97 |  |  | Locate Empty | A | 爺66線（4K66） N相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺66線A0 | 23KV爺66線 N相AMP | FEEDER | [5 empty] | 178 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K67 | 爺67線(4K67) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0152 |  |  | 2-98 |  |  | Locate Empty | KVAR | 爺67線（4K67） KVAR | KVAR_-21600_21600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺67線KVAR | 23KV爺67線 KVAR | FEEDER | [5 empty] | 179 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K67 | 爺67線(4K67) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0153 |  |  | 2-99 |  |  | Locate Empty | A | 爺67線（4K67） R相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺67線A1 | 23KV爺67線 R相AMP | FEEDER | [5 empty] | 180 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K67 | 爺67線(4K67) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0154 |  |  | 2-9A |  |  | Locate Empty | A | 爺67線（4K67） S相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺67線A2 | 23KV爺67線 S相AMP | FEEDER | [5 empty] | 181 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K67 | 爺67線(4K67) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0155 |  |  | 2-9B |  |  | Locate Empty | A | 爺67線（4K67） T相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺67線A3 | 23KV爺67線 T相AMP | FEEDER | [5 empty] | 182 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K67 | 爺67線(4K67) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0156 |  |  | 2-9C |  |  | Locate Empty | A | 爺67線（4K67） N相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺67線A0 | 23KV爺67線 N相AMP | FEEDER | [5 empty] | 183 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K68 | 爺68線(4K68) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0157 |  |  | 2-9D |  |  | Locate Empty | KVAR | 爺68線（4K68） KVAR | KVAR_-21600_21600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺68線KVAR | 23KV爺68線 KVAR | FEEDER | [5 empty] | 184 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K68 | 爺68線(4K68) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0158 |  |  | 2-9E |  |  | Locate Empty | A | 爺68線（4K68） R相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺68線A1 | 23KV爺68線 R相AMP | FEEDER | [5 empty] | 185 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K68 | 爺68線(4K68) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0159 |  |  | 2-9F |  |  | Locate Empty | A | 爺68線（4K68） S相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺68線A2 | 23KV爺68線 S相AMP | FEEDER | [5 empty] | 186 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K68 | 爺68線(4K68) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0160 |  |  | 2-A0 |  |  | Locate Empty | A | 爺68線（4K68） T相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺68線A3 | 23KV爺68線 T相AMP | FEEDER | [5 empty] | 187 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K68 | 爺68線(4K68) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0161 |  |  | 2-A1 |  |  | Locate Empty | A | 爺68線（4K68） N相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺68線A0 | 23KV爺68線 N相AMP | FEEDER | [5 empty] | 188 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 300 | TIE(300) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0162 |  |  | 2-A2 |  |  | Locate Empty | A | 300 R相電流量 | A_-2000_2000(-2000_2000) |  | B3/D05_A1 | [8 empty] | 道爺DS.23KV_300_A1 | 23KV 300 R相AMP | TIE | [5 empty] | 189 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 300 | TIE(300) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0163 |  |  | 2-A3 |  |  | Locate Empty | A | 300 S相電流量 | A_-2000_2000(-2000_2000) |  | B3/D05_A1 | [8 empty] | 道爺DS.23KV_300_A2 | 23KV 300 S相AMP | TIE | [5 empty] | 190 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 300 | TIE(300) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0164 |  |  | 2-A4 |  |  | Locate Empty | A | 300 T相電流量 | A_-2000_2000(-2000_2000) |  | B3/D05_A1 | [8 empty] | 道爺DS.23KV_300_A3 | 23KV 300 T相AMP | TIE | [5 empty] | 191 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 3ABUS | #3ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0165 |  |  | 2-A5 |  |  | Locate Empty | KV | PT-3A BUS | kV_-18_18(-2000_2000) | aba | B3/D05_A1 | [8 empty] | 道爺DS.23KV#3ABUS_KV | 23KV #3ABUS KV | BUS | [5 empty] | 192 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D05 | 道爺DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0166 |  |  | 2-A6 |  |  | Locate Empty | MW | 350 MW | MW_-108_108(-2000_2000) |  | B3/D05_A1 | [8 empty] | 道爺DS.#3DTR(A)_MW | #3DTR二次側(A) MW | MTR | [5 empty] | 193 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0167 |  |  | 2-A7 |  |  | Locate Empty | MVAR | 350 MVAR | MVAR_-72_72(-2000_2000) |  | B3/D05_A1 | [8 empty] | 道爺DS.#3DTR(A)_MVAR | #3DTR二次側(A) MVAR | MTR | [5 empty] | 194 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0168 |  |  | 2-A8 |  |  | Locate Empty | A | 350 R相電流 | A_-3000_3000(-2000_2000) |  | B3/D05_A1 | [8 empty] | 道爺DS.#3DTR(A)_A1 | #3DTR二次側(A) R相AMP | MTR | [5 empty] | 195 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0169 |  |  | 2-A9 |  |  | Locate Empty | A | 350 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D05_A1 | [8 empty] | 道爺DS.#3DTR(A)_A2 | #3DTR二次側(A) S相AMP | MTR | [5 empty] | 196 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0170 |  |  | 2-AA |  |  | Locate Empty | A | 350 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D05_A1 | [8 empty] | 道爺DS.#3DTR(A)_A3 | #3DTR二次側(A) T相AMP | MTR | [5 empty] | 197 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K71 | 爺71線(4K71) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0171 |  |  | 2-AB |  |  | Locate Empty | KVAR | 爺71線（4K71） KVAR | KVAR_-21600_21600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺71線KVAR | 23KV爺71線 KVAR | FEEDER | [5 empty] | 198 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K71 | 爺71線(4K71) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0172 |  |  | 2-AC |  |  | Locate Empty | A | 爺71線（4K71） R相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺71線A1 | 23KV爺71線 R相AMP | FEEDER | [5 empty] | 199 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K71 | 爺71線(4K71) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0173 |  |  | 2-AD |  |  | Locate Empty | A | 爺71線（4K71） S相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺71線A2 | 23KV爺71線 S相AMP | FEEDER | [5 empty] | 200 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K71 | 爺71線(4K71) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0174 |  |  | 2-AE |  |  | Locate Empty | A | 爺71線（4K71） T相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺71線A3 | 23KV爺71線 T相AMP | FEEDER | [5 empty] | 201 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K71 | 爺71線(4K71) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0175 |  |  | 2-AF |  |  | Locate Empty | A | 爺71線（4K71） N相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺71線A0 | 23KV爺71線 N相AMP | FEEDER | [5 empty] | 202 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K72 | 爺72線(4K72) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0176 |  |  | 2-B0 |  |  | Locate Empty | KVAR | 爺72線（4K72） KVAR | KVAR_-21600_21600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺72線KVAR | 23KV爺72線 KVAR | FEEDER | [5 empty] | 203 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K72 | 爺72線(4K72) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0177 |  |  | 2-B1 |  |  | Locate Empty | A | 爺72線（4K72） R相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺72線A1 | 23KV爺72線 R相AMP | FEEDER | [5 empty] | 204 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K72 | 爺72線(4K72) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0178 |  |  | 2-B2 |  |  | Locate Empty | A | 爺72線（4K72） S相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺72線A2 | 23KV爺72線 S相AMP | FEEDER | [5 empty] | 205 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K72 | 爺72線(4K72) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0179 |  |  | 2-B3 |  |  | Locate Empty | A | 爺72線（4K72） T相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺72線A3 | 23KV爺72線 T相AMP | FEEDER | [5 empty] | 206 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K72 | 爺72線(4K72) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0180 |  |  | 2-B4 |  |  | Locate Empty | A | 爺72線（4K72） N相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺72線A0 | 23KV爺72線 N相AMP | FEEDER | [5 empty] | 207 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K73 | 爺73線(4K73) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0181 |  |  | 2-B5 |  |  | Locate Empty | KVAR | 爺73線（4K73） KVAR | KVAR_-21600_21600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺73線KVAR | 23KV爺73線 KVAR | FEEDER | [5 empty] | 208 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K73 | 爺73線(4K73) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0182 |  |  | 2-B6 |  |  | Locate Empty | A | 爺73線（4K73） R相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺73線A1 | 23KV爺73線 R相AMP | FEEDER | [5 empty] | 209 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K73 | 爺73線(4K73) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0183 |  |  | 2-B7 |  |  | Locate Empty | A | 爺73線（4K73） S相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺73線A2 | 23KV爺73線 S相AMP | FEEDER | [5 empty] | 210 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K73 | 爺73線(4K73) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0184 |  |  | 2-B8 |  |  | Locate Empty | A | 爺73線（4K73） T相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺73線A3 | 23KV爺73線 T相AMP | FEEDER | [5 empty] | 211 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K73 | 爺73線(4K73) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0185 |  |  | 2-B9 |  |  | Locate Empty | A | 爺73線（4K73） N相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺73線A0 | 23KV爺73線 N相AMP | FEEDER | [5 empty] | 212 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K74 | 爺74線(4K74) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0186 |  |  | 2-BA |  |  | Locate Empty | KVAR | 爺74線（4K74） KVAR | KVAR_-21600_21600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺74線KVAR | 23KV爺74線 KVAR | FEEDER | [5 empty] | 213 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K74 | 爺74線(4K74) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0187 |  |  | 2-BB |  |  | Locate Empty | A | 爺74線（4K74） R相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺74線A1 | 23KV爺74線 R相AMP | FEEDER | [5 empty] | 214 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K74 | 爺74線(4K74) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0188 |  |  | 2-BC |  |  | Locate Empty | A | 爺74線（4K74） S相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺74線A2 | 23KV爺74線 S相AMP | FEEDER | [5 empty] | 215 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K74 | 爺74線(4K74) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0189 |  |  | 2-BD |  |  | Locate Empty | A | 爺74線（4K74） T相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺74線A3 | 23KV爺74線 T相AMP | FEEDER | [5 empty] | 216 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K74 | 爺74線(4K74) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0190 |  |  | 2-BE |  |  | Locate Empty | A | 爺74線（4K74） N相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺74線A0 | 23KV爺74線 N相AMP | FEEDER | [5 empty] | 217 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 3BBUS | #3BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0191 |  |  | 2-BF |  |  | Locate Empty | KV | PT-3B BUS | kV_-18_18(-2000_2000) | bba | B3/D05_A1 | [8 empty] | 道爺DS.23KV#3BBUS_KV | 23KV #3BBUS KV | BUS | [5 empty] | 218 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D05 | 道爺DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0194 |  |  | 2-C2 |  |  | Locate Empty | MW | 360 MW | MW_-108_108(-2000_2000) |  | B3/D05_A1 | [8 empty] | 道爺DS.#3DTR(B)_MW | #3DTR二次側(B) MW | MTR | [5 empty] | 219 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0195 |  |  | 2-C3 |  |  | Locate Empty | MVAR | 360 MVAR | MVAR_-72_72(-2000_2000) |  | B3/D05_A1 | [8 empty] | 道爺DS.#3DTR(B)_MVAR | #3DTR二次側(B) MVAR | MTR | [5 empty] | 220 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0196 |  |  | 2-C4 |  |  | Locate Empty | A | 360 R相電流 | A_-3000_3000(-2000_2000) |  | B3/D05_A1 | [8 empty] | 道爺DS.#3DTR(B)_A1 | #3DTR二次側(B) R相AMP | MTR | [5 empty] | 221 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0197 |  |  | 2-C5 |  |  | Locate Empty | A | 360 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D05_A1 | [8 empty] | 道爺DS.#3DTR(B)_A2 | #3DTR二次側(B) S相AMP | MTR | [5 empty] | 222 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0198 |  |  | 2-C6 |  |  | Locate Empty | A | 360 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D05_A1 | [8 empty] | 道爺DS.#3DTR(B)_A3 | #3DTR二次側(B) T相AMP | MTR | [5 empty] | 223 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K75 | 爺75線(4K75) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0199 |  |  | 2-C7 |  |  | Locate Empty | KVAR | 爺75線（4K75） KVAR | KVAR_-21600_21600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺75線KVAR | 23KV爺75線 KVAR | FEEDER | [5 empty] | 224 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K75 | 爺75線(4K75) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0200 |  |  | 2-C8 |  |  | Locate Empty | A | 爺75線（4K75） R相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺75線A1 | 23KV爺75線 R相AMP | FEEDER | [5 empty] | 225 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K75 | 爺75線(4K75) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0201 |  |  | 2-C9 |  |  | Locate Empty | A | 爺75線（4K75） S相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺75線A2 | 23KV爺75線 S相AMP | FEEDER | [5 empty] | 226 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K75 | 爺75線(4K75) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0202 |  |  | 2-CA |  |  | Locate Empty | A | 爺75線（4K75） T相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺75線A3 | 23KV爺75線 T相AMP | FEEDER | [5 empty] | 227 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K75 | 爺75線(4K75) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0203 |  |  | 2-CB |  |  | Locate Empty | A | 爺75線（4K75） N相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺75線A0 | 23KV爺75線 N相AMP | FEEDER | [5 empty] | 228 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K76 | 爺76線(4K76) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0204 |  |  | 2-CC |  |  | Locate Empty | KVAR | 爺76線（4K76） KVAR | KVAR_-21600_21600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺76線KVAR | 23KV爺76線 KVAR | FEEDER | [5 empty] | 229 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K76 | 爺76線(4K76) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0205 |  |  | 2-CD |  |  | Locate Empty | A | 爺76線（4K76） R相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺76線A1 | 23KV爺76線 R相AMP | FEEDER | [5 empty] | 230 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K76 | 爺76線(4K76) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0206 |  |  | 2-CE |  |  | Locate Empty | A | 爺76線（4K76） S相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺76線A2 | 23KV爺76線 S相AMP | FEEDER | [5 empty] | 231 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K76 | 爺76線(4K76) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0207 |  |  | 2-CF |  |  | Locate Empty | A | 爺76線（4K76） T相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺76線A3 | 23KV爺76線 T相AMP | FEEDER | [5 empty] | 232 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K76 | 爺76線(4K76) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0208 |  |  | 2-D0 |  |  | Locate Empty | A | 爺76線（4K76） N相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺76線A0 | 23KV爺76線 N相AMP | FEEDER | [5 empty] | 233 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K77 | 爺77線(4K77) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0209 |  |  | 2-D1 |  |  | Locate Empty | KVAR | 爺77線（4K77） KVAR | KVAR_-21600_21600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺77線KVAR | 23KV爺77線 KVAR | FEEDER | [5 empty] | 234 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K77 | 爺77線(4K77) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0210 |  |  | 2-D2 |  |  | Locate Empty | A | 爺77線（4K77） R相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺77線A1 | 23KV爺77線 R相AMP | FEEDER | [5 empty] | 235 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K77 | 爺77線(4K77) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0211 |  |  | 2-D3 |  |  | Locate Empty | A | 爺77線（4K77） S相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺77線A2 | 23KV爺77線 S相AMP | FEEDER | [5 empty] | 236 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K77 | 爺77線(4K77) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0212 |  |  | 2-D4 |  |  | Locate Empty | A | 爺77線（4K77） T相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺77線A3 | 23KV爺77線 T相AMP | FEEDER | [5 empty] | 237 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K77 | 爺77線(4K77) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0213 |  |  | 2-D5 |  |  | Locate Empty | A | 爺77線（4K77） N相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺77線A0 | 23KV爺77線 N相AMP | FEEDER | [5 empty] | 238 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K78 | 爺78線(4K78) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0214 |  |  | 2-D6 |  |  | Locate Empty | KVAR | 爺78線（4K78） KVAR | KVAR_-21600_21600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺78線KVAR | 23KV爺78線 KVAR | FEEDER | [5 empty] | 239 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K78 | 爺78線(4K78) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0215 |  |  | 2-D7 |  |  | Locate Empty | A | 爺78線（4K78） R相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺78線A1 | 23KV爺78線 R相AMP | FEEDER | [5 empty] | 240 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K78 | 爺78線(4K78) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0216 |  |  | 2-D8 |  |  | Locate Empty | A | 爺78線（4K78） S相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺78線A2 | 23KV爺78線 S相AMP | FEEDER | [5 empty] | 241 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K78 | 爺78線(4K78) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0217 |  |  | 2-D9 |  |  | Locate Empty | A | 爺78線（4K78） T相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺78線A3 | 23KV爺78線 T相AMP | FEEDER | [5 empty] | 242 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 4K78 | 爺78線(4K78) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0218 |  |  | 2-DA |  |  | Locate Empty | A | 爺78線（4K78） N相電流 | A_-600_600(-2000_2000) |  | B2/D05_D1 | [8 empty] | 道爺DS.爺78線A0 | 23KV爺78線 N相AMP | FEEDER | [5 empty] | 243 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/E01D051/T2 |  | 0000 |  |  | 1-00-00 |  |  | 1DI-CH3 | 52AS | 1510 南科道爺一路CB |  | aaaa | B2/D05_A1 | [8 empty] | 道爺DS.1510_CB | 1510(南科道爺ㄧ路) CB | LINE161 | [5 empty] | 244 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0001 |  |  | 1-00-01 |  |  | 2DI-CH1 | 87LA | 1510 南科道爺一路 差動電驛警報87LA |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1510_87A | 南科道爺ㄧ路(1510) 87RY | LINE161 | [5 empty] | 245 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | 2DI-CH3 | PHA | 1510 南科道爺一路 相間電驛PHA |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1510_PHA | 南科道爺ㄧ路(1510) 相間RY | LINE161 | [5 empty] | 246 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0004 |  |  | 1-00-04 |  |  | 2DI-CH4 | GDA | 1510 南科道爺一路 接地電驛GDA |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1510_GDA | 南科道爺ㄧ路(1510) 接地RY | LINE161 | [5 empty] | 247 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/E01D052/T2 |  | 0005 |  |  | 1-00-05 |  |  | 1DI-CH3 | 52AS | 1520 南科道爺二路CB |  | aaba | B2/D05_A1 | [8 empty] | 道爺DS.1520_CB | 1520(南科道爺二路) CB | LINE161 | [5 empty] | 248 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | 2DI-CH1 | 87LA | 1520 南科道爺二路 差動電驛警報87LA |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1520_87A | 南科道爺二路(1520) 87RY | LINE161 | [5 empty] | 249 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-01-00 |  |  | 2DI-CH3 | PHA | 1520 南科道爺二路 相間電驛PHA |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1520_PHA | 南科道爺二路(1520) 相間RY | LINE161 | [5 empty] | 250 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | 2DI-CH4 | GDA | 1520 南科道爺二路 接地電驛GDA |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1520_GDA | 南科道爺二路(1520) 接地RY | LINE161 | [5 empty] | 251 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1530 | 南科～道爺三路(1530) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/E01D053/T2 |  | 0010 |  |  | 1-01-02 |  |  | 1DI-CH3 | 52AS | 1530 南科道爺三路CB |  | aaca | B2/D05_A1 | [8 empty] | 道爺DS.1530_CB | 1530(南科道爺三路) CB | LINE161 | [5 empty] | 252 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 161 | 161kV | 1530 | 南科～道爺三路(1530) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-03 |  |  | 2DI-CH1 | 87LA | 1530 南科道爺三路 差動電驛警報87LA |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1530_87A | 南科道爺三路(1530) 87RY | LINE161 | [5 empty] | 253 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1530 | 南科～道爺三路(1530) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0013 |  |  | 1-01-05 |  |  | 2DI-CH3 | PHA | 1530 南科道爺三路 相間電驛PHA |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1530_PHA | 南科道爺三路(1530) 相間RY | LINE161 | [5 empty] | 254 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1530 | 南科～道爺三路(1530) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-06 |  |  | 2DI-CH4 | GDA | 1530 南科道爺三路 接地電驛GDA |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1530_GDA | 南科道爺三路(1530) 接地RY | LINE161 | [5 empty] | 255 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1540 | 南科～道爺四路(1540) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/E01D054/T2 |  | 0015 |  |  | 1-01-07 |  |  | 1DI-CH3 | 52AS | 1540 南科道爺四路CB |  | aada | B2/D05_A1 | [8 empty] | 道爺DS.1540_CB | 1540(南科道爺四路) CB | LINE161 | [5 empty] | 256 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 161 | 161kV | 1540 | 南科～道爺四路(1540) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-02-00 |  |  | 2DI-CH1 | 87LA | 1540 南科道爺四路 差動電驛警報87LA |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1540_87A | 南科道爺四路(1540) 87RY | LINE161 | [5 empty] | 257 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1540 | 南科～道爺四路(1540) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 |  |  | 1-02-02 |  |  | 2DI-CH3 | PHA | 1540 南科道爺四路 相間電驛PHA |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1540_PHA | 南科道爺四路(1540) 相間RY | LINE161 | [5 empty] | 258 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1540 | 南科～道爺四路(1540) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0019 |  |  | 1-02-03 |  |  | 2DI-CH4 | GDA | 1540 南科道爺四路 接地電驛GDA |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1540_GDA | 南科道爺四路(1540) 接地RY | LINE161 | [5 empty] | 259 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺~奇晶七紅線(1550) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D05C12R/T1 |  | 0020 |  |  | 1-02-04 |  |  | 1DI-CH3 | 52AS | 1550 道爺奇晶七紅線CB |  | aafa | B2/D05_A1 | [8 empty] | 道爺DS.1550_CB | 1550(道爺奇晶七紅線) CB | LINE161 | [5 empty] | 260 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺~奇晶七紅線(1550) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-05 |  |  | 2DI-CH1 | 187LA | 1550 道爺奇晶七紅線 差動電驛警報187LA |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1550_87A1 | 奇晶七紅線(1550) #1 87RY | LINE161 | [5 empty] | 261 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺~奇晶七紅線(1550) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0022 |  |  | 1-02-06 |  |  | 2DI-CH6 | 287LA | 1550 道爺奇晶七紅線 差動電驛警報287LA |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1550_87A2 | 奇晶七紅線(1550) #2 87RY | LINE161 | [5 empty] | 262 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺~奇晶七紅線(1550) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0023 |  |  | 1-02-07 |  |  | 2DI-CH3 | PHA | 1550 道爺奇晶七紅線 相間電驛PHA |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1550_PHA | 道爺奇晶七紅線(1550) 相間RY | LINE161 | [5 empty] | 263 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺~奇晶七紅線(1550) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0024 |  |  | 1-03-00 |  |  | 2DI-CH4 | GDA | 1550 道爺奇晶七紅線 接地電驛GDA |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1550_GDA | 道爺奇晶七紅線(1550) 接地RY | LINE161 | [5 empty] | 264 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺~奇晶七白線(1560) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D05C12W/T1 |  | 0025 |  |  | 1-03-01 |  |  | 1DI-CH3 | 52AS | 1560 道爺奇晶七白線CB |  | aaga | B2/D05_A1 | [8 empty] | 道爺DS.1560_CB | 1560(道爺奇晶七白線) CB | LINE161 | [5 empty] | 265 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺~奇晶七白線(1560) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0026 |  |  | 1-03-02 |  |  | 1DI-CH1 | 187LA | 1560 道爺奇晶七白線 差動電驛警報187LA |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1560_87A1 | 奇晶七白線(1560) #1 87RY | LINE161 | [5 empty] | 266 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺~奇晶七白線(1560) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0027 |  |  | 1-03-03 |  |  | 2DI-CH6 | 287LA | 1560 道爺奇晶七白線 差動電驛警報287LA |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1560_87A2 | 奇晶七白線(1560) #2 87RY | LINE161 | [5 empty] | 267 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺~奇晶七白線(1560) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0028 |  |  | 1-03-04 |  |  | 2DI-CH3 | PHA | 1560 道爺奇晶七白線 相間電驛PHA |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1560_PHA | 道爺奇晶七白線(1560) 相間RY | LINE161 | [5 empty] | 268 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺~奇晶七白線(1560) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0029 |  |  | 1-03-05 |  |  | 2DI-CH4 | GDA | 1560 道爺奇晶七白線 接地電驛GDA |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1560_GDA | 道爺奇晶七白線(1560) 接地RY | LINE161 | [5 empty] | 269 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺～奇晶六紅線(1570) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D05C20R/T1 |  | 0030 |  |  | 1-03-06 |  |  | 1DI-CH3 | 52AS | 1570 道爺奇晶六線紅線CB |  | aaha | B2/D05_A1 | [8 empty] | 道爺DS.1570_CB | 1570(道爺奇晶六紅線) CB | LINE161 | [5 empty] | 270 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺～奇晶六紅線(1570) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0031 |  |  | 1-03-07 |  |  | 2DI-CH1 | 187LA | 1570 道爺奇晶六線紅線 差動電驛警報187LA |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1570_87A1 | 奇晶六紅線(1570) #1 87RY | LINE161 | [5 empty] | 271 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺～奇晶六紅線(1570) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0032 |  |  | 1-04-00 |  |  | 2DI-CH6 | 287LA | 1570 道爺奇晶六線紅線 差動電驛警報287LA |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1570_87A2 | 奇晶六紅線(1570) #2 87RY | LINE161 | [5 empty] | 272 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺～奇晶六紅線(1570) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0033 |  |  | 1-04-01 |  |  | 2DI-CH3 | PHA | 1570 道爺奇晶六線紅線 相間電驛PHA |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1570_PHA | 道爺奇晶六紅線(1570) 相間RY | LINE161 | [5 empty] | 273 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺～奇晶六紅線(1570) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0034 |  |  | 1-04-02 |  |  | 2DI-CH4 | GDA | 1570 道爺奇晶六線紅線 接地電驛GDA |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1570_GDA | 道爺奇晶六紅線(1570) 接地RY | LINE161 | [5 empty] | 274 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺～奇晶六白線(1580) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D05C20W/T1 |  | 0035 |  |  | 1-04-03 |  |  | 1DI-CH3 | 52AS | 1580 道爺奇晶六線白線CB |  | aaia | B2/D05_A1 | [8 empty] | 道爺DS.1580_CB | 1580(道爺奇晶六白線) CB | LINE161 | [5 empty] | 275 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺～奇晶六白線(1580) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0036 |  |  | 1-04-04 |  |  | 2DI-CH1 | 187LA | 1580 道爺奇晶六線白線 差動電驛警報187LA |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1580_87A1 | 奇晶六白線(1580) #1 87RY | LINE161 | [5 empty] | 276 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺～奇晶六白線(1580) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0037 |  |  | 1-04-05 |  |  | 2DI-CH6 | 287LA | 1580 道爺奇晶六線白線 差動電驛警報287LA |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1580_87A2 | 奇晶六白線(1580) #2 87RY | LINE161 | [5 empty] | 277 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺～奇晶六白線(1580) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0038 |  |  | 1-04-06 |  |  | 2DI-CH3 | PHA | 1580 道爺奇晶六線白線 相間電驛PHA |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1580_PHA | 道爺奇晶六白線(1580) 相間RY | LINE161 | [5 empty] | 278 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺～奇晶六白線(1580) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0039 |  |  | 1-04-07 |  |  | 2DI-CH4 | GDA | 1580 道爺奇晶六線白線 接地電驛GDA |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1580_GDA | 道爺奇晶六白線(1580) 接地RY | LINE161 | [5 empty] | 279 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1610 | 道爺~安南~新化線(1610) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/3Bus | B/4Bus | L/D05TN03/T2 |  | 0040 |  |  | 1-05-00 |  |  | 1DI-CH3 | 52AS | 1610 道爺安南新化線CB |  | abca | B2/D05_A1 | [8 empty] | 道爺DS.1610_CB | 1610(道爺安南新化線) CB | LINE161 | [5 empty] | 280 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 161 | 161kV | 1610 | 道爺~安南~新化線(1610) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0041 |  |  | 1-05-01 |  |  | 2DI-CH1 | 87LA | 1610 道爺安南新化線 差動電驛警報87LA |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1610_87A | 道爺安南新化線(1610) 87RY | LINE161 | [5 empty] | 281 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1610 | 道爺~安南~新化線(1610) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0043 |  |  | 1-05-03 |  |  | 2DI-CH3 | PHA | 1610 道爺安南新化線 相間電驛PHA |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1610_PHA | 道爺安南新化線(1610) 相間RY | LINE161 | [5 empty] | 282 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1610 | 道爺~安南~新化線(1610) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0044 |  |  | 1-05-04 |  |  | 2DI-CH4 | GDA | 1610 道爺安南新化線 接地電驛GDA |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1610_GDA | 道爺安南新化線(1610) 接地RY | LINE161 | [5 empty] | 283 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1620 | 道爺~和順~新化線(1620) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/3Bus | B/4Bus | L/D05TN04/T2 |  | 0045 |  |  | 1-05-05 |  |  | 1DI-CH3 | 52AS | 1620 道爺和順新化線CB |  | abda | B2/D05_A1 | [8 empty] | 道爺DS.1620_CB | 1620(道爺和順新化線) CB | LINE161 | [5 empty] | 284 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 161 | 161kV | 1620 | 道爺~和順~新化線(1620) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0046 |  |  | 1-05-06 |  |  | 2DI-CH1 | 87LA | 1620 道爺和順新化線 差動電驛警報87LA |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1620_87A | 道爺和順新化線(1620) 87RY | LINE161 | [5 empty] | 285 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1620 | 道爺~和順~新化線(1620) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0048 |  |  | 1-06-00 |  |  | 2DI-CH3 | PHA | 1620 道爺和順新化線 相間電驛PHA |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1620_PHA | 道爺和順新化線(1620) 相間RY | LINE161 | [5 empty] | 286 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1620 | 道爺~和順~新化線(1620) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0049 |  |  | 1-06-01 |  |  | 2DI-CH4 | GDA | 1620 道爺和順新化線 接地電驛GDA |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1620_GDA | 道爺和順新化線(1620) 接地RY | LINE161 | [5 empty] | 287 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0060 |  |  | 1-07-04 |  |  | 1DI-CH3 | 52AS | 1500 TIE CB |  | aaez | B2/D05_A1 | [8 empty] | 道爺DS.1500_CB | 1500(TIE) CB | TIE | [5 empty] | 288 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0061 |  |  | 1-07-05 |  |  | 1DI-CH8 | 50A | 1500 TIE 瞬時電驛50A |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1500_50A | 161KV TIE(1500) 50RY | TIE | [5 empty] | 289 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1600 | TIE(1600) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/3Bus | B/4Bus |  |  | 0062 |  |  | 1-07-06 |  |  | 1DI-CH3 | 52AS | 1600 TIE CB |  | abaz | B2/D05_A1 | [8 empty] | 道爺DS.1600_CB | 1600(TIE) CB | TIE | [5 empty] | 290 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 161 | 161kV | 1600 | TIE(1600) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0063 |  |  | 1-07-07 |  |  | 1DI-CH8 | 50A | 1600 TIE 瞬時電驛50A |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1600_50A | 161KV TIE(1600) 50RY | TIE | [5 empty] | 291 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1700 | TIE(1700) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect2B | B/1Bus | B/3Bus |  |  | 0064 |  |  | 1-08-00 |  |  | 1DI-CH3 | 52AS | 1700 SECTION1 CB |  | no rule | B2/D05_A1 | [8 empty] | 道爺DS.1700_CB | 1700(TIE) CB | TIE | [5 empty] | 292 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1800 | TIE(1800) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect2B | B/2Bus | B/4Bus |  |  | 0066 |  |  | 1-08-02 |  |  | 1DI-CH3 | 52AS | 1800 SECTION2 CB |  | no rule | B2/D05_A1 | [8 empty] | 道爺DS.1800_CB | 1800(TIE) CB | TIE | [5 empty] | 293 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 |  |  | 1-08-04 |  |  | 1DI-CH5 | 87B1A | 161KV #1BUS差動電驛(87B1A) |  |  | B2/D05_A1 | [8 empty] | 道爺DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | [5 empty] | 294 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 |  |  | 1-08-05 |  |  | 1DI-CH6 | 87B2A | 161KV #2BUS差動電驛(87B2A) |  |  | B2/D05_A1 | [8 empty] | 道爺DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | [5 empty] | 295 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 3BUS | #3BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0071 |  |  | 1-08-07 |  |  | 1DI-CH5 | 87B3A | 161KV #3BUS差動電驛(87B3A) |  |  | B2/D05_A1 | [8 empty] | 道爺DS.161#3BUS_87A | 161KV #3BUS 87RY | BUS | [5 empty] | 296 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 4BUS | #4BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0072 |  |  | 1-09-00 |  |  | 1DI-CH6 | 87B4A | 161KV #4BUS差動電驛(87B4A) |  |  | B2/D05_A1 | [8 empty] | 道爺DS.161#4BUS_87A | 161KV #4BUS 87RY | BUS | [5 empty] | 297 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2DTR |  | 0086 |  |  | 1-0A-06 |  |  | 1DI-CH3 | 52AS | 1760 CB |  | aakb | ELEM/D05_A1 | [8 empty] | 道爺DS.1760_CB | 1760(#2DTR) CB | MTR | [5 empty] | 298 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS |  |  | 2DTR | #2DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0087 |  |  | 1-0A-07 |  |  | 1DI-CH5 | 87TA | #2 DTR 差動電驛警報(87TA) |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#2DTR_87A | #2DTR 87RY | MTR | [5 empty] | 299 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS |  |  | 2DTR | #2DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0088 |  |  | 1-0B-00 |  |  | 1DI-CH6 | 96PA | #2 DTR 衝擊油壓警報(96PA) |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | [5 empty] | 300 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS |  |  | 2DTR | #2DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0089 |  |  | 1-0B-01 |  |  | 1DI-CH7 | 51ZA | #2 DTR 中性點接地電驛(51ZA) |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | [5 empty] | 301 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS |  |  | 2DTR | #2DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0090 |  |  | 1-0B-02 |  |  | 2DI-CH7 | RYFA | #2 DTR RYFA |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#2DTR_RYFA | #2DTR 數位電驛故障 | OTHER | [5 empty] | 302 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS |  |  | 2DTR | #2DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0091 |  |  | 1-0B-03 |  |  | 2DI-CH8 | 86A | #2 DTR 86A |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#2DTR_86A | #2DTR 86(50/50N/51Z/87/96)RY | OTHER | [5 empty] | 303 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | A/340^T/2DTR(A) |  |  | 0092 |  |  | 1-0B-04 |  |  | 2DI-CH8 | 52AS | 330 CB |  | aaha | ELEM/D05_A1 | [8 empty] | 道爺DS.330_CB | 330(#2DTR) CB | MTR | [5 empty] | 304 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0093 |  |  | 1-0B-05 |  |  | 2DI-CH1 | PHA | 330 相間電驛PHA |  |  | B3/D05_A1 | [8 empty] | 道爺DS.330_51A | #2DTR二次側(330) 51RY | MTR | [5 empty] | 305 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0094 |  |  | 1-0B-06 |  |  | 2DI-CH2 | GDA | 330 接地電驛GDA |  |  | B3/D05_A1 | [8 empty] | 道爺DS.330_GDA | 330開關箱IED RY GDA | OTHER | [5 empty] | 306 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | A/330^T/2DTR(B) |  |  | 0095 |  |  | 1-0B-07 |  |  | 2DI-CH8 | 52AS | 340 CB |  | baba | ELEM/D05_A1 | [8 empty] | 道爺DS.340_CB | 340(#2DTR) CB | MTR | [5 empty] | 307 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0096 |  |  | 1-0C-00 |  |  | 2DI-CH1 | PHA | 340 相間電驛PHA |  |  | B3/D05_A1 | [8 empty] | 道爺DS.340_51A | #2DTR二次側(340) 51RY | MTR | [5 empty] | 308 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0097 |  |  | 1-0C-01 |  |  | 2DI-CH2 | GDA | 340 接地電驛GDA |  |  | B3/D05_A1 | [8 empty] | 道爺DS.340_GDA | 340開關箱IED RY GDA | OTHER | [5 empty] | 309 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/3Bus | B/4Bus | T/3DTR |  | 0098 |  |  | 1-0C-02 |  |  | 1DI-CH3 | 52AS | 1770 CB |  | abbb | ELEM/D05_A1 | [8 empty] | 道爺DS.1770_CB | 1770(#3DTR) CB | MTR | [5 empty] | 310 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS |  |  | 3DTR | #3DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0099 |  |  | 1-0C-03 |  |  | 1DI-CH5 | 87TA | #3 DTR 差動電驛警報(87TA) |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#3DTR_87A | #3DTR 87RY | MTR | [5 empty] | 311 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS |  |  | 3DTR | #3DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0100 |  |  | 1-0C-04 |  |  | 1DI-CH6 | 96PA | #3 DTR 衝擊油壓警報(96PA) |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#3DTR_96PA | #3DTR 機械保護動作 | MTR | [5 empty] | 312 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS |  |  | 3DTR | #3DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0101 |  |  | 1-0C-05 |  |  | 1DI-CH7 | 51ZA | #3 DTR 中性點接地電驛(51ZA) |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#3DTR_51ZA | #3DTR 51Z RY | MTR | [5 empty] | 313 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS |  |  | 3DTR | #3DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0102 |  |  | 1-0C-06 |  |  | 2DI-CH7 | RYFA | #3 DTR RYFA |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#3DTR_RYFA | #3DTR 數位電驛故障 | OTHER | [5 empty] | 314 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS |  |  | 3DTR | #3DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0103 |  |  | 1-0C-07 |  |  | 2DI-CH8 | 86A | #3 DTR 86A |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#3DTR_86A | #3DTR 86(50/50N/51Z/87/96)RY | OTHER | [5 empty] | 315 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3ABus | A/360^T/3DTR(A) |  |  | 0104 |  |  | 1-0D-00 |  |  | 2DI-CH8 | 52AS | 350 CB |  | abga | ELEM/D05_A1 | [8 empty] | 道爺DS.350_CB | 350(#3DTR) CB | MTR | [5 empty] | 316 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0105 |  |  | 1-0D-01 |  |  | 2DI-CH1 | PHA | 350 相間電驛PHA |  |  | B3/D05_A1 | [8 empty] | 道爺DS.350_51A | #3DTR二次側(350) 51RY | MTR | [5 empty] | 317 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0106 |  |  | 1-0D-02 |  |  | 2DI-CH2 | GDA | 350 接地電驛GDA |  |  | B3/D05_A1 | [8 empty] | 道爺DS.350_GDA | 350開關箱IED RY GDA | OTHER | [5 empty] | 318 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3BBus | A/350^T/3DTR(B) |  |  | 0107 |  |  | 1-0D-03 |  |  | 2DI-CH8 | 52AS | 360 CB |  | bbha | ELEM/D05_A1 | [8 empty] | 道爺DS.360_CB | 360(#3DTR) CB | MTR | [5 empty] | 319 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0108 |  |  | 1-0D-04 |  |  | 2DI-CH1 | PHA | 360 相間電驛PHA |  |  | B3/D05_A1 | [8 empty] | 道爺DS.360_51A | #3DTR二次側(360) 51RY | MTR | [5 empty] | 320 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0109 |  |  | 1-0D-05 |  |  | 2DI-CH2 | GDA | 360 接地電驛GDA |  |  | B3/D05_A1 | [8 empty] | 道爺DS.360_GDA | 360開關箱IED RY GDA | OTHER | [5 empty] | 321 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0122 |  |  | 1-0F-02 |  |  | 軟體點 | 1 RCA | 161KV 系統79電驛動作(RCA) |  |  | B3/D05_A1 | [8 empty] | 道爺DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | [5 empty] | 322 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0123 |  |  | 1-0F-03 |  |  | 軟體點 | 2 RCA | 23KV 系統79電驛動作(RCA) |  |  | B3/D05_A1 | [8 empty] | 道爺DS.11/23KV_RCA | 11/23KV饋線 79RY(復閉)動作 | OTHER | [5 empty] | 323 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0124 |  |  | 1-0F-04 |  |  | 軟體點 | OSCA | 161KV 系統示波器啟動警報(OSCA) |  |  | B3/D05_A1 | [8 empty] | 道爺DS.161KV_OSCA | 161KV示波器啟動警報 | OTHER | [5 empty] | 324 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0125 |  |  | 1-0F-05 |  |  | 軟體點 | OSCF | 161KV 系統示波器故障警報(OSCF) |  |  | B3/D05_A1 | [8 empty] | 道爺DS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | [5 empty] | 325 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | ComPoint |  |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0126 |  |  | 1-0F-06 |  |  | 軟體點 | LOA | 23KV 79 LOA |  |  | B3/D05_A1 | [8 empty] | 道爺DS.11/23KV_LOA | 11/23KV饋線復閉失敗閉鎖 | OTHER | [5 empty] | 326 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | DTTA |  |  | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0127 |  |  | 1-0F-07 |  |  | 1DI-CH2 | DTTA | 1510 南科道爺一路 通訊直接跳脫 |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1510_DTTA | 南科道爺ㄧ路(1510) 遠方遙跳 | OTHER | [5 empty] | 327 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | DTTA |  |  | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0128 |  |  | 1-10-00 |  |  | 1DI-CH2 | DTTA | 1520 南科道爺二路 通訊直接跳脫 |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1520_DTTA | 南科道爺二路(1520) 遠方遙跳 | OTHER | [5 empty] | 328 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1530 | 南科～道爺三路(1530) |  | DTTA |  |  | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0129 |  |  | 1-10-01 |  |  | 1DI-CH2 | DTTA | 1530 南科道爺三路 通訊直接跳脫 |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1530_DTTA | 南科道爺三路(1530) 遠方遙跳 | OTHER | [5 empty] | 329 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1540 | 南科～道爺四路(1540) |  | DTTA |  |  | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-10-02 |  |  | 1DI-CH2 | DTTA | 1540 南科道爺四路 通訊直接跳脫 |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1540_DTTA | 南科道爺四路(1540) 遠方遙跳 | OTHER | [5 empty] | 330 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS |  |  | 2DTR | #2DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0141 |  |  | 1-11-05 |  |  | Locate Empty |  | #2 DTR PHA |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#2DTR_PHA | #2DTR 50/51 RY | OTHER | [5 empty] | 331 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS |  |  | 2DTR | #2DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0142 |  |  | 1-11-06 |  |  | Locate Empty |  | #2 DTR GDA |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#2DTR_GDA | #2DTR 50N/51N RY | OTHER | [5 empty] | 332 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS |  |  | 3DTR | #3DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0143 |  |  | 1-11-07 |  |  | Locate Empty |  | #3 DTR PHA |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#3DTR_PHA | #3DTR 50/51 RY | OTHER | [5 empty] | 333 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS |  |  | 3DTR | #3DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0144 |  |  | 1-12-00 |  |  | Locate Empty |  | #3 DTR GDA |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#3DTR_GDA | #3DTR 50N/51N RY | OTHER | [5 empty] | 334 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 200 | TIE(200) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/2ABus | B/3BBus |  |  | 0193 |  |  | 1-18-01 |  |  | 2DI-CH8 | 52AS | 200 CB |  | aaab | B3/D05_A1 | [8 empty] | 道爺DS.200_CB | 200(TIE) CB | TIE | [5 empty] | 335 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 22 | 22kV | 200 | TIE(200) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0194 |  |  | 1-18-02 |  |  | 2DI-CH1 | PHA | 200 相間電驛PHA |  |  | B3/D05_A1 | [8 empty] | 道爺DS.200_51A | 23KV TIE(200) 51RY | TIE | [5 empty] | 336 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 200 | TIE(200) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0195 |  |  | 1-18-03 |  |  | 2DI-CH2 | GDA | 200 接地電驛GDA |  |  | B3/D05_A1 | [8 empty] | 道爺DS.200_51NA | 23KV TIE(200) 51N RY | TIE | [5 empty] | 337 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 230 | #3SC(230) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | C/3SC |  |  | 0196 |  |  | 1-18-04 |  |  | 2DI-CH8 | 52AS | 230 CB |  | aagb | B3/D05_A1 | [8 empty] | 道爺DS.230_CB | 230(23KV #3SC) CB | SC | [5 empty] | 338 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 230 | #3SC(230) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0197 |  |  | 1-18-05 |  |  | 2DI-CH1 | SCA | 230 相間及接地電驛(SCA) |  |  | B3/D05_A1 | [8 empty] | 道爺DS.230_SCA | 23KV #3SC 51,51N RY | SC | [5 empty] | 339 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 230 | #3SC(230) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0198 |  |  | 1-18-06 |  |  | 2DI-CH2 | UVA | 230 欠壓電驛(UVA) |  |  | B3/D05_A1 | [8 empty] | 道爺DS.230_OUVA | 23KV #3SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 340 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K61 | 爺61線(4K61) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/4K61/T1 |  |  | 0199 |  |  | 1-18-07 |  |  | 2DI-CH8 | 52AS | 爺61線（4K61） CB |  | aabb | B2/D05_D1 | [8 empty] | 道爺DS.4K61_CB | 4K61(23KV爺61線) CB | FEEDER | [5 empty] | 341 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K61 | 爺61線(4K61) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0200 |  |  | 1-19-00 |  |  | 2DI-CH1 | PHA | 爺61線（4K61） 相間電驛PHA |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K61_PHA | 23KV爺61線(4K61) 相間RY | FEEDER | [5 empty] | 342 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K61 | 爺61線(4K61) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0201 |  |  | 1-19-01 |  |  | 2DI-CH2 | GDA | 爺61線（4K61） 接地電驛GDA |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K61_GDA | 23KV爺61線(4K61) 接地RY | FEEDER | [5 empty] | 343 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K62 | 爺62線(4K62) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/4K62/T1 |  |  | 0202 |  |  | 1-19-02 |  |  | 2DI-CH8 | 52AS | 爺62線（4K62） CB |  | aacb | B2/D05_D1 | [8 empty] | 道爺DS.4K62_CB | 4K62(23KV爺62線) CB | FEEDER | [5 empty] | 344 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K62 | 爺62線(4K62) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0203 |  |  | 1-19-03 |  |  | 2DI-CH1 | PHA | 爺62線（4K62） 相間電驛PHA |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K62_PHA | 23KV爺62線(4K62) 相間RY | FEEDER | [5 empty] | 345 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K62 | 爺62線(4K62) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0204 |  |  | 1-19-04 |  |  | 2DI-CH2 | GDA | 爺62線（4K62） 接地電驛GDA |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K62_GDA | 23KV爺62線(4K62) 接地RY | FEEDER | [5 empty] | 346 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K63 | 爺63線(4K63) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/4K63/T1 |  |  | 0205 |  |  | 1-19-05 |  |  | 2DI-CH8 | 52AS | 爺63線（4K63） CB |  | aadb | B2/D05_D1 | [8 empty] | 道爺DS.4K63_CB | 4K63(23KV爺63線) CB | FEEDER | [5 empty] | 347 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K63 | 爺63線(4K63) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0206 |  |  | 1-19-06 |  |  | 2DI-CH1 | PHA | 爺63線（4K63） 相間電驛PHA |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K63_PHA | 23KV爺63線(4K63) 相間RY | FEEDER | [5 empty] | 348 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K63 | 爺63線(4K63) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0207 |  |  | 1-19-07 |  |  | 2DI-CH2 | GDA | 爺63線（4K63） 接地電驛GDA |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K63_GDA | 23KV爺63線(4K63) 接地RY | FEEDER | [5 empty] | 349 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K64 | 爺64線(4K64) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/4K64/T1 |  |  | 0208 |  |  | 1-1A-00 |  |  | 2DI-CH8 | 52AS | 爺64線（4K64） CB |  | aaeb | B2/D05_D1 | [8 empty] | 道爺DS.4K64_CB | 4K64(23KV爺64線) CB | FEEDER | [5 empty] | 350 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K64 | 爺64線(4K64) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0209 |  |  | 1-1A-01 |  |  | 2DI-CH1 | PHA | 爺64線（4K64） 相間電驛PHA |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K64_PHA | 23KV爺64線(4K64) 相間RY | FEEDER | [5 empty] | 351 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K64 | 爺64線(4K64) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0210 |  |  | 1-1A-02 |  |  | 2DI-CH2 | GDA | 爺64線（4K64） 接地電驛GDA |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K64_GDA | 23KV爺64線(4K64) 接地RY | FEEDER | [5 empty] | 352 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 240 | #4SC(240) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | C/4SC |  |  | 0211 |  |  | 1-1A-03 |  |  | 2DI-CH8 | 52AS | 240 CB |  | bahb | B3/D05_A1 | [8 empty] | 道爺DS.240_CB | 240(23KV #4SC) CB | SC | [5 empty] | 353 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 240 | #4SC(240) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0212 |  |  | 1-1A-04 |  |  | 2DI-CH1 | SCA | 240 相間及接地電驛(SCA) |  |  | B3/D05_A1 | [8 empty] | 道爺DS.240_SCA | 23KV #4SC 51,51N RY | SC | [5 empty] | 354 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 240 | #4SC(240) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0213 |  |  | 1-1A-05 |  |  | 2DI-CH2 | UVA | 240 欠壓電驛(UVA) |  |  | B3/D05_A1 | [8 empty] | 道爺DS.240_OUVA | 23KV #4SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 355 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K65 | 爺65線(4K65) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/4K65/T1 |  |  | 0214 |  |  | 1-1A-06 |  |  | 2DI-CH8 | 52AS | 爺65線（4K65） CB |  | bacb | B2/D05_D1 | [8 empty] | 道爺DS.4K65_CB | 4K65(23KV爺65線) CB | FEEDER | [5 empty] | 356 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K65 | 爺65線(4K65) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0215 |  |  | 1-1A-07 |  |  | 2DI-CH1 | PHA | 爺65線（4K65） 相間電驛PHA |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K65_PHA | 23KV爺65線(4K65) 相間RY | FEEDER | [5 empty] | 357 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K65 | 爺65線(4K65) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0216 |  |  | 1-1B-00 |  |  | 2DI-CH2 | GDA | 爺65線（4K65） 接地電驛GDA |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K65_GDA | 23KV爺65線(4K65) 接地RY | FEEDER | [5 empty] | 358 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K66 | 爺66線(4K66) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/4K66/T1 |  |  | 0217 |  |  | 1-1B-01 |  |  | 2DI-CH8 | 52AS | 爺66線（4K66） CB |  | badb | B2/D05_D1 | [8 empty] | 道爺DS.4K66_CB | 4K66(23KV爺66線) CB | FEEDER | [5 empty] | 359 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K66 | 爺66線(4K66) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0218 |  |  | 1-1B-02 |  |  | 2DI-CH1 | PHA | 爺66線（4K66） 相間電驛PHA |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K66_PHA | 23KV爺66線(4K66) 相間RY | FEEDER | [5 empty] | 360 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K66 | 爺66線(4K66) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0219 |  |  | 1-1B-03 |  |  | 2DI-CH2 | GDA | 爺66線（4K66） 接地電驛GDA |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K66_GDA | 23KV爺66線(4K66) 接地RY | FEEDER | [5 empty] | 361 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K67 | 爺67線(4K67) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/4K67/T1 |  |  | 0220 |  |  | 1-1B-04 |  |  | 2DI-CH8 | 52AS | 爺67線（4K67） CB |  | baeb | B2/D05_D1 | [8 empty] | 道爺DS.4K67_CB | 4K67(23KV爺67線) CB | FEEDER | [5 empty] | 362 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K67 | 爺67線(4K67) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0221 |  |  | 1-1B-05 |  |  | 2DI-CH1 | PHA | 爺67線（4K67） 相間電驛PHA |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K67_PHA | 23KV爺67線(4K67) 相間RY | FEEDER | [5 empty] | 363 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K67 | 爺67線(4K67) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0222 |  |  | 1-1B-06 |  |  | 2DI-CH2 | GDA | 爺67線（4K67） 接地電驛GDA |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K67_GDA | 23KV爺67線(4K67) 接地RY | FEEDER | [5 empty] | 364 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K68 | 爺68線(4K68) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/4K68/T1 |  |  | 0223 |  |  | 1-1B-07 |  |  | 2DI-CH8 | 52AS | 爺68線（4K68） CB |  | bafb | B2/D05_D1 | [8 empty] | 道爺DS.4K68_CB | 4K68(23KV爺68線) CB | FEEDER | [5 empty] | 365 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K68 | 爺68線(4K68) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0224 |  |  | 1-1C-00 |  |  | 2DI-CH1 | PHA | 爺68線（4K68） 相間電驛PHA |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K68_PHA | 23KV爺68線(4K68) 相間RY | FEEDER | [5 empty] | 366 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K68 | 爺68線(4K68) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0225 |  |  | 1-1C-01 |  |  | 2DI-CH2 | GDA | 爺68線（4K68） 接地電驛GDA |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K68_GDA | 23KV爺68線(4K68) 接地RY | FEEDER | [5 empty] | 367 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 390 | #1SSTR(390) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | T/1SSTR |  |  | 0226 |  |  | 1-1C-02 |  |  | 2DI-CH8 | 52AS | 390 CB |  | bagb | B3/D05_A1 | [8 empty] | 道爺DS.390_CB | 390(#1SSTR) CB | OTHER | [5 empty] | 368 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 390 | #1SSTR(390) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0227 |  |  | 1-1C-03 |  |  | 2DI-CH1 | PHA | 390 相間電驛PHA |  |  | B3/D05_A1 | [8 empty] | 道爺DS.#1SSTR_51A | #1SSTR 51RY | OTHER | [5 empty] | 369 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 390 | #1SSTR(390) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0228 |  |  | 1-1C-04 |  |  | 2DI-CH2 | GDA | 390 接地電驛GDA |  |  | B3/D05_A1 | [8 empty] | 道爺DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | [5 empty] | 370 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 300 | TIE(300) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/3ABus | B/2BBus |  |  | 0229 |  |  | 1-1C-05 |  |  | 2DI-CH8 | 52AS | 300 CB |  | abab | B3/D05_A1 | [8 empty] | 道爺DS.300_CB | 300(TIE) CB | TIE | [5 empty] | 371 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D05 | 道爺DS | 22 | 22kV | 300 | TIE(300) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0230 |  |  | 1-1C-06 |  |  | 2DI-CH1 | PHA | 300 相間電驛PHA |  |  | B3/D05_A1 | [8 empty] | 道爺DS.300_51A | 23KV TIE(300) 51RY | TIE | [5 empty] | 372 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 300 | TIE(300) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0231 |  |  | 1-1C-07 |  |  | 2DI-CH2 | GDA | 300 接地電驛GDA |  |  | B3/D05_A1 | [8 empty] | 道爺DS.300_51NA | 23KV TIE(300) 51N RY | TIE | [5 empty] | 373 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 250 | #5SC(250) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3ABus | C/5SC |  |  | 0232 |  |  | 1-1D-00 |  |  | 2DI-CH8 | 52AS | 250 CB |  | abfb | B3/D05_A1 | [8 empty] | 道爺DS.250_CB | 250(23KV #5SC) CB | SC | [5 empty] | 374 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 250 | #5SC(250) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0233 |  |  | 1-1D-01 |  |  | 2DI-CH1 | SCA | 250 相間及接地電驛(SCA) |  |  | B3/D05_A1 | [8 empty] | 道爺DS.250_SCA | 23KV #5SC 51,51N RY | SC | [5 empty] | 375 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 250 | #5SC(250) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0234 |  |  | 1-1D-02 |  |  | 2DI-CH2 | UVA | 250 欠壓電驛(UVA) |  |  | B3/D05_A1 | [8 empty] | 道爺DS.250_OUVA | 23KV #5SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 376 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K71 | 爺71線(4K71) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3ABus | L/4K71/T1 |  |  | 0235 |  |  | 1-1D-03 |  |  | 2DI-CH8 | 52AS | 爺71線（4K71） CB |  | abbb | B2/D05_D1 | [8 empty] | 道爺DS.4K71_CB | 4K71(23KV爺71線) CB | FEEDER | [5 empty] | 377 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K71 | 爺71線(4K71) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0236 |  |  | 1-1D-04 |  |  | 2DI-CH1 | PHA | 爺71線（4K71） 相間電驛PHA |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K71_PHA | 23KV爺71線(4K71) 相間RY | FEEDER | [5 empty] | 378 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K71 | 爺71線(4K71) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0237 |  |  | 1-1D-05 |  |  | 2DI-CH2 | GDA | 爺71線（4K71） 接地電驛GDA |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K71_GDA | 23KV爺71線(4K71) 接地RY | FEEDER | [5 empty] | 379 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K72 | 爺72線(4K72) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3ABus | L/4K72/T1 |  |  | 0238 |  |  | 1-1D-06 |  |  | 2DI-CH8 | 52AS | 爺72線（4K72） CB |  | abcb | B2/D05_D1 | [8 empty] | 道爺DS.4K72_CB | 4K72(23KV爺72線) CB | FEEDER | [5 empty] | 380 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K72 | 爺72線(4K72) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0239 |  |  | 1-1D-07 |  |  | 2DI-CH1 | PHA | 爺72線（4K72） 相間電驛PHA |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K72_PHA | 23KV爺72線(4K72) 相間RY | FEEDER | [5 empty] | 381 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K72 | 爺72線(4K72) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0240 |  |  | 1-1E-00 |  |  | 2DI-CH2 | GDA | 爺72線（4K72） 接地電驛GDA |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K72_GDA | 23KV爺72線(4K72) 接地RY | FEEDER | [5 empty] | 382 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K73 | 爺73線(4K73) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3ABus | L/4K73/T1 |  |  | 0241 |  |  | 1-1E-01 |  |  | 2DI-CH8 | 52AS | 爺73線（4K73） CB |  | abdb | B2/D05_D1 | [8 empty] | 道爺DS.4K73_CB | 4K73(23KV爺73線) CB | FEEDER | [5 empty] | 383 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K73 | 爺73線(4K73) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0242 |  |  | 1-1E-02 |  |  | 2DI-CH1 | PHA | 爺73線（4K73） 相間電驛PHA |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K73_PHA | 23KV爺73線(4K73) 相間RY | FEEDER | [5 empty] | 384 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K73 | 爺73線(4K73) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0243 |  |  | 1-1E-03 |  |  | 2DI-CH2 | GDA | 爺73線（4K73） 接地電驛GDA |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K73_GDA | 23KV爺73線(4K73) 接地RY | FEEDER | [5 empty] | 385 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K74 | 爺74線(4K74) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3ABus | L/4K74/T1 |  |  | 0244 |  |  | 1-1E-04 |  |  | 2DI-CH8 | 52AS | 爺74線（4K74） CB |  | abeb | B2/D05_D1 | [8 empty] | 道爺DS.4K74_CB | 4K74(23KV爺74線) CB | FEEDER | [5 empty] | 386 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K74 | 爺74線(4K74) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0245 |  |  | 1-1E-05 |  |  | 2DI-CH1 | PHA | 爺74線（4K74） 相間電驛PHA |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K74_PHA | 23KV爺74線(4K74) 相間RY | FEEDER | [5 empty] | 387 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K74 | 爺74線(4K74) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0246 |  |  | 1-1E-06 |  |  | 2DI-CH2 | GDA | 爺74線（4K74） 接地電驛GDA |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K74_GDA | 23KV爺74線(4K74) 接地RY | FEEDER | [5 empty] | 388 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 260 | #6SC(260) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3BBus | C/6SC |  |  | 0247 |  |  | 1-1E-07 |  |  | 2DI-CH8 | 52AS | 260 CB |  | bbab | B3/D05_A1 | [8 empty] | 道爺DS.260_CB | 260(23KV #6SC) CB | SC | [5 empty] | 389 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 260 | #6SC(260) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0248 |  |  | 1-1F-00 |  |  | 2DI-CH1 | SCA | 260 相間及接地電驛(SCA) |  |  | B3/D05_A1 | [8 empty] | 道爺DS.260_SCA | 23KV #6SC 51,51N RY | SC | [5 empty] | 390 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 260 | #6SC(260) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0249 |  |  | 1-1F-01 |  |  | 2DI-CH2 | UVA | 260 欠壓電驛(UVA) |  |  | B3/D05_A1 | [8 empty] | 道爺DS.260_OUVA | 23KV #6SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 391 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K75 | 爺75線(4K75) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BBus | L/4K75/T1 |  |  | 0250 |  |  | 1-1F-02 |  |  | 2DI-CH8 | 52AS | 爺75線（4K75） CB |  | bbgb | B2/D05_D1 | [8 empty] | 道爺DS.4K75_CB | 4K75(23KV爺75線) CB | FEEDER | [5 empty] | 392 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K75 | 爺75線(4K75) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0251 |  |  | 1-1F-03 |  |  | 2DI-CH1 | PHA | 爺75線（4K75） 相間電驛PHA |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K75_PHA | 23KV爺75線(4K75) 相間RY | FEEDER | [5 empty] | 393 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K75 | 爺75線(4K75) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0252 |  |  | 1-1F-04 |  |  | 2DI-CH2 | GDA | 爺75線（4K75） 接地電驛GDA |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K75_GDA | 23KV爺75線(4K75) 接地RY | FEEDER | [5 empty] | 394 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K76 | 爺76線(4K76) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BBus | L/4K76/T1 |  |  | 0253 |  |  | 1-1F-05 |  |  | 2DI-CH8 | 52AS | 爺76線（4K76） CB |  | bbfb | B2/D05_D1 | [8 empty] | 道爺DS.4K76_CB | 4K76(23KV爺76線) CB | FEEDER | [5 empty] | 395 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K76 | 爺76線(4K76) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0254 |  |  | 1-1F-06 |  |  | 2DI-CH1 | PHA | 爺76線（4K76） 相間電驛PHA |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K76_PHA | 23KV爺76線(4K76) 相間RY | FEEDER | [5 empty] | 396 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K76 | 爺76線(4K76) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0255 |  |  | 1-1F-07 |  |  | 2DI-CH2 | GDA | 爺76線（4K76） 接地電驛GDA |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K76_GDA | 23KV爺76線(4K76) 接地RY | FEEDER | [5 empty] | 397 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K77 | 爺77線(4K77) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BBus | L/4K77/T1 |  |  | 0256 |  |  | 2-00-00 |  |  | 2DI-CH8 | 52AS | 爺77線（4K77） CB |  | bbeb | B2/D05_D1 | [8 empty] | 道爺DS.4K77_CB | 4K77(23KV爺77線) CB | FEEDER | [5 empty] | 398 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K77 | 爺77線(4K77) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0257 |  |  | 2-00-01 |  |  | 2DI-CH1 | PHA | 爺77線（4K77） 相間電驛PHA |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K77_PHA | 23KV爺77線(4K77) 相間RY | FEEDER | [5 empty] | 399 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K77 | 爺77線(4K77) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0258 |  |  | 2-00-02 |  |  | 2DI-CH2 | GDA | 爺77線（4K77） 接地電驛GDA |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K77_GDA | 23KV爺77線(4K77) 接地RY | FEEDER | [5 empty] | 400 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K78 | 爺78線(4K78) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BBus | L/4K78/T1 |  |  | 0259 |  |  | 2-00-03 |  |  | 2DI-CH8 | 52AS | 爺78線（4K78） CB |  | bbcb | B2/D05_D1 | [8 empty] | 道爺DS.4K78_CB | 4K78(23KV爺78線) CB | FEEDER | [5 empty] | 401 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K78 | 爺78線(4K78) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0260 |  |  | 2-00-04 |  |  | 2DI-CH1 | PHA | 爺78線（4K78） 相間電驛PHA |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K78_PHA | 23KV爺78線(4K78) 相間RY | FEEDER | [5 empty] | 402 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K78 | 爺78線(4K78) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0261 |  |  | 2-00-05 |  |  | 2DI-CH2 | GDA | 爺78線（4K78） 接地電驛GDA |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K78_GDA | 23KV爺78線(4K78) 接地RY | FEEDER | [5 empty] | 403 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 490 | #2SSTR(490) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3BBus | T/2SSTR |  |  | 0262 |  |  | 2-00-06 |  |  | 2DI-CH8 | 52AS | 490 CB |  | bbbb | B3/D05_A1 | [8 empty] | 道爺DS.490_CB | 490(#2SSTR) CB | OTHER | [5 empty] | 404 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 490 | #2SSTR(490) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0263 |  |  | 2-00-07 |  |  | 2DI-CH1 | PHA | 490 相間電驛PHA |  |  | B3/D05_A1 | [8 empty] | 道爺DS.#2SSTR_51A | #2SSTR 51RY | OTHER | [5 empty] | 405 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 490 | #2SSTR(490) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0264 |  |  | 2-01-00 |  |  | 2DI-CH2 | GDA | 490 接地電驛GDA |  |  | B3/D05_A1 | [8 empty] | 道爺DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | [5 empty] | 406 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0308 |  |  | 2-06-04 |  |  | 3DI-CH6 | 81A | 330 低頻電驛警報 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.330_81A | 330 #2DTR(A) 81RY動作 | OTHER | [5 empty] | 407 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0309 |  |  | 2-06-05 |  |  | 3DI-CH6 | 81A | 340 低頻電驛警報 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.340_81A | 340 #2DTR(B) 81RY動作 | OTHER | [5 empty] | 408 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0310 |  |  | 2-06-06 |  |  | 3DI-CH6 | 81A | 350 低頻電驛警報 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.350_81A | 350 #3DTR(A) 81RY動作 | OTHER | [5 empty] | 409 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0311 |  |  | 2-06-07 |  |  | 3DI-CH6 | 81A | 360 低頻電驛警報 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.360_81A | 360 #3DTR(B) 81RY動作 | OTHER | [5 empty] | 410 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0512 |  |  | 1-30-00 |  |  | 3DI-CH8 |  | TEST CB |  |  | ELEM/ALL | [8 empty] | 道爺DS.TEST_CB | TEST CB | OTHER | [5 empty] | 411 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | RTU | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0513 |  |  | 1-30-01 |  |  | Locate Empty | L/R | Com Server Local / Remote |  |  | ELEM/D05_A1 | [8 empty] | 道爺DS.COMM_S/L | 通訊處理單元 SUPY/LOCAL | OTHER | [5 empty] | 412 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
D05 | 道爺DS | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0514 |  |  | 1-30-02 |  |  | 1DI-CH1 | 87LS | 1510 南科道爺一路 差動電驛閉鎖開關(87LS) |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1510_87UL | 南科道爺ㄧ路(1510) 87RY U/L | LINE161 | [5 empty] | 413 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0516 |  |  | 1-30-04 |  |  | 1DI-CH3 | 79S | 1510 南科道爺一路 復閉電驛閉鎖開關(79) |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1510_79UL | 南科道爺ㄧ路(1510) 79RY U/L | LINE161 | [5 empty] | 414 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0517 |  |  | 1-30-05 |  |  | 1DI-CH1 | 87LS | 1520 南科道爺二路 差動電驛閉鎖開關(87LS) |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1520_87UL | 南科道爺二路(1520) 87RY U/L | LINE161 | [5 empty] | 415 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0519 |  |  | 1-30-07 |  |  | 1DI-CH3 | 79S | 1520 南科道爺二路 復閉電驛閉鎖開關(79) |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1520_79UL | 南科道爺二路(1520) 79RY U/L | LINE161 | [5 empty] | 416 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1530 | 南科～道爺三路(1530) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0520 |  |  | 1-30-08 |  |  | 1DI-CH1 | 87LS | 1530 南科道爺三路 差動電驛閉鎖開關(87LS) |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1530_87UL | 南科道爺三路(1530) 87RY U/L | LINE161 | [5 empty] | 417 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1530 | 南科～道爺三路(1530) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0522 |  |  | 1-30-10 |  |  | 1DI-CH3 | 79S | 1530 南科道爺三路 復閉電驛閉鎖開關(79) |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1530_79UL | 南科道爺三路(1530) 79RY U/L | LINE161 | [5 empty] | 418 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1540 | 南科～道爺四路(1540) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0523 |  |  | 1-30-11 |  |  | 1DI-CH1 | 87LS | 1540 南科道爺四路 差動電驛閉鎖開關(87LS) |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1540_87UL | 南科道爺四路(1540) 87RY U/L | LINE161 | [5 empty] | 419 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1540 | 南科～道爺四路(1540) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0525 |  |  | 1-30-13 |  |  | 1DI-CH3 | 79S | 1540 南科道爺四路 復閉電驛閉鎖開關(79) |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1540_79UL | 南科道爺四路(1540) 79RY U/L | LINE161 | [5 empty] | 420 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺~奇晶七紅線(1550) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0526 |  |  | 1-30-14 |  |  | 1DI-CH1 | 187LS | 1550 道爺奇晶七紅線 差動電驛閉鎖開關(87LS1) |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1550_87UL1 | 奇晶七紅線(1550) #1 87RY U/L | LINE161 | [5 empty] | 421 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺~奇晶七紅線(1550) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0527 |  |  | 1-30-15 |  |  | 1DI-CH5 | 287LS | 1550 道爺奇晶七紅線 差動電驛閉鎖開關(87LS2) |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1550_87UL2 | 奇晶七紅線(1550) #2 87RY U/L | LINE161 | [5 empty] | 422 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺~奇晶七紅線(1550) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0528 |  |  | 1-31-00 |  |  | 1DI-CH3 | 79S | 1550 道爺奇晶七紅線 復閉電驛閉鎖開關(79) |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1550_79UL | 道爺奇晶七紅線(1550) 79RY U/L | LINE161 | [5 empty] | 423 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺~奇晶七白線(1560) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0529 |  |  | 1-31-01 |  |  | 1DI-CH1 | 187LS | 1560 道爺奇晶七白線 差動電驛閉鎖開關(87LS1) |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1560_87UL1 | 奇晶七白線(1560) #1 87RY U/L | LINE161 | [5 empty] | 424 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺~奇晶七白線(1560) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0530 |  |  | 1-31-02 |  |  | 1DI-CH5 | 287LS | 1560 道爺奇晶七白線 差動電驛閉鎖開關(87LS2) |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1560_87UL2 | 奇晶七白線(1560) #2 87RY U/L | LINE161 | [5 empty] | 425 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺~奇晶七白線(1560) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0531 |  |  | 1-31-03 |  |  | 1DI-CH3 | 79S | 1560 道爺奇晶七白線 復閉電驛閉鎖開關(79) |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1560_79UL | 道爺奇晶七白線(1560) 79RY U/L | LINE161 | [5 empty] | 426 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺～奇晶六紅線(1570) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0532 |  |  | 1-31-04 |  |  | 1DI-CH1 | 187LS | 1570 道爺奇晶六線紅線 差動電驛閉鎖開關(87LS1) |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1570_87UL1 | 奇晶六紅線(1570) #1 87RY U/L | LINE161 | [5 empty] | 427 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺～奇晶六紅線(1570) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0533 |  |  | 1-31-05 |  |  | 1DI-CH5 | 287LS | 1570 道爺奇晶六線紅線 差動電驛閉鎖開關(87LS2) |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1570_87UL2 | 奇晶六紅線(1570) #2 87RY U/L | LINE161 | [5 empty] | 428 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺～奇晶六紅線(1570) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0534 |  |  | 1-31-06 |  |  | 1DI-CH3 | 79S | 1570 道爺奇晶六線紅線 復閉電驛閉鎖開關(79) |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1570_79UL | 道爺奇晶六紅線(1570) 79RY U/L | LINE161 | [5 empty] | 429 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺～奇晶六白線(1580) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0535 |  |  | 1-31-07 |  |  | 1DI-CH1 | 187LS | 1580 道爺奇晶六線白線 差動電驛閉鎖開關(87LS1) |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1580_87UL1 | 奇晶六白線(1580) #1 87RY U/L | LINE161 | [5 empty] | 430 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺～奇晶六白線(1580) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0536 |  |  | 1-31-08 |  |  | 1DI-CH5 | 287LS | 1580 道爺奇晶六線白線 差動電驛閉鎖開關(87LS2) |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1580_87UL2 | 奇晶六白線(1580) #2 87RY U/L | LINE161 | [5 empty] | 431 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺～奇晶六白線(1580) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0537 |  |  | 1-31-09 |  |  | 1DI-CH3 | 79S | 1580 道爺奇晶六線白線 復閉電驛閉鎖開關(79) |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1580_79UL | 道爺奇晶六白線(1580) 79RY U/L | LINE161 | [5 empty] | 432 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1610 | 道爺~安南~新化線(1610) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0538 |  |  | 1-31-10 |  |  | 1DI-CH1 | 87LS | 1610 道爺安南新化線 差動電驛閉鎖開關(87LS) |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1610_87UL | 道爺安南新化線(1610) 87RY U/L | LINE161 | [5 empty] | 433 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1610 | 道爺~安南~新化線(1610) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0540 |  |  | 1-31-12 |  |  | 1DI-CH3 | 79S | 1610 道爺安南新化線 復閉電驛閉鎖開關(79) |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1610_79UL | 道爺安南新化線(1610) 79RY U/L | LINE161 | [5 empty] | 434 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1620 | 道爺~和順~新化線(1620) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0541 |  |  | 1-31-13 |  |  | 1DI-CH1 | 87LS | 1620 道爺和順新化線 差動電驛閉鎖開關(87LS) |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1620_87UL | 道爺和順新化線(1620) 87RY U/L | LINE161 | [5 empty] | 435 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1620 | 道爺~和順~新化線(1620) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0543 |  |  | 1-31-15 |  |  | 1DI-CH3 | 79S | 1620 道爺和順新化線 復閉電驛閉鎖開關(79) |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1620_79UL | 道爺和順新化線(1620) 79RY U/L | LINE161 | [5 empty] | 436 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0550 |  |  | 1-32-06 |  |  | 2DI-CH1 | 50S | 1500 瞬時電驛(50S) |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1500_50SA | 161KV TIE(1500) 50RY 測試/正常 | TIE | [5 empty] | 437 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Test | Test | 1 |  |  | TEST/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1600 | TIE(1600) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0551 |  |  | 1-32-07 |  |  | 2DI-CH1 | 50S | 1600 瞬時電驛(50S) |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1600_50SA | 161KV TIE(1600) 50RY 測試/正常 | TIE | [5 empty] | 438 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Test | Test | 1 |  |  | TEST/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | ComPoint |  |  | 87CTFA1 | #12BUS CT回路故障 |  | Status | 第1具87RY CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0552 |  |  | 1-32-08 |  |  | 2DI-CH8 | 50S | 1700 瞬時電驛(50S) |  |  | B3/D05_A1 | [8 empty] | 道爺DS.161KVBUS_CTFA1 | 161KV #12BUS CT回路故障 | OTHER | [5 empty] | 439 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | ComPoint |  |  | 87CTFA2 | #34BUS CT回路故障 |  | Status | 第2具87RY CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0553 |  |  | 1-32-09 |  |  | 2DI-CH8 | 50S | 1800 瞬時電驛(50S) |  |  | B3/D05_A1 | [8 empty] | 道爺DS.161KVBUS_CTFA2 | 161KV #34BUS CT回路故障 | OTHER | [5 empty] | 440 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0554 |  |  | 1-32-10 |  |  | 1DI-CH4 | 87B1S | 161KV #1BUS差動電驛閉鎖開關(87B1S) |  |  | B2/D05_A1 | [8 empty] | 道爺DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | [5 empty] | 441 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0555 |  |  | 1-32-11 |  |  | 1DI-CH5 | 87B2S | 161KV #2BUS差動電驛閉鎖開關(87B2S) |  |  | B2/D05_A1 | [8 empty] | 道爺DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | [5 empty] | 442 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | ComPoint |  |  | 12B_87UL |  |  | Status | #1#2 BUS 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0556 |  |  | 1-32-12 |  |  | Locate Empty | 87B12S | 161KV #1BUS & #2BUS 差動電驛閉鎖開關(87B12S) |  |  | B3/D05_A1 | [8 empty] | 道爺DS.161KVBUS_RYFA1 | 161KV #12BUS 數位電驛故障 | OTHER | [5 empty] | 443 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 3BUS | #3BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0557 |  |  | 1-32-13 |  |  | 1DI-CH4 | 87B3S | 161KV #3BUS差動電驛閉鎖開關(87B3S) |  |  | B2/D05_A1 | [8 empty] | 道爺DS.161#3BUS_87UL | 161KV #3BUS 87RY U/L | OTHER | [5 empty] | 444 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 4BUS | #4BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0558 |  |  | 1-32-14 |  |  | 1DI-CH5 | 87B4S | 161KV #4BUS差動電驛閉鎖開關(87B4S) |  |  | B2/D05_A1 | [8 empty] | 道爺DS.161#4BUS_87UL | 161KV #4BUS 87RY U/L | OTHER | [5 empty] | 445 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | ComPoint |  |  | 34B_87UL |  |  | Status | #3#4 BUS 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0559 |  |  | 1-32-15 |  |  | Locate Empty | 87B34S | 161KV #3BUS & #4BUS 差動電驛閉鎖開關(87B34S) |  |  | B3/D05_A1 | [8 empty] | 道爺DS.161KVBUS_RYFA2 | 161KV #34BUS 數位電驛故障 | OTHER | [5 empty] | 446 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS |  |  | 2DTR | #2DTR |  | 87UL |  | B3 | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0565 |  |  | 1-33-05 |  |  | 1DI-CH1 | 87TS | #2 DTR 差動電驛閉鎖開關(87TS) |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#2DTR_87UL | #2DTR 87RY U/L | MTR | [5 empty] | 447 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS |  |  | 2DTR | #2DTR |  | SupLocal |  | B3 | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0566 |  |  | 1-33-06 |  |  | 2DI-CH1 | ULTC | #2 DTR ULTC中心/現場 |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#2DTR_S/L | #2DTR OLTC S/L | MTR | [5 empty] | 448 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D05 | 道爺DS |  |  | 2DTR | #2DTR |  | Tap Chan |  | B3,Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0567 |  |  | 1-33-07 |  |  | 2DI-CH2 | ULTC | #2 DTR ULTC自動/手動 |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#2DTR_A/M | #2DTR OLTC A/M | MTR | [5 empty] | 449 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D05 | 道爺DS |  |  | 2DTR | #2DTR |  | TRA |  | B3 | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0568 |  |  | 1-33-08 |  |  | 2DI-CH5 | TRA | #2 DTR 重故障警報 |  | a | B1/D05_A1 | [8 empty] | 道爺DS.#2DTR_TRA | #2DTR 重故障 | MTR | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS |  |  | 2DTR | #2DTR |  | TRF |  | B3 | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0569 |  |  | 1-33-09 |  |  | 2DI-CH6 | TRF | #2 DTR 輕故障警報 |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#2DTR_TRF | #2DTR 輕故障 | MTR | [5 empty] | 451 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS |  |  | 3DTR | #3DTR |  | 87UL |  | B3 | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0570 |  |  | 1-33-10 |  |  | 1DI-CH1 | 87TS | #3 DTR 差動電驛閉鎖開關(87TS) |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#3DTR_87UL | #3DTR 87RY U/L | MTR | [5 empty] | 452 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS |  |  | 3DTR | #3DTR |  | SupLocal |  | B3 | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0571 |  |  | 1-33-11 |  |  | 2DI-CH1 | ULTC | #3 DTR ULTC中心/現場 |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#3DTR_S/L | #3DTR OLTC S/L | MTR | [5 empty] | 453 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D05 | 道爺DS |  |  | 3DTR | #3DTR |  | Tap Chan |  | B3,Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0572 |  |  | 1-33-12 |  |  | 2DI-CH2 | ULTC | #3 DTR ULTC自動/手動 |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#3DTR_A/M | #3DTR OLTC A/M | MTR | [5 empty] | 454 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D05 | 道爺DS |  |  | 3DTR | #3DTR |  | TRA |  | B3 | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0573 |  |  | 1-33-13 |  |  | 2DI-CH5 | TRA | #3 DTR 重故障警報 |  | a | B1/D05_A1 | [8 empty] | 道爺DS.#3DTR_TRA | #3DTR 重故障 | MTR | [5 empty] | 455 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS |  |  | 3DTR | #3DTR |  | TRF |  | B3 | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0574 |  |  | 1-33-14 |  |  | 2DI-CH6 | TRF | #3 DTR 輕故障警報 |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#3DTR_TRF | #3DTR 輕故障 | MTR | [5 empty] | 456 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | MCC |  |  | Status | MCC電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0580 |  |  | 1-34-04 |  |  | Locate Empty | PMCC | PMCC 電驛故障 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.PMCC故障 | PMCC電驛故障 | OTHER | [5 empty] | 457 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | PMCC |  |  | Status | PMCC電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0581 |  |  | 1-34-05 |  |  | Locate Empty | MCC | MCC 電驛故障 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.MCC故障 | MCC電驛故障 | OTHER | [5 empty] | 458 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0582 |  |  | 1-34-06 |  |  | 1DI-CH5 | RYFA | 1510 南科道爺一路 數位電驛故障 |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1510_RYFA | 南科道爺ㄧ路(1510)數位電驛故障 | OTHER | [5 empty] | 459 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0583 |  |  | 1-34-07 |  |  | 1DI-CH4 | 87CFA | 1510 南科道爺一路 線路差流電驛通訊故障警報 |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1510_87CFA | 南科道爺ㄧ路(1510)87RY通訊故障 | OTHER | [5 empty] | 460 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0584 |  |  | 1-34-08 |  |  | 1DI-CH5 | RYFA | 1520 南科道爺二路 數位電驛故障 |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1520_RYFA | 南科道爺二路(1520)數位電驛故障 | OTHER | [5 empty] | 461 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0585 |  |  | 1-34-09 |  |  | 1DI-CH4 | 87CFA | 1520 南科道爺二路 線路差流電驛通訊故障警報 |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1520_87CFA | 南科道爺二路(1520)87RY通訊故障 | OTHER | [5 empty] | 462 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1530 | 南科～道爺三路(1530) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0586 |  |  | 1-34-10 |  |  | 1DI-CH5 | RYFA | 1530 南科道爺三路 數位電驛故障 |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1530_RYFA | 南科道爺三路(1530)數位電驛故障 | OTHER | [5 empty] | 463 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1530 | 南科～道爺三路(1530) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0587 |  |  | 1-34-11 |  |  | 1DI-CH4 | 87CFA | 1530 南科道爺三路 線路差流電驛通訊故障警報 |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1530_87CFA | 南科道爺三路(1530)87RY通訊故障 | OTHER | [5 empty] | 464 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1540 | 南科～道爺四路(1540) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0588 |  |  | 1-34-12 |  |  | 1DI-CH5 | RYFA | 1540 南科道爺四路 數位電驛故障 |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1540_RYFA | 南科道爺四路(1540)數位電驛故障 | OTHER | [5 empty] | 465 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1540 | 南科～道爺四路(1540) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0589 |  |  | 1-34-13 |  |  | 1DI-CH4 | 87CFA | 1540 南科道爺四路 線路差流電驛通訊故障警報 |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1540_87CFA | 南科道爺四路(1540)87RY通訊故障 | OTHER | [5 empty] | 466 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺~奇晶七紅線(1550) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0590 |  |  | 1-34-14 |  |  | 1DI-CH5 | RYFA | 1550 道爺奇晶七紅線 數位電驛故障 |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1550_RYFA | 道爺奇晶七紅線(1550)數位RY故障 | OTHER | [5 empty] | 467 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺~奇晶七紅線(1550) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0591 |  |  | 1-34-15 |  |  | 1DI-CH4 | 87CFA | 1550 道爺奇晶七紅線 線路差流電驛通訊故障警報 |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1550_87CFA | 道爺奇晶七紅線(1550)RY通訊故障 | OTHER | [5 empty] | 468 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺~奇晶七白線(1560) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0592 |  |  | 1-35-00 |  |  | 1DI-CH5 | RYFA | 1560 道爺奇晶七白線 數位電驛故障 |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1560_RYFA | 道爺奇晶七白線(1560)數位RY故障 | OTHER | [5 empty] | 469 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺~奇晶七白線(1560) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0593 |  |  | 1-35-01 |  |  | 1DI-CH4 | 87CFA | 1560 道爺奇晶七白線 線路差流電驛通訊故障警報 |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1560_87CFA | 道爺奇晶七白線(1560)RY通訊故障 | OTHER | [5 empty] | 470 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺～奇晶六紅線(1570) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0594 |  |  | 1-35-02 |  |  | 1DI-CH5 | RYFA | 1570 道爺奇晶六線紅線 數位電驛故障 |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1570_RYFA | 道爺奇晶六紅線(1570)數位RY故障 | OTHER | [5 empty] | 471 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺～奇晶六紅線(1570) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0595 |  |  | 1-35-03 |  |  | 1DI-CH4 | 87CFA | 1570 道爺奇晶六線紅線 線路差流電驛通訊故障警報 |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1570_87CFA | 道爺奇晶六紅線(1570)RY通訊故障 | OTHER | [5 empty] | 472 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺～奇晶六白線(1580) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0596 |  |  | 1-35-04 |  |  | 1DI-CH5 | RYFA | 1580 道爺奇晶六線白線 數位電驛故障 |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1580_RYFA | 道爺奇晶六白線(1580)數位RY故障 | OTHER | [5 empty] | 473 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺～奇晶六白線(1580) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0597 |  |  | 1-35-05 |  |  | 1DI-CH4 | 87CFA | 1580 道爺奇晶六線白線 線路差流電驛通訊故障警報 |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1580_87CFA | 道爺奇晶六白線(1580)RY通訊故障 | OTHER | [5 empty] | 474 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1610 | 道爺~安南~新化線(1610) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0598 |  |  | 1-35-06 |  |  | 1DI-CH5 | RYFA | 1610 道爺安南新化線 數位電驛故障 |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1610_RYFA | 道爺安南新化線(1610)數位RY故障 | OTHER | [5 empty] | 475 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1610 | 道爺~安南~新化線(1610) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0599 |  |  | 1-35-07 |  |  | 1DI-CH4 | 87CFA | 1610 道爺安南新化線 線路差流電驛通訊故障警報 |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1610_87CFA | 道爺安南新化線(1610)RY通訊故障 | OTHER | [5 empty] | 476 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1620 | 道爺~和順~新化線(1620) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0600 |  |  | 1-35-08 |  |  | 1DI-CH5 | RYFA | 1620 道爺和順新化線 數位電驛故障 |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1620_RYFA | 道爺和順新化線(1620)數位RY故障 | OTHER | [5 empty] | 477 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1620 | 道爺~和順~新化線(1620) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0601 |  |  | 1-35-09 |  |  | 1DI-CH4 | 87CFA | 1620 道爺和順新化線 線路差流電驛通訊故障警報 |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1620_87CFA | 道爺和順新化線(1620)RY通訊故障 | OTHER | [5 empty] | 478 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | ComPoint |  |  | OLTC_A |  |  | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0602 |  |  | 1-35-10 |  |  | 3DI-CH5 | OLTCA | OLTC 15分鐘內連動3次警報 (OLTCA) |  |  | B3/D05_A1 | [8 empty] | 道爺DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | [5 empty] | 479 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | Water1 | 1/2 水位警報 |  | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0604 |  |  | 1-35-12 |  |  | 1DI-CH3 |  | 地下室 1/2 水位警報 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.水位警報(1) | 地下室水位警報(1) | OTHER | [5 empty] | 480 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | Water2 | 頂部 水位警報 |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0605 |  |  | 1-35-13 |  |  | 1DI-CH4 |  | 地下室 頂部 水位警報 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.水位警報(2) | 地下室水位警報(2) | OTHER | [5 empty] | 481 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | OilLeak1 |  |  | Status | 洩油池水位警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0606 |  |  | 1-35-14 |  |  | 1DI-CH1 |  | 集油池 1M 時位置 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.集油池警報(1) | 集油池水位(中)警報 | OTHER | [5 empty] | 482 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | OilLeak2 |  |  | Status | 洩油池水位警報2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0607 |  |  | 1-35-15 |  |  | 1DI-CH2 |  | 集油池 2M 時位置 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.集油池警報(2) | 集油池水位(高)警報 | OTHER | [5 empty] | 483 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0608 |  |  | 1-36-00 |  |  | 2DI-CH1 | DCA | 直流用無熔絲開關跳脫警報 |  |  | ELEM/D05_A1 | [8 empty] | 道爺DS.直流電源DCA | 直流電源故障警報 | OTHER | [5 empty] | 484 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0609 |  |  | 1-36-01 |  |  | 2DI-CH2 | DCE | 直流接地警報 |  |  | ELEM/D05_A1 | [8 empty] | 道爺DS.直流電源DCE | 直流電源接地故障警報 | OTHER | [5 empty] | 485 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0610 |  |  | 1-36-02 |  |  | 2DI-CH3 | CHG1 | 變電設備用充電機警報 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.直流充電機故障 | 直流充電機故障 | OTHER | [5 empty] | 486 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0611 |  |  | 1-36-03 |  |  | 2DI-CH4 | CHG2 | 通訊設備用充電機警報 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | [5 empty] | 487 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0612 |  |  | 1-36-04 |  |  | 2DI-CH5 | ACBA | 所內 A.C.電源用 A.C.B.警報 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.所內電源ACBA | 所內電源故障警報 | OTHER | [5 empty] | 488 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0613 |  |  | 1-36-05 |  |  | 2DI-CH6 | STUV | 所內變壓器欠壓警報 |  |  | ELEM/D05_A1 | [8 empty] | 道爺DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | [5 empty] | 489 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | UPSA |  |  | Status | UPS故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0614 |  |  | 1-36-06 |  |  | 3DI-CH2 | UPS Alarm | SCADA UPS 警報 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.SCADA_UPS | SCADA UPS故障 | OTHER | [5 empty] | 490 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0615 |  |  | 1-36-07 |  |  | 3DI-CH3 | ACB1 | 所內電源用ACB1 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | [5 empty] | 491 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0616 |  |  | 1-36-08 |  |  | 3DI-CH4 | ACB2 | 所內電源用ACB2 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | [5 empty] | 492 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | ACBT |  |  | Status | 所內電源ACB TIE | Close/Open | Y | 3 | DI-SP | [6 empty] | 0617 |  |  | 1-36-09 |  |  | 3DI-CH5 | ACBTIE | 所內電源用ACB TIE |  |  | B3/D05_A1 | [8 empty] | 道爺DS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | [5 empty] | 493 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ON/OFF | OFF
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | SCADAA |  |  | Status | LocalSCADA故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0618 |  |  | 1-36-10 |  |  | 3DI-CH1 | SUPA | 變電所監控系統 動作/正常（Local SCADA警報） |  |  | B3/D05_A1 | [8 empty] | 道爺DS.SUPA | 變電所SCADA故障 | OTHER | [5 empty] | 494 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | RTU | RTU |  | RTU_COM |  | B3 | Status | RTU盤間通訊 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0619 |  |  | 1-36-11 |  |  | 3DI-CH2 | RX/TX | RTU傳送訊號故障警報 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.DTUA | DTU故障警報 | OTHER | [5 empty] | 495 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | 1A5Other | 排水泵故障1_涵洞 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0620 |  |  | 1-36-12 |  |  | 3DI-CH3 |  | 涵洞排水泵故障 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.涵洞排水泵 | 涵洞排水泵故障 | OTHER | [5 empty] | 496 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | Fire1 | 受信總機 |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0621 |  |  | 1-36-13 |  |  | 3DI-CH4 | FIR | 火災警報(1)受信總機 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | [5 empty] | 497 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | 2A5Other | 揚水泵警報 | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0622 |  |  | 1-36-14 |  |  | 3DI-CH6 |  | 揚水泵故障 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.揚水泵 | 揚水泵故障 | OTHER | [5 empty] | 498 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | ComPoint |  |  | GRZ100 |  |  | Status | 電驛GRZ100閉鎖 | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0623 |  |  | 1-36-15 |  |  | 3DI-CH7 | USE/LOCK | 本所各GRZ100 Ry U/L |  |  | B3/D05_A1 | [8 empty] | 道爺DS.BVS_RY | 161KV #12BUS GRZ100 RY U/L | OTHER | [5 empty] | 499 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | LOCK/USE | USE
D05 | 道爺DS | 161 | 161kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0624 |  |  | 1-37-00 |  |  | 1DI-CH1 | UVA1 | 161KV 一號匯流排 欠電壓警報 |  |  | B2/D05_A1 | [8 empty] | 道爺DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | [5 empty] | 500 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0625 |  |  | 1-37-01 |  |  | 1DI-CH2 | UVA2 | 161KV 二號匯流排 欠電壓警報 |  |  | B2/D05_A1 | [8 empty] | 道爺DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | [5 empty] | 501 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | GPSA |  |  | Status | GPS故障警報 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0626 |  |  | 1-37-02 |  |  | Locate Empty | GPSA | GPSA |  |  | B3/D05_A1 | [8 empty] | 道爺DS.GPSA | LOCAL GPS故障 | OTHER | [5 empty] | 502 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | DTU_CFA | DTU 通訊異常 | Element | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0627 |  |  | 1-37-03 |  |  | 軟體點 |  | DTU通訊故障警報 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.DTUCFA | DTU通訊故障 | OTHER | [5 empty] | 503 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 3BUS | #3BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0628 |  |  | 1-37-04 |  |  | 1DI-CH1 | UVA3 | 161KV 三號匯流排 欠電壓警報 |  |  | B2/D05_A1 | [8 empty] | 道爺DS.161#3BUS_VUA | 161KV #3BUS 衡相RY | BUS | [5 empty] | 504 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 4BUS | #4BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0629 |  |  | 1-37-05 |  |  | 1DI-CH2 | UVA4 | 161KV 四號匯流排 欠電壓警報 |  |  | B2/D05_A1 | [8 empty] | 道爺DS.161#4BUS_VUA | 161KV #4BUS 衡相RY | BUS | [5 empty] | 505 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | TCA | 斷路器跳脫迴路故障 | Element | Status | 警報等級5動作4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0632 |  |  | 1-37-08 |  |  | Locate Empty | TCA | 斷路器 跳脫線圈警報 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.TCA | 斷路器跳脫回路故障 | OTHER | [5 empty] | 506 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | ComPoint |  |  | FDR_60A |  |  | Status | 11/22kV電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0633 |  |  | 1-37-09 |  |  | 4DI-CH7 |  | SC電壓電驛警報(60A) |  |  | B3/D05_A1 | [8 empty] | 道爺DS.23KV_SC_60A | 11/23KV SC 60A | OTHER | [5 empty] | 507 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0634 |  |  | 1-37-10 |  |  | 軟體點 | CBA | 161kv CB 重故障 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.161KV_CBA | 161KV斷路器重故障 | OTHER | [5 empty] | 508 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0635 |  |  | 1-37-11 |  |  | 軟體點 | CBF | 161kv CB 輕故障 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | [5 empty] | 509 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | ComPoint |  |  | FDR_CBA |  |  | Status | 11/22kV斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0636 |  |  | 1-37-12 |  |  | 軟體點 | CBA | 23KV CB 重故障 |  |  | ELEM/D05_D1 | [8 empty] | 道爺DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | [5 empty] | 510 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | ComPoint |  |  | FDR_CBF |  |  | Status | 11/22kV斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0637 |  |  | 1-37-13 |  |  | 軟體點 | CBF | 23KV CB 輕故障 |  |  | ELEM/D05_D1 | [8 empty] | 道爺DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | [5 empty] | 511 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | Lights1 | 景觀 |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0638 |  |  | 1-37-14 |  |  | 4DI-CH8 | FLA1 | A區照明動作（景觀） |  |  | B3/D05_A1 | [8 empty] | 道爺DS.開關場照明(A) | 景觀照明 | OTHER | [5 empty] | 512 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | Lights2 | 路燈 |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0639 |  |  | 1-37-15 |  |  | 3DI-CH8 | FLA2 | B區照明動作（路燈） |  |  | B3/D05_A1 | [8 empty] | 道爺DS.開關場照明(B) | 路燈照明 | OTHER | [5 empty] | 513 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
D05 | 道爺DS | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | DS1 | 1511 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0640 | 641 |  | 1-38-00 | 1-38-01 |  | 2DI-CH1 | DS(ON) | 1511 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1511_DS | 1511(南科道爺ㄧ路) DS | LINE161 | [5 empty] | 514 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | DS2 | 1512 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0642 | 643 |  | 1-38-02 | 1-38-03 |  | 2DI-CH3 | DS(ON) | 1512 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1512_DS | 1512(南科道爺ㄧ路) DS | LINE161 | [5 empty] | 515 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | DS3 | 1513 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0644 | 645 |  | 1-38-04 | 1-38-05 |  | 2DI-CH5 | DS(ON) | 1513 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1513_DS | 1513(南科道爺ㄧ路) DS | LINE161 | [5 empty] | 516 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | ES3 | 1513E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0646 | 647 |  | 1-38-06 | 1-38-07 |  | 2DI-CH7 | ES(ON) | 1513E AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1513E_ES | 1513E(南科道爺ㄧ路) ES | LINE161 | [5 empty] | 517 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | DS1 | 1521 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0648 | 649 |  | 1-38-08 | 1-38-09 |  | 2DI-CH1 | DS(ON) | 1521 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1521_DS | 1521(南科道爺二路) DS | LINE161 | [5 empty] | 518 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | DS2 | 1522 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0650 | 651 |  | 1-38-10 | 1-38-11 |  | 2DI-CH3 | DS(ON) | 1522 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1522_DS | 1522(南科道爺二路) DS | LINE161 | [5 empty] | 519 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | DS3 | 1523 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0652 | 653 |  | 1-38-12 | 1-38-13 |  | 2DI-CH5 | DS(ON) | 1523 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1523_DS | 1523(南科道爺二路) DS | LINE161 | [5 empty] | 520 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | ES3 | 1523E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0654 | 655 |  | 1-38-14 | 1-38-15 |  | 2DI-CH7 | ES(ON) | 1523E AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1523E_ES | 1523E(南科道爺二路) ES | LINE161 | [5 empty] | 521 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1530 | 南科～道爺三路(1530) |  | DS1 | 1531 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0656 | 657 |  | 1-39-00 | 1-39-01 |  | 2DI-CH1 | DS(ON) | 1531 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1531_DS | 1531(南科道爺三路) DS | LINE161 | [5 empty] | 522 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1530 | 南科～道爺三路(1530) |  | DS2 | 1532 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0658 | 659 |  | 1-39-02 | 1-39-03 |  | 2DI-CH3 | DS(ON) | 1532 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1532_DS | 1532(南科道爺三路) DS | LINE161 | [5 empty] | 523 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1530 | 南科～道爺三路(1530) |  | DS3 | 1533 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0660 | 661 |  | 1-39-04 | 1-39-05 |  | 2DI-CH5 | DS(ON) | 1533 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1533_DS | 1533(南科道爺三路) DS | LINE161 | [5 empty] | 524 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1530 | 南科～道爺三路(1530) |  | ES3 | 1533E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0662 | 663 |  | 1-39-06 | 1-39-07 |  | 2DI-CH7 | ES(ON) | 1533E AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1533E_ES | 1533E(南科道爺三路) ES | LINE161 | [5 empty] | 525 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1540 | 南科～道爺四路(1540) |  | DS1 | 1541 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0664 | 665 |  | 1-39-08 | 1-39-09 |  | 2DI-CH1 | DS(ON) | 1541 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1541_DS | 1541(南科道爺四路) DS | LINE161 | [5 empty] | 526 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1540 | 南科～道爺四路(1540) |  | DS2 | 1542 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0666 | 667 |  | 1-39-10 | 1-39-11 |  | 2DI-CH3 | DS(ON) | 1542 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1542_DS | 1542(南科道爺四路) DS | LINE161 | [5 empty] | 527 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1540 | 南科～道爺四路(1540) |  | DS3 | 1543 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0668 | 669 |  | 1-39-12 | 1-39-13 |  | 2DI-CH5 | DS(ON) | 1543 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1543_DS | 1543(南科道爺四路) DS | LINE161 | [5 empty] | 528 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1540 | 南科～道爺四路(1540) |  | ES3 | 1543E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0670 | 671 |  | 1-39-14 | 1-39-15 |  | 2DI-CH7 | ES(ON) | 1543E AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1543E_ES | 1543E(南科道爺四路) ES | LINE161 | [5 empty] | 529 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺~奇晶七紅線(1550) |  | DS1 | 1551 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0672 | 673 |  | 1-3A-00 | 1-3A-01 |  | 2DI-CH1 | DS(ON) | 1551 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1551_DS | 1551(道爺奇晶七紅線) DS | LINE161 | [5 empty] | 530 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺~奇晶七紅線(1550) |  | DS2 | 1552 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0674 | 675 |  | 1-3A-02 | 1-3A-03 |  | 2DI-CH3 | DS(ON) | 1552 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1552_DS | 1552(道爺奇晶七紅線) DS | LINE161 | [5 empty] | 531 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺~奇晶七紅線(1550) |  | DS3 | 1553 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0676 | 677 |  | 1-3A-04 | 1-3A-05 |  | 2DI-CH5 | DS(ON) | 1553 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1553_DS | 1553(道爺奇晶七紅線) DS | LINE161 | [5 empty] | 532 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺~奇晶七紅線(1550) |  | ES3 | 1553E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0678 | 679 |  | 1-3A-06 | 1-3A-07 |  | 2DI-CH7 | ES(ON) | 1553E AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1553E_ES | 1553E(道爺奇晶七紅線) ES | LINE161 | [5 empty] | 533 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺~奇晶七白線(1560) |  | DS1 | 1561 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0680 | 681 |  | 1-3A-08 | 1-3A-09 |  | 2DI-CH1 | DS(ON) | 1561 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1561_DS | 1561(道爺奇晶七白線) DS | LINE161 | [5 empty] | 534 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺~奇晶七白線(1560) |  | DS2 | 1562 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0682 | 683 |  | 1-3A-10 | 1-3A-11 |  | 2DI-CH3 | DS(ON) | 1562 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1562_DS | 1562(道爺奇晶七白線) DS | LINE161 | [5 empty] | 535 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺~奇晶七白線(1560) |  | DS3 | 1563 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0684 | 685 |  | 1-3A-12 | 1-3A-13 |  | 2DI-CH5 | DS(ON) | 1563 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1563_DS | 1563(道爺奇晶七白線) DS | LINE161 | [5 empty] | 536 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺~奇晶七白線(1560) |  | ES3 | 1563E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0686 | 687 |  | 1-3A-14 | 1-3A-15 |  | 2DI-CH7 | ES(ON) | 1563E AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1563E_ES | 1563E(道爺奇晶七白線) ES | LINE161 | [5 empty] | 537 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺～奇晶六紅線(1570) |  | DS1 | 1571 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0688 | 689 |  | 1-3B-00 | 1-3B-01 |  | 2DI-CH1 | DS(ON) | 1571 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1571_DS | 1571(道爺奇晶六紅線) DS | LINE161 | [5 empty] | 538 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺～奇晶六紅線(1570) |  | DS2 | 1572 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0690 | 691 |  | 1-3B-02 | 1-3B-03 |  | 2DI-CH3 | DS(ON) | 1572 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1572_DS | 1572(道爺奇晶六紅線) DS | LINE161 | [5 empty] | 539 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺～奇晶六紅線(1570) |  | DS3 | 1573 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0692 | 693 |  | 1-3B-04 | 1-3B-05 |  | 2DI-CH5 | DS(ON) | 1573 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1573_DS | 1573(道爺奇晶六紅線) DS | LINE161 | [5 empty] | 540 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺～奇晶六紅線(1570) |  | ES3 | 1573E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0694 | 695 |  | 1-3B-06 | 1-3B-07 |  | 2DI-CH7 | ES(ON) | 1573E AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1573E_ES | 1573E(道爺奇晶六紅線) ES | LINE161 | [5 empty] | 541 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺～奇晶六白線(1580) |  | DS1 | 1581 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0696 | 697 |  | 1-3B-08 | 1-3B-09 |  | 2DI-CH1 | DS(ON) | 1581 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1581_DS | 1581(道爺奇晶六白線) DS | LINE161 | [5 empty] | 542 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺～奇晶六白線(1580) |  | DS2 | 1582 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0698 | 699 |  | 1-3B-10 | 1-3B-11 |  | 2DI-CH3 | DS(ON) | 1582 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1582_DS | 1582(道爺奇晶六白線) DS | LINE161 | [5 empty] | 543 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺～奇晶六白線(1580) |  | DS3 | 1583 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0700 | 701 |  | 1-3B-12 | 1-3B-13 |  | 2DI-CH5 | DS(ON) | 1583 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1583_DS | 1583(道爺奇晶六白線) DS | LINE161 | [5 empty] | 544 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺～奇晶六白線(1580) |  | ES3 | 1583E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0702 | 703 |  | 1-3B-14 | 1-3B-15 |  | 2DI-CH7 | ES(ON) | 1583E AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1583E_ES | 1583E(道爺奇晶六白線) ES | LINE161 | [5 empty] | 545 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1610 | 道爺~安南~新化線(1610) |  | DS1 | 1611 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0704 | 705 |  | 1-3C-00 | 1-3C-01 |  | 2DI-CH1 | DS(ON) | 1611 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1611_DS | 1611(道爺安南新化線) DS | LINE161 | [5 empty] | 546 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1610 | 道爺~安南~新化線(1610) |  | DS2 | 1612 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0706 | 707 |  | 1-3C-02 | 1-3C-03 |  | 2DI-CH3 | DS(ON) | 1612 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1612_DS | 1612(道爺安南新化線) DS | LINE161 | [5 empty] | 547 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1610 | 道爺~安南~新化線(1610) |  | DS3 | 1613 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0708 | 709 |  | 1-3C-04 | 1-3C-05 |  | 2DI-CH5 | DS(ON) | 1613 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1613_DS | 1613(道爺安南新化線) DS | LINE161 | [5 empty] | 548 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1610 | 道爺~安南~新化線(1610) |  | ES3 | 1613E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0710 | 711 |  | 1-3C-06 | 1-3C-07 |  | 2DI-CH7 | ES(ON) | 1613E AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1613E_ES | 1613E(道爺安南新化線) ES | LINE161 | [5 empty] | 549 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1620 | 道爺~和順~新化線(1620) |  | DS1 | 1621 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0712 | 713 |  | 1-3C-08 | 1-3C-09 |  | 2DI-CH1 | DS(ON) | 1621 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1621_DS | 1621(道爺和順新化線) DS | LINE161 | [5 empty] | 550 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1620 | 道爺~和順~新化線(1620) |  | DS2 | 1622 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0714 | 715 |  | 1-3C-10 | 1-3C-11 |  | 2DI-CH3 | DS(ON) | 1622 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1622_DS | 1622(道爺和順新化線) DS | LINE161 | [5 empty] | 551 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1620 | 道爺~和順~新化線(1620) |  | DS3 | 1623 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0716 | 717 |  | 1-3C-12 | 1-3C-13 |  | 2DI-CH5 | DS(ON) | 1623 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1623_DS | 1623(道爺和順新化線) DS | LINE161 | [5 empty] | 552 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1620 | 道爺~和順~新化線(1620) |  | ES3 | 1623E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0718 | 719 |  | 1-3C-14 | 1-3C-15 |  | 2DI-CH7 | ES(ON) | 1623E AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1623E_ES | 1623E(道爺和順新化線) ES | LINE161 | [5 empty] | 553 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0720 | 721 |  | 1-3D-00 | 1-3D-01 |  | 2DI-CH1 | DS(ON) | 1501 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1501_DS | 1501(TIE) DS | TIE | [5 empty] | 554 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0722 | 723 |  | 1-3D-02 | 1-3D-03 |  | 2DI-CH3 | DS(ON) | 1502 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1502_DS | 1502(TIE) DS | TIE | [5 empty] | 555 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1600 | TIE(1600) |  | DS1 | 1601 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0728 | 729 |  | 1-3D-08 | 1-3D-09 |  | 2DI-CH1 | DS(ON) | 1601 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1601_DS | 1601(TIE) DS | TIE | [5 empty] | 556 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1600 | TIE(1600) |  | DS2 | 1602 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0730 | 731 |  | 1-3D-10 | 1-3D-11 |  | 2DI-CH3 | ES(ON) | 1602 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1602_DS | 1602(TIE) DS | TIE | [5 empty] | 557 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1700 | TIE(1700) |  | DS1 | 1701 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0736 | 737 |  | 1-3E-00 | 1-3E-01 |  | 2DI-CH1 | DS(ON) | 1701 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1701_DS | 1701(TIE) DS | TIE | [5 empty] | 558 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1700 | TIE(1700) |  | DS2 | 1702 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0738 | 739 |  | 1-3E-02 | 1-3E-03 |  | 2DI-CH3 | DS(ON) | 1703 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1703_DS | 1703(TIE) DS | TIE | [5 empty] | 559 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1800 | TIE(1800) |  | DS1 | 1801 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0744 | 745 |  | 1-3E-08 | 1-3E-09 |  | 2DI-CH1 | DS(ON) | 1802 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1802_DS | 1802(TIE) DS | TIE | [5 empty] | 560 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1800 | TIE(1800) |  | DS2 | 1802 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0746 | 747 |  | 1-3E-10 | 1-3E-11 |  | 2DI-CH3 | DS(ON) | 1804 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1804_DS | 1804(TIE) DS | TIE | [5 empty] | 561 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0760 | 761 |  | 1-3F-08 | 1-3F-09 |  | 2DI-CH1 | DS(ON) | 1761 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1761_DS | 1761(#2DTR) DS | MTR | [5 empty] | 562 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0762 | 763 |  | 1-3F-10 | 1-3F-11 |  | 2DI-CH3 | DS(ON) | 1762 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1762_DS | 1762(#2DTR) DS | MTR | [5 empty] | 563 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0768 |  |  | 2-30-00 |  |  | 4DI-CH1 | ACF | 通訊系統 A.C. Failure |  |  | B3/D05_A1 | [8 empty] | 道爺DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | [5 empty] | 564 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | R_Temp |  |  | Status | 溫度警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0772 |  |  | 2-30-04 |  |  | 4DI-CH5 | PCMA | 通訊室或控制室溫度警報 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.通信機房溫度 | 通訊室或控制室溫度警報 | OTHER | [5 empty] | 565 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | Burglar1 | 保全警報 |  | Status | 無人化防盜1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0773 |  |  | 2-30-05 |  |  | 3DI-CH5 |  | 保全警報 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | [5 empty] | 566 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | Door1 | 建築物 |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0774 |  |  | 2-30-06 |  |  | 3DI-CH7 | DOR | 門禁警報（建築物） |  |  | B3/D05_A1 | [8 empty] | 道爺DS.無人化門禁(1) | 無人化門禁(1)建築物 | OTHER | [5 empty] | 567 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | Door2 | 大門 |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0775 |  |  | 2-30-07 |  |  | 1DI-CH8 | DOR | 門禁警報（大門） |  |  | B3/D05_A1 | [8 empty] | 道爺DS.無人化門禁(2) | 無人化門禁(2)大門 | OTHER | [5 empty] | 568 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K61 | 爺61線(4K61) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0792 |  |  | 2-31-08 |  |  | 2DI-CH5 | 79S | 爺61線（4K61） 79S |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K61_79UL | 23KV爺61線(4K61) 79RY U/L | FEEDER | [5 empty] | 569 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 4K61 | 爺61線(4K61) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0793 |  |  | 2-31-09 |  |  | 2DI-CH7 | 51NS | 爺61線（4K61） 51NS |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K61_LCO_TAP | 23KV爺61線(4K61) LCO TAP | FEEDER | [5 empty] | 570 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D05 | 道爺DS | 22 | 22kV | 4K62 | 爺62線(4K62) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0794 |  |  | 2-31-10 |  |  | 2DI-CH5 | 79S | 爺62線（4K62） 79S |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K62_79UL | 23KV爺62線(4K62) 79RY U/L | FEEDER | [5 empty] | 571 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 4K62 | 爺62線(4K62) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0795 |  |  | 2-31-11 |  |  | 2DI-CH7 | 51NS | 爺62線（4K62） 51NS |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K62_LCO_TAP | 23KV爺62線(4K62) LCO TAP | FEEDER | [5 empty] | 572 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D05 | 道爺DS | 22 | 22kV | 4K63 | 爺63線(4K63) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0796 |  |  | 2-31-12 |  |  | 2DI-CH5 | 79S | 爺63線（4K63） 79S |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K63_79UL | 23KV爺63線(4K63) 79RY U/L | FEEDER | [5 empty] | 573 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 4K63 | 爺63線(4K63) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0797 |  |  | 2-31-13 |  |  | 2DI-CH7 | 51NS | 爺63線（4K63） 51NS |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K63_LCO_TAP | 23KV爺63線(4K63) LCO TAP | FEEDER | [5 empty] | 574 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D05 | 道爺DS | 22 | 22kV | 4K64 | 爺64線(4K64) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0798 |  |  | 2-31-14 |  |  | 2DI-CH5 | 79S | 爺64線（4K64） 79S |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K64_79UL | 23KV爺64線(4K64) 79RY U/L | FEEDER | [5 empty] | 575 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 4K64 | 爺64線(4K64) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0799 |  |  | 2-31-15 |  |  | 2DI-CH7 | 51NS | 爺64線（4K64） 51NS |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K64_LCO_TAP | 23KV爺64線(4K64) LCO TAP | FEEDER | [5 empty] | 576 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D05 | 道爺DS | 22 | 22kV | 4K65 | 爺65線(4K65) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0800 |  |  | 2-32-00 |  |  | 2DI-CH5 | 79S | 爺65線（4K65） 79S |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K65_79UL | 23KV爺65線(4K65) 79RY U/L | FEEDER | [5 empty] | 577 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 4K65 | 爺65線(4K65) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0801 |  |  | 2-32-01 |  |  | 2DI-CH7 | 51NS | 爺65線（4K65） 51NS |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K65_LCO_TAP | 23KV爺65線(4K65) LCO TAP | FEEDER | [5 empty] | 578 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D05 | 道爺DS | 22 | 22kV | 4K66 | 爺66線(4K66) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0802 |  |  | 2-32-02 |  |  | 2DI-CH5 | 79S | 爺66線（4K66） 79S |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K66_79UL | 23KV爺66線(4K66) 79RY U/L | FEEDER | [5 empty] | 579 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 4K66 | 爺66線(4K66) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0803 |  |  | 2-32-03 |  |  | 2DI-CH7 | 51NS | 爺66線（4K66） 51NS |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K66_LCO_TAP | 23KV爺66線(4K66) LCO TAP | FEEDER | [5 empty] | 580 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D05 | 道爺DS | 22 | 22kV | 4K67 | 爺67線(4K67) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0804 |  |  | 2-32-04 |  |  | 2DI-CH5 | 79S | 爺67線（4K67） 79S |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K67_79UL | 23KV爺67線(4K67) 79RY U/L | FEEDER | [5 empty] | 581 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 4K67 | 爺67線(4K67) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0805 |  |  | 2-32-05 |  |  | 2DI-CH7 | 51NS | 爺67線（4K67） 51NS |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K67_LCO_TAP | 23KV爺67線(4K67) LCO TAP | FEEDER | [5 empty] | 582 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D05 | 道爺DS | 22 | 22kV | 4K68 | 爺68線(4K68) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0806 |  |  | 2-32-06 |  |  | 2DI-CH5 | 79S | 爺68線（4K68） 79S |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K68_79UL | 23KV爺68線(4K68) 79RY U/L | FEEDER | [5 empty] | 583 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 4K68 | 爺68線(4K68) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0807 |  |  | 2-32-07 |  |  | 2DI-CH7 | 51NS | 爺68線（4K68） 51NS |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K68_LCO_TAP | 23KV爺68線(4K68) LCO TAP | FEEDER | [5 empty] | 584 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D05 | 道爺DS | 22 | 22kV | 4K71 | 爺71線(4K71) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0808 |  |  | 2-32-08 |  |  | 2DI-CH5 | 79S | 爺71線（4K71） 79S |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K71_79UL | 23KV爺71線(4K71) 79RY U/L | FEEDER | [5 empty] | 585 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 4K71 | 爺71線(4K71) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0809 |  |  | 2-32-09 |  |  | 2DI-CH7 | 51NS | 爺71線（4K71） 51NS |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K71_LCO_TAP | 23KV爺71線(4K71) LCO TAP | FEEDER | [5 empty] | 586 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D05 | 道爺DS | 22 | 22kV | 4K72 | 爺72線(4K72) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0810 |  |  | 2-32-10 |  |  | 2DI-CH5 | 79S | 爺72線（4K72） 79S |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K72_79UL | 23KV爺72線(4K72) 79RY U/L | FEEDER | [5 empty] | 587 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 4K72 | 爺72線(4K72) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0811 |  |  | 2-32-11 |  |  | 2DI-CH7 | 51NS | 爺72線（4K72） 51NS |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K72_LCO_TAP | 23KV爺72線(4K72) LCO TAP | FEEDER | [5 empty] | 588 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D05 | 道爺DS | 22 | 22kV | 4K73 | 爺73線(4K73) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0812 |  |  | 2-32-12 |  |  | 2DI-CH5 | 79S | 爺73線（4K73） 79S |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K73_79UL | 23KV爺73線(4K73) 79RY U/L | FEEDER | [5 empty] | 589 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 4K73 | 爺73線(4K73) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0813 |  |  | 2-32-13 |  |  | 2DI-CH7 | 51NS | 爺73線（4K73） 51NS |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K73_LCO_TAP | 23KV爺73線(4K73) LCO TAP | FEEDER | [5 empty] | 590 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D05 | 道爺DS | 22 | 22kV | 4K74 | 爺74線(4K74) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0814 |  |  | 2-32-14 |  |  | 2DI-CH5 | 79S | 爺74線（4K74） 79S |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K74_79UL | 23KV爺74線(4K74) 79RY U/L | FEEDER | [5 empty] | 591 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 4K74 | 爺74線(4K74) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0815 |  |  | 2-32-15 |  |  | 2DI-CH7 | 51NS | 爺74線（4K74） 51NS |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K74_LCO_TAP | 23KV爺74線(4K74) LCO TAP | FEEDER | [5 empty] | 592 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D05 | 道爺DS | 22 | 22kV | 4K75 | 爺75線(4K75) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0816 |  |  | 2-33-00 |  |  | 2DI-CH5 | 79S | 爺75線（4K75） 79S |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K75_79UL | 23KV爺75線(4K75) 79RY U/L | FEEDER | [5 empty] | 593 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 4K75 | 爺75線(4K75) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0817 |  |  | 2-33-01 |  |  | 2DI-CH7 | 51NS | 爺75線（4K75） 51NS |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K75_LCO_TAP | 23KV爺75線(4K75) LCO TAP | FEEDER | [5 empty] | 594 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D05 | 道爺DS | 22 | 22kV | 4K76 | 爺76線(4K76) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0818 |  |  | 2-33-02 |  |  | 2DI-CH5 | 79S | 爺76線（4K76） 79S |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K76_79UL | 23KV爺76線(4K76) 79RY U/L | FEEDER | [5 empty] | 595 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 4K76 | 爺76線(4K76) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0819 |  |  | 2-33-03 |  |  | 2DI-CH7 | 51NS | 爺76線（4K76） 51NS |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K76_LCO_TAP | 23KV爺76線(4K76) LCO TAP | FEEDER | [5 empty] | 596 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D05 | 道爺DS | 22 | 22kV | 4K77 | 爺77線(4K77) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0820 |  |  | 2-33-04 |  |  | 2DI-CH5 | 79S | 爺77線（4K77） 79S |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K77_79UL | 23KV爺77線(4K77) 79RY U/L | FEEDER | [5 empty] | 597 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 4K77 | 爺77線(4K77) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0821 |  |  | 2-33-05 |  |  | 2DI-CH7 | 51NS | 爺77線（4K77） 51NS |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K77_LCO_TAP | 23KV爺77線(4K77) LCO TAP | FEEDER | [5 empty] | 598 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D05 | 道爺DS | 22 | 22kV | 4K78 | 爺78線(4K78) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0822 |  |  | 2-33-06 |  |  | 2DI-CH5 | 79S | 爺78線（4K78） 79S |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K78_79UL | 23KV爺78線(4K78) 79RY U/L | FEEDER | [5 empty] | 599 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 4K78 | 爺78線(4K78) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0823 |  |  | 2-33-07 |  |  | 2DI-CH7 | 51NS | 爺78線（4K78） 51NS |  |  | B2/D05_D1 | [8 empty] | 道爺DS.4K78_LCO_TAP | 23KV爺78線(4K78) LCO TAP | FEEDER | [5 empty] | 600 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D05 | 道爺DS |  |  | 2DTR | #2DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0845 |  |  | 2-34-13 |  |  | 3DI-CH4 | 63Q | #2 DTR ULTC 保護電驛警報63Q |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#2DTR_63Q | #2DTR 63Q RY | MTR | [5 empty] | 601 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D05 | 道爺DS |  |  | 2DTR | #2DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0846 |  |  | 2-34-14 |  |  | 3DI-CH7 | 96P | #2 DTR 衝擊油壓電驛警報96P |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#2DTR_96P | #2DTR 96P RY | MTR | [5 empty] | 602 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D05 | 道爺DS |  |  | 2DTR | #2DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0847 |  |  | 2-34-15 |  |  | 3DI-CH3 | 96D | #2 DTR 放壓電驛警報96D |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#2DTR_96D | #2DTR 96D RY | MTR | [5 empty] | 603 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D05 | 道爺DS |  |  | 2DTR | #2DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0848 |  |  | 2-35-00 |  |  | 3DI-CH1 | 96B1 | #2 DTR 撲氣電驛第一段警報96B1 |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | [5 empty] | 604 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D05 | 道爺DS |  |  | 2DTR | #2DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0849 |  |  | 2-35-01 |  |  | 3DI-CH2 | 96B2 | #2 DTR 撲氣電驛第二段警報96B2 |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | [5 empty] | 605 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D05 | 道爺DS |  |  | 3DTR | #3DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0850 |  |  | 2-35-02 |  |  | 3DI-CH4 | 63Q | #3 DTR ULTC 保護電驛警報63Q |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#3DTR_63Q | #3DTR 63Q RY | MTR | [5 empty] | 606 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D05 | 道爺DS |  |  | 3DTR | #3DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0851 |  |  | 2-35-03 |  |  | 3DI-CH7 | 96P | #3 DTR 衝擊油壓電驛警報96P |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#3DTR_96P | #3DTR 96P RY | MTR | [5 empty] | 607 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D05 | 道爺DS |  |  | 3DTR | #3DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0852 |  |  | 2-35-04 |  |  | 3DI-CH3 | 96D | #3 DTR 放壓電驛警報96D |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#3DTR_96D | #3DTR 96D RY | MTR | [5 empty] | 608 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D05 | 道爺DS |  |  | 3DTR | #3DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0853 |  |  | 2-35-05 |  |  | 3DI-CH1 | 96B1 | #3 DTR 撲氣電驛第一段警報96B1 |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#3DTR_96B1 | #3DTR 96B1 RY | MTR | [5 empty] | 609 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D05 | 道爺DS |  |  | 3DTR | #3DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0854 |  |  | 2-35-06 |  |  | 3DI-CH2 | 96B2 | #3 DTR 撲氣電驛第二段警報96B2 |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#3DTR_96B2 | #3DTR 96B2 RY | MTR | [5 empty] | 610 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | ComPoint |  |  | 25TA |  |  | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0860 |  |  | 2-35-12 |  |  | 3DI-CH6/3DI-CH7 | 25TA | 161kv 25電驛超時 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | [5 empty] | 611 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | ComPoint |  |  | 25PFA |  |  | Status | 同步校核電驛電源 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0861 |  |  | 2-35-13 |  |  | 3DI-CH6/3DI-CH7 | 25PFA | 161kv 25電源故障警報 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER | [5 empty] | 612 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | 5A5Other | COM SERVER MASTER 故障 | Element | Status | 警報等級5動作5 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0862 |  |  | 2-35-14 |  |  | 軟體點 |  | COM SERVER MASTER 故障警報 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.COMMA | 通訊處理單元A(COMMA)故障 | OTHER | [5 empty] | 613 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | 6A5Other | COM SERVER SLAVE 故障 | Element | Status | 警報等級5動作6 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0863 |  |  | 2-35-15 |  |  | 軟體點 |  | COM SERVER SLAVE 故障警報 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.COMMB | 通訊處理單元B(COMMB)故障 | OTHER | [5 empty] | 614 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D05 | 道爺DS |  |  | 2DTR | #2DTR |  | 51_UL |  | B2 | Status | 51RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0878 |  |  | 2-36-14 |  |  | Locate Empty | 51S | #2 DTR 51S |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#2DTR_50/51NUL | #2DTR 50/50N/51/51N RY U/L | OTHER | [5 empty] | 615 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS |  |  | 2DTR | #2DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0879 |  |  | 2-36-15 |  |  | Locate Empty | 51ZS | #2 DTR 51ZS |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#2DTR_51ZUL | #2DTR 51Z RY U/L | OTHER | [5 empty] | 616 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS |  |  | 3DTR | #3DTR |  | 51_UL |  | B2 | Status | 51RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0880 |  |  | 2-37-00 |  |  | Locate Empty | 51S | #3 DTR 51S |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#3DTR_50/51NUL | #3DTR 50/50N/51/51N RY U/L | OTHER | [5 empty] | 617 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS |  |  | 3DTR | #3DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0881 |  |  | 2-37-01 |  |  | Locate Empty | 51ZS | #3 DTR 51ZS |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#3DTR_51ZUL | #3DTR 51Z RY U/L | OTHER | [5 empty] | 618 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 0 |  | StaDev | 所內設施 |  | GEN | 緊急發電機運轉 | Element | Status | 警報等級5動作7 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0884 |  |  | 2-37-04 |  |  | 3DI-CH5 |  | 緊急發電機運轉 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.GEN | 緊急發電機運轉 | OTHER | [5 empty] | 619 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ON/OFF | OFF
D05 | 道爺DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0896 | 897 |  | 2-38-00 | 2-38-01 |  | 2DI-CH1 | DS(ON) | 1771 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1771_DS | 1771(#3DTR) DS | MTR | [5 empty] | 620 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 |  | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0898 | 899 |  | 2-38-02 | 2-38-03 |  | 2DI-CH3 | DS(ON) | 1772 AS |  |  | B2/D05_A1 | [8 empty] | 道爺DS.1772_DS | 1772(#3DTR) DS | MTR | [5 empty] | 621 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1530 | 南科～道爺三路(1530) |  | V |  | INSERT | MvMoment | kV |  | Y |  | AI | [6 empty] | 0221 |  |  | 2-DD |  |  | Locate Empty | V | 1530 南科道爺三路 R相電壓 | kV_-210_210(-2000_2000) |  | B2/D05_A1 | [8 empty] | 道爺DS.1530LPD_KV | 南科道爺三路(1530) LPD KV | LINE161 | [5 empty] | 622 | DNPAIPoint | DS056 |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D05 | 道爺DS | 161 | 161kV | 1540 | 南科～道爺四路(1540) |  | V |  | INSERT | MvMoment | kV |  | Y |  | AI | [6 empty] | 0222 |  |  | 2-DE |  |  | Locate Empty | V | 1540 南科道爺四路 R相電壓 | kV_-210_210(-2000_2000) |  | B2/D05_A1 | [8 empty] | 道爺DS.1540LPD_KV | 南科道爺四路(1540) LPD KV | LINE161 | [5 empty] | 623 | DNPAIPoint | DS056 |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺~奇晶七紅線(1550) |  | V |  | INSERT | MvMoment | kV |  | Y |  | AI | [6 empty] | 0223 |  |  | 2-DF |  |  | Locate Empty | V | 1550 道爺奇晶七紅線 R相電壓 | kV_-210_210(-2000_2000) |  | B2/D05_A1 | [8 empty] | 道爺DS.1550LPD_KV | 道爺奇晶七紅線(1550) LPD KV | LINE161 | [5 empty] | 624 | DNPAIPoint | DS056 |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺~奇晶七白線(1560) |  | V |  | INSERT | MvMoment | kV |  | Y |  | AI | [6 empty] | 0224 |  |  | 2-E0 |  |  | Locate Empty | V | 1560 道爺奇晶七白線 R相電壓 | kV_-210_210(-2000_2000) |  | B2/D05_A1 | [8 empty] | 道爺DS.1560LPD_KV | 道爺奇晶七白線(1560) LPD KV | LINE161 | [5 empty] | 625 | DNPAIPoint | DS056 |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺～奇晶六紅線(1570) |  | V |  | INSERT | MvMoment | kV |  | Y |  | AI | [6 empty] | 0225 |  |  | 2-E1 |  |  | Locate Empty | V | 1570 道爺奇晶六線紅線 R相電壓 | kV_-210_210(-2000_2000) |  | B2/D05_A1 | [8 empty] | 道爺DS.1570LPD_KV | 道爺奇晶六紅線(1570) LPD KV | LINE161 | [5 empty] | 626 | DNPAIPoint | DS056 |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺～奇晶六白線(1580) |  | V |  | INSERT | MvMoment | kV |  | Y |  | AI | [6 empty] | 0226 |  |  | 2-E2 |  |  | Locate Empty | V | 1580 道爺奇晶六線白線 R相電壓 | kV_-210_210(-2000_2000) |  | B2/D05_A1 | [8 empty] | 道爺DS.1580LPD_KV | 道爺奇晶六白線(1580) LPD KV | LINE161 | [5 empty] | 627 | DNPAIPoint | DS056 |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D05 | 道爺DS | 161 | 161kV | 1610 | 道爺~安南~新化線(1610) |  | V |  | INSERT | MvMoment | kV |  | Y |  | AI | [6 empty] | 0227 |  |  | 2-E3 |  |  | Locate Empty | V | 1610 道爺安南新化線 R相電壓 | kV_-210_210(-2000_2000) |  | B2/D05_A1 | [8 empty] | 道爺DS.1610LPD_KV | 道爺安南新化線(1610) LPD KV | LINE161 | [5 empty] | 628 | DNPAIPoint | DS056 |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D05 | 道爺DS | 161 | 161kV | 1620 | 道爺~和順~新化線(1620) |  | V |  | INSERT | MvMoment | kV |  | Y |  | AI | [6 empty] | 0228 |  |  | 2-E4 |  |  | Locate Empty | V | 1620 道爺和順新化線 R相電壓 | kV_-210_210(-2000_2000) |  | B2/D05_A1 | [8 empty] | 道爺DS.1620LPD_KV | 道爺和順新化線(1620) LPD KV | LINE161 | [5 empty] | 629 | DNPAIPoint | DS056 |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D05 | 道爺DS | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | V |  | INSERT | MvMoment | kV |  | Y |  | AI | [6 empty] | 0219 |  |  | 2-DB |  |  | Locate Empty | V | 1510 南科道爺一路 R相電壓 | kV_-210_210(-2000_2000) |  | B2/D05_A1 | [8 empty] | 道爺DS.1510LPD_KV | 南科道爺ㄧ路(1510) LPD KV | LINE161 | [5 empty] | 630 | DNPAIPoint | DS056 |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D05 | 道爺DS | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | V |  | INSERT | MvMoment | kV |  | Y |  | AI | [6 empty] | 0220 |  |  | 2-DC |  |  | Locate Empty | V | 1520 南科道爺二路 R相電壓 | kV_-210_210(-2000_2000) |  | B2/D05_A1 | [8 empty] | 道爺DS.1520LPD_KV | 南科道爺二路(1520) LPD KV | LINE161 | [5 empty] | 631 | DNPAIPoint | DS056 |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D05 | 道爺DS | 22 | 22kV | 330 | #2DTR(330) |  | 81UL |  | INSERT | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0870 |  | 0242 | 2-36-06 |  | 2-72 | 3DI-CH5 | 81S | 330 低頻電驛閉鎖開關 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.330_81UL | 330 #2DTR(A) 81RY U/L | OTHER | [5 empty] | 632 | DNPDIPoint | DS056 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 340 | #2DTR(340) |  | 81UL |  | INSERT | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0871 |  | 0243 | 2-36-07 |  | 2-73 | 3DI-CH5 | 81S | 340 低頻電驛閉鎖開關 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.340_81UL | 340 #2DTR(B) 81RY U/L | OTHER | [5 empty] | 633 | DNPDIPoint | DS056 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 350 | #3DTR(350) |  | 81UL |  | INSERT | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0872 |  | 0244 | 2-36-08 |  | 2-74 | 3DI-CH5 | 81S | 350 低頻電驛閉鎖開關 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.350_81UL | 350 #3DTR(A) 81RY U/L | OTHER | [5 empty] | 634 | DNPDIPoint | DS056 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 360 | #3DTR(360) |  | 81UL |  | INSERT | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0873 |  | 0245 | 2-36-09 |  | 2-75 | 3DI-CH5 | 81S | 360 低頻電驛閉鎖開關 |  |  | B3/D05_A1 | [8 empty] | 道爺DS.360_81UL | 360 #3DTR(B) 81RY U/L | OTHER | [5 empty] | 635 | DNPDIPoint | DS056 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D05 | 道爺DS |  |  | 1DTR | #1DTR |  | GDA |  | INSERT | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0140 |  |  | 1-11-04 |  |  | Locate Empty |  | #1 DTR GDA |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#1DTR_GDA | #1DTR 50N/51N RY | OTHER | [5 empty] | 636 | DNPDIPoint | DS056 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS |  |  | 1DTR | #1DTR |  | PHA |  | INSERT | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0139 |  |  | 1-11-03 |  |  | Locate Empty |  | #1 DTR PHA |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#1DTR_PHA | #1DTR 50/51 RY | OTHER | [5 empty] | 637 | DNPDIPoint | DS056 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS |  |  | 4DTR | #4DTR |  | GDA |  | INSERT | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0146 |  |  | 1-12-02 |  |  | Locate Empty |  | #4 DTR GDA |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#4DTR_GDA | #4DTR 50N/51N RY | OTHER | [5 empty] | 638 | DNPDIPoint | DS056 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D05 | 道爺DS |  |  | 4DTR | #4DTR |  | PHA |  | INSERT | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0145 |  |  | 1-12-01 |  |  | Locate Empty |  | #4 DTR PHA |  |  | B1/D05_A1 | [8 empty] | 道爺DS.#4DTR_PHA | #4DTR 50/51 RY | OTHER | [5 empty] | 639 | DNPDIPoint | DS056 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
D05 | 道爺DS | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/D05_A1 | [15 empty] | BEST_SOURCE_161KV_2 |  | v_best_161_12 | OPRD1: D05/161/1BUS/V; OPRD2: D05/161/2BUS/V
D05 | 道爺DS | 0 |  | CalcPoint |  |  | Vbs5 | [9 empty] | B1/D05_A1 | [15 empty] | BEST_SOURCE_161KV_2 |  | v_best_161_34 | OPRD1: D05/161/3BUS/V; OPRD2: D05/161/4BUS/V
D05 | 道爺DS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/D05_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: D05/0/CalcPoint/Vbs4; OPRD5: D05/0/CalcPoint/Vbs5; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
D05 | 道爺DS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/D05_A1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_10 | OPRD1: D05/161/1510/MW; OPRD2: D05/161/1520/MW; OPRD3: D05/161/1530/MW; OPRD4: D05/161/1540/MW; OPRD5: D05/161/1550/MW; OPRD6: D05/161/1560/MW; OPRD7: D05/161/1570/MW; OPRD8: D05/161/1580/MW; OPRD9: D05/161/1610/MW; OPRD10: D05/161/1620/MW
D05 | 道爺DS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/D05_A1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: D05/0/CalcPoint/OPRN2_MW
D05 | 道爺DS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/D05_A1 | [17 empty] | none
D05 | 道爺DS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/D05_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: D05/0/CalcPoint/OPRN1; OPRD2: D05/0/CalcPoint/OPRN2; OPRD3: D05/0/CalcPoint/PRFL_UL
D05 | 道爺DS |  |  | 2DTR | 2DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D05_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D05/22/330/I_R; OPRD2: D05/22/340/I_R
D05 | 道爺DS |  |  | 2DTR | 2DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D05_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D05/22/330/I_S; OPRD2: D05/22/340/I_S
D05 | 道爺DS |  |  | 2DTR | 2DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D05_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D05/22/330/I_T; OPRD2: D05/22/340/I_T
D05 | 道爺DS |  |  | 3DTR | 3DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D05_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D05/22/350/I_R; OPRD2: D05/22/360/I_R
D05 | 道爺DS |  |  | 3DTR | 3DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D05_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D05/22/350/I_S; OPRD2: D05/22/360/I_S
D05 | 道爺DS |  |  | 3DTR | 3DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D05_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D05/22/350/I_T; OPRD2: D05/22/360/I_T
D05 | 道爺DS | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D05_A1 | [12 empty] | 道爺DS.1510_AMP | 南科道爺ㄧ路 AMP | LINE161 | AMP_CAL | C20R1790 | amp_cal | OPRD1: D05/161/1510/MW; OPRD2: D05/161/1510/MVAR; OPRD3: D05/0/CalcPoint/Vbs4
D05 | 道爺DS | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D05_A1 | [12 empty] | 道爺DS.1520_AMP | 南科道爺二路 AMP | LINE161 | AMP_CAL | C20R1790 | amp_cal | OPRD1: D05/161/1520/MW; OPRD2: D05/161/1520/MVAR; OPRD3: D05/0/CalcPoint/Vbs4
D05 | 道爺DS | 161 | 161kV | 1530 | 南科～道爺三路(1530) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D05_A1 | [12 empty] | 道爺DS.1530_AMP | 南科道爺三路 AMP | LINE161 | AMP_CAL | C20R1790 | amp_cal | OPRD1: D05/161/1530/MW; OPRD2: D05/161/1530/MVAR; OPRD3: D05/0/CalcPoint/Vbs4
D05 | 道爺DS | 161 | 161kV | 1540 | 南科～道爺四路(1540) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D05_A1 | [12 empty] | 道爺DS.1540_AMP | 南科道爺四路 AMP | LINE161 | AMP_CAL | C20R1790 | amp_cal | OPRD1: D05/161/1540/MW; OPRD2: D05/161/1540/MVAR; OPRD3: D05/0/CalcPoint/Vbs4
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺~奇晶七紅線(1550) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D05_A1 | [12 empty] | 道爺DS.1550_AMP | 道爺奇晶七紅線 AMP | LINE161 | AMP_CAL | C20R0964 | amp_cal | OPRD1: D05/161/1550/MW; OPRD2: D05/161/1550/MVAR; OPRD3: D05/0/CalcPoint/Vbs4
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺~奇晶七白線(1560) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D05_A1 | [12 empty] | 道爺DS.1560_AMP | 道爺奇晶七白線 AMP | LINE161 | AMP_CAL | C20R0964 | amp_cal | OPRD1: D05/161/1560/MW; OPRD2: D05/161/1560/MVAR; OPRD3: D05/0/CalcPoint/Vbs4
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺～奇晶六紅線(1570) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D05_A1 | [12 empty] | 道爺DS.1570_AMP | 道爺奇晶六紅線 AMP | LINE161 | AMP_CAL | C20R0964 | amp_cal | OPRD1: D05/161/1570/MW; OPRD2: D05/161/1570/MVAR; OPRD3: D05/0/CalcPoint/Vbs4
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺～奇晶六白線(1580) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D05_A1 | [12 empty] | 道爺DS.1580_AMP | 道爺奇晶六白線 AMP | LINE161 | AMP_CAL | C20R0964 | amp_cal | OPRD1: D05/161/1580/MW; OPRD2: D05/161/1580/MVAR; OPRD3: D05/0/CalcPoint/Vbs4
D05 | 道爺DS | 161 | 161kV | 1610 | 道爺~安南~新化線(1610) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D05_A1 | [12 empty] | 道爺DS.1610_AMP | 道爺安南新化線 AMP | LINE161 | AMP_CAL | C20R1790 | amp_cal | OPRD1: D05/161/1610/MW; OPRD2: D05/161/1610/MVAR; OPRD3: D05/0/CalcPoint/Vbs5
D05 | 道爺DS | 161 | 161kV | 1620 | 道爺~和順~新化線(1620) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D05_A1 | [12 empty] | 道爺DS.1620_AMP | 道爺和順新化線 AMP | LINE161 | AMP_CAL | C20R1790 | amp_cal | OPRD1: D05/161/1620/MW; OPRD2: D05/161/1620/MVAR; OPRD3: D05/0/CalcPoint/Vbs5
D05 | 道爺DS | 22 | 22kV | 2ABUS | #2ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D05_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D05/22/2ABUS/V
D05 | 道爺DS | 22 | 22kV | 2BBUS | #2BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D05_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D05/22/2BBUS/V
D05 | 道爺DS | 22 | 22kV | 3ABUS | #3ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D05_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D05/22/3ABUS/V
D05 | 道爺DS | 22 | 22kV | 3BBUS | #3BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D05_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D05/22/3BBUS/V
D05 | 道爺DS |  |  | 2DTR | #2DTR |  | TR_PERM | [9 empty] | B1/D05_A1 | [12 empty] | 道爺DS.#2DTR_PERM | #2DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D05//2DTR/SupLocal; OPRD2: D05//2DTR/Tap Chan
D05 | 道爺DS |  |  | 3DTR | #3DTR |  | TR_PERM | [9 empty] | B1/D05_A1 | [12 empty] | 道爺DS.#3DTR_PERM | #3DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D05//3DTR/SupLocal; OPRD2: D05//3DTR/Tap Chan
D05 | 道爺DS | 22 | 22kV | 4K61 | 爺61線(4K61) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D05_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D05/22/2ABUS/V; OPRD2: D05/22/4K61/I_R; OPRD3: D05/22/4K61/I_S; OPRD4: D05/22/4K61/I_T
D05 | 道爺DS | 22 | 22kV | 4K62 | 爺62線(4K62) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D05_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D05/22/2ABUS/V; OPRD2: D05/22/4K62/I_R; OPRD3: D05/22/4K62/I_S; OPRD4: D05/22/4K62/I_T
D05 | 道爺DS | 22 | 22kV | 4K63 | 爺63線(4K63) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D05_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D05/22/2ABUS/V; OPRD2: D05/22/4K63/I_R; OPRD3: D05/22/4K63/I_S; OPRD4: D05/22/4K63/I_T
D05 | 道爺DS | 22 | 22kV | 4K64 | 爺64線(4K64) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D05_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D05/22/2ABUS/V; OPRD2: D05/22/4K64/I_R; OPRD3: D05/22/4K64/I_S; OPRD4: D05/22/4K64/I_T
D05 | 道爺DS | 22 | 22kV | 4K65 | 爺65線(4K65) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D05_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D05/22/2BBUS/V; OPRD2: D05/22/4K65/I_R; OPRD3: D05/22/4K65/I_S; OPRD4: D05/22/4K65/I_T
D05 | 道爺DS | 22 | 22kV | 4K66 | 爺66線(4K66) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D05_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D05/22/2BBUS/V; OPRD2: D05/22/4K66/I_R; OPRD3: D05/22/4K66/I_S; OPRD4: D05/22/4K66/I_T
D05 | 道爺DS | 22 | 22kV | 4K67 | 爺67線(4K67) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D05_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D05/22/2BBUS/V; OPRD2: D05/22/4K67/I_R; OPRD3: D05/22/4K67/I_S; OPRD4: D05/22/4K67/I_T
D05 | 道爺DS | 22 | 22kV | 4K68 | 爺68線(4K68) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D05_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D05/22/2BBUS/V; OPRD2: D05/22/4K68/I_R; OPRD3: D05/22/4K68/I_S; OPRD4: D05/22/4K68/I_T
D05 | 道爺DS | 22 | 22kV | 4K71 | 爺71線(4K71) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D05_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D05/22/3ABUS/V; OPRD2: D05/22/4K71/I_R; OPRD3: D05/22/4K71/I_S; OPRD4: D05/22/4K71/I_T
D05 | 道爺DS | 22 | 22kV | 4K72 | 爺72線(4K72) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D05_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D05/22/3ABUS/V; OPRD2: D05/22/4K72/I_R; OPRD3: D05/22/4K72/I_S; OPRD4: D05/22/4K72/I_T
D05 | 道爺DS | 22 | 22kV | 4K73 | 爺73線(4K73) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D05_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D05/22/3ABUS/V; OPRD2: D05/22/4K73/I_R; OPRD3: D05/22/4K73/I_S; OPRD4: D05/22/4K73/I_T
D05 | 道爺DS | 22 | 22kV | 4K74 | 爺74線(4K74) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D05_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D05/22/3ABUS/V; OPRD2: D05/22/4K74/I_R; OPRD3: D05/22/4K74/I_S; OPRD4: D05/22/4K74/I_T
D05 | 道爺DS | 22 | 22kV | 4K75 | 爺75線(4K75) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D05_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D05/22/3BBUS/V; OPRD2: D05/22/4K75/I_R; OPRD3: D05/22/4K75/I_S; OPRD4: D05/22/4K75/I_T
D05 | 道爺DS | 22 | 22kV | 4K76 | 爺76線(4K76) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D05_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D05/22/3BBUS/V; OPRD2: D05/22/4K76/I_R; OPRD3: D05/22/4K76/I_S; OPRD4: D05/22/4K76/I_T
D05 | 道爺DS | 22 | 22kV | 4K77 | 爺77線(4K77) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D05_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D05/22/3BBUS/V; OPRD2: D05/22/4K77/I_R; OPRD3: D05/22/4K77/I_S; OPRD4: D05/22/4K77/I_T
D05 | 道爺DS | 22 | 22kV | 4K78 | 爺78線(4K78) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D05_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D05/22/3BBUS/V; OPRD2: D05/22/4K78/I_R; OPRD3: D05/22/4K78/I_S; OPRD4: D05/22/4K78/I_T
D05 | 道爺DS | 22 | 22kV | 4K61 | 爺61線(4K61) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D05_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D05/22/4K61/kVA; OPRD2: D05/22/4K61/KVAR
D05 | 道爺DS | 22 | 22kV | 4K62 | 爺62線(4K62) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D05_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D05/22/4K62/kVA; OPRD2: D05/22/4K62/KVAR
D05 | 道爺DS | 22 | 22kV | 4K63 | 爺63線(4K63) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D05_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D05/22/4K63/kVA; OPRD2: D05/22/4K63/KVAR
D05 | 道爺DS | 22 | 22kV | 4K64 | 爺64線(4K64) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D05_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D05/22/4K64/kVA; OPRD2: D05/22/4K64/KVAR
D05 | 道爺DS | 22 | 22kV | 4K65 | 爺65線(4K65) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D05_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D05/22/4K65/kVA; OPRD2: D05/22/4K65/KVAR
D05 | 道爺DS | 22 | 22kV | 4K66 | 爺66線(4K66) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D05_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D05/22/4K66/kVA; OPRD2: D05/22/4K66/KVAR
D05 | 道爺DS | 22 | 22kV | 4K67 | 爺67線(4K67) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D05_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D05/22/4K67/kVA; OPRD2: D05/22/4K67/KVAR
D05 | 道爺DS | 22 | 22kV | 4K68 | 爺68線(4K68) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D05_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D05/22/4K68/kVA; OPRD2: D05/22/4K68/KVAR
D05 | 道爺DS | 22 | 22kV | 4K71 | 爺71線(4K71) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D05_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D05/22/4K71/kVA; OPRD2: D05/22/4K71/KVAR
D05 | 道爺DS | 22 | 22kV | 4K72 | 爺72線(4K72) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D05_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D05/22/4K72/kVA; OPRD2: D05/22/4K72/KVAR
D05 | 道爺DS | 22 | 22kV | 4K73 | 爺73線(4K73) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D05_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D05/22/4K73/kVA; OPRD2: D05/22/4K73/KVAR
D05 | 道爺DS | 22 | 22kV | 4K74 | 爺74線(4K74) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D05_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D05/22/4K74/kVA; OPRD2: D05/22/4K74/KVAR
D05 | 道爺DS | 22 | 22kV | 4K75 | 爺75線(4K75) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D05_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D05/22/4K75/kVA; OPRD2: D05/22/4K75/KVAR
D05 | 道爺DS | 22 | 22kV | 4K76 | 爺76線(4K76) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D05_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D05/22/4K76/kVA; OPRD2: D05/22/4K76/KVAR
D05 | 道爺DS | 22 | 22kV | 4K77 | 爺77線(4K77) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D05_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D05/22/4K77/kVA; OPRD2: D05/22/4K77/KVAR
D05 | 道爺DS | 22 | 22kV | 4K78 | 爺78線(4K78) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D05_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D05/22/4K78/kVA; OPRD2: D05/22/4K78/KVAR
D05 | 道爺DS | 22 | 22kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D05_A1 | [12 empty] | 道爺DS.230_SC_MVAR | 23KV#3SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D05/22/230/CB; OPRD2: 13.8; OPRD3: 0
D05 | 道爺DS | 22 | 22kV | 240 | #4SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D05_A1 | [12 empty] | 道爺DS.240_SC_MVAR | 23KV#4SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D05/22/240/CB; OPRD2: 13.8; OPRD3: 0
D05 | 道爺DS | 22 | 22kV | 250 | #5SC(250) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D05_A1 | [12 empty] | 道爺DS.250_SC_MVAR | 23KV#5SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D05/22/250/CB; OPRD2: 13.8; OPRD3: 0
D05 | 道爺DS | 22 | 22kV | 260 | #6SC(260) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D05_A1 | [12 empty] | 道爺DS.260_SC_MVAR | 23KV#6SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D05/22/260/CB; OPRD2: 13.8; OPRD3: 0
D05 | 道爺DS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/D05_A1 | [12 empty] | 道爺DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_12 |  | com_alarm_36 | D05//1DTR/GDA | D05//1DTR/PHA | D05//2DTR/96D | D05//2DTR/96B1 | D05//2DTR/96B2 | D05//2DTR/63Q | D05//2DTR/GDA | D05//2DTR/PHA | D05//2DTR/TRA | D05//2DTR/51ZA | D05//2DTR/96PA | D05//2DTR/87A | D05//3DTR/96B1 | D05//3DTR/63Q | D05//3DTR/96B2 | D05//3DTR/GDA | D05//3DTR/PHA | D05//3DTR/51ZA | D05//3DTR/96PA | D05//3DTR/87A | D05//3DTR/TRA | D05//3DTR/96D | D05//4DTR/PHA | D05//4DTR/GDA | D05/161/1BUS/87A | D05/161/2BUS/87A | D05/161/3BUS/87A | D05/161/4BUS/87A | D05/22/330/PHA | D05/22/330/GDA | D05/22/340/GDA | D05/22/340/PHA | D05/22/350/GDA | D05/22/350/PHA | D05/22/360/PHA | D05/22/360/GDA
D05 | 道爺DS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/D05_A1 | [12 empty] | 道爺DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | STATION_FAULT_2 |  | com_alarm_2 | OPRD1: D05//2DTR/TRF; OPRD2: D05//3DTR/TRF
D05 | 道爺DS | 161 | 161kV | 1760_D1 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D05_D1 | [17 empty] | lamp2CC | OPRD1: D05/161/1760/CB
D05 | 道爺DS | 22 | 22kV | 330_D1 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D05_D1 | [17 empty] | lamp2CC | OPRD1: D05/22/330/CB
D05 | 道爺DS | 22 | 22kV | 340_D1 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D05_D1 | [17 empty] | lamp2CC | OPRD1: D05/22/340/CB
D05 | 道爺DS | 161 | 161kV | 1770_D1 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D05_D1 | [17 empty] | lamp2CC | OPRD1: D05/161/1770/CB
D05 | 道爺DS | 22 | 22kV | 350_D1 | #3DTR(A)(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D05_D1 | [17 empty] | lamp2CC | OPRD1: D05/22/350/CB
D05 | 道爺DS | 22 | 22kV | 360_D1 | #3DTR(B)(360) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D05_D1 | [17 empty] | lamp2CC | OPRD1: D05/22/360/CB
D05 | 道爺DS | 0 |  | RTU_D1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/D05_D1 | [17 empty] | lamp2CC | OPRD1: D05/0/RTU/RTU_R_L
D05 | 道爺DS | 0 |  | StaDev_D1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D05_D1 | [17 empty] | lamp2CC | OPRD1: D05/0/StaDev/DCA
D05 | 道爺DS | 0 |  | StaDev_D1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D05_D1 | [17 empty] | lamp2CC | OPRD1: D05/0/StaDev/DCE
D05 | 道爺DS | 0 |  | StaDev_D1 | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/D05_D1 | [17 empty] | lamp2CC | OPRD1: D05/0/StaDev/STUV

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D05 | 道爺DS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 道爺DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS |  |  | BEST_SOURCE_161KV_4 |  |  | 2 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
D05 | 道爺DS | 161 | 161kV | 1530 | 南科道爺三路(1530) |  | I | [25 empty] | ADCS_S | [8 empty] | 道爺DS.1530_AMP | 南科道爺三路 AMP | LINE161 | D05/161/1530/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D05 | 道爺DS | 161 | 161kV | 1540 | 南科道爺四路(1540) |  | I | [25 empty] | ADCS_S | [8 empty] | 道爺DS.1540_AMP | 南科道爺四路 AMP | LINE161 | D05/161/1540/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺奇晶七紅線(1550) |  | I | [25 empty] | ADCS_S | [8 empty] | 道爺DS.1550_AMP | 道爺奇晶七紅線 AMP | LINE161 | D05/161/1550/I |  | AMP_CAL |  |  | 5 | CalcAIPoint | [21 empty] | C20R0964 | 867.599976 | 867.599976 | 964.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺奇晶七白線(1560) |  | I | [25 empty] | ADCS_S | [8 empty] | 道爺DS.1560_AMP | 道爺奇晶七白線 AMP | LINE161 | D05/161/1560/I |  | AMP_CAL |  |  | 6 | CalcAIPoint | [21 empty] | C20R0964 | 867.599976 | 867.599976 | 964.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺奇晶六紅線(1570) |  | I | [25 empty] | ADCS_S | [8 empty] | 道爺DS.1570_AMP | 道爺奇晶六紅線 AMP | LINE161 | D05/161/1570/I |  | AMP_CAL |  |  | 7 | CalcAIPoint | [21 empty] | C20R0964 | 867.599976 | 867.599976 | 964.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺奇晶六白線(1580) |  | I | [25 empty] | ADCS_S | [8 empty] | 道爺DS.1580_AMP | 道爺奇晶六白線 AMP | LINE161 | D05/161/1580/I |  | AMP_CAL |  |  | 8 | CalcAIPoint | [21 empty] | C20R0964 | 867.599976 | 867.599976 | 964.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D05 | 道爺DS | 161 | 161kV | 1610 | 道爺安南新化線(1610) |  | I | [25 empty] | ADCS_S | [8 empty] | 道爺DS.1610_AMP | 道爺安南新化線 AMP | LINE161 | D05/161/1610/I |  | AMP_CAL |  |  | 9 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D05 | 道爺DS | 161 | 161kV | 1620 | 道爺和順新化線(1620) |  | I | [25 empty] | ADCS_S | [8 empty] | 道爺DS.1620_AMP | 道爺和順新化線 AMP | LINE161 | D05/161/1620/I |  | AMP_CAL |  |  | 10 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D05 | 道爺DS | 0 |  |  |  |  | 爺61線KVA | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.爺61線KVA | 23KV爺61線KVA | FEEDER |  |  | KVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  |  |  |  | 爺61線KW | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.爺61線KW | 23KV爺61線KW | FEEDER |  |  | KW_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  |  |  |  | 爺62線KVA | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.爺62線KVA | 23KV爺62線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  |  |  |  | 爺62線KW | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.爺62線KW | 23KV爺62線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  |  |  |  | 爺63線KVA | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.爺63線KVA | 23KV爺63線KVA | FEEDER |  |  | KVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  |  |  |  | 爺63線KW | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.爺63線KW | 23KV爺63線KW | FEEDER |  |  | KW_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  |  |  |  | 爺64線KVA | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.爺64線KVA | 23KV爺64線KVA | FEEDER |  |  | KVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  |  |  |  | 爺64線KW | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.爺64線KW | 23KV爺64線KW | FEEDER |  |  | KW_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  |  |  |  | 爺65線KVA | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.爺65線KVA | 23KV爺65線KVA | FEEDER |  |  | KVA_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  |  |  |  | 爺65線KW | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.爺65線KW | 23KV爺65線KW | FEEDER |  |  | KW_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  |  |  |  | 爺66線KVA | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.爺66線KVA | 23KV爺66線KVA | FEEDER |  |  | KVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  |  |  |  | 爺66線KW | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.爺66線KW | 23KV爺66線KW | FEEDER |  |  | KW_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  |  |  |  | 爺67線KVA | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.爺67線KVA | 23KV爺67線KVA | FEEDER |  |  | KVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  |  |  |  | 爺67線KW | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.爺67線KW | 23KV爺67線KW | FEEDER |  |  | KW_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  |  |  |  | 爺68線KVA | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.爺68線KVA | 23KV爺68線KVA | FEEDER |  |  | KVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  |  |  |  | 爺68線KW | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.爺68線KW | 23KV爺68線KW | FEEDER |  |  | KW_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  |  |  |  | 爺71線KVA | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.爺71線KVA | 23KV爺71線KVA | FEEDER |  |  | KVA_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  |  |  |  | 爺71線KW | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.爺71線KW | 23KV爺71線KW | FEEDER |  |  | KW_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  |  |  |  | 爺72線KVA | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.爺72線KVA | 23KV爺72線KVA | FEEDER |  |  | KVA_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  |  |  |  | 爺72線KW | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.爺72線KW | 23KV爺72線KW | FEEDER |  |  | KW_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  |  |  |  | 爺73線KVA | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.爺73線KVA | 23KV爺73線KVA | FEEDER |  |  | KVA_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  |  |  |  | 爺73線KW | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.爺73線KW | 23KV爺73線KW | FEEDER |  |  | KW_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  |  |  |  | 爺74線KVA | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.爺74線KVA | 23KV爺74線KVA | FEEDER |  |  | KVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  |  |  |  | 爺74線KW | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.爺74線KW | 23KV爺74線KW | FEEDER |  |  | KW_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  |  |  |  | 爺75線KVA | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.爺75線KVA | 23KV爺75線KVA | FEEDER |  |  | KVA_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  |  |  |  | 爺75線KW | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.爺75線KW | 23KV爺75線KW | FEEDER |  |  | KW_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  |  |  |  | 爺76線KVA | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.爺76線KVA | 23KV爺76線KVA | FEEDER |  |  | KVA_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  |  |  |  | 爺76線KW | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.爺76線KW | 23KV爺76線KW | FEEDER |  |  | KW_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  |  |  |  | 爺77線KVA | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.爺77線KVA | 23KV爺77線KVA | FEEDER |  |  | KVA_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  |  |  |  | 爺77線KW | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.爺77線KW | 23KV爺77線KW | FEEDER |  |  | KW_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  |  |  |  | 爺78線KVA | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.爺78線KVA | 23KV爺78線KVA | FEEDER |  |  | KVA_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  |  |  |  | 爺78線KW | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.爺78線KW | 23KV爺78線KW | FEEDER |  |  | KW_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 道爺DS.#2DTR(A)_MVA | #2DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 43 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D05 | 道爺DS | 0 |  | 2DTR(A) | #2DTR(A) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 道爺DS.#2DTR(A)_LOAD | #2DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 44 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D05 | 道爺DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PF | [25 empty] | ADCS_S | [8 empty] | 道爺DS.#2DTR(A)_PF | #2DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 45 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D05 | 道爺DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 道爺DS.#2DTR(B)_MVA | #2DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 46 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D05 | 道爺DS | 0 |  | 2DTR(B) | #2DTR(B) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 道爺DS.#2DTR(B)_LOAD | #2DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 47 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D05 | 道爺DS | 0 |  | 2DTR(B) | #2DTR(B) |  | PF | [25 empty] | ADCS_S | [8 empty] | 道爺DS.#2DTR(B)_PF | #2DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 48 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D05 | 道爺DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 道爺DS.#3DTR(A)_MVA | #3DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 49 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D05 | 道爺DS | 0 |  | 3DTR(A) | #3DTR(A) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 道爺DS.#3DTR(A)_LOAD | #3DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 50 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D05 | 道爺DS | 0 |  | 3DTR(A) | #3DTR(A) |  | PF | [25 empty] | ADCS_S | [8 empty] | 道爺DS.#3DTR(A)_PF | #3DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 51 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D05 | 道爺DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 道爺DS.#3DTR(B)_MVA | #3DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 52 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D05 | 道爺DS | 0 |  | 3DTR(B) | #3DTR(B) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 道爺DS.#3DTR(B)_LOAD | #3DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 53 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D05 | 道爺DS | 0 |  | 3DTR(B) | #3DTR(B) |  | PF | [25 empty] | ADCS_S | [8 empty] | 道爺DS.#3DTR(B)_PF | #3DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 54 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D05 | 道爺DS | 0 |  | 2DTR | #2DTR |  | MW | [25 empty] | ADCS_S | [8 empty] | 道爺DS.#2DTR_MW | #2DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 55 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  | 2DTR | #2DTR |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 道爺DS.#2DTR_MVAR | #2DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 56 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  | 2DTR | #2DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 道爺DS.#2DTR_MVA | #2DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 57 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D05 | 道爺DS | 0 |  | 2DTR | #2DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 道爺DS.#2DTR_LOAD | #2DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 58 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D05 | 道爺DS | 0 |  | 2DTR | #2DTR |  | PF | [25 empty] | ADCS_S | [8 empty] | 道爺DS.#2DTR_PF | #2DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 59 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D05 | 道爺DS | 0 |  | 3DTR | #3DTR |  | MW | [25 empty] | ADCS_S | [8 empty] | 道爺DS.#3DTR_MW | #3DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 60 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  | 3DTR | #3DTR |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 道爺DS.#3DTR_MVAR | #3DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 61 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  | 3DTR | #3DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 道爺DS.#3DTR_MVA | #3DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 62 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D05 | 道爺DS | 0 |  | 3DTR | #3DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 道爺DS.#3DTR_LOAD | #3DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 63 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D05 | 道爺DS | 0 |  | 3DTR | #3DTR |  | PF | [25 empty] | ADCS_S | [8 empty] | 道爺DS.#3DTR_PF | #3DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 64 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D05 | 道爺DS | 22 | 22kV | 230_SC | #3SC | 9 | MVAR | [25 empty] | ADCS_S | [8 empty] | 道爺DS.230_SC_MVAR | 23KV#3SC MVAR | SC | D05/22/230/MVAR |  | SC_CAL_23 |  |  | 65 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 22 | 22kV | 240_SC | #4SC | 9 | MVAR | [25 empty] | ADCS_S | [8 empty] | 道爺DS.240_SC_MVAR | 23KV#4SC MVAR | SC | D05/22/240/MVAR |  | SC_CAL_23 |  |  | 66 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 22 | 22kV | 250_SC | #5SC | 9 | MVAR | [25 empty] | ADCS_S | [8 empty] | 道爺DS.250_SC_MVAR | 23KV#5SC MVAR | SC | D05/22/250/MVAR |  | SC_CAL_23 |  |  | 67 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 22 | 22kV | 260_SC | #6SC | 9 | MVAR | [25 empty] | ADCS_S | [8 empty] | 道爺DS.260_SC_MVAR | 23KV#6SC MVAR | SC | D05/22/260/MVAR |  | SC_CAL_23 |  |  | 68 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  | TRTOT | 道爺主變瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 道爺DS.TRTOT_MW | 道爺主變瞬時供電量 MW |  |  |  | MTR_PQ_CAL |  |  | 69 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 0 |  | TRTOT | 道爺主變瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 道爺DS.TRTOT_MVAR | 道爺主變瞬時供電量 MVAR |  |  |  | MTR_PQ_CAL |  |  | 70 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 22 | 22kV | 2BUS | #2BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 道爺DS.23KV#2BUS_KV | 23KV #2BUS BEST SOURCE | BUS |  |  | BEST_1W2CB |  |  | 71 | CalcAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D05 | 道爺DS | 22 | 22kV | 3BUS | #3BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 道爺DS.23KV#3BUS_KV | 23KV #3BUS BEST SOURCE | BUS |  |  | BEST_1W2CB |  |  | 72 | CalcAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D05 | 道爺DS | 161 | 161kV | 1510 | 南科道爺ㄧ路(1510) |  | I | [25 empty] | ADCS_S | [8 empty] | 道爺DS.1510_AMP | 南科道爺ㄧ路 AMP | LINE161 | D05/161/1510/I |  | AMP_CAL |  |  | 73 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D05 | 道爺DS | 161 | 161kV | 1520 | 南科道爺二路(1520) |  | I | [25 empty] | ADCS_S | [8 empty] | 道爺DS.1520_AMP | 南科道爺二路 AMP | LINE161 | D05/161/1520/I |  | AMP_CAL |  |  | 74 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D05 | 道爺DS | 0 |  | 200_CB | 200(200_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.200_CB_4 | 200 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 75 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 300_CB | 300(300_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.300_CB_4 | 300 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 76 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 22 | 22kV | 11__CBA | 11/斷路器重故障(11__CBA) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.11/23KV_CBA_4 | 11/23KV斷路器重故障 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 77 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 11__CBF | 11/斷路器輕故障(11__CBF) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.11/23KV_CBF_4 | 11/23KV斷路器輕故障 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 78 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | COMM_S_L | 通訊處理單元 |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.COMM_S/L_4 | 通訊處理單元 SUPY/LOCAL (D4) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 79 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D05 | 道爺DS | 0 |  | TCA | 斷路器跳脫回路故障 |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.TCA_4 | 斷路器跳脫回路故障 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 80 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_S | [8 empty] | 道爺DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | D05/0/CalcPoint/SUBA |  | STATION_FAULT_12 |  |  | 81 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 變電所輕故障點燈 | 變電所輕故障點燈 |  | SUBF | [25 empty] | ADCS_S | [8 empty] | 道爺DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | D05/0/CalcPoint/SUBF |  | STATION_FAULT_2 |  |  | 82 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1530_AMP | 南科道爺三路 | [27 empty] | ADCS_S | [8 empty] | 道爺DS.1530_AMP_A | 南科道爺三路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 83 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D05 | 道爺DS | 161 | 161kV | 1540_AMP | 南科道爺四路 | [27 empty] | ADCS_S | [8 empty] | 道爺DS.1540_AMP_A | 南科道爺四路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 84 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D05 | 道爺DS | 161 | 161kV | 1550_AMP | 道爺奇晶七紅線 | [27 empty] | ADCS_S | [8 empty] | 道爺DS.1550_AMP_A | 道爺奇晶七紅線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 85 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D05 | 道爺DS | 161 | 161kV | 1560_AMP | 道爺奇晶七白線 | [27 empty] | ADCS_S | [8 empty] | 道爺DS.1560_AMP_A | 道爺奇晶七白線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 86 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D05 | 道爺DS | 161 | 161kV | 1570_AMP | 道爺奇晶六紅線 | [27 empty] | ADCS_S | [8 empty] | 道爺DS.1570_AMP_A | 道爺奇晶六紅線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 87 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D05 | 道爺DS | 161 | 161kV | 1580_AMP | 道爺奇晶六白線 | [27 empty] | ADCS_S | [8 empty] | 道爺DS.1580_AMP_A | 道爺奇晶六白線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 88 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D05 | 道爺DS | 161 | 161kV | 1610_AMP | 道爺安南新化線 | [27 empty] | ADCS_S | [8 empty] | 道爺DS.1610_AMP_A | 道爺安南新化線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 89 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D05 | 道爺DS | 161 | 161kV | 1620_AMP | 道爺和順新化線 | [27 empty] | ADCS_S | [8 empty] | 道爺DS.1620_AMP_A | 道爺和順新化線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 90 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D05 | 道爺DS | 0 |  | 2DTR | #2DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 道爺DS.#2DTR_PERM | #2DTR TAP PERMISSION POINT | MTR | D05//2DTR/TR_PERM |  | DTR_PERM |  |  | 91 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D05 | 道爺DS | 0 |  | 3DTR | #3DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 道爺DS.#3DTR_PERM | #3DTR TAP PERMISSION POINT | MTR | D05//3DTR/TR_PERM |  | DTR_PERM |  |  | 92 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D05 | 道爺DS | 0 |  | 2DTR_MVA | #2DTR | [27 empty] | ADCS_S | [8 empty] | 道爺DS.#2DTR_MVA_A | #2DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 93 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D05 | 道爺DS | 0 |  | 3DTR_MVA | #3DTR | [27 empty] | ADCS_S | [8 empty] | 道爺DS.#3DTR_MVA_A | #3DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 94 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D05 | 道爺DS | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_S | [8 empty] | 道爺DS.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_PS |  |  | 95 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | PMCC故障 | PMCC電驛故障 |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 道爺DS.PMCC故障_4 | PMCC電驛故障 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 96 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 2ABUS | #2ABUS |  | 23KV#2ABUSC | [25 empty] | CDCS | [8 empty] | 道爺DS.23KV#2ABUSC | #2ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 97 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D05 | 道爺DS | 0 |  | 2BBUS | #2BBUS |  | 23KV#2BBUSC | [25 empty] | CDCS | [8 empty] | 道爺DS.23KV#2BBUSC | #2BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 98 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D05 | 道爺DS | 0 |  | 3ABUS | #3ABUS |  | 23KV#3ABUSC | [25 empty] | CDCS | [8 empty] | 道爺DS.23KV#3ABUSC | #3ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 99 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D05 | 道爺DS | 0 |  | 3BBUS | #3BBUS |  | 23KV#3BBUSC | [25 empty] | CDCS | [8 empty] | 道爺DS.23KV#3BBUSC | #3BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 100 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D05 | 道爺DS | 0 |  | TAP_OVER | TAP |  | SET | [25 empty] | ADCS_S | [8 empty] | 道爺DS.TAP_OVER_SET | TAP OVER HI/LO ALARM | MTR |  |  | 5000_CB_T2 |  |  | 101 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D05 | 道爺DS | 0 |  | BUS_OVER | BUS |  | SET | [25 empty] | ADCS_S | [8 empty] | 道爺DS.BUS_OVER_SET | BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B4 |  |  | 102 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D05 | 道爺DS | 0 |  | 5000 | 虛擬5000 |  | CB動作 | [25 empty] | ADCS_S | [8 empty] | 道爺DS.5000_CB動作 | 虛擬5000 CB動作,請查明原因處理 | MTR |  |  | 5000_CB_M |  |  | 103 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 161 | 161kV | 1510_AMP | 南科道爺ㄧ路 | [27 empty] | ADCS_S | [8 empty] | 道爺DS.1510_AMP_A | 南科道爺ㄧ路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 104 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D05 | 道爺DS | 161 | 161kV | 1520_AMP | 南科道爺二路 | [27 empty] | ADCS_S | [8 empty] | 道爺DS.1520_AMP_A | 南科道爺二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 105 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D05 | 道爺DS | 0 |  | 注意OLTC | 注意OLTC |  | BUS電壓異常 | [25 empty] | ADCS_S | [8 empty] | 道爺DS.BUS電壓異常 | 注意OLTC Tap位置,並將RPDC閉鎖 | OTHER |  |  | STATION_FAULT_2 |  |  | 106 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1BUS | #1BUS |  | V | [14 empty] | 0002 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | D05/161/1BUS/V |  |  |  | DNP | 107 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D05 | 道爺DS | 161 | 161kV | 2BUS | #2BUS |  | V | [14 empty] | 0003 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | D05/161/2BUS/V |  |  |  | DNP | 108 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D05 | 道爺DS | 161 | 161kV | 3BUS | #3BUS |  | V | [14 empty] | 0004 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.161KV#3BUS_KV | 161KV #3BUS KV | BUS | D05/161/3BUS/V |  |  |  | DNP | 109 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D05 | 道爺DS | 161 | 161kV | 4BUS | #4BUS |  | V | [14 empty] | 0005 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.161KV#4BUS_KV | 161KV #4BUS KV | BUS | D05/161/4BUS/V |  |  |  | DNP | 110 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D05 | 道爺DS | 22 | 22kV | 2ABUS | #2ABUS |  | V | [14 empty] | 0108 | [8 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.23KV#2ABUS_KV | 23KV #2ABUS KV | BUS | D05/22/2ABUS/V |  |  |  | DNP | 111 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D05 | 道爺DS | 22 | 22kV | 2BBUS | #2BBUS |  | V | [14 empty] | 0136 | [8 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.23KV#2BBUS_KV | 23KV #2BBUS KV | BUS | D05/22/2BBUS/V |  |  |  | DNP | 112 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D05 | 道爺DS | 22 | 22kV | 3ABUS | #3ABUS |  | V | [14 empty] | 0165 | [8 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.23KV#3ABUS_KV | 23KV #3ABUS KV | BUS | D05/22/3ABUS/V |  |  |  | DNP | 113 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D05 | 道爺DS | 22 | 22kV | 3BBUS | #3BBUS |  | V | [14 empty] | 0191 | [8 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.23KV#3BBUS_KV | 23KV #3BBUS KV | BUS | D05/22/3BBUS/V |  |  |  | DNP | 114 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D05 | 道爺DS | 161 | 161kV | 1530 | 南科道爺三路(1530) |  | MW | [14 empty] | 0010 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.1530_MW | 南科道爺三路 MW | LINE161 | D05/161/1530/MW |  |  |  | DNP | 115 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1530 | 南科道爺三路(1530) |  | MVAR | [14 empty] | 0011 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.1530_MVAR | 南科道爺三路 MVAR | LINE161 | D05/161/1530/MVAR |  |  |  | DNP | 116 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1530LPD | 南科道爺三路(1530) |  | V | [14 empty] | 0221 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.1530LPD_KV | 南科道爺三路(1530) LPD KV | LINE161 | D05/161/1530/V |  |  |  | DNP | 117 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D05 | 道爺DS | 161 | 161kV | 1540 | 南科道爺四路(1540) |  | MW | [14 empty] | 0012 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.1540_MW | 南科道爺四路 MW | LINE161 | D05/161/1540/MW |  |  |  | DNP | 118 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1540 | 南科道爺四路(1540) |  | MVAR | [14 empty] | 0013 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.1540_MVAR | 南科道爺四路 MVAR | LINE161 | D05/161/1540/MVAR |  |  |  | DNP | 119 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1540LPD | 南科道爺四路(1540) |  | V | [14 empty] | 0222 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.1540LPD_KV | 南科道爺四路(1540) LPD KV | LINE161 | D05/161/1540/V |  |  |  | DNP | 120 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺奇晶七紅線(1550) |  | MW | [14 empty] | 0014 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.1550_MW | 道爺奇晶七紅線 MW | LINE161 | D05/161/1550/MW |  |  |  | DNP | 121 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺奇晶七紅線(1550) |  | MVAR | [14 empty] | 0015 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.1550_MVAR | 道爺奇晶七紅線 MVAR | LINE161 | D05/161/1550/MVAR |  |  |  | DNP | 122 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1550LPD | 道爺奇晶七紅線(1550) |  | V | [14 empty] | 0223 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.1550LPD_KV | 道爺奇晶七紅線(1550) LPD KV | LINE161 | D05/161/1550/V |  |  |  | DNP | 123 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺奇晶七白線(1560) |  | MW | [14 empty] | 0016 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.1560_MW | 道爺奇晶七白線 MW | LINE161 | D05/161/1560/MW |  |  |  | DNP | 124 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺奇晶七白線(1560) |  | MVAR | [14 empty] | 0017 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.1560_MVAR | 道爺奇晶七白線 MVAR | LINE161 | D05/161/1560/MVAR |  |  |  | DNP | 125 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1560LPD | 道爺奇晶七白線(1560) |  | V | [14 empty] | 0224 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.1560LPD_KV | 道爺奇晶七白線(1560) LPD KV | LINE161 | D05/161/1560/V |  |  |  | DNP | 126 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺奇晶六紅線(1570) |  | MW | [14 empty] | 0018 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.1570_MW | 道爺奇晶六紅線 MW | LINE161 | D05/161/1570/MW |  |  |  | DNP | 127 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺奇晶六紅線(1570) |  | MVAR | [14 empty] | 0019 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.1570_MVAR | 道爺奇晶六紅線 MVAR | LINE161 | D05/161/1570/MVAR |  |  |  | DNP | 128 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1570LPD | 道爺奇晶六紅線(1570) |  | V | [14 empty] | 0225 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.1570LPD_KV | 道爺奇晶六紅線(1570) LPD KV | LINE161 | D05/161/1570/V |  |  |  | DNP | 129 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺奇晶六白線(1580) |  | MW | [14 empty] | 0020 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.1580_MW | 道爺奇晶六白線 MW | LINE161 | D05/161/1580/MW |  |  |  | DNP | 130 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺奇晶六白線(1580) |  | MVAR | [14 empty] | 0021 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.1580_MVAR | 道爺奇晶六白線 MVAR | LINE161 | D05/161/1580/MVAR |  |  |  | DNP | 131 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1580LPD | 道爺奇晶六白線(1580) |  | V | [14 empty] | 0226 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.1580LPD_KV | 道爺奇晶六白線(1580) LPD KV | LINE161 | D05/161/1580/V |  |  |  | DNP | 132 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D05 | 道爺DS | 161 | 161kV | 1610 | 道爺安南新化線(1610) |  | MW | [14 empty] | 0022 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.1610_MW | 道爺安南新化線 MW | LINE161 | D05/161/1610/MW |  |  |  | DNP | 133 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1610 | 道爺安南新化線(1610) |  | MVAR | [14 empty] | 0023 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.1610_MVAR | 道爺安南新化線 MVAR | LINE161 | D05/161/1610/MVAR |  |  |  | DNP | 134 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1610LPD | 道爺安南新化線(1610) |  | V | [14 empty] | 0227 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.1610LPD_KV | 道爺安南新化線(1610) LPD KV | LINE161 | D05/161/1610/V |  |  |  | DNP | 135 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D05 | 道爺DS | 161 | 161kV | 1620 | 道爺和順新化線(1620) |  | MW | [14 empty] | 0024 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.1620_MW | 道爺和順新化線 MW | LINE161 | D05/161/1620/MW |  |  |  | DNP | 136 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1620 | 道爺和順新化線(1620) |  | MVAR | [14 empty] | 0025 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.1620_MVAR | 道爺和順新化線 MVAR | LINE161 | D05/161/1620/MVAR |  |  |  | DNP | 137 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1620LPD | 道爺和順新化線(1620) |  | V | [14 empty] | 0228 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.1620LPD_KV | 道爺和順新化線(1620) LPD KV | LINE161 | D05/161/1620/V |  |  |  | DNP | 138 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D05 | 道爺DS | 22 | 22kV | 爺61線 | 爺61線 |  | 爺61線KVAR | [14 empty] | 0114 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺61線KVAR | 23KV爺61線 KVAR | FEEDER | D05/22/4K61/KVAR |  |  |  | DNP | 139 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺61線 | 爺61線 |  | 爺61線A1 | [14 empty] | 0115 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺61線A1 | 23KV爺61線 R相AMP | FEEDER | D05/22/4K61/I_R |  |  |  | DNP | 140 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺61線 | 爺61線 |  | 爺61線A2 | [14 empty] | 0116 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺61線A2 | 23KV爺61線 S相AMP | FEEDER | D05/22/4K61/I_S |  |  |  | DNP | 141 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺61線 | 爺61線 |  | 爺61線A3 | [14 empty] | 0117 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺61線A3 | 23KV爺61線 T相AMP | FEEDER | D05/22/4K61/I_T |  |  |  | DNP | 142 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺61線 | 爺61線 |  | 爺61線A0 | [14 empty] | 0118 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺61線A0 | 23KV爺61線 N相AMP | FEEDER | D05/22/4K61/I_N |  |  |  | DNP | 143 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺62線 | 爺62線 |  | 爺62線KVAR | [14 empty] | 0119 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺62線KVAR | 23KV爺62線 KVAR | FEEDER | D05/22/4K62/KVAR |  |  |  | DNP | 144 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺62線 | 爺62線 |  | 爺62線A1 | [14 empty] | 0120 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺62線A1 | 23KV爺62線 R相AMP | FEEDER | D05/22/4K62/I_R |  |  |  | DNP | 145 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺62線 | 爺62線 |  | 爺62線A2 | [14 empty] | 0121 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺62線A2 | 23KV爺62線 S相AMP | FEEDER | D05/22/4K62/I_S |  |  |  | DNP | 146 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺62線 | 爺62線 |  | 爺62線A3 | [14 empty] | 0122 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺62線A3 | 23KV爺62線 T相AMP | FEEDER | D05/22/4K62/I_T |  |  |  | DNP | 147 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺62線 | 爺62線 |  | 爺62線A0 | [14 empty] | 0123 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺62線A0 | 23KV爺62線 N相AMP | FEEDER | D05/22/4K62/I_N |  |  |  | DNP | 148 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺63線 | 爺63線 |  | 爺63線KVAR | [14 empty] | 0124 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺63線KVAR | 23KV爺63線 KVAR | FEEDER | D05/22/4K63/KVAR |  |  |  | DNP | 149 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺63線 | 爺63線 |  | 爺63線A1 | [14 empty] | 0125 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺63線A1 | 23KV爺63線 R相AMP | FEEDER | D05/22/4K63/I_R |  |  |  | DNP | 150 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺63線 | 爺63線 |  | 爺63線A2 | [14 empty] | 0126 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺63線A2 | 23KV爺63線 S相AMP | FEEDER | D05/22/4K63/I_S |  |  |  | DNP | 151 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺63線 | 爺63線 |  | 爺63線A3 | [14 empty] | 0127 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺63線A3 | 23KV爺63線 T相AMP | FEEDER | D05/22/4K63/I_T |  |  |  | DNP | 152 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺63線 | 爺63線 |  | 爺63線A0 | [14 empty] | 0130 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺63線A0 | 23KV爺63線 N相AMP | FEEDER | D05/22/4K63/I_N |  |  |  | DNP | 153 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺64線 | 爺64線 |  | 爺64線KVAR | [14 empty] | 0131 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺64線KVAR | 23KV爺64線 KVAR | FEEDER | D05/22/4K64/KVAR |  |  |  | DNP | 154 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺64線 | 爺64線 |  | 爺64線A1 | [14 empty] | 0132 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺64線A1 | 23KV爺64線 R相AMP | FEEDER | D05/22/4K64/I_R |  |  |  | DNP | 155 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺64線 | 爺64線 |  | 爺64線A2 | [14 empty] | 0133 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺64線A2 | 23KV爺64線 S相AMP | FEEDER | D05/22/4K64/I_S |  |  |  | DNP | 156 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺64線 | 爺64線 |  | 爺64線A3 | [14 empty] | 0134 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺64線A3 | 23KV爺64線 T相AMP | FEEDER | D05/22/4K64/I_T |  |  |  | DNP | 157 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺64線 | 爺64線 |  | 爺64線A0 | [14 empty] | 0135 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺64線A0 | 23KV爺64線 N相AMP | FEEDER | D05/22/4K64/I_N |  |  |  | DNP | 158 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺65線 | 爺65線 |  | 爺65線KVAR | [14 empty] | 0142 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺65線KVAR | 23KV爺65線 KVAR | FEEDER | D05/22/4K65/KVAR |  |  |  | DNP | 159 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺65線 | 爺65線 |  | 爺65線A1 | [14 empty] | 0143 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺65線A1 | 23KV爺65線 R相AMP | FEEDER | D05/22/4K65/I_R |  |  |  | DNP | 160 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺65線 | 爺65線 |  | 爺65線A2 | [14 empty] | 0144 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺65線A2 | 23KV爺65線 S相AMP | FEEDER | D05/22/4K65/I_S |  |  |  | DNP | 161 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺65線 | 爺65線 |  | 爺65線A3 | [14 empty] | 0145 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺65線A3 | 23KV爺65線 T相AMP | FEEDER | D05/22/4K65/I_T |  |  |  | DNP | 162 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺65線 | 爺65線 |  | 爺65線A0 | [14 empty] | 0146 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺65線A0 | 23KV爺65線 N相AMP | FEEDER | D05/22/4K65/I_N |  |  |  | DNP | 163 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺66線 | 爺66線 |  | 爺66線KVAR | [14 empty] | 0147 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺66線KVAR | 23KV爺66線 KVAR | FEEDER | D05/22/4K66/KVAR |  |  |  | DNP | 164 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺66線 | 爺66線 |  | 爺66線A1 | [14 empty] | 0148 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺66線A1 | 23KV爺66線 R相AMP | FEEDER | D05/22/4K66/I_R |  |  |  | DNP | 165 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺66線 | 爺66線 |  | 爺66線A2 | [14 empty] | 0149 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺66線A2 | 23KV爺66線 S相AMP | FEEDER | D05/22/4K66/I_S |  |  |  | DNP | 166 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺66線 | 爺66線 |  | 爺66線A3 | [14 empty] | 0150 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺66線A3 | 23KV爺66線 T相AMP | FEEDER | D05/22/4K66/I_T |  |  |  | DNP | 167 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺66線 | 爺66線 |  | 爺66線A0 | [14 empty] | 0151 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺66線A0 | 23KV爺66線 N相AMP | FEEDER | D05/22/4K66/I_N |  |  |  | DNP | 168 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺67線 | 爺67線 |  | 爺67線KVAR | [14 empty] | 0152 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺67線KVAR | 23KV爺67線 KVAR | FEEDER | D05/22/4K67/KVAR |  |  |  | DNP | 169 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺67線 | 爺67線 |  | 爺67線A1 | [14 empty] | 0153 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺67線A1 | 23KV爺67線 R相AMP | FEEDER | D05/22/4K67/I_R |  |  |  | DNP | 170 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺67線 | 爺67線 |  | 爺67線A2 | [14 empty] | 0154 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺67線A2 | 23KV爺67線 S相AMP | FEEDER | D05/22/4K67/I_S |  |  |  | DNP | 171 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺67線 | 爺67線 |  | 爺67線A3 | [14 empty] | 0155 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺67線A3 | 23KV爺67線 T相AMP | FEEDER | D05/22/4K67/I_T |  |  |  | DNP | 172 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺67線 | 爺67線 |  | 爺67線A0 | [14 empty] | 0156 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺67線A0 | 23KV爺67線 N相AMP | FEEDER | D05/22/4K67/I_N |  |  |  | DNP | 173 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺68線 | 爺68線 |  | 爺68線KVAR | [14 empty] | 0157 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺68線KVAR | 23KV爺68線 KVAR | FEEDER | D05/22/4K68/KVAR |  |  |  | DNP | 174 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺68線 | 爺68線 |  | 爺68線A1 | [14 empty] | 0158 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺68線A1 | 23KV爺68線 R相AMP | FEEDER | D05/22/4K68/I_R |  |  |  | DNP | 175 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺68線 | 爺68線 |  | 爺68線A2 | [14 empty] | 0159 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺68線A2 | 23KV爺68線 S相AMP | FEEDER | D05/22/4K68/I_S |  |  |  | DNP | 176 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺68線 | 爺68線 |  | 爺68線A3 | [14 empty] | 0160 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺68線A3 | 23KV爺68線 T相AMP | FEEDER | D05/22/4K68/I_T |  |  |  | DNP | 177 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺68線 | 爺68線 |  | 爺68線A0 | [14 empty] | 0161 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺68線A0 | 23KV爺68線 N相AMP | FEEDER | D05/22/4K68/I_N |  |  |  | DNP | 178 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺71線 | 爺71線 |  | 爺71線KVAR | [14 empty] | 0171 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺71線KVAR | 23KV爺71線 KVAR | FEEDER | D05/22/4K71/KVAR |  |  |  | DNP | 179 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺71線 | 爺71線 |  | 爺71線A1 | [14 empty] | 0172 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺71線A1 | 23KV爺71線 R相AMP | FEEDER | D05/22/4K71/I_R |  |  |  | DNP | 180 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺71線 | 爺71線 |  | 爺71線A2 | [14 empty] | 0173 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺71線A2 | 23KV爺71線 S相AMP | FEEDER | D05/22/4K71/I_S |  |  |  | DNP | 181 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺71線 | 爺71線 |  | 爺71線A3 | [14 empty] | 0174 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺71線A3 | 23KV爺71線 T相AMP | FEEDER | D05/22/4K71/I_T |  |  |  | DNP | 182 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺71線 | 爺71線 |  | 爺71線A0 | [14 empty] | 0175 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺71線A0 | 23KV爺71線 N相AMP | FEEDER | D05/22/4K71/I_N |  |  |  | DNP | 183 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺72線 | 爺72線 |  | 爺72線KVAR | [14 empty] | 0176 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺72線KVAR | 23KV爺72線 KVAR | FEEDER | D05/22/4K72/KVAR |  |  |  | DNP | 184 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺72線 | 爺72線 |  | 爺72線A1 | [14 empty] | 0177 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺72線A1 | 23KV爺72線 R相AMP | FEEDER | D05/22/4K72/I_R |  |  |  | DNP | 185 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺72線 | 爺72線 |  | 爺72線A2 | [14 empty] | 0178 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺72線A2 | 23KV爺72線 S相AMP | FEEDER | D05/22/4K72/I_S |  |  |  | DNP | 186 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺72線 | 爺72線 |  | 爺72線A3 | [14 empty] | 0179 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺72線A3 | 23KV爺72線 T相AMP | FEEDER | D05/22/4K72/I_T |  |  |  | DNP | 187 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺72線 | 爺72線 |  | 爺72線A0 | [14 empty] | 0180 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺72線A0 | 23KV爺72線 N相AMP | FEEDER | D05/22/4K72/I_N |  |  |  | DNP | 188 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺73線 | 爺73線 |  | 爺73線KVAR | [14 empty] | 0181 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺73線KVAR | 23KV爺73線 KVAR | FEEDER | D05/22/4K73/KVAR |  |  |  | DNP | 189 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺73線 | 爺73線 |  | 爺73線A1 | [14 empty] | 0182 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺73線A1 | 23KV爺73線 R相AMP | FEEDER | D05/22/4K73/I_R |  |  |  | DNP | 190 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺73線 | 爺73線 |  | 爺73線A2 | [14 empty] | 0183 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺73線A2 | 23KV爺73線 S相AMP | FEEDER | D05/22/4K73/I_S |  |  |  | DNP | 191 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺73線 | 爺73線 |  | 爺73線A3 | [14 empty] | 0184 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺73線A3 | 23KV爺73線 T相AMP | FEEDER | D05/22/4K73/I_T |  |  |  | DNP | 192 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺73線 | 爺73線 |  | 爺73線A0 | [14 empty] | 0185 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺73線A0 | 23KV爺73線 N相AMP | FEEDER | D05/22/4K73/I_N |  |  |  | DNP | 193 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺74線 | 爺74線 |  | 爺74線KVAR | [14 empty] | 0186 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺74線KVAR | 23KV爺74線 KVAR | FEEDER | D05/22/4K74/KVAR |  |  |  | DNP | 194 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺74線 | 爺74線 |  | 爺74線A1 | [14 empty] | 0187 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺74線A1 | 23KV爺74線 R相AMP | FEEDER | D05/22/4K74/I_R |  |  |  | DNP | 195 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺74線 | 爺74線 |  | 爺74線A2 | [14 empty] | 0188 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺74線A2 | 23KV爺74線 S相AMP | FEEDER | D05/22/4K74/I_S |  |  |  | DNP | 196 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺74線 | 爺74線 |  | 爺74線A3 | [14 empty] | 0189 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺74線A3 | 23KV爺74線 T相AMP | FEEDER | D05/22/4K74/I_T |  |  |  | DNP | 197 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺74線 | 爺74線 |  | 爺74線A0 | [14 empty] | 0190 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺74線A0 | 23KV爺74線 N相AMP | FEEDER | D05/22/4K74/I_N |  |  |  | DNP | 198 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺75線 | 爺75線 |  | 爺75線KVAR | [14 empty] | 0199 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺75線KVAR | 23KV爺75線 KVAR | FEEDER | D05/22/4K75/KVAR |  |  |  | DNP | 199 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺75線 | 爺75線 |  | 爺75線A1 | [14 empty] | 0200 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺75線A1 | 23KV爺75線 R相AMP | FEEDER | D05/22/4K75/I_R |  |  |  | DNP | 200 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺75線 | 爺75線 |  | 爺75線A2 | [14 empty] | 0201 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺75線A2 | 23KV爺75線 S相AMP | FEEDER | D05/22/4K75/I_S |  |  |  | DNP | 201 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺75線 | 爺75線 |  | 爺75線A3 | [14 empty] | 0202 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺75線A3 | 23KV爺75線 T相AMP | FEEDER | D05/22/4K75/I_T |  |  |  | DNP | 202 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺75線 | 爺75線 |  | 爺75線A0 | [14 empty] | 0203 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺75線A0 | 23KV爺75線 N相AMP | FEEDER | D05/22/4K75/I_N |  |  |  | DNP | 203 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺76線 | 爺76線 |  | 爺76線KVAR | [14 empty] | 0204 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺76線KVAR | 23KV爺76線 KVAR | FEEDER | D05/22/4K76/KVAR |  |  |  | DNP | 204 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺76線 | 爺76線 |  | 爺76線A1 | [14 empty] | 0205 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺76線A1 | 23KV爺76線 R相AMP | FEEDER | D05/22/4K76/I_R |  |  |  | DNP | 205 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺76線 | 爺76線 |  | 爺76線A2 | [14 empty] | 0206 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺76線A2 | 23KV爺76線 S相AMP | FEEDER | D05/22/4K76/I_S |  |  |  | DNP | 206 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺76線 | 爺76線 |  | 爺76線A3 | [14 empty] | 0207 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺76線A3 | 23KV爺76線 T相AMP | FEEDER | D05/22/4K76/I_T |  |  |  | DNP | 207 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺76線 | 爺76線 |  | 爺76線A0 | [14 empty] | 0208 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺76線A0 | 23KV爺76線 N相AMP | FEEDER | D05/22/4K76/I_N |  |  |  | DNP | 208 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺77線 | 爺77線 |  | 爺77線KVAR | [14 empty] | 0209 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺77線KVAR | 23KV爺77線 KVAR | FEEDER | D05/22/4K77/KVAR |  |  |  | DNP | 209 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺77線 | 爺77線 |  | 爺77線A1 | [14 empty] | 0210 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺77線A1 | 23KV爺77線 R相AMP | FEEDER | D05/22/4K77/I_R |  |  |  | DNP | 210 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺77線 | 爺77線 |  | 爺77線A2 | [14 empty] | 0211 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺77線A2 | 23KV爺77線 S相AMP | FEEDER | D05/22/4K77/I_S |  |  |  | DNP | 211 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺77線 | 爺77線 |  | 爺77線A3 | [14 empty] | 0212 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺77線A3 | 23KV爺77線 T相AMP | FEEDER | D05/22/4K77/I_T |  |  |  | DNP | 212 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺77線 | 爺77線 |  | 爺77線A0 | [14 empty] | 0213 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺77線A0 | 23KV爺77線 N相AMP | FEEDER | D05/22/4K77/I_N |  |  |  | DNP | 213 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺78線 | 爺78線 |  | 爺78線KVAR | [14 empty] | 0214 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺78線KVAR | 23KV爺78線 KVAR | FEEDER | D05/22/4K78/KVAR |  |  |  | DNP | 214 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺78線 | 爺78線 |  | 爺78線A1 | [14 empty] | 0215 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺78線A1 | 23KV爺78線 R相AMP | FEEDER | D05/22/4K78/I_R |  |  |  | DNP | 215 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺78線 | 爺78線 |  | 爺78線A2 | [14 empty] | 0216 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺78線A2 | 23KV爺78線 S相AMP | FEEDER | D05/22/4K78/I_S |  |  |  | DNP | 216 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺78線 | 爺78線 |  | 爺78線A3 | [14 empty] | 0217 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺78線A3 | 23KV爺78線 T相AMP | FEEDER | D05/22/4K78/I_T |  |  |  | DNP | 217 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 爺78線 | 爺78線 |  | 爺78線A0 | [14 empty] | 0218 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.爺78線A0 | 23KV爺78線 N相AMP | FEEDER | D05/22/4K78/I_N |  |  |  | DNP | 218 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 0 |  | 1500TIE | 1500TIE |  | I | [14 empty] | 0026 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.1500TIE_AMP | 1500TIE AMP | TIE | D05/161/1500/I_R |  |  |  | DNP | 219 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 0 |  | 1600TIE | 1600TIE |  | I | [14 empty] | 0027 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.1600TIE_AMP | 1600TIE AMP | TIE | D05/161/1600/I_R |  |  |  | DNP | 220 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 0 |  | 1700TIE | 1700TIE |  | I | [14 empty] | 0028 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.1700TIE_AMP | 1700TIE AMP | TIE | D05/161/1700/I_R |  |  |  | DNP | 221 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 0 |  | 1800TIE | 1800TIE |  | I | [14 empty] | 0029 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.1800TIE_AMP | 1800TIE AMP | TIE | D05/161/1800/I_R |  |  |  | DNP | 222 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | _200 | 200 |  | I_R | [14 empty] | 0105 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.23KV_200_A1 | 23KV 200 R相AMP | TIE | D05/22/200/I_R |  |  |  | DNP | 223 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | _200 | 200 |  | I_S | [14 empty] | 0106 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.23KV_200_A2 | 23KV 200 S相AMP | TIE | D05/22/200/I_S |  |  |  | DNP | 224 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | _200 | 200 |  | I_T | [14 empty] | 0107 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.23KV_200_A3 | 23KV 200 T相AMP | TIE | D05/22/200/I_T |  |  |  | DNP | 225 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | _300 | 300 |  | I_R | [14 empty] | 0162 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.23KV_300_A1 | 23KV 300 R相AMP | TIE | D05/22/300/I_R |  |  |  | DNP | 226 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | _300 | 300 |  | I_S | [14 empty] | 0163 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.23KV_300_A2 | 23KV 300 S相AMP | TIE | D05/22/300/I_S |  |  |  | DNP | 227 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | _300 | 300 |  | I_T | [14 empty] | 0164 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.23KV_300_A3 | 23KV 300 T相AMP | TIE | D05/22/300/I_T |  |  |  | DNP | 228 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 0 |  | 2DTR | #2DTR |  | OilTemp | [14 empty] | 0040 | [8 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.#2DTR_OIL | #2DTR 油溫 | MTR | D05//2DTR/OilTemp |  |  |  | DNP | 229 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D05 | 道爺DS | 0 |  | 2DTR | #2DTR |  | CoilTemp | [14 empty] | 0041 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.#2DTR_COIL | #2DTR 線溫 | MTR | D05//2DTR/CoilTemp |  |  |  | DNP | 230 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D05 | 道爺DS | 0 |  | 2DTR | #2DTR |  | TapPosMv | [14 empty] | 0039 |  | 0102 | [6 empty] | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 道爺DS.#2DTR_TAP | #2DTR OLTC TAP | MTR | D05//2DTR/TapPosMv |  |  |  | DNP | 231 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D05 | 道爺DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MW | [14 empty] | 0109 | [8 empty] | MW_-108_108(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | D05/22/330/KW |  |  |  | DNP | 232 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D05 | 道爺DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVAR | [14 empty] | 0110 | [8 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | D05/22/330/KVAR |  |  |  | DNP | 233 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D05 | 道爺DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_R | [14 empty] | 0111 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | D05/22/330/I_R |  |  |  | DNP | 234 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_S | [14 empty] | 0112 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | D05/22/330/I_S |  |  |  | DNP | 235 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_T | [14 empty] | 0113 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | D05/22/330/I_T |  |  |  | DNP | 236 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MW | [14 empty] | 0137 | [8 empty] | MW_-108_108(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | D05/22/340/KW |  |  |  | DNP | 237 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D05 | 道爺DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVAR | [14 empty] | 0138 | [8 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | D05/22/340/KVAR |  |  |  | DNP | 238 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D05 | 道爺DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_R | [14 empty] | 0139 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | D05/22/340/I_R |  |  |  | DNP | 239 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_S | [14 empty] | 0140 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | D05/22/340/I_S |  |  |  | DNP | 240 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_T | [14 empty] | 0141 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | D05/22/340/I_T |  |  |  | DNP | 241 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 0 |  | 3DTR | #3DTR |  | OilTemp | [14 empty] | 0043 | [8 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.#3DTR_OIL | #3DTR 油溫 | MTR | D05//3DTR/OilTemp |  |  |  | DNP | 242 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D05 | 道爺DS | 0 |  | 3DTR | #3DTR |  | CoilTemp | [14 empty] | 0044 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.#3DTR_COIL | #3DTR 線溫 | MTR | D05//3DTR/CoilTemp |  |  |  | DNP | 243 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D05 | 道爺DS | 0 |  | 3DTR | #3DTR |  | TapPosMv | [14 empty] | 0042 |  | 0104 | [6 empty] | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 道爺DS.#3DTR_TAP | #3DTR OLTC TAP | MTR | D05//3DTR/TapPosMv |  |  |  | DNP | 244 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D05 | 道爺DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | MW | [14 empty] | 0166 | [8 empty] | MW_-108_108(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.#3DTR(A)_MW | #3DTR二次側(A) MW | MTR | D05/22/350/KW |  |  |  | DNP | 245 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D05 | 道爺DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | MVAR | [14 empty] | 0167 | [8 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.#3DTR(A)_MVAR | #3DTR二次側(A) MVAR | MTR | D05/22/350/KVAR |  |  |  | DNP | 246 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D05 | 道爺DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | I_R | [14 empty] | 0168 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.#3DTR(A)_A1 | #3DTR二次側(A) R相AMP | MTR | D05/22/350/I_R |  |  |  | DNP | 247 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | I_S | [14 empty] | 0169 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.#3DTR(A)_A2 | #3DTR二次側(A) S相AMP | MTR | D05/22/350/I_S |  |  |  | DNP | 248 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | I_T | [14 empty] | 0170 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.#3DTR(A)_A3 | #3DTR二次側(A) T相AMP | MTR | D05/22/350/I_T |  |  |  | DNP | 249 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | MW | [14 empty] | 0194 | [8 empty] | MW_-108_108(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.#3DTR(B)_MW | #3DTR二次側(B) MW | MTR | D05/22/360/KW |  |  |  | DNP | 250 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D05 | 道爺DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | MVAR | [14 empty] | 0195 | [8 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.#3DTR(B)_MVAR | #3DTR二次側(B) MVAR | MTR | D05/22/360/KVAR |  |  |  | DNP | 251 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D05 | 道爺DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | I_R | [14 empty] | 0196 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.#3DTR(B)_A1 | #3DTR二次側(B) R相AMP | MTR | D05/22/360/I_R |  |  |  | DNP | 252 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | I_S | [14 empty] | 0197 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.#3DTR(B)_A2 | #3DTR二次側(B) S相AMP | MTR | D05/22/360/I_S |  |  |  | DNP | 253 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | I_T | [14 empty] | 0198 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.#3DTR(B)_A3 | #3DTR二次側(B) T相AMP | MTR | D05/22/360/I_T |  |  |  | DNP | 254 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 0 |  |  |  |  | DCV_N | [14 empty] | 0035 | [8 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.直流N電源電壓 | 直流N電源電壓 | OTHER | D05/0/StaDev/DCV_N |  |  |  | DNP | 255 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D05 | 道爺DS | 0 |  |  |  |  | DCV_P | [14 empty] | 0034 | [8 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.直流P電源電壓 | 直流P電源電壓 | OTHER | D05/0/StaDev/DCV_P |  |  |  | DNP | 256 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1510 | 南科道爺ㄧ路(1510) |  | MW | [14 empty] | 0006 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.1510_MW | 南科道爺ㄧ路 MW | LINE161 | D05/161/1510/MW |  |  |  | DNP | 257 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1510 | 南科道爺ㄧ路(1510) |  | MVAR | [14 empty] | 0007 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.1510_MVAR | 南科道爺ㄧ路 MVAR | LINE161 | D05/161/1510/MVAR |  |  |  | DNP | 258 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1510LPD | 南科道爺ㄧ路(1510) |  | V | [14 empty] | 0219 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.1510LPD_KV | 南科道爺ㄧ路(1510) LPD KV | LINE161 | D05/161/1510/V |  |  |  | DNP | 259 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D05 | 道爺DS | 161 | 161kV | 1520 | 南科道爺二路(1520) |  | MW | [14 empty] | 0008 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.1520_MW | 南科道爺二路 MW | LINE161 | D05/161/1520/MW |  |  |  | DNP | 260 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1520 | 南科道爺二路(1520) |  | MVAR | [14 empty] | 0009 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.1520_MVAR | 南科道爺二路 MVAR | LINE161 | D05/161/1520/MVAR |  |  |  | DNP | 261 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1520LPD | 南科道爺二路(1520) |  | V | [14 empty] | 0220 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 道爺DS.1520LPD_KV | 南科道爺二路(1520) LPD KV | LINE161 | D05/161/1520/V |  |  |  | DNP | 262 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D05 | 道爺DS | 22 | 22kV | 奇菱線 | 奇菱線 |  | 奇菱線KVAR | [14 empty] | 0301 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.奇菱線KVAR | 23KV奇菱線 KVAR | FEEDER |  |  |  |  | DNP | 263 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 奇菱線 | 奇菱線 |  | 奇菱線A1 | [14 empty] | 0302 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.奇菱線A1 | 23KV奇菱線 R相AMP | FEEDER |  |  |  |  | DNP | 264 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 奇菱線 | 奇菱線 |  | 奇菱線A2 | [14 empty] | 0303 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.奇菱線A2 | 23KV奇菱線 S相AMP | FEEDER |  |  |  |  | DNP | 265 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 奇菱線 | 奇菱線 |  | 奇菱線A3 | [14 empty] | 0304 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.奇菱線A3 | 23KV奇菱線 T相AMP | FEEDER |  |  |  |  | DNP | 266 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 奇菱線 | 奇菱線 |  | 奇菱線A0 | [14 empty] | 0305 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.奇菱線A0 | 23KV奇菱線 N相AMP | FEEDER |  |  |  |  | DNP | 267 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 奇菱線_KV | 奇菱線 |  | R | [14 empty] | 0306 | [8 empty] | kV_-18_18(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.奇菱線_KV_R | 23KV奇菱線 KV_R | OTHER |  |  |  |  | DNP | 268 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D05 | 道爺DS | 22 | 22kV | 奇菱線_KV | 奇菱線 |  | S | [14 empty] | 0307 | [8 empty] | kV_-18_18(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.奇菱線_KV_S | 23KV奇菱線 KV_S | OTHER |  |  |  |  | DNP | 269 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D05 | 道爺DS | 22 | 22kV | 奇菱線_KV | 奇菱線 |  | T | [14 empty] | 0308 | [8 empty] | kV_-18_18(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.奇菱線_KV_T | 23KV奇菱線 KV_T | OTHER |  |  |  |  | DNP | 270 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D05 | 道爺DS | 22 | 22kV | 奇菱線 | 奇菱線 |  | KW | [14 empty] | 0300 | [8 empty] | KW_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.奇菱線_KW | 23KV奇菱線 KW | OTHER |  |  |  |  | DNP | 271 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 2.700000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 崇越和鑫(4K67) | 崇越和鑫(4K67) |  | PV崇越和鑫KVAR | [14 empty] | 0310 | [8 empty] | KVAR_-7200_7200(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.PV崇越和鑫KVAR | 23KV崇越和鑫(4K67) KVAR | FEEDER |  |  |  |  | DNP | 272 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 7.200000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 崇越和鑫(4K67) | 崇越和鑫(4K67) |  | PV崇越和鑫A1 | [14 empty] | 0311 | [8 empty] | A_-200_200(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.PV崇越和鑫A1 | 23KV崇越和鑫(4K67) R相AMP | FEEDER |  |  |  |  | DNP | 273 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 崇越和鑫(4K67) | 崇越和鑫(4K67) |  | PV崇越和鑫A2 | [14 empty] | 0312 | [8 empty] | A_-200_200(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.PV崇越和鑫A2 | 23KV崇越和鑫(4K67) S相AMP | FEEDER |  |  |  |  | DNP | 274 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 崇越和鑫(4K67) | 崇越和鑫(4K67) |  | 崇越和鑫A3 | [14 empty] | 0313 | [8 empty] | A_-200_200(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.崇越和鑫A3 | 23KV崇越和鑫(4K67) T相AMP | FEEDER |  |  |  |  | DNP | 275 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D05 | 道爺DS | 22 | 22kV | 崇越和鑫 | 崇越和鑫(4K67) |  | KV1 | [14 empty] | 0315 | [8 empty] | kV_-18_18(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.崇越和鑫_KV1 | 23KV崇越和鑫(4K67) R相KV | OTHER |  |  |  |  | DNP | 276 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D05 | 道爺DS | 22 | 22kV | 崇越和鑫 | 崇越和鑫(4K67) |  | KV2 | [14 empty] | 0316 | [8 empty] | kV_-18_18(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.崇越和鑫_KV2 | 23KV崇越和鑫(4K67) S相KV | OTHER |  |  |  |  | DNP | 277 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D05 | 道爺DS | 22 | 22kV | 崇越和鑫 | 崇越和鑫(4K67) |  | KV3 | [14 empty] | 0317 | [8 empty] | kV_-18_18(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.崇越和鑫_KV3 | 23KV崇越和鑫(4K67) T相KV | OTHER |  |  |  |  | DNP | 278 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D05 | 道爺DS | 22 | 22kV | 崇越和鑫 | 崇越和鑫(4K67) |  | KW | [14 empty] | 0309 | [8 empty] | KW_-7200_7200(-2000_2000) |  | DDCS4_1 | [8 empty] | 道爺DS.崇越和鑫_KW | 23KV崇越和鑫(4K67) KW | OTHER |  |  |  |  | DNP | 279 | DNPAIPoint | DS056 |  |  | AI | [17 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 2.700000 | 0.010000
D05 | 道爺DS | 161 | 161kV | 1530 | 南科道爺三路(1530) |  | PHA | [14 empty] | 0013 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1530_PHA | 南科道爺三路(1530) 相間RY | LINE161 | D05/161/1530/PHA |  |  |  | DNP | 280 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1530 | 南科道爺三路(1530) |  | GDA | [14 empty] | 0014 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1530_GDA | 南科道爺三路(1530) 接地RY | LINE161 | D05/161/1530/GDA |  |  |  | DNP | 281 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1530 | 南科道爺三路(1530) |  | 87A | [14 empty] | 0011 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1530_87A | 南科道爺三路(1530) 87RY | LINE161 | D05/161/1530/87A |  |  |  | DNP | 282 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1530 | 南科道爺三路(1530) |  | 87UL | [14 empty] | 0520 |  | 0079 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1530_87UL | 南科道爺三路(1530) 87RY U/L | LINE161 | D05/161/1530/87UL |  |  |  | DNP | 283 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1530 | 南科道爺三路(1530) |  | CB | [14 empty] | 0010 |  | 0003 | [8 empty] | 161KV_S | [8 empty] | 道爺DS.1530_CB | 1530(南科道爺三路) CB | LINE161 | D05/161/1530/CB |  |  |  | DNP | 284 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 161 | 161kV | 1530 | 南科道爺三路(1530) |  | 79UL | [14 empty] | 0522 |  | 0080 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1530_79UL | 南科道爺三路(1530) 79RY U/L | LINE161 | D05/161/1530/79UL |  |  |  | DNP | 285 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1530 | 南科道爺三路(1530) |  | DS1 | 1531 | [13 empty] | 0656 | 657 | 0120 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1531_DS | 1531(南科道爺三路) DS | LINE161 | D05/161/1530/DS1 |  |  |  | DNP | 286 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1530 | 南科道爺三路(1530) |  | DS2 | 1532 | [13 empty] | 0658 | 659 | 0121 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1532_DS | 1532(南科道爺三路) DS | LINE161 | D05/161/1530/DS2 |  |  |  | DNP | 287 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1530 | 南科道爺三路(1530) |  | DS3 | 1533 | [13 empty] | 0660 | 661 | 0122 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1533_DS | 1533(南科道爺三路) DS | LINE161 | D05/161/1530/DS3 |  |  |  | DNP | 288 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1530 | 南科道爺三路(1530) |  | E3 | 1533E | [13 empty] | 0662 | 663 | 0123 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1533E_ES | 1533E(南科道爺三路) ES | LINE161 | D05/161/1530/ES3 |  |  |  | DNP | 289 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1540 | 南科道爺四路(1540) |  | PHA | [14 empty] | 0018 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1540_PHA | 南科道爺四路(1540) 相間RY | LINE161 | D05/161/1540/PHA |  |  |  | DNP | 290 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1540 | 南科道爺四路(1540) |  | GDA | [14 empty] | 0019 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1540_GDA | 南科道爺四路(1540) 接地RY | LINE161 | D05/161/1540/GDA |  |  |  | DNP | 291 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1540 | 南科道爺四路(1540) |  | 87A | [14 empty] | 0016 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1540_87A | 南科道爺四路(1540) 87RY | LINE161 | D05/161/1540/87A |  |  |  | DNP | 292 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1540 | 南科道爺四路(1540) |  | 87UL | [14 empty] | 0523 |  | 0081 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1540_87UL | 南科道爺四路(1540) 87RY U/L | LINE161 | D05/161/1540/87UL |  |  |  | DNP | 293 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1540 | 南科道爺四路(1540) |  | CB | [14 empty] | 0015 |  | 0004 | [8 empty] | 161KV_S | [8 empty] | 道爺DS.1540_CB | 1540(南科道爺四路) CB | LINE161 | D05/161/1540/CB |  |  |  | DNP | 294 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 161 | 161kV | 1540 | 南科道爺四路(1540) |  | 79UL | [14 empty] | 0525 |  | 0082 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1540_79UL | 南科道爺四路(1540) 79RY U/L | LINE161 | D05/161/1540/79UL |  |  |  | DNP | 295 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1540 | 南科道爺四路(1540) |  | DS1 | 1541 | [13 empty] | 0664 | 665 | 0124 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1541_DS | 1541(南科道爺四路) DS | LINE161 | D05/161/1540/DS1 |  |  |  | DNP | 296 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1540 | 南科道爺四路(1540) |  | DS2 | 1542 | [13 empty] | 0666 | 667 | 0125 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1542_DS | 1542(南科道爺四路) DS | LINE161 | D05/161/1540/DS2 |  |  |  | DNP | 297 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1540 | 南科道爺四路(1540) |  | DS3 | 1543 | [13 empty] | 0668 | 669 | 0126 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1543_DS | 1543(南科道爺四路) DS | LINE161 | D05/161/1540/DS3 |  |  |  | DNP | 298 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1540 | 南科道爺四路(1540) |  | E3 | 1543E | [13 empty] | 0670 | 671 | 0127 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1543E_ES | 1543E(南科道爺四路) ES | LINE161 | D05/161/1540/ES3 |  |  |  | DNP | 299 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺奇晶七紅線(1550) |  | PHA | [14 empty] | 0023 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1550_PHA | 道爺奇晶七紅線(1550) 相間RY | LINE161 | D05/161/1550/PHA |  |  |  | DNP | 300 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺奇晶七紅線(1550) |  | GDA | [14 empty] | 0024 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1550_GDA | 道爺奇晶七紅線(1550) 接地RY | LINE161 | D05/161/1550/GDA |  |  |  | DNP | 301 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺奇晶七紅線(1550) |  | CB | [14 empty] | 0020 |  | 0005 | [8 empty] | 161KV_S | [8 empty] | 道爺DS.1550_CB | 1550(道爺奇晶七紅線) CB | LINE161 | D05/161/1550/CB |  |  |  | DNP | 302 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺奇晶七紅線(1550) |  | 79UL | [14 empty] | 0528 |  | 0084 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1550_79UL | 道爺奇晶七紅線(1550) 79RY U/L | LINE161 | D05/161/1550/79UL |  |  |  | DNP | 303 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺奇晶七紅線(1550) |  | DS1 | 1551 | [13 empty] | 0672 | 673 | 0128 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1551_DS | 1551(道爺奇晶七紅線) DS | LINE161 | D05/161/1550/DS1 |  |  |  | DNP | 304 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺奇晶七紅線(1550) |  | DS2 | 1552 | [13 empty] | 0674 | 675 | 0129 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1552_DS | 1552(道爺奇晶七紅線) DS | LINE161 | D05/161/1550/DS2 |  |  |  | DNP | 305 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺奇晶七紅線(1550) |  | DS3 | 1553 | [13 empty] | 0676 | 677 | 0130 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1553_DS | 1553(道爺奇晶七紅線) DS | LINE161 | D05/161/1550/DS3 |  |  |  | DNP | 306 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺奇晶七紅線(1550) |  | E3 | 1553E | [13 empty] | 0678 | 679 | 0131 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1553E_ES | 1553E(道爺奇晶七紅線) ES | LINE161 | D05/161/1550/ES3 |  |  |  | DNP | 307 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺奇晶七白線(1560) |  | PHA | [14 empty] | 0028 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1560_PHA | 道爺奇晶七白線(1560) 相間RY | LINE161 | D05/161/1560/PHA |  |  |  | DNP | 308 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺奇晶七白線(1560) |  | GDA | [14 empty] | 0029 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1560_GDA | 道爺奇晶七白線(1560) 接地RY | LINE161 | D05/161/1560/GDA |  |  |  | DNP | 309 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺奇晶七白線(1560) |  | CB | [14 empty] | 0025 |  | 0006 | [8 empty] | 161KV_S | [8 empty] | 道爺DS.1560_CB | 1560(道爺奇晶七白線) CB | LINE161 | D05/161/1560/CB |  |  |  | DNP | 310 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺奇晶七白線(1560) |  | 79UL | [14 empty] | 0531 |  | 0086 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1560_79UL | 道爺奇晶七白線(1560) 79RY U/L | LINE161 | D05/161/1560/79UL |  |  |  | DNP | 311 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺奇晶七白線(1560) |  | DS1 | 1561 | [13 empty] | 0680 | 681 | 0132 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1561_DS | 1561(道爺奇晶七白線) DS | LINE161 | D05/161/1560/DS1 |  |  |  | DNP | 312 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺奇晶七白線(1560) |  | DS2 | 1562 | [13 empty] | 0682 | 683 | 0133 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1562_DS | 1562(道爺奇晶七白線) DS | LINE161 | D05/161/1560/DS2 |  |  |  | DNP | 313 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺奇晶七白線(1560) |  | DS3 | 1563 | [13 empty] | 0684 | 685 | 0134 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1563_DS | 1563(道爺奇晶七白線) DS | LINE161 | D05/161/1560/DS3 |  |  |  | DNP | 314 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺奇晶七白線(1560) |  | E3 | 1563E | [13 empty] | 0686 | 687 | 0135 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1563E_ES | 1563E(道爺奇晶七白線) ES | LINE161 | D05/161/1560/ES3 |  |  |  | DNP | 315 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺奇晶六紅線(1570) |  | PHA | [14 empty] | 0033 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1570_PHA | 道爺奇晶六紅線(1570) 相間RY | LINE161 | D05/161/1570/PHA |  |  |  | DNP | 316 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺奇晶六紅線(1570) |  | GDA | [14 empty] | 0034 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1570_GDA | 道爺奇晶六紅線(1570) 接地RY | LINE161 | D05/161/1570/GDA |  |  |  | DNP | 317 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺奇晶六紅線(1570) |  | CB | [14 empty] | 0030 |  | 0007 | [8 empty] | 161KV_S | [8 empty] | 道爺DS.1570_CB | 1570(道爺奇晶六紅線) CB | LINE161 | D05/161/1570/CB |  |  |  | DNP | 318 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺奇晶六紅線(1570) |  | 79UL | [14 empty] | 0534 |  | 0088 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1570_79UL | 道爺奇晶六紅線(1570) 79RY U/L | LINE161 | D05/161/1570/79UL |  |  |  | DNP | 319 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺奇晶六紅線(1570) |  | DS1 | 1571 | [13 empty] | 0688 | 689 | 0136 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1571_DS | 1571(道爺奇晶六紅線) DS | LINE161 | D05/161/1570/DS1 |  |  |  | DNP | 320 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺奇晶六紅線(1570) |  | DS2 | 1572 | [13 empty] | 0690 | 691 | 0137 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1572_DS | 1572(道爺奇晶六紅線) DS | LINE161 | D05/161/1570/DS2 |  |  |  | DNP | 321 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺奇晶六紅線(1570) |  | DS3 | 1573 | [13 empty] | 0692 | 693 | 0138 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1573_DS | 1573(道爺奇晶六紅線) DS | LINE161 | D05/161/1570/DS3 |  |  |  | DNP | 322 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺奇晶六紅線(1570) |  | E3 | 1573E | [13 empty] | 0694 | 695 | 0139 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1573E_ES | 1573E(道爺奇晶六紅線) ES | LINE161 | D05/161/1570/ES3 |  |  |  | DNP | 323 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺奇晶六白線(1580) |  | PHA | [14 empty] | 0038 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1580_PHA | 道爺奇晶六白線(1580) 相間RY | LINE161 | D05/161/1580/PHA |  |  |  | DNP | 324 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺奇晶六白線(1580) |  | GDA | [14 empty] | 0039 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1580_GDA | 道爺奇晶六白線(1580) 接地RY | LINE161 | D05/161/1580/GDA |  |  |  | DNP | 325 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺奇晶六白線(1580) |  | CB | [14 empty] | 0035 |  | 0008 | [8 empty] | 161KV_S | [8 empty] | 道爺DS.1580_CB | 1580(道爺奇晶六白線) CB | LINE161 | D05/161/1580/CB |  |  |  | DNP | 326 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺奇晶六白線(1580) |  | 79UL | [14 empty] | 0537 |  | 0090 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1580_79UL | 道爺奇晶六白線(1580) 79RY U/L | LINE161 | D05/161/1580/79UL |  |  |  | DNP | 327 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺奇晶六白線(1580) |  | DS1 | 1581 | [13 empty] | 0696 | 697 | 0140 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1581_DS | 1581(道爺奇晶六白線) DS | LINE161 | D05/161/1580/DS1 |  |  |  | DNP | 328 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺奇晶六白線(1580) |  | DS2 | 1582 | [13 empty] | 0698 | 699 | 0141 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1582_DS | 1582(道爺奇晶六白線) DS | LINE161 | D05/161/1580/DS2 |  |  |  | DNP | 329 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺奇晶六白線(1580) |  | DS3 | 1583 | [13 empty] | 0700 | 701 | 0142 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1583_DS | 1583(道爺奇晶六白線) DS | LINE161 | D05/161/1580/DS3 |  |  |  | DNP | 330 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺奇晶六白線(1580) |  | E3 | 1583E | [13 empty] | 0702 | 703 | 0143 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1583E_ES | 1583E(道爺奇晶六白線) ES | LINE161 | D05/161/1580/ES3 |  |  |  | DNP | 331 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1610 | 道爺安南新化線(1610) |  | PHA | [14 empty] | 0043 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1610_PHA | 道爺安南新化線(1610) 相間RY | LINE161 | D05/161/1610/PHA |  |  |  | DNP | 332 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1610 | 道爺安南新化線(1610) |  | GDA | [14 empty] | 0044 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1610_GDA | 道爺安南新化線(1610) 接地RY | LINE161 | D05/161/1610/GDA |  |  |  | DNP | 333 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1610 | 道爺安南新化線(1610) |  | 87A | [14 empty] | 0041 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1610_87A | 道爺安南新化線(1610) 87RY | LINE161 | D05/161/1610/87A |  |  |  | DNP | 334 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1610 | 道爺安南新化線(1610) |  | 87UL | [14 empty] | 0538 |  | 0091 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1610_87UL | 道爺安南新化線(1610) 87RY U/L | LINE161 | D05/161/1610/87UL |  |  |  | DNP | 335 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1610 | 道爺安南新化線(1610) |  | CB | [14 empty] | 0040 |  | 0009 | [8 empty] | 161KV_S | [8 empty] | 道爺DS.1610_CB | 1610(道爺安南新化線) CB | LINE161 | D05/161/1610/CB |  |  |  | DNP | 336 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 161 | 161kV | 1610 | 道爺安南新化線(1610) |  | 79UL | [14 empty] | 0540 |  | 0092 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1610_79UL | 道爺安南新化線(1610) 79RY U/L | LINE161 | D05/161/1610/79UL |  |  |  | DNP | 337 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1610 | 道爺安南新化線(1610) |  | DS1 | 1611 | [13 empty] | 0704 | 705 | 0144 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1611_DS | 1611(道爺安南新化線) DS | LINE161 | D05/161/1610/DS1 |  |  |  | DNP | 338 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1610 | 道爺安南新化線(1610) |  | DS2 | 1612 | [13 empty] | 0706 | 707 | 0145 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1612_DS | 1612(道爺安南新化線) DS | LINE161 | D05/161/1610/DS2 |  |  |  | DNP | 339 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1610 | 道爺安南新化線(1610) |  | DS3 | 1613 | [13 empty] | 0708 | 709 | 0146 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1613_DS | 1613(道爺安南新化線) DS | LINE161 | D05/161/1610/DS3 |  |  |  | DNP | 340 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1610 | 道爺安南新化線(1610) |  | E3 | 1613E | [13 empty] | 0710 | 711 | 0147 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1613E_ES | 1613E(道爺安南新化線) ES | LINE161 | D05/161/1610/ES3 |  |  |  | DNP | 341 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1620 | 道爺和順新化線(1620) |  | PHA | [14 empty] | 0048 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1620_PHA | 道爺和順新化線(1620) 相間RY | LINE161 | D05/161/1620/PHA |  |  |  | DNP | 342 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1620 | 道爺和順新化線(1620) |  | GDA | [14 empty] | 0049 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1620_GDA | 道爺和順新化線(1620) 接地RY | LINE161 | D05/161/1620/GDA |  |  |  | DNP | 343 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1620 | 道爺和順新化線(1620) |  | 87A | [14 empty] | 0046 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1620_87A | 道爺和順新化線(1620) 87RY | LINE161 | D05/161/1620/87A |  |  |  | DNP | 344 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1620 | 道爺和順新化線(1620) |  | 87UL | [14 empty] | 0541 |  | 0093 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1620_87UL | 道爺和順新化線(1620) 87RY U/L | LINE161 | D05/161/1620/87UL |  |  |  | DNP | 345 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1620 | 道爺和順新化線(1620) |  | CB | [14 empty] | 0045 |  | 0010 | [8 empty] | 161KV_S | [8 empty] | 道爺DS.1620_CB | 1620(道爺和順新化線) CB | LINE161 | D05/161/1620/CB |  |  |  | DNP | 346 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 161 | 161kV | 1620 | 道爺和順新化線(1620) |  | 79UL | [14 empty] | 0543 |  | 0094 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1620_79UL | 道爺和順新化線(1620) 79RY U/L | LINE161 | D05/161/1620/79UL |  |  |  | DNP | 347 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1620 | 道爺和順新化線(1620) |  | DS1 | 1621 | [13 empty] | 0712 | 713 | 0148 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1621_DS | 1621(道爺和順新化線) DS | LINE161 | D05/161/1620/DS1 |  |  |  | DNP | 348 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1620 | 道爺和順新化線(1620) |  | DS2 | 1622 | [13 empty] | 0714 | 715 | 0149 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1622_DS | 1622(道爺和順新化線) DS | LINE161 | D05/161/1620/DS2 |  |  |  | DNP | 349 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1620 | 道爺和順新化線(1620) |  | DS3 | 1623 | [13 empty] | 0716 | 717 | 0150 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1623_DS | 1623(道爺和順新化線) DS | LINE161 | D05/161/1620/DS3 |  |  |  | DNP | 350 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1620 | 道爺和順新化線(1620) |  | E3 | 1623E | [13 empty] | 0718 | 719 | 0151 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1623E_ES | 1623E(道爺和順新化線) ES | LINE161 | D05/161/1620/ES3 |  |  |  | DNP | 351 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 22 | 22kV | 4K61 | 爺61線(4K61) |  | PHA | [14 empty] | 0200 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K61_PHA | 23KV爺61線(4K61) 相間RY | FEEDER | D05/22/4K61/PHA |  |  |  | DNP | 352 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K61 | 爺61線(4K61) |  | GDA | [14 empty] | 0201 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K61_GDA | 23KV爺61線(4K61) 接地RY | FEEDER | D05/22/4K61/GDA |  |  |  | DNP | 353 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K61 | 爺61線(4K61) 79RY |  | 79UL | [14 empty] | 0792 |  | 0192 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K61_79UL | 23KV爺61線(4K61) 79RY U/L | FEEDER | D05/22/4K61/FDR_RCA |  |  |  | DNP | 354 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 4K61_LCO | 爺61線(4K61) LCO |  | TapPosMv | [14 empty] | 0793 |  | 0193 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K61_LCO_TAP | 23KV爺61線(4K61) LCO TAP | FEEDER | D05/22/4K61/51NA |  |  |  | DNP | 355 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D05 | 道爺DS | 22 | 22kV | 4K61 | 爺61線 |  | CB | [14 empty] | 0199 |  | 0037 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K61_CB | 4K61(23KV爺61線) CB | FEEDER | D05/22/4K61/CB |  |  |  | DNP | 356 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K62 | 爺62線(4K62) |  | PHA | [14 empty] | 0203 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K62_PHA | 23KV爺62線(4K62) 相間RY | FEEDER | D05/22/4K62/PHA |  |  |  | DNP | 357 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K62 | 爺62線(4K62) |  | GDA | [14 empty] | 0204 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K62_GDA | 23KV爺62線(4K62) 接地RY | FEEDER | D05/22/4K62/GDA |  |  |  | DNP | 358 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K62 | 爺62線(4K62) 79RY |  | 79UL | [14 empty] | 0794 |  | 0194 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K62_79UL | 23KV爺62線(4K62) 79RY U/L | FEEDER | D05/22/4K62/FDR_RCA |  |  |  | DNP | 359 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 4K62_LCO | 爺62線(4K62) LCO |  | TapPosMv | [14 empty] | 0795 |  | 0195 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K62_LCO_TAP | 23KV爺62線(4K62) LCO TAP | FEEDER | D05/22/4K62/51NA |  |  |  | DNP | 360 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D05 | 道爺DS | 22 | 22kV | 4K62 | 爺62線 |  | CB | [14 empty] | 0202 |  | 0038 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K62_CB | 4K62(23KV爺62線) CB | FEEDER | D05/22/4K62/CB |  |  |  | DNP | 361 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K63 | 爺63線(4K63) |  | PHA | [14 empty] | 0206 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K63_PHA | 23KV爺63線(4K63) 相間RY | FEEDER | D05/22/4K63/PHA |  |  |  | DNP | 362 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K63 | 爺63線(4K63) |  | GDA | [14 empty] | 0207 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K63_GDA | 23KV爺63線(4K63) 接地RY | FEEDER | D05/22/4K63/GDA |  |  |  | DNP | 363 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K63 | 爺63線(4K63) 79RY |  | 79UL | [14 empty] | 0796 |  | 0196 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K63_79UL | 23KV爺63線(4K63) 79RY U/L | FEEDER | D05/22/4K63/FDR_RCA |  |  |  | DNP | 364 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 4K63_LCO | 爺63線(4K63) LCO |  | TapPosMv | [14 empty] | 0797 |  | 0197 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K63_LCO_TAP | 23KV爺63線(4K63) LCO TAP | FEEDER | D05/22/4K63/51NA |  |  |  | DNP | 365 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D05 | 道爺DS | 22 | 22kV | 4K63 | 爺63線 |  | CB | [14 empty] | 0205 |  | 0039 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K63_CB | 4K63(23KV爺63線) CB | FEEDER | D05/22/4K63/CB |  |  |  | DNP | 366 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K64 | 爺64線(4K64) |  | PHA | [14 empty] | 0209 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K64_PHA | 23KV爺64線(4K64) 相間RY | FEEDER | D05/22/4K64/PHA |  |  |  | DNP | 367 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K64 | 爺64線(4K64) |  | GDA | [14 empty] | 0210 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K64_GDA | 23KV爺64線(4K64) 接地RY | FEEDER | D05/22/4K64/GDA |  |  |  | DNP | 368 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K64 | 爺64線(4K64) 79RY |  | 79UL | [14 empty] | 0798 |  | 0198 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K64_79UL | 23KV爺64線(4K64) 79RY U/L | FEEDER | D05/22/4K64/FDR_RCA |  |  |  | DNP | 369 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 4K64_LCO | 爺64線(4K64) LCO |  | TapPosMv | [14 empty] | 0799 |  | 0199 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K64_LCO_TAP | 23KV爺64線(4K64) LCO TAP | FEEDER | D05/22/4K64/51NA |  |  |  | DNP | 370 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D05 | 道爺DS | 22 | 22kV | 4K64 | 爺64線 |  | CB | [14 empty] | 0208 |  | 0040 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K64_CB | 4K64(23KV爺64線) CB | FEEDER | D05/22/4K64/CB |  |  |  | DNP | 371 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K65 | 爺65線(4K65) |  | PHA | [14 empty] | 0215 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K65_PHA | 23KV爺65線(4K65) 相間RY | FEEDER | D05/22/4K65/PHA |  |  |  | DNP | 372 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K65 | 爺65線(4K65) |  | GDA | [14 empty] | 0216 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K65_GDA | 23KV爺65線(4K65) 接地RY | FEEDER | D05/22/4K65/GDA |  |  |  | DNP | 373 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K65 | 爺65線(4K65) 79RY |  | 79UL | [14 empty] | 0800 |  | 0200 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K65_79UL | 23KV爺65線(4K65) 79RY U/L | FEEDER | D05/22/4K65/FDR_RCA |  |  |  | DNP | 374 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 4K65_LCO | 爺65線(4K65) LCO |  | TapPosMv | [14 empty] | 0801 |  | 0201 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K65_LCO_TAP | 23KV爺65線(4K65) LCO TAP | FEEDER | D05/22/4K65/51NA |  |  |  | DNP | 375 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D05 | 道爺DS | 22 | 22kV | 4K65 | 爺65線 |  | CB | [14 empty] | 0214 |  | 0043 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K65_CB | 4K65(23KV爺65線) CB | FEEDER | D05/22/4K65/CB |  |  |  | DNP | 376 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K66 | 爺66線(4K66) |  | PHA | [14 empty] | 0218 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K66_PHA | 23KV爺66線(4K66) 相間RY | FEEDER | D05/22/4K66/PHA |  |  |  | DNP | 377 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K66 | 爺66線(4K66) |  | GDA | [14 empty] | 0219 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K66_GDA | 23KV爺66線(4K66) 接地RY | FEEDER | D05/22/4K66/GDA |  |  |  | DNP | 378 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K66 | 爺66線(4K66) 79RY |  | 79UL | [14 empty] | 0802 |  | 0202 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K66_79UL | 23KV爺66線(4K66) 79RY U/L | FEEDER | D05/22/4K66/FDR_RCA |  |  |  | DNP | 379 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 4K66_LCO | 爺66線(4K66) LCO |  | TapPosMv | [14 empty] | 0803 |  | 0203 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K66_LCO_TAP | 23KV爺66線(4K66) LCO TAP | FEEDER | D05/22/4K66/51NA |  |  |  | DNP | 380 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D05 | 道爺DS | 22 | 22kV | 4K66 | 爺66線 |  | CB | [14 empty] | 0217 |  | 0044 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K66_CB | 4K66(23KV爺66線) CB | FEEDER | D05/22/4K66/CB |  |  |  | DNP | 381 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K67 | 爺67線(4K67) |  | PHA | [14 empty] | 0221 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K67_PHA | 23KV爺67線(4K67) 相間RY | FEEDER | D05/22/4K67/PHA |  |  |  | DNP | 382 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K67 | 爺67線(4K67) |  | GDA | [14 empty] | 0222 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K67_GDA | 23KV爺67線(4K67) 接地RY | FEEDER | D05/22/4K67/GDA |  |  |  | DNP | 383 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K67 | 爺67線(4K67) 79RY |  | 79UL | [14 empty] | 0804 |  | 0204 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K67_79UL | 23KV爺67線(4K67) 79RY U/L | FEEDER | D05/22/4K67/FDR_RCA |  |  |  | DNP | 384 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 4K67_LCO | 爺67線(4K67) LCO |  | TapPosMv | [14 empty] | 0805 |  | 0205 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K67_LCO_TAP | 23KV爺67線(4K67) LCO TAP | FEEDER | D05/22/4K67/51NA |  |  |  | DNP | 385 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D05 | 道爺DS | 22 | 22kV | 4K67 | 爺67線 |  | CB | [14 empty] | 0220 |  | 0045 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K67_CB | 4K67(23KV爺67線) CB | FEEDER | D05/22/4K67/CB |  |  |  | DNP | 386 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K68 | 爺68線(4K68) |  | PHA | [14 empty] | 0224 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K68_PHA | 23KV爺68線(4K68) 相間RY | FEEDER | D05/22/4K68/PHA |  |  |  | DNP | 387 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K68 | 爺68線(4K68) |  | GDA | [14 empty] | 0225 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K68_GDA | 23KV爺68線(4K68) 接地RY | FEEDER | D05/22/4K68/GDA |  |  |  | DNP | 388 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K68 | 爺68線(4K68) 79RY |  | 79UL | [14 empty] | 0806 |  | 0206 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K68_79UL | 23KV爺68線(4K68) 79RY U/L | FEEDER | D05/22/4K68/FDR_RCA |  |  |  | DNP | 389 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 4K68_LCO | 爺68線(4K68) LCO |  | TapPosMv | [14 empty] | 0807 |  | 0207 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K68_LCO_TAP | 23KV爺68線(4K68) LCO TAP | FEEDER | D05/22/4K68/51NA |  |  |  | DNP | 390 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D05 | 道爺DS | 22 | 22kV | 4K68 | 爺68線 |  | CB | [14 empty] | 0223 |  | 0046 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K68_CB | 4K68(23KV爺68線) CB | FEEDER | D05/22/4K68/CB |  |  |  | DNP | 391 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K71 | 爺71線(4K71) |  | PHA | [14 empty] | 0236 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K71_PHA | 23KV爺71線(4K71) 相間RY | FEEDER | D05/22/4K71/PHA |  |  |  | DNP | 392 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K71 | 爺71線(4K71) |  | GDA | [14 empty] | 0237 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K71_GDA | 23KV爺71線(4K71) 接地RY | FEEDER | D05/22/4K71/GDA |  |  |  | DNP | 393 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K71 | 爺71線(4K71) 79RY |  | 79UL | [14 empty] | 0808 |  | 0208 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K71_79UL | 23KV爺71線(4K71) 79RY U/L | FEEDER | D05/22/4K71/FDR_RCA |  |  |  | DNP | 394 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 4K71_LCO | 爺71線(4K71) LCO |  | TapPosMv | [14 empty] | 0809 |  | 0209 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K71_LCO_TAP | 23KV爺71線(4K71) LCO TAP | FEEDER | D05/22/4K71/51NA |  |  |  | DNP | 395 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D05 | 道爺DS | 22 | 22kV | 4K71 | 爺71線 |  | CB | [14 empty] | 0235 |  | 0051 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K71_CB | 4K71(23KV爺71線) CB | FEEDER | D05/22/4K71/CB |  |  |  | DNP | 396 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K72 | 爺72線(4K72) |  | PHA | [14 empty] | 0239 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K72_PHA | 23KV爺72線(4K72) 相間RY | FEEDER | D05/22/4K72/PHA |  |  |  | DNP | 397 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K72 | 爺72線(4K72) |  | GDA | [14 empty] | 0240 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K72_GDA | 23KV爺72線(4K72) 接地RY | FEEDER | D05/22/4K72/GDA |  |  |  | DNP | 398 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K72 | 爺72線(4K72) 79RY |  | 79UL | [14 empty] | 0810 |  | 0210 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K72_79UL | 23KV爺72線(4K72) 79RY U/L | FEEDER | D05/22/4K72/FDR_RCA |  |  |  | DNP | 399 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 4K72_LCO | 爺72線(4K72) LCO |  | TapPosMv | [14 empty] | 0811 |  | 0211 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K72_LCO_TAP | 23KV爺72線(4K72) LCO TAP | FEEDER | D05/22/4K72/51NA |  |  |  | DNP | 400 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D05 | 道爺DS | 22 | 22kV | 4K72 | 爺72線 |  | CB | [14 empty] | 0238 |  | 0052 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K72_CB | 4K72(23KV爺72線) CB | FEEDER | D05/22/4K72/CB |  |  |  | DNP | 401 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K73 | 爺73線(4K73) |  | PHA | [14 empty] | 0242 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K73_PHA | 23KV爺73線(4K73) 相間RY | FEEDER | D05/22/4K73/PHA |  |  |  | DNP | 402 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K73 | 爺73線(4K73) |  | GDA | [14 empty] | 0243 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K73_GDA | 23KV爺73線(4K73) 接地RY | FEEDER | D05/22/4K73/GDA |  |  |  | DNP | 403 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K73 | 爺73線(4K73) 79RY |  | 79UL | [14 empty] | 0812 |  | 0212 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K73_79UL | 23KV爺73線(4K73) 79RY U/L | FEEDER | D05/22/4K73/FDR_RCA |  |  |  | DNP | 404 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 4K73_LCO | 爺73線(4K73) LCO |  | TapPosMv | [14 empty] | 0813 |  | 0213 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K73_LCO_TAP | 23KV爺73線(4K73) LCO TAP | FEEDER | D05/22/4K73/51NA |  |  |  | DNP | 405 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D05 | 道爺DS | 22 | 22kV | 4K73 | 爺73線 |  | CB | [14 empty] | 0241 |  | 0053 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K73_CB | 4K73(23KV爺73線) CB | FEEDER | D05/22/4K73/CB |  |  |  | DNP | 406 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K74 | 爺74線(4K74) |  | PHA | [14 empty] | 0245 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K74_PHA | 23KV爺74線(4K74) 相間RY | FEEDER | D05/22/4K74/PHA |  |  |  | DNP | 407 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K74 | 爺74線(4K74) |  | GDA | [14 empty] | 0246 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K74_GDA | 23KV爺74線(4K74) 接地RY | FEEDER | D05/22/4K74/GDA |  |  |  | DNP | 408 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K74 | 爺74線(4K74) 79RY |  | 79UL | [14 empty] | 0814 |  | 0214 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K74_79UL | 23KV爺74線(4K74) 79RY U/L | FEEDER | D05/22/4K74/FDR_RCA |  |  |  | DNP | 409 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 4K74_LCO | 爺74線(4K74) LCO |  | TapPosMv | [14 empty] | 0815 |  | 0215 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K74_LCO_TAP | 23KV爺74線(4K74) LCO TAP | FEEDER | D05/22/4K74/51NA |  |  |  | DNP | 410 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D05 | 道爺DS | 22 | 22kV | 4K74 | 爺74線 |  | CB | [14 empty] | 0244 |  | 0054 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K74_CB | 4K74(23KV爺74線) CB | FEEDER | D05/22/4K74/CB |  |  |  | DNP | 411 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K75 | 爺75線(4K75) |  | PHA | [14 empty] | 0251 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K75_PHA | 23KV爺75線(4K75) 相間RY | FEEDER | D05/22/4K75/PHA |  |  |  | DNP | 412 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K75 | 爺75線(4K75) |  | GDA | [14 empty] | 0252 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K75_GDA | 23KV爺75線(4K75) 接地RY | FEEDER | D05/22/4K75/GDA |  |  |  | DNP | 413 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K75 | 爺75線(4K75) 79RY |  | 79UL | [14 empty] | 0816 |  | 0216 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K75_79UL | 23KV爺75線(4K75) 79RY U/L | FEEDER | D05/22/4K75/FDR_RCA |  |  |  | DNP | 414 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 4K75_LCO | 爺75線(4K75) LCO |  | TapPosMv | [14 empty] | 0817 |  | 0217 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K75_LCO_TAP | 23KV爺75線(4K75) LCO TAP | FEEDER | D05/22/4K75/51NA |  |  |  | DNP | 415 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D05 | 道爺DS | 22 | 22kV | 4K75 | 爺75線 |  | CB | [14 empty] | 0250 |  | 0057 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K75_CB | 4K75(23KV爺75線) CB | FEEDER | D05/22/4K75/CB |  |  |  | DNP | 416 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K76 | 爺76線(4K76) |  | PHA | [14 empty] | 0254 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K76_PHA | 23KV爺76線(4K76) 相間RY | FEEDER | D05/22/4K76/PHA |  |  |  | DNP | 417 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K76 | 爺76線(4K76) |  | GDA | [14 empty] | 0255 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K76_GDA | 23KV爺76線(4K76) 接地RY | FEEDER | D05/22/4K76/GDA |  |  |  | DNP | 418 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K76 | 爺76線(4K76) 79RY |  | 79UL | [14 empty] | 0818 |  | 0218 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K76_79UL | 23KV爺76線(4K76) 79RY U/L | FEEDER | D05/22/4K76/FDR_RCA |  |  |  | DNP | 419 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 4K76_LCO | 爺76線(4K76) LCO |  | TapPosMv | [14 empty] | 0819 |  | 0219 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K76_LCO_TAP | 23KV爺76線(4K76) LCO TAP | FEEDER | D05/22/4K76/51NA |  |  |  | DNP | 420 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D05 | 道爺DS | 22 | 22kV | 4K76 | 爺76線 |  | CB | [14 empty] | 0253 |  | 0058 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K76_CB | 4K76(23KV爺76線) CB | FEEDER | D05/22/4K76/CB |  |  |  | DNP | 421 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K77 | 爺77線(4K77) |  | PHA | [14 empty] | 0257 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K77_PHA | 23KV爺77線(4K77) 相間RY | FEEDER | D05/22/4K77/PHA |  |  |  | DNP | 422 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K77 | 爺77線(4K77) |  | GDA | [14 empty] | 0258 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K77_GDA | 23KV爺77線(4K77) 接地RY | FEEDER | D05/22/4K77/GDA |  |  |  | DNP | 423 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K77 | 爺77線(4K77) 79RY |  | 79UL | [14 empty] | 0820 |  | 0220 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K77_79UL | 23KV爺77線(4K77) 79RY U/L | FEEDER | D05/22/4K77/FDR_RCA |  |  |  | DNP | 424 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 4K77_LCO | 爺77線(4K77) LCO |  | TapPosMv | [14 empty] | 0821 |  | 0221 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K77_LCO_TAP | 23KV爺77線(4K77) LCO TAP | FEEDER | D05/22/4K77/51NA |  |  |  | DNP | 425 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D05 | 道爺DS | 22 | 22kV | 4K77 | 爺77線 |  | CB | [14 empty] | 0256 |  | 0059 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K77_CB | 4K77(23KV爺77線) CB | FEEDER | D05/22/4K77/CB |  |  |  | DNP | 426 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 4K78 | 爺78線(4K78) |  | PHA | [14 empty] | 0260 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K78_PHA | 23KV爺78線(4K78) 相間RY | FEEDER | D05/22/4K78/PHA |  |  |  | DNP | 427 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K78 | 爺78線(4K78) |  | GDA | [14 empty] | 0261 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K78_GDA | 23KV爺78線(4K78) 接地RY | FEEDER | D05/22/4K78/GDA |  |  |  | DNP | 428 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 4K78 | 爺78線(4K78) 79RY |  | 79UL | [14 empty] | 0822 |  | 0222 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K78_79UL | 23KV爺78線(4K78) 79RY U/L | FEEDER | D05/22/4K78/FDR_RCA |  |  |  | DNP | 429 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 22 | 22kV | 4K78_LCO | 爺78線(4K78) LCO |  | TapPosMv | [14 empty] | 0823 |  | 0223 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K78_LCO_TAP | 23KV爺78線(4K78) LCO TAP | FEEDER | D05/22/4K78/51NA |  |  |  | DNP | 430 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D05 | 道爺DS | 22 | 22kV | 4K78 | 爺78線 |  | CB | [14 empty] | 0259 |  | 0060 | [8 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K78_CB | 4K78(23KV爺78線) CB | FEEDER | D05/22/4K78/CB |  |  |  | DNP | 431 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [14 empty] | 0060 |  | 0013 | [8 empty] | 161KV_S | [8 empty] | 道爺DS.1500_CB | 1500(TIE) CB | TIE | D05/161/1500/CB |  |  |  | DNP | 432 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 1500 | TIE(1500) |  | 50A | [14 empty] | 0061 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1500_50A | 161KV TIE(1500) 50RY | TIE | D05/161/1500/50A |  |  |  | DNP | 433 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [13 empty] | 0720 | 721 | 0160 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1501_DS | 1501(TIE) DS | TIE | D05/161/1500/DS1 |  |  |  | DNP | 434 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [13 empty] | 0722 | 723 | 0161 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1502_DS | 1502(TIE) DS | TIE | D05/161/1500/DS2 |  |  |  | DNP | 435 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 0 |  | 1500 | TIE(1500) |  | 50SA | [14 empty] | 0550 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.1500_50SA | 161KV TIE(1500) 50RY 測試/正常 | TIE | D05/161/1500/50SA |  |  |  | DNP | 436 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TEST/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1600 | TIE(1600) |  | CB | [14 empty] | 0062 |  | 0014 | [8 empty] | 161KV_S | [8 empty] | 道爺DS.1600_CB | 1600(TIE) CB | TIE | D05/161/1600/CB |  |  |  | DNP | 437 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 1600 | TIE(1600) |  | 50A | [14 empty] | 0063 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1600_50A | 161KV TIE(1600) 50RY | TIE | D05/161/1600/50A |  |  |  | DNP | 438 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1600 | TIE(1600) |  | DS1 | 1601 | [13 empty] | 0728 | 729 | 0162 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1601_DS | 1601(TIE) DS | TIE | D05/161/1600/DS1 |  |  |  | DNP | 439 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1600 | TIE(1600) |  | DS2 | 1602 | [13 empty] | 0730 | 731 | 0163 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1602_DS | 1602(TIE) DS | TIE | D05/161/1600/DS2 |  |  |  | DNP | 440 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 0 |  | 1600 | TIE(1600) |  | 50SA | [14 empty] | 0551 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.1600_50SA | 161KV TIE(1600) 50RY 測試/正常 | TIE | D05/161/1600/50SA |  |  |  | DNP | 441 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TEST/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1700 | TIE(1700) |  | CB | [14 empty] | 0064 |  | 0015 | [8 empty] | 161KV_S | [8 empty] | 道爺DS.1700_CB | 1700(TIE) CB | TIE | D05/161/1700/CB |  |  |  | DNP | 442 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1700 | TIE(1700) |  | DS1 | 1701 | [13 empty] | 0736 | 737 | 0164 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1701_DS | 1701(TIE) DS | TIE | D05/161/1700/DS1 |  |  |  | DNP | 443 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1700 | TIE(1700) |  | DS3 | 1703 | [13 empty] | 0738 | 739 | 0165 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1703_DS | 1703(TIE) DS | TIE | D05/161/1700/ABS2 |  |  |  | DNP | 444 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1800 | TIE(1800) |  | CB | [14 empty] | 0066 |  | 0016 | [8 empty] | 161KV_S | [8 empty] | 道爺DS.1800_CB | 1800(TIE) CB | TIE | D05/161/1800/CB |  |  |  | DNP | 445 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1800 | TIE(1800) |  | DS2 | 1802 | [13 empty] | 0744 | 745 | 0166 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1802_DS | 1802(TIE) DS | TIE | D05/161/1800/ABS1 |  |  |  | DNP | 446 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1800 | TIE(1800) |  | DS4 | 1804 | [13 empty] | 0746 | 747 | 0167 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1804_DS | 1804(TIE) DS | TIE | D05/161/1800/DS1 |  |  |  | DNP | 447 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 0 |  | 200 | TIE(200) |  | CB | [14 empty] | 0193 |  | 0034 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.200_CB | 200(TIE) CB | TIE | D05/22/200/CB |  |  |  | DNP | 448 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 200 | TIE(200) |  | 51A | [14 empty] | 0194 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.200_51A | 23KV TIE(200) 51RY | TIE | D05/22/200/PHA |  |  |  | DNP | 449 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 200 | TIE(200) |  | 51NA | [14 empty] | 0195 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.200_51NA | 23KV TIE(200) 51N RY | TIE | D05/22/200/GDA |  |  |  | DNP | 450 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 300 | TIE(300) |  | CB | [14 empty] | 0229 |  | 0048 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.300_CB | 300(TIE) CB | TIE | D05/22/300/CB |  |  |  | DNP | 451 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 300 | TIE(300) |  | 51A | [14 empty] | 0230 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.300_51A | 23KV TIE(300) 51RY | TIE | D05/22/300/PHA |  |  |  | DNP | 452 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 300 | TIE(300) |  | 51NA | [14 empty] | 0231 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.300_51NA | 23KV TIE(300) 51N RY | TIE | D05/22/300/GDA |  |  |  | DNP | 453 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 390 | #1SSTR(390) |  | CB | [14 empty] | 0226 |  | 0047 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.390_CB | 390(#1SSTR) CB | OTHER | D05/22/390/CB |  |  |  | DNP | 454 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 1SSTR | #1SSTR |  | 51A | [14 empty] | 0227 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#1SSTR_51A | #1SSTR 51RY | OTHER | D05/22/390/PHA |  |  |  | DNP | 455 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 1SSTR | #1SSTR |  | 51NA | [14 empty] | 0228 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | D05/22/390/GDA |  |  |  | DNP | 456 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 490 | #2SSTR(490) |  | CB | [14 empty] | 0262 |  | 0061 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.490_CB | 490(#2SSTR) CB | OTHER | D05/22/490/CB |  |  |  | DNP | 457 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 2SSTR | #2SSTR |  | 51A | [14 empty] | 0263 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#2SSTR_51A | #2SSTR 51RY | OTHER | D05/22/490/PHA |  |  |  | DNP | 458 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 2SSTR | #2SSTR |  | 51NA | [14 empty] | 0264 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | D05/22/490/GDA |  |  |  | DNP | 459 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB | [14 empty] | 0086 |  | 0018 | [8 empty] | 161KV_S | [8 empty] | 道爺DS.1760_CB | 1760(#2DTR) CB | MTR | D05/161/1760/CB |  |  |  | DNP | 460 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 330 | #2DTR(330) |  | CB | [14 empty] | 0092 |  | 0035 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.330_CB | 330(#2DTR) CB | MTR | D05/22/330/CB |  |  |  | DNP | 461 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 340 | #2DTR(340) |  | CB | [14 empty] | 0095 |  | 0041 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.340_CB | 340(#2DTR) CB | MTR | D05/22/340/CB |  |  |  | DNP | 462 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 2DTR | #2DTR |  | 51ZA | [14 empty] | 0089 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | D05//2DTR/51ZA |  |  |  | DNP | 463 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 2DTR | #2DTR |  | 87A | [14 empty] | 0087 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.#2DTR_87A | #2DTR 87RY | MTR | D05//2DTR/87A |  |  |  | DNP | 464 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 2DTR | #2DTR |  | 87UL | [14 empty] | 0565 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#2DTR_87UL | #2DTR 87RY U/L | MTR | D05//2DTR/87UL |  |  |  | DNP | 465 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 0 |  | 330 | #2DTR(330) |  | 51A | [14 empty] | 0093 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.330_51A | #2DTR二次側(330) 51RY | MTR | D05/22/330/PHA |  |  |  | DNP | 466 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 340 | #2DTR(340) |  | 51A | [14 empty] | 0096 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.340_51A | #2DTR二次側(340) 51RY | MTR | D05/22/340/PHA |  |  |  | DNP | 467 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 2DTR | #2DTR |  | 96PA | [14 empty] | 0088 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | D05//2DTR/96PA |  |  |  | DNP | 468 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 2DTR | #2DTR |  | 96D | [14 empty] | 0847 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#2DTR_96D | #2DTR 96D RY | MTR | D05//2DTR/96D |  |  |  | DNP | 469 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 2DTR | #2DTR |  | 96P | [14 empty] | 0846 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#2DTR_96P | #2DTR 96P RY | MTR | D05//2DTR/96P |  |  |  | DNP | 470 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 2DTR | #2DTR |  | 63Q | [14 empty] | 0845 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#2DTR_63Q | #2DTR 63Q RY | MTR | D05//2DTR/63Q |  |  |  | DNP | 471 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 2DTR | #2DTR |  | 96B1 | [14 empty] | 0848 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | D05//2DTR/96B1 |  |  |  | DNP | 472 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 2DTR | #2DTR |  | 96B2 | [14 empty] | 0849 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | D05//2DTR/96B2 |  |  |  | DNP | 473 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 2DTR | #2DTR |  | TRA | [14 empty] | 0568 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#2DTR_TRA | #2DTR 重故障 | MTR | D05//2DTR/TRA |  |  |  | DNP | 474 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 2DTR | #2DTR |  | TRF | [14 empty] | 0569 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#2DTR_TRF | #2DTR 輕故障 | MTR | D05//2DTR/TRF |  |  |  | DNP | 475 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 2DTR | #2DTR |  | SupLocal | [14 empty] | 0566 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#2DTR_S/L | #2DTR OLTC S/L | MTR | D05//2DTR/SupLocal |  |  |  | DNP | 476 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D05 | 道爺DS | 0 |  | 2DTR | #2DTR |  | A_M | [14 empty] | 0567 |  | 0101 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.#2DTR_A/M | #2DTR OLTC A/M | MTR | D05//2DTR/Tap Chan |  |  |  | DNP | 477 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D05 | 道爺DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 | [13 empty] | 0760 | 761 | 0170 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1761_DS | 1761(#2DTR) DS | MTR | D05/161/1760/DS1 |  |  |  | DNP | 478 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 | [13 empty] | 0762 | 763 | 0171 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1762_DS | 1762(#2DTR) DS | MTR | D05/161/1760/DS2 |  |  |  | DNP | 479 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB | [14 empty] | 0098 |  | 0019 | [8 empty] | 161KV_S | [8 empty] | 道爺DS.1770_CB | 1770(#3DTR) CB | MTR | D05/161/1770/CB |  |  |  | DNP | 480 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 350 | #3DTR(350) |  | CB | [14 empty] | 0104 |  | 0049 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.350_CB | 350(#3DTR) CB | MTR | D05/22/350/CB |  |  |  | DNP | 481 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 360 | #3DTR(360) |  | CB | [14 empty] | 0107 |  | 0055 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.360_CB | 360(#3DTR) CB | MTR | D05/22/360/CB |  |  |  | DNP | 482 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 3DTR | #3DTR |  | 51ZA | [14 empty] | 0101 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.#3DTR_51ZA | #3DTR 51Z RY | MTR | D05//3DTR/51ZA |  |  |  | DNP | 483 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 3DTR | #3DTR |  | 87A | [14 empty] | 0099 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.#3DTR_87A | #3DTR 87RY | MTR | D05//3DTR/87A |  |  |  | DNP | 484 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 3DTR | #3DTR |  | 87UL | [14 empty] | 0570 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#3DTR_87UL | #3DTR 87RY U/L | MTR | D05//3DTR/87UL |  |  |  | DNP | 485 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 0 |  | 350 | #3DTR(350) |  | 51A | [14 empty] | 0105 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.350_51A | #3DTR二次側(350) 51RY | MTR | D05/22/350/PHA |  |  |  | DNP | 486 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 360 | #3DTR(360) |  | 51A | [14 empty] | 0108 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.360_51A | #3DTR二次側(360) 51RY | MTR | D05/22/360/PHA |  |  |  | DNP | 487 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 3DTR | #3DTR |  | 96PA | [14 empty] | 0100 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.#3DTR_96PA | #3DTR 機械保護動作 | MTR | D05//3DTR/96PA |  |  |  | DNP | 488 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 3DTR | #3DTR |  | 96D | [14 empty] | 0852 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#3DTR_96D | #3DTR 96D RY | MTR | D05//3DTR/96D |  |  |  | DNP | 489 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 3DTR | #3DTR |  | 96P | [14 empty] | 0851 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#3DTR_96P | #3DTR 96P RY | MTR | D05//3DTR/96P |  |  |  | DNP | 490 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 3DTR | #3DTR |  | 63Q | [14 empty] | 0850 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#3DTR_63Q | #3DTR 63Q RY | MTR | D05//3DTR/63Q |  |  |  | DNP | 491 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 3DTR | #3DTR |  | 96B1 | [14 empty] | 0853 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#3DTR_96B1 | #3DTR 96B1 RY | MTR | D05//3DTR/96B1 |  |  |  | DNP | 492 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 3DTR | #3DTR |  | 96B2 | [14 empty] | 0854 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#3DTR_96B2 | #3DTR 96B2 RY | MTR | D05//3DTR/96B2 |  |  |  | DNP | 493 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 3DTR | #3DTR |  | TRA | [14 empty] | 0573 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#3DTR_TRA | #3DTR 重故障 | MTR | D05//3DTR/TRA |  |  |  | DNP | 494 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 3DTR | #3DTR |  | TRF | [14 empty] | 0574 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#3DTR_TRF | #3DTR 輕故障 | MTR | D05//3DTR/TRF |  |  |  | DNP | 495 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 3DTR | #3DTR |  | SupLocal | [14 empty] | 0571 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#3DTR_S/L | #3DTR OLTC S/L | MTR | D05//3DTR/SupLocal |  |  |  | DNP | 496 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D05 | 道爺DS | 0 |  | 3DTR | #3DTR |  | A_M | [14 empty] | 0572 |  | 0103 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.#3DTR_A/M | #3DTR OLTC A/M | MTR | D05//3DTR/Tap Chan |  |  |  | DNP | 497 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D05 | 道爺DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 | [13 empty] | 0896 | 897 | 0172 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1771_DS | 1771(#3DTR) DS | MTR | D05/161/1770/DS2 |  |  |  | DNP | 498 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 | [13 empty] | 0898 | 899 | 0173 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1772_DS | 1772(#3DTR) DS | MTR | D05/161/1770/ABS3 |  |  |  | DNP | 499 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 22 | 22kV | 230 | #3SC(230) |  | CB | [14 empty] | 0196 |  | 0036 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.230_CB | 230(23KV #3SC) CB | SC | D05/22/230/CB |  |  |  | DNP | 500 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 230 | #3SC(230) |  | SCA | [14 empty] | 0197 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.230_SCA | 23KV #3SC 51,51N RY | SC | D05/22/230/SCA |  |  |  | DNP | 501 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 230 | #3SC(230) |  | UVA | [14 empty] | 0198 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.230_OUVA | 23KV #3SC 27,59RY(欠壓或過壓) | SC | D05/22/230/UVA |  |  |  | DNP | 502 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 240 | #4SC(240) |  | CB | [14 empty] | 0211 |  | 0042 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.240_CB | 240(23KV #4SC) CB | SC | D05/22/240/CB |  |  |  | DNP | 503 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 240 | #4SC(240) |  | SCA | [14 empty] | 0212 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.240_SCA | 23KV #4SC 51,51N RY | SC | D05/22/240/SCA |  |  |  | DNP | 504 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 240 | #4SC(240) |  | UVA | [14 empty] | 0213 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.240_OUVA | 23KV #4SC 27,59RY(欠壓或過壓) | SC | D05/22/240/UVA |  |  |  | DNP | 505 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 250 | #5SC(250) |  | CB | [14 empty] | 0232 |  | 0050 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.250_CB | 250(23KV #5SC) CB | SC | D05/22/250/CB |  |  |  | DNP | 506 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 250 | #5SC(250) |  | SCA | [14 empty] | 0233 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.250_SCA | 23KV #5SC 51,51N RY | SC | D05/22/250/SCA |  |  |  | DNP | 507 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 250 | #5SC(250) |  | UVA | [14 empty] | 0234 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.250_OUVA | 23KV #5SC 27,59RY(欠壓或過壓) | SC | D05/22/250/UVA |  |  |  | DNP | 508 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 260 | #6SC(260) |  | CB | [14 empty] | 0247 |  | 0056 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.260_CB | 260(23KV #6SC) CB | SC | D05/22/260/CB |  |  |  | DNP | 509 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 260 | #6SC(260) |  | SCA | [14 empty] | 0248 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.260_SCA | 23KV #6SC 51,51N RY | SC | D05/22/260/SCA |  |  |  | DNP | 510 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 260 | #6SC(260) |  | UVA | [14 empty] | 0249 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.260_OUVA | 23KV #6SC 27,59RY(欠壓或過壓) | SC | D05/22/260/UVA |  |  |  | DNP | 511 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1611BUS | #1BUS |  | VUA | [14 empty] | 0624 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | D05/161/1BUS/BUS_VUA |  |  |  | DNP | 512 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1611BUS | #1BUS |  | 87A | [14 empty] | 0068 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | D05/161/1BUS/87A |  |  |  | DNP | 513 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1612BUS | #2BUS |  | VUA | [14 empty] | 0625 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | D05/161/2BUS/BUS_VUA |  |  |  | DNP | 514 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1612BUS | #2BUS |  | 87A | [14 empty] | 0069 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | D05/161/2BUS/87A |  |  |  | DNP | 515 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1613BUS | #3BUS |  | VUA | [14 empty] | 0628 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.161#3BUS_VUA | 161KV #3BUS 衡相RY | BUS | D05/161/3BUS/BUS_VUA |  |  |  | DNP | 516 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1613BUS | #3BUS |  | 87A | [14 empty] | 0071 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.161#3BUS_87A | 161KV #3BUS 87RY | BUS | D05/161/3BUS/87A |  |  |  | DNP | 517 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1614BUS | #4BUS |  | VUA | [14 empty] | 0629 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.161#4BUS_VUA | 161KV #4BUS 衡相RY | BUS | D05/161/4BUS/BUS_VUA |  |  |  | DNP | 518 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1614BUS | #4BUS |  | 87A | [14 empty] | 0072 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.161#4BUS_87A | 161KV #4BUS 87RY | BUS | D05/161/4BUS/87A |  |  |  | DNP | 519 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 11_ | 11/ |  | CBA | [14 empty] | 0636 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | D05/22/ComPoint/FDR_CBA |  |  |  | DNP | 520 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 11_ | 11/ |  | CBF | [14 empty] | 0637 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | D05/22/ComPoint/FDR_CBF |  |  |  | DNP | 521 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV |  |  |  | CBA | [14 empty] | 0634 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.161KV_CBA | 161KV斷路器重故障 | OTHER | D05/161/ComPoint/CBA |  |  |  | DNP | 522 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV |  |  |  | CBF | [14 empty] | 0635 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | D05/161/ComPoint/CBF |  |  |  | DNP | 523 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | LINE | LINE |  | RCA | [14 empty] | 0122 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | D05/161/ComPoint/RCA |  |  |  | DNP | 524 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | _SC | 11/ SC |  | 60A | [14 empty] | 0633 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.23KV_SC_60A | 11/23KV SC 60A | OTHER | D05/22/ComPoint/FDR_60A |  |  |  | DNP | 525 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | TEST | TEST |  | CB | [14 empty] | 0512 |  | 0000 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.TEST_CB | TEST CB | OTHER | D05/0/RTU/Test_CB |  |  |  | DNP | 526 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  |  |  |  | Fire1 | [14 empty] | 0621 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | D05/0/StaDev/Fire1 |  |  |  | DNP | 527 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  |  |  |  | 25PFA | [14 empty] | 0861 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER | D05/0/ComPoint/25PFA |  |  |  | DNP | 528 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  |  |  |  | 25TA | [14 empty] | 0860 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | D05/0/ComPoint/25TA |  |  |  | DNP | 529 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  |  |  |  | ACB1 | [14 empty] | 0615 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | D05/0/StaDev/ACB1 |  |  |  | DNP | 530 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ON/OFF | ON
D05 | 道爺DS | 0 |  |  |  |  | ACB2 | [14 empty] | 0616 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | D05/0/StaDev/ACB2 |  |  |  | DNP | 531 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ON/OFF | ON
D05 | 道爺DS | 0 |  |  |  |  | ACBA | [14 empty] | 0612 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.所內電源ACBA | 所內電源故障警報 | OTHER | D05/0/StaDev/ACBA |  |  |  | DNP | 532 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 所內電源開關ACB | 所內電源開關ACB |  | ACBT | [14 empty] | 0617 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | D05/0/StaDev/ACBT |  |  |  | DNP | 533 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ON/OFF | OFF
D05 | 道爺DS | 0 |  |  |  |  | STUV | [14 empty] | 0613 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | D05/0/StaDev/STUV |  |  |  | DNP | 534 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  |  |  |  | CHG1 | [14 empty] | 0610 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.直流充電機故障 | 直流充電機故障 | OTHER | D05/0/StaDev/CHG1 |  |  |  | DNP | 535 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  |  |  |  | DCA | [14 empty] | 0608 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.直流電源DCA | 直流電源故障警報 | OTHER | D05/0/StaDev/DCA |  |  |  | DNP | 536 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  |  |  |  | DCE | [14 empty] | 0609 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.直流電源DCE | 直流電源接地故障警報 | OTHER | D05/0/StaDev/DCE |  |  |  | DNP | 537 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  |  |  |  | CHG2 | [14 empty] | 0611 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | D05/0/StaDev/CHG2 |  |  |  | DNP | 538 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  |  |  |  | CommACF | [14 empty] | 0768 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | D05/0/StaDev/CommACF |  |  |  | DNP | 539 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  |  |  |  | Burglar1 | [14 empty] | 0773 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | D05/0/StaDev/Burglar1 |  |  |  | DNP | 540 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  |  |  |  | Door1 | [14 empty] | 0774 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.無人化門禁(1) | 無人化門禁(1)建築物 | OTHER | D05/0/StaDev/Door1 |  |  |  | DNP | 541 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  |  |  |  | Door2 | [14 empty] | 0775 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.無人化門禁(2) | 無人化門禁(2)大門 | OTHER | D05/0/StaDev/Door2 |  |  |  | DNP | 542 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  |  |  |  | Lights1 | [14 empty] | 0638 |  | 0107 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.開關場照明(A) | 景觀照明 | OTHER | D05/0/StaDev/Lights1 |  |  |  | DNP | 543 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ON/OFF | OFF
D05 | 道爺DS | 0 |  |  |  |  | Lights2 | [14 empty] | 0639 |  | 0108 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.開關場照明(B) | 路燈照明 | OTHER | D05/0/StaDev/Lights2 |  |  |  | DNP | 544 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ON/OFF | OFF
D05 | 道爺DS | 22 | 22kV | 11_ | 11/ |  | LOA | [14 empty] | 0126 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.11/23KV_LOA | 11/23KV饋線復閉失敗閉鎖 | OTHER | D05/0/ComPoint/LOA |  |  |  | DNP | 545 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 11_ | 11/饋線 |  | RCA | [14 empty] | 0123 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.11/23KV_RCA | 11/23KV饋線 79RY(復閉)動作 | OTHER | D05/22/ComPoint/RCA |  |  |  | DNP | 546 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 1530 | 南科道爺三路(1530) |  | 87CFA | [14 empty] | 0587 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.1530_87CFA | 南科道爺三路(1530)87RY通訊故障 | OTHER | D05/161/1530/87CFA |  |  |  | DNP | 547 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 1530 | 南科道爺三路(1530) |  | DTTA | [14 empty] | 0129 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.1530_DTTA | 南科道爺三路(1530) 遠方遙跳 | OTHER | D05/161/1530/DTTA |  |  |  | DNP | 548 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 1530 | 南科道爺三路(1530) |  | RYFA | [14 empty] | 0586 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.1530_RYFA | 南科道爺三路(1530)數位電驛故障 | OTHER | D05/161/1530/RYFA |  |  |  | DNP | 549 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 1540 | 南科道爺四路(1540) |  | 87CFA | [14 empty] | 0589 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.1540_87CFA | 南科道爺四路(1540)87RY通訊故障 | OTHER | D05/161/1540/87CFA |  |  |  | DNP | 550 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 1540 | 南科道爺四路(1540) |  | DTTA | [14 empty] | 0130 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.1540_DTTA | 南科道爺四路(1540) 遠方遙跳 | OTHER | D05/161/1540/DTTA |  |  |  | DNP | 551 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 1540 | 南科道爺四路(1540) |  | RYFA | [14 empty] | 0588 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.1540_RYFA | 南科道爺四路(1540)數位電驛故障 | OTHER | D05/161/1540/RYFA |  |  |  | DNP | 552 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 1550 | 道爺奇晶七紅線(1550) |  | 87CFA | [14 empty] | 0591 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.1550_87CFA | 道爺奇晶七紅線(1550)RY通訊故障 | OTHER | D05/161/1550/87CFA |  |  |  | DNP | 553 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 1550 | 道爺奇晶七紅線(1550) |  | RYFA | [14 empty] | 0590 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.1550_RYFA | 道爺奇晶七紅線(1550)數位RY故障 | OTHER | D05/161/1550/RYFA |  |  |  | DNP | 554 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 1560 | 道爺奇晶七白線(1560) |  | 87CFA | [14 empty] | 0593 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.1560_87CFA | 道爺奇晶七白線(1560)RY通訊故障 | OTHER | D05/161/1560/87CFA |  |  |  | DNP | 555 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 1560 | 道爺奇晶七白線(1560) |  | RYFA | [14 empty] | 0592 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.1560_RYFA | 道爺奇晶七白線(1560)數位RY故障 | OTHER | D05/161/1560/RYFA |  |  |  | DNP | 556 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 1570 | 道爺奇晶六紅線(1570) |  | 87CFA | [14 empty] | 0595 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.1570_87CFA | 道爺奇晶六紅線(1570)RY通訊故障 | OTHER | D05/161/1570/87CFA |  |  |  | DNP | 557 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 1570 | 道爺奇晶六紅線(1570) |  | RYFA | [14 empty] | 0594 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.1570_RYFA | 道爺奇晶六紅線(1570)數位RY故障 | OTHER | D05/161/1570/RYFA |  |  |  | DNP | 558 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 1580 | 道爺奇晶六白線(1580) |  | 87CFA | [14 empty] | 0597 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.1580_87CFA | 道爺奇晶六白線(1580)RY通訊故障 | OTHER | D05/161/1580/87CFA |  |  |  | DNP | 559 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 1580 | 道爺奇晶六白線(1580) |  | RYFA | [14 empty] | 0596 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.1580_RYFA | 道爺奇晶六白線(1580)數位RY故障 | OTHER | D05/161/1580/RYFA |  |  |  | DNP | 560 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1611BUS | #1BUS |  | 87UL | [14 empty] | 0554 |  | 0248 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | D05/161/1BUS/87UL |  |  |  | DNP | 561 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1612BUS | #2BUS |  | 87UL | [14 empty] | 0555 |  | 0249 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | D05/161/2BUS/87UL |  |  |  | DNP | 562 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1613BUS | #3BUS |  | 87UL | [14 empty] | 0557 |  | 0250 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.161#3BUS_87UL | 161KV #3BUS 87RY U/L | OTHER | D05/161/3BUS/87UL |  |  |  | DNP | 563 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1614BUS | #4BUS |  | 87UL | [14 empty] | 0558 |  | 0251 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.161#4BUS_87UL | 161KV #4BUS 87RY U/L | OTHER | D05/161/4BUS/87UL |  |  |  | DNP | 564 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 0 |  | 1610 | 道爺安南新化線(1610) |  | 87CFA | [14 empty] | 0599 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.1610_87CFA | 道爺安南新化線(1610)RY通訊故障 | OTHER | D05/161/1610/87CFA |  |  |  | DNP | 565 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 1610 | 道爺安南新化線(1610) |  | RYFA | [14 empty] | 0598 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.1610_RYFA | 道爺安南新化線(1610)數位RY故障 | OTHER | D05/161/1610/RYFA |  |  |  | DNP | 566 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV |  |  |  | OSCA | [14 empty] | 0124 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.161KV_OSCA | 161KV示波器啟動警報 | OTHER | D05/161/ComPoint/OSCA |  |  |  | DNP | 567 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 1620 | 道爺和順新化線(1620) |  | 87CFA | [14 empty] | 0601 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.1620_87CFA | 道爺和順新化線(1620)RY通訊故障 | OTHER | D05/161/1620/87CFA |  |  |  | DNP | 568 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 1620 | 道爺和順新化線(1620) |  | RYFA | [14 empty] | 0600 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.1620_RYFA | 道爺和順新化線(1620)數位RY故障 | OTHER | D05/161/1620/RYFA |  |  |  | DNP | 569 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 330 | #2DTR(330) |  | 81A | [14 empty] | 0308 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.330_81A | 330 #2DTR(A) 81RY動作 | OTHER | D05/22/330/81AS |  |  |  | DNP | 570 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 330 | #2DTR(330) |  | 81UL | [14 empty] | 0870 |  | 0242 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.330_81UL | 330 #2DTR(A) 81RY U/L | OTHER | D05/22/330/81UL |  |  |  | DNP | 571 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 0 |  | 330 | #2DTR(330) |  | GDA | [14 empty] | 0094 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.330_GDA | 330開關箱IED RY GDA | OTHER | D05/22/330/GDA |  |  |  | DNP | 572 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 340 | #2DTR(340) |  | 81A | [14 empty] | 0309 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.340_81A | 340 #2DTR(B) 81RY動作 | OTHER | D05/22/340/81AS |  |  |  | DNP | 573 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 340 | #2DTR(340) |  | 81UL | [14 empty] | 0871 |  | 0243 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.340_81UL | 340 #2DTR(B) 81RY U/L | OTHER | D05/22/340/81UL |  |  |  | DNP | 574 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 0 |  | 340 | #2DTR(340) |  | GDA | [14 empty] | 0097 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.340_GDA | 340開關箱IED RY GDA | OTHER | D05/22/340/GDA |  |  |  | DNP | 575 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 350 | #3DTR(350) |  | 81A | [14 empty] | 0310 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.350_81A | 350 #3DTR(A) 81RY動作 | OTHER | D05/22/350/81AS |  |  |  | DNP | 576 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 350 | #3DTR(350) |  | 81UL | [14 empty] | 0872 |  | 0244 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.350_81UL | 350 #3DTR(A) 81RY U/L | OTHER | D05/22/350/81UL |  |  |  | DNP | 577 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 0 |  | 350 | #3DTR(350) |  | GDA | [14 empty] | 0106 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.350_GDA | 350開關箱IED RY GDA | OTHER | D05/22/350/GDA |  |  |  | DNP | 578 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 360 | #3DTR(360) |  | 81A | [14 empty] | 0311 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.360_81A | 360 #3DTR(B) 81RY動作 | OTHER | D05/22/360/81AS |  |  |  | DNP | 579 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 360 | #3DTR(360) |  | 81UL | [14 empty] | 0873 |  | 0245 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.360_81UL | 360 #3DTR(B) 81RY U/L | OTHER | D05/22/360/81UL |  |  |  | DNP | 580 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 0 |  | 360 | #3DTR(360) |  | GDA | [14 empty] | 0109 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.360_GDA | 360開關箱IED RY GDA | OTHER | D05/22/360/GDA |  |  |  | DNP | 581 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  |  |  |  | COMMA | [14 empty] | 0862 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.COMMA | 通訊處理單元A(COMMA)故障 | OTHER | D05/0/StaDev/5A5Other |  |  |  | DNP | 582 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  |  |  |  | COMMB | [14 empty] | 0863 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.COMMB | 通訊處理單元B(COMMB)故障 | OTHER | D05/0/StaDev/6A5Other |  |  |  | DNP | 583 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | COMM | 通訊處理單元 |  | SupLocal | [14 empty] | 0513 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.COMM_S/L | 通訊處理單元 SUPY/LOCAL | OTHER | D05/0/RTU/RTU_R_L |  |  |  | DNP | 584 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D05 | 道爺DS | 0 |  |  |  |  | DTU_FA | [14 empty] | 0619 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.DTUA | DTU故障警報 | OTHER | D05/0/RTU/RTU_COM |  |  |  | DNP | 585 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | SCADA | SCADA |  | UPS | [14 empty] | 0614 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.SCADA_UPS | SCADA UPS故障 | OTHER | D05/0/StaDev/UPSA |  |  |  | DNP | 586 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  |  |  |  | SUPA | [14 empty] | 0618 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.SUPA | 變電所SCADA故障 | OTHER | D05/0/StaDev/SCADAA |  |  |  | DNP | 587 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  |  |  |  | TCA | [14 empty] | 0632 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.TCA | 斷路器跳脫回路故障 | OTHER | D05/0/StaDev/4A5Other |  |  |  | DNP | 588 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  |  |  |  | 水位警報(1) | [14 empty] | 0604 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.水位警報(1) | 地下室水位警報(1) | OTHER | D05/0/StaDev/Water1 |  |  |  | DNP | 589 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  |  |  |  | 水位警報(2) | [14 empty] | 0605 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.水位警報(2) | 地下室水位警報(2) | OTHER | D05/0/StaDev/Water2 |  |  |  | DNP | 590 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  |  |  |  | 涵洞排水泵 | [14 empty] | 0620 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.涵洞排水泵 | 涵洞排水泵故障 | OTHER | D05/0/StaDev/1A5Other |  |  |  | DNP | 591 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  |  |  |  | 通信機房溫度 | [14 empty] | 0772 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.通信機房溫度 | 通訊室或控制室溫度警報 | OTHER | D05/0/StaDev/R_Temp |  |  |  | DNP | 592 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  |  |  |  | 揚水泵 | [14 empty] | 0622 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.揚水泵 | 揚水泵故障 | OTHER | D05/0/StaDev/2A5Other |  |  |  | DNP | 593 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  |  |  |  | 集油池警報(1) | [14 empty] | 0606 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.集油池警報(1) | 集油池水位(中)警報 | OTHER | D05/0/StaDev/OilLeak1 |  |  |  | DNP | 594 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  |  |  |  | 集油池警報(2) | [14 empty] | 0607 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.集油池警報(2) | 集油池水位(高)警報 | OTHER | D05/0/StaDev/OilLeak2 |  |  |  | DNP | 595 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺奇晶七紅線(1550) |  | 87A1 | [14 empty] | 0021 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1550_87A1 | 奇晶七紅線(1550) #1 87RY | LINE161 | D05/161/1550/87A1 |  |  |  | DNP | 596 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺奇晶七紅線(1550) |  | 1_87UL2 | [14 empty] | 0527 |  | 0095 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1550_87UL2 | 奇晶七紅線(1550) #2 87RY U/L | LINE161 | D05/161/1550/1_87UL2 |  |  |  | DNP | 597 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺奇晶七紅線(1550) |  | 1_87UL1 | [14 empty] | 0526 |  | 0083 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1550_87UL1 | 奇晶七紅線(1550) #1 87RY U/L | LINE161 | D05/161/1550/1_87UL1 |  |  |  | DNP | 598 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺奇晶七紅線(1550) |  | 87A2 | [14 empty] | 0022 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1550_87A2 | 奇晶七紅線(1550) #2 87RY | LINE161 | D05/161/1550/87A2 |  |  |  | DNP | 599 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺奇晶七白線(1560) |  | 87A1 | [14 empty] | 0026 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1560_87A1 | 奇晶七白線(1560) #1 87RY | LINE161 | D05/161/1560/87A1 |  |  |  | DNP | 600 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺奇晶七白線(1560) |  | 1_87UL2 | [14 empty] | 0530 |  | 0096 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1560_87UL2 | 奇晶七白線(1560) #2 87RY U/L | LINE161 | D05/161/1560/1_87UL2 |  |  |  | DNP | 601 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺奇晶七白線(1560) |  | 1_87UL1 | [14 empty] | 0529 |  | 0085 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1560_87UL1 | 奇晶七白線(1560) #1 87RY U/L | LINE161 | D05/161/1560/1_87UL1 |  |  |  | DNP | 602 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺奇晶七白線(1560) |  | 87A2 | [14 empty] | 0027 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1560_87A2 | 奇晶七白線(1560) #2 87RY | LINE161 | D05/161/1560/87A2 |  |  |  | DNP | 603 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺奇晶六紅線(1570) |  | 87A1 | [14 empty] | 0031 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1570_87A1 | 奇晶六紅線(1570) #1 87RY | LINE161 | D05/161/1570/87A1 |  |  |  | DNP | 604 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺奇晶六紅線(1570) |  | 1_87UL2 | [14 empty] | 0533 |  | 0097 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1570_87UL2 | 奇晶六紅線(1570) #2 87RY U/L | LINE161 | D05/161/1570/1_87UL2 |  |  |  | DNP | 605 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺奇晶六紅線(1570) |  | 1_87UL1 | [14 empty] | 0532 |  | 0087 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1570_87UL1 | 奇晶六紅線(1570) #1 87RY U/L | LINE161 | D05/161/1570/1_87UL1 |  |  |  | DNP | 606 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺奇晶六紅線(1570) |  | 87A2 | [14 empty] | 0032 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1570_87A2 | 奇晶六紅線(1570) #2 87RY | LINE161 | D05/161/1570/87A2 |  |  |  | DNP | 607 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺奇晶六白線(1580) |  | 87A1 | [14 empty] | 0036 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1580_87A1 | 奇晶六白線(1580) #1 87RY | LINE161 | D05/161/1580/87A1 |  |  |  | DNP | 608 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺奇晶六白線(1580) |  | 1_87UL2 | [14 empty] | 0536 |  | 0098 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1580_87UL2 | 奇晶六白線(1580) #2 87RY U/L | LINE161 | D05/161/1580/1_87UL2 |  |  |  | DNP | 609 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺奇晶六白線(1580) |  | 1_87UL1 | [14 empty] | 0535 |  | 0089 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1580_87UL1 | 奇晶六白線(1580) #1 87RY U/L | LINE161 | D05/161/1580/1_87UL1 |  |  |  | DNP | 610 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺奇晶六白線(1580) |  | 87A2 | [14 empty] | 0037 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1580_87A2 | 奇晶六白線(1580) #2 87RY | LINE161 | D05/161/1580/87A2 |  |  |  | DNP | 611 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  |  |  |  | MCC | [14 empty] | 0581 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.MCC故障 | MCC電驛故障 | OTHER | D05/0/StaDev/PMCC |  |  |  | DNP | 612 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  |  |  |  | PMCC | [14 empty] | 0580 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.PMCC故障 | PMCC電驛故障 | OTHER | D05/0/StaDev/MCC |  |  |  | DNP | 613 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 2DTR | #2DTR |  | 50_51NUL | [14 empty] | 0878 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#2DTR_50/51NUL | #2DTR 50/50N/51/51N RY U/L | OTHER | D05//2DTR/51_UL |  |  |  | DNP | 614 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 0 |  | 2DTR | #2DTR |  | 51Z_UL | [14 empty] | 0879 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#2DTR_51ZUL | #2DTR 51Z RY U/L | OTHER | D05//2DTR/51Z_UL |  |  |  | DNP | 615 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 0 |  | 2DTR | #2DTR |  | DTR_86A | [14 empty] | 0091 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#2DTR_86A | #2DTR 86(50/50N/51Z/87/96)RY | OTHER | D05//2DTR/DTR_86A |  |  |  | DNP | 616 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 2DTR | #2DTR |  | RYFA | [14 empty] | 0090 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#2DTR_RYFA | #2DTR 數位電驛故障 | OTHER | D05//2DTR/RYFA |  |  |  | DNP | 617 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 3DTR | #3DTR |  | 50_51NUL | [14 empty] | 0880 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#3DTR_50/51NUL | #3DTR 50/50N/51/51N RY U/L | OTHER | D05//3DTR/51_UL |  |  |  | DNP | 618 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 0 |  | 3DTR | #3DTR |  | 51Z_UL | [14 empty] | 0881 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#3DTR_51ZUL | #3DTR 51Z RY U/L | OTHER | D05//3DTR/51Z_UL |  |  |  | DNP | 619 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 0 |  | 3DTR | #3DTR |  | DTR_86A | [14 empty] | 0103 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#3DTR_86A | #3DTR 86(50/50N/51Z/87/96)RY | OTHER | D05//3DTR/DTR_86A |  |  |  | DNP | 620 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 3DTR | #3DTR |  | RYFA | [14 empty] | 0102 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#3DTR_RYFA | #3DTR 數位電驛故障 | OTHER | D05//3DTR/RYFA |  |  |  | DNP | 621 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  |  |  |  | DTUCFA | [14 empty] | 0627 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.DTUCFA | DTU通訊故障 | OTHER | D05/0/StaDev/3A5Other |  |  |  | DNP | 622 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | LOCAL | LOCAL |  | GPSA | [14 empty] | 0626 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.GPSA | LOCAL GPS故障 | OTHER | D05/0/StaDev/GPSA |  |  |  | DNP | 623 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV |  |  |  | OSCF | [14 empty] | 0125 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | D05/161/ComPoint/OSCF |  |  |  | DNP | 624 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | BVS | #12BUS |  | RY | [14 empty] | 0623 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.BVS_RY | 161KV #12BUS GRZ100 RY U/L | OTHER | D05/0/ComPoint/GRZ100 |  |  |  | DNP | 625 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | LOCK/USE | USE
D05 | 道爺DS | 161 | 161kV | 1510 | 南科道爺ㄧ路(1510) |  | PHA | [14 empty] | 0003 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1510_PHA | 南科道爺ㄧ路(1510) 相間RY | LINE161 | D05/161/1510/PHA |  |  |  | DNP | 626 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1510 | 南科道爺ㄧ路(1510) |  | GDA | [14 empty] | 0004 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1510_GDA | 南科道爺ㄧ路(1510) 接地RY | LINE161 | D05/161/1510/GDA |  |  |  | DNP | 627 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1510 | 南科道爺ㄧ路(1510) |  | 87A | [14 empty] | 0001 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1510_87A | 南科道爺ㄧ路(1510) 87RY | LINE161 | D05/161/1510/87A |  |  |  | DNP | 628 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1510 | 南科道爺ㄧ路(1510) |  | 87UL | [14 empty] | 0514 |  | 0075 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1510_87UL | 南科道爺ㄧ路(1510) 87RY U/L | LINE161 | D05/161/1510/87UL |  |  |  | DNP | 629 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1510 | 南科道爺ㄧ路(1510) |  | CB | [14 empty] | 0000 |  | 0001 | [8 empty] | 161KV_S | [8 empty] | 道爺DS.1510_CB | 1510(南科道爺ㄧ路) CB | LINE161 | D05/161/1510/CB |  |  |  | DNP | 630 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 161 | 161kV | 1510 | 南科道爺ㄧ路(1510) |  | 79UL | [14 empty] | 0516 |  | 0076 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1510_79UL | 南科道爺ㄧ路(1510) 79RY U/L | LINE161 | D05/161/1510/79UL |  |  |  | DNP | 631 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1510 | 南科道爺ㄧ路(1510) |  | DS1 | 1511 | [13 empty] | 0640 | 641 | 0112 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1511_DS | 1511(南科道爺ㄧ路) DS | LINE161 | D05/161/1510/DS1 |  |  |  | DNP | 632 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1510 | 南科道爺ㄧ路(1510) |  | DS2 | 1512 | [13 empty] | 0642 | 643 | 0113 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1512_DS | 1512(南科道爺ㄧ路) DS | LINE161 | D05/161/1510/DS2 |  |  |  | DNP | 633 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1510 | 南科道爺ㄧ路(1510) |  | DS3 | 1513 | [13 empty] | 0644 | 645 | 0114 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1513_DS | 1513(南科道爺ㄧ路) DS | LINE161 | D05/161/1510/DS3 |  |  |  | DNP | 634 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1510 | 南科道爺ㄧ路(1510) |  | E3 | 1513E | [13 empty] | 0646 | 647 | 0115 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1513E_ES | 1513E(南科道爺ㄧ路) ES | LINE161 | D05/161/1510/ES3 |  |  |  | DNP | 635 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1520 | 南科道爺二路(1520) |  | PHA | [14 empty] | 0008 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1520_PHA | 南科道爺二路(1520) 相間RY | LINE161 | D05/161/1520/PHA |  |  |  | DNP | 636 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1520 | 南科道爺二路(1520) |  | GDA | [14 empty] | 0009 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1520_GDA | 南科道爺二路(1520) 接地RY | LINE161 | D05/161/1520/GDA |  |  |  | DNP | 637 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1520 | 南科道爺二路(1520) |  | 87A | [14 empty] | 0006 | [10 empty] | 161KV_S | [8 empty] | 道爺DS.1520_87A | 南科道爺二路(1520) 87RY | LINE161 | D05/161/1520/87A |  |  |  | DNP | 638 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | 1520 | 南科道爺二路(1520) |  | 87UL | [14 empty] | 0517 |  | 0077 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1520_87UL | 南科道爺二路(1520) 87RY U/L | LINE161 | D05/161/1520/87UL |  |  |  | DNP | 639 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1520 | 南科道爺二路(1520) |  | CB | [14 empty] | 0005 |  | 0002 | [8 empty] | 161KV_S | [8 empty] | 道爺DS.1520_CB | 1520(南科道爺二路) CB | LINE161 | D05/161/1520/CB |  |  |  | DNP | 640 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 161 | 161kV | 1520 | 南科道爺二路(1520) |  | 79UL | [14 empty] | 0519 |  | 0078 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1520_79UL | 南科道爺二路(1520) 79RY U/L | LINE161 | D05/161/1520/79UL |  |  |  | DNP | 641 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | USE/LOCK | USE
D05 | 道爺DS | 161 | 161kV | 1520 | 南科道爺二路(1520) |  | DS1 | 1521 | [13 empty] | 0648 | 649 | 0116 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1521_DS | 1521(南科道爺二路) DS | LINE161 | D05/161/1520/DS1 |  |  |  | DNP | 642 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 161 | 161kV | 1520 | 南科道爺二路(1520) |  | DS2 | 1522 | [13 empty] | 0650 | 651 | 0117 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1522_DS | 1522(南科道爺二路) DS | LINE161 | D05/161/1520/DS2 |  |  |  | DNP | 643 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1520 | 南科道爺二路(1520) |  | DS3 | 1523 | [13 empty] | 0652 | 653 | 0118 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1523_DS | 1523(南科道爺二路) DS | LINE161 | D05/161/1520/DS3 |  |  |  | DNP | 644 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 161 | 161kV | 1520 | 南科道爺二路(1520) |  | E3 | 1523E | [13 empty] | 0654 | 655 | 0119 | [8 empty] | ADCS_S | [8 empty] | 道爺DS.1523E_ES | 1523E(南科道爺二路) ES | LINE161 | D05/161/1520/ES3 |  |  |  | DNP | 645 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D05 | 道爺DS | 0 |  | 1510 | 南科道爺ㄧ路(1510) |  | 87CFA | [14 empty] | 0583 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.1510_87CFA | 南科道爺ㄧ路(1510)87RY通訊故障 | OTHER | D05/161/1510/87CFA |  |  |  | DNP | 646 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 1510 | 南科道爺ㄧ路(1510) |  | DTTA | [14 empty] | 0127 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.1510_DTTA | 南科道爺ㄧ路(1510) 遠方遙跳 | OTHER | D05/161/1510/DTTA |  |  |  | DNP | 647 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 1510 | 南科道爺ㄧ路(1510) |  | RYFA | [14 empty] | 0582 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.1510_RYFA | 南科道爺ㄧ路(1510)數位電驛故障 | OTHER | D05/161/1510/RYFA |  |  |  | DNP | 648 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 1520 | 南科道爺二路(1520) |  | 87CFA | [14 empty] | 0585 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.1520_87CFA | 南科道爺二路(1520)87RY通訊故障 | OTHER | D05/161/1520/87CFA |  |  |  | DNP | 649 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 1520 | 南科道爺二路(1520) |  | DTTA | [14 empty] | 0128 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.1520_DTTA | 南科道爺二路(1520) 遠方遙跳 | OTHER | D05/161/1520/DTTA |  |  |  | DNP | 650 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 1520 | 南科道爺二路(1520) |  | RYFA | [14 empty] | 0584 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.1520_RYFA | 南科道爺二路(1520)數位電驛故障 | OTHER | D05/161/1520/RYFA |  |  |  | DNP | 651 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  |  |  |  | GEN | [14 empty] | 0884 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.GEN | 緊急發電機運轉 | OTHER | D05/0/StaDev/7A5Other |  |  |  | DNP | 652 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ON/OFF | OFF
D05 | 道爺DS | 0 |  | 1DTR | #1DTR |  | GDA | [14 empty] | 0140 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#1DTR_GDA | #1DTR 50N/51N RY | OTHER | D05//1DTR/GDA |  |  |  | DNP | 653 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 1DTR | #1DTR |  | PHA | [14 empty] | 0139 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#1DTR_PHA | #1DTR 50/51 RY | OTHER | D05//1DTR/PHA |  |  |  | DNP | 654 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 2DTR | #2DTR |  | GDA | [14 empty] | 0142 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#2DTR_GDA | #2DTR 50N/51N RY | OTHER | D05//2DTR/GDA |  |  |  | DNP | 655 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 2DTR | #2DTR |  | PHA | [14 empty] | 0141 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#2DTR_PHA | #2DTR 50/51 RY | OTHER | D05//2DTR/PHA |  |  |  | DNP | 656 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 3DTR | #3DTR |  | GDA | [14 empty] | 0144 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#3DTR_GDA | #3DTR 50N/51N RY | OTHER | D05//3DTR/GDA |  |  |  | DNP | 657 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 3DTR | #3DTR |  | PHA | [14 empty] | 0143 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#3DTR_PHA | #3DTR 50/51 RY | OTHER | D05//3DTR/PHA |  |  |  | DNP | 658 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 4DTR | #4DTR |  | GDA | [14 empty] | 0146 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#4DTR_GDA | #4DTR 50N/51N RY | OTHER | D05//4DTR/GDA |  |  |  | DNP | 659 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | 4DTR | #4DTR |  | PHA | [14 empty] | 0145 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.#4DTR_PHA | #4DTR 50/51 RY | OTHER | D05//4DTR/PHA |  |  |  | DNP | 660 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | BUS | #12BUS |  | CTFA1 | [14 empty] | 0552 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.161KVBUS_CTFA1 | 161KV #12BUS CT回路故障 | OTHER | D05/161/ComPoint/87CTFA1 |  |  |  | DNP | 661 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | BUS | #34BUS |  | CTFA2 | [14 empty] | 0553 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.161KVBUS_CTFA2 | 161KV #34BUS CT回路故障 | OTHER | D05/161/ComPoint/87CTFA2 |  |  |  | DNP | 662 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | BUS | #12BUS |  | RYFA1 | [14 empty] | 0556 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.161KVBUS_RYFA1 | 161KV #12BUS 數位電驛故障 | OTHER | D05/161/ComPoint/12B_87UL |  |  |  | DNP | 663 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 161 | 161kV | BUS | #34BUS |  | RYFA2 | [14 empty] | 0559 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.161KVBUS_RYFA2 | 161KV #34BUS 數位電驛故障 | OTHER | D05/161/ComPoint/34B_87UL |  |  |  | DNP | 664 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | OLTC | OLTC |  | OLTCA | [14 empty] | 0602 | [10 empty] | ADCS_S | [8 empty] | 道爺DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | D05/0/ComPoint/OLTC_A |  |  |  | DNP | 665 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | CHILIN | 奇菱樹谷光電 |  | 27A | [14 empty] | 0333 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.CHILIN_27A | 奇菱樹谷光電 27A | OTHER |  |  |  |  | DNP | 666 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | CHILIN | 奇菱樹谷光電 |  | 59A | [14 empty] | 0334 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.CHILIN_59A | 奇菱樹谷光電 59A | OTHER |  |  |  |  | DNP | 667 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | CHILIN | 奇菱樹谷光電 |  | 59V0 | [14 empty] | 0335 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.CHILIN_59V0 | 奇菱樹谷光電 59V0 | OTHER |  |  |  |  | DNP | 668 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | CHILIN | 奇菱樹谷光電 |  | 81A | [14 empty] | 0336 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.CHILIN_81A | 奇菱樹谷光電 81A | OTHER |  |  |  |  | DNP | 669 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | CHILIN | 奇菱樹谷光電 |  | CB | [14 empty] | 0330 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.CHILIN_CB | 奇菱樹谷光電 CB | OTHER |  |  |  |  | DNP | 670 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | CHILIN | 奇菱樹谷光電 |  | DS1 | CHILIN | [13 empty] | 0936 | 937 | [9 empty] | DDCS4_1 | [8 empty] | 道爺DS.CHILIN_DS | 奇菱樹谷光電 DS | FEEDER |  |  |  |  | DNP | 671 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 0 |  | CHILIN | 奇菱樹谷光電 |  | GDA | [14 empty] | 0332 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.CHILIN_GDA | 奇菱樹谷光電 GDA | OTHER |  |  |  |  | DNP | 672 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 0 |  | CHILIN | 奇菱樹谷光電 |  | PHA | [14 empty] | 0331 | [10 empty] | DDCS4_1 | [8 empty] | 道爺DS.CHILIN_PHA | 奇菱樹谷光電 PHA | OTHER |  |  |  |  | DNP | 673 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | PV崇越和鑫 | 崇越和鑫(4K67) |  | DS1 | PV崇越和鑫 | [13 empty] | 0938 | 939 | [9 empty] | DDCS4_2 | [8 empty] | 道爺DS.PV崇越和鑫_DS | 23KV崇越和鑫(4K67) DS | OTHER |  |  |  |  | DNP | 674 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 22 | 22kV | PV崇越和鑫 | 崇越和鑫(4K67) |  | 27A | [14 empty] | 0340 | [10 empty] | DDCS4_2 | [8 empty] | 道爺DS.PV崇越和鑫_27A | 23KV崇越和鑫(4K67) 27A | OTHER |  |  |  |  | DNP | 675 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | PV崇越和鑫 | 崇越和鑫(4K67) |  | 59A | [14 empty] | 0341 | [10 empty] | DDCS4_2 | [8 empty] | 道爺DS.PV崇越和鑫_59A | 23KV崇越和鑫(4K67) 59A | OTHER |  |  |  |  | DNP | 676 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 崇越和鑫(4K67) | 崇越和鑫(4K67) |  | PV崇越和鑫59V0 | [14 empty] | 0342 | [10 empty] | DDCS4_2 | [8 empty] | 道爺DS.PV崇越和鑫59V0 | 23KV崇越和鑫(4K67) 59V0 | OTHER |  |  |  |  | DNP | 677 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | PV崇越和鑫 | 崇越和鑫(4K67) |  | 81A | [14 empty] | 0343 | [10 empty] | DDCS4_2 | [8 empty] | 道爺DS.PV崇越和鑫_81A | 23KV崇越和鑫(4K67) 81A | OTHER |  |  |  |  | DNP | 678 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | PV崇越和鑫 | 崇越和鑫(4K67) |  | CB | [14 empty] | 0337 | [10 empty] | DDCS4_2 | [8 empty] | 道爺DS.PV崇越和鑫_CB | 23KV崇越和鑫(4K67) CB | OTHER |  |  |  |  | DNP | 679 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 22 | 22kV | 崇越和鑫 | 崇越和鑫(4K67) |  | GDA | [14 empty] | 0339 | [10 empty] | DDCS4_2 | [8 empty] | 道爺DS.崇越和鑫_GDA | 23KV崇越和鑫(4K67) GDA | OTHER |  |  |  |  | DNP | 680 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 崇越和鑫 | 崇越和鑫(4K67) |  | PHA | [14 empty] | 0338 | [10 empty] | DDCS4_2 | [8 empty] | 道爺DS.崇越和鑫_PHA | 23KV崇越和鑫(4K67) PHA | OTHER |  |  |  |  | DNP | 681 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D05 | 道爺DS | 22 | 22kV | 崇越和鑫 | 崇越和鑫(4K67) |  | PTDS | [14 empty] | 0940 | 941 | [9 empty] | DDCS4_2 | [8 empty] | 道爺DS.崇越和鑫_PTDS | 23KV崇越和鑫(4K67) PTDS | OTHER |  |  |  |  | DNP | 682 | DNPDIPoint | DS056 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D05 | 道爺DS | 22 | 22kV | 230_SC | #3SC | 9 | CAP | [25 empty] | ADCS_S | [8 empty] | 道爺DS.230_SC_CAP | 23KV#3SC 容量 | SC | [5 empty] | 683 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 22 | 22kV | 240_SC | #4SC | 9 | CAP | [25 empty] | ADCS_S | [8 empty] | 道爺DS.240_SC_CAP | 23KV#4SC 容量 | SC | [5 empty] | 684 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 22 | 22kV | 250_SC | #5SC | 9 | CAP | [25 empty] | ADCS_S | [8 empty] | 道爺DS.250_SC_CAP | 23KV#5SC 容量 | SC | [5 empty] | 685 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 22 | 22kV | 260_SC | #6SC | 9 | CAP | [25 empty] | ADCS_S | [8 empty] | 道爺DS.260_SC_CAP | 23KV#6SC 容量 | SC | [5 empty] | 686 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D05 | 道爺DS | 161 | 161kV | 1530 | 南科道爺三路(1530) |  | LE0 | 1530LE | [24 empty] | ADCS_S | [8 empty] | 道爺DS.1530LE | 1530LE (非取樣點) | LINE161 | D05/161/1530/LE0 |  |  |  |  | 687 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1530 | 南科道爺三路(1530) |  | BE0 | 1530BE | [24 empty] | ADCS_S | [8 empty] | 道爺DS.1530BE | 1530BE (非取樣點) | LINE161 | D05/161/1530/BE0 |  |  |  |  | 688 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1540 | 南科道爺四路(1540) |  | LE0 | 1540LE | [24 empty] | ADCS_S | [8 empty] | 道爺DS.1540LE | 1540LE (非取樣點) | LINE161 | D05/161/1540/LE0 |  |  |  |  | 689 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1540 | 南科道爺四路(1540) |  | BE0 | 1540BE | [24 empty] | ADCS_S | [8 empty] | 道爺DS.1540BE | 1540BE (非取樣點) | LINE161 | D05/161/1540/BE0 |  |  |  |  | 690 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺奇晶七紅線(1550) |  | LE0 | 1550LE | [24 empty] | ADCS_S | [8 empty] | 道爺DS.1550LE | 1550LE (非取樣點) | LINE161 | D05/161/1550/LE0 |  |  |  |  | 691 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1550 | 道爺奇晶七紅線(1550) |  | BE0 | 1550BE | [24 empty] | ADCS_S | [8 empty] | 道爺DS.1550BE | 1550BE (非取樣點) | LINE161 | D05/161/1550/BE0 |  |  |  |  | 692 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺奇晶七白線(1560) |  | LE0 | 1560LE | [24 empty] | ADCS_S | [8 empty] | 道爺DS.1560LE | 1560LE (非取樣點) | LINE161 | D05/161/1560/LE0 |  |  |  |  | 693 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1560 | 道爺奇晶七白線(1560) |  | BE0 | 1560BE | [24 empty] | ADCS_S | [8 empty] | 道爺DS.1560BE | 1560BE (非取樣點) | LINE161 | D05/161/1560/BE0 |  |  |  |  | 694 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺奇晶六紅線(1570) |  | LE0 | 1570LE | [24 empty] | ADCS_S | [8 empty] | 道爺DS.1570LE | 1570LE (非取樣點) | LINE161 | D05/161/1570/LE0 |  |  |  |  | 695 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1570 | 道爺奇晶六紅線(1570) |  | BE0 | 1570BE | [24 empty] | ADCS_S | [8 empty] | 道爺DS.1570BE | 1570BE (非取樣點) | LINE161 | D05/161/1570/BE0 |  |  |  |  | 696 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺奇晶六白線(1580) |  | LE0 | 1580LE | [24 empty] | ADCS_S | [8 empty] | 道爺DS.1580LE | 1580LE (非取樣點) | LINE161 | D05/161/1580/LE0 |  |  |  |  | 697 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1580 | 道爺奇晶六白線(1580) |  | BE0 | 1580BE | [24 empty] | ADCS_S | [8 empty] | 道爺DS.1580BE | 1580BE (非取樣點) | LINE161 | D05/161/1580/BE0 |  |  |  |  | 698 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1610 | 道爺安南新化線(1610) |  | LE0 | 1610LE | [24 empty] | ADCS_S | [8 empty] | 道爺DS.1610LE | 1610LE (非取樣點) | LINE161 | D05/161/1610/LE0 |  |  |  |  | 699 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1610 | 道爺安南新化線(1610) |  | BE0 | 1610BE | [24 empty] | ADCS_S | [8 empty] | 道爺DS.1610BE | 1610BE (非取樣點) | LINE161 | D05/161/1610/BE0 |  |  |  |  | 700 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1620 | 道爺和順新化線(1620) |  | LE0 | 1620LE | [24 empty] | ADCS_S | [8 empty] | 道爺DS.1620LE | 1620LE (非取樣點) | LINE161 | D05/161/1620/LE0 |  |  |  |  | 701 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1620 | 道爺和順新化線(1620) |  | BE0 | 1620BE | [24 empty] | ADCS_S | [8 empty] | 道爺DS.1620BE | 1620BE (非取樣點) | LINE161 | D05/161/1620/BE0 |  |  |  |  | 702 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 4K61 | 4K61_DS |  | DS1 | 4K61_DS | [24 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K61_DS | 4K61_DS (非取樣點) | FEEDER | D05/22/4K61/DS |  |  |  |  | 703 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 4K61 | 4K61_ES |  | K610 | 4K61_ES | [24 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K61_ES | 4K61_ES (非取樣點) | FEEDER | D05/22/4K61/ES |  |  |  |  | 704 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 4K62 | 4K62_DS |  | DS1 | 4K62_DS | [24 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K62_DS | 4K62_DS (非取樣點) | FEEDER | D05/22/4K62/DS |  |  |  |  | 705 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 4K62 | 4K62_ES |  | K620 | 4K62_ES | [24 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K62_ES | 4K62_ES (非取樣點) | FEEDER | D05/22/4K62/ES |  |  |  |  | 706 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 4K63 | 4K63_DS |  | DS1 | 4K63_DS | [24 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K63_DS | 4K63_DS (非取樣點) | FEEDER | D05/22/4K63/DS |  |  |  |  | 707 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 4K63 | 4K63_ES |  | K630 | 4K63_ES | [24 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K63_ES | 4K63_ES (非取樣點) | FEEDER | D05/22/4K63/ES |  |  |  |  | 708 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 4K64 | 4K64_DS |  | DS1 | 4K64_DS | [24 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K64_DS | 4K64_DS (非取樣點) | FEEDER | D05/22/4K64/DS |  |  |  |  | 709 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 4K64 | 4K64_ES |  | K640 | 4K64_ES | [24 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K64_ES | 4K64_ES (非取樣點) | FEEDER | D05/22/4K64/ES |  |  |  |  | 710 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 4K65 | 4K65_DS |  | DS1 | 4K65_DS | [24 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K65_DS | 4K65_DS (非取樣點) | FEEDER | D05/22/4K65/DS |  |  |  |  | 711 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 4K65 | 4K65_ES |  | K650 | 4K65_ES | [24 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K65_ES | 4K65_ES (非取樣點) | FEEDER | D05/22/4K65/ES |  |  |  |  | 712 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 4K66 | 4K66_DS |  | DS1 | 4K66_DS | [24 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K66_DS | 4K66_DS (非取樣點) | FEEDER | D05/22/4K66/DS |  |  |  |  | 713 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 4K66 | 4K66_ES |  | K660 | 4K66_ES | [24 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K66_ES | 4K66_ES (非取樣點) | FEEDER | D05/22/4K66/ES |  |  |  |  | 714 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 4K67 | 4K67_DS |  | DS1 | 4K67_DS | [24 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K67_DS | 4K67_DS (非取樣點) | FEEDER | D05/22/4K67/DS |  |  |  |  | 715 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 4K67 | 4K67_ES |  | K670 | 4K67_ES | [24 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K67_ES | 4K67_ES (非取樣點) | FEEDER | D05/22/4K67/ES |  |  |  |  | 716 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 4K68 | 4K68_DS |  | DS1 | 4K68_DS | [24 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K68_DS | 4K68_DS (非取樣點) | FEEDER | D05/22/4K68/DS |  |  |  |  | 717 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 4K68 | 4K68_ES |  | K680 | 4K68_ES | [24 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K68_ES | 4K68_ES (非取樣點) | FEEDER | D05/22/4K68/ES |  |  |  |  | 718 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 4K71 | 4K71_DS |  | DS1 | 4K71_DS | [24 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K71_DS | 4K71_DS (非取樣點) | FEEDER | D05/22/4K71/DS |  |  |  |  | 719 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 4K71 | 4K71_ES |  | K710 | 4K71_ES | [24 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K71_ES | 4K71_ES (非取樣點) | FEEDER | D05/22/4K71/ES |  |  |  |  | 720 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 4K72 | 4K72_DS |  | DS1 | 4K72_DS | [24 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K72_DS | 4K72_DS (非取樣點) | FEEDER | D05/22/4K72/DS |  |  |  |  | 721 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 4K72 | 4K72_ES |  | K720 | 4K72_ES | [24 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K72_ES | 4K72_ES (非取樣點) | FEEDER | D05/22/4K72/ES |  |  |  |  | 722 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 4K73 | 4K73_DS |  | DS1 | 4K73_DS | [24 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K73_DS | 4K73_DS (非取樣點) | FEEDER | D05/22/4K73/DS |  |  |  |  | 723 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 4K73 | 4K73_ES |  | K730 | 4K73_ES | [24 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K73_ES | 4K73_ES (非取樣點) | FEEDER | D05/22/4K73/ES |  |  |  |  | 724 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 4K74 | 4K74_DS |  | DS1 | 4K74_DS | [24 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K74_DS | 4K74_DS (非取樣點) | FEEDER | D05/22/4K74/DS |  |  |  |  | 725 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 4K74 | 4K74_ES |  | K740 | 4K74_ES | [24 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K74_ES | 4K74_ES (非取樣點) | FEEDER | D05/22/4K74/ES |  |  |  |  | 726 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 4K75 | 4K75_DS |  | DS1 | 4K75_DS | [24 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K75_DS | 4K75_DS (非取樣點) | FEEDER | D05/22/4K75/DS |  |  |  |  | 727 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 4K75 | 4K75_ES |  | K750 | 4K75_ES | [24 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K75_ES | 4K75_ES (非取樣點) | FEEDER | D05/22/4K75/ES |  |  |  |  | 728 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 4K76 | 4K76_DS |  | DS1 | 4K76_DS | [24 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K76_DS | 4K76_DS (非取樣點) | FEEDER | D05/22/4K76/DS |  |  |  |  | 729 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 4K76 | 4K76_ES |  | K760 | 4K76_ES | [24 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K76_ES | 4K76_ES (非取樣點) | FEEDER | D05/22/4K76/ES |  |  |  |  | 730 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 4K77 | 4K77_DS |  | DS1 | 4K77_DS | [24 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K77_DS | 4K77_DS (非取樣點) | FEEDER | D05/22/4K77/DS |  |  |  |  | 731 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 4K77 | 4K77_ES |  | K770 | 4K77_ES | [24 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K77_ES | 4K77_ES (非取樣點) | FEEDER | D05/22/4K77/ES |  |  |  |  | 732 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 4K78 | 4K78_DS |  | DS1 | 4K78_DS | [24 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K78_DS | 4K78_DS (非取樣點) | FEEDER | D05/22/4K78/DS |  |  |  |  | 733 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 4K78 | 4K78_ES |  | K780 | 4K78_ES | [24 empty] | DDCS4_1 | [8 empty] | 道爺DS.4K78_ES | 4K78_ES (非取樣點) | FEEDER | D05/22/4K78/ES |  |  |  |  | 734 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [24 empty] | ADCS_S | [8 empty] | 道爺DS.1501E | 1501E (非取樣點) | TIE | D05/161/1500/E1 |  |  |  |  | 735 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [24 empty] | ADCS_S | [8 empty] | 道爺DS.1502E | 1502E (非取樣點) | TIE | D05/161/1500/E2 |  |  |  |  | 736 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1600 | TIE(1600) |  | E1 | 1601E | [24 empty] | ADCS_S | [8 empty] | 道爺DS.1601E | 1601E (非取樣點) | TIE | D05/161/1600/E1 |  |  |  |  | 737 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1600 | TIE(1600) |  | E2 | 1602E | [24 empty] | ADCS_S | [8 empty] | 道爺DS.1602E | 1602E (非取樣點) | TIE | D05/161/1600/E2 |  |  |  |  | 738 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1700 | TIE(1700) |  | E1 | 1701E | [24 empty] | ADCS_S | [8 empty] | 道爺DS.1701E | 1701E (非取樣點) | TIE | D05/161/1700/E1 |  |  |  |  | 739 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1700 | TIE(1700) |  | E3 | 1703E | [24 empty] | ADCS_S | [8 empty] | 道爺DS.1703E | 1703E (非取樣點) | TIE | D05/161/1700/E3 |  |  |  |  | 740 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1800 | TIE(1800) |  | E2 | 1802E | [24 empty] | ADCS_S | [8 empty] | 道爺DS.1802E | 1802E (非取樣點) | TIE | D05/161/1800/E2 |  |  |  |  | 741 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1800 | TIE(1800) |  | E4 | 1804E | [24 empty] | ADCS_S | [8 empty] | 道爺DS.1804E | 1804E (非取樣點) | TIE | D05/161/1800/E4 |  |  |  |  | 742 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 200 | TIE(200) |  | E1 | 201E | [24 empty] | ADCS_S | [8 empty] | 道爺DS.201E | 201E (非取樣點) | TIE | D05/22/200/E1 |  |  |  |  | 743 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 200 | TIE(200) |  | E2 | 202E | [24 empty] | ADCS_S | [8 empty] | 道爺DS.202E | 202E (非取樣點) | TIE | D05/22/200/E2 |  |  |  |  | 744 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 201 | 201 |  | 201 | 201 | [24 empty] | ADCS_S | [8 empty] | 道爺DS.201 | 201 (非取樣點) | TIE | D05/22/200/D1 |  |  |  |  | 745 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 202 | 202 |  | 202 | 202 | [24 empty] | ADCS_S | [8 empty] | 道爺DS.202 | 202 (非取樣點) | TIE | D05/22/200/D2 |  |  |  |  | 746 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 300 | TIE(300) |  | E1 | 301E | [24 empty] | ADCS_S | [8 empty] | 道爺DS.301E | 301E (非取樣點) | TIE | D05/22/300/E1 |  |  |  |  | 747 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 300 | TIE(300) |  | E2 | 302E | [24 empty] | ADCS_S | [8 empty] | 道爺DS.302E | 302E (非取樣點) | TIE | D05/22/300/E2 |  |  |  |  | 748 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 301 | 301 |  | 301 | 301 | [24 empty] | ADCS_S | [8 empty] | 道爺DS.301 | 301 (非取樣點) | TIE | D05/22/300/D1 |  |  |  |  | 749 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 302 | 302 |  | 302 | 302 | [24 empty] | ADCS_S | [8 empty] | 道爺DS.302 | 302 (非取樣點) | TIE | D05/22/300/D2 |  |  |  |  | 750 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 391 | 391 |  | 391 | 391 | [24 empty] | ADCS_S | [8 empty] | 道爺DS.391 | 391 (非取樣點) | OTHER | D05/22/390/D1 |  |  |  |  | 751 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 391E | 391E |  | 391E | 391E | [24 empty] | ADCS_S | [8 empty] | 道爺DS.391E | 391E (非取樣點) | OTHER | D05/22/390/E1 |  |  |  |  | 752 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 491 | 491 |  | 491 | 491 | [24 empty] | ADCS_S | [8 empty] | 道爺DS.491 | 491 (非取樣點) | OTHER | D05/22/490/D1 |  |  |  |  | 753 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 491E | 491E |  | 491E | 491E | [24 empty] | ADCS_S | [8 empty] | 道爺DS.491E | 491E (非取樣點) | OTHER | D05/22/490/E1 |  |  |  |  | 754 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | 1760TE | [24 empty] | ADCS_S | [8 empty] | 道爺DS.1760TE | 1760TE (非取樣點) | MTR | D05/161/1760/TE0 |  |  |  |  | 755 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | 1760BE | [24 empty] | ADCS_S | [8 empty] | 道爺DS.1760BE | 1760BE (非取樣點) | MTR | D05/161/1760/BE0 |  |  |  |  | 756 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 331 | 331 |  | 331 | 331 | [24 empty] | ADCS_S | [8 empty] | 道爺DS.331 | 331 (非取樣點) | MTR | D05/22/330/D1 |  |  |  |  | 757 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 330 | #2DTR(330) |  | E1 | 331E | [24 empty] | ADCS_S | [8 empty] | 道爺DS.331E | 331E (非取樣點) | MTR | D05/22/330/E1 |  |  |  |  | 758 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 341 | 341 |  | 341 | 341 | [24 empty] | ADCS_S | [8 empty] | 道爺DS.341 | 341 (非取樣點) | MTR | D05/22/340/D1 |  |  |  |  | 759 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 340 | #2DTR(340) |  | E1 | 341E | [24 empty] | ADCS_S | [8 empty] | 道爺DS.341E | 341E (非取樣點) | MTR | D05/22/340/E1 |  |  |  |  | 760 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | 1770TE | [24 empty] | ADCS_S | [8 empty] | 道爺DS.1770TE | 1770TE (非取樣點) | MTR | D05/161/1770/TE0 |  |  |  |  | 761 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | 1770BE | [24 empty] | ADCS_S | [8 empty] | 道爺DS.1770BE | 1770BE (非取樣點) | MTR | D05/161/1770/BE0 |  |  |  |  | 762 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 351 | 351 |  | 351 | 351 | [24 empty] | ADCS_S | [8 empty] | 道爺DS.351 | 351 (非取樣點) | MTR | D05/22/350/D1 |  |  |  |  | 763 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 350 | #3DTR(350) |  | E1 | 351E | [24 empty] | ADCS_S | [8 empty] | 道爺DS.351E | 351E (非取樣點) | MTR | D05/22/350/E1 |  |  |  |  | 764 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 361 | 361 |  | 361 | 361 | [24 empty] | ADCS_S | [8 empty] | 道爺DS.361 | 361 (非取樣點) | MTR | D05/22/360/D1 |  |  |  |  | 765 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 360 | #3DTR(360) |  | E1 | 361E | [24 empty] | ADCS_S | [8 empty] | 道爺DS.361E | 361E (非取樣點) | MTR | D05/22/360/E1 |  |  |  |  | 766 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 231E | 231E |  | 231E | 231E | [24 empty] | ADCS_S | [8 empty] | 道爺DS.231E | 231E (非取樣點) | SC | D05/22/230/E1 |  |  |  |  | 767 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 231 | 231 |  | 231 | 231 | [24 empty] | ADCS_S | [8 empty] | 道爺DS.231 | 231 (非取樣點) | SC | D05/22/230/D1 |  |  |  |  | 768 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 241E | 241E |  | 241E | 241E | [24 empty] | ADCS_S | [8 empty] | 道爺DS.241E | 241E (非取樣點) | SC | D05/22/240/E1 |  |  |  |  | 769 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 241 | 241 |  | 241 | 241 | [24 empty] | ADCS_S | [8 empty] | 道爺DS.241 | 241 (非取樣點) | SC | D05/22/240/D1 |  |  |  |  | 770 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 251E | 251E |  | 251E | 251E | [24 empty] | ADCS_S | [8 empty] | 道爺DS.251E | 251E (非取樣點) | SC | D05/22/250/E1 |  |  |  |  | 771 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 251 | 251 |  | 251 | 251 | [24 empty] | ADCS_S | [8 empty] | 道爺DS.251 | 251 (非取樣點) | SC | D05/22/250/D1 |  |  |  |  | 772 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 261E | 261E |  | 261E | 261E | [24 empty] | ADCS_S | [8 empty] | 道爺DS.261E | 261E (非取樣點) | SC | D05/22/260/E1 |  |  |  |  | 773 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 261 | 261 |  | 261 | 261 | [24 empty] | ADCS_S | [8 empty] | 道爺DS.261 | 261 (非取樣點) | SC | D05/22/260/D1 |  |  |  |  | 774 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 15B1E | 15B1E |  | BE1 | 15B1E | [24 empty] | ADCS_S | [8 empty] | 道爺DS.15B1E | 15B1E (非取樣點) | BUS | D05/161/161B1E/BE1 |  |  |  |  | 775 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 15B2E | 15B2E |  | BE2 | 15B2E | [24 empty] | ADCS_S | [8 empty] | 道爺DS.15B2E | 15B2E (非取樣點) | BUS | D05/161/161B2E/BE2 |  |  |  |  | 776 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 15B3E | 15B3E |  | BE3 | 15B3E | [24 empty] | ADCS_S | [8 empty] | 道爺DS.15B3E | 15B3E (非取樣點) | BUS | D05/161/3BUS/BE1 |  |  |  |  | 777 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 15B4E | 15B4E |  | BE4 | 15B4E | [24 empty] | ADCS_S | [8 empty] | 道爺DS.15B4E | 15B4E (非取樣點) | BUS | D05/161/4BUS/BE2 |  |  |  |  | 778 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | ADCS_S | [8 empty] | 道爺DS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 779 | NotelDIPoint | [38 empty] | START/STOP | STOP
D05 | 道爺DS | 161 | 161kV | 1510 | 南科道爺ㄧ路(1510) |  | LE0 | 1510LE | [24 empty] | ADCS_S | [8 empty] | 道爺DS.1510LE | 1510LE (非取樣點) | LINE161 | D05/161/1510/LE0 |  |  |  |  | 780 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1510 | 南科道爺ㄧ路(1510) |  | BE0 | 1510BE | [24 empty] | ADCS_S | [8 empty] | 道爺DS.1510BE | 1510BE (非取樣點) | LINE161 | D05/161/1510/BE0 |  |  |  |  | 781 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1520 | 南科道爺二路(1520) |  | LE0 | 1520LE | [24 empty] | ADCS_S | [8 empty] | 道爺DS.1520LE | 1520LE (非取樣點) | LINE161 | D05/161/1520/LE0 |  |  |  |  | 782 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 161 | 161kV | 1520 | 南科道爺二路(1520) |  | BE0 | 1520BE | [24 empty] | ADCS_S | [8 empty] | 道爺DS.1520BE | 1520BE (非取樣點) | LINE161 | D05/161/1520/BE0 |  |  |  |  | 783 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 2ABUS | 2ABUS |  | PTD | 2ABUS_PTD | [24 empty] | ADCS_S | [8 empty] | 道爺DS.2ABUS_PTD | #2ABUS_PTD(非取樣點) | OTHER | [5 empty] | 784 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 2ABUS | 2ABUS |  | PTE | 2ABUS_PTE | [24 empty] | ADCS_S | [8 empty] | 道爺DS.2ABUS_PTE | #2ABUS_PTE(非取樣點) | OTHER | [5 empty] | 785 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 2BBUS | 2BBUS |  | PTD | 2BBUS_PTD | [24 empty] | ADCS_S | [8 empty] | 道爺DS.2BBUS_PTD | #2BBUS_PTD(非取樣點) | OTHER | [5 empty] | 786 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 2BBUS | 2BBUS |  | PTE | 2BBUS_PTE | [24 empty] | ADCS_S | [8 empty] | 道爺DS.2BBUS_PTE | #2BBUS_PTE(非取樣點) | OTHER | [5 empty] | 787 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 3ABUS | 3ABUS |  | PTD | 3ABUS_PTD | [24 empty] | ADCS_S | [8 empty] | 道爺DS.3ABUS_PTD | #3ABUS_PTD(非取樣點) | OTHER | [5 empty] | 788 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 3ABUS | 3ABUS |  | PTE | 3ABUS_PTE | [24 empty] | ADCS_S | [8 empty] | 道爺DS.3ABUS_PTE | #3ABUS_PTE(非取樣點) | OTHER | [5 empty] | 789 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D05 | 道爺DS | 0 |  | 3BBUS | 3BBUS |  | PTD | 3BBUS_PTD | [24 empty] | ADCS_S | [8 empty] | 道爺DS.3BBUS_PTD | #3BBUS_PTD(非取樣點) | OTHER | [5 empty] | 790 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D05 | 道爺DS | 0 |  | 3BBUS | 3BBUS |  | PTE | 3BBUS_PTE | [24 empty] | ADCS_S | [8 empty] | 道爺DS.3BBUS_PTE | #3BBUS_PTE(非取樣點) | OTHER | [5 empty] | 791 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo