## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D06 | 柳營DS | 161 | 161kV | 1510 | 柳營～新高紅線(1510) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_A1 | [8 empty] | 柳營DS.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 2 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1510 | 柳營～新高紅線(1510) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_A1 | [8 empty] | 柳營DS.1510BE | 1510BE (非取樣點) | LINE161 | [5 empty] | 3 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1520 | 柳營～新高、榮特白線(1520) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_A1 | [8 empty] | 柳營DS.1520LE | 1520LE (非取樣點) | LINE161 | [5 empty] | 4 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1520 | 柳營～新高、榮特白線(1520) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_A1 | [8 empty] | 柳營DS.1520BE | 1520BE (非取樣點) | LINE161 | [5 empty] | 5 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1530 | 新營～柳營山線(1530) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_A1 | [8 empty] | 柳營DS.1530LE | 1530LE (非取樣點) | LINE161 | [5 empty] | 6 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1530 | 新營～柳營山線(1530) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_A1 | [8 empty] | 柳營DS.1530BE | 1530BE (非取樣點) | LINE161 | [5 empty] | 7 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1540 | 新營～柳營海線(1540) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_A1 | [8 empty] | 柳營DS.1540LE | 1540LE (非取樣點) | LINE161 | [5 empty] | 8 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1540 | 新營～柳營海線(1540) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_A1 | [8 empty] | 柳營DS.1540BE | 1540BE (非取樣點) | LINE161 | [5 empty] | 9 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1550 | 嘉民～柳營山線(1550) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_A1 | [8 empty] | 柳營DS.1550LE | 1550LE (非取樣點) | LINE161 | [5 empty] | 10 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1550 | 嘉民～柳營山線(1550) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_A1 | [8 empty] | 柳營DS.1550BE | 1550BE (非取樣點) | LINE161 | [5 empty] | 11 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1560 | 嘉民～柳營海線(1560) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_A1 | [8 empty] | 柳營DS.1560LE | 1560LE (非取樣點) | LINE161 | [5 empty] | 12 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1560 | 嘉民～柳營海線(1560) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_A1 | [8 empty] | 柳營DS.1560BE | 1560BE (非取樣點) | LINE161 | [5 empty] | 13 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_A1 | [8 empty] | 柳營DS.1501E | 1501E (非取樣點) | TIE | [5 empty] | 14 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_A1 | [8 empty] | 柳營DS.1502E | 1502E (非取樣點) | TIE | [5 empty] | 15 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_A1 | [8 empty] | 柳營DS.1750TE | 1750TE (非取樣點) | MTR | [5 empty] | 16 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_A1 | [8 empty] | 柳營DS.1750BE | 1750BE (非取樣點) | MTR | [5 empty] | 17 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | D1 | 311(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D06_A1 | [8 empty] | 柳營DS.311 | 311 (非取樣點) | MTR | [5 empty] | 18 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | E1 | 311E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D06_A1 | [8 empty] | 柳營DS.311E | 311E (非取樣點) | MTR | [5 empty] | 19 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | D1 | 321(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D06_A1 | [8 empty] | 柳營DS.321 | 321 (非取樣點) | MTR | [5 empty] | 20 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | E1 | 321E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D06_A1 | [8 empty] | 柳營DS.321E | 321E (非取樣點) | MTR | [5 empty] | 21 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_A1 | [8 empty] | 柳營DS.1760TE | 1760TE (非取樣點) | MTR | [5 empty] | 22 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_A1 | [8 empty] | 柳營DS.1760BE | 1760BE (非取樣點) | MTR | [5 empty] | 23 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | D1 | 331(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D06_A1 | [8 empty] | 柳營DS.331 | 331 (非取樣點) | MTR | [5 empty] | 24 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | E1 | 331E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D06_A1 | [8 empty] | 柳營DS.331E | 331E (非取樣點) | MTR | [5 empty] | 25 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | D1 | 341(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D06_A1 | [8 empty] | 柳營DS.341 | 341 (非取樣點) | MTR | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | E1 | 341E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D06_A1 | [8 empty] | 柳營DS.341E | 341E (非取樣點) | MTR | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1950 | #1SHR(1950) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_A1 | [8 empty] | 柳營DS.1950BE | 1950BE(非取樣點) | OTHER | [5 empty] | 28 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1950 | #1SHR(1950) |  | RE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_A1 | [8 empty] | 柳營DS.1950RE | 1950RE(非取樣點) | OTHER | [5 empty] | 29 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 11 | 11kV | VJ21 | 柳一線(VJ21) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ21_DS | VJ21_DS (非取樣點) | FEEDER | [5 empty] | 30 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | VJ21 | 柳一線(VJ21) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ21_ES | VJ21_ES (非取樣點) | FEEDER | [5 empty] | 31 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 11 | 11kV | VJ22 | 柳二線(VJ22) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ22_DS | VJ22_DS (非取樣點) | FEEDER | [5 empty] | 32 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | VJ22 | 柳二線(VJ22) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ22_ES | VJ22_ES (非取樣點) | FEEDER | [5 empty] | 33 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 11 | 11kV | VJ23 | 柳三線(VJ23) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ23_DS | VJ23_DS (非取樣點) | FEEDER | [5 empty] | 34 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | VJ23 | 柳三線(VJ23) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ23_ES | VJ23_ES (非取樣點) | FEEDER | [5 empty] | 35 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 11 | 11kV | VJ24 | 柳正線(VJ24) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ24_DS | VJ24_DS (非取樣點) | FEEDER | [5 empty] | 36 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | VJ24 | 柳正線(VJ24) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ24_ES | VJ24_ES (非取樣點) | FEEDER | [5 empty] | 37 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 11 | 11kV | VJ25 | 柳五線(VJ25) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ25_DS | VJ25_DS (非取樣點) | FEEDER | [5 empty] | 38 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | VJ25 | 柳五線(VJ25) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ25_ES | VJ25_ES (非取樣點) | FEEDER | [5 empty] | 39 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 11 | 11kV | 210 | #1SC(210) |  | E1 | 211E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D06_A1 | [8 empty] | 柳營DS.211E | 211E (非取樣點) | SC | [5 empty] | 40 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 11 | 11kV | 210 | #1SC(210) |  | D1 | 211(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D06_A1 | [8 empty] | 柳營DS.211 | 211 (非取樣點) | SC | [5 empty] | 41 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | 390 | #1SSTR(390) |  | D1 | 391(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D06_A1 | [8 empty] | 柳營DS.391 | 391 (非取樣點) | OTHER | [5 empty] | 42 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | 390 | #1SSTR(390) |  | E1 | 391E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D06_A1 | [8 empty] | 柳營DS.391E | 391E (非取樣點) | OTHER | [5 empty] | 43 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 22 | 22kV | VJ51 | 柳51線(VJ51) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ51_DS | VJ51_DS (非取樣點) | FEEDER | [5 empty] | 44 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | VJ51 | 柳51線(VJ51) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ51_ES | VJ51_ES (非取樣點) | FEEDER | [5 empty] | 45 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 22 | 22kV | VJ52 | 柳52線(VJ52) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ52_DS | VJ52_DS (非取樣點) | FEEDER | [5 empty] | 46 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | VJ52 | 柳52線(VJ52) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ52_ES | VJ52_ES (非取樣點) | FEEDER | [5 empty] | 47 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 22 | 22kV | VJ53 | 柳53線(VJ53) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ53_DS | VJ53_DS (非取樣點) | FEEDER | [5 empty] | 48 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | VJ53 | 柳53線(VJ53) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ53_ES | VJ53_ES (非取樣點) | FEEDER | [5 empty] | 49 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 22 | 22kV | VJ54 | 柳54線(VJ54) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ54_DS | VJ54_DS (非取樣點) | FEEDER | [5 empty] | 50 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | VJ54 | 柳54線(VJ54) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ54_ES | VJ54_ES (非取樣點) | FEEDER | [5 empty] | 51 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 22 | 22kV | VJ55 | 柳55線(VJ55) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ55_DS | VJ55_DS (非取樣點) | FEEDER | [5 empty] | 52 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | VJ55 | 柳55線(VJ55) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ55_ES | VJ55_ES (非取樣點) | FEEDER | [5 empty] | 53 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 22 | 22kV | 220 | #2SC(220) |  | E1 | 221E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D06_A1 | [8 empty] | 柳營DS.221E | 221E (非取樣點) | SC | [5 empty] | 54 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 22 | 22kV | 220 | #2SC(220) |  | D1 | 221(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D06_A1 | [8 empty] | 柳營DS.221 | 221 (非取樣點) | SC | [5 empty] | 55 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | VJ31 | 十一線(VJ31) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ31_DS | VJ31_DS (非取樣點) | FEEDER | [5 empty] | 56 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | VJ31 | 十一線(VJ31) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ31_ES | VJ31_ES (非取樣點) | FEEDER | [5 empty] | 57 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 11 | 11kV | VJ32 | 十二線(VJ32) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ32_DS | VJ32_DS (非取樣點) | FEEDER | [5 empty] | 58 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | VJ32 | 十二線(VJ32) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ32_ES | VJ32_ES (非取樣點) | FEEDER | [5 empty] | 59 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 11 | 11kV | VJ33 | 十三線(VJ33) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ33_DS | VJ33_DS (非取樣點) | FEEDER | [5 empty] | 60 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | VJ33 | 十三線(VJ33) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ33_ES | VJ33_ES (非取樣點) | FEEDER | [5 empty] | 61 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 11 | 11kV | VJ34 | 十四線(VJ34) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ34_DS | VJ34_DS (非取樣點) | FEEDER | [5 empty] | 62 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | VJ34 | 十四線(VJ34) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ34_ES | VJ34_ES (非取樣點) | FEEDER | [5 empty] | 63 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 11 | 11kV | VJ35 | 十五線(VJ35) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ35_DS | VJ35_DS (非取樣點) | FEEDER | [5 empty] | 64 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | VJ35 | 十五線(VJ35) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ35_ES | VJ35_ES (非取樣點) | FEEDER | [5 empty] | 65 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 11 | 11kV | 230 | #3SC(230) |  | E1 | 231E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D06_A1 | [8 empty] | 柳營DS.231E | 231E (非取樣點) | SC | [5 empty] | 66 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 11 | 11kV | 230 | #3SC(230) |  | D1 | 231(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D06_A1 | [8 empty] | 柳營DS.231 | 231 (非取樣點) | SC | [5 empty] | 67 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | 100 | TIE(100) |  | D1 | 101(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D06_A1 | [8 empty] | 柳營DS.101 | 101 (非取樣點) | TIE | [5 empty] | 68 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | 100 | TIE(100) |  | D2 | 102(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D06_A1 | [8 empty] | 柳營DS.102 | 102 (非取樣點) | TIE | [5 empty] | 69 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | 100 | TIE(100) |  | E1 | 101E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D06_A1 | [8 empty] | 柳營DS.101E | 101E(非取樣點) | OTHER | [5 empty] | 70 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 11 | 11kV | 100 | TIE(100) |  | E2 | 102E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D06_A1 | [8 empty] | 柳營DS.102E | 102E(非取樣點) | OTHER | [5 empty] | 71 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 22 | 22kV | VJ56 | 柳56線(VJ56) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ56_DS | VJ56_DS (非取樣點) | FEEDER | [5 empty] | 72 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | VJ56 | 柳56線(VJ56) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ56_ES | VJ56_ES (非取樣點) | FEEDER | [5 empty] | 73 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 22 | 22kV | VJ57 | 柳57線(VJ57) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ57_DS | VJ57_DS (非取樣點) | FEEDER | [5 empty] | 74 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | VJ57 | 柳57線(VJ57) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ57_ES | VJ57_ES (非取樣點) | FEEDER | [5 empty] | 75 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 22 | 22kV | VJ58 | 柳58線(VJ58) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ58_DS | VJ58_DS (非取樣點) | FEEDER | [5 empty] | 76 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | VJ58 | 柳58線(VJ58) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ58_ES | VJ58_ES (非取樣點) | FEEDER | [5 empty] | 77 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 22 | 22kV | VJ59 | 柳59線(VJ59) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ59_DS | VJ59_DS (非取樣點) | FEEDER | [5 empty] | 78 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | VJ59 | 柳59線(VJ59) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ59_ES | VJ59_ES (非取樣點) | FEEDER | [5 empty] | 79 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 22 | 22kV | VJ60 | 柳60線(VJ60) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ60_DS | VJ60_DS (非取樣點) | FEEDER | [5 empty] | 80 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | VJ60 | 柳60線(VJ60) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D06_D1 | [8 empty] | 柳營DS.VJ60_ES | VJ60_ES (非取樣點) | FEEDER | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 22 | 22kV | 240 | #4SC(240) |  | E1 | 241E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D06_A1 | [8 empty] | 柳營DS.241E | 241E (非取樣點) | SC | [5 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 22 | 22kV | 240 | #4SC(240) |  | D1 | 241(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D06_A1 | [8 empty] | 柳營DS.241 | 241 (非取樣點) | SC | [5 empty] | 83 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | 200 | TIE(200) |  | D1 | 201(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D06_A1 | [8 empty] | 柳營DS.201 | 201 (非取樣點) | TIE | [5 empty] | 84 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | 200 | TIE(200) |  | D2 | 202(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D06_A1 | [8 empty] | 柳營DS.202 | 202 (非取樣點) | TIE | [5 empty] | 85 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | 200 | TIE(200) |  | E1 | 201E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D06_A1 | [8 empty] | 柳營DS.201E | 201E(非取樣點) | OTHER | [5 empty] | 86 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 22 | 22kV | 200 | TIE(200) |  | E2 | 202E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D06_A1 | [8 empty] | 柳營DS.202E | 202E(非取樣點) | OTHER | [5 empty] | 87 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 22 | 22kV | 490 | #2SSTR(490) |  | D1 | 491(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D06_A1 | [8 empty] | 柳營DS.491 | 491 (非取樣點) | OTHER | [5 empty] | 88 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | 490 | #2SSTR(490) |  | E1 | 491E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D06_A1 | [8 empty] | 柳營DS.491E | 491E (非取樣點) | OTHER | [5 empty] | 89 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | 15B1E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aaaz | B2/D06_A1 | [8 empty] | 柳營DS.15B1E | 15B1E (非取樣點) | BUS | [5 empty] | 90 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | 15B2E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/2Bus | [13 empty] | aaaz | B2/D06_A1 | [8 empty] | 柳營DS.15B2E | 15B2E (非取樣點) | BUS | [5 empty] | 91 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | RTU | RTU |  | ADCL1 |  |  | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | [5 empty] | 92 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 0 |  | RTU | RTU |  | ADCH1 |  |  | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.1 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | [5 empty] | 93 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 161 | 161kV | 1BUS | #1BUS |  | V |  | B3 | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 161KV #1BUS | KV | 161KV #1BUS 電壓 | kV_-210_210(-2000_2000) | aaa | B2/D06_A1 | [8 empty] | 柳營DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | [5 empty] | 94 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D06 | 柳營DS | 161 | 161kV | 2BUS | #2BUS |  | V |  | B3 | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0003 |  |  | 1-83 |  |  | 161KV #2BUS | KV | 161KV #2BUS 電壓 | kV_-210_210(-2000_2000) | aab | B2/D06_A1 | [8 empty] | 柳營DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | [5 empty] | 95 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D06 | 柳營DS | 161 | 161kV | 1510 | 柳營～新高紅線(1510) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | L1 | MW | 柳營新高紅線1510 瓦 | MW_-560_560(-2000_2000) |  | B2/D06_A1 | [8 empty] | 柳營DS.1510_MW | 柳營新高紅線 MW | LINE161 | [5 empty] | 96 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D06 | 柳營DS | 161 | 161kV | 1510 | 柳營～新高紅線(1510) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | L1 | MVAR | 柳營新高紅線1510 乏 | MVAR_-560_560(-2000_2000) |  | B2/D06_A1 | [8 empty] | 柳營DS.1510_MVAR | 柳營新高紅線 MVAR | LINE161 | [5 empty] | 97 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D06 | 柳營DS | 161 | 161kV | 1520 | 柳營～新高、榮特白線(1520) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | L2 | MW | 柳營~新高、榮特白線1520 瓦 | MW_-560_560(-2000_2000) |  | B2/D06_A1 | [8 empty] | 柳營DS.1520_MW | 柳營新高榮特白 MW | LINE161 | [5 empty] | 98 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D06 | 柳營DS | 161 | 161kV | 1520 | 柳營～新高、榮特白線(1520) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | L2 | MVAR | 柳營~新高、榮特白線1520 乏 | MVAR_-560_560(-2000_2000) |  | B2/D06_A1 | [8 empty] | 柳營DS.1520_MVAR | 柳營新高榮特白 MVAR | LINE161 | [5 empty] | 99 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D06 | 柳營DS | 161 | 161kV | 1530 | 新營～柳營山線(1530) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | Line3 | MW | 新營柳營山線 1530 瓦 | MW_-560_560(-2000_2000) |  | B2/D06_A1 | [8 empty] | 柳營DS.1530_MW | 新營柳營山線 MW | LINE161 | [5 empty] | 100 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D06 | 柳營DS | 161 | 161kV | 1530 | 新營～柳營山線(1530) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | Line3 | MVAR | 新營柳營山線 1530 乏 | MVAR_-560_560(-2000_2000) |  | B2/D06_A1 | [8 empty] | 柳營DS.1530_MVAR | 新營柳營山線 MVAR | LINE161 | [5 empty] | 101 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D06 | 柳營DS | 161 | 161kV | 1540 | 新營～柳營海線(1540) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | Line4 | MW | 新營柳營海線 1540瓦 | MW_-560_560(-2000_2000) |  | B2/D06_A1 | [8 empty] | 柳營DS.1540_MW | 新營柳營海線 MW | LINE161 | [5 empty] | 102 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D06 | 柳營DS | 161 | 161kV | 1540 | 新營～柳營海線(1540) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | Line4 | MVAR | 新營柳營海線 1540乏 | MVAR_-560_560(-2000_2000) |  | B2/D06_A1 | [8 empty] | 柳營DS.1540_MVAR | 新營柳營海線 MVAR | LINE161 | [5 empty] | 103 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D06 | 柳營DS | 161 | 161kV | 1550 | 嘉民～柳營山線(1550) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0012 |  |  | 1-8C |  |  | Line5 | MW | 嘉民柳營山線 1550 瓦 | MW_-560_560(-2000_2000) |  | B2/D06_A1 | [8 empty] | 柳營DS.1550_MW | 嘉民柳營山線 MW | LINE161 | [5 empty] | 104 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D06 | 柳營DS | 161 | 161kV | 1550 | 嘉民～柳營山線(1550) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0013 |  |  | 1-8D |  |  | Line5 | MVAR | 嘉民柳營山線 1550 乏 | MVAR_-560_560(-2000_2000) |  | B2/D06_A1 | [8 empty] | 柳營DS.1550_MVAR | 嘉民柳營山線 MVAR | LINE161 | [5 empty] | 105 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D06 | 柳營DS | 161 | 161kV | 1560 | 嘉民～柳營海線(1560) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0014 |  |  | 1-8E |  |  | Line6 | MW | 嘉民柳營海線 1560瓦 | MW_-560_560(-2000_2000) |  | B2/D06_A1 | [8 empty] | 柳營DS.1560_MW | 嘉民柳營海線 MW | LINE161 | [5 empty] | 106 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D06 | 柳營DS | 161 | 161kV | 1560 | 嘉民～柳營海線(1560) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0015 |  |  | 1-8F |  |  | Line6 | MVAR | 嘉民柳營海線 1560 乏 | MVAR_-560_560(-2000_2000) |  | B2/D06_A1 | [8 empty] | 柳營DS.1560_MVAR | 嘉民柳營海線 MVAR | LINE161 | [5 empty] | 107 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D06 | 柳營DS | 0 |  | StaDev | 所內設施 |  | DCV_P |  |  | MvMoment | 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | DCV | 65 | DC-P電壓 | kV_-150_150(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.直流P電源電壓 | 直流P電源電壓 | OTHER | [5 empty] | 108 |  |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 | 0.01 | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D06 | 柳營DS | 0 |  | StaDev | 所內設施 |  | DCV_N |  |  | MvMoment | 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | DCV | -65 | DC-N電壓 | kV_-150_150(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.直流N電源電壓 | 直流N電源電壓 | OTHER | [5 empty] | 109 |  |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 | 0.01 | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D06 | 柳營DS | 161 | 161kV | 1500 | TIE(1500) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0024 |  |  | 1-98 |  |  | 161KV TIE | A | (1500) R相電流 | A_-2000_2000(-2000_2000) |  | B2/D06_A1 | [8 empty] | 柳營DS.1500TIE_AMP | 1500TIE AMP | TIE | [5 empty] | 110 |  |  |  |  | AI | [5 empty] | C20R1600 | 1520 | 1600 | 1760 | 1968 | 2.27 | -1520 | -1600 | -1760 | -1968 | 1 | 0.01 | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS |  |  | 1DTR | #1DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | NO.1 DTR. | ℃ | NO.1 DTR. 油溫 | OIL_-120_120(-2000_2000) |  | B1/D06_A1 | [8 empty] | 柳營DS.#1DTR_OIL | #1DTR 油溫 | MTR | [5 empty] | 111 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D06 | 柳營DS |  |  | 1DTR(A) | #1DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | NO.1 DTR.A | ℃ | NO.1 DTR.A 線溫 | COIL_-120_120(-2000_2000) |  | B1/D06_A1 | [8 empty] | 柳營DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | [5 empty] | 112 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D06 | 柳營DS |  |  | 1DTR(B) | #1DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0027 |  |  | 1-9B |  |  | NO.1 DTR.B | ℃ | NO.1 DTR.B 線溫 | COIL_-120_120(-2000_2000) |  | B1/D06_A1 | [8 empty] | 柳營DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | [5 empty] | 113 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D06 | 柳營DS |  |  | 1DTR(A) | #1DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | NO.1 DTR.A | 升/降 | NO.1 DTR.A TAP | TAP_-8.5_8.5(0_2000) |  | B1/D06_A1 | [8 empty] | 柳營DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | [5 empty] | 114 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D06 | 柳營DS |  |  | 1DTR(B) | #1DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | NO.1 DTR.B | 升/降 | NO.1 DTR.B TAP | TAP_-8.5_8.5(0_2000) |  | B1/D06_A1 | [8 empty] | 柳營DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | [5 empty] | 115 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D06 | 柳營DS |  |  | 2DTR | #2DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | NO.2 DTR. | ℃ | NO.2 DTR. 油溫 | OIL_-120_120(-2000_2000) |  | B1/D06_A1 | [8 empty] | 柳營DS.#2DTR_OIL | #2DTR 油溫 | MTR | [5 empty] | 116 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D06 | 柳營DS |  |  | 2DTR(A) | #2DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | NO.2 DTR.A | ℃ | NO.2 DTR.A 線溫 | COIL_-120_120(-2000_2000) |  | B1/D06_A1 | [8 empty] | 柳營DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | [5 empty] | 117 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D06 | 柳營DS |  |  | 2DTR(B) | #2DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | NO.2 DTR.B | ℃ | NO.2 DTR.B 線溫 | COIL_-120_120(-2000_2000) |  | B1/D06_A1 | [8 empty] | 柳營DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | [5 empty] | 118 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D06 | 柳營DS |  |  | 2DTR(A) | #2DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | NO.2 DTR.A | 升/降 | NO.2 DTR.A TAP | TAP_-8.5_8.5(0_2000) |  | B1/D06_A1 | [8 empty] | 柳營DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | [5 empty] | 119 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D06 | 柳營DS |  |  | 2DTR(B) | #2DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | NO.2 DTR.B | 升/降 | NO.2 DTR.B TAP | TAP_-8.5_8.5(0_2000) |  | B1/D06_A1 | [8 empty] | 柳營DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | [5 empty] | 120 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D06 | 柳營DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | D-1A | MW | D-1A 310 瓦 | MW_-54_54(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | [5 empty] | 121 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | D-1A | MVAR | D-1A 310 乏 | MVAR_-36_36(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | [5 empty] | 122 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | D-1A | A | D-1A 310 R相電流 | A_-3000_3000(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | [5 empty] | 123 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | D-1A | A | D-1A 310 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | [5 empty] | 124 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | D-1A | A | D-1A 310 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | [5 empty] | 125 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 1ABUS | #1ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0046 |  |  | 1-AE |  |  | PT-1A | KV | #1A PT R相電壓 | kV_-9_9(-2000_2000) | aaa | B3/D06_A1 | [8 empty] | 柳營DS.11KV#1ABUS_KV | 11KV #1ABUS KV | BUS | [5 empty] | 126 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D06 | 柳營DS | 11 | 11kV | VJ21 | 柳一線(VJ21) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | F1 | KVAR | 柳一線 VJ21 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳一線KVAR | 11KV柳一線 KVAR | FEEDER | [5 empty] | 127 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ21 | 柳一線(VJ21) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | F1 | A | 柳一線 VJ21 R相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳一線A1 | 11KV柳一線 R相AMP | FEEDER | [5 empty] | 128 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ21 | 柳一線(VJ21) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | F1 | A | 柳一線 VJ21 S相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳一線A2 | 11KV柳一線 S相AMP | FEEDER | [5 empty] | 129 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ21 | 柳一線(VJ21) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | F1 | A | 柳一線 VJ21 T相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳一線A3 | 11KV柳一線 T相AMP | FEEDER | [5 empty] | 130 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ21 | 柳一線(VJ21) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | F1 | A | 柳一線 VJ21 N相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳一線A0 | 11KV柳一線 N相AMP | FEEDER | [5 empty] | 131 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ22 | 柳二線(VJ22) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | F2 | KVAR | 柳二線 VJ22 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳二線KVAR | 11KV柳二線 KVAR | FEEDER | [5 empty] | 132 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ22 | 柳二線(VJ22) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | F2 | A | 柳二線 VJ22 R相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳二線A1 | 11KV柳二線 R相AMP | FEEDER | [5 empty] | 133 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ22 | 柳二線(VJ22) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | F2 | A | 柳二線 VJ22 S 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳二線A2 | 11KV柳二線 S相AMP | FEEDER | [5 empty] | 134 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ22 | 柳二線(VJ22) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | F2 | A | 柳二線 VJ22 T 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳二線A3 | 11KV柳二線 T相AMP | FEEDER | [5 empty] | 135 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ22 | 柳二線(VJ22) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | F2 | A | 柳二線 VJ22 N 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳二線A0 | 11KV柳二線 N相AMP | FEEDER | [5 empty] | 136 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ23 | 柳三線(VJ23) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | F3 | KVAR | 柳三線 VJ23 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳三線KVAR | 11KV柳三線 KVAR | FEEDER | [5 empty] | 137 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ23 | 柳三線(VJ23) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | F3 | A | 柳三線 VJ23 R相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳三線A1 | 11KV柳三線 R相AMP | FEEDER | [5 empty] | 138 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ23 | 柳三線(VJ23) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | F3 | A | 柳三線 VJ23 S 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳三線A2 | 11KV柳三線 S相AMP | FEEDER | [5 empty] | 139 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ23 | 柳三線(VJ23) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0060 |  |  | 1-BC |  |  | F3 | A | 柳三線 VJ23 T 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳三線A3 | 11KV柳三線 T相AMP | FEEDER | [5 empty] | 140 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ23 | 柳三線(VJ23) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | F3 | A | 柳三線 VJ23 N 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳三線A0 | 11KV柳三線 N相AMP | FEEDER | [5 empty] | 141 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ24 | 柳正線(VJ24) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | F4 | KVAR | 柳正線 VJ24 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳正線KVAR | 11KV柳正線 KVAR | FEEDER | [5 empty] | 142 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ24 | 柳正線(VJ24) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0063 |  |  | 1-BF |  |  | F4 | A | 柳正線 VJ24 R 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳正線A1 | 11KV柳正線 R相AMP | FEEDER | [5 empty] | 143 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 0 |  | RTU | RTU |  | ADCL2 |  |  | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | [5 empty] | 144 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 0 |  | RTU | RTU |  | ADCH2 |  |  | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.2 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | [5 empty] | 145 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ24 | 柳正線(VJ24) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | F4 | A | 柳正線 VJ24 S 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳正線A2 | 11KV柳正線 S相AMP | FEEDER | [5 empty] | 146 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ24 | 柳正線(VJ24) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | F4 | A | 柳正線 VJ24 T 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳正線A3 | 11KV柳正線 T相AMP | FEEDER | [5 empty] | 147 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ24 | 柳正線(VJ24) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | F4 | A | 柳正線 VJ24 N 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳正線A0 | 11KV柳正線 N相AMP | FEEDER | [5 empty] | 148 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ25 | 柳五線(VJ25) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | F5 | KVAR | 柳五線 VJ25 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳五線KVAR | 11KV柳五線 KVAR | FEEDER | [5 empty] | 149 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ25 | 柳五線(VJ25) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | F5 | A | 柳五線 VJ25 R 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳五線A1 | 11KV柳五線 R相AMP | FEEDER | [5 empty] | 150 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ25 | 柳五線(VJ25) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | F5 | A | 柳五線 VJ25 S 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳五線A2 | 11KV柳五線 S相AMP | FEEDER | [5 empty] | 151 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ25 | 柳五線(VJ25) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | F5 | A | 柳五線 VJ25 T 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳五線A3 | 11KV柳五線 T相AMP | FEEDER | [5 empty] | 152 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ25 | 柳五線(VJ25) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | F5 | A | 柳五線 VJ25 N相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳五線A0 | 11KV柳五線 N相AMP | FEEDER | [5 empty] | 153 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | D-1B | MW | D-1B 320 瓦 | MW_-108_108(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | [5 empty] | 154 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.216 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | D-1B | MVAR | D-1B 320 乏 | MVAR_-72_72(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | [5 empty] | 155 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | D-1B | A | D-1B 320 R相電流 | A_-3000_3000(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | [5 empty] | 156 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | D-1B | A | D-1B 320 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | [5 empty] | 157 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | D-1B | A | D-1B 320 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | [5 empty] | 158 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 1BBUS | #1BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0079 |  |  | 1-CF |  |  | PT-1B | KV | #1B PT R相電壓 | kV_-18_18(-2000_2000) | baa | B3/D06_A1 | [8 empty] | 柳營DS.23KV#1BBUS_KV | 23KV #1BBUS KV | BUS | [5 empty] | 159 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D06 | 柳營DS | 22 | 22kV | VJ51 | 柳51線(VJ51) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | F6 | KVAR | 柳51線 VJ51 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳51線KVAR | 23KV柳51線 KVAR | FEEDER | [5 empty] | 160 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ51 | 柳51線(VJ51) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | F6 | A | 柳51線 VJ51 R 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳51線A1 | 23KV柳51線 R相AMP | FEEDER | [5 empty] | 161 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ51 | 柳51線(VJ51) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | F6 | A | 柳51線 VJ51 S相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳51線A2 | 23KV柳51線 S相AMP | FEEDER | [5 empty] | 162 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ51 | 柳51線(VJ51) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | F6 | A | 柳51線 VJ51 T相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳51線A3 | 23KV柳51線 T相AMP | FEEDER | [5 empty] | 163 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ51 | 柳51線(VJ51) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | F6 | A | 柳51線 VJ51 N相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳51線A0 | 23KV柳51線 N相AMP | FEEDER | [5 empty] | 164 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ52 | 柳52線(VJ52) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | F7 | KVAR | 柳52線 VJ52 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳52線KVAR | 23KV柳52線 KVAR | FEEDER | [5 empty] | 165 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ52 | 柳52線(VJ52) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | F7 | A | 柳52線 VJ52 R相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳52線A1 | 23KV柳52線 R相AMP | FEEDER | [5 empty] | 166 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ52 | 柳52線(VJ52) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | F7 | A | 柳52線 VJ52 S相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳52線A2 | 23KV柳52線 S相AMP | FEEDER | [5 empty] | 167 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ52 | 柳52線(VJ52) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | F7 | A | 柳52線 VJ52 T相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳52線A3 | 23KV柳52線 T相AMP | FEEDER | [5 empty] | 168 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ52 | 柳52線(VJ52) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | F7 | A | 柳52線 VJ52 N相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳52線A0 | 23KV柳52線 N相AMP | FEEDER | [5 empty] | 169 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ53 | 柳53線(VJ53) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | F8 | KVAR | 柳53線 VJ53 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳53線KVAR | 23KV柳53線 KVAR | FEEDER | [5 empty] | 170 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ53 | 柳53線(VJ53) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | F8 | A | 柳53線 VJ53 R相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳53線A1 | 23KV柳53線 R相AMP | FEEDER | [5 empty] | 171 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ53 | 柳53線(VJ53) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | F8 | A | 柳53線 VJ53 S相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳53線A2 | 23KV柳53線 S相AMP | FEEDER | [5 empty] | 172 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ53 | 柳53線(VJ53) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | F8 | A | 柳53線 VJ53 T相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳53線A3 | 23KV柳53線 T相AMP | FEEDER | [5 empty] | 173 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ53 | 柳53線(VJ53) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | F8 | A | 柳53線 VJ53 N相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳53線A0 | 23KV柳53線 N相AMP | FEEDER | [5 empty] | 174 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ54 | 柳54線(VJ54) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | F9 | KVAR | 柳54線 VJ54 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳54線KVAR | 23KV柳54線 KVAR | FEEDER | [5 empty] | 175 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ54 | 柳54線(VJ54) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | F9 | A | 柳54線 VJ54 R相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳54線A1 | 23KV柳54線 R相AMP | FEEDER | [5 empty] | 176 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ54 | 柳54線(VJ54) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | F9 | A | 柳54線 VJ54 S 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳54線A2 | 23KV柳54線 S相AMP | FEEDER | [5 empty] | 177 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ54 | 柳54線(VJ54) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0098 |  |  | 1-E2 |  |  | F9 | A | 柳54線 VJ54 T相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳54線A3 | 23KV柳54線 T相AMP | FEEDER | [5 empty] | 178 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ54 | 柳54線(VJ54) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | F9 | A | 柳54線 VJ54 N相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳54線A0 | 23KV柳54線 N相AMP | FEEDER | [5 empty] | 179 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ55 | 柳55線(VJ55) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | F10 | KVAR | 柳55線 VJ55 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳55線KVAR | 23KV柳55線 KVAR | FEEDER | [5 empty] | 180 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ55 | 柳55線(VJ55) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0101 |  |  | 1-E5 |  |  | F10 | A | 柳55線 VJ55 R相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳55線A1 | 23KV柳55線 R相AMP | FEEDER | [5 empty] | 181 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ55 | 柳55線(VJ55) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | F10 | A | 柳55線 VJ55 S 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳55線A2 | 23KV柳55線 S相AMP | FEEDER | [5 empty] | 182 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ55 | 柳55線(VJ55) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | F10 | A | 柳55線 VJ55 T相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳55線A3 | 23KV柳55線 T相AMP | FEEDER | [5 empty] | 183 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ55 | 柳55線(VJ55) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | F10 | A | 柳55線 VJ55 N相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳55線A0 | 23KV柳55線 N相AMP | FEEDER | [5 empty] | 184 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | D-2A | MW | D-2A 330 瓦 | MW_-54_54(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | [5 empty] | 185 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | D-2A | MVAR | D-2A 330 乏 | MVAR_-36_36(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | [5 empty] | 186 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | D-2A | A | D-2A 330 R 相電流 | A_-3000_3000(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | [5 empty] | 187 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | D-2A | A | D-2A 330 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | [5 empty] | 188 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | D-2A | A | D-2A 330 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | [5 empty] | 189 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 2ABUS | #2ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0110 |  |  | 1-EE |  |  | PT-2A | KV | #2A PT R相電壓 | kV_-9_9(-2000_2000) | aba | B3/D06_A1 | [8 empty] | 柳營DS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS | [5 empty] | 190 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D06 | 柳營DS | 11 | 11kV | VJ31 | 十一線(VJ31) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | F11 | KVAR | 柳十一線 VJ31 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳31線KVAR | 11KV柳31線 KVAR | FEEDER | [5 empty] | 191 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ31 | 十一線(VJ31) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | F11 | A | 柳十一線 VJ31 R 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳31線A1 | 11KV柳31線 R相AMP | FEEDER | [5 empty] | 192 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ31 | 十一線(VJ31) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | F11 | A | 柳十一線 VJ31 S相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳31線A2 | 11KV柳31線 S相AMP | FEEDER | [5 empty] | 193 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ31 | 十一線(VJ31) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | F11 | A | 柳十一線 VJ31 T相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳31線A3 | 11KV柳31線 T相AMP | FEEDER | [5 empty] | 194 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ31 | 十一線(VJ31) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | F11 | A | 柳十一線 VJ31 N相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳31線A0 | 11KV柳31線 N相AMP | FEEDER | [5 empty] | 195 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ32 | 十二線(VJ32) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | F12 | KVAR | 柳十二線 VJ32 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳32線KVAR | 11KV柳32線 KVAR | FEEDER | [5 empty] | 196 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ32 | 十二線(VJ32) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | F12 | A | 柳十二線 VJ32 R相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳32線A1 | 11KV柳32線 R相AMP | FEEDER | [5 empty] | 197 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ32 | 十二線(VJ32) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | F12 | A | 柳十二線 VJ32 S相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳32線A2 | 11KV柳32線 S相AMP | FEEDER | [5 empty] | 198 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ32 | 十二線(VJ32) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | F12 | A | 柳十二線 VJ32 T相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳32線A3 | 11KV柳32線 T相AMP | FEEDER | [5 empty] | 199 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ32 | 十二線(VJ32) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | F12 | A | 柳十二線 VJ32 N相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳32線A0 | 11KV柳32線 N相AMP | FEEDER | [5 empty] | 200 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ33 | 十三線(VJ33) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | F13 | KVAR | 柳十三線 VJ33 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳33線KVAR | 11KV柳33線 KVAR | FEEDER | [5 empty] | 201 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ33 | 十三線(VJ33) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | F13 | A | 柳十三線 VJ33 R 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳33線A1 | 11KV柳33線 R相AMP | FEEDER | [5 empty] | 202 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ33 | 十三線(VJ33) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | F13 | A | 柳十三線 VJ33 S 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳33線A2 | 11KV柳33線 S相AMP | FEEDER | [5 empty] | 203 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ33 | 十三線(VJ33) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | F13 | A | 柳十三線 VJ33 T相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳33線A3 | 11KV柳33線 T相AMP | FEEDER | [5 empty] | 204 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ33 | 十三線(VJ33) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | F13 | A | 柳十三線 VJ33 N相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳33線A0 | 11KV柳33線 N相AMP | FEEDER | [5 empty] | 205 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ34 | 十四線(VJ34) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | F14 | KVAR | 柳十四線 VJ34 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳34線KVAR | 11KV柳34線 KVAR | FEEDER | [5 empty] | 206 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ34 | 十四線(VJ34) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | F14 | A | 柳十四線 VJ34 R 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳34線A1 | 11KV柳34線 R相AMP | FEEDER | [5 empty] | 207 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 0 |  | RTU | RTU |  | ADCL3 |  |  | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.3 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | [5 empty] | 208 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 0 |  | RTU | RTU |  | ADCH3 |  |  | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.3 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | [5 empty] | 209 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ34 | 十四線(VJ34) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | F14 | A | 柳十四線 VJ34 S 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳34線A2 | 11KV柳34線 S相AMP | FEEDER | [5 empty] | 210 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ34 | 十四線(VJ34) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | F14 | A | 柳十四線 VJ34 T 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳34線A3 | 11KV柳34線 T相AMP | FEEDER | [5 empty] | 211 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ34 | 十四線(VJ34) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | F14 | A | 柳十四線 VJ34 N相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳34線A0 | 11KV柳34線 N相AMP | FEEDER | [5 empty] | 212 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ35 | 十五線(VJ35) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0133 |  |  | 2-85 |  |  | F15 | KVAR | 柳十五線 VJ35 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳35線KVAR | 11KV柳35線 KVAR | FEEDER | [5 empty] | 213 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ35 | 十五線(VJ35) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | F15 | A | 柳十五線 VJ35 R 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳35線A1 | 11KV柳35線 R相AMP | FEEDER | [5 empty] | 214 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ35 | 十五線(VJ35) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0135 |  |  | 2-87 |  |  | F15 | A | 柳十五線 VJ35 S 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳35線A2 | 11KV柳35線 S相AMP | FEEDER | [5 empty] | 215 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ35 | 十五線(VJ35) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0136 |  |  | 2-88 |  |  | F15 | A | 柳十五線 VJ35 T 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳35線A3 | 11KV柳35線 T相AMP | FEEDER | [5 empty] | 216 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | VJ35 | 十五線(VJ35) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0137 |  |  | 2-89 |  |  | F15 | A | 柳十五線 VJ35 N相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳35線A0 | 11KV柳35線 N相AMP | FEEDER | [5 empty] | 217 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 100 | TIE(100) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0138 |  |  | 2-8A |  |  | TIE-2A | A | TIE-2A 100 R 相電流 | A_-2000_2000(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.11KV_100_A1 | 11KV 100 R相AMP | TIE | [5 empty] | 218 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 100 | TIE(100) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0139 |  |  | 2-8B |  |  | TIE-2A | A | TIE-2A 100 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.11KV_100_A2 | 11KV 100 S相AMP | TIE | [5 empty] | 219 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 100 | TIE(100) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0140 |  |  | 2-8C |  |  | TIE-2A | A | TIE-2A 100 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.11KV_100_A3 | 11KV 100 T相AMP | TIE | [5 empty] | 220 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0141 |  |  | 2-8D |  |  | D-2B | MW | D-2B 340 瓦 | MW_-108_108(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | [5 empty] | 221 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.216 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0142 |  |  | 2-8E |  |  | D-2B | MVAR | D-2B 340 乏 | MVAR_-72_72(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | [5 empty] | 222 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0143 |  |  | 2-8F |  |  | D-2B | A | D-2B 340 R 相電流 | A_-3000_3000(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | [5 empty] | 223 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0144 |  |  | 2-90 |  |  | D-2B | A | D-2B 340 S 相電流 | A_-3000_3000(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | [5 empty] | 224 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0145 |  |  | 2-91 |  |  | D-2B | A | D-2B 340 T 相電流 | A_-3000_3000(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | [5 empty] | 225 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 2BBUS | #2BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0146 |  |  | 2-92 |  |  | PT-2B | KV | #2B PT R相電壓 | kV_-18_18(-2000_2000) | bba | B3/D06_A1 | [8 empty] | 柳營DS.23KV#2BBUS_KV | 23KV #2BBUS KV | BUS | [5 empty] | 226 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D06 | 柳營DS | 22 | 22kV | VJ56 | 柳56線(VJ56) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0147 |  |  | 2-93 |  |  | F16 | KVAR | 柳56線 VJ56 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳56線KVAR | 23KV柳56線 KVAR | FEEDER | [5 empty] | 227 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ56 | 柳56線(VJ56) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0148 |  |  | 2-94 |  |  | F16 | A | 柳56線 VJ56 R 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳56線A1 | 23KV柳56線 R相AMP | FEEDER | [5 empty] | 228 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ56 | 柳56線(VJ56) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0149 |  |  | 2-95 |  |  | F16 | A | 柳56線 VJ56 S 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳56線A2 | 23KV柳56線 S相AMP | FEEDER | [5 empty] | 229 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ56 | 柳56線(VJ56) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0150 |  |  | 2-96 |  |  | F16 | A | 柳56線 VJ56 T 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳56線A3 | 23KV柳56線 T相AMP | FEEDER | [5 empty] | 230 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ56 | 柳56線(VJ56) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0151 |  |  | 2-97 |  |  | F16 | A | 柳56線 VJ56 N相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳56線A0 | 23KV柳56線 N相AMP | FEEDER | [5 empty] | 231 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ57 | 柳57線(VJ57) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0152 |  |  | 2-98 |  |  | F17 | KVAR | 柳57線 VJ57 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳57線KVAR | 23KV柳57線 KVAR | FEEDER | [5 empty] | 232 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ57 | 柳57線(VJ57) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0153 |  |  | 2-99 |  |  | F17 | A | 柳57線 VJ57 R 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳57線A1 | 23KV柳57線 R相AMP | FEEDER | [5 empty] | 233 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ57 | 柳57線(VJ57) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0154 |  |  | 2-9A |  |  | F17 | A | 柳57線 VJ57 S 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳57線A2 | 23KV柳57線 S相AMP | FEEDER | [5 empty] | 234 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ57 | 柳57線(VJ57) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0155 |  |  | 2-9B |  |  | F17 | A | 柳57線 VJ57 T 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳57線A3 | 23KV柳57線 T相AMP | FEEDER | [5 empty] | 235 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ57 | 柳57線(VJ57) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0156 |  |  | 2-9C |  |  | F17 | A | 柳57線 VJ57 N相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳57線A0 | 23KV柳57線 N相AMP | FEEDER | [5 empty] | 236 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ58 | 柳58線(VJ58) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0157 |  |  | 2-9D |  |  | F18 | KVAR | 柳58線 VJ58 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳58線KVAR | 23KV柳58線 KVAR | FEEDER | [5 empty] | 237 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ58 | 柳58線(VJ58) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0158 |  |  | 2-9E |  |  | F18 | A | 柳58線 VJ58 R 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳58線A1 | 23KV柳58線 R相AMP | FEEDER | [5 empty] | 238 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ58 | 柳58線(VJ58) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0159 |  |  | 2-9F |  |  | F18 | A | 柳58線 VJ58 S 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳58線A2 | 23KV柳58線 S相AMP | FEEDER | [5 empty] | 239 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ58 | 柳58線(VJ58) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0160 |  |  | 2-A0 |  |  | F18 | A | 柳58線 VJ58 T 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳58線A3 | 23KV柳58線 T相AMP | FEEDER | [5 empty] | 240 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ58 | 柳58線(VJ58) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0161 |  |  | 2-A1 |  |  | F18 | A | 柳58線 VJ58 N相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳58線A0 | 23KV柳58線 N相AMP | FEEDER | [5 empty] | 241 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ59 | 柳59線(VJ59) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0162 |  |  | 2-A2 |  |  | F19 | KVAR | 柳59線 VJ59 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳59線KVAR | 23KV柳59線 KVAR | FEEDER | [5 empty] | 242 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ59 | 柳59線(VJ59) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0163 |  |  | 2-A3 |  |  | F19 | A | 柳59線 VJ59 R 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳59線A1 | 23KV柳59線 R相AMP | FEEDER | [5 empty] | 243 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ59 | 柳59線(VJ59) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0164 |  |  | 2-A4 |  |  | F19 | A | 柳59線 VJ59 S 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳59線A2 | 23KV柳59線 S相AMP | FEEDER | [5 empty] | 244 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ59 | 柳59線(VJ59) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0165 |  |  | 2-A5 |  |  | F19 | A | 柳59線 VJ59 T 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳59線A3 | 23KV柳59線 T相AMP | FEEDER | [5 empty] | 245 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ59 | 柳59線(VJ59) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0166 |  |  | 2-A6 |  |  | F19 | A | 柳59線 VJ59 N相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳59線A0 | 23KV柳59線 N相AMP | FEEDER | [5 empty] | 246 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ60 | 柳60線(VJ60) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0167 |  |  | 2-A7 |  |  | F20 | KVAR | 柳60線 VJ60 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳60線KVAR | 23KV柳60線 KVAR | FEEDER | [5 empty] | 247 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ60 | 柳60線(VJ60) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0168 |  |  | 2-A8 |  |  | F20 | A | 柳60線 VJ60 R 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳60線A1 | 23KV柳60線 R相AMP | FEEDER | [5 empty] | 248 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ60 | 柳60線(VJ60) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0169 |  |  | 2-A9 |  |  | F20 | A | 柳60線 VJ60 S 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳60線A2 | 23KV柳60線 S相AMP | FEEDER | [5 empty] | 249 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ60 | 柳60線(VJ60) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0170 |  |  | 2-AA |  |  | F20 | A | 柳60線 VJ60 T 相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳60線A3 | 23KV柳60線 T相AMP | FEEDER | [5 empty] | 250 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | VJ60 | 柳60線(VJ60) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0171 |  |  | 2-AB |  |  | F20 | A | 柳60線 VJ60 N相電流 | A_-600_600(-2000_2000) |  | B2/D06_D1 | [8 empty] | 柳營DS.柳60線A0 | 23KV柳60線 N相AMP | FEEDER | [5 empty] | 251 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 200 | TIE(200) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0172 |  |  | 2-AC |  |  | TIE-2B | A | TIE-2B 200 R 相電流 | A_-2000_2000(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.23KV_200_A1 | 23KV 200 R相AMP | TIE | [5 empty] | 252 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 200 | TIE(200) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0173 |  |  | 2-AD |  |  | TIE-2B | A | TIE-2B 200 S 相電流 | A_-2000_2000(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.23KV_200_A2 | 23KV 200 S相AMP | TIE | [5 empty] | 253 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 200 | TIE(200) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0174 |  |  | 2-AE |  |  | TIE-2B | A | TIE-2B 200 T 相電流 | A_-2000_2000(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.23KV_200_A3 | 23KV 200 T相AMP | TIE | [5 empty] | 254 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 161 | 161kV | 1950 | #1SHR(1950) |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0175 |  |  | 2-AF |  |  | 1950 | ℃ | #1並聯電抗器 (1950) 線溫 | COIL_-120_120(-2000_2000) | [10 empty] | 柳營DS.161#1SHR_COIL | 161KV #1SHR 線溫 | OTHER | [5 empty] | 255 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D06 | 柳營DS | 161 | 161kV | 1950 | #1SHR(1950) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0176 |  |  | 2-B0 |  |  | 1950 | ℃ | #1並聯電抗器 (1950) 油溫 | OIL_-120_120(-2000_2000) | [10 empty] | 柳營DS.161#1SHR_OIL | 161KV #1SHR 油溫 | OTHER | [5 empty] | 256 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D06 | 柳營DS | 0 |  | RTU | RTU |  | ADCL4 |  |  | MvMoment | No4 AI參考點 10% |  | Y |  | AI | [6 empty] | 0192 |  |  | 2-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.4 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | [5 empty] | 257 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 0 |  | RTU | RTU |  | ADCH4 |  |  | MvMoment | No4 AI參考點 90% |  | Y |  | AI | [6 empty] | 0193 |  |  | 2-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.4 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D06_A1 | [8 empty] | 柳營DS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | [5 empty] | 258 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 161 | 161kV | 1510 | 柳營～新高紅線(1510) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D06C64R/T1 |  | 0000 |  |  | 1-00-00 |  |  | 1510 | ON/OFF | 柳營新高紅線(1510)CB ON/OFF |  | aaca | B2/D06_A1 | [8 empty] | 柳營DS.1510_CB | 1510(柳營新高紅線) CB | LINE161 | [5 empty] | 259 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 161 | 161kV | 1510 | 柳營～新高紅線(1510) |  | 21A |  |  | Status | 21RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0001 |  |  | 1-00-01 |  |  | 1510 | 21A | 柳營新高紅線(1510)21A |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1510_21A | 柳營新高紅線(1510) 21RY | LINE161 | [5 empty] | 260 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1510 | 柳營～新高紅線(1510) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | 1510 | PHA | 柳營新高紅線(1510)PHA |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1510_PHA | 柳營新高紅線(1510) 相間RY | LINE161 | [5 empty] | 261 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1510 | 柳營～新高紅線(1510) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0004 |  |  | 1-00-04 |  |  | 1510 | GDA | 柳營新高紅線(1510)GDA |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1510_GDA | 柳營新高紅線(1510) 接地RY | LINE161 | [5 empty] | 262 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1520 | 柳營～新高、榮特白線(1520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D06TN02W/T2 |  | 0005 |  |  | 1-00-05 |  |  | 1520 | ON/OFF | 柳營~新高、榮特白線(1520)CB ON/OFF |  | aada | B2/D06_A1 | [8 empty] | 柳營DS.1520_CB | 1520(柳營新高榮特白) CB | LINE161 | [5 empty] | 263 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 161 | 161kV | 1520 | 柳營～新高、榮特白線(1520) |  | 21A |  |  | Status | 21RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | 1520 | 21A | 柳營~新高、榮特白線(1520)21A |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1520_21A | 柳營新高榮特白(1520) 21RY | LINE161 | [5 empty] | 264 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1520 | 柳營～新高、榮特白線(1520) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-01-00 |  |  | 1520 | PHA | 柳營營高白線(1520)PHA |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1520_PHA | 柳營新高榮特白(1520) 相間RY | LINE161 | [5 empty] | 265 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1520 | 柳營～新高、榮特白線(1520) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | 1520 | GDA | 柳營營高白線(1520)GDA |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1520_GDA | 柳營新高榮特白(1520) 接地RY | LINE161 | [5 empty] | 266 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1530 | 新營～柳營山線(1530) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P01D06M/T2 |  | 0010 |  |  | 1-01-02 |  |  | 1530 | ON/OFF | 新營柳營山線(1530)CB ON/OFF |  | aafa | B2/D06_A1 | [8 empty] | 柳營DS.1530_CB | 1530(新營柳營山線) CB | LINE161 | [5 empty] | 267 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 161 | 161kV | 1530 | 新營～柳營山線(1530) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-03 |  |  | 1530 | 187A | 新營柳營山線(1530) 187A |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1530_87A | 新營柳營山線(1530) 87RY | LINE161 | [5 empty] | 268 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1530 | 新營～柳營山線(1530) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0013 |  |  | 1-01-05 |  |  | 1530 | PHA | 新營柳營山線(1530)PHA |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1530_PHA | 新營柳營山線(1530) 相間RY | LINE161 | [5 empty] | 269 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1540 | 新營～柳營海線(1540) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P01D06O/T2 |  | 0015 |  |  | 1-01-07 |  |  | 1540 | ON/OFF | 新營柳營海線(1540)CB ON/OFF |  | aaga | B2/D06_A1 | [8 empty] | 柳營DS.1540_CB | 1540(新營柳營海線) CB | LINE161 | [5 empty] | 270 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 161 | 161kV | 1540 | 新營～柳營海線(1540) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-02-00 |  |  | 1540 | 187A | 新營柳營海線(1540) 187A |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1540_87A | 新營柳營海線(1540) 87RY | LINE161 | [5 empty] | 271 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1540 | 新營～柳營海線(1540) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 |  |  | 1-02-02 |  |  | 1540 | PHA | 新營柳營海線(1540)PHA |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1540_PHA | 新營柳營海線(1540) 相間RY | LINE161 | [5 empty] | 272 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1540 | 新營～柳營海線(1540) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0019 |  |  | 1-02-03 |  |  | 1540 | GDA | 新營柳營海線(1540)GDA |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1540_GDA | 新營柳營海線(1540) 接地RY | LINE161 | [5 empty] | 273 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1550 | 嘉民～柳營山線(1550) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/E03D06M/T2 |  | 0020 |  |  | 1-02-04 |  |  | 1550 | ON/OFF | 嘉民柳營山線 1550 CB ON/OFF |  | aaia | B2/D06_A1 | [8 empty] | 柳營DS.1550_CB | 1550(嘉民柳營山線) CB | LINE161 | [5 empty] | 274 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 161 | 161kV | 1550 | 嘉民～柳營山線(1550) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-05 |  |  | 1550 | 87A | 嘉民柳營山線 1550 87A |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1550_87A | 嘉民柳營山線(1550) 87RY | LINE161 | [5 empty] | 275 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1550 | 嘉民～柳營山線(1550) |  | DTTA |  |  | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0022 |  |  | 1-02-06 |  |  | 1550 | DTTA | 嘉民柳營山線 1550 DTTA |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1550_DTTA | 嘉民柳營山線(1550)遠方遙跳 | OTHER | [5 empty] | 276 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1550 | 嘉民～柳營山線(1550) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0023 |  |  | 1-02-07 |  |  | 1550 | PHA | 嘉民柳營山線 1550 PHA |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1550_PHA | 嘉民柳營山線(1550) 相間RY | LINE161 | [5 empty] | 277 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1550 | 嘉民～柳營山線(1550) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0024 |  |  | 1-03-00 |  |  | 1550 | GDA | 嘉民柳營山線 1550 GDA |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1550_GDA | 嘉民柳營山線(1550) 接地RY | LINE161 | [5 empty] | 278 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1560 | 嘉民～柳營海線(1560) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/E03D06O/T2 |  | 0025 |  |  | 1-03-01 |  |  | 1560 | ON/OFF | 嘉民柳營海線 1560CB ON/OFF |  | aaja | B2/D06_A1 | [8 empty] | 柳營DS.1560_CB | 1560(嘉民柳營海線) CB | LINE161 | [5 empty] | 279 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 161 | 161kV | 1560 | 嘉民～柳營海線(1560) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0026 |  |  | 1-03-02 |  |  | 1560 | 87A | 嘉民柳營海線 1560 87A |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1560_87A | 嘉民柳營海線(1560) 87RY | LINE161 | [5 empty] | 280 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1560 | 嘉民～柳營海線(1560) |  | DTTA |  |  | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0027 |  |  | 1-03-03 |  |  | 1560 | DTTA | 嘉民柳營海線 1560 DTTA |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1560_DTTA | 嘉民柳營海線(1560)遠方遙跳 | OTHER | [5 empty] | 281 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1560 | 嘉民～柳營海線(1560) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0028 |  |  | 1-03-04 |  |  | 1560 | PHA | 嘉民柳營海線 1560 PHA |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1560_PHA | 嘉民柳營海線(1560) 相間RY | LINE161 | [5 empty] | 282 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1560 | 嘉民～柳營海線(1560) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0029 |  |  | 1-03-05 |  |  | 1560 | GDA | 嘉民柳營海線 1560 GDA |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1560_GDA | 嘉民柳營海線(1560) 接地RY | LINE161 | [5 empty] | 283 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0049 |  |  | 1-06-01 |  |  | Locate Empty | ON/OFF | TIE(1500)CB 52AS |  | aabz | B2/D06_A1 | [8 empty] | 柳營DS.1500_CB | 1500(TIE) CB | TIE | [5 empty] | 284 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0050 |  |  | 1-06-02 |  |  | Locate Empty | A/N | TIE(1500)RY 50A |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1500_50A | 161KV TIE(1500) 50RY | TIE | [5 empty] | 285 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0051 |  |  | 1-06-03 |  |  | #1 BUS | 87B1A | #1 BUS 87B1A |  |  | B2/D06_A1 | [8 empty] | 柳營DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | [5 empty] | 286 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | #2 BUS | 87B2A | #2 BUS 87B2A |  |  | B2/D06_A1 | [8 empty] | 柳營DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | [5 empty] | 287 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0053 |  |  | 1-06-05 |  |  | Locate Empty | A/N | 161KV 79 RY RCA |  |  | B3/D06_A1 | [8 empty] | 柳營DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | [5 empty] | 288 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0054 |  |  | 1-06-06 |  |  | OSCA | A/N | 161KV示波器啟動警報OSCA |  |  | B3/D06_A1 | [8 empty] | 柳營DS.161KV_OSCA_1 | 161KV示波器啟動警報(1) | OTHER | [5 empty] | 289 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/1DTR |  | 0056 |  |  | 1-07-00 |  |  | Locate Empty | ON/OFF | NO.1 1750 CB 52AS |  | aaeb | ELEM/D06_A1 | [8 empty] | 柳營DS.1750_CB | 1750(#1DTR) CB | MTR | [5 empty] | 290 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS |  |  | 1DTR | #1DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0057 |  |  | 1-07-01 |  |  | Locate Empty | A/N | NO.1 DTR 87A 87A |  |  | B1/D06_A1 | [8 empty] | 柳營DS.#1DTR_87A | #1DTR 87RY | MTR | [5 empty] | 291 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS |  |  | 1DTR | #1DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0058 |  |  | 1-07-02 |  |  | Locate Empty | A/N | NO.1 DTR 機械保護動作(96PA) |  |  | B1/D06_A1 | [8 empty] | 柳營DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | [5 empty] | 292 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS |  |  | 1DTR | #1DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0059 |  |  | 1-07-03 |  |  | Locate Empty | A/N | NO.1 DTR 51ZA 51ZA |  |  | B1/D06_A1 | [8 empty] | 柳營DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | [5 empty] | 293 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS |  |  | 1DTR | #1DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0060 |  |  | 1-07-04 |  |  | Locate Empty | A/N | NO.1 DTR PHA PHA |  |  | B1/D06_A1 | [8 empty] | 柳營DS.#1DTR_51A | #1DTR 51RY | MTR | [5 empty] | 294 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS |  |  | 1DTR | #1DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0061 |  |  | 1-07-05 |  |  | Locate Empty | A/N | NO.1 DTR GDA GDA |  |  | B1/D06_A1 | [8 empty] | 柳營DS.#1DTR_51NA | #1DTR 51N RY | MTR | [5 empty] | 295 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | T/1DTR(A) |  |  | 0062 |  |  | 1-07-06 |  |  | Locate Empty | ON/OFF | D1A 310 CB 52AS |  | aaaa | ELEM/D06_A1 | [8 empty] | 柳營DS.310_CB | 310(#1DTR) CB | MTR | [5 empty] | 296 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0063 |  |  | 1-08-00 |  |  | Locate Empty | A/N | D1A 310 PHA |  |  | B3/D06_A1 | [8 empty] | 柳營DS.310_PHA2 | 310開關箱IED RY PHA | OTHER | [5 empty] | 297 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0065 |  |  | 1-08-01 |  |  | Locate Empty | A/N | D1A 310 GDA |  |  | B3/D06_A1 | [8 empty] | 柳營DS.310_GDA | 310開關箱IED RY GDA | OTHER | [5 empty] | 298 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | T/1DTR(B) |  |  | 0066 |  |  | 1-08-02 |  |  | Locate Empty | ON/OFF | D1B 320 CB 52AS |  | baaa | ELEM/D06_A1 | [8 empty] | 柳營DS.320_CB | 320(#1DTR) CB | MTR | [5 empty] | 299 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0067 |  |  | 1-08-04 |  |  | Locate Empty | A/N | D1B 320 PHA |  |  | B3/D06_A1 | [8 empty] | 柳營DS.320_PHA2 | 320開關箱IED RY PHA | OTHER | [5 empty] | 300 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 |  |  | 1-08-05 |  |  | Locate Empty | A/N | D1B 320 GDA |  |  | B3/D06_A1 | [8 empty] | 柳營DS.320_GDA | 320開關箱IED RY GDA | OTHER | [5 empty] | 301 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2DTR |  | 0070 |  |  | 1-08-06 |  |  | Locate Empty | ON/OFF | NO.2 1760 CB 52AS |  | aahb | ELEM/D06_A1 | [8 empty] | 柳營DS.1760_CB | 1760(#2DTR) CB | MTR | [5 empty] | 302 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS |  |  | 2DTR | #2DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0071 |  |  | 1-08-07 |  |  | Locate Empty | A/N | NO.2 DTR 87A 87A |  |  | B1/D06_A1 | [8 empty] | 柳營DS.#2DTR_87A | #2DTR 87RY | MTR | [5 empty] | 303 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS |  |  | 2DTR | #2DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0072 |  |  | 1-09-00 |  |  | Locate Empty | A/N | NO.2 DTR 機械保護動作(96PA) |  |  | B1/D06_A1 | [8 empty] | 柳營DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | [5 empty] | 304 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS |  |  | 2DTR | #2DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0073 |  |  | 1-09-01 |  |  | Locate Empty | A/N | NO.2 DTR 51ZA 51ZA |  |  | B1/D06_A1 | [8 empty] | 柳營DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | [5 empty] | 305 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS |  |  | 2DTR | #2DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-09-02 |  |  | Locate Empty | A/N | NO.2 DTR PHA PHA |  |  | B1/D06_A1 | [8 empty] | 柳營DS.#2DTR_51A | #2DTR 51RY | MTR | [5 empty] | 306 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS |  |  | 2DTR | #2DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0075 |  |  | 1-09-03 |  |  | Locate Empty | A/N | NO.2 DTR GDA GDA |  |  | B1/D06_A1 | [8 empty] | 柳營DS.#2DTR_51NA | #2DTR 51N RY | MTR | [5 empty] | 307 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | T/2DTR(A) |  |  | 0076 |  |  | 1-09-04 |  |  | Locate Empty | ON/OFF | D2A 330 CB 52AS |  | abba | ELEM/D06_A1 | [8 empty] | 柳營DS.330_CB | 330(#2DTR) CB | MTR | [5 empty] | 308 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0077 |  |  | 1-09-06 |  |  | Locate Empty | A/N | D2A 330 PHA PHA |  |  | B3/D06_A1 | [8 empty] | 柳營DS.330_PHA2 | 330開關箱IED RY PHA | OTHER | [5 empty] | 309 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0079 |  |  | 1-09-07 |  |  | Locate Empty | A/N | D2A 330 GDA GDA |  |  | B3/D06_A1 | [8 empty] | 柳營DS.330_GDA | 330開關箱IED RY GDA | OTHER | [5 empty] | 310 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | T/2DTR(B) |  |  | 0080 |  |  | 1-0A-00 |  |  | Locate Empty | ON/OFF | D2B 340 CB 52AS |  | bbba | ELEM/D06_A1 | [8 empty] | 柳營DS.340_CB | 340(#2DTR) CB | MTR | [5 empty] | 311 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0081 |  |  | 1-0A-02 |  |  | Locate Empty | A/N | D2B 340 PHA PHA |  |  | B3/D06_A1 | [8 empty] | 柳營DS.340_PHA2 | 340開關箱IED RY PHA | OTHER | [5 empty] | 312 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0083 |  |  | 1-0A-03 |  |  | Locate Empty | A/N | D2B 340 GDA GDA |  |  | B3/D06_A1 | [8 empty] | 柳營DS.340_GDA | 340開關箱IED RY GDA | OTHER | [5 empty] | 313 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1950 | #1SHR(1950) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | R/1SHR |  | 0105 |  |  | 1-0D-01 |  |  | Locate Empty | ON/OFF | #1SHR 52AS |  | aala | B2/D06_A1 | [8 empty] | 柳營DS.1950_CB | 1950(161KV #1SHR) CB | OTHER | [5 empty] | 314 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 87A |  | B3 | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0106 |  |  | 1-0D-02 |  |  | Locate Empty | 87A | #1SHR 87A |  |  | B2/D06_A1 | [8 empty] | 柳營DS.161#1SHR_87A | 161KV #1SHR 87RY | OTHER | [5 empty] | 315 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 86A |  | B3,Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0107 |  |  | 1-0D-03 |  |  | Locate Empty | 86A | #1SHR 86A |  |  | B2/D06_A1 | [8 empty] | 柳營DS.161#1SHR_86A | 161KV #1SHR 86RY | OTHER | [5 empty] | 316 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 51A |  | B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0108 |  |  | 1-0D-04 |  |  | Locate Empty | GDA | #1SHR 51A |  |  | B2/D06_A1 | [8 empty] | 柳營DS.161#1SHR_51A | 161KV #1SHR 51RY | OTHER | [5 empty] | 317 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 96PA |  | B3 | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0109 |  |  | 1-0D-05 |  |  | Locate Empty | PHA | #1SHR 96A |  |  | B2/D06_A1 | [8 empty] | 柳營DS.161#1SHR96PA | 161KV #1SHR 機械保護動作 | OTHER | [5 empty] | 318 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | RTU | RTU |  | RTU_MCT |  |  | Status | RTU Master Ry | Open/Close | Y | E | DI-SP | [6 empty] | 0110 |  |  | 1-0D-06 |  |  | 161RTU | MCT_ SOE | RTU MASTER RY SOE |  |  | B3/D06_A1 | [16 empty] | 319 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D06 | 柳營DS | 11 | 11kV | VJ21 | 柳一線(VJ21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/VJ21/T1 |  |  | 0128 |  |  | 1-10-00 |  |  | F1 | ON/OFF | 柳一線 VJ21 CB 52AS |  | aadb | B2/D06_D1 | [8 empty] | 柳營DS.VJ21_CB | VJ21(11KV柳一線) CB | FEEDER | [5 empty] | 320 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | VJ21 | 柳一線(VJ21) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0129 |  |  | 1-10-01 |  |  | F1 | PHA | 柳一線 VJ21 RY PHA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ21_PHA | 11KV柳一線(VJ21) 相間RY | FEEDER | [5 empty] | 321 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ21 | 柳一線(VJ21) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-10-02 |  |  | F1 | GDA | 柳一線 VJ21 RY GDA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ21_GDA | 11KV柳一線(VJ21) 接地RY | FEEDER | [5 empty] | 322 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ22 | 柳二線(VJ22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/VJ22/T1 |  |  | 0131 |  |  | 1-10-03 |  |  | F2 | ON/OFF | 柳二線 VJ22 CB 52AS |  | aaeb | B2/D06_D1 | [8 empty] | 柳營DS.VJ22_CB | VJ22(11KV柳二線) CB | FEEDER | [5 empty] | 323 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | VJ22 | 柳二線(VJ22) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0132 |  |  | 1-10-04 |  |  | F2 | PHA | 柳二線 VJ22 RY PHA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ22_PHA | 11KV柳二線(VJ22) 相間RY | FEEDER | [5 empty] | 324 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ22 | 柳二線(VJ22) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0133 |  |  | 1-10-05 |  |  | F2 | GDA | 柳二線 VJ22 RY GDA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ22_GDA | 11KV柳二線(VJ22) 接地RY | FEEDER | [5 empty] | 325 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ23 | 柳三線(VJ23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/VJ23/T1 |  |  | 0134 |  |  | 1-10-06 |  |  | F3 | ON/OFF | 柳三線 VJ23 CB 52AS |  | aagb | B2/D06_D1 | [8 empty] | 柳營DS.VJ23_CB | VJ23(11KV柳三線) CB | FEEDER | [5 empty] | 326 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | VJ23 | 柳三線(VJ23) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0135 |  |  | 1-10-07 |  |  | F3 | PHA | 柳三線 VJ23 RY PHA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ23_PHA | 11KV柳三線(VJ23) 相間RY | FEEDER | [5 empty] | 327 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ23 | 柳三線(VJ23) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0136 |  |  | 1-11-00 |  |  | F3 | GDA | 柳三線 VJ23 RY GDA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ23_GDA | 11KV柳三線(VJ23) 接地RY | FEEDER | [5 empty] | 328 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ24 | 柳正線(VJ24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/VJ24/T1 |  |  | 0137 |  |  | 1-11-01 |  |  | F4 | ON/OFF | 柳正線 VJ24 CB 52AS |  | aahb | B2/D06_D1 | [8 empty] | 柳營DS.VJ24_CB | VJ24(11KV柳正線) CB | FEEDER | [5 empty] | 329 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | VJ24 | 柳正線(VJ24) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0138 |  |  | 1-11-02 |  |  | F4 | PHA | 柳正線 VJ24 RY PHA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ24_PHA | 11KV柳正線(VJ24) 相間RY | FEEDER | [5 empty] | 330 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ24 | 柳正線(VJ24) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0139 |  |  | 1-11-03 |  |  | F4 | GDA | 柳正線 VJ24 RY GDA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ24_GDA | 11KV柳正線(VJ24) 接地RY | FEEDER | [5 empty] | 331 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ25 | 柳五線(VJ25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/VJ25/T1 |  |  | 0140 |  |  | 1-11-04 |  |  | F5 | ON/OFF | 柳五線 VJ25 CB 52AS |  | aaib | B2/D06_D1 | [8 empty] | 柳營DS.VJ25_CB | VJ25(11KV柳五線) CB | FEEDER | [5 empty] | 332 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | VJ25 | 柳五線(VJ25) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0141 |  |  | 1-11-05 |  |  | F5 | PHA | 柳五線 VJ25 RY PHA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ25_PHA | 11KV柳五線(VJ25) 相間RY | FEEDER | [5 empty] | 333 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ25 | 柳五線(VJ25) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0142 |  |  | 1-11-06 |  |  | F5 | GDA | 柳五線 VJ25 RY GDA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ25_GDA | 11KV柳五線(VJ25) 接地RY | FEEDER | [5 empty] | 334 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | 210 | #1SC(210) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | A/LBS210^C/1SC(A) |  |  | 0143 |  |  | 1-11-07 |  |  | #1ASC | ON/OFF | #1SC 210 CB 52AS |  | aabb | B3/D06_A1 | [8 empty] | 柳營DS.210_CB | 210(11KV #1SC) CB | SC | [5 empty] | 335 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0144 |  |  | 1-12-00 |  |  | #1ASC | SCA | #1SC 210 CB RY SCA |  |  | B3/D06_A1 | [8 empty] | 柳營DS.210_SCA | 11KV #1SC 51,51N RY | SC | [5 empty] | 336 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0145 |  |  | 1-12-01 |  |  | #1ASC | UVA | #1SC 210 CB RY UVA |  |  | B3/D06_A1 | [8 empty] | 柳營DS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | [5 empty] | 337 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | 390 | #1SSTR(390) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | T/1SSTR |  |  | 0146 |  |  | 1-12-02 |  |  | #1SSTR | ON/OFF | #1SSTR 390 CB 52AS |  | aacb | B3/D06_A1 | [8 empty] | 柳營DS.390_CB | 390(#1SSTR) CB | OTHER | [5 empty] | 338 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | 390 | #1SSTR(390) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0147 |  |  | 1-12-03 |  |  | #1SSTR | PHA | #1SSTR 390 RY PHA |  |  | B3/D06_A1 | [8 empty] | 柳營DS.#1SSTR_51A | #1SSTR 51RY | OTHER | [5 empty] | 339 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | 390 | #1SSTR(390) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0148 |  |  | 1-12-04 |  |  | #1SSTR | GDA | #1SSTR 390 RY GDA |  |  | B3/D06_A1 | [8 empty] | 柳營DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | [5 empty] | 340 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ51 | 柳51線(VJ51) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/VJ51/T1 |  |  | 0149 |  |  | 1-12-05 |  |  | F6 | ON/OFF | 柳51線 VJ51 CB 52AS |  | bacb | B2/D06_D1 | [8 empty] | 柳營DS.VJ51_CB | VJ51(23KV柳51線) CB | FEEDER | [5 empty] | 341 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | VJ51 | 柳51線(VJ51) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0150 |  |  | 1-12-06 |  |  | F6 | PHA | 柳51線 VJ51 RY PHA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ51_PHA | 23KV柳51線(VJ51) 相間RY | FEEDER | [5 empty] | 342 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ51 | 柳51線(VJ51) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0151 |  |  | 1-12-07 |  |  | F6 | GDA | 柳51線 VJ51 RY GDA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ51_GDA | 23KV柳51線(VJ51) 接地RY | FEEDER | [5 empty] | 343 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ52 | 柳52線(VJ52) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/VJ52/T1 |  |  | 0152 |  |  | 1-13-00 |  |  | F7 | ON/OFF | 柳52線 VJ52 CB 52AS |  | badb | B2/D06_D1 | [8 empty] | 柳營DS.VJ52_CB | VJ52(23KV柳52線) CB | FEEDER | [5 empty] | 344 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | VJ52 | 柳52線(VJ52) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0153 |  |  | 1-13-01 |  |  | F7 | PHA | 柳52線 VJ52 RY PHA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ52_PHA | 23KV柳52線(VJ52) 相間RY | FEEDER | [5 empty] | 345 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ52 | 柳52線(VJ52) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0154 |  |  | 1-13-02 |  |  | F7 | GDA | 柳52線 VJ52 RY GDA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ52_GDA | 23KV柳52線(VJ52) 接地RY | FEEDER | [5 empty] | 346 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ53 | 柳53線(VJ53) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/VJ53/T1 |  |  | 0155 |  |  | 1-13-03 |  |  | F8 | ON/OFF | 柳53線 VJ53 CB 52AS |  | baeb | B2/D06_D1 | [8 empty] | 柳營DS.VJ53_CB | VJ53(23KV柳53線) CB | FEEDER | [5 empty] | 347 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | VJ53 | 柳53線(VJ53) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0156 |  |  | 1-13-04 |  |  | F8 | PHA | 柳53線 VJ53 RY PHA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ53_PHA | 23KV柳53線(VJ53) 相間RY | FEEDER | [5 empty] | 348 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ53 | 柳53線(VJ53) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0157 |  |  | 1-13-05 |  |  | F8 | GDA | 柳53線 VJ53 RY GDA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ53_GDA | 23KV柳53線(VJ53) 接地RY | FEEDER | [5 empty] | 349 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ54 | 柳54線(VJ54) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/VJ54/T1 |  |  | 0158 |  |  | 1-13-06 |  |  | F9 | ON/OFF | 柳54線 VJ54 CB 52AS |  | bagb | B2/D06_D1 | [8 empty] | 柳營DS.VJ54_CB | VJ54(23KV柳54線) CB | FEEDER | [5 empty] | 350 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | VJ54 | 柳54線(VJ54) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0159 |  |  | 1-13-07 |  |  | F9 | PHA | 柳54線 VJ54 RY PHA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ54_PHA | 23KV柳54線(VJ54) 相間RY | FEEDER | [5 empty] | 351 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ54 | 柳54線(VJ54) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0160 |  |  | 1-14-00 |  |  | F9 | GDA | 柳54線 VJ54 RY GDA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ54_GDA | 23KV柳54線(VJ54) 接地RY | FEEDER | [5 empty] | 352 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ55 | 柳55線(VJ55) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/VJ55/T1 |  |  | 0161 |  |  | 1-14-01 |  |  | F10 | ON/OFF | 柳55線 VJ55 CB 52AS |  | bahb | B2/D06_D1 | [8 empty] | 柳營DS.VJ55_CB | VJ55(23KV柳55線) CB | FEEDER | [5 empty] | 353 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | VJ55 | 柳55線(VJ55) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0162 |  |  | 1-14-02 |  |  | F10 | PHA | 柳55線 VJ55 RY PHA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ55_PHA | 23KV柳55線(VJ55) 相間RY | FEEDER | [5 empty] | 354 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ55 | 柳55線(VJ55) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0163 |  |  | 1-14-03 |  |  | F10 | GDA | 柳55線 VJ55 RY GDA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ55_GDA | 23KV柳55線(VJ55) 接地RY | FEEDER | [5 empty] | 355 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | 220 | #2SC(220) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | C/2SC |  |  | 0164 |  |  | 1-14-04 |  |  | #1BSC | ON/OFF | #2SC 220 CB 52AS |  | babb | B3/D06_A1 | [8 empty] | 柳營DS.220_CB | 220(23KV #2SC) CB | SC | [5 empty] | 356 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | 220 | #2SC(220) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0165 |  |  | 1-14-05 |  |  | #1BSC | SCA | #2SC 220 CB RY SCA |  |  | B3/D06_A1 | [8 empty] | 柳營DS.220_SCA | 23KV #2SC 51,51N RY | SC | [5 empty] | 357 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | 220 | #2SC(220) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0166 |  |  | 1-14-06 |  |  | #1BSC | UVA | #2SC 220 CB RY UVA |  |  | B3/D06_A1 | [8 empty] | 柳營DS.220_UVA | 23KV #2SC 27RY(欠壓) | SC | [5 empty] | 358 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ31 | 十一線(VJ31) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/VJ31/T1 |  |  | 0384 |  |  | 2-10-00 |  |  | F11 | ON/OFF | 柳十一線 VJ31 CB 52AS |  | abdb | B2/D06_D1 | [8 empty] | 柳營DS.VJ31_CB | VJ31(11KV柳31線) CB | FEEDER | [5 empty] | 359 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | VJ31 | 十一線(VJ31) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0385 |  |  | 2-10-01 |  |  | F11 | PHA | 柳十一線 VJ31 RY PHA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ31_PHA | 11KV柳31線(VJ31) 相間RY | FEEDER | [5 empty] | 360 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ31 | 十一線(VJ31) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0386 |  |  | 2-10-02 |  |  | F11 | GDA | 柳十一線 VJ31 RY GDA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ31_GDA | 11KV柳31線(VJ31) 接地RY | FEEDER | [5 empty] | 361 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ32 | 十二線(VJ32) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/VJ32/T1 |  |  | 0387 |  |  | 2-10-03 |  |  | F12 | ON/OFF | 柳十二線 VJ32 CB 52AS |  | abfb | B2/D06_D1 | [8 empty] | 柳營DS.VJ32_CB | VJ32(11KV柳32線) CB | FEEDER | [5 empty] | 362 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | VJ32 | 十二線(VJ32) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0388 |  |  | 2-10-04 |  |  | F12 | PHA | 柳十二線 VJ32 RY PHA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ32_PHA | 11KV柳32線(VJ32) 相間RY | FEEDER | [5 empty] | 363 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ32 | 十二線(VJ32) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0389 |  |  | 2-10-05 |  |  | F12 | GDA | 柳十二線 VJ32 RY GDA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ32_GDA | 11KV柳32線(VJ32) 接地RY | FEEDER | [5 empty] | 364 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ33 | 十三線(VJ33) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/VJ33/T1 |  |  | 0390 |  |  | 2-10-06 |  |  | F13 | ON/OFF | 柳十三線 VJ33 CB 52AS |  | abgb | B2/D06_D1 | [8 empty] | 柳營DS.VJ33_CB | VJ33(11KV柳33線) CB | FEEDER | [5 empty] | 365 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | VJ33 | 十三線(VJ33) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0391 |  |  | 2-10-07 |  |  | F13 | PHA | 柳十三線 VJ33 RY PHA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ33_PHA | 11KV柳33線(VJ33) 相間RY | FEEDER | [5 empty] | 366 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ33 | 十三線(VJ33) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0392 |  |  | 2-11-00 |  |  | F13 | GDA | 柳十三線 VJ33 RY GDA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ33_GDA | 11KV柳33線(VJ33) 接地RY | FEEDER | [5 empty] | 367 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ34 | 十四線(VJ34) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/VJ34/T1 |  |  | 0393 |  |  | 2-11-01 |  |  | F14 | ON/OFF | 柳十四線 VJ34 CB 52AS |  | abhb | B2/D06_D1 | [8 empty] | 柳營DS.VJ34_CB | VJ34(11KV柳34線) CB | FEEDER | [5 empty] | 368 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | VJ34 | 十四線(VJ34) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0394 |  |  | 2-11-02 |  |  | F14 | PHA | 柳十四線 VJ34 RY PHA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ34_PHA | 11KV柳34線(VJ34) 相間RY | FEEDER | [5 empty] | 369 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ34 | 十四線(VJ34) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0395 |  |  | 2-11-03 |  |  | F14 | GDA | 柳十四線 VJ34 RY GDA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ34_GDA | 11KV柳34線(VJ34) 接地RY | FEEDER | [5 empty] | 370 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ35 | 十五線(VJ35) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/VJ35/T1 |  |  | 0396 |  |  | 2-11-04 |  |  | F15 | ON/OFF | 柳十五線 VJ35 CB 52AS |  | abib | B2/D06_D1 | [8 empty] | 柳營DS.VJ35_CB | VJ35(11KV柳35線) CB | FEEDER | [5 empty] | 371 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | VJ35 | 十五線(VJ35) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0397 |  |  | 2-11-05 |  |  | F15 | PHA | 柳十五線 VJ35 RY PHA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ35_PHA | 11KV柳35線(VJ35) 相間RY | FEEDER | [5 empty] | 372 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ35 | 十五線(VJ35) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0398 |  |  | 2-11-06 |  |  | F15 | GDA | 柳十五線 VJ35 RY GDA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ35_GDA | 11KV柳35線(VJ35) 接地RY | FEEDER | [5 empty] | 373 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | 230 | #3SC(230) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | A/LBS230^C/3SC(A) |  |  | 0399 |  |  | 2-11-07 |  |  | #2ASC | ON/OFF | #3SC 230 CB 52AS |  | abcb | B3/D06_A1 | [8 empty] | 柳營DS.230_CB | 230(11KV #3SC) CB | SC | [5 empty] | 374 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | 230 | #3SC(230) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0400 |  |  | 2-12-00 |  |  | #2ASC | SCA | #3SC 230 RY SCA |  |  | B3/D06_A1 | [8 empty] | 柳營DS.230_SCA | 11KV #3SC 51,51N RY | SC | [5 empty] | 375 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | 230 | #3SC(230) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0401 |  |  | 2-12-01 |  |  | #2ASC | UVA | #3SC 230 RY UVA |  |  | B3/D06_A1 | [8 empty] | 柳營DS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | [5 empty] | 376 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | 100 | TIE(100) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/2ABus | B/1ABus |  |  | 0402 |  |  | 2-12-02 |  |  | TIE-2A | ON/OFF | TIE-2A 100 CB 52AS |  | abab | B3/D06_A1 | [8 empty] | 柳營DS.100_CB | 100(TIE) CB | TIE | [5 empty] | 377 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 11 | 11kV | 100 | TIE(100) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0403 |  |  | 2-12-03 |  |  | TIE-2A | PHA | TIE-2A 100 RY PHA |  |  | B3/D06_A1 | [8 empty] | 柳營DS.100_51A | 11KV TIE(100) 51RY | TIE | [5 empty] | 378 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | 100 | TIE(100) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0404 |  |  | 2-12-04 |  |  | TIE-2A | GDA | TIE-2A 100 RY GDA |  |  | B3/D06_A1 | [8 empty] | 柳營DS.100_51NA | 11KV TIE(100) 51N RY | TIE | [5 empty] | 379 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ56 | 柳56線(VJ56) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/VJ56/T1 |  |  | 0405 |  |  | 2-12-05 |  |  | F16 | ON/OFF | 柳56線 VJ56 CB 52AS |  | bbeb | B2/D06_D1 | [8 empty] | 柳營DS.VJ56_CB | VJ56(23KV柳56線) CB | FEEDER | [5 empty] | 380 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | VJ56 | 柳56線(VJ56) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0406 |  |  | 2-12-06 |  |  | F16 | PHA | 柳56線 VJ56 RY PHA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ56_PHA | 23KV柳56線(VJ56) 相間RY | FEEDER | [5 empty] | 381 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ56 | 柳56線(VJ56) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0407 |  |  | 2-12-07 |  |  | F16 | GDA | 柳56線 VJ56 RY GDA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ56_GDA | 23KV柳56線(VJ56) 接地RY | FEEDER | [5 empty] | 382 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ57 | 柳57線(VJ57) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/VJ57/T1 |  |  | 0408 |  |  | 2-13-00 |  |  | F17 | ON/OFF | 柳57線 VJ57 CB 52AS |  | bbgb | B2/D06_D1 | [8 empty] | 柳營DS.VJ57_CB | VJ57(23KV柳57線) CB | FEEDER | [5 empty] | 383 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | VJ57 | 柳57線(VJ57) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0409 |  |  | 2-13-01 |  |  | F17 | PHA | 柳57線 VJ57 RY PHA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ57_PHA | 23KV柳57線(VJ57) 相間RY | FEEDER | [5 empty] | 384 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ57 | 柳57線(VJ57) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0410 |  |  | 2-13-02 |  |  | F17 | GDA | 柳57線 VJ57 RY GDA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ57_GDA | 23KV柳57線(VJ57) 接地RY | FEEDER | [5 empty] | 385 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ58 | 柳58線(VJ58) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/VJ58/T1 |  |  | 0411 |  |  | 2-13-03 |  |  | F18 | ON/OFF | 柳58線 VJ58 CB 52AS |  | bbhb | B2/D06_D1 | [8 empty] | 柳營DS.VJ58_CB | VJ58(23KV柳58線) CB | FEEDER | [5 empty] | 386 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | VJ58 | 柳58線(VJ58) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0412 |  |  | 2-13-04 |  |  | F18 | PHA | 柳58線 VJ58 RY PHA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ58_PHA | 23KV柳58線(VJ58) 相間RY | FEEDER | [5 empty] | 387 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ58 | 柳58線(VJ58) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0413 |  |  | 2-13-05 |  |  | F18 | GDA | 柳58線 VJ58 RY GDA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ58_GDA | 23KV柳58線(VJ58) 接地RY | FEEDER | [5 empty] | 388 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ59 | 柳59線(VJ59) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/VJ59/T1 |  |  | 0414 |  |  | 2-13-06 |  |  | F19 | ON/OFF | 柳59線 VJ59 CB 52AS |  | bbib | B2/D06_D1 | [8 empty] | 柳營DS.VJ59_CB | VJ59(23KV柳59線) CB | FEEDER | [5 empty] | 389 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | VJ59 | 柳59線(VJ59) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0415 |  |  | 2-13-07 |  |  | F19 | PHA | 柳59線 VJ59 RY PHA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ59_PHA | 23KV柳59線(VJ59) 相間RY | FEEDER | [5 empty] | 390 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ59 | 柳59線(VJ59) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0416 |  |  | 2-14-00 |  |  | F19 | GDA | 柳59線 VJ59 RY GDA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ59_GDA | 23KV柳59線(VJ59) 接地RY | FEEDER | [5 empty] | 391 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ60 | 柳60線(VJ60) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/VJ60/T1 |  |  | 0417 |  |  | 2-14-01 |  |  | F20 | ON/OFF | 柳60線 VJ60 CB 52AS |  | bbjb | B2/D06_D1 | [8 empty] | 柳營DS.VJ60_CB | VJ60(23KV柳60線) CB | FEEDER | [5 empty] | 392 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | VJ60 | 柳60線(VJ60) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0418 |  |  | 2-14-02 |  |  | F20 | PHA | 柳60線 VJ60 RY PHA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ60_PHA | 23KV柳60線(VJ60) 相間RY | FEEDER | [5 empty] | 393 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ60 | 柳60線(VJ60) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0419 |  |  | 2-14-03 |  |  | F20 | GDA | 柳60線 VJ60 RY GDA |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ60_GDA | 23KV柳60線(VJ60) 接地RY | FEEDER | [5 empty] | 394 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | 240 | #4SC(240) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | C/4SC |  |  | 0420 |  |  | 2-14-04 |  |  | #2BSC | ON/OFF | #4SC 240 CB 52AS |  | bbdb | B3/D06_A1 | [8 empty] | 柳營DS.240_CB | 240(23KV #4SC) CB | SC | [5 empty] | 395 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | 240 | #4SC(240) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0421 |  |  | 2-14-05 |  |  | #2BSC | SCA | #4SC 240 RY SCA |  |  | B3/D06_A1 | [8 empty] | 柳營DS.240_SCA | 23KV #4SC 51,51N RY | SC | [5 empty] | 396 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | 240 | #4SC(240) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0422 |  |  | 2-14-06 |  |  | #2BSC | UVA | #4SC 240 RY UVA |  |  | B3/D06_A1 | [8 empty] | 柳營DS.240_UVA | 23KV #4SC 27RY(欠壓) | SC | [5 empty] | 397 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | 200 | TIE(200) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/2BBus | B/1BBus |  |  | 0423 |  |  | 2-14-07 |  |  | TIE-2B | ON/OFF | TIE-2B 200 CB 52AS |  | bbab | B3/D06_A1 | [8 empty] | 柳營DS.200_CB | 200(TIE) CB | TIE | [5 empty] | 398 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D06 | 柳營DS | 22 | 22kV | 200 | TIE(200) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0424 |  |  | 2-15-00 |  |  | TIE-2B | PHA | TIE-2B 200 RY PHA |  |  | B3/D06_A1 | [8 empty] | 柳營DS.200_51A | 23KV TIE(200) 51RY | TIE | [5 empty] | 399 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | 200 | TIE(200) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0425 |  |  | 2-15-01 |  |  | TIE-2B | GDA | TIE-2B 200 RY GDA |  |  | B3/D06_A1 | [8 empty] | 柳營DS.200_51NA | 23KV TIE(200) 51N RY | TIE | [5 empty] | 400 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | 490 | #2SSTR(490) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | T/2SSTR |  |  | 0426 |  |  | 2-15-02 |  |  | #2SSTR | ON/OFF | SSTR-2 490 CB 52AS |  | bbcb | B3/D06_A1 | [8 empty] | 柳營DS.490_CB | 490(#2SSTR) CB | OTHER | [5 empty] | 401 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | 490 | #2SSTR(490) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0427 |  |  | 2-15-03 |  |  | #2SSTR | PHA | SSTR-2 490 RY PHA |  |  | B3/D06_A1 | [8 empty] | 柳營DS.#2SSTR_51A | #2SSTR 51RY | OTHER | [5 empty] | 402 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | 490 | #2SSTR(490) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0428 |  |  | 2-15-04 |  |  | #2SSTR | GDA | SSTR-2 490 RY GDA |  |  | B3/D06_A1 | [8 empty] | 柳營DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | [5 empty] | 403 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | ComPoint |  |  | 25TA |  |  | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0492 |  |  | 2-1D-04 |  |  | 25RY | A/N | 25TA 同步校核裝置超時 |  |  | B3/D06_A1 | [8 empty] | 柳營DS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | [5 empty] | 404 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | ComPoint |  |  | 25PFA |  |  | Status | 同步校核電驛電源 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0493 |  |  | 2-1D-05 |  |  | 25RY | A/N | 25PFA 同步校核裝置電源 |  |  | B3/D06_A1 | [8 empty] | 柳營DS.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER | [5 empty] | 405 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0494 |  |  | 2-1D-06 |  |  | 310 | 81A | #1DTR D1A 310 低頻電驛動作 |  |  | B3/D06_A1 | [8 empty] | 柳營DS.81RY_A/S(1) | 310低頻電驛動作/復歸 | OTHER | [5 empty] | 406 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
D06 | 柳營DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0495 |  |  | 2-1D-07 |  |  | 320 | 81A | #1DTR D1B 320 低頻電驛動作 |  |  | B3/D06_A1 | [8 empty] | 柳營DS.81RY_A/S(2) | 320低頻電驛動作/復歸 | OTHER | [5 empty] | 407 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
D06 | 柳營DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0496 |  |  | 2-1E-00 |  |  | 330 | 81A | #2DTR D2A 330 低頻電驛動作 |  |  | B3/D06_A1 | [8 empty] | 柳營DS.81RY_A/S(3) | 330低頻電驛動作/復歸 | OTHER | [5 empty] | 408 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
D06 | 柳營DS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0768 |  |  | 1-30-00 |  |  | Test CB | ON/OFF | TEST C.B. |  |  | ELEM/ALL | [8 empty] | 柳營DS.TEST_CB | TEST CB | OTHER | [5 empty] | 409 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | RTU | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0769 |  |  | 1-30-01 |  |  | Locate Empty | L/R | LOCAL/REMOTE STATUS |  |  | ELEM/D06_A1 | [8 empty] | 柳營DS.RTU_S/L | RTU SUPY/LOCAL | OTHER | [5 empty] | 410 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
D06 | 柳營DS | 161 | 161kV | 1530 | 新營～柳營山線(1530) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0774 |  |  | 1-30-06 |  |  | 1530 | USE/LOCK | 新營柳營山線(1530) 87S |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1530_87UL | 新營柳營山線(1530) 87RY U/L | LINE161 | [5 empty] | 411 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D06 | 柳營DS | 161 | 161kV | 1530 | 新營～柳營山線(1530) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0775 |  |  | 1-30-07 |  |  | 1530 | USE/LOCK | 新營柳營山線(1530) 79S |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1530_79UL | 新營柳營山線(1530) 79RY U/L | LINE161 | [5 empty] | 412 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D06 | 柳營DS | 161 | 161kV | 1540 | 新營～柳營海線(1540) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0776 |  |  | 1-30-08 |  |  | 1540 | USE/LOCK | 新營柳營海線(1540) 87S |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1540_87UL | 新營柳營海線(1540) 87RY U/L | LINE161 | [5 empty] | 413 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D06 | 柳營DS | 161 | 161kV | 1540 | 新營～柳營海線(1540) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0777 |  |  | 1-30-09 |  |  | 1540 | USE/LOCK | 新營柳營海線(1540) 79S |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1540_79UL | 新營柳營海線(1540) 79RY U/L | LINE161 | [5 empty] | 414 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D06 | 柳營DS | 161 | 161kV | 1550 | 嘉民～柳營山線(1550) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0778 |  |  | 1-30-10 |  |  | 1550 | USE/LOCK | 嘉民柳營山線 1550 87S |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1550_87UL | 嘉民柳營山線(1550) 87RY U/L | LINE161 | [5 empty] | 415 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D06 | 柳營DS | 161 | 161kV | 1550 | 嘉民～柳營山線(1550) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0779 |  |  | 1-30-11 |  |  | 1550 | USE/LOCK | 嘉民柳營山線 1550 79S |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1550_79UL | 嘉民柳營山線(1550) 79RY U/L | LINE161 | [5 empty] | 416 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D06 | 柳營DS | 161 | 161kV | 1560 | 嘉民～柳營海線(1560) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0780 |  |  | 1-30-12 |  |  | 1560 | USE/LOCK | 嘉民柳營海線 (1560) 87S |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1560_87UL | 嘉民柳營海線(1560) 87RY U/L | LINE161 | [5 empty] | 417 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D06 | 柳營DS | 161 | 161kV | 1560 | 嘉民～柳營海線(1560) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0781 |  |  | 1-30-13 |  |  | 1560 | USE/LOCK | 嘉民柳營海線 (1560) 79S |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1560_79UL | 嘉民柳營海線(1560) 79RY U/L | LINE161 | [5 empty] | 418 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D06 | 柳營DS |  |  | 1DTR | #1DTR |  | 87UL1 |  |  | Status | 第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0790 |  |  | 1-31-06 |  |  | Locate Empty | USE/LOCK | NO.1 D.TR. 187S |  |  | B1/D06_A1 | [8 empty] | 柳營DS.161#1DTR_187UL | 161KV #1DTR 187RY U/L | OTHER | [5 empty] | 419 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D06 | 柳營DS |  |  | 1DTR(A) | #1DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0791 |  |  | 1-31-07 |  |  | Locate Empty | 遙控/現場 | NO.1 D.TR. S/L (A) 143R1S3 |  | c | B1/D06_A1 | [8 empty] | 柳營DS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | [5 empty] | 420 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D06 | 柳營DS |  |  | 1DTR(A) | #1DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0792 |  |  | 1-31-08 |  |  | Locate Empty | OLTC A/M | NO.1 D.TR. A/M (A) 1AX-S1 |  |  | B1/D06_A1 | [8 empty] | 柳營DS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | [5 empty] | 421 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D06 | 柳營DS |  |  | 1DTR(B) | #1DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0793 |  |  | 1-31-09 |  |  | Locate Empty | 遙控/現場 | NO.1 D.TR. S/L (B) 143R2S3 |  | b | B1/D06_A1 | [8 empty] | 柳營DS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | [5 empty] | 422 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D06 | 柳營DS |  |  | 1DTR(B) | #1DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0794 |  |  | 1-31-10 |  |  | Locate Empty | OLTC A/M | NO.1 D.TR. A/M (B) 1AX-S2 |  |  | B1/D06_A1 | [8 empty] | 柳營DS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | [5 empty] | 423 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D06 | 柳營DS |  |  | 1DTR | #1DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0795 |  |  | 1-31-11 |  |  | Locate Empty | A/N | NO.1 D.TR.撲氣電驛(1) 196B1 |  |  | B1/D06_A1 | [8 empty] | 柳營DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | [5 empty] | 424 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS |  |  | 1DTR | #1DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0796 |  |  | 1-31-12 |  |  | Locate Empty | A/N | NO.1 D.TR.撲氣電驛(2) 196B2 |  |  | B1/D06_A1 | [8 empty] | 柳營DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | [5 empty] | 425 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS |  |  | 1DTR | #1DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0797 |  |  | 1-31-13 |  |  | Locate Empty | A/N | NO.1 D.TR.放壓裝置 196D |  |  | B1/D06_A1 | [8 empty] | 柳營DS.#1DTR_96D | #1DTR 96D RY | MTR | [5 empty] | 426 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS |  |  | 1DTR | #1DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0798 |  |  | 1-31-14 |  |  | Locate Empty | A/N | NO.1 D.TR.衝擊油壓 196P |  |  | B1/D06_A1 | [8 empty] | 柳營DS.#1DTR_96P | #1DTR 96P RY | MTR | [5 empty] | 427 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS |  |  | 1DTR | #1DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0799 |  |  | 1-31-15 |  |  | Locate Empty | A/N | NO.1 D.TR. ULTC 163Q |  |  | B1/D06_A1 | [8 empty] | 柳營DS.#1DTR_63Q | #1DTR 63Q RY | MTR | [5 empty] | 428 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS |  |  | 1DTR | #1DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0800 |  |  | 1-32-00 |  |  | Locate Empty | A/N | NO.1 D.TR.輕故障 1TRF |  |  | B1/D06_A1 | [8 empty] | 柳營DS.#1DTR_TRF | #1DTR 輕故障 | MTR | [5 empty] | 429 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D06 | 柳營DS |  |  | 1DTR | #1DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0801 |  |  | 1-32-01 |  |  | Locate Empty | A/N | NO.1 D.TR.重故障 1TRA |  | a | B1/D06_A1 | [8 empty] | 柳營DS.#1DTR_TRA | #1DTR 重故障 | MTR | [5 empty] | 430 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D06 | 柳營DS |  |  | 2DTR | #2DTR |  | 87UL1 |  |  | Status | 第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0802 |  |  | 1-32-02 |  |  | Locate Empty | USE/LOCK | NO.2 D.TR. 287S |  |  | B1/D06_A1 | [8 empty] | 柳營DS.161#2DTR_187UL | 161KV #2DTR 187RY U/L | OTHER | [5 empty] | 431 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D06 | 柳營DS |  |  | 2DTR(A) | #2DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0803 |  |  | 1-32-03 |  |  | Locate Empty | 遙控/現場 | NO.2 D.TR. S/L (A) 243R1S3 |  | c | B1/D06_A1 | [8 empty] | 柳營DS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | [5 empty] | 432 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D06 | 柳營DS |  |  | 2DTR(A) | #2DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0804 |  |  | 1-32-04 |  |  | Locate Empty | OLTC A/M | NO.2 D.TR. A/M (A) 2AX-S1 |  |  | B1/D06_A1 | [8 empty] | 柳營DS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | [5 empty] | 433 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D06 | 柳營DS |  |  | 2DTR(B) | #2DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0805 |  |  | 1-32-05 |  |  | Locate Empty | 遙控/現場 | NO.2 D.TR. S/L (B) 243R2S3 |  | b | B1/D06_A1 | [8 empty] | 柳營DS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | [5 empty] | 434 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D06 | 柳營DS |  |  | 2DTR(B) | #2DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0806 |  |  | 1-32-06 |  |  | Locate Empty | OLTC A/M | NO.2 D.TR. A/M (B) 2AX-S2 |  |  | B1/D06_A1 | [8 empty] | 柳營DS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | [5 empty] | 435 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D06 | 柳營DS |  |  | 2DTR | #2DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0807 |  |  | 1-32-07 |  |  | Locate Empty | A/N | NO.2 D.TR.撲氣電驛(1) 296B1 |  |  | B1/D06_A1 | [8 empty] | 柳營DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | [5 empty] | 436 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS |  |  | 2DTR | #2DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0808 |  |  | 1-32-08 |  |  | Locate Empty | A/N | NO.2 D.TR.撲氣電驛(2) 296B2 |  |  | B1/D06_A1 | [8 empty] | 柳營DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | [5 empty] | 437 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS |  |  | 2DTR | #2DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0809 |  |  | 1-32-09 |  |  | Locate Empty | A/N | NO.2 D.TR.放壓裝置 296D |  |  | B1/D06_A1 | [8 empty] | 柳營DS.#2DTR_96D | #2DTR 96D RY | MTR | [5 empty] | 438 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS |  |  | 2DTR | #2DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0810 |  |  | 1-32-10 |  |  | Locate Empty | A/N | NO.2 D.TR.衝擊油壓 296P |  |  | B1/D06_A1 | [8 empty] | 柳營DS.#2DTR_96P | #2DTR 96P RY | MTR | [5 empty] | 439 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS |  |  | 2DTR | #2DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0811 |  |  | 1-32-11 |  |  | Locate Empty | A/N | NO.2 D.TR. ULTC 263Q |  |  | B1/D06_A1 | [8 empty] | 柳營DS.#2DTR_63Q | #2DTR 63Q RY | MTR | [5 empty] | 440 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS |  |  | 2DTR | #2DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0812 |  |  | 1-32-12 |  |  | Locate Empty | A/N | NO.2 D.TR.輕故障 2TRF |  |  | B1/D06_A1 | [8 empty] | 柳營DS.#2DTR_TRF | #2DTR 輕故障 | MTR | [5 empty] | 441 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D06 | 柳營DS |  |  | 2DTR | #2DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0813 |  |  | 1-32-13 |  |  | Locate Empty | A/N | NO.2 D.TR.重故障 2TRA |  | a | B1/D06_A1 | [8 empty] | 柳營DS.#2DTR_TRA | #2DTR 重故障 | MTR | [5 empty] | 442 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | StaDev | 所內設施 |  | Fire1 | 受信總機 |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0834 |  |  | 1-34-02 |  |  | 火災警報(1) | A/N | 火災警報(1)受信總機 |  |  | B3/D06_A1 | [8 empty] | 柳營DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | [5 empty] | 443 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | StaDev | 所內設施 |  | Fire2 |  |  | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0835 |  |  | 1-34-03 |  |  | 火災警報(2) | A/N | 火災警報(2) |  |  | B3/D06_A1 | [8 empty] | 柳營DS.火災警報(2) | 火災警報(2) | OTHER | [5 empty] | 444 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | StaDev | 所內設施 |  | Fire3 |  |  | Status | 火災警報3 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0836 |  |  | 1-34-04 |  |  | 火災警報(3) | A/N | 火災警報(3) |  |  | B3/D06_A1 | [8 empty] | 柳營DS.火災警報(3) | 火災警報(3) | OTHER | [5 empty] | 445 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | StaDev | 所內設施 |  | Fire4 |  |  | Status | 火災警報4 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0837 |  |  | 1-34-05 |  |  | 火災警報(4) | A/N | 火災警報(4) |  |  | B3/D06_A1 | [8 empty] | 柳營DS.火災警報(4) | 火災警報(4) | OTHER | [5 empty] | 446 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | StaDev | 所內設施 |  | Fire5 |  |  | Status | 火災警報5 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0838 |  |  | 1-34-06 |  |  | 火災警報(5) | A/N | 火災警報(5) |  |  | B3/D06_A1 | [8 empty] | 柳營DS.火災警報(5) | 火災警報(5) | OTHER | [5 empty] | 447 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | StaDev | 所內設施 |  | Door1 | 1樓門禁警報 |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0839 |  |  | 1-34-07 |  |  | Locate Empty | A/N | 無人化門禁(一) 1樓門禁警報 |  |  | B3/D06_A1 | [8 empty] | 柳營DS.無人化門禁(1) | 無人化門禁(1)建築物大門 | OTHER | [5 empty] | 448 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | StaDev | 所內設施 |  | Door2 | 控制室門禁警報 |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0840 |  |  | 1-34-08 |  |  | Locate Empty | A/N | 無人化門禁(二) 控制室門禁警報 |  |  | B3/D06_A1 | [8 empty] | 柳營DS.無人化門禁(2) | 無人化門禁(2)控制室大門 | OTHER | [5 empty] | 449 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | StaDev | 所內設施 |  | Door3 | 保全警報 |  | Status | 無人化門禁3 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0841 |  |  | 1-34-09 |  |  | Locate Empty | A/N | 無人化門禁(三) 保全警報 |  |  | B3/D06_A1 | [8 empty] | 柳營DS.無人化門禁(3) | 無人化門禁(3)保全警報 | OTHER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | StaDev | 所內設施 |  | Door4 | 161KV 電驛室門禁警報 |  | Status | 無人化門禁4 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0842 |  |  | 1-34-10 |  |  | Locate Empty | A/N | 無人化門禁(四) 161KV 電驛室門禁警報 |  |  | B3/D06_A1 | [8 empty] | 柳營DS.無人化門禁(4) | 無人化門禁(4)電驛室門禁警報 | OTHER | [5 empty] | 451 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | NULL | NULL |  | Door5 |  | Element | Status | 無人化門禁5 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0843 |  |  | 1-34-11 |  |  | Locate Empty | A/N | 無人化門禁(五) |  |  | B1/D06_A1 | [8 empty] | 柳營DS.無人化門禁(5) | 無人化門禁(5) | OTHER | [5 empty] | 452 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | StaDev | 所內設施 |  | DD_Light |  |  | Status | 路燈照明 | OFF/ON | Y | 5 | DI-SP | [6 empty] | 0845 |  |  | 1-34-13 |  |  | Locate Empty | ON/OFF | 路燈 FLB |  |  | B3/D06_A1 | [8 empty] | 柳營DS.開關場照明(B) | 路燈照明 | OTHER | [5 empty] | 453 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
D06 | 柳營DS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0846 |  |  | 1-34-14 |  |  | Locate Empty | ON/OFF | 所內電源ACB1 |  |  | B3/D06_A1 | [8 empty] | 柳營DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | [5 empty] | 454 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D06 | 柳營DS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0847 |  |  | 1-34-15 |  |  | Locate Empty | ON/OFF | 所內電源ACB2 |  |  | B3/D06_A1 | [8 empty] | 柳營DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | [5 empty] | 455 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D06 | 柳營DS | 0 |  | StaDev | 所內設施 |  | ACBT |  |  | Status | 所內電源ACB TIE | Close/Open | Y | 3 | DI-SP | [6 empty] | 0848 |  |  | 1-35-00 |  |  | Locate Empty | ON/OFF | 所內電源ACB TIE |  |  | B3/D06_A1 | [8 empty] | 柳營DS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | [5 empty] | 456 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ON/OFF | OFF
D06 | 柳營DS | 0 |  | ComPoint |  |  | OPA |  |  | Status | 充油電纜低壓警報 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0849 |  |  | 1-35-01 |  |  | Locate Empty | A/N | 充油電纜警報 OPA |  |  | B3/D06_A1 | [8 empty] | 柳營DS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | [5 empty] | 457 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0850 |  |  | 1-35-02 |  |  | Locate Empty | A/N | 所內欠壓警報 STUV |  |  | ELEM/D06_A1 | [8 empty] | 柳營DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | [5 empty] | 458 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | StaDev | 所內設施 |  | Water1 |  |  | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0851 |  |  | 1-35-03 |  |  | 地下室 | A/N | 地下室水位第一段警報 |  |  | B3/D06_A1 | [8 empty] | 柳營DS.水位警報(1) | 地下室水位警報(1) | OTHER | [5 empty] | 459 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | StaDev | 所內設施 |  | Water2 |  |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0852 |  |  | 1-35-04 |  |  | 地下室 | A/N | 地下室水位第二段警報 |  |  | B3/D06_A1 | [8 empty] | 柳營DS.水位警報(2) | 地下室水位警報(2) | OTHER | [5 empty] | 460 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0853 |  |  | 1-35-05 |  |  | Locate Empty | A/N | 161KV CB 重故障 CBA |  |  | B3/D06_A1 | [8 empty] | 柳營DS.161KV_CBA | 161KV斷路器重故障 | OTHER | [5 empty] | 461 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0854 |  |  | 1-35-06 |  |  | Locate Empty | A/N | 161KV CB 輕故障 CBF |  |  | B3/D06_A1 | [8 empty] | 柳營DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | [5 empty] | 462 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0855 |  |  | 1-35-07 |  |  | Locate Empty | A/N | NFB跳脫警報 DCA |  |  | ELEM/D06_A1 | [8 empty] | 柳營DS.直流電源DCA | 直流電源故障警報 | OTHER | [5 empty] | 463 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0856 |  |  | 1-35-08 |  |  | Locate Empty | A/N | ACB警報 ACBA |  |  | B3/D06_A1 | [8 empty] | 柳營DS.所內電源ACBA | 所內電源故障警報 | OTHER | [5 empty] | 464 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0857 |  |  | 1-35-09 |  |  | Locate Empty | A/N | 161KV NO.1 BUS欠壓 VUA1 |  |  | B2/D06_A1 | [8 empty] | 柳營DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | [5 empty] | 465 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0858 |  |  | 1-35-10 |  |  | Locate Empty | A/N | 161KV NO.2 BUS欠壓 VUA2 |  |  | B2/D06_A1 | [8 empty] | 柳營DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | [5 empty] | 466 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0859 |  |  | 1-35-11 |  |  | Locate Empty | A/N | 充電機警報 CHG1 |  |  | B3/D06_A1 | [8 empty] | 柳營DS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | [5 empty] | 467 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0860 |  |  | 1-35-12 |  |  | Locate Empty | A/N | DC接地警報 DCE |  |  | ELEM/D06_A1 | [8 empty] | 柳營DS.直流電源DCE | 直流電源接地故障警報 | OTHER | [5 empty] | 468 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | ComPoint |  |  | COMT |  |  | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0861 |  |  | 1-35-13 |  |  | Locate Empty | A/N | 161KV CB空壓機超時運轉 COMT |  |  | B3/D06_A1 | [8 empty] | 柳營DS.161空壓機COMT | 161KV空壓機運轉超時警報 | OTHER | [5 empty] | 469 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | ComPoint |  |  | 60A |  |  | Status | 電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0862 |  |  | 1-35-14 |  |  | Locate Empty | A/N | 23KV SC 60-RY 警報 60A |  |  | B3/D06_A1 | [8 empty] | 柳營DS.11KV_SC_60A | 23/11KV SC 60A | OTHER | [5 empty] | 470 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | StaDev | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0863 |  |  | 1-35-15 |  |  | Locate Empty | A/N | PSF (其他輕故障) |  |  | B3/D06_A1 | [8 empty] | 柳營DS.其他輕故障 | 變電所內其他輕故障 | OTHER | [5 empty] | 471 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | StaDev | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0864 |  |  | 1-36-00 |  |  | Locate Empty | A/N | PSA (其他重故障) |  |  | B3/D06_A1 | [8 empty] | 柳營DS.其他重故障 | 變電所內其他重故障 | OTHER | [5 empty] | 472 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0865 |  |  | 1-36-01 |  |  | Locate Empty | A/N | 22KV CB重故障 CBA |  |  | ELEM/D06_A1 | [8 empty] | 柳營DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | [5 empty] | 473 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0866 |  |  | 1-36-02 |  |  | Locate Empty | A/N | 22KV CB輕故障 CBF |  |  | ELEM/D06_A1 | [8 empty] | 柳營DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | [5 empty] | 474 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | ComPoint |  |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0867 |  |  | 1-36-03 |  |  | Locate Empty | A/N | 22KV FEEDER 79RY LOA |  |  | B3/D06_A1 | [8 empty] | 柳營DS.11/23KV_LOA | 11/23KV饋線復閉失敗閉鎖 | OTHER | [5 empty] | 475 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | StaDev | 所內設施 |  | OilLeak1 |  |  | Status | 洩油池水位警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0868 |  |  | 1-36-04 |  |  | Locate Empty | A/N | OW1蓄油池水位警報1 WPF |  |  | B3/D06_A1 | [8 empty] | 柳營DS.洩油池警報(1) | 洩油池水位警報(1) | OTHER | [5 empty] | 476 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | StaDev | 所內設施 |  | OilLeak2 |  |  | Status | 洩油池水位警報2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0869 |  |  | 1-36-05 |  |  | Locate Empty | A/N | OW2蓄油池水位警報2 WPA |  |  | B3/D06_A1 | [8 empty] | 柳營DS.洩油池警報(2) | 洩油池水位警報(2) | OTHER | [5 empty] | 477 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0870 |  |  | 1-36-06 |  |  | 通訊室 | A/N | 通訊充電機故障 CHG2 |  |  | B3/D06_A1 | [8 empty] | 柳營DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | [5 empty] | 478 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0871 |  |  | 1-36-07 |  |  | 通訊室 | A/N | ACFA (通訊設備AC故障) |  |  | B3/D06_A1 | [8 empty] | 柳營DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | [5 empty] | 479 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | StaDev | 所內設施 |  | R_Temp |  |  | Status | 溫度警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0874 |  |  | 1-36-10 |  |  | 通訊室 | A/N | 通信室溫控警報 |  |  | B3/D06_A1 | [8 empty] | 柳營DS.通信機房溫度 | 通信機房溫度警報 | OTHER | [5 empty] | 480 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1510 | 柳營～新高紅線(1510) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0875 |  |  | 1-36-11 |  |  | Locate Empty | A/N | 柳營新高紅線1510 CHANNEL CFA RY故障 |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1510_21CFA | 柳營新高紅線(1510)21RY通訊故障 | OTHER | [5 empty] | 481 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1510 | 柳營～新高紅線(1510) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0876 |  |  | 1-36-12 |  |  | Locate Empty | A/N | 柳營新高紅線1510 21SA TONE故障 |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1510_RYFA | 柳營新高紅線(1510)數位電驛故障 | OTHER | [5 empty] | 482 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1520 | 柳營～新高、榮特白線(1520) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0877 |  |  | 1-36-13 |  |  | Locate Empty | A/N | 柳營~新高、榮特白線1520 CHANNEL CFA RY故障 |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1520_21CFA | 柳營新高榮特白(1520)RY通訊故障 | OTHER | [5 empty] | 483 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1520 | 柳營～新高、榮特白線(1520) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0878 |  |  | 1-36-14 |  |  | Locate Empty | A/N | 柳營~新高、榮特白線1520 21SA TONE故障 |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1520_RYFA | 柳營新高榮特白(1520)數位RY故障 | OTHER | [5 empty] | 484 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1530 | 新營～柳營山線(1530) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0879 |  |  | 1-36-15 |  |  | Locate Empty | A/N | 新營柳營山線1530 CHANNEL 3RAOA RY故障 |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1530_87CFA | 新營柳營山線(1530)87RY通訊故障 | OTHER | [5 empty] | 485 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1530 | 新營～柳營山線(1530) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0880 |  |  | 1-37-00 |  |  | Locate Empty | A/N | 新營柳營山線1530 387LA TONE故障 |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1530_RYFA | 新營柳營山線(1530)數位電驛故障 | OTHER | [5 empty] | 486 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1540 | 新營～柳營海線(1540) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0881 |  |  | 1-37-01 |  |  | Locate Empty | A/N | 新營柳營海線1540 CHANNEL 4RAOA RY故障 |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1540_87CFA | 新營柳營海線(1540)87RY通訊故障 | OTHER | [5 empty] | 487 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1540 | 新營～柳營海線(1540) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0882 |  |  | 1-37-02 |  |  | Locate Empty | A/N | 新營柳營海線1540 487LA TONE故障 |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1540_RYFA | 新營柳營海線(1540)數位電驛故障 | OTHER | [5 empty] | 488 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1550 | 嘉民～柳營山線(1550) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0883 |  |  | 1-37-03 |  |  | Locate Empty | A/N | 嘉民柳營山線 1550 CHANNEL 5RAOA RY故障 |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1550_87CFA | 嘉民柳營山線(1550)87RY通訊故障 | OTHER | [5 empty] | 489 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1550 | 嘉民～柳營山線(1550) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0884 |  |  | 1-37-04 |  |  | Locate Empty | A/N | 嘉民柳營山線 1550 587LA RY故障 |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1550_RYFA | 嘉民柳營山線(1550)數位電驛故障 | OTHER | [5 empty] | 490 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1560 | 嘉民～柳營海線(1560) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0885 |  |  | 1-37-05 |  |  | Locate Empty | A/N | 嘉民柳營海線 (1560) CHANNEL 6RAOA RY故障 |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1560_87CFA | 嘉民柳營海線(1560)87RY通訊故障 | OTHER | [5 empty] | 491 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1560 | 嘉民～柳營海線(1560) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0886 |  |  | 1-37-06 |  |  | Locate Empty | A/N | 嘉民柳營海線 (1560) 687LA RY故障 |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1560_RYFA | 嘉民柳營海線(1560)數位電驛故障 | OTHER | [5 empty] | 492 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | StaDev | 所內設施 |  | AIRCON |  |  | Status | 冷氣跳脫 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0895 |  |  | 1-37-15 |  |  | 空調機 | A/M | 控制室空調機跳脫警報 |  |  | B3/D06_A1 | [8 empty] | 柳營DS.空調機故障 | 空調機故障或電源跳脫 | OTHER | [5 empty] | 493 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | NORMAL/FAULT | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ21 | 柳一線(VJ21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1024 |  |  | 2-30-00 |  |  | F1 | USE/LOCK | 柳一線 VJ21 79 RY 79S |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ21_79UL | 11KV柳一線(VJ21) 79RY U/L | FEEDER | [5 empty] | 494 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D06 | 柳營DS | 11 | 11kV | VJ21 | 柳一線(VJ21) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1025 |  |  | 2-30-01 |  |  | F1 | USE/LOCK | 柳一線 VJ21 51N TAP 51NS |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ21_LCO_TAP | 11KV柳一線(VJ21) LCO TAP | FEEDER | [5 empty] | 495 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D06 | 柳營DS | 11 | 11kV | VJ22 | 柳二線(VJ22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1026 |  |  | 2-30-02 |  |  | F2 | USE/LOCK | 柳二線 VJ22 79 RY 79S |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ22_79UL | 11KV柳二線(VJ22) 79RY U/L | FEEDER | [5 empty] | 496 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D06 | 柳營DS | 11 | 11kV | VJ22 | 柳二線(VJ22) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1027 |  |  | 2-30-03 |  |  | F2 | USE/LOCK | 柳二線 VJ22 51N TAP 51NS |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ22_LCO_TAP | 11KV柳二線(VJ22) LCO TAP | FEEDER | [5 empty] | 497 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D06 | 柳營DS | 11 | 11kV | VJ23 | 柳三線(VJ23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1028 |  |  | 2-30-04 |  |  | F3 | USE/LOCK | 柳三線 VJ23 79 RY 79S |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ23_79UL | 11KV柳三線(VJ23) 79RY U/L | FEEDER | [5 empty] | 498 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D06 | 柳營DS | 11 | 11kV | VJ23 | 柳三線(VJ23) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1029 |  |  | 2-30-05 |  |  | F3 | USE/LOCK | 柳三線 VJ23 TAP 51NS |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ23_LCO_TAP | 11KV柳三線(VJ23) LCO TAP | FEEDER | [5 empty] | 499 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D06 | 柳營DS | 11 | 11kV | VJ24 | 柳正線(VJ24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1030 |  |  | 2-30-06 |  |  | F4 | USE/LOCK | 柳正線 VJ24 79 RY 79S |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ24_79UL | 11KV柳正線(VJ24) 79RY U/L | FEEDER | [5 empty] | 500 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D06 | 柳營DS | 11 | 11kV | VJ24 | 柳正線(VJ24) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1031 |  |  | 2-30-07 |  |  | F4 | USE/LOCK | 柳正線 VJ24 51N TAP 51NS |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ24_LCO_TAP | 11KV柳正線(VJ24) LCO TAP | FEEDER | [5 empty] | 501 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D06 | 柳營DS | 11 | 11kV | VJ25 | 柳五線(VJ25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1032 |  |  | 2-30-08 |  |  | F5 | USE/LOCK | 柳五線 VJ25 79 RY 79S |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ25_79UL | 11KV柳五線(VJ25) 79RY U/L | FEEDER | [5 empty] | 502 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D06 | 柳營DS | 11 | 11kV | VJ25 | 柳五線(VJ25) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1033 |  |  | 2-30-09 |  |  | F5 | USE/LOCK | 柳五線 VJ25 51N TAP 51NS |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ25_LCO_TAP | 11KV柳五線(VJ25) LCO TAP | FEEDER | [5 empty] | 503 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D06 | 柳營DS | 22 | 22kV | VJ51 | 柳51線(VJ51) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1034 |  |  | 2-30-10 |  |  | F6 | USE/LOCK | 柳51線 VJ51 79 RY 79S |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ51_79UL | 23KV柳51線(VJ51) 79RY U/L | FEEDER | [5 empty] | 504 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D06 | 柳營DS | 22 | 22kV | VJ51 | 柳51線(VJ51) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1035 |  |  | 2-30-11 |  |  | F6 | USE/LOCK | 柳51線 VJ51 51N TAP 51NS |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ51_LCO_TAP | 23KV柳51線(VJ51) LCO TAP | FEEDER | [5 empty] | 505 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D06 | 柳營DS | 22 | 22kV | VJ52 | 柳52線(VJ52) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1036 |  |  | 2-30-12 |  |  | F7 | USE/LOCK | 柳52線 VJ52 79 RY 79S |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ52_79UL | 23KV柳52線(VJ52) 79RY U/L | FEEDER | [5 empty] | 506 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D06 | 柳營DS | 22 | 22kV | VJ52 | 柳52線(VJ52) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1037 |  |  | 2-30-13 |  |  | F7 | USE/LOCK | 柳52線 VJ52 51N TAP 51NS |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ52_LCO_TAP | 23KV柳52線(VJ52) LCO TAP | FEEDER | [5 empty] | 507 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D06 | 柳營DS | 22 | 22kV | VJ53 | 柳53線(VJ53) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1038 |  |  | 2-30-14 |  |  | F8 | USE/LOCK | 柳53線 VJ53 79 RY 79S |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ53_79UL | 23KV柳53線(VJ53) 79RY U/L | FEEDER | [5 empty] | 508 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D06 | 柳營DS | 22 | 22kV | VJ53 | 柳53線(VJ53) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1039 |  |  | 2-30-15 |  |  | F8 | USE/LOCK | 柳53線 VJ53 51N TAP 51NS |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ53_LCO_TAP | 23KV柳53線(VJ53) LCO TAP | FEEDER | [5 empty] | 509 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D06 | 柳營DS | 22 | 22kV | VJ54 | 柳54線(VJ54) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1040 |  |  | 2-31-00 |  |  | F9 | USE/LOCK | 柳54線 VJ54 79 RY 79S |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ54_79UL | 23KV柳54線(VJ54) 79RY U/L | FEEDER | [5 empty] | 510 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D06 | 柳營DS | 22 | 22kV | VJ54 | 柳54線(VJ54) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1041 |  |  | 2-31-01 |  |  | F9 | USE/LOCK | 柳54線 VJ54 51N TAP 51NS |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ54_LCO_TAP | 23KV柳54線(VJ54) LCO TAP | FEEDER | [5 empty] | 511 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D06 | 柳營DS | 22 | 22kV | VJ55 | 柳55線(VJ55) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1042 |  |  | 2-31-02 |  |  | F10 | USE/LOCK | 柳55線 VJ55 79 RY 79S |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ55_79UL | 23KV柳55線(VJ55) 79RY U/L | FEEDER | [5 empty] | 512 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D06 | 柳營DS | 22 | 22kV | VJ55 | 柳55線(VJ55) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1043 |  |  | 2-31-03 |  |  | F10 | USE/LOCK | 柳55線 VJ55 51N TAP 51NS |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ55_LCO_TAP | 23KV柳55線(VJ55) LCO TAP | FEEDER | [5 empty] | 513 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D06 | 柳營DS | 11 | 11kV | VJ31 | 十一線(VJ31) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1044 |  |  | 2-31-04 |  |  | F11 | USE/LOCK | 柳十一線 VJ31 79 RY 79S |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ31_79UL | 11KV柳31線(VJ31) 79RY U/L | FEEDER | [5 empty] | 514 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D06 | 柳營DS | 11 | 11kV | VJ31 | 十一線(VJ31) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1045 |  |  | 2-31-05 |  |  | F11 | USE/LOCK | 柳十一線 VJ31 51N TAP 51NS |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ31_LCO_TAP | 11KV柳31線(VJ31) LCO TAP | FEEDER | [5 empty] | 515 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D06 | 柳營DS | 11 | 11kV | VJ32 | 十二線(VJ32) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1046 |  |  | 2-31-06 |  |  | F12 | USE/LOCK | 柳十二線 VJ32 79 RY 79S |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ32_79UL | 11KV柳32線(VJ32) 79RY U/L | FEEDER | [5 empty] | 516 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D06 | 柳營DS | 11 | 11kV | VJ32 | 十二線(VJ32) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1047 |  |  | 2-31-07 |  |  | F12 | USE/LOCK | 柳十二線 VJ32 51N TAP 51NS |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ32_LCO_TAP | 11KV柳32線(VJ32) LCO TAP | FEEDER | [5 empty] | 517 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D06 | 柳營DS | 11 | 11kV | VJ33 | 十三線(VJ33) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1048 |  |  | 2-31-08 |  |  | F13 | USE/LOCK | 柳十三線 VJ33 79 RY 79S |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ33_79UL | 11KV柳33線(VJ33) 79RY U/L | FEEDER | [5 empty] | 518 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D06 | 柳營DS | 11 | 11kV | VJ33 | 十三線(VJ33) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1049 |  |  | 2-31-09 |  |  | F13 | USE/LOCK | 柳十三線 VJ33 51N TAP 51NS |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ33_LCO_TAP | 11KV柳33線(VJ33) LCO TAP | FEEDER | [5 empty] | 519 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D06 | 柳營DS | 11 | 11kV | VJ34 | 十四線(VJ34) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1050 |  |  | 2-31-10 |  |  | F14 | USE/LOCK | 柳十四線 VJ34 79 RY 79S |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ34_79UL | 11KV柳34線(VJ34) 79RY U/L | FEEDER | [5 empty] | 520 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D06 | 柳營DS | 11 | 11kV | VJ34 | 十四線(VJ34) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1051 |  |  | 2-31-11 |  |  | F14 | USE/LOCK | 柳十四線 VJ34 51N TAP 51NS |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ34_LCO_TAP | 11KV柳34線(VJ34) LCO TAP | FEEDER | [5 empty] | 521 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D06 | 柳營DS | 11 | 11kV | VJ35 | 十五線(VJ35) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1052 |  |  | 2-31-12 |  |  | F15 | USE/LOCK | 柳十五線 VJ35 79 RY 79S |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ35_79UL | 11KV柳35線(VJ35) 79RY U/L | FEEDER | [5 empty] | 522 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D06 | 柳營DS | 11 | 11kV | VJ35 | 十五線(VJ35) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1053 |  |  | 2-31-13 |  |  | F15 | USE/LOCK | 柳十五線 VJ35 51N TAP 51NS |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ35_LCO_TAP | 11KV柳35線(VJ35) LCO TAP | FEEDER | [5 empty] | 523 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D06 | 柳營DS | 22 | 22kV | VJ56 | 柳56線(VJ56) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1054 |  |  | 2-31-14 |  |  | F16 | USE/LOCK | 柳56線 VJ56 79 RY 79S |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ56_79UL | 23KV柳56線(VJ56) 79RY U/L | FEEDER | [5 empty] | 524 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D06 | 柳營DS | 22 | 22kV | VJ56 | 柳56線(VJ56) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1055 |  |  | 2-31-15 |  |  | F16 | USE/LOCK | 柳56線 VJ56 51N TAP 51NS |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ56_LCO_TAP | 23KV柳56線(VJ56) LCO TAP | FEEDER | [5 empty] | 525 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D06 | 柳營DS | 22 | 22kV | VJ57 | 柳57線(VJ57) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1056 |  |  | 2-32-00 |  |  | F17 | USE/LOCK | 柳57線 VJ57 79 RY 79S |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ57_79UL | 23KV柳57線(VJ57) 79RY U/L | FEEDER | [5 empty] | 526 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D06 | 柳營DS | 22 | 22kV | VJ57 | 柳57線(VJ57) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1057 |  |  | 2-32-01 |  |  | F17 | USE/LOCK | 柳57線 VJ57 51N TAP 51NS |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ57_LCO_TAP | 23KV柳57線(VJ57) LCO TAP | FEEDER | [5 empty] | 527 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D06 | 柳營DS | 22 | 22kV | VJ58 | 柳58線(VJ58) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1058 |  |  | 2-32-02 |  |  | F18 | USE/LOCK | 柳58線 VJ58 79 RY 79S |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ58_79UL | 23KV柳58線(VJ58) 79RY U/L | FEEDER | [5 empty] | 528 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D06 | 柳營DS | 22 | 22kV | VJ58 | 柳58線(VJ58) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1059 |  |  | 2-32-03 |  |  | F18 | USE/LOCK | 柳58線 VJ58 51N TAP 51NS |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ58_LCO_TAP | 23KV柳58線(VJ58) LCO TAP | FEEDER | [5 empty] | 529 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D06 | 柳營DS | 22 | 22kV | VJ59 | 柳59線(VJ59) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1060 |  |  | 2-32-04 |  |  | F19 | USE/LOCK | 柳59線 VJ59 79 RY 79S |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ59_79UL | 23KV柳59線(VJ59) 79RY U/L | FEEDER | [5 empty] | 530 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D06 | 柳營DS | 22 | 22kV | VJ59 | 柳59線(VJ59) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1061 |  |  | 2-32-05 |  |  | F19 | USE/LOCK | 柳59線 VJ59 51N TAP 51NS |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ59_LCO_TAP | 23KV柳59線(VJ59) LCO TAP | FEEDER | [5 empty] | 531 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D06 | 柳營DS | 22 | 22kV | VJ60 | 柳60線(VJ60) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1062 |  |  | 2-32-06 |  |  | F20 | USE/LOCK | 柳60線 VJ60 79 RY 79S |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ60_79UL | 23KV柳60線(VJ60) 79RY U/L | FEEDER | [5 empty] | 532 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D06 | 柳營DS | 22 | 22kV | VJ60 | 柳60線(VJ60) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1063 |  |  | 2-32-07 |  |  | F20 | USE/LOCK | 柳60線 VJ60 51N TAP 51NS |  |  | B2/D06_D1 | [8 empty] | 柳營DS.VJ60_LCO_TAP | 23KV柳60線(VJ60) LCO TAP | FEEDER | [5 empty] | 533 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D06 | 柳營DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1096 |  |  | 2-34-08 |  |  | 1950 | 96B1 | #1SHR 96B1 |  |  | B2/D06_A1 | [8 empty] | 柳營DS.161#1SHR_96B1 | 161KV #1SHR 96B1 RY | OTHER | [5 empty] | 534 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 96B2 |  | B3 | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1097 |  |  | 2-34-09 |  |  | 1950 | 96B2 | #1SHR 96B2 |  |  | B2/D06_A1 | [8 empty] | 柳營DS.161#1SHR_96B2 | 161KV #1SHR 96B2 RY | OTHER | [5 empty] | 535 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 96D |  | B3 | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1098 |  |  | 2-34-10 |  |  | 1950 | 96D | #1SHR 96D |  |  | B2/D06_A1 | [8 empty] | 柳營DS.161#1SHR_96D | 161KV #1SHR 96D RY | OTHER | [5 empty] | 536 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 96P |  | B3 | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1099 |  |  | 2-34-11 |  |  | 1950 | 96P | #1SHR 96P |  |  | B2/D06_A1 | [8 empty] | 柳營DS.161#1SHR_96P | 161KV #1SHR 96P RY | OTHER | [5 empty] | 537 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1950 | #1SHR(1950) |  | SHRF |  | B3 | Status | 電抗器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1100 |  |  | 2-34-12 |  |  | 1950 | SRF | #1SHR SRF |  |  | B2/D06_A1 | [8 empty] | 柳營DS.161#1SHR_SRF | 161KV #1SHR 輕故障 | OTHER | [5 empty] | 538 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1950 | #1SHR(1950) |  | SHRA |  | B3 | Status | 電抗器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1101 |  |  | 2-34-13 |  |  | 1950 | SRA | #1SHR SRA |  |  | B2/D06_A1 | [8 empty] | 柳營DS.161#1SHR_SRA | 161KV #1SHR 重故障 | OTHER | [5 empty] | 539 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1950 | #1SHR(1950) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1102 |  |  | 2-34-14 |  |  | 1950 | RYFA | #1SHR RYFA |  |  | B2/D06_A1 | [8 empty] | 柳營DS.161_1SHR_RYFA | 161KV 1SHR(1950)數位電驛故障 | OTHER | [5 empty] | 540 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | ComPoint |  |  | GRZ100 |  |  | Status | 電驛GRZ100閉鎖 | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1103 |  |  | 2-34-15 |  |  | BVS盤 | LOCK/USE | 本所各GRZ100 Ry U/L |  |  | B3/D06_A1 | [8 empty] | 柳營DS.BVS_RY | BVS GRZ100 RY U/L | OTHER | [5 empty] | 541 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | LOCK/USE | USE
D06 | 柳營DS | 161 | 161kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1105 |  |  | 2-35-01 |  |  | # 1BUS | USE/LOCE | #1 BUS╴87UL |  |  | B2/D06_A1 | [8 empty] | 柳營DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | [5 empty] | 542 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D06 | 柳營DS | 161 | 161kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1106 |  |  | 2-35-02 |  |  | # 2BUS | USE/LOCE | #2 BUS╴87UL |  |  | B2/D06_A1 | [8 empty] | 柳營DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | [5 empty] | 543 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D06 | 柳營DS | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 1107 |  |  | 2-35-03 |  |  | Locate Empty | 加壓/正常 | 161KV BUS TIE 1500 150SA |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | [5 empty] | 544 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Test | Test | 1 |  |  | TEST/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1108 |  |  | 2-35-04 |  |  | OSCF | A/N | 161KV示波器缺紙或故障警報OSCF |  |  | B3/D06_A1 | [8 empty] | 柳營DS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | [5 empty] | 545 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | StaDev | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1109 |  |  | 2-35-05 |  |  | Power Meter | A/N | Power Meter 故障警報 PMA |  |  | ELEM/D06_A1 | [8 empty] | 柳營DS.PMA | 電力量測表計故障 | OTHER | [5 empty] | 546 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 1_87UL1 |  | B3 | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1110 |  |  | 2-35-06 |  |  | 1950 | 87R1S | #1SHR 187 RY U/L |  |  | B2/D06_A1 | [8 empty] | 柳營DS.161#1SHR_187UL | 161KV #1SHR 187RY U/L | OTHER | [5 empty] | 547 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D06 | 柳營DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 1_87UL2 |  | B3 | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1111 |  |  | 2-35-07 |  |  | 1950 | 87R2S | #1SHR 287 RY U/L |  |  | B2/D06_A1 | [8 empty] | 柳營DS.161#1SHR_287UL | 161KV #1SHR 287RY U/L | OTHER | [5 empty] | 548 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D06 | 柳營DS | 0 |  | StaDev | 所內設施 |  | GEN | 緊急發電機運轉 | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1113 |  |  | 2-35-09 |  |  | Locate Empty | ON/OFF | 緊急發電機運轉 |  |  | B1/D06_A1 | [8 empty] | 柳營DS.GEN | 緊急發電機運轉 | OTHER | [5 empty] | 549 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ON/OFF | OFF
D06 | 柳營DS | 161 | 161kV | ComPoint |  |  | BUS_RYFA |  |  | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1114 |  |  | 2-35-10 |  |  | BUS | RYFA | BUS數位電驛故障 |  |  | B3/D06_A1 | [8 empty] | 柳營DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | [5 empty] | 550 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | ComPoint |  |  | 87CTFA |  | Element | Status | 87RY CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1115 |  |  | 2-35-11 |  |  | BUS | A/N | BUS 87RY CT 迴路故障 |  |  | B2/D06_A1 | [8 empty] | 柳營DS.161KV_BUS_CTFA | 161KV BUS CT回路故障 | OTHER | [5 empty] | 551 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | ComPoint |  |  | OLTC_A |  |  | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1116 |  |  | 2-35-12 |  |  | OLTC | OLTCA | OLTC 15分鐘內連動3次警報 |  |  | B3/D06_A1 | [8 empty] | 柳營DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | [5 empty] | 552 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1510 | 柳營～新高紅線(1510) |  | DS1 | 1511 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0896 | 641 |  | 1-38-00 | 1-38-01 |  | 1511 | ON | 柳營新高紅線(1511) DS-AS |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1511_DS | 1511(柳營新高紅線) DS | LINE161 | [5 empty] | 553 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1510 | 柳營～新高紅線(1510) |  | DS2 | 1512 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0898 | 643 |  | 1-38-02 | 1-38-03 |  | 1512 | ON | 柳營新高紅線 (1512) DS-AS |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1512_DS | 1512(柳營新高紅線) DS | LINE161 | [5 empty] | 554 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D06 | 柳營DS | 161 | 161kV | 1510 | 柳營～新高紅線(1510) |  | DS3 | 1513 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0900 | 645 |  | 1-38-04 | 1-38-05 |  | 1513 | ON | 柳營新高紅線 (1513) DS-AS |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1513_DS | 1513(柳營新高紅線) DS | LINE161 | [5 empty] | 555 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1510 | 柳營～新高紅線(1510) |  | ES3 | 1513E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0902 | 647 |  | 1-38-06 | 1-38-07 |  | 1513E | ON | 柳營新高紅線 (1513E) ES-AS |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1513E_ES | 1513E(柳營新高紅線) ES | LINE161 | [5 empty] | 556 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D06 | 柳營DS | 161 | 161kV | 1520 | 柳營～新高、榮特白線(1520) |  | DS1 | 1521 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0904 | 649 |  | 1-38-08 | 1-38-09 |  | 1521 | ON | 柳營~新高、榮特白線 (1521) DS-AS |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1521_DS | 1521(柳營新高榮特白) DS | LINE161 | [5 empty] | 557 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D06 | 柳營DS | 161 | 161kV | 1520 | 柳營～新高、榮特白線(1520) |  | DS2 | 1522 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0906 | 651 |  | 1-38-10 | 1-38-11 |  | 1522 | ON | 柳營~新高、榮特白線 (1522) DS-AS |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1522_DS | 1522(柳營新高榮特白) DS | LINE161 | [5 empty] | 558 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1520 | 柳營～新高、榮特白線(1520) |  | DS3 | 1523 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0908 | 653 |  | 1-38-12 | 1-38-13 |  | 1523 | ON | 柳營~新高、榮特白線 (1523) DS-AS |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1523_DS | 1523(柳營新高榮特白) DS | LINE161 | [5 empty] | 559 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1520 | 柳營～新高、榮特白線(1520) |  | ES3 | 1523E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0910 | 655 |  | 1-38-14 | 1-38-15 |  | 1523E | ON | 柳營~新高、榮特白線 (1523E) ES-AS |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1523E_ES | 1523E(柳營新高榮特白) ES | LINE161 | [5 empty] | 560 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D06 | 柳營DS | 161 | 161kV | 1530 | 新營～柳營山線(1530) |  | DS1 | 1531 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0912 | 657 |  | 1-39-00 | 1-39-01 |  | 1531 | ON | 新營柳營山線 (1531) DS-AS |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1531_DS | 1531(新營柳營山線) DS | LINE161 | [5 empty] | 561 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1530 | 新營～柳營山線(1530) |  | DS2 | 1532 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0914 | 659 |  | 1-39-02 | 1-39-03 |  | 1532 | ON | 新營柳營山線 (1532) DS-AS |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1532_DS | 1532(新營柳營山線) DS | LINE161 | [5 empty] | 562 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D06 | 柳營DS | 161 | 161kV | 1530 | 新營～柳營山線(1530) |  | DS3 | 1533 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0916 | 661 |  | 1-39-04 | 1-39-05 |  | 1533 | ON | 新營柳營山線 (1533) DS-AS |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1533_DS | 1533(新營柳營山線) DS | LINE161 | [5 empty] | 563 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1530 | 新營～柳營山線(1530) |  | ES3 | 1533E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0918 | 663 |  | 1-39-06 | 1-39-07 |  | 1533E | ON | 新營柳營山線 (1533E) ES-AS |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1533E_ES | 1533E(新營柳營山線) ES | LINE161 | [5 empty] | 564 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D06 | 柳營DS | 161 | 161kV | 1540 | 新營～柳營海線(1540) |  | DS1 | 1541 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0920 | 665 |  | 1-39-08 | 1-39-09 |  | 1541 | ON | 新營柳營海線 (1541) DS-AS |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1541_DS | 1541(新營柳營海線) DS | LINE161 | [5 empty] | 565 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D06 | 柳營DS | 161 | 161kV | 1540 | 新營～柳營海線(1540) |  | DS2 | 1542 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0922 | 667 |  | 1-39-10 | 1-39-11 |  | 1542 | ON | 新營柳營海線 (1542) DS-AS |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1542_DS | 1542(新營柳營海線) DS | LINE161 | [5 empty] | 566 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1540 | 新營～柳營海線(1540) |  | DS3 | 1543 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0924 | 669 |  | 1-39-12 | 1-39-13 |  | 1543 | ON | 新營柳營海線 (1543) DS-AS |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1543_DS | 1543(新營柳營海線) DS | LINE161 | [5 empty] | 567 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1540 | 新營～柳營海線(1540) |  | ES3 | 1543E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0926 | 671 |  | 1-39-14 | 1-39-15 |  | 1543E | ON | 新營柳營海線 (1543E) ES-AS |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1543E_ES | 1543E(新營柳營海線) ES | LINE161 | [5 empty] | 568 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D06 | 柳營DS | 161 | 161kV | 1550 | 嘉民～柳營山線(1550) |  | DS1 | 1551 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0928 | 673 |  | 1-3A-00 | 1-3A-01 |  | 1551 | ON | 嘉民柳營山線 (1551) DS-AS |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1551_DS | 1551(嘉民柳營山線) DS | LINE161 | [5 empty] | 569 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1550 | 嘉民～柳營山線(1550) |  | DS2 | 1552 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0930 | 675 |  | 1-3A-02 | 1-3A-03 |  | 1552 | ON | 嘉民柳營山線 (1552) DS-AS |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1552_DS | 1552(嘉民柳營山線) DS | LINE161 | [5 empty] | 570 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D06 | 柳營DS | 161 | 161kV | 1550 | 嘉民～柳營山線(1550) |  | DS3 | 1553 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0932 | 677 |  | 1-3A-04 | 1-3A-05 |  | 1553 | ON | 嘉民柳營山線 (1553) DS-AS |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1553_DS | 1553(嘉民柳營山線) DS | LINE161 | [5 empty] | 571 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1550 | 嘉民～柳營山線(1550) |  | ES3 | 1553E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0934 | 679 |  | 1-3A-06 | 1-3A-07 |  | 1553E | ON | 嘉民柳營山線 (1553E) ES-AS |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1553E_ES | 1553E(嘉民柳營山線) ES | LINE161 | [5 empty] | 572 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D06 | 柳營DS | 161 | 161kV | 1560 | 嘉民～柳營海線(1560) |  | DS1 | 1561 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0936 | 681 |  | 1-3A-08 | 1-3A-09 |  | 1561 | ON | 嘉民柳營海線 (1561) DS-AS |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1561_DS | 1561(嘉民柳營海線) DS | LINE161 | [5 empty] | 573 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D06 | 柳營DS | 161 | 161kV | 1560 | 嘉民～柳營海線(1560) |  | DS2 | 1562 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0938 | 683 |  | 1-3A-10 | 1-3A-11 |  | 1562 | ON | 嘉民柳營海線 (1562) DS-AS |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1562_DS | 1562(嘉民柳營海線) DS | LINE161 | [5 empty] | 574 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1560 | 嘉民～柳營海線(1560) |  | DS3 | 1563 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0940 | 685 |  | 1-3A-12 | 1-3A-13 |  | 1563 | ON | 嘉民柳營海線 (1563) DS-AS |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1563_DS | 1563(嘉民柳營海線) DS | LINE161 | [5 empty] | 575 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1560 | 嘉民～柳營海線(1560) |  | ES3 | 1563E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0942 | 687 |  | 1-3A-14 | 1-3A-15 |  | 1563E | ON | 嘉民柳營海線 (1563E) ES-AS |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1563E_ES | 1563E(嘉民柳營海線) ES | LINE161 | [5 empty] | 576 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D06 | 柳營DS | 161 | 161kV | 1950 | #1SHR(1950) |  | DS1 | 1951 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0960 | 705 |  | 1-3C-00 | 1-3C-01 |  | 1951 | ON | #1SHR(1951) DS-AS |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1951_DS | 1951(161KV #1SHR) DS | OTHER | [5 empty] | 577 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1950 | #1SHR(1950) |  | DS2 | 1952 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0962 | 707 |  | 1-3C-02 | 1-3C-03 |  | 1952 | ON | #1SHR(1952) DS-AS |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1952_DS | 1952(161KV #1SHR) DS | OTHER | [5 empty] | 578 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0976 | 721 |  | 1-3D-00 | 1-3D-01 |  | 1501 | ON | 161 TIE (1501) DS-AS |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1501_DS | 1501(TIE) DS | TIE | [5 empty] | 579 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0978 | 723 |  | 1-3D-02 | 1-3D-03 |  | 1502 | ON | 161 TIE (1502) DS-AS |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1502_DS | 1502(TIE) DS | TIE | [5 empty] | 580 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0980 | 725 |  | 1-3D-04 | 1-3D-05 |  | 1751 | ON | NO.1 DTR(1751) DS-AS |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1751_DS | 1751(#1DTR) DS | MTR | [5 empty] | 581 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0982 | 727 |  | 1-3D-06 | 1-3D-07 |  | 1752 | ON | NO.1 DTR(1752) DS-AS |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1752_DS | 1752(#1DTR) DS | MTR | [5 empty] | 582 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D06 | 柳營DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0984 | 729 |  | 1-3D-08 | 1-3D-09 |  | 1761 | ON | NO.2 DTR(1761) DS-AS |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1761_DS | 1761(#2DTR) DS | MTR | [5 empty] | 583 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D06 | 柳營DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0986 | 731 |  | 1-3D-10 | 1-3D-11 |  | 1762 | ON | NO.2 DTR(1762) DS-AS |  |  | B2/D06_A1 | [8 empty] | 柳營DS.1762_DS | 1762(#2DTR) DS | MTR | [5 empty] | 584 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 11 | 11kV | LBS210 | #1SC(210) |  | LBS |  |  | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/210 | C/1SC(B) |  |  | 0996 | 741 |  | 1-3E-04 | 1-3E-05 |  | SC1A | ON | #1SC 210 LBS LBS-AS |  |  | B3/D06_A1 | [8 empty] | 柳營DS.210_LBS | 210(11KV #1SC) LBS | SC | [5 empty] | 585 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 11 | 11kV | LBS230 | #3SC(230) |  | LBS |  |  | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/230 | C/3SC(B) |  |  | 1000 | 745 |  | 1-3E-08 | 1-3E-09 |  | SC2A | ON | #3SC 230 LBS LBS-AS |  |  | B3/D06_A1 | [8 empty] | 柳營DS.230_LBS | 230(11KV #3SC) LBS | SC | [5 empty] | 586 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1530 | 新營～柳營山線(1530) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 | [10 empty] | B2/D06_A1 | [8 empty] | 柳營DS.1530_GDA | 新營柳營山線(1530) 接地RY | LINE161 | [5 empty] | 587 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D06 | 柳營DS |  |  | 1DTR | #1DTR |  | 87UL2 |  |  | Status | 第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1117 | [10 empty] | B1/D06_A1 | [16 empty] | 588 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D06 | 柳營DS |  |  | 2DTR | #2DTR |  | 87UL2 |  |  | Status | 第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1120 | [10 empty] | B1/D06_A1 | [16 empty] | 589 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D06 | 柳營DS |  |  | 1DTR | #1DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0112 | [10 empty] | B1/D06_A1 | [16 empty] | 590 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D06 | 柳營DS |  |  | 2DTR | #2DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0113 | [10 empty] | B1/D06_A1 | [16 empty] | 591 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D06 | 柳營DS |  |  | 1DTR | #1DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1119 | [10 empty] | B1/D06_A1 | [16 empty] | 592 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D06 | 柳營DS |  |  | 2DTR | #2DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1122 | [10 empty] | B1/D06_A1 | [16 empty] | 593 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D06 | 柳營DS |  |  | 1DTR | #1DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1118 | [10 empty] | B1/D06_A1 | [16 empty] | 594 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D06 | 柳營DS |  |  | 2DTR | #2DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1121 | [10 empty] | B1/D06_A1 | [16 empty] | 595 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
D06 | 柳營DS | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/D06_A1 | [12 empty] | 柳營DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: D06/161/1BUS/V; OPRD2: D06/161/2BUS/V
D06 | 柳營DS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/D06_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: D06/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
D06 | 柳營DS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/D06_A1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_6 | OPRD1: D06/161/1510/MW; OPRD2: D06/161/1520/MW; OPRD3: D06/161/1530/MW; OPRD4: D06/161/1540/MW; OPRD5: D06/161/1550/MW; OPRD6: D06/161/1560/MW
D06 | 柳營DS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/D06_A1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: D06/0/CalcPoint/OPRN2_MW
D06 | 柳營DS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/D06_A1 | [17 empty] | none
D06 | 柳營DS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/D06_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: D06/0/CalcPoint/OPRN1; OPRD2: D06/0/CalcPoint/OPRN2; OPRD3: D06/0/CalcPoint/PRFL_UL
D06 | 柳營DS |  |  | 1DTR | 1DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D06_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D06/11/310/I_R; OPRD2: D06/22/320/I_R
D06 | 柳營DS |  |  | 1DTR | 1DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D06_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D06/11/310/I_S; OPRD2: D06/22/320/I_S
D06 | 柳營DS |  |  | 1DTR | 1DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D06_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D06/11/310/I_T; OPRD2: D06/22/320/I_T
D06 | 柳營DS |  |  | 2DTR | 2DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D06_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D06/11/330/I_R; OPRD2: D06/22/340/I_R
D06 | 柳營DS |  |  | 2DTR | 2DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D06_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D06/11/330/I_S; OPRD2: D06/22/340/I_S
D06 | 柳營DS |  |  | 2DTR | 2DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D06_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D06/11/330/I_T; OPRD2: D06/22/340/I_T
D06 | 柳營DS | 161 | 161kV | 1510 | 柳營～新高紅線(1510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D06_A1 | [12 empty] | 柳營DS.1510_AMP | 柳營新高紅線 AMP | LINE161 | AMP_CAL | C20R0964 | amp_cal | OPRD1: D06/161/1510/MW; OPRD2: D06/161/1510/MVAR; OPRD3: D06/0/CalcPoint/Vbs4
D06 | 柳營DS | 161 | 161kV | 1520 | 柳營～新高、榮特白線(1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D06_A1 | [12 empty] | 柳營DS.1520_AMP | 柳營新高榮特白 AMP | LINE161 | AMP_CAL | C20R0964 | amp_cal | OPRD1: D06/161/1520/MW; OPRD2: D06/161/1520/MVAR; OPRD3: D06/0/CalcPoint/Vbs4
D06 | 柳營DS | 161 | 161kV | 1530 | 新營～柳營山線(1530) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D06_A1 | [12 empty] | 柳營DS.1530_AMP | 新營柳營山線 AMP | LINE161 | AMP_CAL | C20R1328 | amp_cal | OPRD1: D06/161/1530/MW; OPRD2: D06/161/1530/MVAR; OPRD3: D06/0/CalcPoint/Vbs4
D06 | 柳營DS | 161 | 161kV | 1540 | 新營～柳營海線(1540) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D06_A1 | [12 empty] | 柳營DS.1540_AMP | 新營柳營海線 AMP | LINE161 | AMP_CAL | C20R1328 | amp_cal | OPRD1: D06/161/1540/MW; OPRD2: D06/161/1540/MVAR; OPRD3: D06/0/CalcPoint/Vbs4
D06 | 柳營DS | 161 | 161kV | 1550 | 嘉民～柳營山線(1550) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D06_A1 | [12 empty] | 柳營DS.1550_AMP | 嘉民柳營山線 AMP | LINE161 | AMP_CAL | C20R1328 | amp_cal | OPRD1: D06/161/1550/MW; OPRD2: D06/161/1550/MVAR; OPRD3: D06/0/CalcPoint/Vbs4
D06 | 柳營DS | 161 | 161kV | 1560 | 嘉民～柳營海線(1560) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D06_A1 | [12 empty] | 柳營DS.1560_AMP | 嘉民柳營海線 AMP | LINE161 | AMP_CAL | C20R1328 | amp_cal | OPRD1: D06/161/1560/MW; OPRD2: D06/161/1560/MVAR; OPRD3: D06/0/CalcPoint/Vbs4
D06 | 柳營DS | 11 | 11kV | 1ABUS | #1ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D06_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D06/11/1ABUS/V
D06 | 柳營DS | 11 | 11kV | 2ABUS | #2ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D06_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D06/11/2ABUS/V
D06 | 柳營DS | 22 | 22kV | 1BBUS | #1BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D06_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D06/22/1BBUS/V
D06 | 柳營DS | 22 | 22kV | 2BBUS | #2BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D06_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D06/22/2BBUS/V
D06 | 柳營DS |  |  | 1DTR(A) | #1DTR(A) |  | TR_PERM | [9 empty] | B1/D06_A1 | [12 empty] | 柳營DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D06//1DTR(A)/SupLocal; OPRD2: D06//1DTR(A)/Tap Chan
D06 | 柳營DS |  |  | 1DTR(B) | #1DTR(B) |  | TR_PERM | [9 empty] | B1/D06_A1 | [12 empty] | 柳營DS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D06//1DTR(B)/SupLocal; OPRD2: D06//1DTR(B)/Tap Chan
D06 | 柳營DS |  |  | 2DTR(A) | #2DTR(A) |  | TR_PERM | [9 empty] | B1/D06_A1 | [12 empty] | 柳營DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D06//2DTR(A)/SupLocal; OPRD2: D06//2DTR(A)/Tap Chan
D06 | 柳營DS |  |  | 2DTR(B) | #2DTR(B) |  | TR_PERM | [9 empty] | B1/D06_A1 | [12 empty] | 柳營DS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D06//2DTR(B)/SupLocal; OPRD2: D06//2DTR(B)/Tap Chan
D06 | 柳營DS | 11 | 11kV | VJ21 | 柳一線(VJ21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D06/11/1ABUS/V; OPRD2: D06/11/VJ21/I_R; OPRD3: D06/11/VJ21/I_S; OPRD4: D06/11/VJ21/I_T
D06 | 柳營DS | 11 | 11kV | VJ22 | 柳二線(VJ22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D06/11/1ABUS/V; OPRD2: D06/11/VJ22/I_R; OPRD3: D06/11/VJ22/I_S; OPRD4: D06/11/VJ22/I_T
D06 | 柳營DS | 11 | 11kV | VJ23 | 柳三線(VJ23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D06/11/1ABUS/V; OPRD2: D06/11/VJ23/I_R; OPRD3: D06/11/VJ23/I_S; OPRD4: D06/11/VJ23/I_T
D06 | 柳營DS | 11 | 11kV | VJ24 | 柳正線(VJ24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D06/11/1ABUS/V; OPRD2: D06/11/VJ24/I_R; OPRD3: D06/11/VJ24/I_S; OPRD4: D06/11/VJ24/I_T
D06 | 柳營DS | 11 | 11kV | VJ25 | 柳五線(VJ25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D06/11/1ABUS/V; OPRD2: D06/11/VJ25/I_R; OPRD3: D06/11/VJ25/I_S; OPRD4: D06/11/VJ25/I_T
D06 | 柳營DS | 11 | 11kV | VJ31 | 十一線(VJ31) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D06/11/2ABUS/V; OPRD2: D06/11/VJ31/I_R; OPRD3: D06/11/VJ31/I_S; OPRD4: D06/11/VJ31/I_T
D06 | 柳營DS | 11 | 11kV | VJ32 | 十二線(VJ32) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D06/11/2ABUS/V; OPRD2: D06/11/VJ32/I_R; OPRD3: D06/11/VJ32/I_S; OPRD4: D06/11/VJ32/I_T
D06 | 柳營DS | 11 | 11kV | VJ33 | 十三線(VJ33) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D06/11/2ABUS/V; OPRD2: D06/11/VJ33/I_R; OPRD3: D06/11/VJ33/I_S; OPRD4: D06/11/VJ33/I_T
D06 | 柳營DS | 11 | 11kV | VJ34 | 十四線(VJ34) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D06/11/2ABUS/V; OPRD2: D06/11/VJ34/I_R; OPRD3: D06/11/VJ34/I_S; OPRD4: D06/11/VJ34/I_T
D06 | 柳營DS | 11 | 11kV | VJ35 | 十五線(VJ35) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D06/11/2ABUS/V; OPRD2: D06/11/VJ35/I_R; OPRD3: D06/11/VJ35/I_S; OPRD4: D06/11/VJ35/I_T
D06 | 柳營DS | 22 | 22kV | VJ51 | 柳51線(VJ51) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D06/22/1BBUS/V; OPRD2: D06/22/VJ51/I_R; OPRD3: D06/22/VJ51/I_S; OPRD4: D06/22/VJ51/I_T
D06 | 柳營DS | 22 | 22kV | VJ52 | 柳52線(VJ52) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D06/22/1BBUS/V; OPRD2: D06/22/VJ52/I_R; OPRD3: D06/22/VJ52/I_S; OPRD4: D06/22/VJ52/I_T
D06 | 柳營DS | 22 | 22kV | VJ53 | 柳53線(VJ53) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D06/22/1BBUS/V; OPRD2: D06/22/VJ53/I_R; OPRD3: D06/22/VJ53/I_S; OPRD4: D06/22/VJ53/I_T
D06 | 柳營DS | 22 | 22kV | VJ54 | 柳54線(VJ54) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D06/22/1BBUS/V; OPRD2: D06/22/VJ54/I_R; OPRD3: D06/22/VJ54/I_S; OPRD4: D06/22/VJ54/I_T
D06 | 柳營DS | 22 | 22kV | VJ55 | 柳55線(VJ55) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D06/22/1BBUS/V; OPRD2: D06/22/VJ55/I_R; OPRD3: D06/22/VJ55/I_S; OPRD4: D06/22/VJ55/I_T
D06 | 柳營DS | 22 | 22kV | VJ56 | 柳56線(VJ56) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D06/22/2BBUS/V; OPRD2: D06/22/VJ56/I_R; OPRD3: D06/22/VJ56/I_S; OPRD4: D06/22/VJ56/I_T
D06 | 柳營DS | 22 | 22kV | VJ57 | 柳57線(VJ57) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D06/22/2BBUS/V; OPRD2: D06/22/VJ57/I_R; OPRD3: D06/22/VJ57/I_S; OPRD4: D06/22/VJ57/I_T
D06 | 柳營DS | 22 | 22kV | VJ58 | 柳58線(VJ58) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D06/22/2BBUS/V; OPRD2: D06/22/VJ58/I_R; OPRD3: D06/22/VJ58/I_S; OPRD4: D06/22/VJ58/I_T
D06 | 柳營DS | 22 | 22kV | VJ59 | 柳59線(VJ59) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D06/22/2BBUS/V; OPRD2: D06/22/VJ59/I_R; OPRD3: D06/22/VJ59/I_S; OPRD4: D06/22/VJ59/I_T
D06 | 柳營DS | 22 | 22kV | VJ60 | 柳60線(VJ60) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D06/22/2BBUS/V; OPRD2: D06/22/VJ60/I_R; OPRD3: D06/22/VJ60/I_S; OPRD4: D06/22/VJ60/I_T
D06 | 柳營DS | 11 | 11kV | VJ21 | 柳一線(VJ21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D06/11/VJ21/kVA; OPRD2: D06/11/VJ21/KVAR
D06 | 柳營DS | 11 | 11kV | VJ22 | 柳二線(VJ22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D06/11/VJ22/kVA; OPRD2: D06/11/VJ22/KVAR
D06 | 柳營DS | 11 | 11kV | VJ23 | 柳三線(VJ23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D06/11/VJ23/kVA; OPRD2: D06/11/VJ23/KVAR
D06 | 柳營DS | 11 | 11kV | VJ24 | 柳正線(VJ24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D06/11/VJ24/kVA; OPRD2: D06/11/VJ24/KVAR
D06 | 柳營DS | 11 | 11kV | VJ25 | 柳五線(VJ25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D06/11/VJ25/kVA; OPRD2: D06/11/VJ25/KVAR
D06 | 柳營DS | 11 | 11kV | VJ31 | 十一線(VJ31) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D06/11/VJ31/kVA; OPRD2: D06/11/VJ31/KVAR
D06 | 柳營DS | 11 | 11kV | VJ32 | 十二線(VJ32) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D06/11/VJ32/kVA; OPRD2: D06/11/VJ32/KVAR
D06 | 柳營DS | 11 | 11kV | VJ33 | 十三線(VJ33) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D06/11/VJ33/kVA; OPRD2: D06/11/VJ33/KVAR
D06 | 柳營DS | 11 | 11kV | VJ34 | 十四線(VJ34) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D06/11/VJ34/kVA; OPRD2: D06/11/VJ34/KVAR
D06 | 柳營DS | 11 | 11kV | VJ35 | 十五線(VJ35) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D06/11/VJ35/kVA; OPRD2: D06/11/VJ35/KVAR
D06 | 柳營DS | 22 | 22kV | VJ51 | 柳51線(VJ51) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D06/22/VJ51/kVA; OPRD2: D06/22/VJ51/KVAR
D06 | 柳營DS | 22 | 22kV | VJ52 | 柳52線(VJ52) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D06/22/VJ52/kVA; OPRD2: D06/22/VJ52/KVAR
D06 | 柳營DS | 22 | 22kV | VJ53 | 柳53線(VJ53) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D06/22/VJ53/kVA; OPRD2: D06/22/VJ53/KVAR
D06 | 柳營DS | 22 | 22kV | VJ54 | 柳54線(VJ54) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D06/22/VJ54/kVA; OPRD2: D06/22/VJ54/KVAR
D06 | 柳營DS | 22 | 22kV | VJ55 | 柳55線(VJ55) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D06/22/VJ55/kVA; OPRD2: D06/22/VJ55/KVAR
D06 | 柳營DS | 22 | 22kV | VJ56 | 柳56線(VJ56) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D06/22/VJ56/kVA; OPRD2: D06/22/VJ56/KVAR
D06 | 柳營DS | 22 | 22kV | VJ57 | 柳57線(VJ57) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D06/22/VJ57/kVA; OPRD2: D06/22/VJ57/KVAR
D06 | 柳營DS | 22 | 22kV | VJ58 | 柳58線(VJ58) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D06/22/VJ58/kVA; OPRD2: D06/22/VJ58/KVAR
D06 | 柳營DS | 22 | 22kV | VJ59 | 柳59線(VJ59) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D06/22/VJ59/kVA; OPRD2: D06/22/VJ59/KVAR
D06 | 柳營DS | 22 | 22kV | VJ60 | 柳60線(VJ60) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D06_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D06/22/VJ60/kVA; OPRD2: D06/22/VJ60/KVAR
D06 | 柳營DS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D06_A1 | [12 empty] | 柳營DS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D06/11/210/CB; OPRD2: 6.9; OPRD3: 0
D06 | 柳營DS | 11 | 11kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D06_A1 | [12 empty] | 柳營DS.230_SC_MVAR | 11KV#3SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D06/11/230/CB; OPRD2: 6.9; OPRD3: 0
D06 | 柳營DS | 22 | 22kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D06_A1 | [12 empty] | 柳營DS.220_SC_MVAR | 23KV#2SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D06/22/220/CB; OPRD2: 13.8; OPRD3: 0
D06 | 柳營DS | 22 | 22kV | 240 | #4SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D06_A1 | [12 empty] | 柳營DS.240_SC_MVAR | 23KV#4SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D06/22/240/CB; OPRD2: 13.8; OPRD3: 0
D06 | 柳營DS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/D06_A1 | [12 empty] | 柳營DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_10 |  | com_alarm_30 | D06//1DTR/GDA | D06//1DTR/PHA | D06//1DTR/96D | D06//1DTR/TRA | D06//1DTR/63Q | D06//1DTR/96B2 | D06//1DTR/96B1 | D06//1DTR/87A | D06//1DTR/51ZA | D06//1DTR/96PA | D06//2DTR/63Q | D06//2DTR/TRA | D06//2DTR/96D | D06//2DTR/96B1 | D06//2DTR/96B2 | D06//2DTR/GDA | D06//2DTR/51ZA | D06//2DTR/PHA | D06//2DTR/87A | D06//2DTR/96PA | D06/11/310/PHA | D06/11/310/GDA | D06/11/330/PHA | D06/11/330/GDA | D06/161/1BUS/87A | D06/161/2BUS/87A | D06/22/320/GDA | D06/22/320/PHA | D06/22/340/GDA | D06/22/340/PHA
D06 | 柳營DS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/D06_A1 | [12 empty] | 柳營DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | STATION_FAULT_2 |  | com_alarm_2 | OPRD1: D06//1DTR/TRF; OPRD2: D06//2DTR/TRF
D06 | 柳營DS | 161 | 161kV | 1750_D1 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D06_D1 | [17 empty] | lamp2CC | OPRD1: D06/161/1750/CB
D06 | 柳營DS | 11 | 11kV | 310_D1 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D06_D1 | [17 empty] | lamp2CC | OPRD1: D06/11/310/CB
D06 | 柳營DS | 22 | 22kV | 320_D1 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D06_D1 | [17 empty] | lamp2CC | OPRD1: D06/22/320/CB
D06 | 柳營DS | 161 | 161kV | 1760_D1 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D06_D1 | [17 empty] | lamp2CC | OPRD1: D06/161/1760/CB
D06 | 柳營DS | 11 | 11kV | 330_D1 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D06_D1 | [17 empty] | lamp2CC | OPRD1: D06/11/330/CB
D06 | 柳營DS | 22 | 22kV | 340_D1 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D06_D1 | [17 empty] | lamp2CC | OPRD1: D06/22/340/CB
D06 | 柳營DS | 0 |  | RTU_D1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/D06_D1 | [17 empty] | lamp2CC | OPRD1: D06/0/RTU/RTU_R_L
D06 | 柳營DS | 0 |  | StaDev_D1 | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/D06_D1 | [17 empty] | lamp2CC | OPRD1: D06/0/StaDev/STUV
D06 | 柳營DS | 0 |  | StaDev_D1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D06_D1 | [17 empty] | lamp2CC | OPRD1: D06/0/StaDev/DCA
D06 | 柳營DS | 0 |  | StaDev_D1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D06_D1 | [17 empty] | lamp2CC | OPRD1: D06/0/StaDev/DCE
D06 | 柳營DS | 22 | 22kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D06_D1 | [17 empty] | lamp2CC | OPRD1: D06/22/ComPoint/CBA
D06 | 柳營DS | 22 | 22kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | ELEM/D06_D1 | [17 empty] | lamp2CC | OPRD1: D06/22/ComPoint/CBF
D06 | 柳營DS | 0 |  | StaDev_D1 | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D06_D1 | [17 empty] | lamp2CC | OPRD1: D06/0/StaDev/PMA

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D06 | 柳營DS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 柳營DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | D06/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
D06 | 柳營DS | 161 | 161kV | 1510 | 柳營新高紅線(1510) |  | I | [25 empty] | ADCS_N | [8 empty] | 柳營DS.1510_AMP | 柳營新高紅線 AMP | LINE161 | D06/161/1510/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C20R0964 | 867.599976 | 867.599976 | 964.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D06 | 柳營DS | 161 | 161kV | 1520 | 柳營新高榮特白(1520) |  | I | [25 empty] | ADCS_N | [8 empty] | 柳營DS.1520_AMP | 柳營新高榮特白 AMP | LINE161 | D06/161/1520/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C20R0964 | 867.599976 | 867.599976 | 964.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D06 | 柳營DS | 161 | 161kV | 1530 | 新營柳營山線(1530) |  | I | [25 empty] | ADCS_N | [8 empty] | 柳營DS.1530_AMP | 新營柳營山線 AMP | LINE161 | D06/161/1530/I |  | AMP_CAL |  |  | 5 | CalcAIPoint | [21 empty] | C20R1328 | 1195.199951 | 1195.199951 | 1328.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D06 | 柳營DS | 161 | 161kV | 1540 | 新營柳營海線(1540) |  | I | [25 empty] | ADCS_N | [8 empty] | 柳營DS.1540_AMP | 新營柳營海線 AMP | LINE161 | D06/161/1540/I |  | AMP_CAL |  |  | 6 | CalcAIPoint | [21 empty] | C20R1328 | 1195.199951 | 1195.199951 | 1328.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D06 | 柳營DS | 161 | 161kV | 1550 | 嘉民柳營山線(1550) |  | I | [25 empty] | ADCS_N | [8 empty] | 柳營DS.1550_AMP | 嘉民柳營山線 AMP | LINE161 | D06/161/1550/I |  | AMP_CAL |  |  | 7 | CalcAIPoint | [21 empty] | C20R1328 | 1195.199951 | 1195.199951 | 1328.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D06 | 柳營DS | 161 | 161kV | 1560 | 嘉民柳營海線(1560) |  | I | [25 empty] | ADCS_N | [8 empty] | 柳營DS.1560_AMP | 嘉民柳營海線 AMP | LINE161 | D06/161/1560/I |  | AMP_CAL |  |  | 8 | CalcAIPoint | [21 empty] | C20R1328 | 1195.199951 | 1195.199951 | 1328.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳二線KVA | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳二線KVA | 11KV柳二線KVA | FEEDER |  |  | KVA_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳二線KW | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳二線KW | 11KV柳二線KW | FEEDER |  |  | KW_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳三線KVA | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳三線KVA | 11KV柳三線KVA | FEEDER |  |  | KVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳三線KW | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳三線KW | 11KV柳三線KW | FEEDER |  |  | KW_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳五線KVA | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳五線KVA | 11KV柳五線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳五線KW | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳五線KW | 11KV柳五線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳正線KVA | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳正線KVA | 11KV柳正線KVA | FEEDER |  |  | KVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳正線KW | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳正線KW | 11KV柳正線KW | FEEDER |  |  | KW_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 柳營DS.#1DTR(A)_MVA | #1DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D06 | 柳營DS | 0 |  | 1DTR(A) | #1DTR(A) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 柳營DS.#1DTR(A)_LOAD | #1DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 18 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D06 | 柳營DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PF | [25 empty] | ADCS_N | [8 empty] | 柳營DS.#1DTR(A)_PF | #1DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D06 | 柳營DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 柳營DS.#1DTR(B)_MVA | #1DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D06 | 柳營DS | 0 |  | 1DTR(B) | #1DTR(B) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 柳營DS.#1DTR(B)_LOAD | #1DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 21 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D06 | 柳營DS | 0 |  | 1DTR(B) | #1DTR(B) |  | PF | [25 empty] | ADCS_N | [8 empty] | 柳營DS.#1DTR(B)_PF | #1DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D06 | 柳營DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 柳營DS.#2DTR(A)_MVA | #2DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D06 | 柳營DS | 0 |  | 2DTR(A) | #2DTR(A) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 柳營DS.#2DTR(A)_LOAD | #2DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 24 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D06 | 柳營DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PF | [25 empty] | ADCS_N | [8 empty] | 柳營DS.#2DTR(A)_PF | #2DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D06 | 柳營DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 柳營DS.#2DTR(B)_MVA | #2DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D06 | 柳營DS | 0 |  | 2DTR(B) | #2DTR(B) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 柳營DS.#2DTR(B)_LOAD | #2DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 27 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D06 | 柳營DS | 0 |  | 2DTR(B) | #2DTR(B) |  | PF | [25 empty] | ADCS_N | [8 empty] | 柳營DS.#2DTR(B)_PF | #2DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D06 | 柳營DS | 0 |  | 1DTR | #1DTR |  | MW | [25 empty] | ADCS_N | [8 empty] | 柳營DS.#1DTR_MW | #1DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  | 1DTR | #1DTR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 柳營DS.#1DTR_MVAR | #1DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  | 1DTR | #1DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 柳營DS.#1DTR_MVA | #1DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D06 | 柳營DS | 0 |  | 1DTR | #1DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 柳營DS.#1DTR_LOAD | #1DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 32 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D06 | 柳營DS | 0 |  | 2DTR | #2DTR |  | MW | [25 empty] | ADCS_N | [8 empty] | 柳營DS.#2DTR_MW | #2DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  | 2DTR | #2DTR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 柳營DS.#2DTR_MVAR | #2DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  | 2DTR | #2DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 柳營DS.#2DTR_MVA | #2DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D06 | 柳營DS | 0 |  | 2DTR | #2DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 柳營DS.#2DTR_LOAD | #2DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 36 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D06 | 柳營DS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 柳營DS.210_SC_MVAR | 11KV#1SC MVAR | SC | D06/11/210/MVAR |  | SC_LBS_11 |  |  | 37 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 22 | 22kV | 220_SC | #2SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 柳營DS.220_SC_MVAR | 23KV#2SC MVAR | SC | D06/22/220/MVAR |  | SC_CAL_23 |  |  | 38 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 11 | 11kV | 230_SC | #3SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 柳營DS.230_SC_MVAR | 11KV#3SC MVAR | SC | D06/11/230/MVAR |  | SC_LBS_11 |  |  | 39 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 22 | 22kV | 240_SC | #4SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 柳營DS.240_SC_MVAR | 23KV#4SC MVAR | SC | D06/22/240/MVAR |  | SC_CAL_23 |  |  | 40 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳一線KVA | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳一線KVA | 11KV柳一線KVA | FEEDER |  |  | KVA_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳一線KW | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳一線KW | 11KV柳一線KW | FEEDER |  |  | KW_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  | TRTOT | 柳營主變瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 柳營DS.TRTOT_MW | 柳營主變瞬時供電量 MW |  |  |  | MTR_PQ_CAL |  |  | 43 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  | TRTOT | 柳營主變瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 柳營DS.TRTOT_MVAR | 柳營主變瞬時供電量 MVAR |  |  |  | MTR_PQ_CAL |  |  | 44 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳51線KVA | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳51線KVA | 23KV柳51線KVA | FEEDER |  |  | KVA_CAL |  |  | 45 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳51線KW | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳51線KW | 23KV柳51線KW | FEEDER |  |  | KW_CAL |  |  | 46 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳52線KVA | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳52線KVA | 23KV柳52線KVA | FEEDER |  |  | KVA_CAL |  |  | 47 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳52線KW | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳52線KW | 23KV柳52線KW | FEEDER |  |  | KW_CAL |  |  | 48 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳53線KVA | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳53線KVA | 23KV柳53線KVA | FEEDER |  |  | KVA_CAL |  |  | 49 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳53線KW | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳53線KW | 23KV柳53線KW | FEEDER |  |  | KW_CAL |  |  | 50 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳54線KVA | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳54線KVA | 23KV柳54線KVA | FEEDER |  |  | KVA_CAL |  |  | 51 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳54線KW | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳54線KW | 23KV柳54線KW | FEEDER |  |  | KW_CAL |  |  | 52 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳55線KVA | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳55線KVA | 23KV柳55線KVA | FEEDER |  |  | KVA_CAL |  |  | 53 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳55線KW | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳55線KW | 23KV柳55線KW | FEEDER |  |  | KW_CAL |  |  | 54 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳56線KVA | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳56線KVA | 23KV柳56線KVA | FEEDER |  |  | KVA_CAL |  |  | 55 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳56線KW | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳56線KW | 23KV柳56線KW | FEEDER |  |  | KW_CAL |  |  | 56 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳57線KVA | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳57線KVA | 23KV柳57線KVA | FEEDER |  |  | KVA_CAL |  |  | 57 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳57線KW | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳57線KW | 23KV柳57線KW | FEEDER |  |  | KW_CAL |  |  | 58 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳58線KVA | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳58線KVA | 23KV柳58線KVA | FEEDER |  |  | KVA_CAL |  |  | 59 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳58線KW | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳58線KW | 23KV柳58線KW | FEEDER |  |  | KW_CAL |  |  | 60 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳59線KVA | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳59線KVA | 23KV柳59線KVA | FEEDER |  |  | KVA_CAL |  |  | 61 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳59線KW | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳59線KW | 23KV柳59線KW | FEEDER |  |  | KW_CAL |  |  | 62 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳60線KVA | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳60線KVA | 23KV柳60線KVA | FEEDER |  |  | KVA_CAL |  |  | 63 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳60線KW | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳60線KW | 23KV柳60線KW | FEEDER |  |  | KW_CAL |  |  | 64 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  | TEN_DAYS06 | (1510+1520 MW) |  | MW | [25 empty] | CDCS | [8 empty] | 柳營DS.TEN_DAYS06_MW | (1510+1520 MW) |  |  |  | MTR_PQ_CAL |  |  | 65 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 161 | 161kV | 1950_SHR | #1SHR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 柳營DS.1950_SHR_MVAR | 161KV#1SHR MVAR | SC |  |  | SHR_CAL_324_5 |  |  | 66 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳31線KVA | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳31線KVA | 11KV柳31線KVA | FEEDER |  |  | KVA_CAL |  |  | 67 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳31線KW | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳31線KW | 11KV柳31線KW | FEEDER |  |  | KW_CAL |  |  | 68 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳32線KVA | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳32線KVA | 11KV柳32線KVA | FEEDER |  |  | KVA_CAL |  |  | 69 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳32線KW | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳32線KW | 11KV柳32線KW | FEEDER |  |  | KW_CAL |  |  | 70 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳33線KVA | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳33線KVA | 11KV柳33線KVA | FEEDER |  |  | KVA_CAL |  |  | 71 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳33線KW | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳33線KW | 11KV柳33線KW | FEEDER |  |  | KW_CAL |  |  | 72 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳34線KVA | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳34線KVA | 11KV柳34線KVA | FEEDER |  |  | KVA_CAL |  |  | 73 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳34線KW | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳34線KW | 11KV柳34線KW | FEEDER |  |  | KW_CAL |  |  | 74 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳35線KVA | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳35線KVA | 11KV柳35線KVA | FEEDER |  |  | KVA_CAL |  |  | 75 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  |  |  |  | 柳35線KW | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.柳35線KW | 11KV柳35線KW | FEEDER |  |  | KW_CAL |  |  | 76 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  | 100_CB | 100(100_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.100_CB_3 | 100 CB (D3) | TIE |  |  | AD_LAMP_DD_1 |  |  | 77 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | 200_CB | 200(200_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.200_CB_3 | 200 CB (D3) | TIE |  |  | AD_LAMP_DD_1 |  |  | 78 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | 1750_CB | #1DTR(1750_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.1750_CB_3 | 1750(#1DTR) CB (D3) | MTR |  |  | AD_LAMP_DD_1 |  |  | 79 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | 310_CB | #1DTR(310_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.310_CB_3 | 310(#1DTR) CB (D3) | MTR |  |  | AD_LAMP_DD_1 |  |  | 80 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | 320_CB | #1DTR(320_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.320_CB_3 | 320(#1DTR) CB (D3) | MTR |  |  | AD_LAMP_DD_1 |  |  | 81 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | 1760_CB | #2DTR(1760_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.1760_CB_3 | 1760(#2DTR) CB (D3) | MTR |  |  | AD_LAMP_DD_1 |  |  | 82 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | 330_CB | #2DTR(330_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.330_CB_3 | 330(#2DTR) CB (D3) | MTR |  |  | AD_LAMP_DD_1 |  |  | 83 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | 340_CB | #2DTR(340_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.340_CB_3 | 340(#2DTR) CB (D3) | MTR |  |  | AD_LAMP_DD_1 |  |  | 84 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | 210_CB | #1SC(210_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.210_CB_3 | 210(11KV #1SC) CB (D3) | SC |  |  | AD_LAMP_DD_1 |  |  | 85 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | 220_CB | #2SC(220_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.220_CB_3 | 220(23KV #2SC) CB (D3) | SC |  |  | AD_LAMP_DD_1 |  |  | 86 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | 230_CB | #3SC(230_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.230_CB_3 | 230(11KV #3SC) CB (D3) | SC |  |  | AD_LAMP_DD_1 |  |  | 87 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | 240_CB | #4SC(240_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.240_CB_3 | 240(23KV #4SC) CB (D3) | SC |  |  | AD_LAMP_DD_1 |  |  | 88 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | 11__CBA | 11/斷路器重故障(11__CBA) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.11/23KV_CBA_3 | 11/23KV斷路器重故障 (D3) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 89 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | 11__CBF | 11/斷路器輕故障(11__CBF) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.11/23KV_CBF_3 | 11/23KV斷路器輕故障 (D3) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 90 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | RTU_S_L | RTU |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.RTU_S/L_3 | RTU SUPY/LOCAL (D3) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 91 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D06 | 柳營DS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_N | [8 empty] | 柳營DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | D06/0/CalcPoint/SUBA |  | STATION_FAULT_10 |  |  | 92 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 變電所輕故障點燈 | 變電所輕故障點燈 |  | SUBF | [25 empty] | ADCS_N | [8 empty] | 柳營DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | D06/0/CalcPoint/SUBF |  | STATION_FAULT_2 |  |  | 93 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.變電所重故障_3 | 變電所重故障點燈 (D3) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 94 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.變電所輕故障_3 | 變電所輕故障點燈 (D3) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 95 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1510_AMP | 柳營新高紅線 | [27 empty] | ADCS_N | [8 empty] | 柳營DS.1510_AMP_A | 柳營新高紅線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 96 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D06 | 柳營DS | 161 | 161kV | 1520_AMP | 柳營新高榮特白 | [27 empty] | ADCS_N | [8 empty] | 柳營DS.1520_AMP_A | 柳營新高榮特白 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 97 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D06 | 柳營DS | 161 | 161kV | 1530_AMP | 新營柳營山線 | [27 empty] | ADCS_N | [8 empty] | 柳營DS.1530_AMP_A | 新營柳營山線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 98 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D06 | 柳營DS | 161 | 161kV | 1540_AMP | 新營柳營海線 | [27 empty] | ADCS_N | [8 empty] | 柳營DS.1540_AMP_A | 新營柳營海線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 99 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D06 | 柳營DS | 161 | 161kV | 1550_AMP | 嘉民柳營山線 | [27 empty] | ADCS_N | [8 empty] | 柳營DS.1550_AMP_A | 嘉民柳營山線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 100 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D06 | 柳營DS | 161 | 161kV | 1560_AMP | 嘉民柳營海線 | [27 empty] | ADCS_N | [8 empty] | 柳營DS.1560_AMP_A | 嘉民柳營海線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 101 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D06 | 柳營DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PERM | [25 empty] | ADCS_N | [8 empty] | 柳營DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | D06//1DTR(A)/TR_PERM |  | DTR_PERM |  |  | 102 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D06 | 柳營DS | 0 |  | 1DTR(B) | #1DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 柳營DS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | D06//1DTR(B)/TR_PERM |  | DTR_PERM |  |  | 103 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D06 | 柳營DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PERM | [25 empty] | ADCS_N | [8 empty] | 柳營DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | D06//2DTR(A)/TR_PERM |  | DTR_PERM |  |  | 104 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D06 | 柳營DS | 0 |  | 2DTR(B) | #2DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 柳營DS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | D06//2DTR(B)/TR_PERM |  | DTR_PERM |  |  | 105 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D06 | 柳營DS | 0 |  | 1DTR_MVA | #1DTR | [27 empty] | ADCS_N | [8 empty] | 柳營DS.#1DTR_MVA_A | #1DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 106 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D06 | 柳營DS | 0 |  | 1DTR_MVA | #1DTR(A) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.#1DTR_MVA_3 | #1DTR(A) MVA 點燈 (D3) | MTR |  |  | MAP_SET |  |  | 107 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D06 | 柳營DS | 0 |  | 1DTR_MVA | #1DTR(B) |  | 4 | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.#1DTR_MVA_4 | #1DTR(B) MVA 點燈 (D3) | MTR |  |  | MAP_SET |  |  | 108 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D06 | 柳營DS | 0 |  | 2DTR_MVA | #2DTR | [27 empty] | ADCS_N | [8 empty] | 柳營DS.#2DTR_MVA_A | #2DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 109 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D06 | 柳營DS | 0 |  | 2DTR_MVA | #2DTR(A) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.#2DTR_MVA_3 | #2DTR(A) MVA 點燈 (D3) | MTR |  |  | MAP_SET |  |  | 110 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D06 | 柳營DS | 0 |  | 2DTR_MVA | #2DTR(B) |  | 4 | [25 empty] | DDCS3_1 | [8 empty] | 柳營DS.#2DTR_MVA_4 | #2DTR(B) MVA 點燈 (D3) | MTR |  |  | MAP_SET |  |  | 111 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D06 | 柳營DS | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_N | [8 empty] | 柳營DS.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_DS |  |  | 112 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | PWR_FAIL_SW | 全停電啟動開關 | [27 empty] | ADCS_N | [8 empty] | 柳營DS.PWR_FAIL_SW_A | 全停電啟動開關 (AD) | OTHER |  |  | AD_PWR_FAIL |  |  | 113 | CalcDIPoint | [38 empty] | USE/LOCK | LOCK
D06 | 柳營DS | 0 |  | PWR_FAIL | PWR_FAIL |  | SCL | [25 empty] | ADCS_N | [8 empty] | 柳營DS.PWR_FAIL_SCL | 全停電操作啟動按鈕 | [6 empty] | 114 | CalcDIPoint | [38 empty] | RUNNING/STOPPED | STOPPED
D06 | 柳營DS | 0 |  | 1ABUS | #1ABUS |  | 11KV#1ABUSC | [25 empty] | CDCS | [8 empty] | 柳營DS.11KV#1ABUSC | #1ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 115 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D06 | 柳營DS | 0 |  | 1BBUS | #1BBUS |  | 23KV#1BBUSC | [25 empty] | CDCS | [8 empty] | 柳營DS.23KV#1BBUSC | #1BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 116 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D06 | 柳營DS | 0 |  | 2ABUS | #2ABUS |  | 11KV#2ABUSC | [25 empty] | CDCS | [8 empty] | 柳營DS.11KV#2ABUSC | #2ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 117 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D06 | 柳營DS | 0 |  | 2BBUS | #2BBUS |  | 23KV#2BBUSC | [25 empty] | CDCS | [8 empty] | 柳營DS.23KV#2BBUSC | #2BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 118 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D06 | 柳營DS | 0 |  | TAP_OVER | TAP |  | SET | [25 empty] | ADCS_N | [8 empty] | 柳營DS.TAP_OVER_SET | TAP OVER HI/LO ALARM | MTR |  |  | 5000_CB_T4 |  |  | 119 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D06 | 柳營DS | 0 |  | BUS_OVER | BUS |  | SET | [25 empty] | ADCS_N | [8 empty] | 柳營DS.BUS_OVER_SET | BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B4 |  |  | 120 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D06 | 柳營DS | 0 |  | 5000 | 虛擬5000 |  | CB動作 | [25 empty] | ADCS_N | [8 empty] | 柳營DS.5000_CB動作 | 虛擬5000 CB動作,請查明原因處理 | MTR |  |  | 5000_CB_M |  |  | 121 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | 注意OLTC | 注意OLTC |  | BUS電壓異常 | [25 empty] | ADCS_N | [8 empty] | 柳營DS.BUS電壓異常 | 注意OLTC Tap位置,並將RPDC閉鎖 | OTHER |  |  | STATION_FAULT_2 |  |  | 122 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | D06/0/RTU/ADCH1 |  |  |  | CDC | 123 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | D06/0/RTU/ADCH2 |  |  |  | CDC | 124 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | D06/0/RTU/ADCH3 |  |  |  | CDC | 125 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 0 |  | AI | AI |  | ADCH4 | [17 empty] | 2-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | D06/0/RTU/ADCH4 |  |  |  | CDC | 126 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 0 |  | AI | AI |  | ADCH5 | [17 empty] | 3-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.AI_ADCH5 | AI 90%參考點 ADCH5 | OTHER |  |  |  |  | CDC | 127 | GENERICAIPoint | DS044_L3 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | D06/0/RTU/ADCL1 |  |  |  | CDC | 128 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | D06/0/RTU/ADCL2 |  |  |  | CDC | 129 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | D06/0/RTU/ADCL3 |  |  |  | CDC | 130 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 0 |  | AI | AI |  | ADCL4 | [17 empty] | 2-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | D06/0/RTU/ADCL4 |  |  |  | CDC | 131 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 0 |  | AI | AI |  | ADCL5 | [17 empty] | 3-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.AI_ADCL5 | AI 10%參考點 ADCL5 | OTHER |  |  |  |  | CDC | 132 | GENERICAIPoint | DS044_L3 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 161 | 161kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | D06/161/1BUS/V |  |  |  | CDC | 133 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D06 | 柳營DS | 161 | 161kV | 2BUS | #2BUS |  | V | [17 empty] | 1-83 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | D06/161/2BUS/V |  |  |  | CDC | 134 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D06 | 柳營DS | 11 | 11kV | 1ABUS | #1ABUS |  | V | [17 empty] | 1-AE | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.11KV#1ABUS_KV | 11KV #1ABUS KV | BUS | D06/11/1ABUS/V |  |  |  | CDC | 135 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D06 | 柳營DS | 11 | 11kV | 2ABUS | #2ABUS |  | V | [17 empty] | 1-EE | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS | D06/11/2ABUS/V |  |  |  | CDC | 136 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D06 | 柳營DS | 161 | 161kV | 1510 | 柳營新高紅線(1510) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.1510_MW | 柳營新高紅線 MW | LINE161 | D06/161/1510/MW |  |  |  | CDC | 137 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D06 | 柳營DS | 161 | 161kV | 1510 | 柳營新高紅線(1510) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.1510_MVAR | 柳營新高紅線 MVAR | LINE161 | D06/161/1510/MVAR |  |  |  | CDC | 138 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D06 | 柳營DS | 161 | 161kV | 1520 | 柳營新高榮特白(1520) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.1520_MW | 柳營新高榮特白 MW | LINE161 | D06/161/1520/MW |  |  |  | CDC | 139 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D06 | 柳營DS | 161 | 161kV | 1520 | 柳營新高榮特白(1520) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.1520_MVAR | 柳營新高榮特白 MVAR | LINE161 | D06/161/1520/MVAR |  |  |  | CDC | 140 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D06 | 柳營DS | 161 | 161kV | 1530 | 新營柳營山線(1530) |  | MW | [17 empty] | 1-88 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.1530_MW | 新營柳營山線 MW | LINE161 | D06/161/1530/MW |  |  |  | CDC | 141 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D06 | 柳營DS | 161 | 161kV | 1530 | 新營柳營山線(1530) |  | MVAR | [17 empty] | 1-89 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.1530_MVAR | 新營柳營山線 MVAR | LINE161 | D06/161/1530/MVAR |  |  |  | CDC | 142 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D06 | 柳營DS | 161 | 161kV | 1540 | 新營柳營海線(1540) |  | MW | [17 empty] | 1-8A | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.1540_MW | 新營柳營海線 MW | LINE161 | D06/161/1540/MW |  |  |  | CDC | 143 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D06 | 柳營DS | 161 | 161kV | 1540 | 新營柳營海線(1540) |  | MVAR | [17 empty] | 1-8B | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.1540_MVAR | 新營柳營海線 MVAR | LINE161 | D06/161/1540/MVAR |  |  |  | CDC | 144 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D06 | 柳營DS | 161 | 161kV | 1550 | 嘉民柳營山線(1550) |  | MW | [17 empty] | 1-8C | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.1550_MW | 嘉民柳營山線 MW | LINE161 | D06/161/1550/MW |  |  |  | CDC | 145 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D06 | 柳營DS | 161 | 161kV | 1550 | 嘉民柳營山線(1550) |  | MVAR | [17 empty] | 1-8D | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.1550_MVAR | 嘉民柳營山線 MVAR | LINE161 | D06/161/1550/MVAR |  |  |  | CDC | 146 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D06 | 柳營DS | 161 | 161kV | 1560 | 嘉民柳營海線(1560) |  | MW | [17 empty] | 1-8E | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.1560_MW | 嘉民柳營海線 MW | LINE161 | D06/161/1560/MW |  |  |  | CDC | 147 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D06 | 柳營DS | 161 | 161kV | 1560 | 嘉民柳營海線(1560) |  | MVAR | [17 empty] | 1-8F | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.1560_MVAR | 嘉民柳營海線 MVAR | LINE161 | D06/161/1560/MVAR |  |  |  | CDC | 148 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳二線 | 柳二線 |  | 柳二線KVAR | [17 empty] | 1-B4 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳二線KVAR | 11KV柳二線 KVAR | FEEDER | D06/11/VJ22/KVAR |  |  |  | CDC | 149 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳二線 | 柳二線 |  | 柳二線A1 | [17 empty] | 1-B5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳二線A1 | 11KV柳二線 R相AMP | FEEDER | D06/11/VJ22/I_R |  |  |  | CDC | 150 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳二線 | 柳二線 |  | 柳二線A2 | [17 empty] | 1-B6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳二線A2 | 11KV柳二線 S相AMP | FEEDER | D06/11/VJ22/I_S |  |  |  | CDC | 151 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳二線 | 柳二線 |  | 柳二線A3 | [17 empty] | 1-B7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳二線A3 | 11KV柳二線 T相AMP | FEEDER | D06/11/VJ22/I_T |  |  |  | CDC | 152 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳二線 | 柳二線 |  | 柳二線A0 | [17 empty] | 1-B8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳二線A0 | 11KV柳二線 N相AMP | FEEDER | D06/11/VJ22/I_N |  |  |  | CDC | 153 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳三線 | 柳三線 |  | 柳三線KVAR | [17 empty] | 1-B9 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳三線KVAR | 11KV柳三線 KVAR | FEEDER | D06/11/VJ23/KVAR |  |  |  | CDC | 154 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳三線 | 柳三線 |  | 柳三線A1 | [17 empty] | 1-BA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳三線A1 | 11KV柳三線 R相AMP | FEEDER | D06/11/VJ23/I_R |  |  |  | CDC | 155 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳三線 | 柳三線 |  | 柳三線A2 | [17 empty] | 1-BB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳三線A2 | 11KV柳三線 S相AMP | FEEDER | D06/11/VJ23/I_S |  |  |  | CDC | 156 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳三線 | 柳三線 |  | 柳三線A3 | [17 empty] | 1-BC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳三線A3 | 11KV柳三線 T相AMP | FEEDER | D06/11/VJ23/I_T |  |  |  | CDC | 157 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳三線 | 柳三線 |  | 柳三線A0 | [17 empty] | 1-BD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳三線A0 | 11KV柳三線 N相AMP | FEEDER | D06/11/VJ23/I_N |  |  |  | CDC | 158 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳五線 | 柳五線 |  | 柳五線KVAR | [17 empty] | 1-C5 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳五線KVAR | 11KV柳五線 KVAR | FEEDER | D06/11/VJ25/KVAR |  |  |  | CDC | 159 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳五線 | 柳五線 |  | 柳五線A1 | [17 empty] | 1-C6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳五線A1 | 11KV柳五線 R相AMP | FEEDER | D06/11/VJ25/I_R |  |  |  | CDC | 160 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳五線 | 柳五線 |  | 柳五線A2 | [17 empty] | 1-C7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳五線A2 | 11KV柳五線 S相AMP | FEEDER | D06/11/VJ25/I_S |  |  |  | CDC | 161 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳五線 | 柳五線 |  | 柳五線A3 | [17 empty] | 1-C8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳五線A3 | 11KV柳五線 T相AMP | FEEDER | D06/11/VJ25/I_T |  |  |  | CDC | 162 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳五線 | 柳五線 |  | 柳五線A0 | [17 empty] | 1-C9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳五線A0 | 11KV柳五線 N相AMP | FEEDER | D06/11/VJ25/I_N |  |  |  | CDC | 163 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳正線 | 柳正線 |  | 柳正線KVAR | [17 empty] | 1-BE | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳正線KVAR | 11KV柳正線 KVAR | FEEDER | D06/11/VJ24/KVAR |  |  |  | CDC | 164 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳正線 | 柳正線 |  | 柳正線A1 | [17 empty] | 1-BF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳正線A1 | 11KV柳正線 R相AMP | FEEDER | D06/11/VJ24/I_R |  |  |  | CDC | 165 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳正線 | 柳正線 |  | 柳正線A2 | [17 empty] | 1-C2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳正線A2 | 11KV柳正線 S相AMP | FEEDER | D06/11/VJ24/I_S |  |  |  | CDC | 166 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳正線 | 柳正線 |  | 柳正線A3 | [17 empty] | 1-C3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳正線A3 | 11KV柳正線 T相AMP | FEEDER | D06/11/VJ24/I_T |  |  |  | CDC | 167 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳正線 | 柳正線 |  | 柳正線A0 | [17 empty] | 1-C4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳正線A0 | 11KV柳正線 N相AMP | FEEDER | D06/11/VJ24/I_N |  |  |  | CDC | 168 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 0 |  | 1500TIE | 1500TIE |  | I | [17 empty] | 1-98 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.1500TIE_AMP | 1500TIE AMP | TIE | D06/161/1500/I_R |  |  |  | CDC | 169 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | _100 | 100 |  | I_R | [17 empty] | 2-8A | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.11KV_100_A1 | 11KV 100 R相AMP | TIE | D06/11/100/I_R |  |  |  | CDC | 170 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | _100 | 100 |  | I_S | [17 empty] | 2-8B | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.11KV_100_A2 | 11KV 100 S相AMP | TIE | D06/11/100/I_S |  |  |  | CDC | 171 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | _100 | 100 |  | I_T | [17 empty] | 2-8C | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.11KV_100_A3 | 11KV 100 T相AMP | TIE | D06/11/100/I_T |  |  |  | CDC | 172 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MW | [17 empty] | 1-A9 | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | D06/11/310/KW |  |  |  | CDC | 173 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D06 | 柳營DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVAR | [17 empty] | 1-AA | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | D06/11/310/KVAR |  |  |  | CDC | 174 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D06 | 柳營DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_R | [17 empty] | 1-AB | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | D06/11/310/I_R |  |  |  | CDC | 175 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_S | [17 empty] | 1-AC | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | D06/11/310/I_S |  |  |  | CDC | 176 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_T | [17 empty] | 1-AD | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | D06/11/310/I_T |  |  |  | CDC | 177 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 0 |  | 1DTR | #1DTR |  | OilTemp | [17 empty] | 1-99 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.#1DTR_OIL | #1DTR 油溫 | MTR | D06//1DTR/OilTemp |  |  |  | CDC | 178 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D06 | 柳營DS | 0 |  | 1DTR(A) | #1DTR(A) |  | CoilTemp | [17 empty] | 1-9A | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | D06//1DTR(A)/CoilTemp |  |  |  | CDC | 179 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D06 | 柳營DS | 0 |  | 1DTR(A) | #1DTR(A) |  | TapPosMv | [17 empty] | 1-9C |  | 1-39 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 柳營DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | D06//1DTR(A)/TapPosMv |  |  |  | CDC | 180 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D06 | 柳營DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MW | [17 empty] | 1-CA | [5 empty] | MW_-108_108(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | D06/22/320/KW |  |  |  | CDC | 181 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D06 | 柳營DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVAR | [17 empty] | 1-CB | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | D06/22/320/KVAR |  |  |  | CDC | 182 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D06 | 柳營DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_R | [17 empty] | 1-CC | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | D06/22/320/I_R |  |  |  | CDC | 183 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_S | [17 empty] | 1-CD | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | D06/22/320/I_S |  |  |  | CDC | 184 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_T | [17 empty] | 1-CE | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | D06/22/320/I_T |  |  |  | CDC | 185 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 0 |  | 1DTR(B) | #1DTR(B) |  | CoilTemp | [17 empty] | 1-9B | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | D06//1DTR(B)/CoilTemp |  |  |  | CDC | 186 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D06 | 柳營DS | 0 |  | 1DTR(B) | #1DTR(B) |  | TapPosMv | [17 empty] | 1-9D |  | 1-3B |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 柳營DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | D06//1DTR(B)/TapPosMv |  |  |  | CDC | 187 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D06 | 柳營DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MW | [17 empty] | 1-E9 | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | D06/11/330/KW |  |  |  | CDC | 188 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D06 | 柳營DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVAR | [17 empty] | 1-EA | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | D06/11/330/KVAR |  |  |  | CDC | 189 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D06 | 柳營DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_R | [17 empty] | 1-EB | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | D06/11/330/I_R |  |  |  | CDC | 190 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_S | [17 empty] | 1-EC | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | D06/11/330/I_S |  |  |  | CDC | 191 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_T | [17 empty] | 1-ED | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | D06/11/330/I_T |  |  |  | CDC | 192 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 0 |  | 2DTR | #2DTR |  | OilTemp | [17 empty] | 1-9E | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.#2DTR_OIL | #2DTR 油溫 | MTR | D06//2DTR/OilTemp |  |  |  | CDC | 193 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D06 | 柳營DS | 0 |  | 2DTR(A) | #2DTR(A) |  | CoilTemp | [17 empty] | 1-9F | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | D06//2DTR(A)/CoilTemp |  |  |  | CDC | 194 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D06 | 柳營DS | 0 |  | 2DTR(A) | #2DTR(A) |  | TapPosMv | [17 empty] | 1-A1 |  | 1-3D |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 柳營DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | D06//2DTR(A)/TapPosMv |  |  |  | CDC | 195 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D06 | 柳營DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MW | [17 empty] | 2-8D | [5 empty] | MW_-108_108(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | D06/22/340/KW |  |  |  | CDC | 196 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D06 | 柳營DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVAR | [17 empty] | 2-8E | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | D06/22/340/KVAR |  |  |  | CDC | 197 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D06 | 柳營DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_R | [17 empty] | 2-8F | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | D06/22/340/I_R |  |  |  | CDC | 198 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_S | [17 empty] | 2-90 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | D06/22/340/I_S |  |  |  | CDC | 199 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_T | [17 empty] | 2-91 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | D06/22/340/I_T |  |  |  | CDC | 200 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 0 |  | 2DTR(B) | #2DTR(B) |  | CoilTemp | [17 empty] | 1-A0 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | D06//2DTR(B)/CoilTemp |  |  |  | CDC | 201 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D06 | 柳營DS | 0 |  | 2DTR(B) | #2DTR(B) |  | TapPosMv | [17 empty] | 1-A2 |  | 1-3F |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 柳營DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | D06//2DTR(B)/TapPosMv |  |  |  | CDC | 202 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D06 | 柳營DS | 0 |  |  |  |  | DCV_N | [17 empty] | 1-97 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.直流N電源電壓 | 直流N電源電壓 | OTHER | D06/0/StaDev/DCV_N |  |  |  | CDC | 203 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D06 | 柳營DS | 0 |  |  |  |  | DCV_P | [17 empty] | 1-96 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.直流P電源電壓 | 直流P電源電壓 | OTHER | D06/0/StaDev/DCV_P |  |  |  | CDC | 204 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳一線 | 柳一線 |  | 柳一線KVAR | [17 empty] | 1-AF | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳一線KVAR | 11KV柳一線 KVAR | FEEDER | D06/11/VJ21/KVAR |  |  |  | CDC | 205 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳一線 | 柳一線 |  | 柳一線A1 | [17 empty] | 1-B0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳一線A1 | 11KV柳一線 R相AMP | FEEDER | D06/11/VJ21/I_R |  |  |  | CDC | 206 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳一線 | 柳一線 |  | 柳一線A2 | [17 empty] | 1-B1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳一線A2 | 11KV柳一線 S相AMP | FEEDER | D06/11/VJ21/I_S |  |  |  | CDC | 207 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳一線 | 柳一線 |  | 柳一線A3 | [17 empty] | 1-B2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳一線A3 | 11KV柳一線 T相AMP | FEEDER | D06/11/VJ21/I_T |  |  |  | CDC | 208 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳一線 | 柳一線 |  | 柳一線A0 | [17 empty] | 1-B3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳一線A0 | 11KV柳一線 N相AMP | FEEDER | D06/11/VJ21/I_N |  |  |  | CDC | 209 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 1BBUS | #1BBUS |  | V | [17 empty] | 1-CF | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.23KV#1BBUS_KV | 23KV #1BBUS KV | BUS | D06/22/1BBUS/V |  |  |  | CDC | 210 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D06 | 柳營DS | 22 | 22kV | 2BBUS | #2BBUS |  | V | [17 empty] | 2-92 | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.23KV#2BBUS_KV | 23KV #2BBUS KV | BUS | D06/22/2BBUS/V |  |  |  | CDC | 211 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D06 | 柳營DS | 22 | 22kV | 柳51線 | 柳51線 |  | 柳51線KVAR | [17 empty] | 1-D0 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳51線KVAR | 23KV柳51線 KVAR | FEEDER | D06/22/VJ51/KVAR |  |  |  | CDC | 212 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳51線 | 柳51線 |  | 柳51線A1 | [17 empty] | 1-D1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳51線A1 | 23KV柳51線 R相AMP | FEEDER | D06/22/VJ51/I_R |  |  |  | CDC | 213 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳51線 | 柳51線 |  | 柳51線A2 | [17 empty] | 1-D2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳51線A2 | 23KV柳51線 S相AMP | FEEDER | D06/22/VJ51/I_S |  |  |  | CDC | 214 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳51線 | 柳51線 |  | 柳51線A3 | [17 empty] | 1-D3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳51線A3 | 23KV柳51線 T相AMP | FEEDER | D06/22/VJ51/I_T |  |  |  | CDC | 215 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳51線 | 柳51線 |  | 柳51線A0 | [17 empty] | 1-D4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳51線A0 | 23KV柳51線 N相AMP | FEEDER | D06/22/VJ51/I_N |  |  |  | CDC | 216 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳52線 | 柳52線 |  | 柳52線KVAR | [17 empty] | 1-D5 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳52線KVAR | 23KV柳52線 KVAR | FEEDER | D06/22/VJ52/KVAR |  |  |  | CDC | 217 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳52線 | 柳52線 |  | 柳52線A1 | [17 empty] | 1-D6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳52線A1 | 23KV柳52線 R相AMP | FEEDER | D06/22/VJ52/I_R |  |  |  | CDC | 218 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳52線 | 柳52線 |  | 柳52線A2 | [17 empty] | 1-D7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳52線A2 | 23KV柳52線 S相AMP | FEEDER | D06/22/VJ52/I_S |  |  |  | CDC | 219 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳52線 | 柳52線 |  | 柳52線A3 | [17 empty] | 1-D8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳52線A3 | 23KV柳52線 T相AMP | FEEDER | D06/22/VJ52/I_T |  |  |  | CDC | 220 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳52線 | 柳52線 |  | 柳52線A0 | [17 empty] | 1-D9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳52線A0 | 23KV柳52線 N相AMP | FEEDER | D06/22/VJ52/I_N |  |  |  | CDC | 221 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳53線 | 柳53線 |  | 柳53線KVAR | [17 empty] | 1-DA | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳53線KVAR | 23KV柳53線 KVAR | FEEDER | D06/22/VJ53/KVAR |  |  |  | CDC | 222 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳53線 | 柳53線 |  | 柳53線A1 | [17 empty] | 1-DB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳53線A1 | 23KV柳53線 R相AMP | FEEDER | D06/22/VJ53/I_R |  |  |  | CDC | 223 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳53線 | 柳53線 |  | 柳53線A2 | [17 empty] | 1-DC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳53線A2 | 23KV柳53線 S相AMP | FEEDER | D06/22/VJ53/I_S |  |  |  | CDC | 224 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳53線 | 柳53線 |  | 柳53線A3 | [17 empty] | 1-DD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳53線A3 | 23KV柳53線 T相AMP | FEEDER | D06/22/VJ53/I_T |  |  |  | CDC | 225 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳53線 | 柳53線 |  | 柳53線A0 | [17 empty] | 1-DE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳53線A0 | 23KV柳53線 N相AMP | FEEDER | D06/22/VJ53/I_N |  |  |  | CDC | 226 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳54線 | 柳54線 |  | 柳54線KVAR | [17 empty] | 1-DF | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳54線KVAR | 23KV柳54線 KVAR | FEEDER | D06/22/VJ54/KVAR |  |  |  | CDC | 227 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳54線 | 柳54線 |  | 柳54線A1 | [17 empty] | 1-E0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳54線A1 | 23KV柳54線 R相AMP | FEEDER | D06/22/VJ54/I_R |  |  |  | CDC | 228 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳54線 | 柳54線 |  | 柳54線A2 | [17 empty] | 1-E1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳54線A2 | 23KV柳54線 S相AMP | FEEDER | D06/22/VJ54/I_S |  |  |  | CDC | 229 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳54線 | 柳54線 |  | 柳54線A3 | [17 empty] | 1-E2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳54線A3 | 23KV柳54線 T相AMP | FEEDER | D06/22/VJ54/I_T |  |  |  | CDC | 230 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳54線 | 柳54線 |  | 柳54線A0 | [17 empty] | 1-E3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳54線A0 | 23KV柳54線 N相AMP | FEEDER | D06/22/VJ54/I_N |  |  |  | CDC | 231 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳55線 | 柳55線 |  | 柳55線KVAR | [17 empty] | 1-E4 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳55線KVAR | 23KV柳55線 KVAR | FEEDER | D06/22/VJ55/KVAR |  |  |  | CDC | 232 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳55線 | 柳55線 |  | 柳55線A1 | [17 empty] | 1-E5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳55線A1 | 23KV柳55線 R相AMP | FEEDER | D06/22/VJ55/I_R |  |  |  | CDC | 233 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳55線 | 柳55線 |  | 柳55線A2 | [17 empty] | 1-E6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳55線A2 | 23KV柳55線 S相AMP | FEEDER | D06/22/VJ55/I_S |  |  |  | CDC | 234 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳55線 | 柳55線 |  | 柳55線A3 | [17 empty] | 1-E7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳55線A3 | 23KV柳55線 T相AMP | FEEDER | D06/22/VJ55/I_T |  |  |  | CDC | 235 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳55線 | 柳55線 |  | 柳55線A0 | [17 empty] | 1-E8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳55線A0 | 23KV柳55線 N相AMP | FEEDER | D06/22/VJ55/I_N |  |  |  | CDC | 236 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳56線 | 柳56線 |  | 柳56線KVAR | [17 empty] | 2-93 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳56線KVAR | 23KV柳56線 KVAR | FEEDER | D06/22/VJ56/KVAR |  |  |  | CDC | 237 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳56線 | 柳56線 |  | 柳56線A1 | [17 empty] | 2-94 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳56線A1 | 23KV柳56線 R相AMP | FEEDER | D06/22/VJ56/I_R |  |  |  | CDC | 238 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳56線 | 柳56線 |  | 柳56線A2 | [17 empty] | 2-95 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳56線A2 | 23KV柳56線 S相AMP | FEEDER | D06/22/VJ56/I_S |  |  |  | CDC | 239 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳56線 | 柳56線 |  | 柳56線A3 | [17 empty] | 2-96 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳56線A3 | 23KV柳56線 T相AMP | FEEDER | D06/22/VJ56/I_T |  |  |  | CDC | 240 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳56線 | 柳56線 |  | 柳56線A0 | [17 empty] | 2-97 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳56線A0 | 23KV柳56線 N相AMP | FEEDER | D06/22/VJ56/I_N |  |  |  | CDC | 241 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳57線 | 柳57線 |  | 柳57線KVAR | [17 empty] | 2-98 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳57線KVAR | 23KV柳57線 KVAR | FEEDER | D06/22/VJ57/KVAR |  |  |  | CDC | 242 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳57線 | 柳57線 |  | 柳57線A1 | [17 empty] | 2-99 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳57線A1 | 23KV柳57線 R相AMP | FEEDER | D06/22/VJ57/I_R |  |  |  | CDC | 243 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳57線 | 柳57線 |  | 柳57線A2 | [17 empty] | 2-9A | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳57線A2 | 23KV柳57線 S相AMP | FEEDER | D06/22/VJ57/I_S |  |  |  | CDC | 244 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳57線 | 柳57線 |  | 柳57線A3 | [17 empty] | 2-9B | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳57線A3 | 23KV柳57線 T相AMP | FEEDER | D06/22/VJ57/I_T |  |  |  | CDC | 245 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳57線 | 柳57線 |  | 柳57線A0 | [17 empty] | 2-9C | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳57線A0 | 23KV柳57線 N相AMP | FEEDER | D06/22/VJ57/I_N |  |  |  | CDC | 246 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳58線 | 柳58線 |  | 柳58線KVAR | [17 empty] | 2-9D | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳58線KVAR | 23KV柳58線 KVAR | FEEDER | D06/22/VJ58/KVAR |  |  |  | CDC | 247 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳58線 | 柳58線 |  | 柳58線A1 | [17 empty] | 2-9E | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳58線A1 | 23KV柳58線 R相AMP | FEEDER | D06/22/VJ58/I_R |  |  |  | CDC | 248 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳58線 | 柳58線 |  | 柳58線A2 | [17 empty] | 2-9F | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳58線A2 | 23KV柳58線 S相AMP | FEEDER | D06/22/VJ58/I_S |  |  |  | CDC | 249 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳58線 | 柳58線 |  | 柳58線A3 | [17 empty] | 2-A0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳58線A3 | 23KV柳58線 T相AMP | FEEDER | D06/22/VJ58/I_T |  |  |  | CDC | 250 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳58線 | 柳58線 |  | 柳58線A0 | [17 empty] | 2-A1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳58線A0 | 23KV柳58線 N相AMP | FEEDER | D06/22/VJ58/I_N |  |  |  | CDC | 251 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳59線 | 柳59線 |  | 柳59線KVAR | [17 empty] | 2-A2 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳59線KVAR | 23KV柳59線 KVAR | FEEDER | D06/22/VJ59/KVAR |  |  |  | CDC | 252 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳59線 | 柳59線 |  | 柳59線A1 | [17 empty] | 2-A3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳59線A1 | 23KV柳59線 R相AMP | FEEDER | D06/22/VJ59/I_R |  |  |  | CDC | 253 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳59線 | 柳59線 |  | 柳59線A2 | [17 empty] | 2-A4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳59線A2 | 23KV柳59線 S相AMP | FEEDER | D06/22/VJ59/I_S |  |  |  | CDC | 254 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳59線 | 柳59線 |  | 柳59線A3 | [17 empty] | 2-A5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳59線A3 | 23KV柳59線 T相AMP | FEEDER | D06/22/VJ59/I_T |  |  |  | CDC | 255 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳59線 | 柳59線 |  | 柳59線A0 | [17 empty] | 2-A6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳59線A0 | 23KV柳59線 N相AMP | FEEDER | D06/22/VJ59/I_N |  |  |  | CDC | 256 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳60線 | 柳60線 |  | 柳60線KVAR | [17 empty] | 2-A7 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳60線KVAR | 23KV柳60線 KVAR | FEEDER | D06/22/VJ60/KVAR |  |  |  | CDC | 257 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳60線 | 柳60線 |  | 柳60線A1 | [17 empty] | 2-A8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳60線A1 | 23KV柳60線 R相AMP | FEEDER | D06/22/VJ60/I_R |  |  |  | CDC | 258 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳60線 | 柳60線 |  | 柳60線A2 | [17 empty] | 2-A9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳60線A2 | 23KV柳60線 S相AMP | FEEDER | D06/22/VJ60/I_S |  |  |  | CDC | 259 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳60線 | 柳60線 |  | 柳60線A3 | [17 empty] | 2-AA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳60線A3 | 23KV柳60線 T相AMP | FEEDER | D06/22/VJ60/I_T |  |  |  | CDC | 260 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | 柳60線 | 柳60線 |  | 柳60線A0 | [17 empty] | 2-AB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳60線A0 | 23KV柳60線 N相AMP | FEEDER | D06/22/VJ60/I_N |  |  |  | CDC | 261 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | _200 | 200 |  | I_R | [17 empty] | 2-AC | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.23KV_200_A1 | 23KV 200 R相AMP | TIE | D06/22/200/I_R |  |  |  | CDC | 262 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | _200 | 200 |  | I_S | [17 empty] | 2-AD | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.23KV_200_A2 | 23KV 200 S相AMP | TIE | D06/22/200/I_S |  |  |  | CDC | 263 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 22 | 22kV | _200 | 200 |  | I_T | [17 empty] | 2-AE | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.23KV_200_A3 | 23KV 200 T相AMP | TIE | D06/22/200/I_T |  |  |  | CDC | 264 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 161 | 161kV | 1611SHR | #1SHR |  | CoilTemp | [17 empty] | 2-AF | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.161#1SHR_COIL | 161KV #1SHR 線溫 | OTHER | D06//1SHR/OilTemp |  |  |  | CDC | 265 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D06 | 柳營DS | 161 | 161kV | 1611SHR | #1SHR |  | OilTemp | [17 empty] | 2-B0 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 柳營DS.161#1SHR_OIL | 161KV #1SHR 油溫 | OTHER | D06//1SHR/CoilTemp |  |  |  | CDC | 266 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D06 | 柳營DS | 11 | 11kV | 柳31線 | 柳31線 |  | 柳31線KVAR | [17 empty] | 1-EF | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳31線KVAR | 11KV柳31線 KVAR | FEEDER | D06/11/VJ31/KVAR |  |  |  | CDC | 267 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳31線 | 柳31線 |  | 柳31線A1 | [17 empty] | 1-F0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳31線A1 | 11KV柳31線 R相AMP | FEEDER | D06/11/VJ31/I_R |  |  |  | CDC | 268 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳31線 | 柳31線 |  | 柳31線A2 | [17 empty] | 1-F1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳31線A2 | 11KV柳31線 S相AMP | FEEDER | D06/11/VJ31/I_S |  |  |  | CDC | 269 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳31線 | 柳31線 |  | 柳31線A3 | [17 empty] | 1-F2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳31線A3 | 11KV柳31線 T相AMP | FEEDER | D06/11/VJ31/I_T |  |  |  | CDC | 270 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳31線 | 柳31線 |  | 柳31線A0 | [17 empty] | 1-F3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳31線A0 | 11KV柳31線 N相AMP | FEEDER | D06/11/VJ31/I_N |  |  |  | CDC | 271 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳32線 | 柳32線 |  | 柳32線KVAR | [17 empty] | 1-F4 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳32線KVAR | 11KV柳32線 KVAR | FEEDER | D06/11/VJ32/KVAR |  |  |  | CDC | 272 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳32線 | 柳32線 |  | 柳32線A1 | [17 empty] | 1-F5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳32線A1 | 11KV柳32線 R相AMP | FEEDER | D06/11/VJ32/I_R |  |  |  | CDC | 273 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳32線 | 柳32線 |  | 柳32線A2 | [17 empty] | 1-F6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳32線A2 | 11KV柳32線 S相AMP | FEEDER | D06/11/VJ32/I_S |  |  |  | CDC | 274 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳32線 | 柳32線 |  | 柳32線A3 | [17 empty] | 1-F7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳32線A3 | 11KV柳32線 T相AMP | FEEDER | D06/11/VJ32/I_T |  |  |  | CDC | 275 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳32線 | 柳32線 |  | 柳32線A0 | [17 empty] | 1-F8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳32線A0 | 11KV柳32線 N相AMP | FEEDER | D06/11/VJ32/I_N |  |  |  | CDC | 276 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳33線 | 柳33線 |  | 柳33線KVAR | [17 empty] | 1-F9 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳33線KVAR | 11KV柳33線 KVAR | FEEDER | D06/11/VJ33/KVAR |  |  |  | CDC | 277 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳33線 | 柳33線 |  | 柳33線A1 | [17 empty] | 1-FA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳33線A1 | 11KV柳33線 R相AMP | FEEDER | D06/11/VJ33/I_R |  |  |  | CDC | 278 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳33線 | 柳33線 |  | 柳33線A2 | [17 empty] | 1-FB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳33線A2 | 11KV柳33線 S相AMP | FEEDER | D06/11/VJ33/I_S |  |  |  | CDC | 279 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳33線 | 柳33線 |  | 柳33線A3 | [17 empty] | 1-FC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳33線A3 | 11KV柳33線 T相AMP | FEEDER | D06/11/VJ33/I_T |  |  |  | CDC | 280 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳33線 | 柳33線 |  | 柳33線A0 | [17 empty] | 1-FD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳33線A0 | 11KV柳33線 N相AMP | FEEDER | D06/11/VJ33/I_N |  |  |  | CDC | 281 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳34線 | 柳34線 |  | 柳34線KVAR | [17 empty] | 1-FE | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳34線KVAR | 11KV柳34線 KVAR | FEEDER | D06/11/VJ34/KVAR |  |  |  | CDC | 282 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳34線 | 柳34線 |  | 柳34線A1 | [17 empty] | 1-FF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳34線A1 | 11KV柳34線 R相AMP | FEEDER | D06/11/VJ34/I_R |  |  |  | CDC | 283 | GENERICAIPoint | DS044_L1 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳34線 | 柳34線 |  | 柳34線A2 | [17 empty] | 2-82 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳34線A2 | 11KV柳34線 S相AMP | FEEDER | D06/11/VJ34/I_S |  |  |  | CDC | 284 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳34線 | 柳34線 |  | 柳34線A3 | [17 empty] | 2-83 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳34線A3 | 11KV柳34線 T相AMP | FEEDER | D06/11/VJ34/I_T |  |  |  | CDC | 285 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳34線 | 柳34線 |  | 柳34線A0 | [17 empty] | 2-84 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳34線A0 | 11KV柳34線 N相AMP | FEEDER | D06/11/VJ34/I_N |  |  |  | CDC | 286 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳35線 | 柳35線 |  | 柳35線KVAR | [17 empty] | 2-85 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳35線KVAR | 11KV柳35線 KVAR | FEEDER | D06/11/VJ35/KVAR |  |  |  | CDC | 287 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳35線 | 柳35線 |  | 柳35線A1 | [17 empty] | 2-86 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳35線A1 | 11KV柳35線 R相AMP | FEEDER | D06/11/VJ35/I_R |  |  |  | CDC | 288 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳35線 | 柳35線 |  | 柳35線A2 | [17 empty] | 2-87 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳35線A2 | 11KV柳35線 S相AMP | FEEDER | D06/11/VJ35/I_S |  |  |  | CDC | 289 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳35線 | 柳35線 |  | 柳35線A3 | [17 empty] | 2-88 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳35線A3 | 11KV柳35線 T相AMP | FEEDER | D06/11/VJ35/I_T |  |  |  | CDC | 290 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 11 | 11kV | 柳35線 | 柳35線 |  | 柳35線A0 | [17 empty] | 2-89 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 柳營DS.柳35線A0 | 11KV柳35線 N相AMP | FEEDER | D06/11/VJ35/I_N |  |  |  | CDC | 291 | GENERICAIPoint | DS044_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D06 | 柳營DS | 161 | 161kV | 1510 | 柳營新高紅線(1510) |  | PHA | [17 empty] | 1-00-03 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.1510_PHA | 柳營新高紅線(1510) 相間RY | LINE161 | D06/161/1510/PHA |  |  |  | CDC | 292 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1510 | 柳營新高紅線(1510) |  | GDA | [17 empty] | 1-00-04 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.1510_GDA | 柳營新高紅線(1510) 接地RY | LINE161 | D06/161/1510/GDA |  |  |  | CDC | 293 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1510 | 柳營新高紅線(1510) |  | 21A | [17 empty] | 1-00-01 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.1510_21A | 柳營新高紅線(1510) 21RY | LINE161 | D06/161/1510/21A |  |  |  | CDC | 294 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1510 | 柳營新高紅線(1510) |  | CB | [17 empty] | 1-00-00 |  | 1-01 | [5 empty] | 161KV_N | [8 empty] | 柳營DS.1510_CB | 1510(柳營新高紅線) CB | LINE161 | D06/161/1510/CB |  |  |  | CDC | 295 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 161 | 161kV | 1510 | 柳營新高紅線(1510) |  | DS1 | 1511 | [16 empty] | 1-38-00 | 1-38-01 | 1-44 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1511_DS | 1511(柳營新高紅線) DS | LINE161 | D06/161/1510/DS1 |  |  |  | CDC | 296 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1510 | 柳營新高紅線(1510) |  | DS2 | 1512 | [16 empty] | 1-38-02 | 1-38-03 | 1-45 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1512_DS | 1512(柳營新高紅線) DS | LINE161 | D06/161/1510/DS2 |  |  |  | CDC | 297 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D06 | 柳營DS | 161 | 161kV | 1510 | 柳營新高紅線(1510) |  | DS3 | 1513 | [16 empty] | 1-38-04 | 1-38-05 | 1-46 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1513_DS | 1513(柳營新高紅線) DS | LINE161 | D06/161/1510/DS3 |  |  |  | CDC | 298 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1510 | 柳營新高紅線(1510) |  | E3 | 1513E | [16 empty] | 1-38-06 | 1-38-07 | 1-47 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1513E_ES | 1513E(柳營新高紅線) ES | LINE161 | D06/161/1510/ES3 |  |  |  | CDC | 299 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D06 | 柳營DS | 161 | 161kV | 1520 | 柳營新高榮特白(1520) |  | PHA | [17 empty] | 1-01-00 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.1520_PHA | 柳營新高榮特白(1520) 相間RY | LINE161 | D06/161/1520/PHA |  |  |  | CDC | 300 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1520 | 柳營新高榮特白(1520) |  | GDA | [17 empty] | 1-01-01 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.1520_GDA | 柳營新高榮特白(1520) 接地RY | LINE161 | D06/161/1520/GDA |  |  |  | CDC | 301 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1520 | 柳營新高榮特白(1520) |  | 21A | [17 empty] | 1-00-06 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.1520_21A | 柳營新高榮特白(1520) 21RY | LINE161 | D06/161/1520/21A |  |  |  | CDC | 302 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1520 | 柳營新高榮特白(1520) |  | CB | [17 empty] | 1-00-05 |  | 1-02 | [5 empty] | 161KV_N | [8 empty] | 柳營DS.1520_CB | 1520(柳營新高榮特白) CB | LINE161 | D06/161/1520/CB |  |  |  | CDC | 303 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 161 | 161kV | 1520 | 柳營新高榮特白(1520) |  | DS1 | 1521 | [16 empty] | 1-38-08 | 1-38-09 | 1-48 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1521_DS | 1521(柳營新高榮特白) DS | LINE161 | D06/161/1520/DS1 |  |  |  | CDC | 304 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D06 | 柳營DS | 161 | 161kV | 1520 | 柳營新高榮特白(1520) |  | DS2 | 1522 | [16 empty] | 1-38-10 | 1-38-11 | 1-49 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1522_DS | 1522(柳營新高榮特白) DS | LINE161 | D06/161/1520/DS2 |  |  |  | CDC | 305 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1520 | 柳營新高榮特白(1520) |  | DS3 | 1523 | [16 empty] | 1-38-12 | 1-38-13 | 1-4A | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1523_DS | 1523(柳營新高榮特白) DS | LINE161 | D06/161/1520/DS3 |  |  |  | CDC | 306 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1520 | 柳營新高榮特白(1520) |  | E3 | 1523E | [16 empty] | 1-38-14 | 1-38-15 | 1-4B | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1523E_ES | 1523E(柳營新高榮特白) ES | LINE161 | D06/161/1520/ES3 |  |  |  | CDC | 307 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D06 | 柳營DS | 161 | 161kV | 1530 | 新營柳營山線(1530) |  | PHA | [17 empty] | 1-01-05 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.1530_PHA | 新營柳營山線(1530) 相間RY | LINE161 | D06/161/1530/PHA |  |  |  | CDC | 308 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1530 | 新營柳營山線(1530) |  | GDA | [17 empty] | 1-01-06 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.1530_GDA | 新營柳營山線(1530) 接地RY | LINE161 | D06/161/1530/GDA |  |  |  | CDC | 309 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1530 | 新營柳營山線(1530) |  | 87UL | [17 empty] | 1-30-06 |  | 1-28 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1530_87UL | 新營柳營山線(1530) 87RY U/L | LINE161 | D06/161/1530/87UL |  |  |  | CDC | 310 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 161 | 161kV | 1530 | 新營柳營山線(1530) |  | CB | [17 empty] | 1-01-02 |  | 1-03 | [5 empty] | 161KV_N | [8 empty] | 柳營DS.1530_CB | 1530(新營柳營山線) CB | LINE161 | D06/161/1530/CB |  |  |  | CDC | 311 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 161 | 161kV | 1530 | 新營柳營山線(1530) |  | 79UL | [17 empty] | 1-30-07 |  | 1-29 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1530_79UL | 新營柳營山線(1530) 79RY U/L | LINE161 | D06/161/1530/79UL |  |  |  | CDC | 312 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 161 | 161kV | 1530 | 新營柳營山線(1530) |  | DS1 | 1531 | [16 empty] | 1-39-00 | 1-39-01 | 1-4C | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1531_DS | 1531(新營柳營山線) DS | LINE161 | D06/161/1530/DS1 |  |  |  | CDC | 313 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1530 | 新營柳營山線(1530) |  | DS2 | 1532 | [16 empty] | 1-39-02 | 1-39-03 | 1-4D | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1532_DS | 1532(新營柳營山線) DS | LINE161 | D06/161/1530/DS2 |  |  |  | CDC | 314 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D06 | 柳營DS | 161 | 161kV | 1530 | 新營柳營山線(1530) |  | DS3 | 1533 | [16 empty] | 1-39-04 | 1-39-05 | 1-4E | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1533_DS | 1533(新營柳營山線) DS | LINE161 | D06/161/1530/DS3 |  |  |  | CDC | 315 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1530 | 新營柳營山線(1530) |  | E3 | 1533E | [16 empty] | 1-39-06 | 1-39-07 | 1-4F | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1533E_ES | 1533E(新營柳營山線) ES | LINE161 | D06/161/1530/ES3 |  |  |  | CDC | 316 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D06 | 柳營DS | 161 | 161kV | 1540 | 新營柳營海線(1540) |  | PHA | [17 empty] | 1-02-02 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.1540_PHA | 新營柳營海線(1540) 相間RY | LINE161 | D06/161/1540/PHA |  |  |  | CDC | 317 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1540 | 新營柳營海線(1540) |  | GDA | [17 empty] | 1-02-03 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.1540_GDA | 新營柳營海線(1540) 接地RY | LINE161 | D06/161/1540/GDA |  |  |  | CDC | 318 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1540 | 新營柳營海線(1540) |  | 87UL | [17 empty] | 1-30-08 |  | 1-2A | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1540_87UL | 新營柳營海線(1540) 87RY U/L | LINE161 | D06/161/1540/87UL |  |  |  | CDC | 319 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 161 | 161kV | 1540 | 新營柳營海線(1540) |  | CB | [17 empty] | 1-01-07 |  | 1-04 | [5 empty] | 161KV_N | [8 empty] | 柳營DS.1540_CB | 1540(新營柳營海線) CB | LINE161 | D06/161/1540/CB |  |  |  | CDC | 320 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 161 | 161kV | 1540 | 新營柳營海線(1540) |  | 79UL | [17 empty] | 1-30-09 |  | 1-2B | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1540_79UL | 新營柳營海線(1540) 79RY U/L | LINE161 | D06/161/1540/79UL |  |  |  | CDC | 321 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 161 | 161kV | 1540 | 新營柳營海線(1540) |  | DS1 | 1541 | [16 empty] | 1-39-08 | 1-39-09 | 1-50 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1541_DS | 1541(新營柳營海線) DS | LINE161 | D06/161/1540/DS1 |  |  |  | CDC | 322 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D06 | 柳營DS | 161 | 161kV | 1540 | 新營柳營海線(1540) |  | DS2 | 1542 | [16 empty] | 1-39-10 | 1-39-11 | 1-51 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1542_DS | 1542(新營柳營海線) DS | LINE161 | D06/161/1540/DS2 |  |  |  | CDC | 323 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1540 | 新營柳營海線(1540) |  | DS3 | 1543 | [16 empty] | 1-39-12 | 1-39-13 | 1-52 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1543_DS | 1543(新營柳營海線) DS | LINE161 | D06/161/1540/DS3 |  |  |  | CDC | 324 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1540 | 新營柳營海線(1540) |  | E3 | 1543E | [16 empty] | 1-39-14 | 1-39-15 | 1-53 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1543E_ES | 1543E(新營柳營海線) ES | LINE161 | D06/161/1540/ES3 |  |  |  | CDC | 325 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D06 | 柳營DS | 161 | 161kV | 1550 | 嘉民柳營山線(1550) |  | PHA | [17 empty] | 1-02-07 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.1550_PHA | 嘉民柳營山線(1550) 相間RY | LINE161 | D06/161/1550/PHA |  |  |  | CDC | 326 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1550 | 嘉民柳營山線(1550) |  | GDA | [17 empty] | 1-03-00 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.1550_GDA | 嘉民柳營山線(1550) 接地RY | LINE161 | D06/161/1550/GDA |  |  |  | CDC | 327 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1550 | 嘉民柳營山線(1550) |  | 87UL | [17 empty] | 1-30-10 |  | 1-2C | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1550_87UL | 嘉民柳營山線(1550) 87RY U/L | LINE161 | D06/161/1550/87UL |  |  |  | CDC | 328 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 161 | 161kV | 1550 | 嘉民柳營山線(1550) |  | CB | [17 empty] | 1-02-04 |  | 1-05 | [5 empty] | 161KV_N | [8 empty] | 柳營DS.1550_CB | 1550(嘉民柳營山線) CB | LINE161 | D06/161/1550/CB |  |  |  | CDC | 329 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 161 | 161kV | 1550 | 嘉民柳營山線(1550) |  | 79UL | [17 empty] | 1-30-11 |  | 1-2D | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1550_79UL | 嘉民柳營山線(1550) 79RY U/L | LINE161 | D06/161/1550/79UL |  |  |  | CDC | 330 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 161 | 161kV | 1550 | 嘉民柳營山線(1550) |  | DS1 | 1551 | [16 empty] | 1-3A-00 | 1-3A-01 | 1-54 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1551_DS | 1551(嘉民柳營山線) DS | LINE161 | D06/161/1550/DS1 |  |  |  | CDC | 331 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1550 | 嘉民柳營山線(1550) |  | DS2 | 1552 | [16 empty] | 1-3A-02 | 1-3A-03 | 1-55 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1552_DS | 1552(嘉民柳營山線) DS | LINE161 | D06/161/1550/DS2 |  |  |  | CDC | 332 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D06 | 柳營DS | 161 | 161kV | 1550 | 嘉民柳營山線(1550) |  | DS3 | 1553 | [16 empty] | 1-3A-04 | 1-3A-05 | 1-56 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1553_DS | 1553(嘉民柳營山線) DS | LINE161 | D06/161/1550/DS3 |  |  |  | CDC | 333 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1550 | 嘉民柳營山線(1550) |  | E3 | 1553E | [16 empty] | 1-3A-06 | 1-3A-07 | 1-57 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1553E_ES | 1553E(嘉民柳營山線) ES | LINE161 | D06/161/1550/ES3 |  |  |  | CDC | 334 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D06 | 柳營DS | 161 | 161kV | 1560 | 嘉民柳營海線(1560) |  | PHA | [17 empty] | 1-03-04 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.1560_PHA | 嘉民柳營海線(1560) 相間RY | LINE161 | D06/161/1560/PHA |  |  |  | CDC | 335 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1560 | 嘉民柳營海線(1560) |  | GDA | [17 empty] | 1-03-05 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.1560_GDA | 嘉民柳營海線(1560) 接地RY | LINE161 | D06/161/1560/GDA |  |  |  | CDC | 336 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1560 | 嘉民柳營海線(1560) |  | 87UL | [17 empty] | 1-30-12 |  | 1-2E | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1560_87UL | 嘉民柳營海線(1560) 87RY U/L | LINE161 | D06/161/1560/87UL |  |  |  | CDC | 337 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 161 | 161kV | 1560 | 嘉民柳營海線(1560) |  | CB | [17 empty] | 1-03-01 |  | 1-06 | [5 empty] | 161KV_N | [8 empty] | 柳營DS.1560_CB | 1560(嘉民柳營海線) CB | LINE161 | D06/161/1560/CB |  |  |  | CDC | 338 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 161 | 161kV | 1560 | 嘉民柳營海線(1560) |  | 79UL | [17 empty] | 1-30-13 |  | 1-2F | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1560_79UL | 嘉民柳營海線(1560) 79RY U/L | LINE161 | D06/161/1560/79UL |  |  |  | CDC | 339 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 161 | 161kV | 1560 | 嘉民柳營海線(1560) |  | DS1 | 1561 | [16 empty] | 1-3A-08 | 1-3A-09 | 1-58 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1561_DS | 1561(嘉民柳營海線) DS | LINE161 | D06/161/1560/DS1 |  |  |  | CDC | 340 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D06 | 柳營DS | 161 | 161kV | 1560 | 嘉民柳營海線(1560) |  | DS2 | 1562 | [16 empty] | 1-3A-10 | 1-3A-11 | 1-59 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1562_DS | 1562(嘉民柳營海線) DS | LINE161 | D06/161/1560/DS2 |  |  |  | CDC | 341 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1560 | 嘉民柳營海線(1560) |  | DS3 | 1563 | [16 empty] | 1-3A-12 | 1-3A-13 | 1-5A | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1563_DS | 1563(嘉民柳營海線) DS | LINE161 | D06/161/1560/DS3 |  |  |  | CDC | 342 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1560 | 嘉民柳營海線(1560) |  | E3 | 1563E | [16 empty] | 1-3A-14 | 1-3A-15 | 1-5B | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1563E_ES | 1563E(嘉民柳營海線) ES | LINE161 | D06/161/1560/ES3 |  |  |  | CDC | 343 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D06 | 柳營DS | 11 | 11kV | VJ21 | 柳一線(VJ21) |  | PHA | [17 empty] | 1-10-01 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ21_PHA | 11KV柳一線(VJ21) 相間RY | FEEDER | D06/11/VJ21/PHA |  |  |  | CDC | 344 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ21 | 柳一線(VJ21) |  | GDA | [17 empty] | 1-10-02 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ21_GDA | 11KV柳一線(VJ21) 接地RY | FEEDER | D06/11/VJ21/GDA |  |  |  | CDC | 345 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ21 | 柳一線(VJ21) 79RY |  | 79UL | [17 empty] | 2-30-00 |  | 2-24 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ21_79UL | 11KV柳一線(VJ21) 79RY U/L | FEEDER | D06/11/VJ21/79UL |  |  |  | CDC | 346 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 11 | 11kV | VJ21_LCO | 柳一線(VJ21) LCO |  | TapPosMv | [17 empty] | 2-30-01 |  | 2-25 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ21_LCO_TAP | 11KV柳一線(VJ21) LCO TAP | FEEDER | D06/11/VJ21/ADJ |  |  |  | CDC | 347 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D06 | 柳營DS | 11 | 11kV | VJ21 | VJ21(11KV柳一線) |  | CB | [17 empty] | 1-10-00 |  | 1-13 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ21_CB | VJ21(11KV柳一線) CB | FEEDER | D06/11/VJ21/CB |  |  |  | CDC | 348 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | VJ22 | 柳二線(VJ22) |  | PHA | [17 empty] | 1-10-04 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ22_PHA | 11KV柳二線(VJ22) 相間RY | FEEDER | D06/11/VJ22/PHA |  |  |  | CDC | 349 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ22 | 柳二線(VJ22) |  | GDA | [17 empty] | 1-10-05 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ22_GDA | 11KV柳二線(VJ22) 接地RY | FEEDER | D06/11/VJ22/GDA |  |  |  | CDC | 350 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ22 | 柳二線(VJ22) 79RY |  | 79UL | [17 empty] | 2-30-02 |  | 2-26 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ22_79UL | 11KV柳二線(VJ22) 79RY U/L | FEEDER | D06/11/VJ22/79UL |  |  |  | CDC | 351 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 11 | 11kV | VJ22_LCO | 柳二線(VJ22) LCO |  | TapPosMv | [17 empty] | 2-30-03 |  | 2-27 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ22_LCO_TAP | 11KV柳二線(VJ22) LCO TAP | FEEDER | D06/11/VJ22/ADJ |  |  |  | CDC | 352 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D06 | 柳營DS | 11 | 11kV | VJ22 | VJ22(11KV柳二線) |  | CB | [17 empty] | 1-10-03 |  | 1-14 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ22_CB | VJ22(11KV柳二線) CB | FEEDER | D06/11/VJ22/CB |  |  |  | CDC | 353 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | VJ23 | 柳三線(VJ23) |  | PHA | [17 empty] | 1-10-07 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ23_PHA | 11KV柳三線(VJ23) 相間RY | FEEDER | D06/11/VJ23/PHA |  |  |  | CDC | 354 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ23 | 柳三線(VJ23) |  | GDA | [17 empty] | 1-11-00 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ23_GDA | 11KV柳三線(VJ23) 接地RY | FEEDER | D06/11/VJ23/GDA |  |  |  | CDC | 355 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ23 | 柳三線(VJ23) 79RY |  | 79UL | [17 empty] | 2-30-04 |  | 2-28 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ23_79UL | 11KV柳三線(VJ23) 79RY U/L | FEEDER | D06/11/VJ23/79UL |  |  |  | CDC | 356 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 11 | 11kV | VJ23_LCO | 柳三線(VJ23) LCO |  | TapPosMv | [17 empty] | 2-30-05 |  | 2-29 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ23_LCO_TAP | 11KV柳三線(VJ23) LCO TAP | FEEDER | D06/11/VJ23/ADJ |  |  |  | CDC | 357 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D06 | 柳營DS | 11 | 11kV | VJ23 | VJ23(11KV柳三線) |  | CB | [17 empty] | 1-10-06 |  | 1-15 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ23_CB | VJ23(11KV柳三線) CB | FEEDER | D06/11/VJ23/CB |  |  |  | CDC | 358 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | VJ24 | 柳正線(VJ24) |  | PHA | [17 empty] | 1-11-02 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ24_PHA | 11KV柳正線(VJ24) 相間RY | FEEDER | D06/11/VJ24/PHA |  |  |  | CDC | 359 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ24 | 柳正線(VJ24) |  | GDA | [17 empty] | 1-11-03 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ24_GDA | 11KV柳正線(VJ24) 接地RY | FEEDER | D06/11/VJ24/GDA |  |  |  | CDC | 360 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ24 | 柳正線(VJ24) 79RY |  | 79UL | [17 empty] | 2-30-06 |  | 2-2A | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ24_79UL | 11KV柳正線(VJ24) 79RY U/L | FEEDER | D06/11/VJ24/79UL |  |  |  | CDC | 361 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 11 | 11kV | VJ24_LCO | 柳正線(VJ24) LCO |  | TapPosMv | [17 empty] | 2-30-07 |  | 2-2B | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ24_LCO_TAP | 11KV柳正線(VJ24) LCO TAP | FEEDER | D06/11/VJ24/ADJ |  |  |  | CDC | 362 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D06 | 柳營DS | 11 | 11kV | VJ24 | VJ24(11KV柳正線) |  | CB | [17 empty] | 1-11-01 |  | 1-16 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ24_CB | VJ24(11KV柳正線) CB | FEEDER | D06/11/VJ24/CB |  |  |  | CDC | 363 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | VJ25 | 柳五線(VJ25) |  | PHA | [17 empty] | 1-11-05 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ25_PHA | 11KV柳五線(VJ25) 相間RY | FEEDER | D06/11/VJ25/PHA |  |  |  | CDC | 364 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ25 | 柳五線(VJ25) |  | GDA | [17 empty] | 1-11-06 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ25_GDA | 11KV柳五線(VJ25) 接地RY | FEEDER | D06/11/VJ25/GDA |  |  |  | CDC | 365 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ25 | 柳五線(VJ25) 79RY |  | 79UL | [17 empty] | 2-30-08 |  | 2-2C | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ25_79UL | 11KV柳五線(VJ25) 79RY U/L | FEEDER | D06/11/VJ25/79UL |  |  |  | CDC | 366 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 11 | 11kV | VJ25_LCO | 柳五線(VJ25) LCO |  | TapPosMv | [17 empty] | 2-30-09 |  | 2-2D | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ25_LCO_TAP | 11KV柳五線(VJ25) LCO TAP | FEEDER | D06/11/VJ25/ADJ |  |  |  | CDC | 367 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D06 | 柳營DS | 11 | 11kV | VJ25 | VJ25(11KV柳五線) |  | CB | [17 empty] | 1-11-04 |  | 1-17 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ25_CB | VJ25(11KV柳五線) CB | FEEDER | D06/11/VJ25/CB |  |  |  | CDC | 368 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | VJ31 | 柳31線(VJ31) |  | PHA | [17 empty] | 2-10-01 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ31_PHA | 11KV柳31線(VJ31) 相間RY | FEEDER | D06/11/VJ31/PHA |  |  |  | CDC | 369 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ31 | 柳31線(VJ31) |  | GDA | [17 empty] | 2-10-02 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ31_GDA | 11KV柳31線(VJ31) 接地RY | FEEDER | D06/11/VJ31/GDA |  |  |  | CDC | 370 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ31 | 柳31線(VJ31) 79RY |  | 79UL | [17 empty] | 2-31-04 |  | 2-38 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ31_79UL | 11KV柳31線(VJ31) 79RY U/L | FEEDER | D06/11/VJ31/79UL |  |  |  | CDC | 371 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 11 | 11kV | VJ31_LCO | 柳31線(VJ31) LCO |  | TapPosMv | [17 empty] | 2-31-05 |  | 2-39 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ31_LCO_TAP | 11KV柳31線(VJ31) LCO TAP | FEEDER | D06/11/VJ31/ADJ |  |  |  | CDC | 372 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D06 | 柳營DS | 11 | 11kV | VJ31 | VJ31(11KV柳31線) |  | CB | [17 empty] | 2-10-00 |  | 2-02 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ31_CB | VJ31(11KV柳31線) CB | FEEDER | D06/11/VJ31/CB |  |  |  | CDC | 373 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | VJ32 | 柳32線(VJ32) |  | PHA | [17 empty] | 2-10-04 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ32_PHA | 11KV柳32線(VJ32) 相間RY | FEEDER | D06/11/VJ32/PHA |  |  |  | CDC | 374 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ32 | 柳32線(VJ32) |  | GDA | [17 empty] | 2-10-05 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ32_GDA | 11KV柳32線(VJ32) 接地RY | FEEDER | D06/11/VJ32/GDA |  |  |  | CDC | 375 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ32 | 柳32線(VJ32) 79RY |  | 79UL | [17 empty] | 2-31-06 |  | 2-3A | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ32_79UL | 11KV柳32線(VJ32) 79RY U/L | FEEDER | D06/11/VJ32/79UL |  |  |  | CDC | 376 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 11 | 11kV | VJ32_LCO | 柳32線(VJ32) LCO |  | TapPosMv | [17 empty] | 2-31-07 |  | 2-3B | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ32_LCO_TAP | 11KV柳32線(VJ32) LCO TAP | FEEDER | D06/11/VJ32/ADJ |  |  |  | CDC | 377 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D06 | 柳營DS | 11 | 11kV | VJ32 | VJ32(11KV柳32線) |  | CB | [17 empty] | 2-10-03 |  | 2-03 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ32_CB | VJ32(11KV柳32線) CB | FEEDER | D06/11/VJ32/CB |  |  |  | CDC | 378 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | VJ33 | 柳33線(VJ33) |  | PHA | [17 empty] | 2-10-07 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ33_PHA | 11KV柳33線(VJ33) 相間RY | FEEDER | D06/11/VJ33/PHA |  |  |  | CDC | 379 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ33 | 柳33線(VJ33) |  | GDA | [17 empty] | 2-11-00 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ33_GDA | 11KV柳33線(VJ33) 接地RY | FEEDER | D06/11/VJ33/GDA |  |  |  | CDC | 380 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ33 | 柳33線(VJ33) 79RY |  | 79UL | [17 empty] | 2-31-08 |  | 2-3C | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ33_79UL | 11KV柳33線(VJ33) 79RY U/L | FEEDER | D06/11/VJ33/79UL |  |  |  | CDC | 381 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 11 | 11kV | VJ33_LCO | 柳33線(VJ33) LCO |  | TapPosMv | [17 empty] | 2-31-09 |  | 2-3D | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ33_LCO_TAP | 11KV柳33線(VJ33) LCO TAP | FEEDER | D06/11/VJ33/ADJ |  |  |  | CDC | 382 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D06 | 柳營DS | 11 | 11kV | VJ33 | VJ33(11KV柳33線) |  | CB | [17 empty] | 2-10-06 |  | 2-04 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ33_CB | VJ33(11KV柳33線) CB | FEEDER | D06/11/VJ33/CB |  |  |  | CDC | 383 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | VJ34 | 柳34線(VJ34) |  | PHA | [17 empty] | 2-11-02 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ34_PHA | 11KV柳34線(VJ34) 相間RY | FEEDER | D06/11/VJ34/PHA |  |  |  | CDC | 384 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ34 | 柳34線(VJ34) |  | GDA | [17 empty] | 2-11-03 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ34_GDA | 11KV柳34線(VJ34) 接地RY | FEEDER | D06/11/VJ34/GDA |  |  |  | CDC | 385 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ34 | 柳34線(VJ34) 79RY |  | 79UL | [17 empty] | 2-31-10 |  | 2-3E | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ34_79UL | 11KV柳34線(VJ34) 79RY U/L | FEEDER | D06/11/VJ34/79UL |  |  |  | CDC | 386 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 11 | 11kV | VJ34_LCO | 柳34線(VJ34) LCO |  | TapPosMv | [17 empty] | 2-31-11 |  | 2-3F | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ34_LCO_TAP | 11KV柳34線(VJ34) LCO TAP | FEEDER | D06/11/VJ34/ADJ |  |  |  | CDC | 387 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D06 | 柳營DS | 11 | 11kV | VJ34 | VJ34(11KV柳34線) |  | CB | [17 empty] | 2-11-01 |  | 2-05 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ34_CB | VJ34(11KV柳34線) CB | FEEDER | D06/11/VJ34/CB |  |  |  | CDC | 388 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | VJ35 | 柳35線(VJ35) |  | PHA | [17 empty] | 2-11-05 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ35_PHA | 11KV柳35線(VJ35) 相間RY | FEEDER | D06/11/VJ35/PHA |  |  |  | CDC | 389 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ35 | 柳35線(VJ35) |  | GDA | [17 empty] | 2-11-06 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ35_GDA | 11KV柳35線(VJ35) 接地RY | FEEDER | D06/11/VJ35/GDA |  |  |  | CDC | 390 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | VJ35 | 柳35線(VJ35) 79RY |  | 79UL | [17 empty] | 2-31-12 |  | 2-40 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ35_79UL | 11KV柳35線(VJ35) 79RY U/L | FEEDER | D06/11/VJ35/79UL |  |  |  | CDC | 391 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 11 | 11kV | VJ35_LCO | 柳35線(VJ35) LCO |  | TapPosMv | [17 empty] | 2-31-13 |  | 2-41 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ35_LCO_TAP | 11KV柳35線(VJ35) LCO TAP | FEEDER | D06/11/VJ35/ADJ |  |  |  | CDC | 392 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D06 | 柳營DS | 11 | 11kV | VJ35 | VJ35(11KV柳35線) |  | CB | [17 empty] | 2-11-04 |  | 2-06 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ35_CB | VJ35(11KV柳35線) CB | FEEDER | D06/11/VJ35/CB |  |  |  | CDC | 393 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | 100 | TIE(100) |  | CB | [17 empty] | 2-12-02 |  | 2-00 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.100_CB | 100(TIE) CB | TIE | D06/11/100/CB |  |  |  | CDC | 394 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | 100 | TIE(100) |  | 51A | [17 empty] | 2-12-03 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.100_51A | 11KV TIE(100) 51RY | TIE | D06/11/100/PHA |  |  |  | CDC | 395 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 100 | TIE(100) |  | 51NA | [17 empty] | 2-12-04 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.100_51NA | 11KV TIE(100) 51N RY | TIE | D06/11/100/GDA |  |  |  | CDC | 396 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [17 empty] | 1-06-01 |  | 1-0B | [5 empty] | 161KV_N | [8 empty] | 柳營DS.1500_CB | 1500(TIE) CB | TIE | D06/161/1500/CB |  |  |  | CDC | 397 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | 1500 | TIE(1500) |  | 50A | [17 empty] | 1-06-02 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.1500_50A | 161KV TIE(1500) 50RY | TIE | D06/161/1500/50A |  |  |  | CDC | 398 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [16 empty] | 1-3D-00 | 1-3D-01 | 1-6C | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1501_DS | 1501(TIE) DS | TIE | D06/161/1500/DS1 |  |  |  | CDC | 399 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [16 empty] | 1-3D-02 | 1-3D-03 | 1-6D | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1502_DS | 1502(TIE) DS | TIE | D06/161/1500/DS2 |  |  |  | CDC | 400 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 0 |  | 200 | TIE(200) |  | CB | [17 empty] | 2-14-07 |  | 2-07 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.200_CB | 200(TIE) CB | TIE | D06/22/200/CB |  |  |  | CDC | 401 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | 200 | TIE(200) |  | 51A | [17 empty] | 2-15-00 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.200_51A | 23KV TIE(200) 51RY | TIE | D06/22/200/PHA |  |  |  | CDC | 402 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 200 | TIE(200) |  | 51NA | [17 empty] | 2-15-01 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.200_51NA | 23KV TIE(200) 51N RY | TIE | D06/22/200/GDA |  |  |  | CDC | 403 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 390 | #1SSTR(390) |  | CB | [17 empty] | 1-12-02 |  | 1-12 | [5 empty] | 161KV_N | [8 empty] | 柳營DS.390_CB | 390(#1SSTR) CB | OTHER | D06/11/390/CB |  |  |  | CDC | 404 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | 1SSTR | #1SSTR |  | 51A | [17 empty] | 1-12-03 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.#1SSTR_51A | #1SSTR 51RY | OTHER | D06/11/390/PHA |  |  |  | CDC | 405 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 1SSTR | #1SSTR |  | 51NA | [17 empty] | 1-12-04 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | D06/11/390/GDA |  |  |  | CDC | 406 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 490 | #2SSTR(490) |  | CB | [17 empty] | 2-15-02 |  | 2-08 | [5 empty] | 161KV_N | [8 empty] | 柳營DS.490_CB | 490(#2SSTR) CB | OTHER | D06/22/490/CB |  |  |  | CDC | 407 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | 2SSTR | #2SSTR |  | 51A | [17 empty] | 2-15-03 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.#2SSTR_51A | #2SSTR 51RY | OTHER | D06/22/490/PHA |  |  |  | CDC | 408 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 2SSTR | #2SSTR |  | 51NA | [17 empty] | 2-15-04 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | D06/22/490/GDA |  |  |  | CDC | 409 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB | [17 empty] | 1-07-00 |  | 1-0C | [5 empty] | 161KV_N | [8 empty] | 柳營DS.1750_CB | 1750(#1DTR) CB | MTR | D06/161/1750/CB |  |  |  | CDC | 410 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | 310 | #1DTR(310) |  | CB | [17 empty] | 1-07-06 |  | 1-10 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.310_CB | 310(#1DTR) CB | MTR | D06/11/310/CB |  |  |  | CDC | 411 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | 320 | #1DTR(320) |  | CB | [17 empty] | 1-08-02 |  | 1-18 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.320_CB | 320(#1DTR) CB | MTR | D06/22/320/CB |  |  |  | CDC | 412 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | 1DTR | #1DTR |  | 51A | [17 empty] | 1-07-04 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.#1DTR_51A | #1DTR 51RY | MTR | D06//1DTR/PHA |  |  |  | CDC | 413 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 1DTR | #1DTR |  | 51NA | [17 empty] | 1-07-05 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.#1DTR_51NA | #1DTR 51N RY | MTR | D06//1DTR/GDA |  |  |  | CDC | 414 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 1DTR | #1DTR |  | 51ZA | [17 empty] | 1-07-03 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | D06//1DTR/51ZA |  |  |  | CDC | 415 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 1DTR | #1DTR |  | 87A | [17 empty] | 1-07-01 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.#1DTR_87A | #1DTR 87RY | MTR | D06//1DTR/87A |  |  |  | CDC | 416 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 310 | #1DTR(310) |  | 51A | [17 empty] | 1-07-07 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.310_51A | #1DTR二次側(310) 51RY | MTR |  |  |  |  | CDC | 417 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 320 | #1DTR(320) |  | 51A | [17 empty] | 1-08-03 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.320_51A | #1DTR二次側(320) 51RY | MTR |  |  |  |  | CDC | 418 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 1DTR | #1DTR |  | 96PA | [17 empty] | 1-07-02 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | D06//1DTR/96PA |  |  |  | CDC | 419 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 1DTR | #1DTR |  | 96D | [17 empty] | 1-31-13 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.#1DTR_96D | #1DTR 96D RY | MTR | D06//1DTR/96D |  |  |  | CDC | 420 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 1DTR | #1DTR |  | 96P | [17 empty] | 1-31-14 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.#1DTR_96P | #1DTR 96P RY | MTR | D06//1DTR/96P |  |  |  | CDC | 421 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 1DTR | #1DTR |  | 63Q | [17 empty] | 1-31-15 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.#1DTR_63Q | #1DTR 63Q RY | MTR | D06//1DTR/63Q |  |  |  | CDC | 422 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 1DTR | #1DTR |  | 96B1 | [17 empty] | 1-31-11 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | D06//1DTR/96B1 |  |  |  | CDC | 423 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 1DTR | #1DTR |  | 96B2 | [17 empty] | 1-31-12 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | D06//1DTR/96B2 |  |  |  | CDC | 424 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 1DTR | #1DTR |  | TRA | [17 empty] | 1-32-01 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.#1DTR_TRA | #1DTR 重故障 | MTR | D06//1DTR/TRA |  |  |  | CDC | 425 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 1DTR | #1DTR |  | TRF | [17 empty] | 1-32-00 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.#1DTR_TRF | #1DTR 輕故障 | MTR | D06//1DTR/TRF |  |  |  | CDC | 426 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 1DTR(A) | #1DTR(A) |  | SupLocal | [17 empty] | 1-31-07 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | D06//1DTR(A)/SupLocal |  |  |  | CDC | 427 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D06 | 柳營DS | 0 |  | 1DTR(A) | #1DTR(A) |  | A_M | [17 empty] | 1-31-08 |  | 1-38 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | D06//1DTR(A)/Tap Chan |  |  |  | CDC | 428 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D06 | 柳營DS | 0 |  | 1DTR(B) | #1DTR(B) |  | SupLocal | [17 empty] | 1-31-09 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | D06//1DTR(B)/SupLocal |  |  |  | CDC | 429 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D06 | 柳營DS | 0 |  | 1DTR(B) | #1DTR(B) |  | A_M | [17 empty] | 1-31-10 |  | 1-3A | [5 empty] | ADCS_N | [8 empty] | 柳營DS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | D06//1DTR(B)/Tap Chan |  |  |  | CDC | 430 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D06 | 柳營DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 | [16 empty] | 1-3D-04 | 1-3D-05 | 1-6E | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1751_DS | 1751(#1DTR) DS | MTR | D06/161/1750/DS1 |  |  |  | CDC | 431 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 | [16 empty] | 1-3D-06 | 1-3D-07 | 1-6F | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1752_DS | 1752(#1DTR) DS | MTR | D06/161/1750/DS2 |  |  |  | CDC | 432 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D06 | 柳營DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB | [17 empty] | 1-08-06 |  | 1-0D | [5 empty] | 161KV_N | [8 empty] | 柳營DS.1760_CB | 1760(#2DTR) CB | MTR | D06/161/1760/CB |  |  |  | CDC | 433 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | 330 | #2DTR(330) |  | CB | [17 empty] | 1-09-04 |  | 1-20 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.330_CB | 330(#2DTR) CB | MTR | D06/11/330/CB |  |  |  | CDC | 434 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | 340 | #2DTR(340) |  | CB | [17 empty] | 1-0A-00 |  | 1-21 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.340_CB | 340(#2DTR) CB | MTR | D06/22/340/CB |  |  |  | CDC | 435 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | 2DTR | #2DTR |  | 51A | [17 empty] | 1-09-02 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.#2DTR_51A | #2DTR 51RY | MTR | D06//2DTR/PHA |  |  |  | CDC | 436 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 2DTR | #2DTR |  | 51NA | [17 empty] | 1-09-03 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.#2DTR_51NA | #2DTR 51N RY | MTR | D06//2DTR/GDA |  |  |  | CDC | 437 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 2DTR | #2DTR |  | 51ZA | [17 empty] | 1-09-01 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | D06//2DTR/51ZA |  |  |  | CDC | 438 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 2DTR | #2DTR |  | 87A | [17 empty] | 1-08-07 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.#2DTR_87A | #2DTR 87RY | MTR | D06//2DTR/87A |  |  |  | CDC | 439 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 330 | #2DTR(330) |  | 51A | [17 empty] | 1-09-05 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.330_51A | #2DTR二次側(330) 51RY | MTR |  |  |  |  | CDC | 440 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 340 | #2DTR(340) |  | 51A | [17 empty] | 1-0A-01 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.340_51A | #2DTR二次側(340) 51RY | MTR |  |  |  |  | CDC | 441 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 2DTR | #2DTR |  | 96PA | [17 empty] | 1-09-00 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | D06//2DTR/96PA |  |  |  | CDC | 442 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 2DTR | #2DTR |  | 96D | [17 empty] | 1-32-09 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.#2DTR_96D | #2DTR 96D RY | MTR | D06//2DTR/96D |  |  |  | CDC | 443 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 2DTR | #2DTR |  | 96P | [17 empty] | 1-32-10 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.#2DTR_96P | #2DTR 96P RY | MTR | D06//2DTR/96P |  |  |  | CDC | 444 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 2DTR | #2DTR |  | 63Q | [17 empty] | 1-32-11 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.#2DTR_63Q | #2DTR 63Q RY | MTR | D06//2DTR/63Q |  |  |  | CDC | 445 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 2DTR | #2DTR |  | 96B1 | [17 empty] | 1-32-07 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | D06//2DTR/96B1 |  |  |  | CDC | 446 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 2DTR | #2DTR |  | 96B2 | [17 empty] | 1-32-08 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | D06//2DTR/96B2 |  |  |  | CDC | 447 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 2DTR | #2DTR |  | TRA | [17 empty] | 1-32-13 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.#2DTR_TRA | #2DTR 重故障 | MTR | D06//2DTR/TRA |  |  |  | CDC | 448 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 2DTR | #2DTR |  | TRF | [17 empty] | 1-32-12 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.#2DTR_TRF | #2DTR 輕故障 | MTR | D06//2DTR/TRF |  |  |  | CDC | 449 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 2DTR(A) | #2DTR(A) |  | SupLocal | [17 empty] | 1-32-03 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | D06//2DTR(A)/SupLocal |  |  |  | CDC | 450 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D06 | 柳營DS | 0 |  | 2DTR(A) | #2DTR(A) |  | A_M | [17 empty] | 1-32-04 |  | 1-3C | [5 empty] | ADCS_N | [8 empty] | 柳營DS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | D06//2DTR(A)/Tap Chan |  |  |  | CDC | 451 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D06 | 柳營DS | 0 |  | 2DTR(B) | #2DTR(B) |  | SupLocal | [17 empty] | 1-32-05 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | D06//2DTR(B)/SupLocal |  |  |  | CDC | 452 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D06 | 柳營DS | 0 |  | 2DTR(B) | #2DTR(B) |  | A_M | [17 empty] | 1-32-06 |  | 1-3E | [5 empty] | ADCS_N | [8 empty] | 柳營DS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | D06//2DTR(B)/Tap Chan |  |  |  | CDC | 453 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D06 | 柳營DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 | [16 empty] | 1-3D-08 | 1-3D-09 | 1-70 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1761_DS | 1761(#2DTR) DS | MTR | D06/161/1760/DS1 |  |  |  | CDC | 454 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D06 | 柳營DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 | [16 empty] | 1-3D-10 | 1-3D-11 | 1-71 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1762_DS | 1762(#2DTR) DS | MTR | D06/161/1760/DS2 |  |  |  | CDC | 455 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-11-07 |  | 1-11 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.210_CB | 210(11KV #1SC) CB | SC | D06/11/210/CB |  |  |  | CDC | 456 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-12-00 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.210_SCA | 11KV #1SC 51,51N RY | SC | D06/11/210/SCA |  |  |  | CDC | 457 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-12-01 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | D06/11/210/UVA |  |  |  | CDC | 458 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | 210 | #1SC(210) |  | LBS | [17 empty] | 1-3E-04 | 1-3E-05 | 1-76 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.210_LBS | 210(11KV #1SC) LBS | SC | D06/11/210/LBS |  |  |  | CDC | 459 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 22 | 22kV | 220 | #2SC(220) |  | CB | [17 empty] | 1-14-04 |  | 1-19 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.220_CB | 220(23KV #2SC) CB | SC | D06/22/220/CB |  |  |  | CDC | 460 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | 220 | #2SC(220) |  | SCA | [17 empty] | 1-14-05 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.220_SCA | 23KV #2SC 51,51N RY | SC | D06/22/220/SCA |  |  |  | CDC | 461 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | 220 | #2SC(220) |  | UVA | [17 empty] | 1-14-06 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.220_UVA | 23KV #2SC 27RY(欠壓) | SC | D06/22/220/UVA |  |  |  | CDC | 462 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | 230 | #3SC(230) |  | CB | [17 empty] | 2-11-07 |  | 2-01 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.230_CB | 230(11KV #3SC) CB | SC | D06/11/230/CB |  |  |  | CDC | 463 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 11 | 11kV | 230 | #3SC(230) |  | SCA | [17 empty] | 2-12-00 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.230_SCA | 11KV #3SC 51,51N RY | SC | D06/11/230/SCA |  |  |  | CDC | 464 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | 230 | #3SC(230) |  | UVA | [17 empty] | 2-12-01 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | D06/11/230/UVA |  |  |  | CDC | 465 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | 230 | #3SC(230) |  | LBS | [17 empty] | 1-3E-08 | 1-3E-09 | 1-78 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.230_LBS | 230(11KV #3SC) LBS | SC | D06/11/230/LBS |  |  |  | CDC | 466 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 22 | 22kV | 240 | #4SC(240) |  | CB | [17 empty] | 2-14-04 |  | 2-09 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.240_CB | 240(23KV #4SC) CB | SC | D06/22/240/CB |  |  |  | CDC | 467 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | 240 | #4SC(240) |  | SCA | [17 empty] | 2-14-05 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.240_SCA | 23KV #4SC 51,51N RY | SC | D06/22/240/SCA |  |  |  | CDC | 468 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | 240 | #4SC(240) |  | UVA | [17 empty] | 2-14-06 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.240_UVA | 23KV #4SC 27RY(欠壓) | SC | D06/22/240/UVA |  |  |  | CDC | 469 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1611BUS | #1BUS |  | VUA | [17 empty] | 1-35-09 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | D06/161/1BUS/BUS_VUA |  |  |  | CDC | 470 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1611BUS | #1BUS |  | 87A | [17 empty] | 1-06-03 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | D06/161/1BUS/87A |  |  |  | CDC | 471 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1611BUS | #1BUS |  | 87UL | [17 empty] | 2-35-01 |  | 1-7C | [5 empty] | ADCS_N | [8 empty] | 柳營DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | D06/161/1BUS/87UL |  |  |  | CDC | 472 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 161 | 161kV | 1612BUS | #2BUS |  | VUA | [17 empty] | 1-35-10 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | D06/161/2BUS/BUS_VUA |  |  |  | CDC | 473 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1612BUS | #2BUS |  | 87A | [17 empty] | 1-06-04 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | D06/161/2BUS/87A |  |  |  | CDC | 474 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1612BUS | #2BUS |  | 87UL | [17 empty] | 2-35-02 |  | 1-7D | [5 empty] | ADCS_N | [8 empty] | 柳營DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | D06/161/2BUS/87UL |  |  |  | CDC | 475 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 22 | 22kV | 11_ | 11/ |  | CBA | [17 empty] | 1-36-01 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | D06/22/ComPoint/CBA |  |  |  | CDC | 476 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | 11_ | 11/ |  | CBF | [17 empty] | 1-36-02 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | D06/22/ComPoint/CBF |  |  |  | CDC | 477 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | _SC | 23/ SC |  | 60A | [17 empty] | 1-35-14 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.11KV_SC_60A | 23/11KV SC 60A | OTHER | D06/22/ComPoint/60A |  |  |  | CDC | 478 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV |  |  |  | CBA | [17 empty] | 1-35-05 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.161KV_CBA | 161KV斷路器重故障 | OTHER | D06/161/ComPoint/CBA |  |  |  | CDC | 479 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV |  |  |  | CBF | [17 empty] | 1-35-06 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | D06/161/ComPoint/CBF |  |  |  | CDC | 480 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | LINE | LINE |  | RCA | [17 empty] | 1-06-05 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | D06/161/ComPoint/RCA |  |  |  | CDC | 481 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV |  |  |  | COMT | [17 empty] | 1-35-13 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.161空壓機COMT | 161KV空壓機運轉超時警報 | OTHER | D06/0/ComPoint/COMT |  |  |  | CDC | 482 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.RTU_S/L | RTU SUPY/LOCAL | OTHER | D06/0/RTU/RTU_R_L |  |  |  | CDC | 483 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D06 | 柳營DS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.TEST_CB | TEST CB | OTHER | D06/0/RTU/Test_CB |  |  |  | CDC | 484 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  |  |  |  | Fire1 | [17 empty] | 1-34-02 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | D06/0/StaDev/Fire1 |  |  |  | CDC | 485 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  |  |  |  | Fire2 | [17 empty] | 1-34-03 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.火災警報(2) | 火災警報(2) | OTHER | D06/0/StaDev/Fire2 |  |  |  | CDC | 486 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  |  |  |  | Fire3 | [17 empty] | 1-34-04 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.火災警報(3) | 火災警報(3) | OTHER | D06/0/StaDev/Fire3 |  |  |  | CDC | 487 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  |  |  |  | Fire4 | [17 empty] | 1-34-05 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.火災警報(4) | 火災警報(4) | OTHER | D06/0/StaDev/Fire4 |  |  |  | CDC | 488 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  |  |  |  | OPA | [17 empty] | 1-35-01 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | D06/0/ComPoint/OPA |  |  |  | CDC | 489 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  |  |  |  | 25PFA | [17 empty] | 2-1D-05 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER | D06/0/ComPoint/25PFA |  |  |  | CDC | 490 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  |  |  |  | 25TA | [17 empty] | 2-1D-04 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | D06/0/ComPoint/25TA |  |  |  | CDC | 491 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  |  |  |  | SUBA | [17 empty] | 1-36-00 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.其他重故障 | 變電所內其他重故障 | OTHER | D06/0/StaDev/PSA |  |  |  | CDC | 492 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  |  |  |  | SUBF | [17 empty] | 1-35-15 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.其他輕故障 | 變電所內其他輕故障 | OTHER | D06/0/StaDev/PSF |  |  |  | CDC | 493 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  |  |  |  | ACB1 | [17 empty] | 1-34-14 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | D06/0/StaDev/ACB1 |  |  |  | CDC | 494 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
D06 | 柳營DS | 0 |  |  |  |  | ACB2 | [17 empty] | 1-34-15 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | D06/0/StaDev/ACB2 |  |  |  | CDC | 495 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
D06 | 柳營DS | 0 |  |  |  |  | ACBA | [17 empty] | 1-35-08 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.所內電源ACBA | 所內電源故障警報 | OTHER | D06/0/StaDev/ACBA |  |  |  | CDC | 496 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 所內電源開關ACB | 所內電源開關ACB |  | ACBT | [17 empty] | 1-35-00 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | D06/0/StaDev/ACBT |  |  |  | CDC | 497 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D06 | 柳營DS | 0 |  |  |  |  | STUV | [17 empty] | 1-35-02 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | D06/0/StaDev/STUV |  |  |  | CDC | 498 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-35-11 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | D06/0/StaDev/CHG1 |  |  |  | CDC | 499 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  |  |  |  | DCA | [17 empty] | 1-35-07 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.直流電源DCA | 直流電源故障警報 | OTHER | D06/0/StaDev/DCA |  |  |  | CDC | 500 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  |  |  |  | DCE | [17 empty] | 1-35-12 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.直流電源DCE | 直流電源接地故障警報 | OTHER | D06/0/StaDev/DCE |  |  |  | CDC | 501 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-36-06 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | D06/0/StaDev/CHG2 |  |  |  | CDC | 502 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  |  |  |  | CommACF | [17 empty] | 1-36-07 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | D06/0/StaDev/CommACF |  |  |  | CDC | 503 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  |  |  |  | Door1 | [17 empty] | 1-34-07 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.無人化門禁(1) | 無人化門禁(1)建築物大門 | OTHER | D06/0/StaDev/Door1 |  |  |  | CDC | 504 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  |  |  |  | Door2 | [17 empty] | 1-34-08 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.無人化門禁(2) | 無人化門禁(2)控制室大門 | OTHER | D06/0/StaDev/Door2 |  |  |  | CDC | 505 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  |  |  |  | Lights1 | [17 empty] | 1-34-12 |  | 1-7A | [5 empty] | ADCS_N | [8 empty] | 柳營DS.開關場照明(A) | 開關場照明(A) | OTHER |  |  |  |  | CDC | 506 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D06 | 柳營DS | 0 |  |  |  |  | Lights2 | [17 empty] | 1-34-13 |  | 1-7B | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.開關場照明(B) | 路燈照明 | OTHER | D06/0/StaDev/DD_Light |  |  |  | CDC | 507 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D06 | 柳營DS | 0 |  | 1500TIE | 1500 |  | 50SA | [17 empty] | 2-35-03 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | D06/161/1500/50SA |  |  |  | CDC | 508 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | TEST/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 1550 | 嘉民柳營山線(1550) |  | DTTA | [17 empty] | 1-02-06 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.1550_DTTA | 嘉民柳營山線(1550)遠方遙跳 | OTHER | D06/161/1550/DTTA |  |  |  | CDC | 509 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 1560 | 嘉民柳營海線(1560) |  | DTTA | [17 empty] | 1-03-03 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.1560_DTTA | 嘉民柳營海線(1560)遠方遙跳 | OTHER | D06/161/1560/DTTA |  |  |  | CDC | 510 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | _OSCA | _OSCA |  | 1 | [17 empty] | 1-06-06 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.161KV_OSCA_1 | 161KV示波器啟動警報(1) | OTHER | D06/161/ComPoint/OSCA |  |  |  | CDC | 511 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | _OSCA | _OSCA | [19 empty] | 1-06-07 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.161KV_OSCA_2 | 161KV示波器啟動警報(2) | OTHER |  |  |  |  | CDC | 512 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 310 | #1DTR(310) |  | GDA | [17 empty] | 1-08-01 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.310_GDA | 310開關箱IED RY GDA | OTHER | D06/11/310/GDA |  |  |  | CDC | 513 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 310 | #1DTR(310) |  | PHA2 | [17 empty] | 1-08-00 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.310_PHA2 | 310開關箱IED RY PHA | OTHER | D06/11/310/PHA |  |  |  | CDC | 514 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 320 | #1DTR(320) |  | GDA | [17 empty] | 1-08-05 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.320_GDA | 320開關箱IED RY GDA | OTHER | D06/22/320/GDA |  |  |  | CDC | 515 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 320 | #1DTR(320) |  | PHA2 | [17 empty] | 1-08-04 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.320_PHA2 | 320開關箱IED RY PHA | OTHER | D06/22/320/PHA |  |  |  | CDC | 516 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 330 | #2DTR(330) |  | GDA | [17 empty] | 1-09-07 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.330_GDA | 330開關箱IED RY GDA | OTHER | D06/11/330/GDA |  |  |  | CDC | 517 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 330 | #2DTR(330) |  | PHA2 | [17 empty] | 1-09-06 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.330_PHA2 | 330開關箱IED RY PHA | OTHER | D06/11/330/PHA |  |  |  | CDC | 518 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 340 | #2DTR(340) |  | GDA | [17 empty] | 1-0A-03 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.340_GDA | 340開關箱IED RY GDA | OTHER | D06/22/340/GDA |  |  |  | CDC | 519 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 340 | #2DTR(340) |  | PHA2 | [17 empty] | 1-0A-02 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.340_PHA2 | 340開關箱IED RY PHA | OTHER | D06/22/340/PHA |  |  |  | CDC | 520 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 0 |  |  |  |  | 水位警報(1) | [17 empty] | 1-35-03 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.水位警報(1) | 地下室水位警報(1) | OTHER | D06/0/StaDev/Water1 |  |  |  | CDC | 521 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  |  |  |  | 水位警報(2) | [17 empty] | 1-35-04 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.水位警報(2) | 地下室水位警報(2) | OTHER | D06/0/StaDev/Water2 |  |  |  | CDC | 522 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  |  |  |  | 火災警報(5) | [17 empty] | 1-34-06 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.火災警報(5) | 火災警報(5) | OTHER | D06/0/StaDev/Fire5 |  |  |  | CDC | 523 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  |  |  |  | 空調機故障 | [17 empty] | 1-37-15 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.空調機故障 | 空調機故障或電源跳脫 | OTHER | D06/0/StaDev/AIRCON |  |  |  | CDC | 524 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | NORMAL/FAULT | NORMAL
D06 | 柳營DS | 0 |  |  |  |  | OilLeak1 | [17 empty] | 1-36-04 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.洩油池警報(1) | 洩油池水位警報(1) | OTHER | D06/0/StaDev/OilLeak1 |  |  |  | CDC | 525 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  |  |  |  | OilLeak2 | [17 empty] | 1-36-05 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.洩油池警報(2) | 洩油池水位警報(2) | OTHER | D06/0/StaDev/OilLeak2 |  |  |  | CDC | 526 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  |  |  |  | Door3 | [17 empty] | 1-34-09 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.無人化門禁(3) | 無人化門禁(3)保全警報 | OTHER | D06/0/StaDev/Door3 |  |  |  | CDC | 527 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  |  |  |  | 無人化門禁(4) | [17 empty] | 1-34-10 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.無人化門禁(4) | 無人化門禁(4)電驛室門禁警報 | OTHER | D06/0/StaDev/Door4 |  |  |  | CDC | 528 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  |  |  |  | 無人化門禁(5) | [17 empty] | 1-34-11 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.無人化門禁(5) | 無人化門禁(5) | OTHER | D06/0/NULL/Door5 |  |  |  | CDC | 529 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 161 | 161kV | 1530 | 新營柳營山線(1530) |  | 87A | [17 empty] | 1-01-03 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.1530_87A | 新營柳營山線(1530) 87RY | LINE161 | D06/161/1530/87A1 |  |  |  | CDC | 530 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1540 | 新營柳營海線(1540) |  | 87A | [17 empty] | 1-02-00 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.1540_87A | 新營柳營海線(1540) 87RY | LINE161 | D06/161/1540/87A1 |  |  |  | CDC | 531 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1550 | 嘉民柳營山線(1550) |  | 87A | [17 empty] | 1-02-05 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.1550_87A | 嘉民柳營山線(1550) 87RY | LINE161 | D06/161/1550/87A |  |  |  | CDC | 532 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1560 | 嘉民柳營海線(1560) |  | 87A | [17 empty] | 1-03-02 | [7 empty] | 161KV_N | [8 empty] | 柳營DS.1560_87A | 嘉民柳營海線(1560) 87RY | LINE161 | D06/161/1560/87A |  |  |  | CDC | 533 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 0 |  |  |  |  | 通信機房溫度 | [17 empty] | 1-36-10 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.通信機房溫度 | 通信機房溫度警報 | OTHER | D06/0/StaDev/R_Temp |  |  |  | CDC | 534 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV |  |  |  | OSCF | [17 empty] | 2-35-04 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | D06/0/ComPoint/OSCF |  |  |  | CDC | 535 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  |  |  |  | PMA | [17 empty] | 2-35-05 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.PMA | 電力量測表計故障 | OTHER | D06/0/StaDev/PMA |  |  |  | CDC | 536 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 1510 | 柳營新高紅線(1510) |  | 21CFA | [17 empty] | 1-36-11 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.1510_21CFA | 柳營新高紅線(1510)21RY通訊故障 | OTHER | D06/161/1510/87CFA |  |  |  | CDC | 537 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 1510 | 柳營新高紅線(1510) |  | RYFA | [17 empty] | 1-36-12 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.1510_RYFA | 柳營新高紅線(1510)數位電驛故障 | OTHER | D06/161/1510/RYFA |  |  |  | CDC | 538 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 1520 | 柳營新高榮特白(1520) |  | 21CFA | [17 empty] | 1-36-13 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.1520_21CFA | 柳營新高榮特白(1520)RY通訊故障 | OTHER | D06/161/1520/87CFA |  |  |  | CDC | 539 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 1520 | 柳營新高榮特白(1520) |  | RYFA | [17 empty] | 1-36-14 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.1520_RYFA | 柳營新高榮特白(1520)數位RY故障 | OTHER | D06/161/1520/RYFA |  |  |  | CDC | 540 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 1530 | 新營柳營山線(1530) |  | 87CFA | [17 empty] | 1-36-15 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.1530_87CFA | 新營柳營山線(1530)87RY通訊故障 | OTHER | D06/161/1530/87CFA |  |  |  | CDC | 541 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 1530 | 新營柳營山線(1530) |  | RYFA | [17 empty] | 1-37-00 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.1530_RYFA | 新營柳營山線(1530)數位電驛故障 | OTHER | D06/161/1530/RYFA |  |  |  | CDC | 542 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 1540 | 新營柳營海線(1540) |  | 87CFA | [17 empty] | 1-37-01 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.1540_87CFA | 新營柳營海線(1540)87RY通訊故障 | OTHER | D06/161/1540/87CFA |  |  |  | CDC | 543 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 1540 | 新營柳營海線(1540) |  | RYFA | [17 empty] | 1-37-02 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.1540_RYFA | 新營柳營海線(1540)數位電驛故障 | OTHER | D06/161/1540/RYFA |  |  |  | CDC | 544 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 1550 | 嘉民柳營山線(1550) |  | 87CFA | [17 empty] | 1-37-03 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.1550_87CFA | 嘉民柳營山線(1550)87RY通訊故障 | OTHER | D06/161/1550/87CFA |  |  |  | CDC | 545 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 1550 | 嘉民柳營山線(1550) |  | RYFA | [17 empty] | 1-37-04 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.1550_RYFA | 嘉民柳營山線(1550)數位電驛故障 | OTHER | D06/161/1550/RYFA |  |  |  | CDC | 546 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 1560 | 嘉民柳營海線(1560) |  | 87CFA | [17 empty] | 1-37-05 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.1560_87CFA | 嘉民柳營海線(1560)87RY通訊故障 | OTHER | D06/161/1560/87CFA |  |  |  | CDC | 547 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 1560 | 嘉民柳營海線(1560) |  | RYFA | [17 empty] | 1-37-06 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.1560_RYFA | 嘉民柳營海線(1560)數位電驛故障 | OTHER | D06/161/1560/RYFA |  |  |  | CDC | 548 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ51 | 柳51線(VJ51) |  | PHA | [17 empty] | 1-12-06 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ51_PHA | 23KV柳51線(VJ51) 相間RY | FEEDER | D06/22/VJ51/PHA |  |  |  | CDC | 549 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ51 | 柳51線(VJ51) |  | GDA | [17 empty] | 1-12-07 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ51_GDA | 23KV柳51線(VJ51) 接地RY | FEEDER | D06/22/VJ51/GDA |  |  |  | CDC | 550 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ51 | 柳51線(VJ51) 79RY |  | 79UL | [17 empty] | 2-30-10 |  | 2-2E | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ51_79UL | 23KV柳51線(VJ51) 79RY U/L | FEEDER | D06/22/VJ51/79UL |  |  |  | CDC | 551 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 22 | 22kV | VJ51_LCO | 柳51線(VJ51) LCO |  | TapPosMv | [17 empty] | 2-30-11 |  | 2-2F | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ51_LCO_TAP | 23KV柳51線(VJ51) LCO TAP | FEEDER | D06/22/VJ51/ADJ |  |  |  | CDC | 552 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D06 | 柳營DS | 22 | 22kV | VJ51 | VJ51(23KV柳51線) |  | CB | [17 empty] | 1-12-05 |  | 1-1A | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ51_CB | VJ51(23KV柳51線) CB | FEEDER | D06/22/VJ51/CB |  |  |  | CDC | 553 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | VJ52 | 柳52線(VJ52) |  | PHA | [17 empty] | 1-13-01 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ52_PHA | 23KV柳52線(VJ52) 相間RY | FEEDER | D06/22/VJ52/PHA |  |  |  | CDC | 554 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ52 | 柳52線(VJ52) |  | GDA | [17 empty] | 1-13-02 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ52_GDA | 23KV柳52線(VJ52) 接地RY | FEEDER | D06/22/VJ52/GDA |  |  |  | CDC | 555 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ52 | 柳52線(VJ52) 79RY |  | 79UL | [17 empty] | 2-30-12 |  | 2-30 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ52_79UL | 23KV柳52線(VJ52) 79RY U/L | FEEDER | D06/22/VJ52/79UL |  |  |  | CDC | 556 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 22 | 22kV | VJ52_LCO | 柳52線(VJ52) LCO |  | TapPosMv | [17 empty] | 2-30-13 |  | 2-31 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ52_LCO_TAP | 23KV柳52線(VJ52) LCO TAP | FEEDER | D06/22/VJ52/ADJ |  |  |  | CDC | 557 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D06 | 柳營DS | 22 | 22kV | VJ52 | VJ52(23KV柳52線) |  | CB | [17 empty] | 1-13-00 |  | 1-1B | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ52_CB | VJ52(23KV柳52線) CB | FEEDER | D06/22/VJ52/CB |  |  |  | CDC | 558 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | VJ53 | 柳53線(VJ53) |  | PHA | [17 empty] | 1-13-04 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ53_PHA | 23KV柳53線(VJ53) 相間RY | FEEDER | D06/22/VJ53/PHA |  |  |  | CDC | 559 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ53 | 柳53線(VJ53) |  | GDA | [17 empty] | 1-13-05 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ53_GDA | 23KV柳53線(VJ53) 接地RY | FEEDER | D06/22/VJ53/GDA |  |  |  | CDC | 560 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ53 | 柳53線(VJ53) 79RY |  | 79UL | [17 empty] | 2-30-14 |  | 2-32 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ53_79UL | 23KV柳53線(VJ53) 79RY U/L | FEEDER | D06/22/VJ53/79UL |  |  |  | CDC | 561 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 22 | 22kV | VJ53_LCO | 柳53線(VJ53) LCO |  | TapPosMv | [17 empty] | 2-30-15 |  | 2-33 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ53_LCO_TAP | 23KV柳53線(VJ53) LCO TAP | FEEDER | D06/22/VJ53/ADJ |  |  |  | CDC | 562 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D06 | 柳營DS | 22 | 22kV | VJ53 | VJ53(23KV柳53線) |  | CB | [17 empty] | 1-13-03 |  | 1-1C | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ53_CB | VJ53(23KV柳53線) CB | FEEDER | D06/22/VJ53/CB |  |  |  | CDC | 563 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | VJ54 | 柳54線(VJ54) |  | PHA | [17 empty] | 1-13-07 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ54_PHA | 23KV柳54線(VJ54) 相間RY | FEEDER | D06/22/VJ54/PHA |  |  |  | CDC | 564 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ54 | 柳54線(VJ54) |  | GDA | [17 empty] | 1-14-00 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ54_GDA | 23KV柳54線(VJ54) 接地RY | FEEDER | D06/22/VJ54/GDA |  |  |  | CDC | 565 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ54 | 柳54線(VJ54) 79RY |  | 79UL | [17 empty] | 2-31-00 |  | 2-34 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ54_79UL | 23KV柳54線(VJ54) 79RY U/L | FEEDER | D06/22/VJ54/79UL |  |  |  | CDC | 566 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 22 | 22kV | VJ54_LCO | 柳54線(VJ54) LCO |  | TapPosMv | [17 empty] | 2-31-01 |  | 2-35 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ54_LCO_TAP | 23KV柳54線(VJ54) LCO TAP | FEEDER | D06/22/VJ54/ADJ |  |  |  | CDC | 567 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D06 | 柳營DS | 22 | 22kV | VJ54 | VJ54(23KV柳54線) |  | CB | [17 empty] | 1-13-06 |  | 1-1D | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ54_CB | VJ54(23KV柳54線) CB | FEEDER | D06/22/VJ54/CB |  |  |  | CDC | 568 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | VJ55 | 柳55線(VJ55) |  | PHA | [17 empty] | 1-14-02 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ55_PHA | 23KV柳55線(VJ55) 相間RY | FEEDER | D06/22/VJ55/PHA |  |  |  | CDC | 569 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ55 | 柳55線(VJ55) |  | GDA | [17 empty] | 1-14-03 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ55_GDA | 23KV柳55線(VJ55) 接地RY | FEEDER | D06/22/VJ55/GDA |  |  |  | CDC | 570 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ55 | 柳55線(VJ55) 79RY |  | 79UL | [17 empty] | 2-31-02 |  | 2-36 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ55_79UL | 23KV柳55線(VJ55) 79RY U/L | FEEDER | D06/22/VJ55/79UL |  |  |  | CDC | 571 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 22 | 22kV | VJ55_LCO | 柳55線(VJ55) LCO |  | TapPosMv | [17 empty] | 2-31-03 |  | 2-37 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ55_LCO_TAP | 23KV柳55線(VJ55) LCO TAP | FEEDER | D06/22/VJ55/ADJ |  |  |  | CDC | 572 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D06 | 柳營DS | 22 | 22kV | VJ55 | VJ55(23KV柳55線) |  | CB | [17 empty] | 1-14-01 |  | 1-1E | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ55_CB | VJ55(23KV柳55線) CB | FEEDER | D06/22/VJ55/CB |  |  |  | CDC | 573 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | VJ56 | 柳56線(VJ56) |  | PHA | [17 empty] | 2-12-06 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ56_PHA | 23KV柳56線(VJ56) 相間RY | FEEDER | D06/22/VJ56/PHA |  |  |  | CDC | 574 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ56 | 柳56線(VJ56) |  | GDA | [17 empty] | 2-12-07 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ56_GDA | 23KV柳56線(VJ56) 接地RY | FEEDER | D06/22/VJ56/GDA |  |  |  | CDC | 575 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ56 | 柳56線(VJ56) 79RY |  | 79UL | [17 empty] | 2-31-14 |  | 2-42 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ56_79UL | 23KV柳56線(VJ56) 79RY U/L | FEEDER | D06/22/VJ56/79UL |  |  |  | CDC | 576 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 22 | 22kV | VJ56_LCO | 柳56線(VJ56) LCO |  | TapPosMv | [17 empty] | 2-31-15 |  | 2-43 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ56_LCO_TAP | 23KV柳56線(VJ56) LCO TAP | FEEDER | D06/22/VJ56/ADJ |  |  |  | CDC | 577 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D06 | 柳營DS | 22 | 22kV | VJ56 | VJ56(23KV柳56線) |  | CB | [17 empty] | 2-12-05 |  | 2-0A | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ56_CB | VJ56(23KV柳56線) CB | FEEDER | D06/22/VJ56/CB |  |  |  | CDC | 578 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | VJ57 | 柳57線(VJ57) |  | PHA | [17 empty] | 2-13-01 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ57_PHA | 23KV柳57線(VJ57) 相間RY | FEEDER | D06/22/VJ57/PHA |  |  |  | CDC | 579 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ57 | 柳57線(VJ57) |  | GDA | [17 empty] | 2-13-02 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ57_GDA | 23KV柳57線(VJ57) 接地RY | FEEDER | D06/22/VJ57/GDA |  |  |  | CDC | 580 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ57 | 柳57線(VJ57) 79RY |  | 79UL | [17 empty] | 2-32-00 |  | 2-44 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ57_79UL | 23KV柳57線(VJ57) 79RY U/L | FEEDER | D06/22/VJ57/79UL |  |  |  | CDC | 581 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 22 | 22kV | VJ57_LCO | 柳57線(VJ57) LCO |  | TapPosMv | [17 empty] | 2-32-01 |  | 2-45 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ57_LCO_TAP | 23KV柳57線(VJ57) LCO TAP | FEEDER | D06/22/VJ57/ADJ |  |  |  | CDC | 582 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D06 | 柳營DS | 22 | 22kV | VJ57 | VJ57(23KV柳57線) |  | CB | [17 empty] | 2-13-00 |  | 2-0B | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ57_CB | VJ57(23KV柳57線) CB | FEEDER | D06/22/VJ57/CB |  |  |  | CDC | 583 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | VJ58 | 柳58線(VJ58) |  | PHA | [17 empty] | 2-13-04 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ58_PHA | 23KV柳58線(VJ58) 相間RY | FEEDER | D06/22/VJ58/PHA |  |  |  | CDC | 584 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ58 | 柳58線(VJ58) |  | GDA | [17 empty] | 2-13-05 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ58_GDA | 23KV柳58線(VJ58) 接地RY | FEEDER | D06/22/VJ58/GDA |  |  |  | CDC | 585 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ58 | 柳58線(VJ58) 79RY |  | 79UL | [17 empty] | 2-32-02 |  | 2-46 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ58_79UL | 23KV柳58線(VJ58) 79RY U/L | FEEDER | D06/22/VJ58/79UL |  |  |  | CDC | 586 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 22 | 22kV | VJ58_LCO | 柳58線(VJ58) LCO |  | TapPosMv | [17 empty] | 2-32-03 |  | 2-47 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ58_LCO_TAP | 23KV柳58線(VJ58) LCO TAP | FEEDER | D06/22/VJ58/ADJ |  |  |  | CDC | 587 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D06 | 柳營DS | 22 | 22kV | VJ58 | VJ58(23KV柳58線) |  | CB | [17 empty] | 2-13-03 |  | 2-0C | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ58_CB | VJ58(23KV柳58線) CB | FEEDER | D06/22/VJ58/CB |  |  |  | CDC | 588 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | VJ59 | 柳59線(VJ59) |  | PHA | [17 empty] | 2-13-07 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ59_PHA | 23KV柳59線(VJ59) 相間RY | FEEDER | D06/22/VJ59/PHA |  |  |  | CDC | 589 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ59 | 柳59線(VJ59) |  | GDA | [17 empty] | 2-14-00 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ59_GDA | 23KV柳59線(VJ59) 接地RY | FEEDER | D06/22/VJ59/GDA |  |  |  | CDC | 590 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ59 | 柳59線(VJ59) 79RY |  | 79UL | [17 empty] | 2-32-04 |  | 2-48 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ59_79UL | 23KV柳59線(VJ59) 79RY U/L | FEEDER | D06/22/VJ59/79UL |  |  |  | CDC | 591 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 22 | 22kV | VJ59_LCO | 柳59線(VJ59) LCO |  | TapPosMv | [17 empty] | 2-32-05 |  | 2-49 | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ59_LCO_TAP | 23KV柳59線(VJ59) LCO TAP | FEEDER | D06/22/VJ59/ADJ |  |  |  | CDC | 592 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D06 | 柳營DS | 22 | 22kV | VJ59 | VJ59(23KV柳59線) |  | CB | [17 empty] | 2-13-06 |  | 2-0D | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ59_CB | VJ59(23KV柳59線) CB | FEEDER | D06/22/VJ59/CB |  |  |  | CDC | 593 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | VJ60 | 柳60線(VJ60) |  | PHA | [17 empty] | 2-14-02 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ60_PHA | 23KV柳60線(VJ60) 相間RY | FEEDER | D06/22/VJ60/PHA |  |  |  | CDC | 594 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ60 | 柳60線(VJ60) |  | GDA | [17 empty] | 2-14-03 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ60_GDA | 23KV柳60線(VJ60) 接地RY | FEEDER | D06/22/VJ60/GDA |  |  |  | CDC | 595 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 22 | 22kV | VJ60 | 柳60線(VJ60) 79RY |  | 79UL | [17 empty] | 2-32-06 |  | 2-4A | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ60_79UL | 23KV柳60線(VJ60) 79RY U/L | FEEDER | D06/22/VJ60/79UL |  |  |  | CDC | 596 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 22 | 22kV | VJ60_LCO | 柳60線(VJ60) LCO |  | TapPosMv | [17 empty] | 2-32-07 |  | 2-4B | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ60_LCO_TAP | 23KV柳60線(VJ60) LCO TAP | FEEDER | D06/22/VJ60/ADJ |  |  |  | CDC | 597 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D06 | 柳營DS | 22 | 22kV | VJ60 | VJ60(23KV柳60線) |  | CB | [17 empty] | 2-14-01 |  | 2-0E | [5 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ60_CB | VJ60(23KV柳60線) CB | FEEDER | D06/22/VJ60/CB |  |  |  | CDC | 598 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 22 | 22kV | 11_ | 11/ |  | LOA | [17 empty] | 1-36-03 | [7 empty] | DDCS3_1 | [8 empty] | 柳營DS.11/23KV_LOA | 11/23KV饋線復閉失敗閉鎖 | OTHER | D06/22/ComPoint/LOA |  |  |  | CDC | 599 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | 81RY | 81RY |  | A/S(1) | [17 empty] | 2-1D-06 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.81RY_A/S(1) | 310低頻電驛動作/復歸 | OTHER | D06/11/310/81AS |  |  |  | CDC | 600 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
D06 | 柳營DS | 0 |  | 81RY | 81RY |  | A/S(2) | [17 empty] | 2-1D-07 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.81RY_A/S(2) | 320低頻電驛動作/復歸 | OTHER | D06/22/320/81AS |  |  |  | CDC | 601 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
D06 | 柳營DS | 0 |  | 81RY | 81RY |  | A/S(3) | [17 empty] | 2-1E-00 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.81RY_A/S(3) | 330低頻電驛動作/復歸 | OTHER | D06/11/330/81AS |  |  |  | CDC | 602 | GENERICDIPoint | DS044_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
D06 | 柳營DS | 0 |  | BVS | BVS |  | RY | [17 empty] | 2-34-15 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.BVS_RY | BVS GRZ100 RY U/L | OTHER | D06/0/ComPoint/GRZ100 |  |  |  | CDC | 603 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | LOCK/USE | USE
D06 | 柳營DS | 161 | 161kV | 1SHR | #1SHR |  | 161#1SHR96PA | [17 empty] | 1-0D-05 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.161#1SHR96PA | 161KV #1SHR 機械保護動作 | OTHER | D06/161/1950/96PA |  |  |  | CDC | 604 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1611SHR | #1SHR |  | 187UL | [17 empty] | 2-35-06 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.161#1SHR_187UL | 161KV #1SHR 187RY U/L | OTHER | D06/161/1950/1_87UL1 |  |  |  | CDC | 605 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 161 | 161kV | 1611SHR | #1SHR |  | 287UL | [17 empty] | 2-35-07 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.161#1SHR_287UL | 161KV #1SHR 287RY U/L | OTHER | D06/161/1950/1_87UL2 |  |  |  | CDC | 606 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 161 | 161kV | 1611SHR | #1SHR |  | 51A | [17 empty] | 1-0D-04 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.161#1SHR_51A | 161KV #1SHR 51RY | OTHER | D06/161/1950/51A |  |  |  | CDC | 607 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1611SHR | #1SHR |  | 86A | [17 empty] | 1-0D-03 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.161#1SHR_86A | 161KV #1SHR 86RY | OTHER | D06/161/1950/1A5Other |  |  |  | CDC | 608 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1611SHR | #1SHR |  | 87A | [17 empty] | 1-0D-02 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.161#1SHR_87A | 161KV #1SHR 87RY | OTHER | D06/161/1950/87A |  |  |  | CDC | 609 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1611SHR | #1SHR |  | 96B1 | [17 empty] | 2-34-08 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.161#1SHR_96B1 | 161KV #1SHR 96B1 RY | OTHER | D06/161/1950/96B1 |  |  |  | CDC | 610 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1611SHR | #1SHR |  | 96B2 | [17 empty] | 2-34-09 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.161#1SHR_96B2 | 161KV #1SHR 96B2 RY | OTHER | D06/161/1950/96B2 |  |  |  | CDC | 611 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1611SHR | #1SHR |  | 96D | [17 empty] | 2-34-10 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.161#1SHR_96D | 161KV #1SHR 96D RY | OTHER | D06/161/1950/96D |  |  |  | CDC | 612 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1611SHR | #1SHR |  | 96P | [17 empty] | 2-34-11 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.161#1SHR_96P | 161KV #1SHR 96P RY | OTHER | D06/161/1950/96P |  |  |  | CDC | 613 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1611SHR | #1SHR |  | SHRA | [17 empty] | 2-34-13 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.161#1SHR_SRA | 161KV #1SHR 重故障 | OTHER | D06/161/1950/SHRA |  |  |  | CDC | 614 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1611SHR | #1SHR |  | SRF | [17 empty] | 2-34-12 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.161#1SHR_SRF | 161KV #1SHR 輕故障 | OTHER | D06/161/1950/SHRF |  |  |  | CDC | 615 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 161_1SHR | 161_1SHR |  | RYFA | [17 empty] | 2-34-14 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.161_1SHR_RYFA | 161KV 1SHR(1950)數位電驛故障 | OTHER | D06/161/1950/RYFA |  |  |  | CDC | 616 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1950 | #1SHR(1950) |  | CB | [17 empty] | 1-0D-01 |  | 1-09 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1950_CB | 1950(161KV #1SHR) CB | OTHER | D06/161/1950/CB |  |  |  | CDC | 617 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1950 | #1SHR(1950) |  | DS1 | 1951 | [16 empty] | 1-3C-00 | 1-3C-01 | 1-64 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1951_DS | 1951(161KV #1SHR) DS | OTHER | D06/161/1950/DS1 |  |  |  | CDC | 618 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1950 | #1SHR(1950) |  | DS2 | 1952 | [16 empty] | 1-3C-02 | 1-3C-03 | 1-65 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1952_DS | 1952(161KV #1SHR) DS | OTHER | D06/161/1950/DS2 |  |  |  | CDC | 619 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB | [17 empty] | 1-0A-04 |  | 1-0E | [5 empty] | 161KV_N | [8 empty] | 柳營DS.1770_CB | 1770(#3DTR) CB | MTR |  |  |  |  | CDC | 620 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 | [16 empty] | 1-3D-12 | 1-3D-13 | 1-72 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1771_DS | 1771(#3DTR) DS | MTR |  |  |  |  | CDC | 621 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D06 | 柳營DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 | [16 empty] | 1-3D-14 | 1-3D-15 | 1-73 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.1772_DS | 1772(#3DTR) DS | MTR |  |  |  |  | CDC | 622 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D06 | 柳營DS | 0 |  |  |  |  | GEN | [17 empty] | 2-35-09 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.GEN | 緊急發電機運轉 | OTHER | D06/0/NULL/2A5Other |  |  |  | CDC | 623 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D06 | 柳營DS | 161 | 161kV | _BUS | BUS |  | 87CTFA | [17 empty] | 2-35-11 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.161KV_BUS_CTFA | 161KV BUS CT回路故障 | OTHER | D06/161/NULL/87CTFA |  |  |  | CDC | 624 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | _BUS | BUS |  | RYFA | [17 empty] | 2-35-10 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | D06/161/ComPoint/BUS_RYFA |  |  |  | CDC | 625 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D06 | 柳營DS | 0 |  | OLTC | OLTC |  | OLTCA | [17 empty] | 2-35-12 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | D06/0/ComPoint/OLTC_A |  |  |  | CDC | 626 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1611DTR | #1DTR |  | DTR_86A | [17 empty] | 1-0E-00 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.161#1DTR_86A | 161KV #1DTR 86RY | OTHER |  |  |  |  | CDC | 627 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1612DTR | #2DTR |  | DTR_86A | [17 empty] | 1-0E-01 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.161#2DTR_86A | 161KV #2DTR 86RY | OTHER |  |  |  |  | CDC | 628 | GENERICDIPoint | DS044_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1611DTR | #1DTR |  | 187UL | [17 empty] | 1-31-06 |  | 2-6C | [5 empty] | ADCS_N | [8 empty] | 柳營DS.161#1DTR_187UL | 161KV #1DTR 187RY U/L | OTHER | D06//1DTR/87UL1 |  |  |  | CDC | 629 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 161 | 161kV | 1611DTR | #1DTR |  | 287UL | [17 empty] | 2-35-13 |  | 2-6D | [5 empty] | ADCS_N | [8 empty] | 柳營DS.161#1DTR_287UL | 161KV #1DTR 287RY U/L | OTHER |  |  |  |  | CDC | 630 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 161 | 161kV | 1611DTR | #1DTR |  | 51Z_UL | [17 empty] | 2-35-14 |  | 2-6E | [5 empty] | ADCS_N | [8 empty] | 柳營DS.161#1DTR_51ZUL | 161KV #1DTR 51ZRY U/L | OTHER |  |  |  |  | CDC | 631 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 161 | 161kV | 1612DTR | #2DTR |  | 187UL | [17 empty] | 1-32-02 |  | 2-6F | [5 empty] | ADCS_N | [8 empty] | 柳營DS.161#2DTR_187UL | 161KV #2DTR 187RY U/L | OTHER | D06//2DTR/87UL1 |  |  |  | CDC | 632 | GENERICDIPoint | DS044_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 161 | 161kV | 1612DTR | #2DTR |  | 287UL | [17 empty] | 2-36-00 |  | 2-70 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.161#2DTR_287UL | 161KV #2DTR 287RY U/L | OTHER |  |  |  |  | CDC | 633 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 161 | 161kV | 1612DTR | #2DTR |  | 51Z_UL | [17 empty] | 2-36-01 |  | 2-71 | [5 empty] | ADCS_N | [8 empty] | 柳營DS.161#2DTR_51ZUL | 161KV #2DTR 51ZRY U/L | OTHER |  |  |  |  | CDC | 634 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D06 | 柳營DS | 161 | 161kV | 1611DTR | #1DTR |  | RYFA | [17 empty] | 2-35-15 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.161#1DTR_RYFA | 161KV #1DTR RYFA | OTHER |  |  |  |  | CDC | 635 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 161 | 161kV | 1612DTR | #2DTR |  | RYFA | [17 empty] | 2-36-02 | [7 empty] | ADCS_N | [8 empty] | 柳營DS.161#2DTR_RYFA | 161KV #2DTR RYFA | OTHER |  |  |  |  | CDC | 636 | GENERICDIPoint | DS044_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D06 | 柳營DS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 柳營DS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 637 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 22 | 22kV | 220_SC | #2SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 柳營DS.220_SC_CAP | 23KV#2SC 容量 | SC | [5 empty] | 638 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 11 | 11kV | 230_SC | #3SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 柳營DS.230_SC_CAP | 11KV#3SC 容量 | SC | [5 empty] | 639 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 22 | 22kV | 240_SC | #4SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 柳營DS.240_SC_CAP | 23KV#4SC 容量 | SC | [5 empty] | 640 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D06 | 柳營DS | 0 |  | TRD | 柳營DS |  | 169 | [25 empty] | TRAIN_AD | [8 empty] | 柳營DS.TRD_169 | 柳營DS NT #1ADTR 11KV_Hi_Limit | [6 empty] | 641 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D06 | 柳營DS | 0 |  | TRD | 柳營DS |  | 170 | [25 empty] | TRAIN_AD | [8 empty] | 柳營DS.TRD_170 | 柳營DS NT #1ADTR 11KV_Lo_Limit | [6 empty] | 642 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D06 | 柳營DS | 0 |  | TRD | 柳營DS |  | 171 | [25 empty] | TRAIN_AD | [8 empty] | 柳營DS.TRD_171 | 柳營DS NT #1BDTR 11KV_Hi_Limit | [6 empty] | 643 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D06 | 柳營DS | 0 |  | TRD | 柳營DS |  | 172 | [25 empty] | TRAIN_AD | [8 empty] | 柳營DS.TRD_172 | 柳營DS NT #1BDTR 11KV_Lo_Limit | [6 empty] | 644 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D06 | 柳營DS | 0 |  | TRD | 柳營DS |  | 173 | [25 empty] | TRAIN_AD | [8 empty] | 柳營DS.TRD_173 | 柳營DS NT #2ADTR 11KV_Hi_Limit | [6 empty] | 645 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D06 | 柳營DS | 0 |  | TRD | 柳營DS |  | 174 | [25 empty] | TRAIN_AD | [8 empty] | 柳營DS.TRD_174 | 柳營DS NT #2ADTR 11KV_Lo_Limit | [6 empty] | 646 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D06 | 柳營DS | 0 |  | TRD | 柳營DS |  | 175 | [25 empty] | TRAIN_AD | [8 empty] | 柳營DS.TRD_175 | 柳營DS NT #2BDTR 11KV_Hi_Limit | [6 empty] | 647 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D06 | 柳營DS | 0 |  | TRD | 柳營DS |  | 176 | [25 empty] | TRAIN_AD | [8 empty] | 柳營DS.TRD_176 | 柳營DS NT #2BDTR 11KV_Lo_Limit | [6 empty] | 648 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D06 | 柳營DS | 161 | 161kV | 1510 | 柳營新高紅線(1510) |  | LE0 | 1510LE | [24 empty] | ADCS_N | [8 empty] | 柳營DS.1510LE | 1510LE (非取樣點) | LINE161 | D06/161/1510/LE0 |  |  |  |  | 649 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1510 | 柳營新高紅線(1510) |  | BE0 | 1510BE | [24 empty] | ADCS_N | [8 empty] | 柳營DS.1510BE | 1510BE (非取樣點) | LINE161 | D06/161/1510/BE0 |  |  |  |  | 650 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1520 | 柳營新高榮特白(1520) |  | LE0 | 1520LE | [24 empty] | ADCS_N | [8 empty] | 柳營DS.1520LE | 1520LE (非取樣點) | LINE161 | D06/161/1520/LE0 |  |  |  |  | 651 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1520 | 柳營新高榮特白(1520) |  | BE0 | 1520BE | [24 empty] | ADCS_N | [8 empty] | 柳營DS.1520BE | 1520BE (非取樣點) | LINE161 | D06/161/1520/BE0 |  |  |  |  | 652 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1530 | 新營柳營山線(1530) |  | LE0 | 1530LE | [24 empty] | ADCS_N | [8 empty] | 柳營DS.1530LE | 1530LE (非取樣點) | LINE161 | D06/161/1530/LE0 |  |  |  |  | 653 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1530 | 新營柳營山線(1530) |  | BE0 | 1530BE | [24 empty] | ADCS_N | [8 empty] | 柳營DS.1530BE | 1530BE (非取樣點) | LINE161 | D06/161/1530/BE0 |  |  |  |  | 654 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1540 | 新營柳營海線(1540) |  | LE0 | 1540LE | [24 empty] | ADCS_N | [8 empty] | 柳營DS.1540LE | 1540LE (非取樣點) | LINE161 | D06/161/1540/LE0 |  |  |  |  | 655 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1540 | 新營柳營海線(1540) |  | BE0 | 1540BE | [24 empty] | ADCS_N | [8 empty] | 柳營DS.1540BE | 1540BE (非取樣點) | LINE161 | D06/161/1540/BE0 |  |  |  |  | 656 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1550 | 嘉民柳營山線(1550) |  | LE0 | 1550LE | [24 empty] | ADCS_N | [8 empty] | 柳營DS.1550LE | 1550LE (非取樣點) | LINE161 | D06/161/1550/LE0 |  |  |  |  | 657 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1550 | 嘉民柳營山線(1550) |  | BE0 | 1550BE | [24 empty] | ADCS_N | [8 empty] | 柳營DS.1550BE | 1550BE (非取樣點) | LINE161 | D06/161/1550/BE0 |  |  |  |  | 658 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1560 | 嘉民柳營海線(1560) |  | LE0 | 1560LE | [24 empty] | ADCS_N | [8 empty] | 柳營DS.1560LE | 1560LE (非取樣點) | LINE161 | D06/161/1560/LE0 |  |  |  |  | 659 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1560 | 嘉民柳營海線(1560) |  | BE0 | 1560BE | [24 empty] | ADCS_N | [8 empty] | 柳營DS.1560BE | 1560BE (非取樣點) | LINE161 | D06/161/1560/BE0 |  |  |  |  | 660 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | VJ21 | VJ21_DS |  | DS1 | VJ21_DS | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ21_DS | VJ21_DS (非取樣點) | FEEDER | D06/11/VJ21/DS |  |  |  |  | 661 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | VJ21 | VJ21_ES |  | LE0 | VJ21_ES | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ21_ES | VJ21_ES (非取樣點) | FEEDER | D06/11/VJ21/ES |  |  |  |  | 662 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | VJ22 | VJ22_DS |  | DS1 | VJ22_DS | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ22_DS | VJ22_DS (非取樣點) | FEEDER | D06/11/VJ22/DS |  |  |  |  | 663 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | VJ22 | VJ22_ES |  | LE0 | VJ22_ES | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ22_ES | VJ22_ES (非取樣點) | FEEDER | D06/11/VJ22/ES |  |  |  |  | 664 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | VJ23 | VJ23_DS |  | DS1 | VJ23_DS | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ23_DS | VJ23_DS (非取樣點) | FEEDER | D06/11/VJ23/DS |  |  |  |  | 665 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | VJ23 | VJ23_ES |  | LE0 | VJ23_ES | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ23_ES | VJ23_ES (非取樣點) | FEEDER | D06/11/VJ23/ES |  |  |  |  | 666 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | VJ24 | VJ24_DS |  | DS1 | VJ24_DS | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ24_DS | VJ24_DS (非取樣點) | FEEDER | D06/11/VJ24/DS |  |  |  |  | 667 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | VJ24 | VJ24_ES |  | LE0 | VJ24_ES | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ24_ES | VJ24_ES (非取樣點) | FEEDER | D06/11/VJ24/ES |  |  |  |  | 668 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | VJ25 | VJ25_DS |  | DS1 | VJ25_DS | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ25_DS | VJ25_DS (非取樣點) | FEEDER | D06/11/VJ25/DS |  |  |  |  | 669 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | VJ25 | VJ25_ES |  | LE0 | VJ25_ES | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ25_ES | VJ25_ES (非取樣點) | FEEDER | D06/11/VJ25/ES |  |  |  |  | 670 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | VJ31 | VJ31_DS |  | DS1 | VJ31_DS | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ31_DS | VJ31_DS (非取樣點) | FEEDER | D06/11/VJ31/DS |  |  |  |  | 671 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | VJ31 | VJ31_ES |  | LE0 | VJ31_ES | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ31_ES | VJ31_ES (非取樣點) | FEEDER | D06/11/VJ31/ES |  |  |  |  | 672 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | VJ32 | VJ32_DS |  | DS1 | VJ32_DS | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ32_DS | VJ32_DS (非取樣點) | FEEDER | D06/11/VJ32/DS |  |  |  |  | 673 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | VJ32 | VJ32_ES |  | LE0 | VJ32_ES | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ32_ES | VJ32_ES (非取樣點) | FEEDER | D06/11/VJ32/ES |  |  |  |  | 674 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | VJ33 | VJ33_DS |  | DS1 | VJ33_DS | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ33_DS | VJ33_DS (非取樣點) | FEEDER | D06/11/VJ33/DS |  |  |  |  | 675 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | VJ33 | VJ33_ES |  | LE0 | VJ33_ES | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ33_ES | VJ33_ES (非取樣點) | FEEDER | D06/11/VJ33/ES |  |  |  |  | 676 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | VJ34 | VJ34_DS |  | DS1 | VJ34_DS | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ34_DS | VJ34_DS (非取樣點) | FEEDER | D06/11/VJ34/DS |  |  |  |  | 677 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | VJ34 | VJ34_ES |  | LE0 | VJ34_ES | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ34_ES | VJ34_ES (非取樣點) | FEEDER | D06/11/VJ34/ES |  |  |  |  | 678 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | VJ35 | VJ35_DS |  | DS1 | VJ35_DS | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ35_DS | VJ35_DS (非取樣點) | FEEDER | D06/11/VJ35/DS |  |  |  |  | 679 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | VJ35 | VJ35_ES |  | LE0 | VJ35_ES | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ35_ES | VJ35_ES (非取樣點) | FEEDER | D06/11/VJ35/ES |  |  |  |  | 680 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | 101 | 101 |  | 101 | 101 | [24 empty] | ADCS_N | [8 empty] | 柳營DS.101 | 101 (非取樣點) | TIE | D06/11/100/D1 |  |  |  |  | 681 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | 102 | 102 |  | 102 | 102 | [24 empty] | ADCS_N | [8 empty] | 柳營DS.102 | 102 (非取樣點) | TIE | D06/11/100/D2 |  |  |  |  | 682 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [24 empty] | ADCS_N | [8 empty] | 柳營DS.1501E | 1501E (非取樣點) | TIE | D06/161/1500/E1 |  |  |  |  | 683 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [24 empty] | ADCS_N | [8 empty] | 柳營DS.1502E | 1502E (非取樣點) | TIE | D06/161/1500/E2 |  |  |  |  | 684 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | 201 | 201 |  | 201 | 201 | [24 empty] | ADCS_N | [8 empty] | 柳營DS.201 | 201 (非取樣點) | TIE | D06/22/200/D1 |  |  |  |  | 685 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | 202 | 202 |  | 202 | 202 | [24 empty] | ADCS_N | [8 empty] | 柳營DS.202 | 202 (非取樣點) | TIE | D06/22/200/D2 |  |  |  |  | 686 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | 391 | 391 |  | 391 | 391 | [24 empty] | ADCS_N | [8 empty] | 柳營DS.391 | 391 (非取樣點) | OTHER | D06/11/390/D1 |  |  |  |  | 687 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | 391E | 391E |  | 391E | 391E | [24 empty] | ADCS_N | [8 empty] | 柳營DS.391E | 391E (非取樣點) | OTHER | D06/11/390/E1 |  |  |  |  | 688 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | 491 | 491 |  | 491 | 491 | [24 empty] | ADCS_N | [8 empty] | 柳營DS.491 | 491 (非取樣點) | OTHER | D06/22/490/D1 |  |  |  |  | 689 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | 491E | 491E |  | 491E | 491E | [24 empty] | ADCS_N | [8 empty] | 柳營DS.491E | 491E (非取樣點) | OTHER | D06/22/490/E1 |  |  |  |  | 690 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | 1750TE | [24 empty] | ADCS_N | [8 empty] | 柳營DS.1750TE | 1750TE (非取樣點) | MTR | D06/161/1750/TE0 |  |  |  |  | 691 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | 1750BE | [24 empty] | ADCS_N | [8 empty] | 柳營DS.1750BE | 1750BE (非取樣點) | MTR | D06/161/1750/BE0 |  |  |  |  | 692 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | 311 | 311 |  | 311 | 311 | [24 empty] | ADCS_N | [8 empty] | 柳營DS.311 | 311 (非取樣點) | MTR | D06/11/310/D1 |  |  |  |  | 693 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | 310 | #1DTR(310) |  | E1 | 311E | [24 empty] | ADCS_N | [8 empty] | 柳營DS.311E | 311E (非取樣點) | MTR | D06/11/310/E1 |  |  |  |  | 694 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | 321 | 321 |  | 321 | 321 | [24 empty] | ADCS_N | [8 empty] | 柳營DS.321 | 321 (非取樣點) | MTR | D06/22/320/D1 |  |  |  |  | 695 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | 320 | #1DTR(320) |  | E1 | 321E | [24 empty] | ADCS_N | [8 empty] | 柳營DS.321E | 321E (非取樣點) | MTR | D06/22/320/E1 |  |  |  |  | 696 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | 1760TE | [24 empty] | ADCS_N | [8 empty] | 柳營DS.1760TE | 1760TE (非取樣點) | MTR | D06/161/1760/TE0 |  |  |  |  | 697 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | 1760BE | [24 empty] | ADCS_N | [8 empty] | 柳營DS.1760BE | 1760BE (非取樣點) | MTR | D06/161/1760/BE0 |  |  |  |  | 698 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | 331 | 331 |  | 331 | 331 | [24 empty] | ADCS_N | [8 empty] | 柳營DS.331 | 331 (非取樣點) | MTR | D06/11/330/D1 |  |  |  |  | 699 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | 330 | #2DTR(330) |  | E1 | 331E | [24 empty] | ADCS_N | [8 empty] | 柳營DS.331E | 331E (非取樣點) | MTR | D06/11/330/E1 |  |  |  |  | 700 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | 341 | 341 |  | 341 | 341 | [24 empty] | ADCS_N | [8 empty] | 柳營DS.341 | 341 (非取樣點) | MTR | D06/22/340/D1 |  |  |  |  | 701 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | 340 | #2DTR(340) |  | E1 | 341E | [24 empty] | ADCS_N | [8 empty] | 柳營DS.341E | 341E (非取樣點) | MTR | D06/22/340/E1 |  |  |  |  | 702 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | 211E | 211E |  | 211E | 211E | [24 empty] | ADCS_N | [8 empty] | 柳營DS.211E | 211E (非取樣點) | SC | D06/11/210/E1 |  |  |  |  | 703 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | 211 | 211 |  | 211 | 211 | [24 empty] | ADCS_N | [8 empty] | 柳營DS.211 | 211 (非取樣點) | SC | D06/11/210/D1 |  |  |  |  | 704 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | 221E | 221E |  | 221E | 221E | [24 empty] | ADCS_N | [8 empty] | 柳營DS.221E | 221E (非取樣點) | SC | D06/22/220/E1 |  |  |  |  | 705 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | 221 | 221 |  | 221 | 221 | [24 empty] | ADCS_N | [8 empty] | 柳營DS.221 | 221 (非取樣點) | SC | D06/22/220/D1 |  |  |  |  | 706 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | 231E | 231E |  | 231E | 231E | [24 empty] | ADCS_N | [8 empty] | 柳營DS.231E | 231E (非取樣點) | SC | D06/11/230/E1 |  |  |  |  | 707 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | 231 | 231 |  | 231 | 231 | [24 empty] | ADCS_N | [8 empty] | 柳營DS.231 | 231 (非取樣點) | SC | D06/11/230/D1 |  |  |  |  | 708 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | 241E | 241E |  | 241E | 241E | [24 empty] | ADCS_N | [8 empty] | 柳營DS.241E | 241E (非取樣點) | SC | D06/22/240/E1 |  |  |  |  | 709 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | 241 | 241 |  | 241 | 241 | [24 empty] | ADCS_N | [8 empty] | 柳營DS.241 | 241 (非取樣點) | SC | D06/22/240/D1 |  |  |  |  | 710 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | 15B1E | 15B1E |  | BE1 | 15B1E | [24 empty] | ADCS_N | [8 empty] | 柳營DS.15B1E | 15B1E (非取樣點) | BUS | D06/161/161B1E/BE1 |  |  |  |  | 711 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | 15B2E | 15B2E |  | BE2 | 15B2E | [24 empty] | ADCS_N | [8 empty] | 柳營DS.15B2E | 15B2E (非取樣點) | BUS | D06/161/161B2E/BE2 |  |  |  |  | 712 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | ADCS_N | [8 empty] | 柳營DS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 713 | NotelDIPoint | [38 empty] | START/STOP | STOP
D06 | 柳營DS | 0 |  |  |  |  | 101E | 101E | [24 empty] | ADCS_N | [8 empty] | 柳營DS.101E | 101E(非取樣點) | OTHER | D06/11/100/E1 |  |  |  |  | 714 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  |  |  |  | 102E | 102E | [24 empty] | ADCS_N | [8 empty] | 柳營DS.102E | 102E(非取樣點) | OTHER | D06/11/100/E2 |  |  |  |  | 715 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  |  |  |  | 201E | 201E | [24 empty] | ADCS_N | [8 empty] | 柳營DS.201E | 201E(非取樣點) | OTHER | D06/22/200/E1 |  |  |  |  | 716 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  |  |  |  | 202E | 202E | [24 empty] | ADCS_N | [8 empty] | 柳營DS.202E | 202E(非取樣點) | OTHER | D06/22/200/E2 |  |  |  |  | 717 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | VJ51 | VJ51_DS |  | DS1 | VJ51_DS | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ51_DS | VJ51_DS (非取樣點) | FEEDER | D06/22/VJ51/DS |  |  |  |  | 718 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | VJ51 | VJ51_ES |  | LE0 | VJ51_ES | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ51_ES | VJ51_ES (非取樣點) | FEEDER | D06/22/VJ51/ES |  |  |  |  | 719 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | VJ52 | VJ52_DS |  | DS1 | VJ52_DS | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ52_DS | VJ52_DS (非取樣點) | FEEDER | D06/22/VJ52/DS |  |  |  |  | 720 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | VJ52 | VJ52_ES |  | LE0 | VJ52_ES | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ52_ES | VJ52_ES (非取樣點) | FEEDER | D06/22/VJ52/ES |  |  |  |  | 721 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | VJ53 | VJ53_DS |  | DS1 | VJ53_DS | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ53_DS | VJ53_DS (非取樣點) | FEEDER | D06/22/VJ53/DS |  |  |  |  | 722 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | VJ53 | VJ53_ES |  | LE0 | VJ53_ES | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ53_ES | VJ53_ES (非取樣點) | FEEDER | D06/22/VJ53/ES |  |  |  |  | 723 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | VJ54 | VJ54_DS |  | DS1 | VJ54_DS | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ54_DS | VJ54_DS (非取樣點) | FEEDER | D06/22/VJ54/DS |  |  |  |  | 724 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | VJ54 | VJ54_ES |  | LE0 | VJ54_ES | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ54_ES | VJ54_ES (非取樣點) | FEEDER | D06/22/VJ54/ES |  |  |  |  | 725 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | VJ55 | VJ55_DS |  | DS1 | VJ55_DS | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ55_DS | VJ55_DS (非取樣點) | FEEDER | D06/22/VJ55/DS |  |  |  |  | 726 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | VJ55 | VJ55_ES |  | LE0 | VJ55_ES | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ55_ES | VJ55_ES (非取樣點) | FEEDER | D06/22/VJ55/ES |  |  |  |  | 727 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | VJ56 | VJ56_DS |  | DS1 | VJ56_DS | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ56_DS | VJ56_DS (非取樣點) | FEEDER | D06/22/VJ56/DS |  |  |  |  | 728 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | VJ56 | VJ56_ES |  | LE0 | VJ56_ES | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ56_ES | VJ56_ES (非取樣點) | FEEDER | D06/22/VJ56/ES |  |  |  |  | 729 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | VJ57 | VJ57_DS |  | DS1 | VJ57_DS | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ57_DS | VJ57_DS (非取樣點) | FEEDER | D06/22/VJ57/DS |  |  |  |  | 730 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | VJ57 | VJ57_ES |  | LE0 | VJ57_ES | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ57_ES | VJ57_ES (非取樣點) | FEEDER | D06/22/VJ57/ES |  |  |  |  | 731 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | VJ58 | VJ58_DS |  | DS1 | VJ58_DS | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ58_DS | VJ58_DS (非取樣點) | FEEDER | D06/22/VJ58/DS |  |  |  |  | 732 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | VJ58 | VJ58_ES |  | LE0 | VJ58_ES | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ58_ES | VJ58_ES (非取樣點) | FEEDER | D06/22/VJ58/ES |  |  |  |  | 733 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | VJ59 | VJ59_DS |  | DS1 | VJ59_DS | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ59_DS | VJ59_DS (非取樣點) | FEEDER | D06/22/VJ59/DS |  |  |  |  | 734 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | VJ59 | VJ59_ES |  | LE0 | VJ59_ES | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ59_ES | VJ59_ES (非取樣點) | FEEDER | D06/22/VJ59/ES |  |  |  |  | 735 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | VJ60 | VJ60_DS |  | DS1 | VJ60_DS | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ60_DS | VJ60_DS (非取樣點) | FEEDER | D06/22/VJ60/DS |  |  |  |  | 736 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | VJ60 | VJ60_ES |  | LE0 | VJ60_ES | [24 empty] | DDCS3_1 | [8 empty] | 柳營DS.VJ60_ES | VJ60_ES (非取樣點) | FEEDER | D06/22/VJ60/ES |  |  |  |  | 737 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | 1A | #1A |  | BE | #1A_BE | [24 empty] | ADCS_N | [8 empty] | 柳營DS.#1A_BE | #1A BE(非取樣點) | OTHER | [5 empty] | 738 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | 1B | #1B |  | BE | #1B_BE | [24 empty] | ADCS_N | [8 empty] | 柳營DS.#1B_BE | #1B BE(非取樣點) | OTHER | [5 empty] | 739 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | 2A | #2A |  | BE | #2A_BE | [24 empty] | ADCS_N | [8 empty] | 柳營DS.#2A_BE | #2A BE(非取樣點) | OTHER | [5 empty] | 740 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | 2B | #2B |  | BE | #2B_BE | [24 empty] | ADCS_N | [8 empty] | 柳營DS.#2B_BE | #2B BE(非取樣點) | OTHER | [5 empty] | 741 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  |  |  |  | 1950BE | 1950BE | [24 empty] | ADCS_N | [8 empty] | 柳營DS.1950BE | 1950BE(非取樣點) | OTHER | D06/161/1950/BE0 |  |  |  |  | 742 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  |  |  |  | 1950RE | 1950RE | [24 empty] | ADCS_N | [8 empty] | 柳營DS.1950RE | 1950RE(非取樣點) | OTHER | D06/161/1950/RE0 |  |  |  |  | 743 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | 1770TE | [24 empty] | ADCS_N | [8 empty] | 柳營DS.1770TE | 1770TE (非取樣點) | MTR | [5 empty] | 744 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | 1770BE | [24 empty] | ADCS_N | [8 empty] | 柳營DS.1770BE | 1770BE (非取樣點) | MTR | [5 empty] | 745 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | 1ABUS | 1ABUS |  | PTD | 1ABUS_PTD | [24 empty] | ADCS_N | [8 empty] | 柳營DS.1ABUS_PTD | #1ABUS_PTD(非取樣點) | OTHER | [5 empty] | 746 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | 1ABUS | 1ABUS |  | PTE | 1ABUS_PTE | [24 empty] | ADCS_N | [8 empty] | 柳營DS.1ABUS_PTE | #1ABUS_PTE(非取樣點) | OTHER | [5 empty] | 747 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | 1BBUS | 1BBUS |  | PTD | 1BBUS_PTD | [24 empty] | ADCS_N | [8 empty] | 柳營DS.1BBUS_PTD | #1BBUS_PTD(非取樣點) | OTHER | [5 empty] | 748 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | 1BBUS | 1BBUS |  | PTE | 1BBUS_PTE | [24 empty] | ADCS_N | [8 empty] | 柳營DS.1BBUS_PTE | #1BBUS_PTE(非取樣點) | OTHER | [5 empty] | 749 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | 2ABUS | 2ABUS |  | PTD | 2ABUS_PTD | [24 empty] | ADCS_N | [8 empty] | 柳營DS.2ABUS_PTD | #2ABUS_PTD(非取樣點) | OTHER | [5 empty] | 750 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | 2ABUS | 2ABUS |  | PTE | 2ABUS_PTE | [24 empty] | ADCS_N | [8 empty] | 柳營DS.2ABUS_PTE | #2ABUS_PTE(非取樣點) | OTHER | [5 empty] | 751 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D06 | 柳營DS | 0 |  | 2BBUS | 2BBUS |  | PTD | 2BBUS_PTD | [24 empty] | ADCS_N | [8 empty] | 柳營DS.2BBUS_PTD | #2BBUS_PTD(非取樣點) | OTHER | [5 empty] | 752 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D06 | 柳營DS | 0 |  | 2BBUS | 2BBUS |  | PTE | 2BBUS_PTE | [24 empty] | ADCS_N | [8 empty] | 柳營DS.2BBUS_PTE | #2BBUS_PTE(非取樣點) | OTHER | [5 empty] | 753 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo