## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D07 | 太鐵DS | 161 | 161kV | 1510 | 太鐵～槺榔一路(1510) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_A1 | [8 empty] | 太鐵DS.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 2 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1510 | 太鐵～槺榔一路(1510) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_A1 | [8 empty] | 太鐵DS.1510BE | 1510BE (非取樣點) | LINE161 | [5 empty] | 3 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1520 | 太鐵～槺榔二路(1520) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_A1 | [8 empty] | 太鐵DS.1520LE | 1520LE (非取樣點) | LINE161 | [5 empty] | 4 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1520 | 太鐵～槺榔二路(1520) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_A1 | [8 empty] | 太鐵DS.1520BE | 1520BE (非取樣點) | LINE161 | [5 empty] | 5 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_A1 | [8 empty] | 太鐵DS.1530LE | 1530LE (非取樣點) | LINE161 | [5 empty] | 6 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_A1 | [8 empty] | 太鐵DS.1530BE | 1530BE (非取樣點) | LINE161 | [5 empty] | 7 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_A1 | [8 empty] | 太鐵DS.1540LE | 1540LE (非取樣點) | LINE161 | [5 empty] | 8 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_A1 | [8 empty] | 太鐵DS.1540BE | 1540BE (非取樣點) | LINE161 | [5 empty] | 9 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1550 | 後壁太鐵一路(1550) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_A1 | [8 empty] | 太鐵DS.1550LE | 1550LE (非取樣點) | LINE161 | [5 empty] | 10 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1550 | 後壁太鐵一路(1550) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_A1 | [8 empty] | 太鐵DS.1550BE | 1550BE (非取樣點) | LINE161 | [5 empty] | 11 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1560 | 後壁太鐵二路(1560) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_A1 | [8 empty] | 太鐵DS.1560LE | 1560LE (非取樣點) | LINE161 | [5 empty] | 12 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1560 | 後壁太鐵二路(1560) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_A1 | [8 empty] | 太鐵DS.1560BE | 1560BE (非取樣點) | LINE161 | [5 empty] | 13 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_A1 | [8 empty] | 太鐵DS.1501E | 1501E (非取樣點) | TIE | [5 empty] | 14 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_A1 | [8 empty] | 太鐵DS.1502E | 1502E (非取樣點) | TIE | [5 empty] | 15 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_A1 | [8 empty] | 太鐵DS.1750TE | 1750TE (非取樣點) | MTR | [5 empty] | 16 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_A1 | [8 empty] | 太鐵DS.1750BE | 1750BE (非取樣點) | MTR | [5 empty] | 17 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | D1 | 311(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D07_A1 | [8 empty] | 太鐵DS.311 | 311 (非取樣點) | MTR | [5 empty] | 18 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | E1 | 311E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D07_A1 | [8 empty] | 太鐵DS.311E | 311E (非取樣點) | MTR | [5 empty] | 19 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | D1 | 321(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D07_A1 | [8 empty] | 太鐵DS.321 | 321 (非取樣點) | MTR | [5 empty] | 20 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | E1 | 321E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D07_A1 | [8 empty] | 太鐵DS.321E | 321E (非取樣點) | MTR | [5 empty] | 21 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_A1 | [8 empty] | 太鐵DS.1760TE | 1760TE (非取樣點) | MTR | [5 empty] | 22 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_A1 | [8 empty] | 太鐵DS.1760BE | 1760BE (非取樣點) | MTR | [5 empty] | 23 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | D1 | 331(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D07_A1 | [8 empty] | 太鐵DS.331 | 331 (非取樣點) | MTR | [5 empty] | 24 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | E1 | 331E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D07_A1 | [8 empty] | 太鐵DS.331E | 331E (非取樣點) | MTR | [5 empty] | 25 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | D1 | 341(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D07_A1 | [8 empty] | 太鐵DS.341 | 341 (非取樣點) | MTR | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | E1 | 341E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D07_A1 | [8 empty] | 太鐵DS.341E | 341E (非取樣點) | MTR | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1950 | #1SHR(1950) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_A1 | [8 empty] | 太鐵DS.1950BE | 1950BE(非取樣點) | OTHER | [5 empty] | 28 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1950 | #1SHR(1950) |  | RE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_A1 | [8 empty] | 太鐵DS.1950RE | 1950RE(非取樣點) | OTHER | [5 empty] | 29 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 11 | 11kV | JV21 | 鐵21(JV21) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV21_DS | JV21_DS (非取樣點) | FEEDER | [5 empty] | 30 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | JV21 | 鐵21(JV21) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV21_ES | JV21_ES (非取樣點) | FEEDER | [5 empty] | 31 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 11 | 11kV | JV22 | 鐵22(JV22) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV22_DS | JV22_DS (非取樣點) | FEEDER | [5 empty] | 32 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | JV22 | 鐵22(JV22) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV22_ES | JV22_ES (非取樣點) | FEEDER | [5 empty] | 33 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 11 | 11kV | JV23 | 鐵23(JV23) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV23_DS | JV23_DS (非取樣點) | FEEDER | [5 empty] | 34 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | JV23 | 鐵23(JV23) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV23_ES | JV23_ES (非取樣點) | FEEDER | [5 empty] | 35 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 11 | 11kV | JV24 | 鐵24(JV24) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV24_DS | JV24_DS (非取樣點) | FEEDER | [5 empty] | 36 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | JV24 | 鐵24(JV24) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV24_ES | JV24_ES (非取樣點) | FEEDER | [5 empty] | 37 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 11 | 11kV | JV25 | 鐵25(JV25) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV25_DS | JV25_DS (非取樣點) | FEEDER | [5 empty] | 38 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | JV25 | 鐵25(JV25) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV25_ES | JV25_ES (非取樣點) | FEEDER | [5 empty] | 39 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 11 | 11kV | 210 | #1SC(210) |  | E1 | 211E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D07_A1 | [8 empty] | 太鐵DS.211E | 211E (非取樣點) | SC | [5 empty] | 40 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 11 | 11kV | 210 | #1SC(210) |  | D1 | 211(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D07_A1 | [8 empty] | 太鐵DS.211 | 211 (非取樣點) | SC | [5 empty] | 41 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | 390 | #1SSTR(390) |  | D1 | 391(非取樣點) | B3 | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D07_A1 | [8 empty] | 太鐵DS.391 | 391 (非取樣點) | OTHER | [5 empty] | 42 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | 390 | #1SSTR(390) |  | E1 | 391E(非取樣點) | B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D07_A1 | [8 empty] | 太鐵DS.391E | 391E (非取樣點) | OTHER | [5 empty] | 43 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 22 | 22kV | JV56 | 鐵56(JV56) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV56_DS | JV56_DS (非取樣點) | FEEDER | [5 empty] | 44 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | JV56 | 鐵56(JV56) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV56_ES | JV56_ES (非取樣點) | FEEDER | [5 empty] | 45 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 22 | 22kV | JV57 | 鐵57(JV57) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV57_DS | JV57_DS (非取樣點) | FEEDER | [5 empty] | 46 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | JV57 | 鐵57(JV57) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV57_ES | JV57_ES (非取樣點) | FEEDER | [5 empty] | 47 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 22 | 22kV | JV58 | 鐵58(JV58) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV58_DS | JV58_DS (非取樣點) | FEEDER | [5 empty] | 48 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | JV58 | 鐵58(JV58) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV58_ES | JV58_ES (非取樣點) | FEEDER | [5 empty] | 49 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 22 | 22kV | JV59 | 鐵59(JV59) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV59_DS | JV59_DS (非取樣點) | FEEDER | [5 empty] | 50 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | JV59 | 鐵59(JV59) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV59_ES | JV59_ES (非取樣點) | FEEDER | [5 empty] | 51 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 22 | 22kV | JV60 | 鐵60(JV60) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV60_DS | JV60_DS (非取樣點) | FEEDER | [5 empty] | 52 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | JV60 | 鐵60(JV60) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV60_ES | JV60_ES (非取樣點) | FEEDER | [5 empty] | 53 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 22 | 22kV | 220 | #2SC(220) |  | E1 | 221E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D07_A1 | [8 empty] | 太鐵DS.221E | 221E (非取樣點) | SC | [5 empty] | 54 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 22 | 22kV | 220 | #2SC(220) |  | D1 | 221(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D07_A1 | [8 empty] | 太鐵DS.221 | 221 (非取樣點) | SC | [5 empty] | 55 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | JV31 | 鐵31(JV31) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV31_DS | JV31_DS (非取樣點) | FEEDER | [5 empty] | 56 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | JV31 | 鐵31(JV31) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV31_ES | JV31_ES (非取樣點) | FEEDER | [5 empty] | 57 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 11 | 11kV | JV32 | 鐵32(JV32) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV32_DS | JV32_DS (非取樣點) | FEEDER | [5 empty] | 58 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | JV32 | 鐵32(JV32) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV32_ES | JV32_ES (非取樣點) | FEEDER | [5 empty] | 59 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 11 | 11kV | JV33 | 鐵33(JV33) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV33_DS | JV33_DS (非取樣點) | FEEDER | [5 empty] | 60 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | JV33 | 鐵33(JV33) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV33_ES | JV33_ES (非取樣點) | FEEDER | [5 empty] | 61 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 11 | 11kV | JV34 | 鐵34(JV34) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV34_DS | JV34_DS (非取樣點) | FEEDER | [5 empty] | 62 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | JV34 | 鐵34(JV34) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV34_ES | JV34_ES (非取樣點) | FEEDER | [5 empty] | 63 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 11 | 11kV | JV35 | 鐵35(JV35) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV35_DS | JV35_DS (非取樣點) | FEEDER | [5 empty] | 64 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | JV35 | 鐵35(JV35) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV35_ES | JV35_ES (非取樣點) | FEEDER | [5 empty] | 65 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 11 | 11kV | 230 | #3SC(230) |  | E1 | 231E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D07_A1 | [8 empty] | 太鐵DS.231E | 231E (非取樣點) | SC | [5 empty] | 66 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 11 | 11kV | 230 | #3SC(230) |  | D1 | 231(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D07_A1 | [8 empty] | 太鐵DS.231 | 231 (非取樣點) | SC | [5 empty] | 67 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | 100 | TIE(100) |  | E1 | 101E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D07_A1 | [8 empty] | 太鐵DS.101E | 101E (非取樣點) | TIE | [5 empty] | 68 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 11 | 11kV | 100 | TIE(100) |  | E2 | 102E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D07_A1 | [8 empty] | 太鐵DS.102E | 102E (非取樣點) | TIE | [5 empty] | 69 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 11 | 11kV | 100 | TIE(100) |  | D1 | 101(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D07_A1 | [8 empty] | 太鐵DS.101 | 101 (非取樣點) | TIE | [5 empty] | 70 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | 100 | TIE(100) |  | D2 | 102(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D07_A1 | [8 empty] | 太鐵DS.102 | 102 (非取樣點) | TIE | [5 empty] | 71 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | JV66 | 鐵66(JV66) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV66_DS | JV66_DS (非取樣點) | FEEDER | [5 empty] | 72 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | JV66 | 鐵66(JV66) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV66_ES | JV66_ES (非取樣點) | FEEDER | [5 empty] | 73 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 22 | 22kV | JV67 | 鐵67(JV67) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV67_DS | JV67_DS (非取樣點) | FEEDER | [5 empty] | 74 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | JV67 | 鐵67(JV67) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV67_ES | JV67_ES (非取樣點) | FEEDER | [5 empty] | 75 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 22 | 22kV | JV68 | 鐵68(JV68) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV68_DS | JV68_DS (非取樣點) | FEEDER | [5 empty] | 76 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | JV68 | 鐵68(JV68) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV68_ES | JV68_ES (非取樣點) | FEEDER | [5 empty] | 77 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 22 | 22kV | JV69 | 鐵69(JV69) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV69_DS | JV69_DS (非取樣點) | FEEDER | [5 empty] | 78 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | JV69 | 鐵69(JV69) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV69_ES | JV69_ES (非取樣點) | FEEDER | [5 empty] | 79 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 22 | 22kV | JV70 | 鐵70(JV70) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV70_DS | JV70_DS (非取樣點) | FEEDER | [5 empty] | 80 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | JV70 | 鐵70(JV70) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D07_D1 | [8 empty] | 太鐵DS.JV70_ES | JV70_ES (非取樣點) | FEEDER | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 22 | 22kV | 240 | #4SC(240) |  | E1 | 241E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D07_A1 | [8 empty] | 太鐵DS.241E | 241E (非取樣點) | SC | [5 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 22 | 22kV | 240 | #4SC(240) |  | D1 | 241(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D07_A1 | [8 empty] | 太鐵DS.241 | 241 (非取樣點) | SC | [5 empty] | 83 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | 200 | TIE(200) |  | E1 | 201E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D07_A1 | [8 empty] | 太鐵DS.201E | 201E (非取樣點) | TIE | [5 empty] | 84 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 22 | 22kV | 200 | TIE(200) |  | E2 | 202E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D07_A1 | [8 empty] | 太鐵DS.202E | 202E (非取樣點) | TIE | [5 empty] | 85 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 22 | 22kV | 200 | TIE(200) |  | D1 | 201(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D07_A1 | [8 empty] | 太鐵DS.201 | 201 (非取樣點) | TIE | [5 empty] | 86 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | 200 | TIE(200) |  | D2 | 202(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D07_A1 | [8 empty] | 太鐵DS.202 | 202 (非取樣點) | TIE | [5 empty] | 87 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | 490 | #2SSTR(490) |  | D1 | 491(非取樣點) | B3 | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D07_A1 | [8 empty] | 太鐵DS.491 | 491 (非取樣點) | OTHER | [5 empty] | 88 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | 490 | #2SSTR(490) |  | E1 | 491E(非取樣點) | B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D07_A1 | [8 empty] | 太鐵DS.491E | 491E (非取樣點) | OTHER | [5 empty] | 89 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | 15B1E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aaaz | B2/D07_A1 | [8 empty] | 太鐵DS.15B1E | 15B1E (非取樣點) | BUS | [5 empty] | 90 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | 15B2E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/2Bus | [13 empty] | aaaz | B2/D07_A1 | [8 empty] | 太鐵DS.15B2E | 15B2E (非取樣點) | BUS | [5 empty] | 91 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | RTU | RTU |  | ADCL1 |  |  | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS |  |  |  |  | B3/D07_A1 | [16 empty] | 92 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D07 | 太鐵DS | 0 |  | RTU | RTU |  | ADCH1 |  |  | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS |  |  |  |  | B3/D07_A1 | [16 empty] | 93 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D07 | 太鐵DS | 161 | 161kV | 1BUS | #1BUS |  | V |  | B3 | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 161KV #1BUS 電壓 |  |  | kV_-210_210(-2000_2000) | aaa | B2/D07_A1 | [8 empty] | 太鐵DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | [5 empty] | 94 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D07 | 太鐵DS | 161 | 161kV | 2BUS | #2BUS |  | V |  | B3 | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0003 |  |  | 1-83 |  |  | 161KV #2BUS 電壓 |  |  | kV_-210_210(-2000_2000) | aab | B2/D07_A1 | [8 empty] | 太鐵DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | [5 empty] | 95 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D07 | 太鐵DS | 161 | 161kV | 1510 | 太鐵～槺榔一路(1510) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 太鐵糠榔一路1510 瓦 |  |  | MW_-560_560(-2000_2000) |  | B2/D07_A1 | [8 empty] | 太鐵DS.1510_MW | 太鐵糠榔一路 MW | LINE161 | [5 empty] | 96 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D07 | 太鐵DS | 161 | 161kV | 1510 | 太鐵～槺榔一路(1510) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 太鐵糠榔一路1510 乏 |  |  | MVAR_-560_560(-2000_2000) |  | B2/D07_A1 | [8 empty] | 太鐵DS.1510_MVAR | 太鐵糠榔一路 MVAR | LINE161 | [5 empty] | 97 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D07 | 太鐵DS | 161 | 161kV | 1520 | 太鐵～槺榔二路(1520) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 太鐵糠榔二路1520 瓦 |  |  | MW_-560_560(-2000_2000) |  | B2/D07_A1 | [8 empty] | 太鐵DS.1520_MW | 太鐵糠榔二路 MW | LINE161 | [5 empty] | 98 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D07 | 太鐵DS | 161 | 161kV | 1520 | 太鐵～槺榔二路(1520) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 太鐵糠榔二路1520 乏 |  |  | MVAR_-560_560(-2000_2000) |  | B2/D07_A1 | [8 empty] | 太鐵DS.1520_MVAR | 太鐵糠榔二路 MVAR | LINE161 | [5 empty] | 99 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D07 | 太鐵DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | 北回太鐵紅線1530 瓦 |  |  | MW_-560_560(-2000_2000) |  | B2/D07_A1 | [8 empty] | 太鐵DS.1530_MW | 北回太鐵紅線 MW | LINE161 | [5 empty] | 100 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D07 | 太鐵DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 北回太鐵紅線1530 乏 |  |  | MVAR_-560_560(-2000_2000) |  | B2/D07_A1 | [8 empty] | 太鐵DS.1530_MVAR | 北回太鐵紅線 MVAR | LINE161 | [5 empty] | 101 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D07 | 太鐵DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | 北回太鐵白線1540 瓦 |  |  | MW_-560_560(-2000_2000) |  | B2/D07_A1 | [8 empty] | 太鐵DS.1540_MW | 北回太鐵白線 MW | LINE161 | [5 empty] | 102 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D07 | 太鐵DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | 北回太鐵白線1540 乏 |  |  | MVAR_-560_560(-2000_2000) |  | B2/D07_A1 | [8 empty] | 太鐵DS.1540_MVAR | 北回太鐵白線 MVAR | LINE161 | [5 empty] | 103 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D07 | 太鐵DS | 161 | 161kV | 1550 | 後壁太鐵一路(1550) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0012 |  |  | 1-8C |  |  | 後壁太鐵一路1550 瓦 |  |  | MW_-560_560(-2000_2000) |  | B2/D07_A1 | [8 empty] | 太鐵DS.1550_MW | 後壁太鐵一路 MW | LINE161 | [5 empty] | 104 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D07 | 太鐵DS | 161 | 161kV | 1550 | 後壁太鐵一路(1550) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0013 |  |  | 1-8D |  |  | 後壁太鐵一路1550 乏 |  |  | MVAR_-560_560(-2000_2000) |  | B2/D07_A1 | [8 empty] | 太鐵DS.1550_MVAR | 後壁太鐵一路 MVAR | LINE161 | [5 empty] | 105 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D07 | 太鐵DS | 161 | 161kV | 1560 | 後壁太鐵二路(1560) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0014 |  |  | 1-8E |  |  | 後壁太鐵二路1560 瓦 |  |  | MW_-560_560(-2000_2000) |  | B2/D07_A1 | [8 empty] | 太鐵DS.1560_MW | 後壁太鐵二路 MW | LINE161 | [5 empty] | 106 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D07 | 太鐵DS | 161 | 161kV | 1560 | 後壁太鐵二路(1560) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0015 |  |  | 1-8F |  |  | 後壁太鐵二路1560 乏 |  |  | MVAR_-560_560(-2000_2000) |  | B2/D07_A1 | [8 empty] | 太鐵DS.1560_MVAR | 後壁太鐵二路 MVAR | LINE161 | [5 empty] | 107 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D07 | 太鐵DS | 0 |  | StaDev | 所內設施 |  | DCV_P |  |  | MvMoment | 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0024 |  |  | 1-98 |  |  | 直流P電源電壓 |  |  | kV_-150_150(-2000_2000) |  | B3/D07_A1 | [8 empty] | 太鐵DS.直流P電源電壓 | 直流P電源電壓 | OTHER | [5 empty] | 108 |  |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 | 0.01 | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D07 | 太鐵DS | 0 |  | StaDev | 所內設施 |  | DCV_N |  |  | MvMoment | 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | 直流N電源電壓 |  |  | kV_-150_150(-2000_2000) |  | B3/D07_A1 | [8 empty] | 太鐵DS.直流N電源電壓 | 直流N電源電壓 | OTHER | [5 empty] | 109 |  |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 | 0.01 | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D07 | 太鐵DS | 161 | 161kV | 1950 | #1SHR(1950) |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | #1 SHR 油溫 |  |  | OIL_-120_120(-2000_2000) | [10 empty] | 太鐵DS.161#1SHR_OIL | 161KV #1SHR 油溫 | OTHER | [5 empty] | 110 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D07 | 太鐵DS | 161 | 161kV | 1950 | #1SHR(1950) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0027 |  |  | 1-9B |  |  | #1 SHR 線溫 |  |  | COIL_-120_120(-2000_2000) | [10 empty] | 太鐵DS.161#1SHR_COIL | 161KV #1SHR 線溫 | OTHER | [5 empty] | 111 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D07 | 太鐵DS | 161 | 161kV | 1500 | TIE(1500) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | 161KV TIE (1500) R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/D07_A1 | [8 empty] | 太鐵DS.1500TIE_AMP | 1500TIE AMP | TIE | [5 empty] | 112 |  |  |  |  | AI | [5 empty] | C20R1600 | 1520 | 1600 | 1760 | 1968 | 2.27 | -1520 | -1600 | -1760 | -1968 | 1 | 0.01 | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS |  |  | 1DTR | #1DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | NO.1 DTR.油溫 |  |  | OIL_-120_120(-2000_2000) |  | B1/D07_A1 | [8 empty] | 太鐵DS.#1DTR_OIL | #1DTR 油溫 | MTR | [5 empty] | 113 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D07 | 太鐵DS |  |  | 1DTR(A) | #1DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | NO.1 DTRA 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/D07_A1 | [8 empty] | 太鐵DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | [5 empty] | 114 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D07 | 太鐵DS |  |  | 1DTR(B) | #1DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | NO.1 DTRB 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/D07_A1 | [8 empty] | 太鐵DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | [5 empty] | 115 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D07 | 太鐵DS |  |  | 1DTR(A) | #1DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | NO.1 DTRA TAP |  |  | TAP_-8.5_8.5(0_2000) |  | B1/D07_A1 | [8 empty] | 太鐵DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | [5 empty] | 116 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D07 | 太鐵DS |  |  | 1DTR(B) | #1DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | NO.1 DTRB TAP |  |  | TAP_-8.5_8.5(0_2000) |  | B1/D07_A1 | [8 empty] | 太鐵DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | [5 empty] | 117 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D07 | 太鐵DS |  |  | 2DTR | #2DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | NO.2 DTR.油溫 |  |  | OIL_-120_120(-2000_2000) |  | B1/D07_A1 | [8 empty] | 太鐵DS.#2DTR_OIL | #2DTR 油溫 | MTR | [5 empty] | 118 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D07 | 太鐵DS |  |  | 2DTR(A) | #2DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | NO.2 DTRA 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/D07_A1 | [8 empty] | 太鐵DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | [5 empty] | 119 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D07 | 太鐵DS |  |  | 2DTR(B) | #2DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | NO.2 DTRB 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/D07_A1 | [8 empty] | 太鐵DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | [5 empty] | 120 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D07 | 太鐵DS |  |  | 2DTR(A) | #2DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | NO.2 DTRA TAP |  |  | TAP_-8.5_8.5(0_2000) |  | B1/D07_A1 | [8 empty] | 太鐵DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | [5 empty] | 121 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D07 | 太鐵DS |  |  | 2DTR(B) | #2DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | NO.2 DTRB TAP |  |  | TAP_-8.5_8.5(0_2000) |  | B1/D07_A1 | [8 empty] | 太鐵DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | [5 empty] | 122 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D07 | 太鐵DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | NO.1 DTR-1A 310 瓦 |  |  | MW_-54_54(-2000_2000) |  | B3/D07_A1 | [8 empty] | 太鐵DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | [5 empty] | 123 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.054 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.054000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | NO.1 DTR-1A 310 乏 |  |  | MVAR_-36_36(-2000_2000) |  | B3/D07_A1 | [8 empty] | 太鐵DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | [5 empty] | 124 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.036 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.036000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | NO.1 DTR-1A 310 R相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D07_A1 | [8 empty] | 太鐵DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | [5 empty] | 125 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | NO.1 DTR-1A 310 S相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D07_A1 | [8 empty] | 太鐵DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | [5 empty] | 126 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | NO.1 DTR-1A 310 T相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D07_A1 | [8 empty] | 太鐵DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | [5 empty] | 127 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 1ABUS | #1ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0051 |  |  | 1-B3 |  |  | PT-1A R相電壓 |  |  | kV_-9_9(-2000_2000) | aaa | B3/D07_A1 | [8 empty] | 太鐵DS.11KV#1ABUS_KV | 11KV #1ABUS KV | BUS | [5 empty] | 128 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D07 | 太鐵DS | 11 | 11kV | JV21 | 鐵21(JV21) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | F1鐵21 (JV21)乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵21線KVAR | 11KV鐵21線 KVAR | FEEDER | [5 empty] | 129 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV21 | 鐵21(JV21) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | F1鐵21 (JV21) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵21線A1 | 11KV鐵21線 R相AMP | FEEDER | [5 empty] | 130 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV21 | 鐵21(JV21) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | F1鐵21 (JV21) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵21線A2 | 11KV鐵21線 S相AMP | FEEDER | [5 empty] | 131 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV21 | 鐵21(JV21) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | F1鐵21 (JV21) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵21線A3 | 11KV鐵21線 T相AMP | FEEDER | [5 empty] | 132 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV21 | 鐵21(JV21) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | F1鐵21 (JV21) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵21線A0 | 11KV鐵21線 N相AMP | FEEDER | [5 empty] | 133 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV22 | 鐵22(JV22) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | F2鐵22 (JV22)乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵22線KVAR | 11KV鐵22線 KVAR | FEEDER | [5 empty] | 134 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV22 | 鐵22(JV22) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | F2鐵22 (JV22) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵22線A1 | 11KV鐵22線 R相AMP | FEEDER | [5 empty] | 135 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV22 | 鐵22(JV22) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | F2鐵22 (JV22) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵22線A2 | 11KV鐵22線 S相AMP | FEEDER | [5 empty] | 136 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV22 | 鐵22(JV22) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0060 |  |  | 1-BC |  |  | F2鐵22 (JV22) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵22線A3 | 11KV鐵22線 T相AMP | FEEDER | [5 empty] | 137 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV22 | 鐵22(JV22) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | F2鐵22 (JV22) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵22線A0 | 11KV鐵22線 N相AMP | FEEDER | [5 empty] | 138 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV23 | 鐵23(JV23) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | F3鐵23 (JV23)乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵23線KVAR | 11KV鐵23線 KVAR | FEEDER | [5 empty] | 139 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV23 | 鐵23(JV23) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0063 |  |  | 1-BF |  |  | F3鐵23 (JV23)R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵23線A1 | 11KV鐵23線 R相AMP | FEEDER | [5 empty] | 140 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 0 |  | RTU | RTU |  | ADCL2 |  |  | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS |  |  |  |  | B3/D07_A1 | [16 empty] | 141 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D07 | 太鐵DS | 0 |  | RTU | RTU |  | ADCH2 |  |  | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS |  |  |  |  | B3/D07_A1 | [16 empty] | 142 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D07 | 太鐵DS | 11 | 11kV | JV23 | 鐵23(JV23) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | F3鐵23 (JV23) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵23線A2 | 11KV鐵23線 S相AMP | FEEDER | [5 empty] | 143 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV23 | 鐵23(JV23) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | F3鐵23 (JV23) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵23線A3 | 11KV鐵23線 T相AMP | FEEDER | [5 empty] | 144 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV23 | 鐵23(JV23) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | F3鐵23 (JV23) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵23線A0 | 11KV鐵23線 N相AMP | FEEDER | [5 empty] | 145 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV24 | 鐵24(JV24) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | F4鐵24 (JV24)乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵24線KVAR | 11KV鐵24線 KVAR | FEEDER | [5 empty] | 146 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV24 | 鐵24(JV24) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | F4鐵24 (JV24)R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵24線A1 | 11KV鐵24線 R相AMP | FEEDER | [5 empty] | 147 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV24 | 鐵24(JV24) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | F4鐵24 (JV24)S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵24線A2 | 11KV鐵24線 S相AMP | FEEDER | [5 empty] | 148 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV24 | 鐵24(JV24) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | F4鐵24 (JV24)T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵24線A3 | 11KV鐵24線 T相AMP | FEEDER | [5 empty] | 149 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV24 | 鐵24(JV24) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | F4鐵24 (JV24) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵24線A0 | 11KV鐵24線 N相AMP | FEEDER | [5 empty] | 150 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV25 | 鐵25(JV25) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | F5鐵25 (JV25)乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵25線KVAR | 11KV鐵25線 KVAR | FEEDER | [5 empty] | 151 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV25 | 鐵25(JV25) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | F5鐵25 (JV25)R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵25線A1 | 11KV鐵25線 R相AMP | FEEDER | [5 empty] | 152 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV25 | 鐵25(JV25) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | F5鐵25 (JV25) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵25線A2 | 11KV鐵25線 S相AMP | FEEDER | [5 empty] | 153 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV25 | 鐵25(JV25) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | F5鐵25 (JV25) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵25線A3 | 11KV鐵25線 T相AMP | FEEDER | [5 empty] | 154 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV25 | 鐵25(JV25) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | F5鐵25 (JV25) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵25線A0 | 11KV鐵25線 N相AMP | FEEDER | [5 empty] | 155 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | NO.1 DTR-1B 320 瓦 |  |  | MW_-108_108(-2000_2000) |  | B3/D07_A1 | [8 empty] | 太鐵DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | [5 empty] | 156 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | NO.1 DTR-1B 320 乏 |  |  | MVAR_-72_72(-2000_2000) |  | B3/D07_A1 | [8 empty] | 太鐵DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | [5 empty] | 157 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | NO.1 DTR-1B 320 R相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D07_A1 | [8 empty] | 太鐵DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | [5 empty] | 158 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | NO.1 DTR-1B 320 S相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D07_A1 | [8 empty] | 太鐵DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | [5 empty] | 159 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | NO.1 DTR-1B 320 T相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D07_A1 | [8 empty] | 太鐵DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | [5 empty] | 160 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 1BBUS | #1BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0084 |  |  | 1-D4 |  |  | PT-1B R相電壓 |  |  | kV_-18_18(-2000_2000) | baa | B3/D07_A1 | [8 empty] | 太鐵DS.23KV#1BBUS_KV | 23KV #1BBUS KV | BUS | [5 empty] | 161 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D07 | 太鐵DS | 22 | 22kV | JV56 | 鐵56(JV56) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | F6鐵56 (JV56)乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵56線KVAR | 23KV鐵56線 KVAR | FEEDER | [5 empty] | 162 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV56 | 鐵56(JV56) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | F6鐵56 (JV56)R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵56線A1 | 23KV鐵56線 R相AMP | FEEDER | [5 empty] | 163 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV56 | 鐵56(JV56) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | F6鐵56 (JV56) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵56線A2 | 23KV鐵56線 S相AMP | FEEDER | [5 empty] | 164 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV56 | 鐵56(JV56) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | F6鐵56 (JV56)T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵56線A3 | 23KV鐵56線 T相AMP | FEEDER | [5 empty] | 165 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV56 | 鐵56(JV56) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | F6鐵56 (JV56)N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵56線A0 | 23KV鐵56線 N相AMP | FEEDER | [5 empty] | 166 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV57 | 鐵57(JV57) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | F7鐵57 (JV57)乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵57線KVAR | 23KV鐵57線 KVAR | FEEDER | [5 empty] | 167 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV57 | 鐵57(JV57) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | F7鐵57 (JV57)R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵57線A1 | 23KV鐵57線 R相AMP | FEEDER | [5 empty] | 168 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV57 | 鐵57(JV57) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | F7鐵57 (JV57)S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵57線A2 | 23KV鐵57線 S相AMP | FEEDER | [5 empty] | 169 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV57 | 鐵57(JV57) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | F7鐵57 (JV57)T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵57線A3 | 23KV鐵57線 T相AMP | FEEDER | [5 empty] | 170 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV57 | 鐵57(JV57) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | F7鐵57 (JV57)N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵57線A0 | 23KV鐵57線 N相AMP | FEEDER | [5 empty] | 171 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV58 | 鐵58(JV58) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | F8鐵58 (JV58) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵58線KVAR | 23KV鐵58線 KVAR | FEEDER | [5 empty] | 172 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV58 | 鐵58(JV58) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | F8鐵58 (JV58) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵58線A1 | 23KV鐵58線 R相AMP | FEEDER | [5 empty] | 173 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV58 | 鐵58(JV58) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | F8鐵58 (JV58) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵58線A2 | 23KV鐵58線 S相AMP | FEEDER | [5 empty] | 174 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV58 | 鐵58(JV58) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0098 |  |  | 1-E2 |  |  | F8鐵58 (JV58) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵58線A3 | 23KV鐵58線 T相AMP | FEEDER | [5 empty] | 175 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV58 | 鐵58(JV58) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | F8鐵58 (JV58) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵58線A0 | 23KV鐵58線 N相AMP | FEEDER | [5 empty] | 176 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV59 | 鐵59(JV59) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | F9鐵59 (JV59) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵59線KVAR | 23KV鐵59線 KVAR | FEEDER | [5 empty] | 177 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV59 | 鐵59(JV59) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0101 |  |  | 1-E5 |  |  | F9鐵59 (JV59)R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵59線A1 | 23KV鐵59線 R相AMP | FEEDER | [5 empty] | 178 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV59 | 鐵59(JV59) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | F9鐵59 (JV59)S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵59線A2 | 23KV鐵59線 S相AMP | FEEDER | [5 empty] | 179 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV59 | 鐵59(JV59) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | F9鐵59 (JV59)T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵59線A3 | 23KV鐵59線 T相AMP | FEEDER | [5 empty] | 180 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV59 | 鐵59(JV59) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | F9鐵59 (JV59)N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵59線A0 | 23KV鐵59線 N相AMP | FEEDER | [5 empty] | 181 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV60 | 鐵60(JV60) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | F10鐵60 (JV60) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵60線KVAR | 23KV鐵60線 KVAR | FEEDER | [5 empty] | 182 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV60 | 鐵60(JV60) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | F10鐵60 (JV60) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵60線A1 | 23KV鐵60線 R相AMP | FEEDER | [5 empty] | 183 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV60 | 鐵60(JV60) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | F10鐵60 (JV60) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵60線A2 | 23KV鐵60線 S相AMP | FEEDER | [5 empty] | 184 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV60 | 鐵60(JV60) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | F10鐵60 (JV60) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵60線A3 | 23KV鐵60線 T相AMP | FEEDER | [5 empty] | 185 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV60 | 鐵60(JV60) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | F10鐵60 (JV60) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵60線A0 | 23KV鐵60線 N相AMP | FEEDER | [5 empty] | 186 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | NO.2 DTR-2A 330 瓦 |  |  | MW_-54_54(-2000_2000) |  | B3/D07_A1 | [8 empty] | 太鐵DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | [5 empty] | 187 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.054 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.054000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | NO.2 DTR-2A 330 乏 |  |  | MVAR_-36_36(-2000_2000) |  | B3/D07_A1 | [8 empty] | 太鐵DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | [5 empty] | 188 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.036 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.036000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | NO.2 DTR-2A 330 R 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D07_A1 | [8 empty] | 太鐵DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | [5 empty] | 189 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | NO.2 DTR-2A 330 S相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D07_A1 | [8 empty] | 太鐵DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | [5 empty] | 190 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | NO.2 DTR-2A 330 T相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D07_A1 | [8 empty] | 太鐵DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | [5 empty] | 191 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 2ABUS | #2ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0115 |  |  | 1-F3 |  |  | PT-2A R相電壓 |  |  | kV_-9_9(-2000_2000) | aba | B3/D07_A1 | [8 empty] | 太鐵DS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS | [5 empty] | 192 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D07 | 太鐵DS | 11 | 11kV | JV31 | 鐵31(JV31) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | F11鐵31 (JV31) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵31線KVAR | 11KV鐵31線 KVAR | FEEDER | [5 empty] | 193 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV31 | 鐵31(JV31) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | F11鐵31 (JV31) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵31線A1 | 11KV鐵31線 R相AMP | FEEDER | [5 empty] | 194 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV31 | 鐵31(JV31) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | F11鐵31 (JV31) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵31線A2 | 11KV鐵31線 S相AMP | FEEDER | [5 empty] | 195 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV31 | 鐵31(JV31) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | F11鐵31 (JV31) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵31線A3 | 11KV鐵31線 T相AMP | FEEDER | [5 empty] | 196 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV31 | 鐵31(JV31) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | F11鐵31 (JV31) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵31線A0 | 11KV鐵31線 N相AMP | FEEDER | [5 empty] | 197 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV32 | 鐵32(JV32) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | F12鐵32 (JV32) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵32線KVAR | 11KV鐵32線 KVAR | FEEDER | [5 empty] | 198 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV32 | 鐵32(JV32) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | F12鐵32 (JV32) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵32線A1 | 11KV鐵32線 R相AMP | FEEDER | [5 empty] | 199 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV32 | 鐵32(JV32) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | F12鐵32 (JV32) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵32線A2 | 11KV鐵32線 S相AMP | FEEDER | [5 empty] | 200 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV32 | 鐵32(JV32) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | F12鐵32 (JV32) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵32線A3 | 11KV鐵32線 T相AMP | FEEDER | [5 empty] | 201 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV32 | 鐵32(JV32) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | F12鐵32 (JV32) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵32線A0 | 11KV鐵32線 N相AMP | FEEDER | [5 empty] | 202 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV33 | 鐵33(JV33) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | F13鐵33 (JV33) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵33線KVAR | 11KV鐵33線 KVAR | FEEDER | [5 empty] | 203 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV33 | 鐵33(JV33) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | F13鐵33 (JV33) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵33線A1 | 11KV鐵33線 R相AMP | FEEDER | [5 empty] | 204 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 0 |  | RTU | RTU |  | ADCL3 |  |  | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS |  |  |  |  | B3/D07_A1 | [16 empty] | 205 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D07 | 太鐵DS | 0 |  | RTU | RTU |  | ADCH3 |  |  | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS |  |  |  |  | B3/D07_A1 | [16 empty] | 206 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D07 | 太鐵DS | 11 | 11kV | JV33 | 鐵33(JV33) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | F13鐵33 (JV33) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵33線A2 | 11KV鐵33線 S相AMP | FEEDER | [5 empty] | 207 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV33 | 鐵33(JV33) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | F13鐵33 (JV33) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵33線A3 | 11KV鐵33線 T相AMP | FEEDER | [5 empty] | 208 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV33 | 鐵33(JV33) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | F13鐵33 (JV33) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵33線A0 | 11KV鐵33線 N相AMP | FEEDER | [5 empty] | 209 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV34 | 鐵34(JV34) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0133 |  |  | 2-85 |  |  | F14鐵33 (JV34) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵34線KVAR | 11KV鐵34線 KVAR | FEEDER | [5 empty] | 210 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV34 | 鐵34(JV34) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | F14鐵33 (JV34) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵34線A1 | 11KV鐵34線 R相AMP | FEEDER | [5 empty] | 211 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV34 | 鐵34(JV34) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0135 |  |  | 2-87 |  |  | F14鐵33 (JV34) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵34線A2 | 11KV鐵34線 S相AMP | FEEDER | [5 empty] | 212 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV34 | 鐵34(JV34) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0136 |  |  | 2-88 |  |  | F14鐵33 (JV34) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵34線A3 | 11KV鐵34線 T相AMP | FEEDER | [5 empty] | 213 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV34 | 鐵34(JV34) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0137 |  |  | 2-89 |  |  | F14鐵33 (JV34) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵34線A0 | 11KV鐵34線 N相AMP | FEEDER | [5 empty] | 214 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV35 | 鐵35(JV35) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0138 |  |  | 2-8A |  |  | F15鐵35 (JV35) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵35線KVAR | 11KV鐵35線 KVAR | FEEDER | [5 empty] | 215 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV35 | 鐵35(JV35) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0139 |  |  | 2-8B |  |  | F15鐵35 (JV35) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵35線A1 | 11KV鐵35線 R相AMP | FEEDER | [5 empty] | 216 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV35 | 鐵35(JV35) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0140 |  |  | 2-8C |  |  | F15鐵35 (JV35) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵35線A2 | 11KV鐵35線 S相AMP | FEEDER | [5 empty] | 217 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV35 | 鐵35(JV35) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0141 |  |  | 2-8D |  |  | F15鐵35 (JV35) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵35線A3 | 11KV鐵35線 T相AMP | FEEDER | [5 empty] | 218 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | JV35 | 鐵35(JV35) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0142 |  |  | 2-8E |  |  | F15鐵35 (JV35) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵35線A0 | 11KV鐵35線 N相AMP | FEEDER | [5 empty] | 219 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 100 | TIE(100) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0143 |  |  | 2-8F |  |  | TIE-2A 100 R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B3/D07_A1 | [8 empty] | 太鐵DS.11KV_100_A1 | 11KV 100 R相AMP | TIE | [5 empty] | 220 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 100 | TIE(100) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0144 |  |  | 2-90 |  |  | TIE-2A 100 S 相電流 |  |  | A_-2000_2000(-2000_2000) |  | B3/D07_A1 | [8 empty] | 太鐵DS.11KV_100_A2 | 11KV 100 S相AMP | TIE | [5 empty] | 221 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 100 | TIE(100) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0145 |  |  | 2-91 |  |  | TIE-2A 100 T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B3/D07_A1 | [8 empty] | 太鐵DS.11KV_100_A3 | 11KV 100 T相AMP | TIE | [5 empty] | 222 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0146 |  |  | 2-92 |  |  | NO.2 DTR-2B 340 瓦 |  |  | MW_-108_108(-2000_2000) |  | B3/D07_A1 | [8 empty] | 太鐵DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | [5 empty] | 223 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0147 |  |  | 2-93 |  |  | NO.2 DTR-2B 340 乏 |  |  | MVAR_-72_72(-2000_2000) |  | B3/D07_A1 | [8 empty] | 太鐵DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | [5 empty] | 224 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0148 |  |  | 2-94 |  |  | NO.2 DTR-2B 340 R 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D07_A1 | [8 empty] | 太鐵DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | [5 empty] | 225 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0149 |  |  | 2-95 |  |  | NO.2 DTR-2B 340 330 S相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D07_A1 | [8 empty] | 太鐵DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | [5 empty] | 226 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0150 |  |  | 2-96 |  |  | NO.2 DTR-2B 340 330 T相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D07_A1 | [8 empty] | 太鐵DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | [5 empty] | 227 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 2BBUS | #2BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0151 |  |  | 2-97 |  |  | PT-2B R相電壓 |  |  | kV_-18_18(-2000_2000) | bba | B3/D07_A1 | [8 empty] | 太鐵DS.23KV#2BBUS_KV | 23KV #2BBUS KV | BUS | [5 empty] | 228 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D07 | 太鐵DS | 22 | 22kV | JV66 | 鐵66(JV66) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0152 |  |  | 2-98 |  |  | F16鐵66 (JV66)乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵66線KVAR | 23KV鐵66線 KVAR | FEEDER | [5 empty] | 229 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV66 | 鐵66(JV66) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0153 |  |  | 2-99 |  |  | F16鐵66 (JV66)R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵66線A1 | 23KV鐵66線 R相AMP | FEEDER | [5 empty] | 230 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV66 | 鐵66(JV66) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0154 |  |  | 2-9A |  |  | F16鐵66 (JV66)S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵66線A2 | 23KV鐵66線 S相AMP | FEEDER | [5 empty] | 231 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV66 | 鐵66(JV66) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0155 |  |  | 2-9B |  |  | F16鐵66 (JV66) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵66線A3 | 23KV鐵66線 T相AMP | FEEDER | [5 empty] | 232 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV66 | 鐵66(JV66) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0156 |  |  | 2-9C |  |  | F16鐵66 (JV66)N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵66線A0 | 23KV鐵66線 N相AMP | FEEDER | [5 empty] | 233 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV67 | 鐵67(JV67) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0157 |  |  | 2-9D |  |  | F17鐵67 (JV67) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵67線KVAR | 23KV鐵67線 KVAR | FEEDER | [5 empty] | 234 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV67 | 鐵67(JV67) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0158 |  |  | 2-9E |  |  | F17鐵67 (JV67) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵67線A1 | 23KV鐵67線 R相AMP | FEEDER | [5 empty] | 235 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV67 | 鐵67(JV67) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0159 |  |  | 2-9F |  |  | F17鐵67 (JV67) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵67線A2 | 23KV鐵67線 S相AMP | FEEDER | [5 empty] | 236 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV67 | 鐵67(JV67) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0160 |  |  | 2-A0 |  |  | F17鐵67 (JV67) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵67線A3 | 23KV鐵67線 T相AMP | FEEDER | [5 empty] | 237 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV67 | 鐵67(JV67) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0161 |  |  | 2-A1 |  |  | F17鐵67 (JV67) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵67線A0 | 23KV鐵67線 N相AMP | FEEDER | [5 empty] | 238 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV68 | 鐵68(JV68) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0162 |  |  | 2-A2 |  |  | F18鐵68 (JV68) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵68線KVAR | 23KV鐵68線 KVAR | FEEDER | [5 empty] | 239 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV68 | 鐵68(JV68) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0163 |  |  | 2-A3 |  |  | F18鐵68 (JV68) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵68線A1 | 23KV鐵68線 R相AMP | FEEDER | [5 empty] | 240 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV68 | 鐵68(JV68) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0164 |  |  | 2-A4 |  |  | F18鐵68 (JV68) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵68線A2 | 23KV鐵68線 S相AMP | FEEDER | [5 empty] | 241 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV68 | 鐵68(JV68) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0165 |  |  | 2-A5 |  |  | F18鐵68 (JV68) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵68線A3 | 23KV鐵68線 T相AMP | FEEDER | [5 empty] | 242 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV68 | 鐵68(JV68) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0166 |  |  | 2-A6 |  |  | F18鐵68 (JV68) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵68線A0 | 23KV鐵68線 N相AMP | FEEDER | [5 empty] | 243 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV69 | 鐵69(JV69) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0167 |  |  | 2-A7 |  |  | F19鐵69 (JV69)乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵69線KVAR | 23KV鐵69線 KVAR | FEEDER | [5 empty] | 244 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV69 | 鐵69(JV69) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0168 |  |  | 2-A8 |  |  | F19鐵69 (JV69)R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵69線A1 | 23KV鐵69線 R相AMP | FEEDER | [5 empty] | 245 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV69 | 鐵69(JV69) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0169 |  |  | 2-A9 |  |  | F19鐵69 (JV69)S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵69線A2 | 23KV鐵69線 S相AMP | FEEDER | [5 empty] | 246 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV69 | 鐵69(JV69) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0170 |  |  | 2-AA |  |  | F19鐵69 (JV69)T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵69線A3 | 23KV鐵69線 T相AMP | FEEDER | [5 empty] | 247 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV69 | 鐵69(JV69) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0171 |  |  | 2-AB |  |  | F19鐵69 (JV69)N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵69線A0 | 23KV鐵69線 N相AMP | FEEDER | [5 empty] | 248 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV70 | 鐵70(JV70) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0172 |  |  | 2-AC |  |  | F20鐵70 (JV70) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵70線KVAR | 23KV鐵70線 KVAR | FEEDER | [5 empty] | 249 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV70 | 鐵70(JV70) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0173 |  |  | 2-AD |  |  | F20鐵70 (JV70) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵70線A1 | 23KV鐵70線 R相AMP | FEEDER | [5 empty] | 250 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV70 | 鐵70(JV70) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0174 |  |  | 2-AE |  |  | F20鐵70 (JV70) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵70線A2 | 23KV鐵70線 S相AMP | FEEDER | [5 empty] | 251 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV70 | 鐵70(JV70) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0175 |  |  | 2-AF |  |  | F20鐵70 (JV70) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵70線A3 | 23KV鐵70線 T相AMP | FEEDER | [5 empty] | 252 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | JV70 | 鐵70(JV70) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0176 |  |  | 2-B0 |  |  | F20鐵70 (JV70) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D07_D1 | [8 empty] | 太鐵DS.鐵70線A0 | 23KV鐵70線 N相AMP | FEEDER | [5 empty] | 253 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 200 | TIE(200) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0177 |  |  | 2-B1 |  |  | TIE-2B R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B3/D07_A1 | [8 empty] | 太鐵DS.23KV_200_A1 | 23KV 200 R相AMP | TIE | [5 empty] | 254 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 200 | TIE(200) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0178 |  |  | 2-B2 |  |  | TIE-2B S 相電流 |  |  | A_-2000_2000(-2000_2000) |  | B3/D07_A1 | [8 empty] | 太鐵DS.23KV_200_A2 | 23KV 200 S相AMP | TIE | [5 empty] | 255 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 200 | TIE(200) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0179 |  |  | 2-B3 |  |  | TIE-2B T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B3/D07_A1 | [8 empty] | 太鐵DS.23KV_200_A3 | 23KV 200 T相AMP | TIE | [5 empty] | 256 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 0 |  | RTU | RTU |  | ADCL4 |  |  | MvMoment | No4 AI參考點 10% |  | Y |  | AI | [6 empty] | 0192 |  |  | 2-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS |  |  |  |  | B3/D07_A1 | [16 empty] | 257 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D07 | 太鐵DS | 0 |  | RTU | RTU |  | ADCH4 |  |  | MvMoment | No4 AI參考點 90% |  | Y |  | AI | [6 empty] | 0193 |  |  | 2-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS |  |  |  |  | B3/D07_A1 | [16 empty] | 258 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D07 | 太鐵DS | 0 |  | RTU | RTU |  | ADCL5 |  |  | MvMoment | No5 AI參考點 10% |  | Y |  | AI | [6 empty] | 0256 |  |  | 3-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS |  | SP |  |  | B3/D07_A1 | [16 empty] | 259 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D07 | 太鐵DS | 0 |  | RTU | RTU |  | ADCH5 |  |  | MvMoment | No5 AI參考點 90% |  | Y |  | AI | [6 empty] | 0257 |  |  | 3-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS |  | SP |  |  | B3/D07_A1 | [16 empty] | 260 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D07 | 太鐵DS | 161 | 161kV | 1510 | 太鐵～槺榔一路(1510) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D07D191/T1 |  | 0000 |  |  | 1-00-00 |  |  | L1 | ON/OFF | L1(太鐵糠榔一路1510) CB 52AS |  | aaca | B2/D07_A1 | [8 empty] | 太鐵DS.1510_CB | 1510(太鐵糠榔一路) CB | LINE161 | [5 empty] | 261 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1510 | 太鐵～槺榔一路(1510) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0001 |  |  | 1-00-01 |  |  | L1 | 87A | L1(太鐵糠榔一路1510) RY 87A |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1510_87A | 太鐵糠榔一路(1510) 87RY | LINE161 | [5 empty] | 262 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1510 | 太鐵～槺榔一路(1510) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0002 |  |  | 1-00-02 |  |  | L1 | PHA | L1(太鐵糠榔一路1510) RY PHA |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1510_PHA | 太鐵糠榔一路(1510) 相間RY | LINE161 | [5 empty] | 263 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1510 | 太鐵～槺榔一路(1510) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | L1 | GDA | L1(太鐵糠榔一路1510) RY GDA |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1510_GDA | 太鐵糠榔一路(1510) 接地RY | LINE161 | [5 empty] | 264 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1520 | 太鐵～槺榔二路(1520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D07D192/T1 |  | 0004 |  |  | 1-00-04 |  |  | L2 | ON/OFF | L2(太鐵糠榔二路1520) CB 52AS |  | aada | B2/D07_A1 | [8 empty] | 太鐵DS.1520_CB | 1520(太鐵糠榔二路) CB | LINE161 | [5 empty] | 265 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1520 | 太鐵～槺榔二路(1520) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0005 |  |  | 1-00-05 |  |  | L2 | 87A | L2(太鐵糠榔二路1520) RY 87A |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1520_87A | 太鐵糠榔二路(1520) 87RY | LINE161 | [5 empty] | 266 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1520 | 太鐵～槺榔二路(1520) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | L2 | PHA | L2(太鐵糠榔二路1520) RY PHA |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1520_PHA | 太鐵糠榔二路(1520) 相間RY | LINE161 | [5 empty] | 267 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1520 | 太鐵～槺榔二路(1520) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-07 |  |  | L2 | GDA | L2(太鐵糠榔二路1520) RY GDA |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1520_GDA | 太鐵糠榔二路(1520) 接地RY | LINE161 | [5 empty] | 268 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D14D07R/T2 |  | 0008 |  |  | 1-01-00 |  |  | L3 | ON/OFF | L3(北回太鐵紅線1530) CB 52AS |  | aaga | B2/D07_A1 | [8 empty] | 太鐵DS.1530_CB | 1530(北回太鐵紅線) CB | LINE161 | [5 empty] | 269 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | L3 | 87A | L3(北回太鐵紅線1530) RY 87A |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1530_87A | 北回太鐵紅線(1530) 87RY | LINE161 | [5 empty] | 270 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0010 |  |  | 1-01-02 |  |  | L3 | PHA | L3(北回太鐵紅線1530) RY PHA |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1530_PHA | 北回太鐵紅線(1530) 相間RY | LINE161 | [5 empty] | 271 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-03 |  |  | L3 | GDA | L3(北回太鐵紅線1530) RY GDA |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1530_GDA | 北回太鐵紅線(1530) 接地RY | LINE161 | [5 empty] | 272 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D14D07W/T2 |  | 0012 |  |  | 1-01-04 |  |  | L4 | ON/OFF | L4(北回太鐵白線1540) CB 52AS |  | aaha | B2/D07_A1 | [8 empty] | 太鐵DS.1540_CB | 1540(北回太鐵白線) CB | LINE161 | [5 empty] | 273 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0013 |  |  | 1-01-05 |  |  | L4 | 87A | L4(北回太鐵白線1540) RY 87A |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1540_87A | 北回太鐵白線(1540) 87RY | LINE161 | [5 empty] | 274 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-06 |  |  | L4 | PHA | L4(北回太鐵白線1540) RY PHA |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1540_PHA | 北回太鐵白線(1540) 相間RY | LINE161 | [5 empty] | 275 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0015 |  |  | 1-01-07 |  |  | L4 | GDA | L4(北回太鐵白線1540) RY GDA |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1540_GDA | 北回太鐵白線(1540) 接地RY | LINE161 | [5 empty] | 276 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1550 | 後壁太鐵一路(1550) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/備用線/T2 |  | 0016 |  |  | 1-02-00 |  |  | L5 | ON/OFF | L5(後壁太鐵一路1550) CB 52AS |  | aaia | B2/D07_A1 | [8 empty] | 太鐵DS.1550_CB | 1550(後壁太鐵一路) CB | LINE161 | [5 empty] | 277 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1550 | 後壁太鐵一路(1550) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0017 |  |  | 1-02-01 |  |  | L5 | 87A | L5(後壁太鐵一路1550) RY 87A |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1550_87A | 後壁太鐵一路(1550) 87RY | LINE161 | [5 empty] | 278 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1550 | 後壁太鐵一路(1550) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 |  |  | 1-02-02 |  |  | L5 | PHA | L5(後壁太鐵一路1550) RY PHA |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1550_PHA | 後壁太鐵一路(1550) 相間RY | LINE161 | [5 empty] | 279 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1550 | 後壁太鐵一路(1550) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0019 |  |  | 1-02-03 |  |  | L5 | GDA | L5(後壁太鐵一路1550) RY GDA |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1550_GDA | 後壁太鐵一路(1550) 接地RY | LINE161 | [5 empty] | 280 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1560 | 後壁太鐵二路(1560) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/備用線/T2 |  | 0020 |  |  | 1-02-04 |  |  | L6 | ON/OFF | L6(後壁太鐵二路1560) CB 52AS |  | aaja | B2/D07_A1 | [8 empty] | 太鐵DS.1560_CB | 1560(後壁太鐵二路) CB | LINE161 | [5 empty] | 281 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1560 | 後壁太鐵二路(1560) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-05 |  |  | L6 | 87A | L6(後壁太鐵二路1560) RY 87A |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1560_87A | 後壁太鐵二路(1560) 87RY | LINE161 | [5 empty] | 282 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1560 | 後壁太鐵二路(1560) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0022 |  |  | 1-02-06 |  |  | L6 | PHA | L6(後壁太鐵二路1560) RY PHA |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1560_PHA | 後壁太鐵二路(1560) 相間RY | LINE161 | [5 empty] | 283 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1560 | 後壁太鐵二路(1560) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0023 |  |  | 1-02-07 |  |  | L6 | GDA | L6(後壁太鐵二路1560) RY GDA |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1560_GDA | 後壁太鐵二路(1560) 接地RY | LINE161 | [5 empty] | 284 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0050 |  |  | 1-06-02 |  |  | 161KV TIE | ON/OFF | 161KV TIE(1500)CB 52AS |  | aafz | B2/D07_A1 | [8 empty] | 太鐵DS.1500_CB | 1500(TIE) CB | TIE | [5 empty] | 285 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0051 |  |  | 1-06-03 |  |  | 161KV TIE | A/N | 161KV TIE(1500)RY 50A |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1500_50A | 161KV TIE(1500) 50RY | TIE | [5 empty] | 286 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | 161KV BUS | 87B1A | 161KV #1BUS 87A |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | [5 empty] | 287 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0053 |  |  | 1-06-05 |  |  | 161KV BUS | 87B2A | 161KV #2BUS 87A |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | [5 empty] | 288 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0055 |  |  | 1-06-07 |  |  | Locate Empty | A/N | 161KV 79 RY RCA |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | [5 empty] | 289 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0056 |  |  | 1-07-00 |  |  | OSC1A | A/N | 161KV 示波器啟動警報OSC1A |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.161KV_OSCA_1 | 161KV示波器啟動警報 | OTHER | [5 empty] | 290 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/1DTR |  | 0058 |  |  | 1-07-02 |  |  | #1DTR | ON/OFF | NO.1 1750 CB 52AS |  | aabb | ELEM/D07_A1 | [8 empty] | 太鐵DS.1750_CB | 1750(#1DTR) CB | MTR | [5 empty] | 291 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS |  |  | 1DTR | #1DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0059 |  |  | 1-07-03 |  |  | #1DTR | A/N | NO.1 DTR 87A 87A |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#1DTR_87A | #1DTR 87RY | MTR | [5 empty] | 292 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS |  |  | 1DTR | #1DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0060 |  |  | 1-07-04 |  |  | #1DTR | A/N | NO.1 DTR 機械保護動作(96A) |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | [5 empty] | 293 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS |  |  | 1DTR | #1DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0061 |  |  | 1-07-05 |  |  | #1DTR | A/N | NO.1 DTR 51ZA 51ZA |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | [5 empty] | 294 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS |  |  | 1DTR | #1DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0062 |  |  | 1-07-06 |  |  | #1DTR | PHA | NO.1 DTR PHA PHA |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#1DTR_51A | #1DTR 51RY | MTR | [5 empty] | 295 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS |  |  | 1DTR | #1DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0063 |  |  | 1-07-07 |  |  | #1DTR | GDA | NO.1 DTR GDA GDA |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#1DTR_51NA | #1DTR 51N RY | MTR | [5 empty] | 296 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0064 |  |  | 1-08-00 |  |  | 310 | PHA | NO.1 DTR-1A 310 PHA (51-3φ) |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.310_51A | #1DTR二次側(310) 51RY | MTR | [5 empty] | 297 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0065 |  |  | 1-08-01 |  |  | 320 | PHA | NO.1 DTR-1B 320 PHA (51-3φ) |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.320_51A | #1DTR二次側(320) 51RY | MTR | [5 empty] | 298 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | T/1DTR(A) |  |  | 0066 |  |  | 1-08-02 |  |  | 310 | ON/OFF | NO.1 DTR-1A 310 CB 52AS |  | aaba | ELEM/D07_A1 | [8 empty] | 太鐵DS.310_CB | 310(#1DTR) CB | MTR | [5 empty] | 299 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0067 |  |  | 1-08-03 |  |  | 310 | PHA | NO.1 DTR-1A 310 PHA PHA |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.310_PHA2 | 310開關箱IED RY PHA | OTHER | [5 empty] | 300 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 |  |  | 1-08-04 |  |  | 310 | GDA | NO.1 DTR-1A 310 GDA GDA |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.310_GDA | 310開關箱IED RY GDA | OTHER | [5 empty] | 301 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | T/1DTR(B) |  |  | 0070 |  |  | 1-08-06 |  |  | 320 | ON/OFF | NO.1 DTR-1B 320 CB 52AS |  | baaa | ELEM/D07_A1 | [8 empty] | 太鐵DS.320_CB | 320(#1DTR) CB | MTR | [5 empty] | 302 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0071 |  |  | 1-08-07 |  |  | 320 | PHA | NO.1 DTR-1B 320 PHA PHA |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.320_PHA2 | 320開關箱IED RY PHA | OTHER | [5 empty] | 303 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0072 |  |  | 1-09-00 |  |  | 320 | GDA | NO.1 DTR-1B 320 GDA GDA |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.320_GDA | 320開關箱IED RY GDA | OTHER | [5 empty] | 304 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2DTR |  | 0074 |  |  | 1-09-02 |  |  | #2DTR | ON/OFF | NO.2 1760 CB 52AS |  | aaeb | ELEM/D07_A1 | [8 empty] | 太鐵DS.1760_CB | 1760(#2DTR) CB | MTR | [5 empty] | 305 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS |  |  | 2DTR | #2DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0075 |  |  | 1-09-03 |  |  | #2DTR | A/N | NO.2 DTR 87A 87A |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#2DTR_87A | #2DTR 87RY | MTR | [5 empty] | 306 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS |  |  | 2DTR | #2DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0076 |  |  | 1-09-04 |  |  | #2DTR | A/N | NO.2 DTR 機械保護動作(96A) |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | [5 empty] | 307 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS |  |  | 2DTR | #2DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0077 |  |  | 1-09-05 |  |  | #2DTR | A/N | NO.2 DTR 51ZA 51ZA |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | [5 empty] | 308 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS |  |  | 2DTR | #2DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0078 |  |  | 1-09-06 |  |  | #2DTR | PHA | NO.2 DTR PHA PHA |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#2DTR_51A | #2DTR 51RY | MTR | [5 empty] | 309 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS |  |  | 2DTR | #2DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0079 |  |  | 1-09-07 |  |  | #2DTR | GDA | NO.2 DTR GDA GDA |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#2DTR_51NA | #2DTR 51N RY | MTR | [5 empty] | 310 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0080 |  |  | 1-0A-00 |  |  | 320 | PHA | NO.2 DTR-2A 320 PHA (51-3φ) |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.330_51A | #2DTR二次側(330) 51RY | MTR | [5 empty] | 311 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0081 |  |  | 1-0A-01 |  |  | 330 | PHA | NO.2 DTR-2B 330 PHA (51-3φ) |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.340_51A | #2DTR二次側(340) 51RY | MTR | [5 empty] | 312 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | T/2DTR(A) |  |  | 0082 |  |  | 1-0A-02 |  |  | 320 | ON/OFF | NO.2 DTR-2A 320 CB 52AS |  | abba | ELEM/D07_A1 | [8 empty] | 太鐵DS.330_CB | 330(#2DTR) CB | MTR | [5 empty] | 313 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0083 |  |  | 1-0A-03 |  |  | 320 | PHA | NO.2 DTR-2A 320 PHA PHA |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.330_PHA2 | 330開關箱IED RY PHA | OTHER | [5 empty] | 314 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0084 |  |  | 1-0A-04 |  |  | 320 | GDA | NO.2 DTR-2A 320 GDA GDA |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.330_GDA | 330開關箱IED RY GDA | OTHER | [5 empty] | 315 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | T/2DTR(B) |  |  | 0086 |  |  | 1-0A-06 |  |  | 330 | ON/OFF | NO.2 DTR-2B 330 CB 52AS |  | bbca | ELEM/D07_A1 | [8 empty] | 太鐵DS.340_CB | 340(#2DTR) CB | MTR | [5 empty] | 316 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0087 |  |  | 1-0A-07 |  |  | 330 | PHA | NO.2 DTR-2B 330 PHA PHA |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.340_PHA2 | 340開關箱IED RY PHA | OTHER | [5 empty] | 317 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0088 |  |  | 1-0B-00 |  |  | 330 | GDA | NO.2 DTR-2B 330 GDA GDA |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.340_GDA | 340開關箱IED RY GDA | OTHER | [5 empty] | 318 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1950 | #1SHR(1950) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | R/1SHR |  | 0112 |  |  | 1-0E-00 |  |  | #1 SHR | ON/OFF | #1 SHR 1950 CB |  | aakb | B2/D07_A1 | [8 empty] | 太鐵DS.1950_CB | 1950(161KV #1SHR) CB | OTHER | [5 empty] | 319 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 87A |  | B3 | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0113 |  |  | 1-0E-01 |  |  | #1 SHR | A/N | #1 SHR 87A |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.161#1SHR_87A | 161KV #1SHR 87RY | OTHER | [5 empty] | 320 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 96PA |  | B3 | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0114 |  |  | 1-0E-02 |  |  | #1 SHR | A/N | #1 SHR 機械保護動作(96PA) |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.161#1SHR96PA | 161KV #1SHR 機械保護動作 | OTHER | [5 empty] | 321 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 86A |  | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0115 |  |  | 1-0E-03 |  |  | #1 SHR | A/N | #1 SHR 86A |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.161#1SHR_86A | 161KV #1SHR 86RY | OTHER | [5 empty] | 322 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 51A |  | B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0116 |  |  | 1-0E-04 |  |  | #1 SHR | A/N | #1 SHR 51A |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.161#1SHR_51A | 161KV #1SHR 51RY | OTHER | [5 empty] | 323 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | RTU | RTU |  | RTU_MCT |  |  | Status | RTU Master Ry | Open/Close | Y | E | DI-SP | [6 empty] | 0117 |  |  | 1-0E-05 |  |  | 161RTU | MCT_ SOE | RTU Master Ry SOE |  |  | B3/D07_A1 | [16 empty] | 324 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D07 | 太鐵DS | 0 |  | RTU | RTU |  | RTUA |  |  | Status | RTU故障警報 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0118 |  |  | 1-0E-06 |  |  | RTU | RTUA | RTU發生異常 |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.RTUA | RTU發生異常 | OTHER | [5 empty] | 325 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS |  |  | 1DTR | #1DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0119 |  |  | 1-0E-07 |  |  | #1DTR | A/N | NO.1 DTR 86A 86A |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#1DTR_86A | #1DTR 86A | OTHER | [5 empty] | 326 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D07 | 太鐵DS |  |  | 2DTR | #2DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0120 |  |  | 1-0F-00 |  |  | #2DTR | A/N | NO.2 DTR 86A 86A |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#2DTR_86A | #2DTR 86A | OTHER | [5 empty] | 327 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV21 | 鐵21(JV21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/JV21/T1 |  |  | 0128 |  |  | 1-10-00 |  |  | F1 | ON/OFF | F1鐵21 (JV21)CB 52AS |  | aadb | B2/D07_D1 | [8 empty] | 太鐵DS.JV21_CB | JV21(11KV鐵21線) CB | FEEDER | [5 empty] | 328 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | JV21 | 鐵21(JV21) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0129 |  |  | 1-10-01 |  |  | F1 | PHA | F1鐵21 (JV21)RY PHA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV21_PHA | 11KV鐵21線(JV21) 相間RY | FEEDER | [5 empty] | 329 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV21 | 鐵21(JV21) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-10-02 |  |  | F1 | GDA | F1鐵21 (JV21)RY GDA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV21_GDA | 11KV鐵21線(JV21) 接地RY | FEEDER | [5 empty] | 330 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV22 | 鐵22(JV22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/JV22/T1 |  |  | 0132 |  |  | 1-10-04 |  |  | F2 | ON/OFF | F2鐵22 (JV22) CB 52AS |  | aaeb | B2/D07_D1 | [8 empty] | 太鐵DS.JV22_CB | JV22(11KV鐵22線) CB | FEEDER | [5 empty] | 331 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | JV22 | 鐵22(JV22) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0133 |  |  | 1-10-05 |  |  | F2 | PHA | F2鐵22 (JV22)RY PHA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV22_PHA | 11KV鐵22線(JV22) 相間RY | FEEDER | [5 empty] | 332 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV22 | 鐵22(JV22) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0134 |  |  | 1-10-06 |  |  | F2 | GDA | F2鐵22 (JV22)RY GDA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV22_GDA | 11KV鐵22線(JV22) 接地RY | FEEDER | [5 empty] | 333 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV23 | 鐵23(JV23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/JV23/T1 |  |  | 0136 |  |  | 1-11-00 |  |  | F3 | ON/OFF | F3鐵23 (JV23) CB 52AS |  | aafb | B2/D07_D1 | [8 empty] | 太鐵DS.JV23_CB | JV23(11KV鐵23線) CB | FEEDER | [5 empty] | 334 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | JV23 | 鐵23(JV23) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0137 |  |  | 1-11-01 |  |  | F3 | PHA | F3鐵23 (JV23)RY PHA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV23_PHA | 11KV鐵23線(JV23) 相間RY | FEEDER | [5 empty] | 335 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV23 | 鐵23(JV23) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0138 |  |  | 1-11-02 |  |  | F3 | GDA | F3鐵23 (JV23)RY GDA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV23_GDA | 11KV鐵23線(JV23) 接地RY | FEEDER | [5 empty] | 336 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV24 | 鐵24(JV24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/JV24/T1 |  |  | 0140 |  |  | 1-11-04 |  |  | F4 | ON/OFF | F4鐵24 (JV24) CB 52AS |  | aahb | B2/D07_D1 | [8 empty] | 太鐵DS.JV24_CB | JV24(11KV鐵24線) CB | FEEDER | [5 empty] | 337 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | JV24 | 鐵24(JV24) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0141 |  |  | 1-11-05 |  |  | F4 | PHA | F4鐵24 (JV24)RY PHA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV24_PHA | 11KV鐵24線(JV24) 相間RY | FEEDER | [5 empty] | 338 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV24 | 鐵24(JV24) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0142 |  |  | 1-11-06 |  |  | F4 | GDA | F4鐵24 (JV24)RY GDA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV24_GDA | 11KV鐵24線(JV24) 接地RY | FEEDER | [5 empty] | 339 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV25 | 鐵25(JV25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/JV25/T1 |  |  | 0144 |  |  | 1-12-00 |  |  | F5 | ON/OFF | F5鐵25 (JV25) CB 52AS |  | aaib | B2/D07_D1 | [8 empty] | 太鐵DS.JV25_CB | JV25(11KV鐵25線) CB | FEEDER | [5 empty] | 340 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | JV25 | 鐵25(JV25) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0145 |  |  | 1-12-01 |  |  | F5 | PHA | F5鐵25 (JV25)RY PHA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV25_PHA | 11KV鐵25線(JV25) 相間RY | FEEDER | [5 empty] | 341 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV25 | 鐵25(JV25) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0146 |  |  | 1-12-02 |  |  | F5 | GDA | F5鐵25 (JV25)RY GDA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV25_GDA | 11KV鐵25線(JV25) 接地RY | FEEDER | [5 empty] | 342 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | 210 | #1SC(210) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | C/1SC |  |  | 0148 |  |  | 1-12-04 |  |  | SC-1 | ON/OFF | SC-1 210 CB 52AS |  | aacb | B3/D07_A1 | [8 empty] | 太鐵DS.210_CB | 210(11KV #1SC) CB | SC | [5 empty] | 343 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0149 |  |  | 1-12-05 |  |  | SC-1 | SCA | SC-1 210 CB RY SCA |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.210_SCA | 11KV #1SC 51,51N RY | SC | [5 empty] | 344 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0150 |  |  | 1-12-06 |  |  | SC-1 | UVA | SC-1 210 CB RY UVA |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.210_OUVA | 11KV #1SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 345 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | 390 | #1SSTR(390) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | T/1SSTR |  |  | 0151 |  |  | 1-12-07 |  |  | SSTR-1 | ON/OFF | SSTR-1 390 CB 52AS |  | aaab | B3/D07_A1 | [8 empty] | 太鐵DS.390_CB | 390(#1SSTR) CB | OTHER | [5 empty] | 346 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | 390 | #1SSTR(390) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0152 |  |  | 1-13-00 |  |  | SSTR-1 | PHA | SSTR-1 390 CB RY PHA |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.#1SSTR_51A | #1SSTR 51RY | OTHER | [5 empty] | 347 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | 390 | #1SSTR(390) |  | GDA |  | B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0153 |  |  | 1-13-01 |  |  | SSTR-1 | GDA | SSTR-1 390 CB RY GDA |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | [5 empty] | 348 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV56 | 鐵56(JV56) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/JV56/T1 |  |  | 0154 |  |  | 1-13-02 |  |  | F6 | ON/OFF | F6鐵56 (JV56)CB 52AS |  | bahb | B2/D07_D1 | [8 empty] | 太鐵DS.JV56_CB | JV56(23KV鐵56線) CB | FEEDER | [5 empty] | 349 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | JV56 | 鐵56(JV56) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0155 |  |  | 1-13-03 |  |  | F6 | PHA | F6鐵56 (JV56)RY PHA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV56_PHA | 23KV鐵56線(JV56) 相間RY | FEEDER | [5 empty] | 350 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV56 | 鐵56(JV56) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0156 |  |  | 1-13-04 |  |  | F6 | GDA | F6鐵56 (JV56)RY GDA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV56_GDA | 23KV鐵56線(JV56) 接地RY | FEEDER | [5 empty] | 351 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV57 | 鐵57(JV57) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/JV57/T1 |  |  | 0158 |  |  | 1-13-06 |  |  | F7 | ON/OFF | F7鐵57 (JV57)CB 52AS |  | bagb | B2/D07_D1 | [8 empty] | 太鐵DS.JV57_CB | JV57(23KV鐵57線) CB | FEEDER | [5 empty] | 352 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | JV57 | 鐵57(JV57) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0159 |  |  | 1-13-07 |  |  | F7 | PHA | F7鐵57 (JV57)RY PHA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV57_PHA | 23KV鐵57線(JV57) 相間RY | FEEDER | [5 empty] | 353 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV57 | 鐵57(JV57) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0160 |  |  | 1-14-00 |  |  | F7 | GDA | F7鐵57 (JV57)RY GDA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV57_GDA | 23KV鐵57線(JV57) 接地RY | FEEDER | [5 empty] | 354 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV58 | 鐵58(JV58) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/JV58/T1 |  |  | 0162 |  |  | 1-14-02 |  |  | F8 | ON/OFF | F8鐵58 (JV58) CB 52AS |  | baeb | B2/D07_D1 | [8 empty] | 太鐵DS.JV58_CB | JV58(23KV鐵58線) CB | FEEDER | [5 empty] | 355 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | JV58 | 鐵58(JV58) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0163 |  |  | 1-14-03 |  |  | F8 | PHA | F8鐵58 (JV58) RY PHA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV58_PHA | 23KV鐵58線(JV58) 相間RY | FEEDER | [5 empty] | 356 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV58 | 鐵58(JV58) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0164 |  |  | 1-14-04 |  |  | F8 | GDA | F8鐵58 (JV58) RY GDA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV58_GDA | 23KV鐵58線(JV58) 接地RY | FEEDER | [5 empty] | 357 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV59 | 鐵59(JV59) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/JV59/T1 |  |  | 0166 |  |  | 1-14-06 |  |  | F9 | ON/OFF | F9鐵59 (JV59) CB 52AS |  | badb | B2/D07_D1 | [8 empty] | 太鐵DS.JV59_CB | JV59(23KV鐵59線) CB | FEEDER | [5 empty] | 358 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | JV59 | 鐵59(JV59) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0167 |  |  | 1-14-07 |  |  | F9 | PHA | F9鐵59 (JV59) RY PHA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV59_PHA | 23KV鐵59線(JV59) 相間RY | FEEDER | [5 empty] | 359 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV59 | 鐵59(JV59) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0168 |  |  | 1-15-00 |  |  | F9 | GDA | F9鐵59 (JV59) RY GDA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV59_GDA | 23KV鐵59線(JV59) 接地RY | FEEDER | [5 empty] | 360 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV60 | 鐵60(JV60) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/JV60/T1 |  |  | 0170 |  |  | 1-15-02 |  |  | F10 | ON/OFF | F10鐵60 (JV60) CB 52AS |  | bacb | B2/D07_D1 | [8 empty] | 太鐵DS.JV60_CB | JV60(23KV鐵60線) CB | FEEDER | [5 empty] | 361 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | JV60 | 鐵60(JV60) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0171 |  |  | 1-15-03 |  |  | F10 | PHA | F10鐵60 (JV60) RY PHA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV60_PHA | 23KV鐵60線(JV60) 相間RY | FEEDER | [5 empty] | 362 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV60 | 鐵60(JV60) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0172 |  |  | 1-15-04 |  |  | F10 | GDA | F10鐵60 (JV60) RY GDA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV60_GDA | 23KV鐵60線(JV60) 接地RY | FEEDER | [5 empty] | 363 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | 220 | #2SC(220) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | C/2SC |  |  | 0208 |  |  | 1-1A-00 |  |  | SC-2 | ON/OFF | SC-2 220 CB 52AS |  | babb | B3/D07_A1 | [8 empty] | 太鐵DS.220_CB | 220(23KV #2SC) CB | SC | [5 empty] | 364 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | 220 | #2SC(220) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0209 |  |  | 1-1A-01 |  |  | SC-2 | SCA | SC-2 220 CB RY SCA |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.220_SCA | 23KV #2SC 51,51N RY | SC | [5 empty] | 365 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | 220 | #2SC(220) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0210 |  |  | 1-1A-02 |  |  | SC-2 | UVA | SC-2 220 CB RY UVA |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.220_OUVA | 23KV #2SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 366 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV31 | 鐵31(JV31) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/JV31/T1 |  |  | 0211 |  |  | 1-1A-03 |  |  | F11 | ON/OFF | F11鐵31 (JV31) CB 52AS |  | abdb | B2/D07_D1 | [8 empty] | 太鐵DS.JV31_CB | JV31(11KV鐵31線) CB | FEEDER | [5 empty] | 367 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | JV31 | 鐵31(JV31) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0212 |  |  | 1-1A-04 |  |  | F11 | PHA | F11鐵31 (JV31)RY PHA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV31_PHA | 11KV鐵31線(JV31) 相間RY | FEEDER | [5 empty] | 368 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV31 | 鐵31(JV31) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0213 |  |  | 1-1A-05 |  |  | F11 | GDA | F11鐵31 (JV31)RY GDA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV31_GDA | 11KV鐵31線(JV31) 接地RY | FEEDER | [5 empty] | 369 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV32 | 鐵32(JV32) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/JV32/T1 |  |  | 0215 |  |  | 1-1A-07 |  |  | F12 | ON/OFF | F12鐵32 (JV32) CB 52AS |  | abeb | B2/D07_D1 | [8 empty] | 太鐵DS.JV32_CB | JV32(11KV鐵32線) CB | FEEDER | [5 empty] | 370 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | JV32 | 鐵32(JV32) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0216 |  |  | 1-1B-00 |  |  | F12 | PHA | F12鐵32 (JV32)RY PHA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV32_PHA | 11KV鐵32線(JV32) 相間RY | FEEDER | [5 empty] | 371 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV32 | 鐵32(JV32) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0217 |  |  | 1-1B-01 |  |  | F12 | GDA | F12鐵32 (JV32)RY GDA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV32_GDA | 11KV鐵32線(JV32) 接地RY | FEEDER | [5 empty] | 372 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV33 | 鐵33(JV33) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/JV33/T1 |  |  | 0219 |  |  | 1-1B-03 |  |  | F13 | ON/OFF | F13鐵33 (JV33) CB 52AS |  | abgb | B2/D07_D1 | [8 empty] | 太鐵DS.JV33_CB | JV33(11KV鐵33線) CB | FEEDER | [5 empty] | 373 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | JV33 | 鐵33(JV33) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0220 |  |  | 1-1B-04 |  |  | F13 | PHA | F13鐵33 (JV33)RY PHA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV33_PHA | 11KV鐵33線(JV33) 相間RY | FEEDER | [5 empty] | 374 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV33 | 鐵33(JV33) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0221 |  |  | 1-1B-05 |  |  | F13 | GDA | F13鐵33 (JV33)RY GDA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV33_GDA | 11KV鐵33線(JV33) 接地RY | FEEDER | [5 empty] | 375 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV34 | 鐵34(JV34) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/JV34/T1 |  |  | 0223 |  |  | 1-1B-07 |  |  | F14 | ON/OFF | F14鐵33 (JV34) CB 52AS |  | abhb | B2/D07_D1 | [8 empty] | 太鐵DS.JV34_CB | JV34(11KV鐵34線) CB | FEEDER | [5 empty] | 376 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | JV34 | 鐵34(JV34) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0224 |  |  | 1-1C-00 |  |  | F14 | PHA | F14鐵33 (JV34)RY PHA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV34_PHA | 11KV鐵34線(JV34) 相間RY | FEEDER | [5 empty] | 377 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV34 | 鐵34(JV34) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0225 |  |  | 1-1C-01 |  |  | F14 | GDA | F14鐵33 (JV34)RY GDA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV34_GDA | 11KV鐵34線(JV34) 接地RY | FEEDER | [5 empty] | 378 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV35 | 鐵35(JV35) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/JV35/T1 |  |  | 0227 |  |  | 1-1C-03 |  |  | F15 | ON/OFF | F15鐵35 (JV35) CB 52AS |  | abib | B2/D07_D1 | [8 empty] | 太鐵DS.JV35_CB | JV35(11KV鐵35線) CB | FEEDER | [5 empty] | 379 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | JV35 | 鐵35(JV35) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0228 |  |  | 1-1C-04 |  |  | F15 | PHA | F15鐵35 (JV35)RY PHA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV35_PHA | 11KV鐵35線(JV35) 相間RY | FEEDER | [5 empty] | 380 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV35 | 鐵35(JV35) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0229 |  |  | 1-1C-05 |  |  | F15 | GDA | F15鐵35 (JV35)RY GDA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV35_GDA | 11KV鐵35線(JV35) 接地RY | FEEDER | [5 empty] | 381 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | 230 | #3SC(230) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | C/3SC |  |  | 0231 |  |  | 1-1C-07 |  |  | SC-3 | ON/OFF | SC-3 230 CB 52AS |  | abcb | B3/D07_A1 | [8 empty] | 太鐵DS.230_CB | 230(11KV #3SC) CB | SC | [5 empty] | 382 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | 230 | #3SC(230) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0232 |  |  | 1-1D-00 |  |  | SC-3 | SCA | SC-3 230 CB RY SCA |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.230_SCA | 11KV #3SC 51,51N RY | SC | [5 empty] | 383 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | 230 | #3SC(230) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0233 |  |  | 1-1D-01 |  |  | SC-3 | UVA | SC-3 230 CB RY UVA |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.230_OUVA | 11KV #3SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 384 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | 100 | TIE(100) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/2ABus | B/1ABus |  |  | 0234 |  |  | 1-1D-02 |  |  | TIE-2A | ON/OFF | TIE-2A CB 52AS |  | abab | B3/D07_A1 | [8 empty] | 太鐵DS.100_CB | 100(TIE) CB | TIE | [5 empty] | 385 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 11 | 11kV | 100 | TIE(100) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0235 |  |  | 1-1D-03 |  |  | TIE-2A | PHA | TIE-2A RY PHA |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.100_51A | 11KV TIE(100) 51RY | TIE | [5 empty] | 386 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | 100 | TIE(100) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0236 |  |  | 1-1D-04 |  |  | TIE-2A | GDA | TIE-2A RY GDA |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.100_51NA | 11KV TIE(100) 51N RY | TIE | [5 empty] | 387 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV66 | 鐵66(JV66) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/JV66/T1 |  |  | 0237 |  |  | 1-1D-05 |  |  | F16 | ON/OFF | F16鐵66 (JV66) CB 52AS |  | bbjb | B2/D07_D1 | [8 empty] | 太鐵DS.JV66_CB | JV66(23KV鐵66線) CB | FEEDER | [5 empty] | 388 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | JV66 | 鐵66(JV66) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0238 |  |  | 1-1D-06 |  |  | F16 | PHA | F16鐵66 (JV66)RY PHA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV66_PHA | 23KV鐵66線(JV66) 相間RY | FEEDER | [5 empty] | 389 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV66 | 鐵66(JV66) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0239 |  |  | 1-1D-07 |  |  | F16 | GDA | F16鐵66 (JV66)RY GDA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV66_GDA | 23KV鐵66線(JV66) 接地RY | FEEDER | [5 empty] | 390 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV67 | 鐵67(JV67) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/JV67/T1 |  |  | 0241 |  |  | 1-1E-01 |  |  | F17 | ON/OFF | F17鐵67 (JV67) CB 52AS |  | bbib | B2/D07_D1 | [8 empty] | 太鐵DS.JV67_CB | JV67(23KV鐵67線) CB | FEEDER | [5 empty] | 391 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | JV67 | 鐵67(JV67) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0242 |  |  | 1-1E-02 |  |  | F17 | PHA | F17鐵67 (JV67)RY PHA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV67_PHA | 23KV鐵67線(JV67) 相間RY | FEEDER | [5 empty] | 392 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV67 | 鐵67(JV67) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0243 |  |  | 1-1E-03 |  |  | F17 | GDA | F17鐵67 (JV67)RY GDA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV67_GDA | 23KV鐵67線(JV67) 接地RY | FEEDER | [5 empty] | 393 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV68 | 鐵68(JV68) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/JV68/T1 |  |  | 0245 |  |  | 1-1E-05 |  |  | F18 | ON/OFF | F18鐵68 (JV68) CB 52AS |  | bbhb | B2/D07_D1 | [8 empty] | 太鐵DS.JV68_CB | JV68(23KV鐵68線) CB | FEEDER | [5 empty] | 394 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | JV68 | 鐵68(JV68) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0246 |  |  | 1-1E-06 |  |  | F18 | PHA | F18鐵68 (JV68)RY PHA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV68_PHA | 23KV鐵68線(JV68) 相間RY | FEEDER | [5 empty] | 395 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV68 | 鐵68(JV68) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0247 |  |  | 1-1E-07 |  |  | F18 | GDA | F18鐵68 (JV68)RY GDA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV68_GDA | 23KV鐵68線(JV68) 接地RY | FEEDER | [5 empty] | 396 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV69 | 鐵69(JV69) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/JV69/T1 |  |  | 0249 |  |  | 1-1F-01 |  |  | F19 | ON/OFF | F19鐵69 (JV69) CB 52AS |  | bbfb | B2/D07_D1 | [8 empty] | 太鐵DS.JV69_CB | JV69(23KV鐵69線) CB | FEEDER | [5 empty] | 397 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | JV69 | 鐵69(JV69) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0250 |  |  | 1-1F-02 |  |  | F19 | PHA | F19鐵69 (JV69)RY PHA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV69_PHA | 23KV鐵69線(JV69) 相間RY | FEEDER | [5 empty] | 398 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV69 | 鐵69(JV69) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0251 |  |  | 1-1F-03 |  |  | F19 | GDA | F19鐵69 (JV69)RY GDA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV69_GDA | 23KV鐵69線(JV69) 接地RY | FEEDER | [5 empty] | 399 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV70 | 鐵70(JV70) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/JV70/T1 |  |  | 0253 |  |  | 1-1F-05 |  |  | F20 | ON/OFF | F20鐵70 (JV70) CB 52AS |  | bbeb | B2/D07_D1 | [8 empty] | 太鐵DS.JV70_CB | JV70(23KV鐵70線) CB | FEEDER | [5 empty] | 400 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | JV70 | 鐵70(JV70) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0254 |  |  | 1-1F-06 |  |  | F20 | PHA | F20鐵70 (JV70)RY PHA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV70_PHA | 23KV鐵70線(JV70) 相間RY | FEEDER | [5 empty] | 401 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV70 | 鐵70(JV70) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0255 |  |  | 1-1F-07 |  |  | F20 | GDA | F20鐵70 (JV70)RY GDA |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV70_GDA | 23KV鐵70線(JV70) 接地RY | FEEDER | [5 empty] | 402 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | 240 | #4SC(240) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | C/4SC |  |  | 0257 |  |  | 2-00-01 |  |  | SC-4 | ON/OFF | SC-4 240 CB 52AS |  | bbdb | B3/D07_A1 | [8 empty] | 太鐵DS.240_CB | 240(23KV #4SC) CB | SC | [5 empty] | 403 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | 240 | #4SC(240) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0258 |  |  | 2-00-02 |  |  | SC-4 | SCA | SC-4 240 RY SCA |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.240_SCA | 23KV #4SC 51,51N RY | SC | [5 empty] | 404 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | 240 | #4SC(240) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0259 |  |  | 2-00-03 |  |  | SC-4 | UVA | SC-4 240 RY UVA |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.240_OUVA | 23KV #4SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 405 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | 200 | TIE(200) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/2BBus | B/1BBus |  |  | 0260 |  |  | 2-00-04 |  |  | TIE-2B | ON/OFF | TIE-2B CB 52AS |  | bbab | B3/D07_A1 | [8 empty] | 太鐵DS.200_CB | 200(TIE) CB | TIE | [5 empty] | 406 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 22 | 22kV | 200 | TIE(200) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0261 |  |  | 2-00-05 |  |  | TIE-2B | PHA | TIE-2B RY PHA |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.200_51A | 23KV TIE(200) 51RY | TIE | [5 empty] | 407 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | 200 | TIE(200) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0262 |  |  | 2-00-06 |  |  | TIE-2B | GDA | TIE-2B RY GDA |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.200_51NA | 23KV TIE(200) 51N RY | TIE | [5 empty] | 408 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | 490 | #2SSTR(490) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | T/2SSTR |  |  | 0263 |  |  | 2-00-07 |  |  | SSTR-2 | ON/OFF | SSTR- 2 490 CB 52AS |  | bbbb | B3/D07_A1 | [8 empty] | 太鐵DS.490_CB | 490(#2SSTR) CB | OTHER | [5 empty] | 409 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | 490 | #2SSTR(490) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0264 |  |  | 2-01-00 |  |  | SSTR-2 | PHA | SSTR-2 490 RY PHA |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.#2SSTR_51A | #2SSTR 51RY | OTHER | [5 empty] | 410 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | 490 | #2SSTR(490) |  | GDA |  | B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0265 |  |  | 2-01-01 |  |  | SSTR-2 | GDA | SSTR-2 490 RY GDA |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | [5 empty] | 411 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | ComPoint |  |  | 25PFA |  |  | Status | 同步校核電驛電源 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0368 |  |  | 2-0E-00 |  |  | 25RY | A/N | 同步校核裝置電源 25TA |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | [5 empty] | 412 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | ComPoint |  |  | 25TA |  |  | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0369 |  |  | 2-0E-01 |  |  | 25RY | A/N | 同步校核裝置超時 25PFA |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER | [5 empty] | 413 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0512 |  |  | 1-30-00 |  |  | Test CB | ON/OFF | TEST C.B. |  |  | ELEM/ALL | [8 empty] | 太鐵DS.TEST_CB | TEST CB | OTHER | [5 empty] | 414 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | RTU | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0513 |  |  | 1-30-01 |  |  | Locate Empty | L/R | LOCAL/REMOTE STATUS |  |  | ELEM/D07_A1 | [8 empty] | 太鐵DS.RTU_S/L | RTU SUPY/LOCAL | OTHER | [5 empty] | 415 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
D07 | 太鐵DS | 161 | 161kV | 1510 | 太鐵～槺榔一路(1510) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0514 |  |  | 1-30-02 |  |  | L1 | USE/LOCK | L1(太鐵糠榔一路1510)87RY 87S |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1510_87UL | 太鐵糠榔一路(1510) 87RY U/L | LINE161 | [5 empty] | 416 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 161 | 161kV | 1510 | 太鐵～槺榔一路(1510) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0515 |  |  | 1-30-03 |  |  | L1 | USE/LOCK | L1(太鐵糠榔一路1510)79RY 79S |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1510_79UL | 太鐵糠榔一路(1510) 79RY U/L | LINE161 | [5 empty] | 417 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 161 | 161kV | 1520 | 太鐵～槺榔二路(1520) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0516 |  |  | 1-30-04 |  |  | L2 | USE/LOCK | L2(太鐵糠榔二路1520)87RY 87S |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1520_87UL | 太鐵糠榔二路(1520) 87RY U/L | LINE161 | [5 empty] | 418 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 161 | 161kV | 1520 | 太鐵～槺榔二路(1520) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0517 |  |  | 1-30-05 |  |  | L2 | USE/LOCK | L2(太鐵糠榔二路1520)79RY 79S |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1520_79UL | 太鐵糠榔二路(1520) 79RY U/L | LINE161 | [5 empty] | 419 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0518 |  |  | 1-30-06 |  |  | L3 | USE/LOCK | L3(北回太鐵紅線1530)87RY 87S |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1530_87UL | 北回太鐵紅線(1530) 87RY U/L | LINE161 | [5 empty] | 420 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0519 |  |  | 1-30-07 |  |  | L3 | USE/LOCK | L3(北回太鐵紅線1530)79RY 79S |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1530_79UL | 北回太鐵紅線(1530) 79RY U/L | LINE161 | [5 empty] | 421 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0520 |  |  | 1-30-08 |  |  | L4 | USE/LOCK | L4(北回太鐵白線1540)87RY 87S |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1540_87UL | 北回太鐵白線(1540) 87RY U/L | LINE161 | [5 empty] | 422 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0521 |  |  | 1-30-09 |  |  | L4 | USE/LOCK | L4(北回太鐵白線1540)79RY 79S |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1540_79UL | 北回太鐵白線(1540) 79RY U/L | LINE161 | [5 empty] | 423 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 161 | 161kV | 1550 | 後壁太鐵一路(1550) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0522 |  |  | 1-30-10 |  |  | L5 | USE/LOCK | L5(後壁太鐵一路1550)87RY 87S |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1550_87UL | 後壁太鐵一路(1550) 87RY U/L | LINE161 | [5 empty] | 424 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 161 | 161kV | 1550 | 後壁太鐵一路(1550) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0523 |  |  | 1-30-11 |  |  | L5 | USE/LOCK | L5(後壁太鐵一路1550)79RY 79S |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1550_79UL | 後壁太鐵一路(1550) 79RY U/L | LINE161 | [5 empty] | 425 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 161 | 161kV | 1560 | 後壁太鐵二路(1560) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0524 |  |  | 1-30-12 |  |  | L6 | USE/LOCK | L6(後壁太鐵二路1560)87RY 87S |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1560_87UL | 後壁太鐵二路(1560) 87RY U/L | LINE161 | [5 empty] | 426 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 161 | 161kV | 1560 | 後壁太鐵二路(1560) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0525 |  |  | 1-30-13 |  |  | L6 | USE/LOCK | L6(後壁太鐵二路1560)79RY 79S |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1560_79UL | 後壁太鐵二路(1560) 79RY U/L | LINE161 | [5 empty] | 427 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 161 | 161kV | ComPoint |  |  | BUS_RYFA |  |  | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0534 |  |  | 1-31-06 |  |  | BUS | A/N | 161KV BUS數位電驛故障 |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | [5 empty] | 428 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | ComPoint |  |  | 12B_CTFA | 待新增!!__BUS_87CTFA | Element | Status | #1#2 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0535 |  |  | 1-31-07 |  |  | BUS | A/N | 161KV BUS 87RY CT 迴路故障 |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.161KV_BUS_CTFA | 161KV BUS 87RY CT回路故障 | OTHER | [5 empty] | 429 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1510 | 太鐵～槺榔一路(1510) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0536 |  |  | 1-31-08 |  |  | L1 | A/N | 太鐵糠榔一路1510 87CFA |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1510_87CFA | 太鐵糠榔一路(1510)87RY通訊故障 | OTHER | [5 empty] | 430 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1510 | 太鐵～槺榔一路(1510) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0537 |  |  | 1-31-09 |  |  | L1 | A/N | 太鐵糠榔一路1510 RYFA |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1510_RYFA | 太鐵糠榔一路(1510)數位電驛故障 | OTHER | [5 empty] | 431 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1520 | 太鐵～槺榔二路(1520) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0538 |  |  | 1-31-10 |  |  | L2 | A/N | 太鐵糠榔二路1520 87CFA |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1520_87CFA | 太鐵糠榔二路(1520)87RY通訊故障 | OTHER | [5 empty] | 432 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1520 | 太鐵～槺榔二路(1520) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0539 |  |  | 1-31-11 |  |  | L2 | A/N | 太鐵糠榔二路1520 RYFA RY故障 |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1520_RYFA | 太鐵糠榔二路(1520)數位電驛故障 | OTHER | [5 empty] | 433 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0540 |  |  | 1-31-12 |  |  | L3 | A/N | 北回太鐵紅線1530 87CFA |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1530_87CFA | 北回太鐵紅線(1530)87RY通訊故障 | OTHER | [5 empty] | 434 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0541 |  |  | 1-31-13 |  |  | L3 | A/N | 北回太鐵紅線1530 RYFA RY故障 |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1530_RYFA | 北回太鐵紅線(1530)數位電驛故障 | OTHER | [5 empty] | 435 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0542 |  |  | 1-31-14 |  |  | L4 | A/N | 北回太鐵白線1540 87CFA |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1540_87CFA | 北回太鐵白線(1540)87RY通訊故障 | OTHER | [5 empty] | 436 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0543 |  |  | 1-31-15 |  |  | L4 | A/N | 北回太鐵白線1540 RYFA RY故障 |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1540_RYFA | 北回太鐵白線(1540)數位電驛故障 | OTHER | [5 empty] | 437 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1550 | 後壁太鐵一路(1550) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0544 |  |  | 1-32-00 |  |  | L5 | A/N | 後壁太鐵一路1550 87CFA |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1550_87CFA | 後壁太鐵一路(1550)87RY通訊故障 | OTHER | [5 empty] | 438 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1550 | 後壁太鐵一路(1550) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0545 |  |  | 1-32-01 |  |  | L5 | A/N | 後壁太鐵一路1550 RYFA RY故障 |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1550_RYFA | 後壁太鐵一路(1550)數位電驛故障 | OTHER | [5 empty] | 439 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1560 | 後壁太鐵二路(1560) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0546 |  |  | 1-32-02 |  |  | L6 | A/N | 後壁太鐵二路1560 87CFA |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1560_87CFA | 後壁太鐵二路(1560)87RY通訊故障 | OTHER | [5 empty] | 440 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1560 | 後壁太鐵二路(1560) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0547 |  |  | 1-32-03 |  |  | L6 | A/N | 後壁太鐵二路1560 RYFA RY故障 |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1560_RYFA | 後壁太鐵二路(1560)數位電驛故障 | OTHER | [5 empty] | 441 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | StaDev | 所內設施 |  | Water1 |  |  | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0556 |  |  | 1-32-12 |  |  | Locate Empty | A/N | 地下室水位警報(1) UW1 |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.水位警報(1) | 地下室水位警報(1) | OTHER | [5 empty] | 442 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | StaDev | 所內設施 |  | Water2 |  |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0557 |  |  | 1-32-13 |  |  | Locate Empty | A/N | 地下室水位警報(2) UW2 |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.水位警報(2) | 地下室水位警報(2) | OTHER | [5 empty] | 443 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | ComPoint |  |  | 60A |  |  | Status | 電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0558 |  |  | 1-32-14 |  |  | Locate Empty | A/N | 23KV SC 60-RY 警報 60A |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.23KV_SC_60A | 11/23KV SC 60A | OTHER | [5 empty] | 444 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0559 |  |  | 1-32-15 |  |  | Locate Empty | A/N | 23KV CB重故障 CBA |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | [5 empty] | 445 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0560 |  |  | 1-33-00 |  |  | Locate Empty | A/N | 23KV CB輕故障 CBF |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | [5 empty] | 446 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | ComPoint |  |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0561 |  |  | 1-33-01 |  |  | Locate Empty | A/N | 23KV FEEDER 79RY LOA |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.11/23KV_LOA | 11/23KV饋線復閉失敗閉鎖 | OTHER | [5 empty] | 447 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | StaDev | 所內設施 |  | OilLeak1 |  |  | Status | 洩油池水位警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0562 |  |  | 1-33-02 |  |  | Locate Empty | A/N | OW1蓄油池水位警報1 WPF |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.蓄油池警報(1) | 蓄油池水位警報(1) | OTHER | [5 empty] | 448 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | StaDev | 所內設施 |  | OilLeak2 |  |  | Status | 洩油池水位警報2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0563 |  |  | 1-33-03 |  |  | Locate Empty | A/N | OW2蓄油池水位警報2 WPA |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.蓄油池警報(2) | 蓄油池水位警報(2) | OTHER | [5 empty] | 449 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0565 |  |  | 1-33-05 |  |  | #1 BUS | ON/OFF | 161KV #1 BUS╴87UL |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 161 | 161kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0566 |  |  | 1-33-06 |  |  | #2 BUS | ON/OFF | 161KV #2 BUS╴87UL |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | [5 empty] | 451 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0567 |  |  | 1-33-07 |  |  | 161KV TIE | 測試/正常 | 161KV TIE (1500)50RY 測試/正常150SA |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1500_50SA | 161KV TIE(1500) 50RY 測試/正常 | TIE | [5 empty] | 452 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Test | Test | 1 |  |  | TEST/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | ComPoint |  |  | OLTC_A |  |  | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0568 |  |  | 1-33-08 |  |  | OLTC | OLTCA | OLTC 15分鐘內連動3次警報 |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | [5 empty] | 453 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS |  |  | 1DTR(A) | #1DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0571 |  |  | 1-33-11 |  |  | Locate Empty | 遙控/現場 | NO.1 D.TR. S/L (A) 143R1S3 |  | c | B1/D07_A1 | [8 empty] | 太鐵DS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | [5 empty] | 454 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D07 | 太鐵DS |  |  | 1DTR(A) | #1DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0572 |  |  | 1-33-12 |  |  | Locate Empty | OLTC A/M | NO.1 D.TR. A/M (A) 1AX-S1 |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | [5 empty] | 455 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D07 | 太鐵DS |  |  | 1DTR(B) | #1DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0573 |  |  | 1-33-13 |  |  | Locate Empty | 遙控/現場 | NO.1 D.TR. S/L (B) 143R2S3 |  | b | B1/D07_A1 | [8 empty] | 太鐵DS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | [5 empty] | 456 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D07 | 太鐵DS |  |  | 1DTR(B) | #1DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0574 |  |  | 1-33-14 |  |  | Locate Empty | OLTC A/M | NO.1 D.TR. A/M (B) 1AX-S2 |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | [5 empty] | 457 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D07 | 太鐵DS |  |  | 1DTR | #1DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0575 |  |  | 1-33-15 |  |  | Locate Empty | A/N | NO.1 D.TR.撲氣電驛(1) 196B1 |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | [5 empty] | 458 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS |  |  | 1DTR | #1DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0576 |  |  | 1-34-00 |  |  | Locate Empty | A/N | NO.1 D.TR.撲氣電驛(2) 196B2 |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | [5 empty] | 459 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS |  |  | 1DTR | #1DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0577 |  |  | 1-34-01 |  |  | Locate Empty | A/N | NO.1 D.TR.放壓裝置 196D |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#1DTR_96D | #1DTR 96D RY | MTR | [5 empty] | 460 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS |  |  | 1DTR | #1DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0578 |  |  | 1-34-02 |  |  | Locate Empty | A/N | NO.1 D.TR.衝擊油壓 196P |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#1DTR_96P | #1DTR 96P RY | MTR | [5 empty] | 461 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS |  |  | 1DTR | #1DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0579 |  |  | 1-34-03 |  |  | Locate Empty | A/N | NO.1 D.TR. ULTC 163Q |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#1DTR_63Q | #1DTR 63Q RY | MTR | [5 empty] | 462 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS |  |  | 1DTR | #1DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0580 |  |  | 1-34-04 |  |  | Locate Empty | A/N | NO.1 D.TR.輕故障 1TRF |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#1DTR_TRF | #1DTR 輕故障 | MTR | [5 empty] | 463 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D07 | 太鐵DS |  |  | 1DTR | #1DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0581 |  |  | 1-34-05 |  |  | Locate Empty | A/N | NO.1 D.TR.重故障 1TRA |  | a | B1/D07_A1 | [8 empty] | 太鐵DS.#1DTR_TRA | #1DTR 重故障 | MTR | [5 empty] | 464 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D07 | 太鐵DS |  |  | 2DTR(A) | #2DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0583 |  |  | 1-34-07 |  |  | Locate Empty | 遙控/現場 | NO.2 D.TR. S/L (A) 243R1S3 |  | c | B1/D07_A1 | [8 empty] | 太鐵DS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | [5 empty] | 465 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D07 | 太鐵DS |  |  | 2DTR(A) | #2DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0584 |  |  | 1-34-08 |  |  | Locate Empty | OLTC A/M | NO.2 D.TR. A/M (A) 2AX-S1 |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | [5 empty] | 466 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D07 | 太鐵DS |  |  | 2DTR(B) | #2DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0585 |  |  | 1-34-09 |  |  | Locate Empty | 遙控/現場 | NO.2 D.TR. S/L (B) 243R2S3 |  | b | B1/D07_A1 | [8 empty] | 太鐵DS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | [5 empty] | 467 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D07 | 太鐵DS |  |  | 2DTR(B) | #2DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0586 |  |  | 1-34-10 |  |  | Locate Empty | OLTC A/M | NO.2 D.TR. A/M (B) 2AX-S2 |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | [5 empty] | 468 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D07 | 太鐵DS |  |  | 2DTR | #2DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0587 |  |  | 1-34-11 |  |  | Locate Empty | A/N | NO.2 D.TR.撲氣電驛(1) 296B1 |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | [5 empty] | 469 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS |  |  | 2DTR | #2DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0588 |  |  | 1-34-12 |  |  | Locate Empty | A/N | NO.2 D.TR.撲氣電驛(2) 296B2 |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | [5 empty] | 470 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS |  |  | 2DTR | #2DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0589 |  |  | 1-34-13 |  |  | Locate Empty | A/N | NO.2 D.TR.放壓裝置 296D |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#2DTR_96D | #2DTR 96D RY | MTR | [5 empty] | 471 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS |  |  | 2DTR | #2DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0590 |  |  | 1-34-14 |  |  | Locate Empty | A/N | NO.2 D.TR.衝擊油壓 296P |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#2DTR_96P | #2DTR 96P RY | MTR | [5 empty] | 472 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS |  |  | 2DTR | #2DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0591 |  |  | 1-34-15 |  |  | Locate Empty | A/N | NO.2 D.TR. ULTC 263Q |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#2DTR_63Q | #2DTR 63Q RY | MTR | [5 empty] | 473 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS |  |  | 2DTR | #2DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0592 |  |  | 1-35-00 |  |  | Locate Empty | A/N | NO.2 D.TR.輕故障 2TRF |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#2DTR_TRF | #2DTR 輕故障 | MTR | [5 empty] | 474 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D07 | 太鐵DS |  |  | 2DTR | #2DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0593 |  |  | 1-35-01 |  |  | Locate Empty | A/N | NO.2 D.TR.重故障 2TRA |  | a | B1/D07_A1 | [8 empty] | 太鐵DS.#2DTR_TRA | #2DTR 重故障 | MTR | [5 empty] | 475 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | StaDev | 所內設施 |  | Fire1 | 受信總機 |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0614 |  |  | 1-36-06 |  |  | 火災警報(1) | A/N | 火災警報(1)受信總機 |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | [5 empty] | 476 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | StaDev | 所內設施 |  | Fire2 |  |  | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0615 |  |  | 1-36-07 |  |  | 火災警報(2) | A/N | 火災警報(2) |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.火災警報(2) | 火災警報(2) | OTHER | [5 empty] | 477 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | StaDev | 所內設施 |  | Fire3 |  |  | Status | 火災警報3 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0616 |  |  | 1-36-08 |  |  | 火災警報(3) | A/N | 火災警報(3) |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.火災警報(3) | 火災警報(3) | OTHER | [5 empty] | 478 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | StaDev | 所內設施 |  | Fire4 |  |  | Status | 火災警報4 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0617 |  |  | 1-36-09 |  |  | 火災警報(4) | A/N | 火災警報(4) |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.火災警報(4) | 火災警報(4) | OTHER | [5 empty] | 479 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | StaDev | 所內設施 |  | Fire5 |  |  | Status | 火災警報5 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0618 |  |  | 1-36-10 |  |  | 火災警報(5) | A/N | 火災警報(5) |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.火災警報(5) | 火災警報(5) | OTHER | [5 empty] | 480 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | StaDev | 所內設施 |  | Door1 | 圍牆大門 |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0619 |  |  | 1-36-11 |  |  | Locate Empty | A/N | 無人化門禁(一)圍牆大門 DOOR1 |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.無人化門禁(1) | 無人化門禁(1)圍牆大門 | OTHER | [5 empty] | 481 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | OPEN/CLOSE | CLOSE
D07 | 太鐵DS | 0 |  | StaDev | 所內設施 |  | Door2 | 建築物大小門 |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0620 |  |  | 1-36-12 |  |  | Locate Empty | A/N | 無人化門禁(二)建築物大小門 DOOR2 |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.無人化門禁(2) | 無人化門禁(2)建築物大小門 | OTHER | [5 empty] | 482 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | OPEN/CLOSE | CLOSE
D07 | 太鐵DS | 0 |  | StaDev | 所內設施 |  | Door3 | 保全 |  | Status | 無人化門禁3 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0621 |  |  | 1-36-13 |  |  | Locate Empty | A/N | 無人化門禁(三)保全 DOOR3 |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | [5 empty] | 483 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | StaDev | 所內設施 |  | Door4 |  |  | Status | 無人化門禁4 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0622 |  |  | 1-36-14 |  |  | Locate Empty | A/N | 無人化門禁(四) DOOR4 |  |  | B3/D07_A1 | [16 empty] | 484 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D07 | 太鐵DS | 0 |  | StaDev | 所內設施 |  | Door5 |  | Element | Status | 無人化門禁5 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0623 |  |  | 1-36-15 |  |  | Locate Empty | A/N | 無人化門禁(五) DOOR5 |  |  | B3/D07_A1 | [16 empty] | 485 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D07 | 太鐵DS | 0 |  | StaDev | 所內設施 |  | Lights1 |  |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0624 |  |  | 1-37-00 |  |  | Locate Empty | ON/OFF | 無人化開關場照明(A) FLA |  |  | B3/D07_A1 | [16 empty] | 486 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D07 | 太鐵DS | 0 |  | StaDev | 所內設施 |  | Lights2 |  |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0625 |  |  | 1-37-01 |  |  | Locate Empty | ON/OFF | 無人化開關場照明(B) FLB |  |  | B3/D07_A1 | [16 empty] | 487 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D07 | 太鐵DS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0626 |  |  | 1-37-02 |  |  | Locate Empty | ON/OFF | 所內電源ACB1 |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | [5 empty] | 488 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D07 | 太鐵DS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0627 |  |  | 1-37-03 |  |  | Locate Empty | ON/OFF | 所內電源ACB2 |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | [5 empty] | 489 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D07 | 太鐵DS | 0 |  | StaDev | 所內設施 |  | ACBT |  |  | Status | 所內電源ACB TIE | Close/Open | Y | 3 | DI-SP | [6 empty] | 0628 |  |  | 1-37-04 |  |  | Locate Empty | ON/OFF | 所內電源ACB TIE |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | [5 empty] | 490 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ON/OFF | OFF
D07 | 太鐵DS | 161 | 161kV | ComPoint |  |  | OPA |  |  | Status | 充油電纜低壓警報 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0629 |  |  | 1-37-05 |  |  | Locate Empty | A/N | 充油電纜警報 OPA |  |  | B3/D07_A1 | [16 empty] | 491 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D07 | 太鐵DS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0630 |  |  | 1-37-06 |  |  | Locate Empty | A/N | 所內欠壓警報 STUV |  |  | ELEM/D07_A1 | [8 empty] | 太鐵DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | [5 empty] | 492 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0631 |  |  | 1-37-07 |  |  | Locate Empty | A/N | 161KV CB 重故障 CBA |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.161KV_CBA | 161KV斷路器重故障 | OTHER | [5 empty] | 493 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0632 |  |  | 1-37-08 |  |  | Locate Empty | A/N | 161KV CB 輕故障 CBF |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | [5 empty] | 494 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0633 |  |  | 1-37-09 |  |  | Locate Empty | A/N | NFB跳脫警報 DCA |  |  | ELEM/D07_A1 | [8 empty] | 太鐵DS.直流電源DCA | 直流電源故障警報 | OTHER | [5 empty] | 495 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0634 |  |  | 1-37-10 |  |  | Locate Empty | A/N | ACB警報 ACBA |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.所內電源ACBA | 所內電源故障警報 | OTHER | [5 empty] | 496 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0635 |  |  | 1-37-11 |  |  | Locate Empty | A/N | 161KV NO.1 BUS欠壓 VUA1 |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | [5 empty] | 497 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0636 |  |  | 1-37-12 |  |  | Locate Empty | A/N | 161KV NO.2 BUS欠壓 VUA2 |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | [5 empty] | 498 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0637 |  |  | 1-37-13 |  |  | Locate Empty | A/N | 充電機警報 CHG1 |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.直流充電機故障 | 直流充電機故障 | OTHER | [5 empty] | 499 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0638 |  |  | 1-37-14 |  |  | Locate Empty | A/N | DC接地警報 DCE |  |  | ELEM/D07_A1 | [8 empty] | 太鐵DS.直流電源DCE | 直流電源接地故障警報 | OTHER | [5 empty] | 500 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | ComPoint |  |  | COMT |  |  | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0639 |  |  | 1-37-15 |  |  | Locate Empty | A/N | 161KV CB空壓機超時運轉 COMT |  |  | B3/D07_A1 | [16 empty] | 501 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D07 | 太鐵DS | 0 |  | StaDev | 所內設施 |  | GEN | 緊急發電機運轉 | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0640 |  |  | 1-38-00 |  |  | Locate Empty | ON/OFF | 緊急發電機運轉 |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.GEN | 緊急發電機運轉 | OTHER | [5 empty] | 502 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ON/OFF | OFF
D07 | 太鐵DS | 0 |  | StaDev | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0646 |  |  | 1-38-06 |  |  | PMA | A/N | 電力量測器故障 PMA |  |  | ELEM/D07_A1 | [8 empty] | 太鐵DS.PMA | 電力量測表計故障 | OTHER | [5 empty] | 503 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | ComPoint |  |  | OSCF1 | [14 empty] | 0647 |  |  | 1-38-07 |  |  | OSCF1 | A/N | 161KV示波器缺紙或故障警報OSCF1 |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.161KV_OSCF_1 | 161KV示波器故障/缺紙(1) | OTHER | [5 empty] | 504 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | ComPoint |  |  | OSCF2 | [14 empty] | 0648 |  |  | 1-38-08 |  |  | OSCF2 | A/N | 161KV示波器缺紙或故障警報OSCF2 |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.161KV_OSCF_2 | 161KV示波器故障/缺紙(2) | OTHER | [5 empty] | 505 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | StaDev | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0649 |  |  | 1-38-09 |  |  | Locate Empty | A/N | 其他輕故障 PSF |  |  | B3/D07_A1 | [16 empty] | 506 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D07 | 太鐵DS | 0 |  | StaDev | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0650 |  |  | 1-38-10 |  |  | Locate Empty | A/N | 其他重故障 PSA |  |  | B3/D07_A1 | [16 empty] | 507 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D07 | 太鐵DS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0651 |  |  | 1-38-11 |  |  | 通訊室 | A/N | 通訊充電機故障 CHG2 |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | [5 empty] | 508 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0652 |  |  | 1-38-12 |  |  | 通訊室 | A/N | 通訊設備AC故障 ACFA |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | [5 empty] | 509 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | StaDev | 所內設施 |  | R_Temp |  |  | Status | 溫度警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0655 |  |  | 1-38-15 |  |  | 通訊室 | A/N | 通訊室或控制室溫度警報 |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.通信機房溫度 | 通訊室或控制室溫度警報 | OTHER | [5 empty] | 510 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0656 |  |  | 1-39-00 |  |  | Locate Empty |  | #1 SHR 96B1 |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.161#1SHR_96B1 | 161KV #1SHR 96B1 RY | OTHER | [5 empty] | 511 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0657 |  |  | 1-39-01 |  |  | Locate Empty |  | #1 SHR 96B2 |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.161#1SHR_96B2 | 161KV #1SHR 96B2 RY | OTHER | [5 empty] | 512 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0658 |  |  | 1-39-02 |  |  | Locate Empty |  | #1 SHR 96D |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.161#1SHR_96D | 161KV #1SHR 96D RY | OTHER | [5 empty] | 513 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0659 |  |  | 1-39-03 |  |  | Locate Empty |  | #1 SHR 96P |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.161#1SHR_96P | 161KV #1SHR 96P RY | OTHER | [5 empty] | 514 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1950 | #1SHR(1950) |  | SHRF | 電抗器輕故障 | Element | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0660 |  |  | 1-39-04 |  |  | Locate Empty |  | #1 SHR SRF 輕故障 |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.161#1SHR_SRF | 161KV #1SHR 輕故障 | OTHER | [5 empty] | 515 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1950 | #1SHR(1950) |  | SHRA | 電抗器重故障 | Element | Status | 警報等級5動作4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0661 |  |  | 1-39-05 |  |  | Locate Empty |  | #1 SHR SRA 重故障 |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.161#1SHR_SRA | 161KV #1SHR 重故障 | OTHER | [5 empty] | 516 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1950 | #1SHR(1950) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0662 |  |  | 1-39-06 |  |  | Locate Empty |  | #1 SHR RYFA |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.161_1SHR_RYFA | 161KV 1SHR(1950)數位電驛故障 | OTHER | [5 empty] | 517 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0663 |  |  | 1-39-07 |  |  | Locate Empty |  | #1 SHR 第一套 87RY U/L |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.161#1SHR_187UL | 161KV #1SHR 187RY U/L | OTHER | [5 empty] | 518 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0664 |  |  | 1-39-08 |  |  | Locate Empty |  | #1 SHR 第二套 87RY U/L |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.161#1SHR_287UL | 161KV #1SHR 287RY U/L | OTHER | [5 empty] | 519 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 161 | 161kV | 1510 | 太鐵～槺榔一路(1510) |  | DS1 | 1511 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0688 | 689 |  | 1-3B-00 |  |  | L1 | ON | L1 (太鐵糠榔一路1511) DS-AS |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1511_DS | 1511(太鐵糠榔一路) DS | LINE161 | [5 empty] | 520 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1510 | 太鐵～槺榔一路(1510) |  | DS2 | 1512 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0690 | 691 |  | 1-3B-02 |  |  | L1 | ON | L1 (太鐵糠榔一路1512) DS-AS |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1512_DS | 1512(太鐵糠榔一路) DS | LINE161 | [5 empty] | 521 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D07 | 太鐵DS | 161 | 161kV | 1510 | 太鐵～槺榔一路(1510) |  | DS3 | 1513 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0692 | 693 |  | 1-3B-04 |  |  | L1 | ON | L1 (太鐵糠榔一路1513) DS-AS |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1513_DS | 1513(太鐵糠榔一路) DS | LINE161 | [5 empty] | 522 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1510 | 太鐵～槺榔一路(1510) |  | ES3 | 1513E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0694 | 695 |  | 1-3B-06 |  |  | L1 | ON | L1 (太鐵糠榔一路1513E) ES-AS |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1513E_ES | 1513E(太鐵糠榔一路) ES | LINE161 | [5 empty] | 523 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D07 | 太鐵DS | 161 | 161kV | 1520 | 太鐵～槺榔二路(1520) |  | DS1 | 1521 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0696 | 697 |  | 1-3B-08 |  |  | L2 | ON | L2 (太鐵糠榔二路1521) DS-AS |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1521_DS | 1521(太鐵糠榔二路) DS | LINE161 | [5 empty] | 524 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D07 | 太鐵DS | 161 | 161kV | 1520 | 太鐵～槺榔二路(1520) |  | DS2 | 1522 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0698 | 699 |  | 1-3B-10 |  |  | L2 | ON | L2 (太鐵糠榔二路1522) DS-AS |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1522_DS | 1522(太鐵糠榔二路) DS | LINE161 | [5 empty] | 525 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1520 | 太鐵～槺榔二路(1520) |  | DS3 | 1523 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0700 | 701 |  | 1-3B-12 |  |  | L2 | ON | L2 (太鐵糠榔二路1523) DS-AS |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1523_DS | 1523(太鐵糠榔二路) DS | LINE161 | [5 empty] | 526 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1520 | 太鐵～槺榔二路(1520) |  | ES3 | 1523E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0702 | 703 |  | 1-3B-14 |  |  | L2 | ON | L2 (太鐵糠榔二路1523E) ES-AS |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1523E_ES | 1523E(太鐵糠榔二路) ES | LINE161 | [5 empty] | 527 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D07 | 太鐵DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | DS1 | 1531 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0704 | 705 |  | 1-3C-00 |  |  | L3 | ON | L3 (北回太鐵紅線1531) DS-AS |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1531_DS | 1531(北回太鐵紅線) DS | LINE161 | [5 empty] | 528 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | DS2 | 1532 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0706 | 707 |  | 1-3C-02 |  |  | L3 | ON | L3 (北回太鐵紅線1532) DS-AS |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1532_DS | 1532(北回太鐵紅線) DS | LINE161 | [5 empty] | 529 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D07 | 太鐵DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | DS3 | 1533 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0708 | 709 |  | 1-3C-04 |  |  | L3 | ON | L3 (北回太鐵紅線1533) DS-AS |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1533_DS | 1533(北回太鐵紅線) DS | LINE161 | [5 empty] | 530 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | ES3 | 1533E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0710 | 711 |  | 1-3C-06 |  |  | L3 | ON | L3 (北回太鐵紅線1533E) ES-AS |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1533E_ES | 1533E(北回太鐵紅線) ES | LINE161 | [5 empty] | 531 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D07 | 太鐵DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | DS1 | 1541 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0712 | 713 |  | 1-3C-08 |  |  | L4 | ON | L4 (北回太鐵白線1541) DS-AS |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1541_DS | 1541(北回太鐵白線) DS | LINE161 | [5 empty] | 532 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D07 | 太鐵DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | DS2 | 1542 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0714 | 715 |  | 1-3C-10 |  |  | L4 | ON | L4 (北回太鐵白線1542) DS-AS |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1542_DS | 1542(北回太鐵白線) DS | LINE161 | [5 empty] | 533 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | DS3 | 1543 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0716 | 717 |  | 1-3C-12 |  |  | L4 | ON | L4 (北回太鐵白線1543) DS-AS |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1543_DS | 1543(北回太鐵白線) DS | LINE161 | [5 empty] | 534 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | ES3 | 1543E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0718 | 719 |  | 1-3C-14 |  |  | L4 | ON | L4 (北回太鐵白線1543E) ES-AS |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1543E_ES | 1543E(北回太鐵白線) ES | LINE161 | [5 empty] | 535 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D07 | 太鐵DS | 161 | 161kV | 1550 | 後壁太鐵一路(1550) |  | DS1 | 1551 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0720 | 721 |  | 1-3D-00 |  |  | L5 | ON | L5 (後壁太鐵一路1551) DS-AS |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1551_DS | 1551(後壁太鐵一路) DS | LINE161 | [5 empty] | 536 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1550 | 後壁太鐵一路(1550) |  | DS2 | 1552 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0722 | 723 |  | 1-3D-02 |  |  | L5 | ON | L5 (後壁太鐵一路1552) DS-AS |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1552_DS | 1552(後壁太鐵一路) DS | LINE161 | [5 empty] | 537 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D07 | 太鐵DS | 161 | 161kV | 1550 | 後壁太鐵一路(1550) |  | DS3 | 1553 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0724 | 725 |  | 1-3D-04 |  |  | L5 | ON | L5 (後壁太鐵一路1553) DS-AS |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1553_DS | 1553(後壁太鐵一路) DS | LINE161 | [5 empty] | 538 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1550 | 後壁太鐵一路(1550) |  | ES3 | 1553E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0726 | 727 |  | 1-3D-06 |  |  | L5 | ON | L5 (後壁太鐵一路1553E) ES-AS |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1553E_ES | 1553E(後壁太鐵一路) ES | LINE161 | [5 empty] | 539 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D07 | 太鐵DS | 161 | 161kV | 1560 | 後壁太鐵二路(1560) |  | DS1 | 1561 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0728 | 729 |  | 1-3D-08 |  |  | L6 | ON | L6 (後壁太鐵二路1561) DS-AS |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1561_DS | 1561(後壁太鐵二路) DS | LINE161 | [5 empty] | 540 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D07 | 太鐵DS | 161 | 161kV | 1560 | 後壁太鐵二路(1560) |  | DS2 | 1562 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0730 | 731 |  | 1-3D-10 |  |  | L6 | ON | L6 (後壁太鐵二路1562) DS-AS |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1562_DS | 1562(後壁太鐵二路) DS | LINE161 | [5 empty] | 541 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1560 | 後壁太鐵二路(1560) |  | DS3 | 1563 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0732 | 733 |  | 1-3D-12 |  |  | L6 | ON | L6 (後壁太鐵二路1563) DS-AS |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1563_DS | 1563(後壁太鐵二路) DS | LINE161 | [5 empty] | 542 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1560 | 後壁太鐵二路(1560) |  | ES3 | 1563E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0734 | 735 |  | 1-3D-14 |  |  | L6 | ON | L6 (後壁太鐵二路1563E) ES-AS |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1563E_ES | 1563E(後壁太鐵二路) ES | LINE161 | [5 empty] | 543 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D07 | 太鐵DS | 161 | 161kV | 1950 | #1SHR(1950) |  | DS1 | 1951 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0768 | 769 |  | 2-30-00 |  |  | Locate Empty | ON | #1 SHR(1951) DS-AS |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1951_DS | 1951(161KV #1SHR) DS | OTHER | [5 empty] | 544 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1950 | #1SHR(1950) |  | DS2 | 1952 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0770 | 771 |  | 2-30-02 |  |  | Locate Empty | ON | #1 SHR(1952) DS-AS |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1952_DS | 1952(161KV #1SHR) DS | OTHER | [5 empty] | 545 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0784 | 785 |  | 2-31-00 |  |  | Locate Empty | ON | 161KV TIE (1501) DS-AS |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1501_DS | 1501(TIE) DS | TIE | [5 empty] | 546 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0786 | 787 |  | 2-31-02 |  |  | Locate Empty | ON | 161KV TIE (1502) DS-AS |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1502_DS | 1502(TIE) DS | TIE | [5 empty] | 547 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0788 | 789 |  | 2-31-04 |  |  | Locate Empty | ON | NO.1 DTR(1751) DS-AS |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1751_DS | 1751(#1DTR) DS | MTR | [5 empty] | 548 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0790 | 791 |  | 2-31-06 |  |  | Locate Empty | ON | NO.1 DTR(1752) DS-AS |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1752_DS | 1752(#1DTR) DS | MTR | [5 empty] | 549 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D07 | 太鐵DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0792 | 793 |  | 2-31-08 |  |  | Locate Empty | ON | NO.2 DTR(1761) DS-AS |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1761_DS | 1761(#2DTR) DS | MTR | [5 empty] | 550 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D07 | 太鐵DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0794 | 795 |  | 2-31-10 |  |  | Locate Empty | ON | NO.2 DTR(1762) DS-AS |  |  | B2/D07_A1 | [8 empty] | 太鐵DS.1762_DS | 1762(#2DTR) DS | MTR | [5 empty] | 551 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 11 | 11kV | LBS210 | #1SC(210) |  | LBS |  | Element | Status | 警報等級5動作5 | Normal/Alarm | Y | 5 | DI-SP |  | Bay1BbLBS | A/210 | C/1SC(B) |  |  | 0804 | 805 |  | 2-32-04 |  |  | SC1 | ON | SC-1 210 LBS LBS-AS |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.210_LBS | 210(11KV #1SC) LBS | SC | [5 empty] | 552 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm |  | 2 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 11 | 11kV | LBS230 | #3SC(230) |  | LBS |  | Element | Status | 警報等級5動作6 | Normal/Alarm | Y | 5 | DI-SP |  | Bay1BbLBS | A/230 | C/3SC(B) |  |  | 0808 | 809 |  | 2-32-08 |  |  | SC3 | ON | SC-3 230 LBS LBS-AS |  |  | B3/D07_A1 | [8 empty] | 太鐵DS.230_LBS | 230(11KV #3SC) LBS | SC | [5 empty] | 553 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm |  | 2 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 11 | 11kV | JV21 | 鐵21(JV21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0898 |  |  | 2-38-02 |  |  | F1 | USE/LOCK | F1鐵21 (JV21) 79 RY 79S |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV21_79UL | 11KV鐵21線(JV21) 79RY U/L | FEEDER | [5 empty] | 554 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 11 | 11kV | JV21 | 鐵21(JV21) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0899 |  |  | 2-38-03 |  |  | F1 | USE/LOCK | F1鐵21 (JV21) 51N TAP 51NS |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV21_LCO_TAP | 11KV鐵21線(JV21) LCO TAP | FEEDER | [5 empty] | 555 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D07 | 太鐵DS | 11 | 11kV | JV22 | 鐵22(JV22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0900 |  |  | 2-38-04 |  |  | F2 | USE/LOCK | F2鐵22 (JV22) 79 RY 79S |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV22_79UL | 11KV鐵22線(JV22) 79RY U/L | FEEDER | [5 empty] | 556 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 11 | 11kV | JV22 | 鐵22(JV22) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0901 |  |  | 2-38-05 |  |  | F2 | USE/LOCK | F2鐵22 (JV22) 51N TAP 51NS |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV22_LCO_TAP | 11KV鐵22線(JV22) LCO TAP | FEEDER | [5 empty] | 557 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D07 | 太鐵DS | 11 | 11kV | JV23 | 鐵23(JV23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0902 |  |  | 2-38-06 |  |  | F3 | USE/LOCK | F3鐵23 (JV23) 79 RY 79S |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV23_79UL | 11KV鐵23線(JV23) 79RY U/L | FEEDER | [5 empty] | 558 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 11 | 11kV | JV23 | 鐵23(JV23) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0903 |  |  | 2-38-07 |  |  | F3 | USE/LOCK | F3鐵23 (JV23) 51N TAP 51NS |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV23_LCO_TAP | 11KV鐵23線(JV23) LCO TAP | FEEDER | [5 empty] | 559 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D07 | 太鐵DS | 11 | 11kV | JV24 | 鐵24(JV24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0904 |  |  | 2-38-08 |  |  | F4 | USE/LOCK | F4鐵24 (JV24) 79 RY 79S |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV24_79UL | 11KV鐵24線(JV24) 79RY U/L | FEEDER | [5 empty] | 560 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 11 | 11kV | JV24 | 鐵24(JV24) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0905 |  |  | 2-38-09 |  |  | F4 | USE/LOCK | F4鐵24 (JV24) 51N TAP 51NS |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV24_LCO_TAP | 11KV鐵24線(JV24) LCO TAP | FEEDER | [5 empty] | 561 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D07 | 太鐵DS | 11 | 11kV | JV25 | 鐵25(JV25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0906 |  |  | 2-38-10 |  |  | F5 | USE/LOCK | F5鐵25 (JV25) 79 RY 79S |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV25_79UL | 11KV鐵25線(JV25) 79RY U/L | FEEDER | [5 empty] | 562 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 11 | 11kV | JV25 | 鐵25(JV25) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0907 |  |  | 2-38-11 |  |  | F5 | USE/LOCK | F5鐵25 (JV25) 51N TAP 51NS |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV25_LCO_TAP | 11KV鐵25線(JV25) LCO TAP | FEEDER | [5 empty] | 563 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D07 | 太鐵DS | 22 | 22kV | JV56 | 鐵56(JV56) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0908 |  |  | 2-38-12 |  |  | F6 | USE/LOCK | F6鐵56 (JV56) 79 RY 79S |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV56_79UL | 23KV鐵56線(JV56) 79RY U/L | FEEDER | [5 empty] | 564 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 22 | 22kV | JV56 | 鐵56(JV56) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0909 |  |  | 2-38-13 |  |  | F6 | USE/LOCK | F6鐵56 (JV56) 51N TAP 51NS |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV56_LCO_TAP | 23KV鐵56線(JV56) LCO TAP | FEEDER | [5 empty] | 565 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D07 | 太鐵DS | 22 | 22kV | JV57 | 鐵57(JV57) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0910 |  |  | 2-38-14 |  |  | F7 | USE/LOCK | F7鐵57 (JV57) 79 RY 79S |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV57_79UL | 23KV鐵57線(JV57) 79RY U/L | FEEDER |  | CDC_Mon2_DPC,DNP_DI_Mon2_DPC |  |  |  | 566 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 22 | 22kV | JV57 | 鐵57(JV57) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0911 |  |  | 2-38-15 |  |  | F7 | USE/LOCK | F7鐵57 (JV57) 51N TAP 51NS |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV57_LCO_TAP | 23KV鐵57線(JV57) LCO TAP | FEEDER |  | CDC_Mon2_DPC,DNP_DI_Mon2_DPC |  |  |  | 567 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D07 | 太鐵DS | 22 | 22kV | JV58 | 鐵58(JV58) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0912 |  |  | 2-39-00 |  |  | F8 | USE/LOCK | F8鐵58 (JV58) 79 RY 79S |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV58_79UL | 23KV鐵58線(JV58) 79RY U/L | FEEDER |  | CDC_Mon2_DPC,DNP_DI_Mon2_DPC |  |  |  | 568 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 22 | 22kV | JV58 | 鐵58(JV58) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0913 |  |  | 2-39-01 |  |  | F8 | USE/LOCK | F8鐵58 (JV58) 51N TAP 51NS |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV58_LCO_TAP | 23KV鐵58線(JV58) LCO TAP | FEEDER |  | CDC_Mon2_DPC,DNP_DI_Mon2_DPC |  |  |  | 569 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D07 | 太鐵DS | 22 | 22kV | JV59 | 鐵59(JV59) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0914 |  |  | 2-39-02 |  |  | F9 | USE/LOCK | F9鐵59 (JV59) 79 RY 79S |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV59_79UL | 23KV鐵59線(JV59) 79RY U/L | FEEDER | [5 empty] | 570 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 22 | 22kV | JV59 | 鐵59(JV59) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0915 |  |  | 2-39-03 |  |  | F9 | USE/LOCK | F9鐵59 (JV59) 51N TAP 51NS |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV59_LCO_TAP | 23KV鐵59線(JV59) LCO TAP | FEEDER | [5 empty] | 571 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D07 | 太鐵DS | 22 | 22kV | JV60 | 鐵60(JV60) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0916 |  |  | 2-39-04 |  |  | F10 | USE/LOCK | F10鐵60 (JV60) 79 RY 79S |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV60_79UL | 23KV鐵60線(JV60) 79RY U/L | FEEDER | [5 empty] | 572 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 22 | 22kV | JV60 | 鐵60(JV60) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0917 |  |  | 2-39-05 |  |  | F10 | USE/LOCK | F10鐵60 (JV60) 51N TAP 51NS |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV60_LCO_TAP | 23KV鐵60線(JV60) LCO TAP | FEEDER | [5 empty] | 573 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D07 | 太鐵DS | 11 | 11kV | JV31 | 鐵31(JV31) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0920 |  |  | 2-39-08 |  |  | F11 | USE/LOCK | F11鐵31 (JV31) 79 RY 79S |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV31_79UL | 11KV鐵31線(JV31) 79RY U/L | FEEDER | [5 empty] | 574 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 11 | 11kV | JV31 | 鐵31(JV31) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0921 |  |  | 2-39-09 |  |  | F11 | USE/LOCK | F11鐵31 (JV31) 51N TAP 51NS |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV31_LCO_TAP | 11KV鐵31線(JV31) LCO TAP | FEEDER | [5 empty] | 575 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D07 | 太鐵DS | 11 | 11kV | JV32 | 鐵32(JV32) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0922 |  |  | 2-39-10 |  |  | F12 | USE/LOCK | F12鐵32 (JV32) 79 RY 79S |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV32_79UL | 11KV鐵32線(JV32) 79RY U/L | FEEDER | [5 empty] | 576 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 11 | 11kV | JV32 | 鐵32(JV32) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0923 |  |  | 2-39-11 |  |  | F12 | USE/LOCK | F12鐵32 (JV32) 51N TAP 51NS |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV32_LCO_TAP | 11KV鐵32線(JV32) LCO TAP | FEEDER | [5 empty] | 577 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D07 | 太鐵DS | 11 | 11kV | JV33 | 鐵33(JV33) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0924 |  |  | 2-39-12 |  |  | F13 | USE/LOCK | F13鐵33 (JV33) 79 RY 79S |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV33_79UL | 11KV鐵33線(JV33) 79RY U/L | FEEDER | [5 empty] | 578 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 11 | 11kV | JV33 | 鐵33(JV33) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0925 |  |  | 2-39-13 |  |  | F13 | USE/LOCK | F13鐵33 (JV33) 51N TAP 51NS |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV33_LCO_TAP | 11KV鐵33線(JV33) LCO TAP | FEEDER | [5 empty] | 579 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D07 | 太鐵DS | 11 | 11kV | JV34 | 鐵34(JV34) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0926 |  |  | 2-39-14 |  |  | F14 | USE/LOCK | F14鐵33 (JV34) 79 RY 79S |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV34_79UL | 11KV鐵34線(JV34) 79RY U/L | FEEDER |  | CDC_Mon2_DPC,DNP_DI_Mon2_DPC |  |  |  | 580 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 11 | 11kV | JV34 | 鐵34(JV34) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0927 |  |  | 2-39-15 |  |  | F14 | USE/LOCK | F14鐵33 (JV34) 51N TAP 51NS |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV34_LCO_TAP | 11KV鐵34線(JV34) LCO TAP | FEEDER |  | CDC_Mon2_DPC,DNP_DI_Mon2_DPC |  |  |  | 581 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D07 | 太鐵DS | 11 | 11kV | JV35 | 鐵35(JV35) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0928 |  |  | 2-3A-00 |  |  | F15 | USE/LOCK | F15鐵35 (JV35) 79 RY 79S |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV35_79UL | 11KV鐵35線(JV35) 79RY U/L | FEEDER |  | CDC_Mon2_DPC,DNP_DI_Mon2_DPC |  |  |  | 582 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 11 | 11kV | JV35 | 鐵35(JV35) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0929 |  |  | 2-3A-01 |  |  | F15 | USE/LOCK | F15鐵35 (JV35) 51N TAP 51NS |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV35_LCO_TAP | 11KV鐵35線(JV35) LCO TAP | FEEDER |  | CDC_Mon2_DPC,DNP_DI_Mon2_DPC |  |  |  | 583 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D07 | 太鐵DS | 22 | 22kV | JV66 | 鐵66(JV66) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0930 |  |  | 2-3A-02 |  |  | F16 | USE/LOCK | F16鐵66 (JV66) 79 RY 79S |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV66_79UL | 23KV鐵66線(JV66) 79RY U/L | FEEDER |  | CDC_Mon2_DPC,DNP_DI_Mon2_DPC |  |  |  | 584 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 22 | 22kV | JV66 | 鐵66(JV66) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0931 |  |  | 2-3A-03 |  |  | F16 | USE/LOCK | F16鐵66 (JV66) 51N TAP 51NS |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV66_LCO_TAP | 23KV鐵66線(JV66) LCO TAP | FEEDER |  | CDC_Mon2_DPC,DNP_DI_Mon2_DPC |  |  |  | 585 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D07 | 太鐵DS | 22 | 22kV | JV67 | 鐵67(JV67) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0932 |  |  | 2-3A-04 |  |  | F17 | USE/LOCK | F17鐵67 (JV67) 79 RY 79S |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV67_79UL | 23KV鐵67線(JV67) 79RY U/L | FEEDER |  | CDC_Mon2_DPC,DNP_DI_Mon2_DPC |  |  |  | 586 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 22 | 22kV | JV67 | 鐵67(JV67) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0933 |  |  | 2-3A-05 |  |  | F17 | USE/LOCK | F17鐵67 (JV67) 51N TAP 51NS |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV67_LCO_TAP | 23KV鐵67線(JV67) LCO TAP | FEEDER |  | CDC_Mon2_DPC,DNP_DI_Mon2_DPC |  |  |  | 587 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D07 | 太鐵DS | 22 | 22kV | JV68 | 鐵68(JV68) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0934 |  |  | 2-3A-06 |  |  | F18 | USE/LOCK | F18鐵68 (JV68) 79 RY 79S |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV68_79UL | 23KV鐵68線(JV68) 79RY U/L | FEEDER |  | CDC_Mon2_DPC,DNP_DI_Mon2_DPC |  |  |  | 588 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 22 | 22kV | JV68 | 鐵68(JV68) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0935 |  |  | 2-3A-07 |  |  | F18 | USE/LOCK | F18鐵68 (JV68) 51N TAP 51NS |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV68_LCO_TAP | 23KV鐵68線(JV68) LCO TAP | FEEDER |  | CDC_Mon2_DPC,DNP_DI_Mon2_DPC |  |  |  | 589 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D07 | 太鐵DS | 22 | 22kV | JV69 | 鐵69(JV69) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0936 |  |  | 2-3A-08 |  |  | F19 | USE/LOCK | F19鐵69 (JV69) 79 RY 79S |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV69_79UL | 23KV鐵69線(JV69) 79RY U/L | FEEDER |  | CDC_Mon2_DPC,DNP_DI_Mon2_DPC |  |  |  | 590 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 22 | 22kV | JV69 | 鐵69(JV69) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0937 |  |  | 2-3A-09 |  |  | F19 | USE/LOCK | F19鐵69 (JV69) 51N TAP 51NS |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV69_LCO_TAP | 23KV鐵69線(JV69) LCO TAP | FEEDER |  | CDC_Mon2_DPC,DNP_DI_Mon2_DPC |  |  |  | 591 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D07 | 太鐵DS | 22 | 22kV | JV70 | 鐵70(JV70) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0938 |  |  | 2-3A-10 |  |  | F20 | USE/LOCK | F20鐵70 (JV70) 79 RY 79S |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV70_79UL | 23KV鐵70線(JV70) 79RY U/L | FEEDER | [5 empty] | 592 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS | 22 | 22kV | JV70 | 鐵70(JV70) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0939 |  |  | 2-3A-11 |  |  | F20 | USE/LOCK | F20鐵70 (JV70) 51N TAP 51NS |  |  | B2/D07_D1 | [8 empty] | 太鐵DS.JV70_LCO_TAP | 23KV鐵70線(JV70) LCO TAP | FEEDER | [5 empty] | 593 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D07 | 太鐵DS |  |  | 1DTR | #1DTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0976 |  |  | 2-3D-00 |  |  | #1DTR | USE/LOCK | #1DTR. #1 87RY U/L |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#1DTR_87UL1 | #1DTR #1 87RY U/L | OTHER | [5 empty] | 594 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS |  |  | 1DTR | #1DTR |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0977 |  |  | 2-3D-01 |  |  | #1DTR | USE/LOCK | #1DTR. #2 87RY U/L |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#1DTR_87UL2 | #1DTR #2 87RY U/L | OTHER | [5 empty] | 595 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS |  |  | 1DTR | #1DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0978 |  |  | 2-3D-02 |  |  | #1DTR | USE/LOCK | #1DTR. 51Z U/L |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#1DTR_51ZUL | #1DTR 51ZRY U/L | OTHER | [5 empty] | 596 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS |  |  | 1DTR | #1DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0979 |  |  | 2-3D-03 |  |  | #1DTR | USE/LOCK | #1DTR. 數位電驛故障 |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#1DTR_RYFA | #1DTR數位電驛故障 | OTHER | [5 empty] | 597 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D07 | 太鐵DS |  |  | 2DTR | #2DTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0980 |  |  | 2-3D-04 |  |  | #2DTR | USE/LOCK | #2DTR. #1 87RY U/L |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#2DTR_87UL1 | #2DTR #1 87RY U/L | OTHER | [5 empty] | 598 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS |  |  | 2DTR | #2DTR |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0981 |  |  | 2-3D-05 |  |  | #2DTR | USE/LOCK | #2DTR. #2 87RY U/L |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#2DTR_87UL2 | #2DTR #2 87RY U/L | OTHER | [5 empty] | 599 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS |  |  | 2DTR | #2DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0982 |  |  | 2-3D-06 |  |  | #2DTR | USE/LOCK | #2DTR. 51Z U/L |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#2DTR_51ZUL | #2DTR 51ZRY U/L | OTHER | [5 empty] | 600 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D07 | 太鐵DS |  |  | 2DTR | #2DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0983 |  |  | 2-3D-07 |  |  | #2DTR | USE/LOCK | #2DTR. 數位電驛故障 |  |  | B1/D07_A1 | [8 empty] | 太鐵DS.#2DTR_RYFA | #2DTR數位電驛故障 | OTHER | [5 empty] | 601 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
D07 | 太鐵DS | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/D07_A1 | [12 empty] | 太鐵DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: D07/161/1BUS/V; OPRD2: D07/161/2BUS/V
D07 | 太鐵DS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/D07_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: D07/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
D07 | 太鐵DS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/D07_A1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_6 | OPRD1: D07/161/1510/MW; OPRD2: D07/161/1520/MW; OPRD3: D07/161/1530/MW; OPRD4: D07/161/1540/MW; OPRD5: D07/161/1550/MW; OPRD6: D07/161/1560/MW
D07 | 太鐵DS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/D07_A1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: D07/0/CalcPoint/OPRN2_MW
D07 | 太鐵DS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/D07_A1 | [17 empty] | none
D07 | 太鐵DS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/D07_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: D07/0/CalcPoint/OPRN1; OPRD2: D07/0/CalcPoint/OPRN2; OPRD3: D07/0/CalcPoint/PRFL_UL
D07 | 太鐵DS |  |  | 1DTR | 1DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D07_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D07/11/310/I_R; OPRD2: D07/22/320/I_R
D07 | 太鐵DS |  |  | 1DTR | 1DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D07_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D07/11/310/I_S; OPRD2: D07/22/320/I_S
D07 | 太鐵DS |  |  | 1DTR | 1DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D07_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D07/11/310/I_T; OPRD2: D07/22/320/I_T
D07 | 太鐵DS |  |  | 2DTR | 2DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D07_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D07/11/330/I_R; OPRD2: D07/22/340/I_R
D07 | 太鐵DS |  |  | 2DTR | 2DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D07_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D07/11/330/I_S; OPRD2: D07/22/340/I_S
D07 | 太鐵DS |  |  | 2DTR | 2DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D07_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D07/11/330/I_T; OPRD2: D07/22/340/I_T
D07 | 太鐵DS | 161 | 161kV | 1510 | 太鐵～槺榔一路(1510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D07_A1 | [12 empty] | 太鐵DS.1510_AMP | 太鐵糠榔一路 AMP | LINE161 | AMP_CAL | C20R1930 | amp_cal | OPRD1: D07/161/1510/MW; OPRD2: D07/161/1510/MVAR; OPRD3: D07/0/CalcPoint/Vbs4
D07 | 太鐵DS | 161 | 161kV | 1520 | 太鐵～槺榔二路(1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D07_A1 | [12 empty] | 太鐵DS.1520_AMP | 太鐵糠榔二路 AMP | LINE161 | AMP_CAL | C20R1930 | amp_cal | OPRD1: D07/161/1520/MW; OPRD2: D07/161/1520/MVAR; OPRD3: D07/0/CalcPoint/Vbs4
D07 | 太鐵DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D07_A1 | [12 empty] | 太鐵DS.1530_AMP | 北回太鐵紅線 AMP | LINE161 | AMP_CAL | C20R1930 | amp_cal | OPRD1: D07/161/1530/MW; OPRD2: D07/161/1530/MVAR; OPRD3: D07/0/CalcPoint/Vbs4
D07 | 太鐵DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D07_A1 | [12 empty] | 太鐵DS.1540_AMP | 北回太鐵白線 AMP | LINE161 | AMP_CAL | C20R1930 | amp_cal | OPRD1: D07/161/1540/MW; OPRD2: D07/161/1540/MVAR; OPRD3: D07/0/CalcPoint/Vbs4
D07 | 太鐵DS | 161 | 161kV | 1550 | 後壁太鐵一路(1550) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D07_A1 | [12 empty] | 太鐵DS.1550_AMP | 後壁太鐵一路 AMP | LINE161 | AMP_CAL | C20R1000 | amp_cal | OPRD1: D07/161/1550/MW; OPRD2: D07/161/1550/MVAR; OPRD3: D07/0/CalcPoint/Vbs4
D07 | 太鐵DS | 161 | 161kV | 1560 | 後壁太鐵二路(1560) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D07_A1 | [12 empty] | 太鐵DS.1560_AMP | 後壁太鐵二路 AMP | LINE161 | AMP_CAL | C20R1000 | amp_cal | OPRD1: D07/161/1560/MW; OPRD2: D07/161/1560/MVAR; OPRD3: D07/0/CalcPoint/Vbs4
D07 | 太鐵DS | 11 | 11kV | 1ABUS | #1ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D07_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D07/11/1ABUS/V
D07 | 太鐵DS | 11 | 11kV | 2ABUS | #2ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D07_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D07/11/2ABUS/V
D07 | 太鐵DS | 22 | 22kV | 1BBUS | #1BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D07_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D07/22/1BBUS/V
D07 | 太鐵DS | 22 | 22kV | 2BBUS | #2BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D07_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D07/22/2BBUS/V
D07 | 太鐵DS |  |  | 1DTR(A) | #1DTR(A) |  | TR_PERM | [9 empty] | B1/D07_A1 | [12 empty] | 太鐵DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D07//1DTR(A)/SupLocal; OPRD2: D07//1DTR(A)/Tap Chan
D07 | 太鐵DS |  |  | 1DTR(B) | #1DTR(B) |  | TR_PERM | [9 empty] | B1/D07_A1 | [12 empty] | 太鐵DS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D07//1DTR(B)/SupLocal; OPRD2: D07//1DTR(B)/Tap Chan
D07 | 太鐵DS |  |  | 2DTR(A) | #2DTR(A) |  | TR_PERM | [9 empty] | B1/D07_A1 | [12 empty] | 太鐵DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D07//2DTR(A)/SupLocal; OPRD2: D07//2DTR(A)/Tap Chan
D07 | 太鐵DS |  |  | 2DTR(B) | #2DTR(B) |  | TR_PERM | [9 empty] | B1/D07_A1 | [12 empty] | 太鐵DS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D07//2DTR(B)/SupLocal; OPRD2: D07//2DTR(B)/Tap Chan
D07 | 太鐵DS | 11 | 11kV | JV21 | 鐵21(JV21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D07/11/1ABUS/V; OPRD2: D07/11/JV21/I_R; OPRD3: D07/11/JV21/I_S; OPRD4: D07/11/JV21/I_T
D07 | 太鐵DS | 11 | 11kV | JV22 | 鐵22(JV22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D07/11/1ABUS/V; OPRD2: D07/11/JV22/I_R; OPRD3: D07/11/JV22/I_S; OPRD4: D07/11/JV22/I_T
D07 | 太鐵DS | 11 | 11kV | JV23 | 鐵23(JV23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D07/11/1ABUS/V; OPRD2: D07/11/JV23/I_R; OPRD3: D07/11/JV23/I_S; OPRD4: D07/11/JV23/I_T
D07 | 太鐵DS | 11 | 11kV | JV24 | 鐵24(JV24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D07/11/1ABUS/V; OPRD2: D07/11/JV24/I_R; OPRD3: D07/11/JV24/I_S; OPRD4: D07/11/JV24/I_T
D07 | 太鐵DS | 11 | 11kV | JV25 | 鐵25(JV25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D07/11/1ABUS/V; OPRD2: D07/11/JV25/I_R; OPRD3: D07/11/JV25/I_S; OPRD4: D07/11/JV25/I_T
D07 | 太鐵DS | 11 | 11kV | JV31 | 鐵31(JV31) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D07/11/2ABUS/V; OPRD2: D07/11/JV31/I_R; OPRD3: D07/11/JV31/I_S; OPRD4: D07/11/JV31/I_T
D07 | 太鐵DS | 11 | 11kV | JV32 | 鐵32(JV32) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D07/11/2ABUS/V; OPRD2: D07/11/JV32/I_R; OPRD3: D07/11/JV32/I_S; OPRD4: D07/11/JV32/I_T
D07 | 太鐵DS | 11 | 11kV | JV33 | 鐵33(JV33) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D07/11/2ABUS/V; OPRD2: D07/11/JV33/I_R; OPRD3: D07/11/JV33/I_S; OPRD4: D07/11/JV33/I_T
D07 | 太鐵DS | 11 | 11kV | JV34 | 鐵34(JV34) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D07/11/2ABUS/V; OPRD2: D07/11/JV34/I_R; OPRD3: D07/11/JV34/I_S; OPRD4: D07/11/JV34/I_T
D07 | 太鐵DS | 11 | 11kV | JV35 | 鐵35(JV35) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D07/11/2ABUS/V; OPRD2: D07/11/JV35/I_R; OPRD3: D07/11/JV35/I_S; OPRD4: D07/11/JV35/I_T
D07 | 太鐵DS | 22 | 22kV | JV56 | 鐵56(JV56) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D07/22/1BBUS/V; OPRD2: D07/22/JV56/I_R; OPRD3: D07/22/JV56/I_S; OPRD4: D07/22/JV56/I_T
D07 | 太鐵DS | 22 | 22kV | JV57 | 鐵57(JV57) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D07/22/1BBUS/V; OPRD2: D07/22/JV57/I_R; OPRD3: D07/22/JV57/I_S; OPRD4: D07/22/JV57/I_T
D07 | 太鐵DS | 22 | 22kV | JV58 | 鐵58(JV58) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D07/22/1BBUS/V; OPRD2: D07/22/JV58/I_R; OPRD3: D07/22/JV58/I_S; OPRD4: D07/22/JV58/I_T
D07 | 太鐵DS | 22 | 22kV | JV59 | 鐵59(JV59) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D07/22/1BBUS/V; OPRD2: D07/22/JV59/I_R; OPRD3: D07/22/JV59/I_S; OPRD4: D07/22/JV59/I_T
D07 | 太鐵DS | 22 | 22kV | JV60 | 鐵60(JV60) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D07/22/1BBUS/V; OPRD2: D07/22/JV60/I_R; OPRD3: D07/22/JV60/I_S; OPRD4: D07/22/JV60/I_T
D07 | 太鐵DS | 22 | 22kV | JV66 | 鐵66(JV66) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D07/22/2BBUS/V; OPRD2: D07/22/JV66/I_R; OPRD3: D07/22/JV66/I_S; OPRD4: D07/22/JV66/I_T
D07 | 太鐵DS | 22 | 22kV | JV67 | 鐵67(JV67) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D07/22/2BBUS/V; OPRD2: D07/22/JV67/I_R; OPRD3: D07/22/JV67/I_S; OPRD4: D07/22/JV67/I_T
D07 | 太鐵DS | 22 | 22kV | JV68 | 鐵68(JV68) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D07/22/2BBUS/V; OPRD2: D07/22/JV68/I_R; OPRD3: D07/22/JV68/I_S; OPRD4: D07/22/JV68/I_T
D07 | 太鐵DS | 22 | 22kV | JV69 | 鐵69(JV69) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D07/22/2BBUS/V; OPRD2: D07/22/JV69/I_R; OPRD3: D07/22/JV69/I_S; OPRD4: D07/22/JV69/I_T
D07 | 太鐵DS | 22 | 22kV | JV70 | 鐵70(JV70) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D07/22/2BBUS/V; OPRD2: D07/22/JV70/I_R; OPRD3: D07/22/JV70/I_S; OPRD4: D07/22/JV70/I_T
D07 | 太鐵DS | 11 | 11kV | JV21 | 鐵21(JV21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D07/11/JV21/kVA; OPRD2: D07/11/JV21/KVAR
D07 | 太鐵DS | 11 | 11kV | JV22 | 鐵22(JV22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D07/11/JV22/kVA; OPRD2: D07/11/JV22/KVAR
D07 | 太鐵DS | 11 | 11kV | JV23 | 鐵23(JV23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D07/11/JV23/kVA; OPRD2: D07/11/JV23/KVAR
D07 | 太鐵DS | 11 | 11kV | JV24 | 鐵24(JV24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D07/11/JV24/kVA; OPRD2: D07/11/JV24/KVAR
D07 | 太鐵DS | 11 | 11kV | JV25 | 鐵25(JV25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D07/11/JV25/kVA; OPRD2: D07/11/JV25/KVAR
D07 | 太鐵DS | 11 | 11kV | JV31 | 鐵31(JV31) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D07/11/JV31/kVA; OPRD2: D07/11/JV31/KVAR
D07 | 太鐵DS | 11 | 11kV | JV32 | 鐵32(JV32) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D07/11/JV32/kVA; OPRD2: D07/11/JV32/KVAR
D07 | 太鐵DS | 11 | 11kV | JV33 | 鐵33(JV33) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D07/11/JV33/kVA; OPRD2: D07/11/JV33/KVAR
D07 | 太鐵DS | 11 | 11kV | JV34 | 鐵34(JV34) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D07/11/JV34/kVA; OPRD2: D07/11/JV34/KVAR
D07 | 太鐵DS | 11 | 11kV | JV35 | 鐵35(JV35) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D07/11/JV35/kVA; OPRD2: D07/11/JV35/KVAR
D07 | 太鐵DS | 22 | 22kV | JV56 | 鐵56(JV56) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D07/22/JV56/kVA; OPRD2: D07/22/JV56/KVAR
D07 | 太鐵DS | 22 | 22kV | JV57 | 鐵57(JV57) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D07/22/JV57/kVA; OPRD2: D07/22/JV57/KVAR
D07 | 太鐵DS | 22 | 22kV | JV58 | 鐵58(JV58) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D07/22/JV58/kVA; OPRD2: D07/22/JV58/KVAR
D07 | 太鐵DS | 22 | 22kV | JV59 | 鐵59(JV59) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D07/22/JV59/kVA; OPRD2: D07/22/JV59/KVAR
D07 | 太鐵DS | 22 | 22kV | JV60 | 鐵60(JV60) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D07/22/JV60/kVA; OPRD2: D07/22/JV60/KVAR
D07 | 太鐵DS | 22 | 22kV | JV66 | 鐵66(JV66) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D07/22/JV66/kVA; OPRD2: D07/22/JV66/KVAR
D07 | 太鐵DS | 22 | 22kV | JV67 | 鐵67(JV67) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D07/22/JV67/kVA; OPRD2: D07/22/JV67/KVAR
D07 | 太鐵DS | 22 | 22kV | JV68 | 鐵68(JV68) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D07/22/JV68/kVA; OPRD2: D07/22/JV68/KVAR
D07 | 太鐵DS | 22 | 22kV | JV69 | 鐵69(JV69) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D07/22/JV69/kVA; OPRD2: D07/22/JV69/KVAR
D07 | 太鐵DS | 22 | 22kV | JV70 | 鐵70(JV70) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D07_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D07/22/JV70/kVA; OPRD2: D07/22/JV70/KVAR
D07 | 太鐵DS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D07_A1 | [12 empty] | 太鐵DS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D07/11/210/CB; OPRD2: 6.9; OPRD3: 0
D07 | 太鐵DS | 11 | 11kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D07_A1 | [12 empty] | 太鐵DS.230_SC_MVAR | 11KV#3SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D07/11/230/CB; OPRD2: 6.9; OPRD3: 0
D07 | 太鐵DS | 22 | 22kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D07_A1 | [12 empty] | 太鐵DS.220_SC_MVAR | 23KV#2SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D07/22/220/CB; OPRD2: 13.8; OPRD3: 0
D07 | 太鐵DS | 22 | 22kV | 240 | #4SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D07_A1 | [12 empty] | 太鐵DS.240_SC_MVAR | 23KV#4SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D07/22/240/CB; OPRD2: 13.8; OPRD3: 0
D07 | 太鐵DS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/D07_A1 | [12 empty] | 太鐵DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_10 |  | com_alarm_30 | D07//1DTR/GDA | D07//1DTR/PHA | D07//1DTR/96D | D07//1DTR/TRA | D07//1DTR/63Q | D07//1DTR/96B2 | D07//1DTR/96B1 | D07//1DTR/87A | D07//1DTR/51ZA | D07//1DTR/96PA | D07//2DTR/63Q | D07//2DTR/TRA | D07//2DTR/96D | D07//2DTR/96B1 | D07//2DTR/96B2 | D07//2DTR/GDA | D07//2DTR/51ZA | D07//2DTR/PHA | D07//2DTR/87A | D07//2DTR/96PA | D07/11/310/PHA | D07/11/310/GDA | D07/11/330/PHA | D07/11/330/GDA | D07/161/1BUS/87A | D07/161/2BUS/87A | D07/22/320/GDA | D07/22/320/PHA | D07/22/340/GDA | D07/22/340/PHA
D07 | 太鐵DS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/D07_A1 | [12 empty] | 太鐵DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | STATION_FAULT_2 |  | com_alarm_2 | OPRD1: D07//1DTR/TRF; OPRD2: D07//2DTR/TRF
D07 | 太鐵DS | 161 | 161kV | 1750_D1 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D07_D1 | [17 empty] | lamp2CC | OPRD1: D07/161/1750/CB
D07 | 太鐵DS | 11 | 11kV | 310_D1 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D07_D1 | [17 empty] | lamp2CC | OPRD1: D07/11/310/CB
D07 | 太鐵DS | 22 | 22kV | 320_D1 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D07_D1 | [17 empty] | lamp2CC | OPRD1: D07/22/320/CB
D07 | 太鐵DS | 161 | 161kV | 1760_D1 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D07_D1 | [17 empty] | lamp2CC | OPRD1: D07/161/1760/CB
D07 | 太鐵DS | 11 | 11kV | 330_D1 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D07_D1 | [17 empty] | lamp2CC | OPRD1: D07/11/330/CB
D07 | 太鐵DS | 22 | 22kV | 340_D1 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D07_D1 | [17 empty] | lamp2CC | OPRD1: D07/22/340/CB
D07 | 太鐵DS | 0 |  | RTU_D1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/D07_D1 | [17 empty] | lamp2CC | OPRD1: D07/0/RTU/RTU_R_L
D07 | 太鐵DS | 0 |  | StaDev_D1 | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/D07_D1 | [17 empty] | lamp2CC | OPRD1: D07/0/StaDev/STUV
D07 | 太鐵DS | 0 |  | StaDev_D1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D07_D1 | [17 empty] | lamp2CC | OPRD1: D07/0/StaDev/DCA
D07 | 太鐵DS | 0 |  | StaDev_D1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D07_D1 | [17 empty] | lamp2CC | OPRD1: D07/0/StaDev/DCE
D07 | 太鐵DS | 0 |  | StaDev_D1 | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D07_D1 | [17 empty] | lamp2CC | OPRD1: D07/0/StaDev/PMA

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D07 | 太鐵DS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | D07/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
D07 | 太鐵DS | 161 | 161kV | 1510 | 太鐵糠榔一路(1510) |  | I | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.1510_AMP | 太鐵糠榔一路 AMP | LINE161 | D07/161/1510/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C20R1930 | 1737.800049 | 1737.800049 | 1930.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D07 | 太鐵DS | 161 | 161kV | 1520 | 太鐵糠榔二路(1520) |  | I | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.1520_AMP | 太鐵糠榔二路 AMP | LINE161 | D07/161/1520/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C20R1930 | 1737.800049 | 1737.800049 | 1930.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D07 | 太鐵DS | 161 | 161kV | 1530 | 北回太鐵紅線(1530) |  | I | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.1530_AMP | 北回太鐵紅線 AMP | LINE161 | D07/161/1530/I |  | AMP_CAL |  |  | 5 | CalcAIPoint | [21 empty] | C20R1930 | 1737.800049 | 1737.800049 | 1930.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D07 | 太鐵DS | 161 | 161kV | 1540 | 北回太鐵白線(1540) |  | I | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.1540_AMP | 北回太鐵白線 AMP | LINE161 | D07/161/1540/I |  | AMP_CAL |  |  | 6 | CalcAIPoint | [21 empty] | C20R1930 | 1737.800049 | 1737.800049 | 1930.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D07 | 太鐵DS | 161 | 161kV | 1550 | 後壁太鐵一路(1550) |  | I | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.1550_AMP | 後壁太鐵一路 AMP | LINE161 | D07/161/1550/I |  | AMP_CAL |  |  | 7 | CalcAIPoint | [21 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D07 | 太鐵DS | 161 | 161kV | 1560 | 後壁太鐵二路(1560) |  | I | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.1560_AMP | 後壁太鐵二路 AMP | LINE161 | D07/161/1560/I |  | AMP_CAL |  |  | 8 | CalcAIPoint | [21 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵21線KVA | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵21線KVA | 11KV鐵21線KVA | FEEDER |  |  | KVA_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵21線KW | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵21線KW | 11KV鐵21線KW | FEEDER |  |  | KW_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵22線KVA | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵22線KVA | 11KV鐵22線KVA | FEEDER |  |  | KVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵22線KW | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵22線KW | 11KV鐵22線KW | FEEDER |  |  | KW_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵23線KVA | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵23線KVA | 11KV鐵23線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵23線KW | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵23線KW | 11KV鐵23線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵24線KVA | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵24線KVA | 11KV鐵24線KVA | FEEDER |  |  | KVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵24線KW | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵24線KW | 11KV鐵24線KW | FEEDER |  |  | KW_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵25線KVA | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵25線KVA | 11KV鐵25線KVA | FEEDER |  |  | KVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵25線KW | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵25線KW | 11KV鐵25線KW | FEEDER |  |  | KW_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵31線KVA | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵31線KVA | 11KV鐵31線KVA | FEEDER |  |  | KVA_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵31線KW | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵31線KW | 11KV鐵31線KW | FEEDER |  |  | KW_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵32線KVA | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵32線KVA | 11KV鐵32線KVA | FEEDER |  |  | KVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵32線KW | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵32線KW | 11KV鐵32線KW | FEEDER |  |  | KW_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵33線KVA | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵33線KVA | 11KV鐵33線KVA | FEEDER |  |  | KVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵33線KW | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵33線KW | 11KV鐵33線KW | FEEDER |  |  | KW_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵34線KVA | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵34線KVA | 11KV鐵34線KVA | FEEDER |  |  | KVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵34線KW | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵34線KW | 11KV鐵34線KW | FEEDER |  |  | KW_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵35線KVA | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵35線KVA | 11KV鐵35線KVA | FEEDER |  |  | KVA_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵35線KW | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵35線KW | 11KV鐵35線KW | FEEDER |  |  | KW_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵56線KVA | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵56線KVA | 23KV鐵56線KVA | FEEDER |  |  | KVA_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵56線KW | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵56線KW | 23KV鐵56線KW | FEEDER |  |  | KW_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵57線KVA | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵57線KVA | 23KV鐵57線KVA | FEEDER |  |  | KVA_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵57線KW | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵57線KW | 23KV鐵57線KW | FEEDER |  |  | KW_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵58線KVA | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵58線KVA | 23KV鐵58線KVA | FEEDER |  |  | KVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵58線KW | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵58線KW | 23KV鐵58線KW | FEEDER |  |  | KW_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵59線KVA | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵59線KVA | 23KV鐵59線KVA | FEEDER |  |  | KVA_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵59線KW | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵59線KW | 23KV鐵59線KW | FEEDER |  |  | KW_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵60線KVA | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵60線KVA | 23KV鐵60線KVA | FEEDER |  |  | KVA_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵60線KW | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵60線KW | 23KV鐵60線KW | FEEDER |  |  | KW_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵66線KVA | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵66線KVA | 23KV鐵66線KVA | FEEDER |  |  | KVA_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵66線KW | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵66線KW | 23KV鐵66線KW | FEEDER |  |  | KW_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵67線KVA | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵67線KVA | 23KV鐵67線KVA | FEEDER |  |  | KVA_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵67線KW | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵67線KW | 23KV鐵67線KW | FEEDER |  |  | KW_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵68線KVA | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵68線KVA | 23KV鐵68線KVA | FEEDER |  |  | KVA_CAL |  |  | 43 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵68線KW | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵68線KW | 23KV鐵68線KW | FEEDER |  |  | KW_CAL |  |  | 44 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵69線KVA | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵69線KVA | 23KV鐵69線KVA | FEEDER |  |  | KVA_CAL |  |  | 45 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵69線KW | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵69線KW | 23KV鐵69線KW | FEEDER |  |  | KW_CAL |  |  | 46 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵70線KVA | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵70線KVA | 23KV鐵70線KVA | FEEDER |  |  | KVA_CAL |  |  | 47 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  |  |  |  | 鐵70線KW | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.鐵70線KW | 23KV鐵70線KW | FEEDER |  |  | KW_CAL |  |  | 48 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.#1DTR(A)_MVA | #1DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 49 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D07 | 太鐵DS | 0 |  | 1DTR(A) | #1DTR(A) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.#1DTR(A)_LOAD | #1DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 50 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D07 | 太鐵DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PF | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.#1DTR(A)_PF | #1DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 51 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D07 | 太鐵DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.#1DTR(B)_MVA | #1DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 52 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D07 | 太鐵DS | 0 |  | 1DTR(B) | #1DTR(B) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.#1DTR(B)_LOAD | #1DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 53 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D07 | 太鐵DS | 0 |  | 1DTR(B) | #1DTR(B) |  | PF | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.#1DTR(B)_PF | #1DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 54 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D07 | 太鐵DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.#2DTR(A)_MVA | #2DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 55 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D07 | 太鐵DS | 0 |  | 2DTR(A) | #2DTR(A) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.#2DTR(A)_LOAD | #2DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 56 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D07 | 太鐵DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PF | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.#2DTR(A)_PF | #2DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 57 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D07 | 太鐵DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.#2DTR(B)_MVA | #2DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 58 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D07 | 太鐵DS | 0 |  | 2DTR(B) | #2DTR(B) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.#2DTR(B)_LOAD | #2DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 59 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D07 | 太鐵DS | 0 |  | 2DTR(B) | #2DTR(B) |  | PF | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.#2DTR(B)_PF | #2DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 60 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D07 | 太鐵DS | 0 |  | 1DTR | #1DTR |  | MW | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.#1DTR_MW | #1DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 61 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  | 1DTR | #1DTR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.#1DTR_MVAR | #1DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 62 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  | 1DTR | #1DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.#1DTR_MVA | #1DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 63 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D07 | 太鐵DS | 0 |  | 1DTR | #1DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.#1DTR_LOAD | #1DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 64 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D07 | 太鐵DS | 0 |  | 1DTR | #1DTR |  | PF | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.#1DTR_PF | #1DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 65 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D07 | 太鐵DS | 0 |  | 2DTR | #2DTR |  | MW | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.#2DTR_MW | #2DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 66 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  | 2DTR | #2DTR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.#2DTR_MVAR | #2DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 67 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  | 2DTR | #2DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.#2DTR_MVA | #2DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 68 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D07 | 太鐵DS | 0 |  | 2DTR | #2DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.#2DTR_LOAD | #2DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 69 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D07 | 太鐵DS | 0 |  | 2DTR | #2DTR |  | PF | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.#2DTR_PF | #2DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 70 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D07 | 太鐵DS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.210_SC_MVAR | 11KV#1SC MVAR | SC | D07/11/210/MVAR |  | SC_LBS_11 |  |  | 71 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 11 | 11kV | 230_SC | #3SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.230_SC_MVAR | 11KV#3SC MVAR | SC | D07/11/230/MVAR |  | SC_LBS_11 |  |  | 72 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 22 | 22kV | 220_SC | #2SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.220_SC_MVAR | 23KV#2SC MVAR | SC | D07/22/220/MVAR |  | SC_CAL_23 |  |  | 73 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 22 | 22kV | 240_SC | #4SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.240_SC_MVAR | 23KV#4SC MVAR | SC | D07/22/240/MVAR |  | SC_CAL_23 |  |  | 74 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  | TRTOT | 太鐵主變瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 太鐵DS.TRTOT_MW | 太鐵主變瞬時供電量 MW |  |  |  | MTR_PQ_CAL |  |  | 75 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 0 |  | TRTOT | 太鐵主變瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 太鐵DS.TRTOT_MVAR | 太鐵主變瞬時供電量 MVAR |  |  |  | MTR_PQ_CAL |  |  | 76 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 161 | 161kV | 1950_SHR | #1SHR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.1950_SHR_MVAR | 161KV#1SHR MVAR | SC |  |  | SHR_CAL_324_5 |  |  | 77 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 161 | 161kV | 1510_AMP | 太鐵糠榔一路 | [27 empty] | ADCS_N | [8 empty] | 太鐵DS.1510_AMP_A | 太鐵糠榔一路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 78 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D07 | 太鐵DS | 0 |  | 100_CB | 100(100_CB) | [27 empty] | DDCS2_1 | [8 empty] | 太鐵DS.100_CB_2 | 100 CB (D2) | TIE |  |  | AD_LAMP_DD_1 |  |  | 79 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | 200_CB | 200(200_CB) | [27 empty] | DDCS2_1 | [8 empty] | 太鐵DS.200_CB_2 | 200 CB (D2) | TIE |  |  | AD_LAMP_DD_1 |  |  | 80 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | 310_CB | #1DTR(310_CB) | [27 empty] | DDCS2_1 | [8 empty] | 太鐵DS.310_CB_2 | 310(#1DTR) CB (D2) | MTR |  |  | AD_LAMP_DD_1 |  |  | 81 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | 320_CB | #1DTR(320_CB) | [27 empty] | DDCS2_1 | [8 empty] | 太鐵DS.320_CB_2 | 320(#1DTR) CB (D2) | MTR |  |  | AD_LAMP_DD_1 |  |  | 82 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | 330_CB | #2DTR(330_CB) | [27 empty] | DDCS2_1 | [8 empty] | 太鐵DS.330_CB_2 | 330(#2DTR) CB (D2) | MTR |  |  | AD_LAMP_DD_1 |  |  | 83 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | 340_CB | #2DTR(340_CB) | [27 empty] | DDCS2_1 | [8 empty] | 太鐵DS.340_CB_2 | 340(#2DTR) CB (D2) | MTR |  |  | AD_LAMP_DD_1 |  |  | 84 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | 210_CB | #1SC(210_CB) | [27 empty] | DDCS2_1 | [8 empty] | 太鐵DS.210_CB_2 | 210(11KV #1SC) CB (D2) | SC |  |  | AD_LAMP_DD_1 |  |  | 85 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | 230_CB | #3SC(230_CB) | [27 empty] | DDCS2_1 | [8 empty] | 太鐵DS.230_CB_2 | 230(11KV #3SC) CB (D2) | SC |  |  | AD_LAMP_DD_1 |  |  | 86 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | 220_CB | #2SC(220_CB) | [27 empty] | DDCS2_1 | [8 empty] | 太鐵DS.220_CB_2 | 220(23KV #2SC) CB (D2) | SC |  |  | AD_LAMP_DD_1 |  |  | 87 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | 240_CB | #4SC(240_CB) | [27 empty] | DDCS2_1 | [8 empty] | 太鐵DS.240_CB_2 | 240(23KV #4SC) CB (D2) | SC |  |  | AD_LAMP_DD_1 |  |  | 88 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | 11__CBA | 11/斷路器重故障(11__CBA) | [27 empty] | DDCS2_1 | [8 empty] | 太鐵DS.11/23KV_CBA_2 | 11/23KV斷路器重故障 (D2) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 89 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | 11__CBF | 11/斷路器輕故障(11__CBF) | [27 empty] | DDCS2_1 | [8 empty] | 太鐵DS.11/23KV_CBF_2 | 11/23KV斷路器輕故障 (D2) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 90 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | RTU_S_L | RTU | [27 empty] | DDCS2_1 | [8 empty] | 太鐵DS.RTU_S/L_2 | RTU SUPY/LOCAL (D2) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 91 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D07 | 太鐵DS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | D07/0/CalcPoint/SUBA |  | STATION_FAULT_10 |  |  | 92 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 變電所輕故障點燈 | 變電所輕故障點燈 |  | SUBF | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | D07/0/CalcPoint/SUBF |  | STATION_FAULT_2 |  |  | 93 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_DS |  |  | 94 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1520_AMP | 太鐵糠榔二路 | [27 empty] | ADCS_N | [8 empty] | 太鐵DS.1520_AMP_A | 太鐵糠榔二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 95 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1530_AMP | 北回太鐵紅線 | [27 empty] | ADCS_N | [8 empty] | 太鐵DS.1530_AMP_A | 北回太鐵紅線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 96 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1540_AMP | 北回太鐵白線 | [27 empty] | ADCS_N | [8 empty] | 太鐵DS.1540_AMP_A | 北回太鐵白線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 97 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1550_AMP | 後壁太鐵一路 | [27 empty] | ADCS_N | [8 empty] | 太鐵DS.1550_AMP_A | 後壁太鐵一路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 98 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1560_AMP | 後壁太鐵二路 | [27 empty] | ADCS_N | [8 empty] | 太鐵DS.1560_AMP_A | 後壁太鐵二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 99 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D07 | 太鐵DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PERM | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | D07//1DTR(A)/TR_PERM |  | DTR_PERM |  |  | 100 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D07 | 太鐵DS | 0 |  | 1DTR(B) | #1DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | D07//1DTR(B)/TR_PERM |  | DTR_PERM |  |  | 101 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D07 | 太鐵DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PERM | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | D07//2DTR(A)/TR_PERM |  | DTR_PERM |  |  | 102 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D07 | 太鐵DS | 0 |  | 2DTR(B) | #2DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | D07//2DTR(B)/TR_PERM |  | DTR_PERM |  |  | 103 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D07 | 太鐵DS | 0 |  | 1DTR_MVA | #1DTR | [27 empty] | ADCS_N | [8 empty] | 太鐵DS.#1DTR_MVA_A | #1DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 104 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D07 | 太鐵DS | 0 |  | 1DTR_MVA | #1DTR(A) | [27 empty] | DDCS2_1 | [8 empty] | 太鐵DS.#1DTR_MVA_2 | #1DTR(A) MVA 點燈 (D2) | MTR |  |  | MAP_SET |  |  | 105 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
D07 | 太鐵DS | 0 |  | 1DTR_MVA | #1DTR(B) |  | 3 | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.#1DTR_MVA_3 | #1DTR(B) MVA 點燈 (D2) | MTR |  |  | MAP_SET |  |  | 106 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D07 | 太鐵DS | 0 |  | 2DTR_MVA | #2DTR | [27 empty] | ADCS_N | [8 empty] | 太鐵DS.#2DTR_MVA_A | #2DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 107 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D07 | 太鐵DS | 0 |  | 2DTR_MVA | #2DTR(A) | [27 empty] | DDCS2_1 | [8 empty] | 太鐵DS.#2DTR_MVA_2 | #2DTR(A) MVA 點燈 (D2) | MTR |  |  | MAP_SET |  |  | 108 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
D07 | 太鐵DS | 0 |  | 2DTR_MVA | #2DTR(B) |  | 3 | [25 empty] | DDCS2_1 | [8 empty] | 太鐵DS.#2DTR_MVA_3 | #2DTR(B) MVA 點燈 (D2) | MTR |  |  | MAP_SET |  |  | 109 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D07 | 太鐵DS | 0 |  | 1ABUS | #1ABUS |  | 11KV#1ABUSC | [25 empty] | CDCS | [8 empty] | 太鐵DS.11KV#1ABUSC | #1ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 110 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D07 | 太鐵DS | 0 |  | 1BBUS | #1BBUS |  | 23KV#1BBUSC | [25 empty] | CDCS | [8 empty] | 太鐵DS.23KV#1BBUSC | #1BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 111 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D07 | 太鐵DS | 0 |  | 2ABUS | #2ABUS |  | 11KV#2ABUSC | [25 empty] | CDCS | [8 empty] | 太鐵DS.11KV#2ABUSC | #2ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 112 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D07 | 太鐵DS | 0 |  | 2BBUS | #2BBUS |  | 23KV#2BBUSC | [25 empty] | CDCS | [8 empty] | 太鐵DS.23KV#2BBUSC | #2BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 113 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D07 | 太鐵DS | 0 |  | TAP_OVER | TAP |  | SET | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.TAP_OVER_SET | TAP OVER HI/LO ALARM | MTR |  |  | 5000_CB_T4 |  |  | 114 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D07 | 太鐵DS | 0 |  | BUS_OVER | BUS |  | SET | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.BUS_OVER_SET | BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B4 |  |  | 115 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D07 | 太鐵DS | 0 |  | 5000 | 虛擬5000 |  | CB動作 | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.5000_CB動作 | 虛擬5000 CB動作,請查明原因處理 | MTR |  |  | 5000_CB_M |  |  | 116 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | 注意OLTC | 注意OLTC |  | BUS電壓異常 | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.BUS電壓異常 | 注意OLTC Tap位置,並將RPDC閉鎖 | OTHER |  |  | STATION_FAULT_3 |  |  | 117 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1BUS | #1BUS |  | V | [14 empty] | 0002 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | D07/161/1BUS/V |  |  |  | DNP | 118 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D07 | 太鐵DS | 161 | 161kV | 2BUS | #2BUS |  | V | [14 empty] | 0003 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | D07/161/2BUS/V |  |  |  | DNP | 119 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D07 | 太鐵DS | 161 | 161kV | 1510 | 太鐵糠榔一路(1510) |  | MW | [14 empty] | 0004 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.1510_MW | 太鐵糠榔一路 MW | LINE161 | D07/161/1510/MW |  |  |  | DNP | 120 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D07 | 太鐵DS | 161 | 161kV | 1510 | 太鐵糠榔一路(1510) |  | MVAR | [14 empty] | 0005 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.1510_MVAR | 太鐵糠榔一路 MVAR | LINE161 | D07/161/1510/MVAR |  |  |  | DNP | 121 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 1ABUS | #1ABUS |  | V | [14 empty] | 0051 | [8 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.11KV#1ABUS_KV | 11KV #1ABUS KV | BUS | D07/11/1ABUS/V |  |  |  | DNP | 122 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D07 | 太鐵DS | 11 | 11kV | 2ABUS | #2ABUS |  | V | [14 empty] | 0115 | [8 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS | D07/11/2ABUS/V |  |  |  | DNP | 123 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D07 | 太鐵DS | 22 | 22kV | 1BBUS | #1BBUS |  | V | [14 empty] | 0084 | [8 empty] | kV_-18_18(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.23KV#1BBUS_KV | 23KV #1BBUS KV | BUS | D07/22/1BBUS/V |  |  |  | DNP | 124 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D07 | 太鐵DS | 22 | 22kV | 2BBUS | #2BBUS |  | V | [14 empty] | 0151 | [8 empty] | kV_-18_18(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.23KV#2BBUS_KV | 23KV #2BBUS KV | BUS | D07/22/2BBUS/V |  |  |  | DNP | 125 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D07 | 太鐵DS | 161 | 161kV | 1520 | 太鐵糠榔二路(1520) |  | MW | [14 empty] | 0006 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.1520_MW | 太鐵糠榔二路 MW | LINE161 | D07/161/1520/MW |  |  |  | DNP | 126 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D07 | 太鐵DS | 161 | 161kV | 1520 | 太鐵糠榔二路(1520) |  | MVAR | [14 empty] | 0007 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.1520_MVAR | 太鐵糠榔二路 MVAR | LINE161 | D07/161/1520/MVAR |  |  |  | DNP | 127 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D07 | 太鐵DS | 161 | 161kV | 1530 | 北回太鐵紅線(1530) |  | MW | [14 empty] | 0008 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.1530_MW | 北回太鐵紅線 MW | LINE161 | D07/161/1530/MW |  |  |  | DNP | 128 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D07 | 太鐵DS | 161 | 161kV | 1530 | 北回太鐵紅線(1530) |  | MVAR | [14 empty] | 0009 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.1530_MVAR | 北回太鐵紅線 MVAR | LINE161 | D07/161/1530/MVAR |  |  |  | DNP | 129 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D07 | 太鐵DS | 161 | 161kV | 1540 | 北回太鐵白線(1540) |  | MW | [14 empty] | 0010 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.1540_MW | 北回太鐵白線 MW | LINE161 | D07/161/1540/MW |  |  |  | DNP | 130 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D07 | 太鐵DS | 161 | 161kV | 1540 | 北回太鐵白線(1540) |  | MVAR | [14 empty] | 0011 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.1540_MVAR | 北回太鐵白線 MVAR | LINE161 | D07/161/1540/MVAR |  |  |  | DNP | 131 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D07 | 太鐵DS | 161 | 161kV | 1550 | 後壁太鐵一路(1550) |  | MW | [14 empty] | 0012 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.1550_MW | 後壁太鐵一路 MW | LINE161 | D07/161/1550/MW |  |  |  | DNP | 132 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D07 | 太鐵DS | 161 | 161kV | 1550 | 後壁太鐵一路(1550) |  | MVAR | [14 empty] | 0013 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.1550_MVAR | 後壁太鐵一路 MVAR | LINE161 | D07/161/1550/MVAR |  |  |  | DNP | 133 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D07 | 太鐵DS | 161 | 161kV | 1560 | 後壁太鐵二路(1560) |  | MW | [14 empty] | 0014 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.1560_MW | 後壁太鐵二路 MW | LINE161 | D07/161/1560/MW |  |  |  | DNP | 134 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D07 | 太鐵DS | 161 | 161kV | 1560 | 後壁太鐵二路(1560) |  | MVAR | [14 empty] | 0015 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.1560_MVAR | 後壁太鐵二路 MVAR | LINE161 | D07/161/1560/MVAR |  |  |  | DNP | 135 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵21線 | 鐵21線 |  | 鐵21線KVAR | [14 empty] | 0052 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵21線KVAR | 11KV鐵21線 KVAR | FEEDER | D07/11/JV21/KVAR |  |  |  | DNP | 136 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵21線 | 鐵21線 |  | 鐵21線A1 | [14 empty] | 0053 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵21線A1 | 11KV鐵21線 R相AMP | FEEDER | D07/11/JV21/I_R |  |  |  | DNP | 137 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵21線 | 鐵21線 |  | 鐵21線A2 | [14 empty] | 0054 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵21線A2 | 11KV鐵21線 S相AMP | FEEDER | D07/11/JV21/I_S |  |  |  | DNP | 138 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵21線 | 鐵21線 |  | 鐵21線A3 | [14 empty] | 0055 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵21線A3 | 11KV鐵21線 T相AMP | FEEDER | D07/11/JV21/I_T |  |  |  | DNP | 139 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵21線 | 鐵21線 |  | 鐵21線A0 | [14 empty] | 0056 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵21線A0 | 11KV鐵21線 N相AMP | FEEDER | D07/11/JV21/I_N |  |  |  | DNP | 140 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵22線 | 鐵22線 |  | 鐵22線KVAR | [14 empty] | 0057 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵22線KVAR | 11KV鐵22線 KVAR | FEEDER | D07/11/JV22/KVAR |  |  |  | DNP | 141 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵22線 | 鐵22線 |  | 鐵22線A1 | [14 empty] | 0058 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵22線A1 | 11KV鐵22線 R相AMP | FEEDER | D07/11/JV22/I_R |  |  |  | DNP | 142 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵22線 | 鐵22線 |  | 鐵22線A2 | [14 empty] | 0059 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵22線A2 | 11KV鐵22線 S相AMP | FEEDER | D07/11/JV22/I_S |  |  |  | DNP | 143 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵22線 | 鐵22線 |  | 鐵22線A3 | [14 empty] | 0060 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵22線A3 | 11KV鐵22線 T相AMP | FEEDER | D07/11/JV22/I_T |  |  |  | DNP | 144 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵22線 | 鐵22線 |  | 鐵22線A0 | [14 empty] | 0061 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵22線A0 | 11KV鐵22線 N相AMP | FEEDER | D07/11/JV22/I_N |  |  |  | DNP | 145 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵23線 | 鐵23線 |  | 鐵23線KVAR | [14 empty] | 0062 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵23線KVAR | 11KV鐵23線 KVAR | FEEDER | D07/11/JV23/KVAR |  |  |  | DNP | 146 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵23線 | 鐵23線 |  | 鐵23線A1 | [14 empty] | 0063 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵23線A1 | 11KV鐵23線 R相AMP | FEEDER | D07/11/JV23/I_R |  |  |  | DNP | 147 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵23線 | 鐵23線 |  | 鐵23線A2 | [14 empty] | 0066 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵23線A2 | 11KV鐵23線 S相AMP | FEEDER | D07/11/JV23/I_S |  |  |  | DNP | 148 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵23線 | 鐵23線 |  | 鐵23線A3 | [14 empty] | 0067 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵23線A3 | 11KV鐵23線 T相AMP | FEEDER | D07/11/JV23/I_T |  |  |  | DNP | 149 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵23線 | 鐵23線 |  | 鐵23線A0 | [14 empty] | 0068 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵23線A0 | 11KV鐵23線 N相AMP | FEEDER | D07/11/JV23/I_N |  |  |  | DNP | 150 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵24線 | 鐵24線 |  | 鐵24線KVAR | [14 empty] | 0069 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵24線KVAR | 11KV鐵24線 KVAR | FEEDER | D07/11/JV24/KVAR |  |  |  | DNP | 151 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵24線 | 鐵24線 |  | 鐵24線A1 | [14 empty] | 0070 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵24線A1 | 11KV鐵24線 R相AMP | FEEDER | D07/11/JV24/I_R |  |  |  | DNP | 152 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵24線 | 鐵24線 |  | 鐵24線A2 | [14 empty] | 0071 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵24線A2 | 11KV鐵24線 S相AMP | FEEDER | D07/11/JV24/I_S |  |  |  | DNP | 153 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵24線 | 鐵24線 |  | 鐵24線A3 | [14 empty] | 0072 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵24線A3 | 11KV鐵24線 T相AMP | FEEDER | D07/11/JV24/I_T |  |  |  | DNP | 154 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵24線 | 鐵24線 |  | 鐵24線A0 | [14 empty] | 0073 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵24線A0 | 11KV鐵24線 N相AMP | FEEDER | D07/11/JV24/I_N |  |  |  | DNP | 155 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵25線 | 鐵25線 |  | 鐵25線KVAR | [14 empty] | 0074 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵25線KVAR | 11KV鐵25線 KVAR | FEEDER | D07/11/JV25/KVAR |  |  |  | DNP | 156 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵25線 | 鐵25線 |  | 鐵25線A1 | [14 empty] | 0075 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵25線A1 | 11KV鐵25線 R相AMP | FEEDER | D07/11/JV25/I_R |  |  |  | DNP | 157 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵25線 | 鐵25線 |  | 鐵25線A2 | [14 empty] | 0076 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵25線A2 | 11KV鐵25線 S相AMP | FEEDER | D07/11/JV25/I_S |  |  |  | DNP | 158 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵25線 | 鐵25線 |  | 鐵25線A3 | [14 empty] | 0077 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵25線A3 | 11KV鐵25線 T相AMP | FEEDER | D07/11/JV25/I_T |  |  |  | DNP | 159 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵25線 | 鐵25線 |  | 鐵25線A0 | [14 empty] | 0078 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵25線A0 | 11KV鐵25線 N相AMP | FEEDER | D07/11/JV25/I_N |  |  |  | DNP | 160 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵31線 | 鐵31線 |  | 鐵31線KVAR | [14 empty] | 0116 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵31線KVAR | 11KV鐵31線 KVAR | FEEDER | D07/11/JV31/KVAR |  |  |  | DNP | 161 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵31線 | 鐵31線 |  | 鐵31線A1 | [14 empty] | 0117 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵31線A1 | 11KV鐵31線 R相AMP | FEEDER | D07/11/JV31/I_R |  |  |  | DNP | 162 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵31線 | 鐵31線 |  | 鐵31線A2 | [14 empty] | 0118 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵31線A2 | 11KV鐵31線 S相AMP | FEEDER | D07/11/JV31/I_S |  |  |  | DNP | 163 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵31線 | 鐵31線 |  | 鐵31線A3 | [14 empty] | 0119 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵31線A3 | 11KV鐵31線 T相AMP | FEEDER | D07/11/JV31/I_T |  |  |  | DNP | 164 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵31線 | 鐵31線 |  | 鐵31線A0 | [14 empty] | 0120 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵31線A0 | 11KV鐵31線 N相AMP | FEEDER | D07/11/JV31/I_N |  |  |  | DNP | 165 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵32線 | 鐵32線 |  | 鐵32線KVAR | [14 empty] | 0121 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵32線KVAR | 11KV鐵32線 KVAR | FEEDER | D07/11/JV32/KVAR |  |  |  | DNP | 166 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵32線 | 鐵32線 |  | 鐵32線A1 | [14 empty] | 0122 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵32線A1 | 11KV鐵32線 R相AMP | FEEDER | D07/11/JV32/I_R |  |  |  | DNP | 167 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵32線 | 鐵32線 |  | 鐵32線A2 | [14 empty] | 0123 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵32線A2 | 11KV鐵32線 S相AMP | FEEDER | D07/11/JV32/I_S |  |  |  | DNP | 168 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵32線 | 鐵32線 |  | 鐵32線A3 | [14 empty] | 0124 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵32線A3 | 11KV鐵32線 T相AMP | FEEDER | D07/11/JV32/I_T |  |  |  | DNP | 169 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵32線 | 鐵32線 |  | 鐵32線A0 | [14 empty] | 0125 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵32線A0 | 11KV鐵32線 N相AMP | FEEDER | D07/11/JV32/I_N |  |  |  | DNP | 170 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵33線 | 鐵33線 |  | 鐵33線KVAR | [14 empty] | 0126 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵33線KVAR | 11KV鐵33線 KVAR | FEEDER | D07/11/JV33/KVAR |  |  |  | DNP | 171 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵33線 | 鐵33線 |  | 鐵33線A1 | [14 empty] | 0127 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵33線A1 | 11KV鐵33線 R相AMP | FEEDER | D07/11/JV33/I_R |  |  |  | DNP | 172 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵33線 | 鐵33線 |  | 鐵33線A2 | [14 empty] | 0130 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵33線A2 | 11KV鐵33線 S相AMP | FEEDER | D07/11/JV33/I_S |  |  |  | DNP | 173 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵33線 | 鐵33線 |  | 鐵33線A3 | [14 empty] | 0131 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵33線A3 | 11KV鐵33線 T相AMP | FEEDER | D07/11/JV33/I_T |  |  |  | DNP | 174 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵33線 | 鐵33線 |  | 鐵33線A0 | [14 empty] | 0132 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵33線A0 | 11KV鐵33線 N相AMP | FEEDER | D07/11/JV33/I_N |  |  |  | DNP | 175 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵34線 | 鐵34線 |  | 鐵34線KVAR | [14 empty] | 0133 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵34線KVAR | 11KV鐵34線 KVAR | FEEDER | D07/11/JV34/KVAR |  |  |  | DNP | 176 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵34線 | 鐵34線 |  | 鐵34線A1 | [14 empty] | 0134 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵34線A1 | 11KV鐵34線 R相AMP | FEEDER | D07/11/JV34/I_R |  |  |  | DNP | 177 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵34線 | 鐵34線 |  | 鐵34線A2 | [14 empty] | 0135 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵34線A2 | 11KV鐵34線 S相AMP | FEEDER | D07/11/JV34/I_S |  |  |  | DNP | 178 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵34線 | 鐵34線 |  | 鐵34線A3 | [14 empty] | 0136 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵34線A3 | 11KV鐵34線 T相AMP | FEEDER | D07/11/JV34/I_T |  |  |  | DNP | 179 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵34線 | 鐵34線 |  | 鐵34線A0 | [14 empty] | 0137 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵34線A0 | 11KV鐵34線 N相AMP | FEEDER | D07/11/JV34/I_N |  |  |  | DNP | 180 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵35線 | 鐵35線 |  | 鐵35線KVAR | [14 empty] | 0138 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵35線KVAR | 11KV鐵35線 KVAR | FEEDER | D07/11/JV35/KVAR |  |  |  | DNP | 181 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵35線 | 鐵35線 |  | 鐵35線A1 | [14 empty] | 0139 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵35線A1 | 11KV鐵35線 R相AMP | FEEDER | D07/11/JV35/I_R |  |  |  | DNP | 182 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵35線 | 鐵35線 |  | 鐵35線A2 | [14 empty] | 0140 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵35線A2 | 11KV鐵35線 S相AMP | FEEDER | D07/11/JV35/I_S |  |  |  | DNP | 183 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵35線 | 鐵35線 |  | 鐵35線A3 | [14 empty] | 0141 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵35線A3 | 11KV鐵35線 T相AMP | FEEDER | D07/11/JV35/I_T |  |  |  | DNP | 184 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | 鐵35線 | 鐵35線 |  | 鐵35線A0 | [14 empty] | 0142 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵35線A0 | 11KV鐵35線 N相AMP | FEEDER | D07/11/JV35/I_N |  |  |  | DNP | 185 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵56線 | 鐵56線 |  | 鐵56線KVAR | [14 empty] | 0085 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵56線KVAR | 23KV鐵56線 KVAR | FEEDER | D07/22/JV56/KVAR |  |  |  | DNP | 186 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵56線 | 鐵56線 |  | 鐵56線A1 | [14 empty] | 0086 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵56線A1 | 23KV鐵56線 R相AMP | FEEDER | D07/22/JV56/I_R |  |  |  | DNP | 187 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵56線 | 鐵56線 |  | 鐵56線A2 | [14 empty] | 0087 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵56線A2 | 23KV鐵56線 S相AMP | FEEDER | D07/22/JV56/I_S |  |  |  | DNP | 188 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵56線 | 鐵56線 |  | 鐵56線A3 | [14 empty] | 0088 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵56線A3 | 23KV鐵56線 T相AMP | FEEDER | D07/22/JV56/I_T |  |  |  | DNP | 189 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵56線 | 鐵56線 |  | 鐵56線A0 | [14 empty] | 0089 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵56線A0 | 23KV鐵56線 N相AMP | FEEDER | D07/22/JV56/I_N |  |  |  | DNP | 190 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵57線 | 鐵57線 |  | 鐵57線KVAR | [14 empty] | 0090 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵57線KVAR | 23KV鐵57線 KVAR | FEEDER | D07/22/JV57/KVAR |  |  |  | DNP | 191 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵57線 | 鐵57線 |  | 鐵57線A1 | [14 empty] | 0091 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵57線A1 | 23KV鐵57線 R相AMP | FEEDER | D07/22/JV57/I_R |  |  |  | DNP | 192 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵57線 | 鐵57線 |  | 鐵57線A2 | [14 empty] | 0092 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵57線A2 | 23KV鐵57線 S相AMP | FEEDER | D07/22/JV57/I_S |  |  |  | DNP | 193 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵57線 | 鐵57線 |  | 鐵57線A3 | [14 empty] | 0093 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵57線A3 | 23KV鐵57線 T相AMP | FEEDER | D07/22/JV57/I_T |  |  |  | DNP | 194 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵57線 | 鐵57線 |  | 鐵57線A0 | [14 empty] | 0094 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵57線A0 | 23KV鐵57線 N相AMP | FEEDER | D07/22/JV57/I_N |  |  |  | DNP | 195 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵58線 | 鐵58線 |  | 鐵58線KVAR | [14 empty] | 0095 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵58線KVAR | 23KV鐵58線 KVAR | FEEDER | D07/22/JV58/KVAR |  |  |  | DNP | 196 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵58線 | 鐵58線 |  | 鐵58線A1 | [14 empty] | 0096 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵58線A1 | 23KV鐵58線 R相AMP | FEEDER | D07/22/JV58/I_R |  |  |  | DNP | 197 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵58線 | 鐵58線 |  | 鐵58線A2 | [14 empty] | 0097 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵58線A2 | 23KV鐵58線 S相AMP | FEEDER | D07/22/JV58/I_S |  |  |  | DNP | 198 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵58線 | 鐵58線 |  | 鐵58線A3 | [14 empty] | 0098 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵58線A3 | 23KV鐵58線 T相AMP | FEEDER | D07/22/JV58/I_T |  |  |  | DNP | 199 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵58線 | 鐵58線 |  | 鐵58線A0 | [14 empty] | 0099 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵58線A0 | 23KV鐵58線 N相AMP | FEEDER | D07/22/JV58/I_N |  |  |  | DNP | 200 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵59線 | 鐵59線 |  | 鐵59線KVAR | [14 empty] | 0100 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵59線KVAR | 23KV鐵59線 KVAR | FEEDER | D07/22/JV59/KVAR |  |  |  | DNP | 201 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵59線 | 鐵59線 |  | 鐵59線A1 | [14 empty] | 0101 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵59線A1 | 23KV鐵59線 R相AMP | FEEDER | D07/22/JV59/I_R |  |  |  | DNP | 202 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵59線 | 鐵59線 |  | 鐵59線A2 | [14 empty] | 0102 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵59線A2 | 23KV鐵59線 S相AMP | FEEDER | D07/22/JV59/I_S |  |  |  | DNP | 203 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵59線 | 鐵59線 |  | 鐵59線A3 | [14 empty] | 0103 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵59線A3 | 23KV鐵59線 T相AMP | FEEDER | D07/22/JV59/I_T |  |  |  | DNP | 204 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵59線 | 鐵59線 |  | 鐵59線A0 | [14 empty] | 0104 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵59線A0 | 23KV鐵59線 N相AMP | FEEDER | D07/22/JV59/I_N |  |  |  | DNP | 205 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵60線 | 鐵60線 |  | 鐵60線KVAR | [14 empty] | 0105 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵60線KVAR | 23KV鐵60線 KVAR | FEEDER | D07/22/JV60/KVAR |  |  |  | DNP | 206 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵60線 | 鐵60線 |  | 鐵60線A1 | [14 empty] | 0106 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵60線A1 | 23KV鐵60線 R相AMP | FEEDER | D07/22/JV60/I_R |  |  |  | DNP | 207 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵60線 | 鐵60線 |  | 鐵60線A2 | [14 empty] | 0107 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵60線A2 | 23KV鐵60線 S相AMP | FEEDER | D07/22/JV60/I_S |  |  |  | DNP | 208 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵60線 | 鐵60線 |  | 鐵60線A3 | [14 empty] | 0108 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵60線A3 | 23KV鐵60線 T相AMP | FEEDER | D07/22/JV60/I_T |  |  |  | DNP | 209 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵60線 | 鐵60線 |  | 鐵60線A0 | [14 empty] | 0109 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵60線A0 | 23KV鐵60線 N相AMP | FEEDER | D07/22/JV60/I_N |  |  |  | DNP | 210 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵66線 | 鐵66線 |  | 鐵66線KVAR | [14 empty] | 0152 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵66線KVAR | 23KV鐵66線 KVAR | FEEDER | D07/22/JV66/KVAR |  |  |  | DNP | 211 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵66線 | 鐵66線 |  | 鐵66線A1 | [14 empty] | 0153 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵66線A1 | 23KV鐵66線 R相AMP | FEEDER | D07/22/JV66/I_R |  |  |  | DNP | 212 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵66線 | 鐵66線 |  | 鐵66線A2 | [14 empty] | 0154 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵66線A2 | 23KV鐵66線 S相AMP | FEEDER | D07/22/JV66/I_S |  |  |  | DNP | 213 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵66線 | 鐵66線 |  | 鐵66線A3 | [14 empty] | 0155 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵66線A3 | 23KV鐵66線 T相AMP | FEEDER | D07/22/JV66/I_T |  |  |  | DNP | 214 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵66線 | 鐵66線 |  | 鐵66線A0 | [14 empty] | 0156 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵66線A0 | 23KV鐵66線 N相AMP | FEEDER | D07/22/JV66/I_N |  |  |  | DNP | 215 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵67線 | 鐵67線 |  | 鐵67線KVAR | [14 empty] | 0157 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵67線KVAR | 23KV鐵67線 KVAR | FEEDER | D07/22/JV67/KVAR |  |  |  | DNP | 216 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵67線 | 鐵67線 |  | 鐵67線A1 | [14 empty] | 0158 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵67線A1 | 23KV鐵67線 R相AMP | FEEDER | D07/22/JV67/I_R |  |  |  | DNP | 217 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵67線 | 鐵67線 |  | 鐵67線A2 | [14 empty] | 0159 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵67線A2 | 23KV鐵67線 S相AMP | FEEDER | D07/22/JV67/I_S |  |  |  | DNP | 218 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵67線 | 鐵67線 |  | 鐵67線A3 | [14 empty] | 0160 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵67線A3 | 23KV鐵67線 T相AMP | FEEDER | D07/22/JV67/I_T |  |  |  | DNP | 219 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵67線 | 鐵67線 |  | 鐵67線A0 | [14 empty] | 0161 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵67線A0 | 23KV鐵67線 N相AMP | FEEDER | D07/22/JV67/I_N |  |  |  | DNP | 220 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵68線 | 鐵68線 |  | 鐵68線KVAR | [14 empty] | 0162 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵68線KVAR | 23KV鐵68線 KVAR | FEEDER | D07/22/JV68/KVAR |  |  |  | DNP | 221 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵68線 | 鐵68線 |  | 鐵68線A1 | [14 empty] | 0163 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵68線A1 | 23KV鐵68線 R相AMP | FEEDER | D07/22/JV68/I_R |  |  |  | DNP | 222 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵68線 | 鐵68線 |  | 鐵68線A2 | [14 empty] | 0164 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵68線A2 | 23KV鐵68線 S相AMP | FEEDER | D07/22/JV68/I_S |  |  |  | DNP | 223 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵68線 | 鐵68線 |  | 鐵68線A3 | [14 empty] | 0165 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵68線A3 | 23KV鐵68線 T相AMP | FEEDER | D07/22/JV68/I_T |  |  |  | DNP | 224 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵68線 | 鐵68線 |  | 鐵68線A0 | [14 empty] | 0166 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵68線A0 | 23KV鐵68線 N相AMP | FEEDER | D07/22/JV68/I_N |  |  |  | DNP | 225 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵69線 | 鐵69線 |  | 鐵69線KVAR | [14 empty] | 0167 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵69線KVAR | 23KV鐵69線 KVAR | FEEDER | D07/22/JV69/KVAR |  |  |  | DNP | 226 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵69線 | 鐵69線 |  | 鐵69線A1 | [14 empty] | 0168 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵69線A1 | 23KV鐵69線 R相AMP | FEEDER | D07/22/JV69/I_R |  |  |  | DNP | 227 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵69線 | 鐵69線 |  | 鐵69線A2 | [14 empty] | 0169 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵69線A2 | 23KV鐵69線 S相AMP | FEEDER | D07/22/JV69/I_S |  |  |  | DNP | 228 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵69線 | 鐵69線 |  | 鐵69線A3 | [14 empty] | 0170 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵69線A3 | 23KV鐵69線 T相AMP | FEEDER | D07/22/JV69/I_T |  |  |  | DNP | 229 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵69線 | 鐵69線 |  | 鐵69線A0 | [14 empty] | 0171 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵69線A0 | 23KV鐵69線 N相AMP | FEEDER | D07/22/JV69/I_N |  |  |  | DNP | 230 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵70線 | 鐵70線 |  | 鐵70線KVAR | [14 empty] | 0172 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵70線KVAR | 23KV鐵70線 KVAR | FEEDER | D07/22/JV70/KVAR |  |  |  | DNP | 231 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵70線 | 鐵70線 |  | 鐵70線A1 | [14 empty] | 0173 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵70線A1 | 23KV鐵70線 R相AMP | FEEDER | D07/22/JV70/I_R |  |  |  | DNP | 232 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵70線 | 鐵70線 |  | 鐵70線A2 | [14 empty] | 0174 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵70線A2 | 23KV鐵70線 S相AMP | FEEDER | D07/22/JV70/I_S |  |  |  | DNP | 233 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵70線 | 鐵70線 |  | 鐵70線A3 | [14 empty] | 0175 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵70線A3 | 23KV鐵70線 T相AMP | FEEDER | D07/22/JV70/I_T |  |  |  | DNP | 234 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | 鐵70線 | 鐵70線 |  | 鐵70線A0 | [14 empty] | 0176 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_1 | [8 empty] | 太鐵DS.鐵70線A0 | 23KV鐵70線 N相AMP | FEEDER | D07/22/JV70/I_N |  |  |  | DNP | 235 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 0 |  | 1500TIE | 1500TIE |  | I | [14 empty] | 0028 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.1500TIE_AMP | 1500TIE AMP | TIE | D07/161/1500/I_R |  |  |  | DNP | 236 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | _100 | 100 |  | I_R | [14 empty] | 0143 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.11KV_100_A1 | 11KV 100 R相AMP | TIE | D07/11/100/I_R |  |  |  | DNP | 237 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | _100 | 100 |  | I_S | [14 empty] | 0144 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.11KV_100_A2 | 11KV 100 S相AMP | TIE | D07/11/100/I_S |  |  |  | DNP | 238 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 11 | 11kV | _100 | 100 |  | I_T | [14 empty] | 0145 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.11KV_100_A3 | 11KV 100 T相AMP | TIE | D07/11/100/I_T |  |  |  | DNP | 239 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | _200 | 200 |  | I_R | [14 empty] | 0177 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.23KV_200_A1 | 23KV 200 R相AMP | TIE | D07/22/200/I_R |  |  |  | DNP | 240 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | _200 | 200 |  | I_S | [14 empty] | 0178 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.23KV_200_A2 | 23KV 200 S相AMP | TIE | D07/22/200/I_S |  |  |  | DNP | 241 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 22 | 22kV | _200 | 200 |  | I_T | [14 empty] | 0179 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.23KV_200_A3 | 23KV 200 T相AMP | TIE | D07/22/200/I_T |  |  |  | DNP | 242 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MW | [14 empty] | 0046 | [8 empty] | MW_-54_54(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | D07/11/310/KW |  |  |  | DNP | 243 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.054000 | 0.010000
D07 | 太鐵DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVAR | [14 empty] | 0047 | [8 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | D07/11/310/KVAR |  |  |  | DNP | 244 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.036000 | 0.010000
D07 | 太鐵DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_R | [14 empty] | 0048 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | D07/11/310/I_R |  |  |  | DNP | 245 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_S | [14 empty] | 0049 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | D07/11/310/I_S |  |  |  | DNP | 246 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_T | [14 empty] | 0050 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | D07/11/310/I_T |  |  |  | DNP | 247 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 0 |  | 1DTR | #1DTR |  | OilTemp | [14 empty] | 0029 | [8 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.#1DTR_OIL | #1DTR 油溫 | MTR | D07//1DTR/OilTemp |  |  |  | DNP | 248 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D07 | 太鐵DS | 0 |  | 1DTR(A) | #1DTR(A) |  | CoilTemp | [14 empty] | 0030 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | D07//1DTR(A)/CoilTemp |  |  |  | DNP | 249 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D07 | 太鐵DS | 0 |  | 1DTR(A) | #1DTR(A) |  | TapPosMv | [14 empty] | 0032 |  | 0075 | [6 empty] | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 太鐵DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | D07//1DTR(A)/TapPosMv |  |  |  | DNP | 250 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D07 | 太鐵DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MW | [14 empty] | 0079 | [8 empty] | MW_-108_108(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | D07/22/320/KW |  |  |  | DNP | 251 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D07 | 太鐵DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVAR | [14 empty] | 0080 | [8 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | D07/22/320/KVAR |  |  |  | DNP | 252 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D07 | 太鐵DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_R | [14 empty] | 0081 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | D07/22/320/I_R |  |  |  | DNP | 253 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_S | [14 empty] | 0082 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | D07/22/320/I_S |  |  |  | DNP | 254 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_T | [14 empty] | 0083 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | D07/22/320/I_T |  |  |  | DNP | 255 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 0 |  | 1DTR(B) | #1DTR(B) |  | CoilTemp | [14 empty] | 0031 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | D07//1DTR(B)/CoilTemp |  |  |  | DNP | 256 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D07 | 太鐵DS | 0 |  | 1DTR(B) | #1DTR(B) |  | TapPosMv | [14 empty] | 0033 |  | 0077 | [6 empty] | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 太鐵DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | D07//1DTR(B)/TapPosMv |  |  |  | DNP | 257 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D07 | 太鐵DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MW | [14 empty] | 0110 | [8 empty] | MW_-54_54(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | D07/11/330/KW |  |  |  | DNP | 258 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.054000 | 0.010000
D07 | 太鐵DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVAR | [14 empty] | 0111 | [8 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | D07/11/330/KVAR |  |  |  | DNP | 259 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.036000 | 0.010000
D07 | 太鐵DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_R | [14 empty] | 0112 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | D07/11/330/I_R |  |  |  | DNP | 260 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_S | [14 empty] | 0113 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | D07/11/330/I_S |  |  |  | DNP | 261 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_T | [14 empty] | 0114 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | D07/11/330/I_T |  |  |  | DNP | 262 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 0 |  | 2DTR | #2DTR |  | OilTemp | [14 empty] | 0034 | [8 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.#2DTR_OIL | #2DTR 油溫 | MTR | D07//2DTR/OilTemp |  |  |  | DNP | 263 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D07 | 太鐵DS | 0 |  | 2DTR(A) | #2DTR(A) |  | CoilTemp | [14 empty] | 0035 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | D07//2DTR(A)/CoilTemp |  |  |  | DNP | 264 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D07 | 太鐵DS | 0 |  | 2DTR(A) | #2DTR(A) |  | TapPosMv | [14 empty] | 0037 |  | 0079 | [6 empty] | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 太鐵DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | D07//2DTR(A)/TapPosMv |  |  |  | DNP | 265 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D07 | 太鐵DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MW | [14 empty] | 0146 | [8 empty] | MW_-108_108(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | D07/22/340/KW |  |  |  | DNP | 266 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D07 | 太鐵DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVAR | [14 empty] | 0147 | [8 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | D07/22/340/KVAR |  |  |  | DNP | 267 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D07 | 太鐵DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_R | [14 empty] | 0148 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | D07/22/340/I_R |  |  |  | DNP | 268 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_S | [14 empty] | 0149 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | D07/22/340/I_S |  |  |  | DNP | 269 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_T | [14 empty] | 0150 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | D07/22/340/I_T |  |  |  | DNP | 270 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D07 | 太鐵DS | 0 |  | 2DTR(B) | #2DTR(B) |  | CoilTemp | [14 empty] | 0036 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | D07//2DTR(B)/CoilTemp |  |  |  | DNP | 271 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D07 | 太鐵DS | 0 |  | 2DTR(B) | #2DTR(B) |  | TapPosMv | [14 empty] | 0038 |  | 0081 | [6 empty] | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 太鐵DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | D07//2DTR(B)/TapPosMv |  |  |  | DNP | 272 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D07 | 太鐵DS | 0 |  |  |  |  | DCV_N | [14 empty] | 0025 | [8 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.直流N電源電壓 | 直流N電源電壓 | OTHER | D07/0/StaDev/DCV_N |  |  |  | DNP | 273 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D07 | 太鐵DS | 0 |  |  |  |  | DCV_P | [14 empty] | 0024 | [8 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.直流P電源電壓 | 直流P電源電壓 | OTHER | D07/0/StaDev/DCV_P |  |  |  | DNP | 274 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D07 | 太鐵DS | 161 | 161kV | 1611SHR | #1SHR |  | CoilTemp | [14 empty] | 0027 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.161#1SHR_COIL | 161KV #1SHR 線溫 | OTHER | D07//1SHR/CoilTemp |  |  |  | DNP | 275 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D07 | 太鐵DS | 161 | 161kV | 1611SHR | #1SHR |  | OilTemp | [14 empty] | 0026 | [8 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 太鐵DS.161#1SHR_OIL | 161KV #1SHR 油溫 | OTHER | D07//1SHR/OilTemp |  |  |  | DNP | 276 | DNPAIPoint | DS053 |  |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D07 | 太鐵DS | 161 | 161kV | 1510 | 太鐵糠榔一路(1510) |  | PHA | [14 empty] | 0002 | [10 empty] | 161KV_N | [8 empty] | 太鐵DS.1510_PHA | 太鐵糠榔一路(1510) 相間RY | LINE161 | D07/161/1510/PHA |  |  |  | DNP | 277 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1510 | 太鐵糠榔一路(1510) |  | GDA | [14 empty] | 0003 | [10 empty] | 161KV_N | [8 empty] | 太鐵DS.1510_GDA | 太鐵糠榔一路(1510) 接地RY | LINE161 | D07/161/1510/GDA |  |  |  | DNP | 278 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1510 | 太鐵糠榔一路(1510) |  | 87A | [14 empty] | 0001 | [10 empty] | 161KV_N | [8 empty] | 太鐵DS.1510_87A | 太鐵糠榔一路(1510) 87RY | LINE161 | D07/161/1510/87A |  |  |  | DNP | 279 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1510 | 太鐵糠榔一路(1510) |  | 87UL | [14 empty] | 0514 |  | 0022 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1510_87UL | 太鐵糠榔一路(1510) 87RY U/L | LINE161 | D07/161/1510/87UL |  |  |  | DNP | 280 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 161 | 161kV | 1510 | 太鐵糠榔一路(1510) |  | CB | [14 empty] | 0000 |  | 0002 | [8 empty] | 161KV_N | [8 empty] | 太鐵DS.1510_CB | 1510(太鐵糠榔一路) CB | LINE161 | D07/161/1510/CB |  |  |  | DNP | 281 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1510 | 太鐵糠榔一路(1510) |  | 79UL | [14 empty] | 0515 |  | 0023 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1510_79UL | 太鐵糠榔一路(1510) 79RY U/L | LINE161 | D07/161/1510/79UL |  |  |  | DNP | 282 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 161 | 161kV | 1510 | 太鐵糠榔一路(1510) |  | DS1 | 1511 | [13 empty] | 0688 | 689 | 0086 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1511_DS | 1511(太鐵糠榔一路) DS | LINE161 | D07/161/1510/DS1 |  |  |  | DNP | 283 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1510 | 太鐵糠榔一路(1510) |  | DS2 | 1512 | [13 empty] | 0690 | 691 | 0087 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1512_DS | 1512(太鐵糠榔一路) DS | LINE161 | D07/161/1510/DS2 |  |  |  | DNP | 284 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D07 | 太鐵DS | 161 | 161kV | 1510 | 太鐵糠榔一路(1510) |  | DS3 | 1513 | [13 empty] | 0692 | 693 | 0088 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1513_DS | 1513(太鐵糠榔一路) DS | LINE161 | D07/161/1510/DS3 |  |  |  | DNP | 285 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1510 | 太鐵糠榔一路(1510) |  | E3 | 1513E | [13 empty] | 0694 | 695 | 0089 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1513E_ES | 1513E(太鐵糠榔一路) ES | LINE161 | D07/161/1510/ES3 |  |  |  | DNP | 286 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D07 | 太鐵DS | 0 |  | 1510 | 太鐵糠榔一路(1510) |  | 87CFA | [14 empty] | 0536 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.1510_87CFA | 太鐵糠榔一路(1510)87RY通訊故障 | OTHER | D07/161/1510/87CFA |  |  |  | DNP | 287 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 1510 | 太鐵糠榔一路(1510) |  | RYFA | [14 empty] | 0537 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.1510_RYFA | 太鐵糠榔一路(1510)數位電驛故障 | OTHER | D07/161/1510/RYFA |  |  |  | DNP | 288 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1520 | 太鐵糠榔二路(1520) |  | PHA | [14 empty] | 0006 | [10 empty] | 161KV_N | [8 empty] | 太鐵DS.1520_PHA | 太鐵糠榔二路(1520) 相間RY | LINE161 | D07/161/1520/PHA |  |  |  | DNP | 289 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1520 | 太鐵糠榔二路(1520) |  | GDA | [14 empty] | 0007 | [10 empty] | 161KV_N | [8 empty] | 太鐵DS.1520_GDA | 太鐵糠榔二路(1520) 接地RY | LINE161 | D07/161/1520/GDA |  |  |  | DNP | 290 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1520 | 太鐵糠榔二路(1520) |  | 87A | [14 empty] | 0005 | [10 empty] | 161KV_N | [8 empty] | 太鐵DS.1520_87A | 太鐵糠榔二路(1520) 87RY | LINE161 | D07/161/1520/87A |  |  |  | DNP | 291 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1520 | 太鐵糠榔二路(1520) |  | 87UL | [14 empty] | 0516 |  | 0024 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1520_87UL | 太鐵糠榔二路(1520) 87RY U/L | LINE161 | D07/161/1520/87UL |  |  |  | DNP | 292 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 161 | 161kV | 1520 | 太鐵糠榔二路(1520) |  | CB | [14 empty] | 0004 |  | 0003 | [8 empty] | 161KV_N | [8 empty] | 太鐵DS.1520_CB | 1520(太鐵糠榔二路) CB | LINE161 | D07/161/1520/CB |  |  |  | DNP | 293 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1520 | 太鐵糠榔二路(1520) |  | 79UL | [14 empty] | 0517 |  | 0025 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1520_79UL | 太鐵糠榔二路(1520) 79RY U/L | LINE161 | D07/161/1520/79UL |  |  |  | DNP | 294 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 161 | 161kV | 1520 | 太鐵糠榔二路(1520) |  | DS1 | 1521 | [13 empty] | 0696 | 697 | 0090 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1521_DS | 1521(太鐵糠榔二路) DS | LINE161 | D07/161/1520/DS1 |  |  |  | DNP | 295 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D07 | 太鐵DS | 161 | 161kV | 1520 | 太鐵糠榔二路(1520) |  | DS2 | 1522 | [13 empty] | 0698 | 699 | 0091 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1522_DS | 1522(太鐵糠榔二路) DS | LINE161 | D07/161/1520/DS2 |  |  |  | DNP | 296 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1520 | 太鐵糠榔二路(1520) |  | DS3 | 1523 | [13 empty] | 0700 | 701 | 0092 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1523_DS | 1523(太鐵糠榔二路) DS | LINE161 | D07/161/1520/DS3 |  |  |  | DNP | 297 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1520 | 太鐵糠榔二路(1520) |  | E3 | 1523E | [13 empty] | 0702 | 703 | 0093 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1523E_ES | 1523E(太鐵糠榔二路) ES | LINE161 | D07/161/1520/ES3 |  |  |  | DNP | 298 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D07 | 太鐵DS | 161 | 161kV | 1530 | 北回太鐵紅線(1530) |  | PHA | [14 empty] | 0010 | [10 empty] | 161KV_N | [8 empty] | 太鐵DS.1530_PHA | 北回太鐵紅線(1530) 相間RY | LINE161 | D07/161/1530/PHA |  |  |  | DNP | 299 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1530 | 北回太鐵紅線(1530) |  | GDA | [14 empty] | 0011 | [10 empty] | 161KV_N | [8 empty] | 太鐵DS.1530_GDA | 北回太鐵紅線(1530) 接地RY | LINE161 | D07/161/1530/GDA |  |  |  | DNP | 300 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1530 | 北回太鐵紅線(1530) |  | 87A | [14 empty] | 0009 | [10 empty] | 161KV_N | [8 empty] | 太鐵DS.1530_87A | 北回太鐵紅線(1530) 87RY | LINE161 | D07/161/1530/87A |  |  |  | DNP | 301 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1530 | 北回太鐵紅線(1530) |  | 87UL | [14 empty] | 0518 |  | 0026 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1530_87UL | 北回太鐵紅線(1530) 87RY U/L | LINE161 | D07/161/1530/87UL |  |  |  | DNP | 302 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 161 | 161kV | 1530 | 北回太鐵紅線(1530) |  | CB | [14 empty] | 0008 |  | 0004 | [8 empty] | 161KV_N | [8 empty] | 太鐵DS.1530_CB | 1530(北回太鐵紅線) CB | LINE161 | D07/161/1530/CB |  |  |  | DNP | 303 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1530 | 北回太鐵紅線(1530) |  | 79UL | [14 empty] | 0519 |  | 0027 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1530_79UL | 北回太鐵紅線(1530) 79RY U/L | LINE161 | D07/161/1530/79UL |  |  |  | DNP | 304 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 161 | 161kV | 1530 | 北回太鐵紅線(1530) |  | DS1 | 1531 | [13 empty] | 0704 | 705 | 0094 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1531_DS | 1531(北回太鐵紅線) DS | LINE161 | D07/161/1530/DS1 |  |  |  | DNP | 305 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1530 | 北回太鐵紅線(1530) |  | DS2 | 1532 | [13 empty] | 0706 | 707 | 0095 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1532_DS | 1532(北回太鐵紅線) DS | LINE161 | D07/161/1530/DS2 |  |  |  | DNP | 306 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D07 | 太鐵DS | 161 | 161kV | 1530 | 北回太鐵紅線(1530) |  | DS3 | 1533 | [13 empty] | 0708 | 709 | 0096 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1533_DS | 1533(北回太鐵紅線) DS | LINE161 | D07/161/1530/DS3 |  |  |  | DNP | 307 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1530 | 北回太鐵紅線(1530) |  | E3 | 1533E | [13 empty] | 0710 | 711 | 0097 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1533E_ES | 1533E(北回太鐵紅線) ES | LINE161 | D07/161/1530/ES3 |  |  |  | DNP | 308 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D07 | 太鐵DS | 161 | 161kV | 1540 | 北回太鐵白線(1540) |  | PHA | [14 empty] | 0014 | [10 empty] | 161KV_N | [8 empty] | 太鐵DS.1540_PHA | 北回太鐵白線(1540) 相間RY | LINE161 | D07/161/1540/PHA |  |  |  | DNP | 309 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1540 | 北回太鐵白線(1540) |  | GDA | [14 empty] | 0015 | [10 empty] | 161KV_N | [8 empty] | 太鐵DS.1540_GDA | 北回太鐵白線(1540) 接地RY | LINE161 | D07/161/1540/GDA |  |  |  | DNP | 310 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1540 | 北回太鐵白線(1540) |  | 87A | [14 empty] | 0013 | [10 empty] | 161KV_N | [8 empty] | 太鐵DS.1540_87A | 北回太鐵白線(1540) 87RY | LINE161 | D07/161/1540/87A |  |  |  | DNP | 311 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1540 | 北回太鐵白線(1540) |  | 87UL | [14 empty] | 0520 |  | 0028 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1540_87UL | 北回太鐵白線(1540) 87RY U/L | LINE161 | D07/161/1540/87UL |  |  |  | DNP | 312 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 161 | 161kV | 1540 | 北回太鐵白線(1540) |  | CB | [14 empty] | 0012 |  | 0005 | [8 empty] | 161KV_N | [8 empty] | 太鐵DS.1540_CB | 1540(北回太鐵白線) CB | LINE161 | D07/161/1540/CB |  |  |  | DNP | 313 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1540 | 北回太鐵白線(1540) |  | 79UL | [14 empty] | 0521 |  | 0029 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1540_79UL | 北回太鐵白線(1540) 79RY U/L | LINE161 | D07/161/1540/79UL |  |  |  | DNP | 314 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 161 | 161kV | 1540 | 北回太鐵白線(1540) |  | DS1 | 1541 | [13 empty] | 0712 | 713 | 0098 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1541_DS | 1541(北回太鐵白線) DS | LINE161 | D07/161/1540/DS1 |  |  |  | DNP | 315 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D07 | 太鐵DS | 161 | 161kV | 1540 | 北回太鐵白線(1540) |  | DS2 | 1542 | [13 empty] | 0714 | 715 | 0099 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1542_DS | 1542(北回太鐵白線) DS | LINE161 | D07/161/1540/DS2 |  |  |  | DNP | 316 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1540 | 北回太鐵白線(1540) |  | DS3 | 1543 | [13 empty] | 0716 | 717 | 0100 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1543_DS | 1543(北回太鐵白線) DS | LINE161 | D07/161/1540/DS3 |  |  |  | DNP | 317 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1540 | 北回太鐵白線(1540) |  | E3 | 1543E | [13 empty] | 0718 | 719 | 0101 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1543E_ES | 1543E(北回太鐵白線) ES | LINE161 | D07/161/1540/ES3 |  |  |  | DNP | 318 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D07 | 太鐵DS | 161 | 161kV | 1550 | 後壁太鐵一路(1550) |  | PHA | [14 empty] | 0018 | [10 empty] | 161KV_N | [8 empty] | 太鐵DS.1550_PHA | 後壁太鐵一路(1550) 相間RY | LINE161 | D07/161/1550/PHA |  |  |  | DNP | 319 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1550 | 後壁太鐵一路(1550) |  | GDA | [14 empty] | 0019 | [10 empty] | 161KV_N | [8 empty] | 太鐵DS.1550_GDA | 後壁太鐵一路(1550) 接地RY | LINE161 | D07/161/1550/GDA |  |  |  | DNP | 320 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1550 | 後壁太鐵一路(1550) |  | 87A | [14 empty] | 0017 | [10 empty] | 161KV_N | [8 empty] | 太鐵DS.1550_87A | 後壁太鐵一路(1550) 87RY | LINE161 | D07/161/1550/87A |  |  |  | DNP | 321 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1550 | 後壁太鐵一路(1550) |  | 87UL | [14 empty] | 0522 |  | 0030 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1550_87UL | 後壁太鐵一路(1550) 87RY U/L | LINE161 | D07/161/1550/87UL |  |  |  | DNP | 322 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 161 | 161kV | 1550 | 後壁太鐵一路(1550) |  | CB | [14 empty] | 0016 |  | 0006 | [8 empty] | 161KV_N | [8 empty] | 太鐵DS.1550_CB | 1550(後壁太鐵一路) CB | LINE161 | D07/161/1550/CB |  |  |  | DNP | 323 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1550 | 後壁太鐵一路(1550) |  | 79UL | [14 empty] | 0523 |  | 0031 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1550_79UL | 後壁太鐵一路(1550) 79RY U/L | LINE161 | D07/161/1550/79UL |  |  |  | DNP | 324 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 161 | 161kV | 1550 | 後壁太鐵一路(1550) |  | DS1 | 1551 | [13 empty] | 0720 | 721 | 0102 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1551_DS | 1551(後壁太鐵一路) DS | LINE161 | D07/161/1550/DS1 |  |  |  | DNP | 325 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1550 | 後壁太鐵一路(1550) |  | DS2 | 1552 | [13 empty] | 0722 | 723 | 0103 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1552_DS | 1552(後壁太鐵一路) DS | LINE161 | D07/161/1550/DS2 |  |  |  | DNP | 326 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D07 | 太鐵DS | 161 | 161kV | 1550 | 後壁太鐵一路(1550) |  | DS3 | 1553 | [13 empty] | 0724 | 725 | 0104 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1553_DS | 1553(後壁太鐵一路) DS | LINE161 | D07/161/1550/DS3 |  |  |  | DNP | 327 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1550 | 後壁太鐵一路(1550) |  | E3 | 1553E | [13 empty] | 0726 | 727 | 0105 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1553E_ES | 1553E(後壁太鐵一路) ES | LINE161 | D07/161/1550/ES3 |  |  |  | DNP | 328 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D07 | 太鐵DS | 161 | 161kV | 1560 | 後壁太鐵二路(1560) |  | PHA | [14 empty] | 0022 | [10 empty] | 161KV_N | [8 empty] | 太鐵DS.1560_PHA | 後壁太鐵二路(1560) 相間RY | LINE161 | D07/161/1560/PHA |  |  |  | DNP | 329 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1560 | 後壁太鐵二路(1560) |  | GDA | [14 empty] | 0023 | [10 empty] | 161KV_N | [8 empty] | 太鐵DS.1560_GDA | 後壁太鐵二路(1560) 接地RY | LINE161 | D07/161/1560/GDA |  |  |  | DNP | 330 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1560 | 後壁太鐵二路(1560) |  | 87A | [14 empty] | 0021 | [10 empty] | 161KV_N | [8 empty] | 太鐵DS.1560_87A | 後壁太鐵二路(1560) 87RY | LINE161 | D07/161/1560/87A |  |  |  | DNP | 331 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1560 | 後壁太鐵二路(1560) |  | 87UL | [14 empty] | 0524 |  | 0032 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1560_87UL | 後壁太鐵二路(1560) 87RY U/L | LINE161 | D07/161/1560/87UL |  |  |  | DNP | 332 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 161 | 161kV | 1560 | 後壁太鐵二路(1560) |  | CB | [14 empty] | 0020 |  | 0007 | [8 empty] | 161KV_N | [8 empty] | 太鐵DS.1560_CB | 1560(後壁太鐵二路) CB | LINE161 | D07/161/1560/CB |  |  |  | DNP | 333 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1560 | 後壁太鐵二路(1560) |  | 79UL | [14 empty] | 0525 |  | 0033 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1560_79UL | 後壁太鐵二路(1560) 79RY U/L | LINE161 | D07/161/1560/79UL |  |  |  | DNP | 334 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 161 | 161kV | 1560 | 後壁太鐵二路(1560) |  | DS1 | 1561 | [13 empty] | 0728 | 729 | 0106 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1561_DS | 1561(後壁太鐵二路) DS | LINE161 | D07/161/1560/DS1 |  |  |  | DNP | 335 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D07 | 太鐵DS | 161 | 161kV | 1560 | 後壁太鐵二路(1560) |  | DS2 | 1562 | [13 empty] | 0730 | 731 | 0107 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1562_DS | 1562(後壁太鐵二路) DS | LINE161 | D07/161/1560/DS2 |  |  |  | DNP | 336 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1560 | 後壁太鐵二路(1560) |  | DS3 | 1563 | [13 empty] | 0732 | 733 | 0108 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1563_DS | 1563(後壁太鐵二路) DS | LINE161 | D07/161/1560/DS3 |  |  |  | DNP | 337 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1560 | 後壁太鐵二路(1560) |  | E3 | 1563E | [13 empty] | 0734 | 735 | 0109 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1563E_ES | 1563E(後壁太鐵二路) ES | LINE161 | D07/161/1560/ES3 |  |  |  | DNP | 338 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D07 | 太鐵DS | 11 | 11kV | JV21 | 鐵21線(JV21) |  | PHA | [14 empty] | 0129 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV21_PHA | 11KV鐵21線(JV21) 相間RY | FEEDER | D07/11/JV21/PHA |  |  |  | DNP | 339 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV21 | 鐵21線(JV21) |  | GDA | [14 empty] | 0130 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV21_GDA | 11KV鐵21線(JV21) 接地RY | FEEDER | D07/11/JV21/GDA |  |  |  | DNP | 340 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV21 | 鐵21線(JV21) 79RY |  | 79UL | [14 empty] | 0898 |  | 0190 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV21_79UL | 11KV鐵21線(JV21) 79RY U/L | FEEDER | D07/11/JV21/79UL |  |  |  | DNP | 341 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 11 | 11kV | JV21_LCO | 鐵21線(JV21) LCO |  | TapPosMv | [14 empty] | 0899 |  | 0191 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV21_LCO_TAP | 11KV鐵21線(JV21) LCO TAP | FEEDER | D07/11/JV21/ADJ |  |  |  | DNP | 342 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D07 | 太鐵DS | 11 | 11kV | JV21 | JV21(11KV鐵21線) |  | CB | [14 empty] | 0128 |  | 0049 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV21_CB | JV21(11KV鐵21線) CB | FEEDER | D07/11/JV21/CB |  |  |  | DNP | 343 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | JV22 | 鐵22線(JV22) |  | PHA | [14 empty] | 0133 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV22_PHA | 11KV鐵22線(JV22) 相間RY | FEEDER | D07/11/JV22/PHA |  |  |  | DNP | 344 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV22 | 鐵22線(JV22) |  | GDA | [14 empty] | 0134 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV22_GDA | 11KV鐵22線(JV22) 接地RY | FEEDER | D07/11/JV22/GDA |  |  |  | DNP | 345 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV22 | 鐵22線(JV22) 79RY |  | 79UL | [14 empty] | 0900 |  | 0192 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV22_79UL | 11KV鐵22線(JV22) 79RY U/L | FEEDER | D07/11/JV22/79UL |  |  |  | DNP | 346 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 11 | 11kV | JV22_LCO | 鐵22線(JV22) LCO |  | TapPosMv | [14 empty] | 0901 |  | 0193 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV22_LCO_TAP | 11KV鐵22線(JV22) LCO TAP | FEEDER | D07/11/JV22/ADJ |  |  |  | DNP | 347 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D07 | 太鐵DS | 11 | 11kV | JV22 | JV22(11KV鐵22線) |  | CB | [14 empty] | 0132 |  | 0050 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV22_CB | JV22(11KV鐵22線) CB | FEEDER | D07/11/JV22/CB |  |  |  | DNP | 348 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | JV23 | 鐵23線(JV23) |  | PHA | [14 empty] | 0137 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV23_PHA | 11KV鐵23線(JV23) 相間RY | FEEDER | D07/11/JV23/PHA |  |  |  | DNP | 349 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV23 | 鐵23線(JV23) |  | GDA | [14 empty] | 0138 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV23_GDA | 11KV鐵23線(JV23) 接地RY | FEEDER | D07/11/JV23/GDA |  |  |  | DNP | 350 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV23 | 鐵23線(JV23) 79RY |  | 79UL | [14 empty] | 0902 |  | 0194 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV23_79UL | 11KV鐵23線(JV23) 79RY U/L | FEEDER | D07/11/JV23/79UL |  |  |  | DNP | 351 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 11 | 11kV | JV23_LCO | 鐵23線(JV23) LCO |  | TapPosMv | [14 empty] | 0903 |  | 0195 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV23_LCO_TAP | 11KV鐵23線(JV23) LCO TAP | FEEDER | D07/11/JV23/ADJ |  |  |  | DNP | 352 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D07 | 太鐵DS | 11 | 11kV | JV23 | JV23(11KV鐵23線) |  | CB | [14 empty] | 0136 |  | 0051 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV23_CB | JV23(11KV鐵23線) CB | FEEDER | D07/11/JV23/CB |  |  |  | DNP | 353 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | JV24 | 鐵24線(JV24) |  | PHA | [14 empty] | 0141 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV24_PHA | 11KV鐵24線(JV24) 相間RY | FEEDER | D07/11/JV24/PHA |  |  |  | DNP | 354 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV24 | 鐵24線(JV24) |  | GDA | [14 empty] | 0142 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV24_GDA | 11KV鐵24線(JV24) 接地RY | FEEDER | D07/11/JV24/GDA |  |  |  | DNP | 355 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV24 | 鐵24線(JV24) 79RY |  | 79UL | [14 empty] | 0904 |  | 0196 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV24_79UL | 11KV鐵24線(JV24) 79RY U/L | FEEDER | D07/11/JV24/79UL |  |  |  | DNP | 356 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 11 | 11kV | JV24_LCO | 鐵24線(JV24) LCO |  | TapPosMv | [14 empty] | 0905 |  | 0197 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV24_LCO_TAP | 11KV鐵24線(JV24) LCO TAP | FEEDER | D07/11/JV24/ADJ |  |  |  | DNP | 357 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D07 | 太鐵DS | 11 | 11kV | JV24 | JV24(11KV鐵24線) |  | CB | [14 empty] | 0140 |  | 0052 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV24_CB | JV24(11KV鐵24線) CB | FEEDER | D07/11/JV24/CB |  |  |  | DNP | 358 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | JV25 | 鐵25線(JV25) |  | PHA | [14 empty] | 0145 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV25_PHA | 11KV鐵25線(JV25) 相間RY | FEEDER | D07/11/JV25/PHA |  |  |  | DNP | 359 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV25 | 鐵25線(JV25) |  | GDA | [14 empty] | 0146 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV25_GDA | 11KV鐵25線(JV25) 接地RY | FEEDER | D07/11/JV25/GDA |  |  |  | DNP | 360 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV25 | 鐵25線(JV25) 79RY |  | 79UL | [14 empty] | 0906 |  | 0198 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV25_79UL | 11KV鐵25線(JV25) 79RY U/L | FEEDER | D07/11/JV25/79UL |  |  |  | DNP | 361 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 11 | 11kV | JV25_LCO | 鐵25線(JV25) LCO |  | TapPosMv | [14 empty] | 0907 |  | 0199 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV25_LCO_TAP | 11KV鐵25線(JV25) LCO TAP | FEEDER | D07/11/JV25/ADJ |  |  |  | DNP | 362 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D07 | 太鐵DS | 11 | 11kV | JV25 | JV25(11KV鐵25線) |  | CB | [14 empty] | 0144 |  | 0053 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV25_CB | JV25(11KV鐵25線) CB | FEEDER | D07/11/JV25/CB |  |  |  | DNP | 363 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | JV31 | 鐵31線(JV31) |  | PHA | [14 empty] | 0212 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV31_PHA | 11KV鐵31線(JV31) 相間RY | FEEDER | D07/11/JV31/PHA |  |  |  | DNP | 364 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV31 | 鐵31線(JV31) |  | GDA | [14 empty] | 0213 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV31_GDA | 11KV鐵31線(JV31) 接地RY | FEEDER | D07/11/JV31/GDA |  |  |  | DNP | 365 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV31 | 鐵31線(JV31) 79RY |  | 79UL | [14 empty] | 0920 |  | 0210 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV31_79UL | 11KV鐵31線(JV31) 79RY U/L | FEEDER | D07/11/JV31/79UL |  |  |  | DNP | 366 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 11 | 11kV | JV31_LCO | 鐵31線(JV31) LCO |  | TapPosMv | [14 empty] | 0921 |  | 0211 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV31_LCO_TAP | 11KV鐵31線(JV31) LCO TAP | FEEDER | D07/11/JV31/ADJ |  |  |  | DNP | 367 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D07 | 太鐵DS | 11 | 11kV | JV31 | JV31(11KV鐵31線) |  | CB | [14 empty] | 0211 |  | 0152 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV31_CB | JV31(11KV鐵31線) CB | FEEDER | D07/11/JV31/CB |  |  |  | DNP | 368 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | JV32 | 鐵32線(JV32) |  | PHA | [14 empty] | 0216 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV32_PHA | 11KV鐵32線(JV32) 相間RY | FEEDER | D07/11/JV32/PHA |  |  |  | DNP | 369 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV32 | 鐵32線(JV32) |  | GDA | [14 empty] | 0217 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV32_GDA | 11KV鐵32線(JV32) 接地RY | FEEDER | D07/11/JV32/GDA |  |  |  | DNP | 370 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV32 | 鐵32線(JV32) 79RY |  | 79UL | [14 empty] | 0922 |  | 0212 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV32_79UL | 11KV鐵32線(JV32) 79RY U/L | FEEDER | D07/11/JV32/79UL |  |  |  | DNP | 371 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 11 | 11kV | JV32_LCO | 鐵32線(JV32) LCO |  | TapPosMv | [14 empty] | 0923 |  | 0213 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV32_LCO_TAP | 11KV鐵32線(JV32) LCO TAP | FEEDER | D07/11/JV32/ADJ |  |  |  | DNP | 372 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D07 | 太鐵DS | 11 | 11kV | JV32 | JV32(11KV鐵32線) |  | CB | [14 empty] | 0215 |  | 0153 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV32_CB | JV32(11KV鐵32線) CB | FEEDER | D07/11/JV32/CB |  |  |  | DNP | 373 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | JV33 | 鐵33線(JV33) |  | PHA | [14 empty] | 0220 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV33_PHA | 11KV鐵33線(JV33) 相間RY | FEEDER | D07/11/JV33/PHA |  |  |  | DNP | 374 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV33 | 鐵33線(JV33) |  | GDA | [14 empty] | 0221 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV33_GDA | 11KV鐵33線(JV33) 接地RY | FEEDER | D07/11/JV33/GDA |  |  |  | DNP | 375 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV33 | 鐵33線(JV33) 79RY |  | 79UL | [14 empty] | 0924 |  | 0214 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV33_79UL | 11KV鐵33線(JV33) 79RY U/L | FEEDER | D07/11/JV33/79UL |  |  |  | DNP | 376 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 11 | 11kV | JV33_LCO | 鐵33線(JV33) LCO |  | TapPosMv | [14 empty] | 0925 |  | 0215 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV33_LCO_TAP | 11KV鐵33線(JV33) LCO TAP | FEEDER | D07/11/JV33/ADJ |  |  |  | DNP | 377 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D07 | 太鐵DS | 11 | 11kV | JV33 | JV33(11KV鐵33線) |  | CB | [14 empty] | 0219 |  | 0154 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV33_CB | JV33(11KV鐵33線) CB | FEEDER | D07/11/JV33/CB |  |  |  | DNP | 378 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | JV34 | 鐵34線(JV34) |  | PHA | [14 empty] | 0224 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV34_PHA | 11KV鐵34線(JV34) 相間RY | FEEDER | D07/11/JV34/PHA |  |  |  | DNP | 379 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV34 | 鐵34線(JV34) |  | GDA | [14 empty] | 0225 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV34_GDA | 11KV鐵34線(JV34) 接地RY | FEEDER | D07/11/JV34/GDA |  |  |  | DNP | 380 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV34 | 鐵34線(JV34) 79RY |  | 79UL | [14 empty] | 0926 |  | 0216 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV34_79UL | 11KV鐵34線(JV34) 79RY U/L | FEEDER | D07/11/JV34/79UL |  |  |  | DNP | 381 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 11 | 11kV | JV34_LCO | 鐵34線(JV34) LCO |  | TapPosMv | [14 empty] | 0927 |  | 0217 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV34_LCO_TAP | 11KV鐵34線(JV34) LCO TAP | FEEDER | D07/11/JV34/ADJ |  |  |  | DNP | 382 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D07 | 太鐵DS | 11 | 11kV | JV34 | JV34(11KV鐵34線) |  | CB | [14 empty] | 0223 |  | 0155 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV34_CB | JV34(11KV鐵34線) CB | FEEDER | D07/11/JV34/CB |  |  |  | DNP | 383 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | JV35 | 鐵35線(JV35) |  | PHA | [14 empty] | 0228 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV35_PHA | 11KV鐵35線(JV35) 相間RY | FEEDER | D07/11/JV35/PHA |  |  |  | DNP | 384 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV35 | 鐵35線(JV35) |  | GDA | [14 empty] | 0229 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV35_GDA | 11KV鐵35線(JV35) 接地RY | FEEDER | D07/11/JV35/GDA |  |  |  | DNP | 385 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | JV35 | 鐵35線(JV35) 79RY |  | 79UL | [14 empty] | 0928 |  | 0218 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV35_79UL | 11KV鐵35線(JV35) 79RY U/L | FEEDER | D07/11/JV35/79UL |  |  |  | DNP | 386 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 11 | 11kV | JV35_LCO | 鐵35線(JV35) LCO |  | TapPosMv | [14 empty] | 0929 |  | 0219 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV35_LCO_TAP | 11KV鐵35線(JV35) LCO TAP | FEEDER | D07/11/JV35/ADJ |  |  |  | DNP | 387 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D07 | 太鐵DS | 11 | 11kV | JV35 | JV35(11KV鐵35線) |  | CB | [14 empty] | 0227 |  | 0156 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV35_CB | JV35(11KV鐵35線) CB | FEEDER | D07/11/JV35/CB |  |  |  | DNP | 388 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | JV56 | 鐵56線(JV56) |  | PHA | [14 empty] | 0155 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV56_PHA | 23KV鐵56線(JV56) 相間RY | FEEDER | D07/22/JV56/PHA |  |  |  | DNP | 389 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV56 | 鐵56線(JV56) |  | GDA | [14 empty] | 0156 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV56_GDA | 23KV鐵56線(JV56) 接地RY | FEEDER | D07/22/JV56/GDA |  |  |  | DNP | 390 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV56 | 鐵56線(JV56) 79RY |  | 79UL | [14 empty] | 0908 |  | 0200 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV56_79UL | 23KV鐵56線(JV56) 79RY U/L | FEEDER | D07/22/JV56/79UL |  |  |  | DNP | 391 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 22 | 22kV | JV56_LCO | 鐵56線(JV56) LCO |  | TapPosMv | [14 empty] | 0909 |  | 0201 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV56_LCO_TAP | 23KV鐵56線(JV56) LCO TAP | FEEDER | D07/22/JV56/ADJ |  |  |  | DNP | 392 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D07 | 太鐵DS | 22 | 22kV | JV56 | JV56(23KV鐵56線) |  | CB | [14 empty] | 0154 |  | 0064 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV56_CB | JV56(23KV鐵56線) CB | FEEDER | D07/22/JV56/CB |  |  |  | DNP | 393 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | JV57 | 鐵57線(JV57) |  | PHA | [14 empty] | 0159 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV57_PHA | 23KV鐵57線(JV57) 相間RY | FEEDER | D07/22/JV57/PHA |  |  |  | DNP | 394 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV57 | 鐵57線(JV57) |  | GDA | [14 empty] | 0160 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV57_GDA | 23KV鐵57線(JV57) 接地RY | FEEDER | D07/22/JV57/GDA |  |  |  | DNP | 395 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV57 | 鐵57線(JV57) 79RY |  | 79UL | [14 empty] | 0910 |  | 0202 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV57_79UL | 23KV鐵57線(JV57) 79RY U/L | FEEDER | D07/22/JV57/79UL |  |  |  | DNP | 396 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 22 | 22kV | JV57_LCO | 鐵57線(JV57) LCO |  | TapPosMv | [14 empty] | 0911 |  | 0203 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV57_LCO_TAP | 23KV鐵57線(JV57) LCO TAP | FEEDER | D07/22/JV57/ADJ |  |  |  | DNP | 397 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D07 | 太鐵DS | 22 | 22kV | JV57 | JV57(23KV鐵57線) |  | CB | [14 empty] | 0158 |  | 0065 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV57_CB | JV57(23KV鐵57線) CB | FEEDER | D07/22/JV57/CB |  |  |  | DNP | 398 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | JV58 | 鐵58線(JV58) |  | PHA | [14 empty] | 0163 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV58_PHA | 23KV鐵58線(JV58) 相間RY | FEEDER | D07/22/JV58/PHA |  |  |  | DNP | 399 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV58 | 鐵58線(JV58) |  | GDA | [14 empty] | 0164 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV58_GDA | 23KV鐵58線(JV58) 接地RY | FEEDER | D07/22/JV58/GDA |  |  |  | DNP | 400 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV58 | 鐵58線(JV58) 79RY |  | 79UL | [14 empty] | 0912 |  | 0204 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV58_79UL | 23KV鐵58線(JV58) 79RY U/L | FEEDER | D07/22/JV58/79UL |  |  |  | DNP | 401 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 22 | 22kV | JV58_LCO | 鐵58線(JV58) LCO |  | TapPosMv | [14 empty] | 0913 |  | 0205 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV58_LCO_TAP | 23KV鐵58線(JV58) LCO TAP | FEEDER | D07/22/JV58/ADJ |  |  |  | DNP | 402 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D07 | 太鐵DS | 22 | 22kV | JV58 | JV58(23KV鐵58線) |  | CB | [14 empty] | 0162 |  | 0066 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV58_CB | JV58(23KV鐵58線) CB | FEEDER | D07/22/JV58/CB |  |  |  | DNP | 403 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | JV59 | 鐵59線(JV59) |  | PHA | [14 empty] | 0167 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV59_PHA | 23KV鐵59線(JV59) 相間RY | FEEDER | D07/22/JV59/PHA |  |  |  | DNP | 404 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV59 | 鐵59線(JV59) |  | GDA | [14 empty] | 0168 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV59_GDA | 23KV鐵59線(JV59) 接地RY | FEEDER | D07/22/JV59/GDA |  |  |  | DNP | 405 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV59 | 鐵59線(JV59) 79RY |  | 79UL | [14 empty] | 0914 |  | 0206 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV59_79UL | 23KV鐵59線(JV59) 79RY U/L | FEEDER | D07/22/JV59/79UL |  |  |  | DNP | 406 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 22 | 22kV | JV59_LCO | 鐵59線(JV59) LCO |  | TapPosMv | [14 empty] | 0915 |  | 0207 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV59_LCO_TAP | 23KV鐵59線(JV59) LCO TAP | FEEDER | D07/22/JV59/ADJ |  |  |  | DNP | 407 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D07 | 太鐵DS | 22 | 22kV | JV59 | JV59(23KV鐵59線) |  | CB | [14 empty] | 0166 |  | 0067 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV59_CB | JV59(23KV鐵59線) CB | FEEDER | D07/22/JV59/CB |  |  |  | DNP | 408 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | JV60 | 鐵60線(JV60) |  | PHA | [14 empty] | 0171 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV60_PHA | 23KV鐵60線(JV60) 相間RY | FEEDER | D07/22/JV60/PHA |  |  |  | DNP | 409 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV60 | 鐵60線(JV60) |  | GDA | [14 empty] | 0172 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV60_GDA | 23KV鐵60線(JV60) 接地RY | FEEDER | D07/22/JV60/GDA |  |  |  | DNP | 410 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV60 | 鐵60線(JV60) 79RY |  | 79UL | [14 empty] | 0916 |  | 0208 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV60_79UL | 23KV鐵60線(JV60) 79RY U/L | FEEDER | D07/22/JV60/79UL |  |  |  | DNP | 411 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 22 | 22kV | JV60_LCO | 鐵60線(JV60) LCO |  | TapPosMv | [14 empty] | 0917 |  | 0209 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV60_LCO_TAP | 23KV鐵60線(JV60) LCO TAP | FEEDER | D07/22/JV60/ADJ |  |  |  | DNP | 412 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D07 | 太鐵DS | 22 | 22kV | JV60 | JV60(23KV鐵60線) |  | CB | [14 empty] | 0170 |  | 0068 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV60_CB | JV60(23KV鐵60線) CB | FEEDER | D07/22/JV60/CB |  |  |  | DNP | 413 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | JV66 | 鐵66線(JV66) |  | PHA | [14 empty] | 0238 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV66_PHA | 23KV鐵66線(JV66) 相間RY | FEEDER | D07/22/JV66/PHA |  |  |  | DNP | 414 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV66 | 鐵66線(JV66) |  | GDA | [14 empty] | 0239 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV66_GDA | 23KV鐵66線(JV66) 接地RY | FEEDER | D07/22/JV66/GDA |  |  |  | DNP | 415 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV66 | 鐵66線(JV66) 79RY |  | 79UL | [14 empty] | 0930 |  | 0220 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV66_79UL | 23KV鐵66線(JV66) 79RY U/L | FEEDER | D07/22/JV66/79UL |  |  |  | DNP | 416 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 22 | 22kV | JV66_LCO | 鐵66線(JV66) LCO |  | TapPosMv | [14 empty] | 0931 |  | 0221 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV66_LCO_TAP | 23KV鐵66線(JV66) LCO TAP | FEEDER | D07/22/JV66/ADJ |  |  |  | DNP | 417 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D07 | 太鐵DS | 22 | 22kV | JV66 | JV66(23KV鐵66線) |  | CB | [14 empty] | 0237 |  | 0160 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV66_CB | JV66(23KV鐵66線) CB | FEEDER | D07/22/JV66/CB |  |  |  | DNP | 418 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | JV67 | 鐵67線(JV67) |  | PHA | [14 empty] | 0242 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV67_PHA | 23KV鐵67線(JV67) 相間RY | FEEDER | D07/22/JV67/PHA |  |  |  | DNP | 419 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV67 | 鐵67線(JV67) |  | GDA | [14 empty] | 0243 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV67_GDA | 23KV鐵67線(JV67) 接地RY | FEEDER | D07/22/JV67/GDA |  |  |  | DNP | 420 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV67 | 鐵67線(JV67) 79RY |  | 79UL | [14 empty] | 0932 |  | 0222 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV67_79UL | 23KV鐵67線(JV67) 79RY U/L | FEEDER | D07/22/JV67/79UL |  |  |  | DNP | 421 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 22 | 22kV | JV67_LCO | 鐵67線(JV67) LCO |  | TapPosMv | [14 empty] | 0933 |  | 0223 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV67_LCO_TAP | 23KV鐵67線(JV67) LCO TAP | FEEDER | D07/22/JV67/ADJ |  |  |  | DNP | 422 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D07 | 太鐵DS | 22 | 22kV | JV67 | JV67(23KV鐵67線) |  | CB | [14 empty] | 0241 |  | 0161 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV67_CB | JV67(23KV鐵67線) CB | FEEDER | D07/22/JV67/CB |  |  |  | DNP | 423 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | JV68 | 鐵68線(JV68) |  | PHA | [14 empty] | 0246 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV68_PHA | 23KV鐵68線(JV68) 相間RY | FEEDER | D07/22/JV68/PHA |  |  |  | DNP | 424 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV68 | 鐵68線(JV68) |  | GDA | [14 empty] | 0247 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV68_GDA | 23KV鐵68線(JV68) 接地RY | FEEDER | D07/22/JV68/GDA |  |  |  | DNP | 425 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV68 | 鐵68線(JV68) 79RY |  | 79UL | [14 empty] | 0934 |  | 0224 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV68_79UL | 23KV鐵68線(JV68) 79RY U/L | FEEDER | D07/22/JV68/79UL |  |  |  | DNP | 426 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 22 | 22kV | JV68_LCO | 鐵68線(JV68) LCO |  | TapPosMv | [14 empty] | 0935 |  | 0225 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV68_LCO_TAP | 23KV鐵68線(JV68) LCO TAP | FEEDER | D07/22/JV68/ADJ |  |  |  | DNP | 427 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D07 | 太鐵DS | 22 | 22kV | JV68 | JV68(23KV鐵68線) |  | CB | [14 empty] | 0245 |  | 0162 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV68_CB | JV68(23KV鐵68線) CB | FEEDER | D07/22/JV68/CB |  |  |  | DNP | 428 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | JV69 | 鐵69線(JV69) |  | PHA | [14 empty] | 0250 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV69_PHA | 23KV鐵69線(JV69) 相間RY | FEEDER | D07/22/JV69/PHA |  |  |  | DNP | 429 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV69 | 鐵69線(JV69) |  | GDA | [14 empty] | 0251 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV69_GDA | 23KV鐵69線(JV69) 接地RY | FEEDER | D07/22/JV69/GDA |  |  |  | DNP | 430 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV69 | 鐵69線(JV69) 79RY |  | 79UL | [14 empty] | 0936 |  | 0226 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV69_79UL | 23KV鐵69線(JV69) 79RY U/L | FEEDER | D07/22/JV69/79UL |  |  |  | DNP | 431 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 22 | 22kV | JV69_LCO | 鐵69線(JV69) LCO |  | TapPosMv | [14 empty] | 0937 |  | 0227 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV69_LCO_TAP | 23KV鐵69線(JV69) LCO TAP | FEEDER | D07/22/JV69/ADJ |  |  |  | DNP | 432 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D07 | 太鐵DS | 22 | 22kV | JV69 | JV69(23KV鐵69線) |  | CB | [14 empty] | 0249 |  | 0163 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV69_CB | JV69(23KV鐵69線) CB | FEEDER | D07/22/JV69/CB |  |  |  | DNP | 433 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | JV70 | 鐵70線(JV70) |  | PHA | [14 empty] | 0254 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV70_PHA | 23KV鐵70線(JV70) 相間RY | FEEDER | D07/22/JV70/PHA |  |  |  | DNP | 434 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV70 | 鐵70線(JV70) |  | GDA | [14 empty] | 0255 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV70_GDA | 23KV鐵70線(JV70) 接地RY | FEEDER | D07/22/JV70/GDA |  |  |  | DNP | 435 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | JV70 | 鐵70線(JV70) 79RY |  | 79UL | [14 empty] | 0938 |  | 0228 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV70_79UL | 23KV鐵70線(JV70) 79RY U/L | FEEDER | D07/22/JV70/79UL |  |  |  | DNP | 436 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 22 | 22kV | JV70_LCO | 鐵70線(JV70) LCO |  | TapPosMv | [14 empty] | 0939 |  | 0229 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV70_LCO_TAP | 23KV鐵70線(JV70) LCO TAP | FEEDER | D07/22/JV70/ADJ |  |  |  | DNP | 437 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D07 | 太鐵DS | 22 | 22kV | JV70 | JV70(23KV鐵70線) |  | CB | [14 empty] | 0253 |  | 0164 | [8 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV70_CB | JV70(23KV鐵70線) CB | FEEDER | D07/22/JV70/CB |  |  |  | DNP | 438 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | 100 | TIE(100) |  | CB | [14 empty] | 0234 |  | 0150 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.100_CB | 100(TIE) CB | TIE | D07/11/100/CB |  |  |  | DNP | 439 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | 100 | TIE(100) |  | 51A | [14 empty] | 0235 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.100_51A | 11KV TIE(100) 51RY | TIE | D07/11/100/PHA |  |  |  | DNP | 440 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 100 | TIE(100) |  | 51NA | [14 empty] | 0236 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.100_51NA | 11KV TIE(100) 51N RY | TIE | D07/11/100/GDA |  |  |  | DNP | 441 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [14 empty] | 0050 |  | 0014 | [8 empty] | 161KV_N | [8 empty] | 太鐵DS.1500_CB | 1500(TIE) CB | TIE | D07/161/1500/CB |  |  |  | DNP | 442 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | 1500 | TIE(1500) |  | 50A | [14 empty] | 0051 | [10 empty] | 161KV_N | [8 empty] | 太鐵DS.1500_50A | 161KV TIE(1500) 50RY | TIE | D07/161/1500/50A |  |  |  | DNP | 443 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [13 empty] | 0784 | 785 | 0134 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1501_DS | 1501(TIE) DS | TIE | D07/161/1500/DS1 |  |  |  | DNP | 444 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [13 empty] | 0786 | 787 | 0135 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1502_DS | 1502(TIE) DS | TIE | D07/161/1500/DS2 |  |  |  | DNP | 445 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 0 |  | 1500 | TIE(1500) |  | 50SA | [14 empty] | 0567 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.1500_50SA | 161KV TIE(1500) 50RY 測試/正常 | TIE | D07/161/1500/50SA |  |  |  | DNP | 446 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TEST/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 200 | TIE(200) |  | CB | [14 empty] | 0260 |  | 0157 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.200_CB | 200(TIE) CB | TIE | D07/22/200/CB |  |  |  | DNP | 447 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | 200 | TIE(200) |  | 51A | [14 empty] | 0261 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.200_51A | 23KV TIE(200) 51RY | TIE | D07/22/200/PHA |  |  |  | DNP | 448 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 200 | TIE(200) |  | 51NA | [14 empty] | 0262 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.200_51NA | 23KV TIE(200) 51N RY | TIE | D07/22/200/GDA |  |  |  | DNP | 449 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 390 | #1SSTR(390) |  | CB | [14 empty] | 0151 |  | 0046 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.390_CB | 390(#1SSTR) CB | OTHER | D07/11/390/CB |  |  |  | DNP | 450 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | 1SSTR | #1SSTR |  | 51A | [14 empty] | 0152 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.#1SSTR_51A | #1SSTR 51RY | OTHER | D07/11/390/PHA |  |  |  | DNP | 451 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 1SSTR | #1SSTR |  | 51NA | [14 empty] | 0153 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | D07/11/390/GDA |  |  |  | DNP | 452 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 490 | #2SSTR(490) |  | CB | [14 empty] | 0263 |  | 0158 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.490_CB | 490(#2SSTR) CB | OTHER | D07/22/490/CB |  |  |  | DNP | 453 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | 2SSTR | #2SSTR |  | 51A | [14 empty] | 0264 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.#2SSTR_51A | #2SSTR 51RY | OTHER | D07/22/490/PHA |  |  |  | DNP | 454 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 2SSTR | #2SSTR |  | 51NA | [14 empty] | 0265 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | D07/22/490/GDA |  |  |  | DNP | 455 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB | [14 empty] | 0058 |  | 0015 | [8 empty] | 161KV_N | [8 empty] | 太鐵DS.1750_CB | 1750(#1DTR) CB | MTR | D07/161/1750/CB |  |  |  | DNP | 456 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | 310 | #1DTR(310) |  | CB | [14 empty] | 0066 |  | 0047 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.310_CB | 310(#1DTR) CB | MTR | D07/11/310/CB |  |  |  | DNP | 457 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | 320 | #1DTR(320) |  | CB | [14 empty] | 0070 |  | 0062 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.320_CB | 320(#1DTR) CB | MTR | D07/22/320/CB |  |  |  | DNP | 458 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | 1DTR | #1DTR |  | 51A | [14 empty] | 0062 | [10 empty] | 161KV_N | [8 empty] | 太鐵DS.#1DTR_51A | #1DTR 51RY | MTR | D07//1DTR/PHA |  |  |  | DNP | 459 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 1DTR | #1DTR |  | 51NA | [14 empty] | 0063 | [10 empty] | 161KV_N | [8 empty] | 太鐵DS.#1DTR_51NA | #1DTR 51N RY | MTR | D07//1DTR/GDA |  |  |  | DNP | 460 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 1DTR | #1DTR |  | 51ZA | [14 empty] | 0061 | [10 empty] | 161KV_N | [8 empty] | 太鐵DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | D07//1DTR/51ZA |  |  |  | DNP | 461 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 1DTR | #1DTR |  | 87A | [14 empty] | 0059 | [10 empty] | 161KV_N | [8 empty] | 太鐵DS.#1DTR_87A | #1DTR 87RY | MTR | D07//1DTR/87A |  |  |  | DNP | 462 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 310 | #1DTR(310) |  | 51A | [14 empty] | 0064 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.310_51A | #1DTR二次側(310) 51RY | MTR | D07/11/310/51A |  |  |  | DNP | 463 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 320 | #1DTR(320) |  | 51A | [14 empty] | 0065 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.320_51A | #1DTR二次側(320) 51RY | MTR | D07/22/320/51A |  |  |  | DNP | 464 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 1DTR | #1DTR |  | 96PA | [14 empty] | 0060 | [10 empty] | 161KV_N | [8 empty] | 太鐵DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | D07//1DTR/96PA |  |  |  | DNP | 465 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 1DTR | #1DTR |  | 96D | [14 empty] | 0577 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.#1DTR_96D | #1DTR 96D RY | MTR | D07//1DTR/96D |  |  |  | DNP | 466 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 1DTR | #1DTR |  | 96P | [14 empty] | 0578 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.#1DTR_96P | #1DTR 96P RY | MTR | D07//1DTR/96P |  |  |  | DNP | 467 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 1DTR | #1DTR |  | 63Q | [14 empty] | 0579 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.#1DTR_63Q | #1DTR 63Q RY | MTR | D07//1DTR/63Q |  |  |  | DNP | 468 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 1DTR | #1DTR |  | 96B1 | [14 empty] | 0575 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | D07//1DTR/96B1 |  |  |  | DNP | 469 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 1DTR | #1DTR |  | 96B2 | [14 empty] | 0576 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | D07//1DTR/96B2 |  |  |  | DNP | 470 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 1DTR | #1DTR |  | TRA | [14 empty] | 0581 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.#1DTR_TRA | #1DTR 重故障 | MTR | D07//1DTR/TRA |  |  |  | DNP | 471 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 1DTR | #1DTR |  | TRF | [14 empty] | 0580 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.#1DTR_TRF | #1DTR 輕故障 | MTR | D07//1DTR/TRF |  |  |  | DNP | 472 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 1DTR(A) | #1DTR(A) |  | SupLocal | [14 empty] | 0571 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | D07//1DTR(A)/SupLocal |  |  |  | DNP | 473 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D07 | 太鐵DS | 0 |  | 1DTR(A) | #1DTR(A) |  | A_M | [14 empty] | 0572 |  | 0074 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | D07//1DTR(A)/Tap Chan |  |  |  | DNP | 474 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D07 | 太鐵DS | 0 |  | 1DTR(B) | #1DTR(B) |  | SupLocal | [14 empty] | 0573 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | D07//1DTR(B)/SupLocal |  |  |  | DNP | 475 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D07 | 太鐵DS | 0 |  | 1DTR(B) | #1DTR(B) |  | A_M | [14 empty] | 0574 |  | 0076 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | D07//1DTR(B)/Tap Chan |  |  |  | DNP | 476 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D07 | 太鐵DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 | [13 empty] | 0788 | 789 | 0136 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1751_DS | 1751(#1DTR) DS | MTR | D07/161/1750/DS1 |  |  |  | DNP | 477 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 | [13 empty] | 0790 | 791 | 0137 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1752_DS | 1752(#1DTR) DS | MTR | D07/161/1750/DS2 |  |  |  | DNP | 478 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D07 | 太鐵DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB | [14 empty] | 0074 |  | 0016 | [8 empty] | 161KV_N | [8 empty] | 太鐵DS.1760_CB | 1760(#2DTR) CB | MTR | D07/161/1760/CB |  |  |  | DNP | 479 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | 330 | #2DTR(330) |  | CB | [14 empty] | 0082 |  | 0069 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.330_CB | 330(#2DTR) CB | MTR | D07/11/330/CB |  |  |  | DNP | 480 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | 340 | #2DTR(340) |  | CB | [14 empty] | 0086 |  | 0070 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.340_CB | 340(#2DTR) CB | MTR | D07/22/340/CB |  |  |  | DNP | 481 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | 2DTR | #2DTR |  | 51A | [14 empty] | 0078 | [10 empty] | 161KV_N | [8 empty] | 太鐵DS.#2DTR_51A | #2DTR 51RY | MTR | D07//2DTR/PHA |  |  |  | DNP | 482 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 2DTR | #2DTR |  | 51NA | [14 empty] | 0079 | [10 empty] | 161KV_N | [8 empty] | 太鐵DS.#2DTR_51NA | #2DTR 51N RY | MTR | D07//2DTR/GDA |  |  |  | DNP | 483 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 2DTR | #2DTR |  | 51ZA | [14 empty] | 0077 | [10 empty] | 161KV_N | [8 empty] | 太鐵DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | D07//2DTR/51ZA |  |  |  | DNP | 484 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 2DTR | #2DTR |  | 87A | [14 empty] | 0075 | [10 empty] | 161KV_N | [8 empty] | 太鐵DS.#2DTR_87A | #2DTR 87RY | MTR | D07//2DTR/87A |  |  |  | DNP | 485 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 330 | #2DTR(330) |  | 51A | [14 empty] | 0080 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.330_51A | #2DTR二次側(330) 51RY | MTR | D07/11/330/51A |  |  |  | DNP | 486 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 340 | #2DTR(340) |  | 51A | [14 empty] | 0081 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.340_51A | #2DTR二次側(340) 51RY | MTR | D07/22/340/51A |  |  |  | DNP | 487 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 2DTR | #2DTR |  | 96PA | [14 empty] | 0076 | [10 empty] | 161KV_N | [8 empty] | 太鐵DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | D07//2DTR/96PA |  |  |  | DNP | 488 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 2DTR | #2DTR |  | 96D | [14 empty] | 0589 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.#2DTR_96D | #2DTR 96D RY | MTR | D07//2DTR/96D |  |  |  | DNP | 489 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 2DTR | #2DTR |  | 96P | [14 empty] | 0590 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.#2DTR_96P | #2DTR 96P RY | MTR | D07//2DTR/96P |  |  |  | DNP | 490 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 2DTR | #2DTR |  | 63Q | [14 empty] | 0591 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.#2DTR_63Q | #2DTR 63Q RY | MTR | D07//2DTR/63Q |  |  |  | DNP | 491 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 2DTR | #2DTR |  | 96B1 | [14 empty] | 0587 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | D07//2DTR/96B1 |  |  |  | DNP | 492 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 2DTR | #2DTR |  | 96B2 | [14 empty] | 0588 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | D07//2DTR/96B2 |  |  |  | DNP | 493 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 2DTR | #2DTR |  | TRA | [14 empty] | 0593 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.#2DTR_TRA | #2DTR 重故障 | MTR | D07//2DTR/TRA |  |  |  | DNP | 494 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 2DTR | #2DTR |  | TRF | [14 empty] | 0592 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.#2DTR_TRF | #2DTR 輕故障 | MTR | D07//2DTR/TRF |  |  |  | DNP | 495 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 2DTR(A) | #2DTR(A) |  | SupLocal | [14 empty] | 0583 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | D07//2DTR(A)/SupLocal |  |  |  | DNP | 496 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D07 | 太鐵DS | 0 |  | 2DTR(A) | #2DTR(A) |  | A_M | [14 empty] | 0584 |  | 0078 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | D07//2DTR(A)/Tap Chan |  |  |  | DNP | 497 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D07 | 太鐵DS | 0 |  | 2DTR(B) | #2DTR(B) |  | SupLocal | [14 empty] | 0585 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | D07//2DTR(B)/SupLocal |  |  |  | DNP | 498 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D07 | 太鐵DS | 0 |  | 2DTR(B) | #2DTR(B) |  | A_M | [14 empty] | 0586 |  | 0080 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | D07//2DTR(B)/Tap Chan |  |  |  | DNP | 499 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D07 | 太鐵DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 | [13 empty] | 0792 | 793 | 0138 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1761_DS | 1761(#2DTR) DS | MTR | D07/161/1760/DS1 |  |  |  | DNP | 500 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D07 | 太鐵DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 | [13 empty] | 0794 | 795 | 0139 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1762_DS | 1762(#2DTR) DS | MTR | D07/161/1760/DS2 |  |  |  | DNP | 501 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 11 | 11kV | 210 | #1SC(210) |  | CB | [14 empty] | 0148 |  | 0048 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.210_CB | 210(11KV #1SC) CB | SC | D07/11/210/CB |  |  |  | DNP | 502 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [14 empty] | 0149 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.210_SCA | 11KV #1SC 51,51N RY | SC | D07/11/210/SCA |  |  |  | DNP | 503 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [14 empty] | 0150 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.210_OUVA | 11KV #1SC 27,59RY(欠壓或過壓) | SC | D07/11/210/UVA |  |  |  | DNP | 504 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | 210 | #1SC(210) |  | LBS | [14 empty] | 0804 | 805 | 0146 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.210_LBS | 210(11KV #1SC) LBS | SC | D07/11/210/5A5Other |  |  |  | DNP | 505 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 11 | 11kV | 230 | #3SC(230) |  | CB | [14 empty] | 0231 |  | 0151 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.230_CB | 230(11KV #3SC) CB | SC | D07/11/230/CB |  |  |  | DNP | 506 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 11 | 11kV | 230 | #3SC(230) |  | SCA | [14 empty] | 0232 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.230_SCA | 11KV #3SC 51,51N RY | SC | D07/11/230/SCA |  |  |  | DNP | 507 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | 230 | #3SC(230) |  | UVA | [14 empty] | 0233 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.230_OUVA | 11KV #3SC 27,59RY(欠壓或過壓) | SC | D07/11/230/UVA |  |  |  | DNP | 508 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | 230 | #3SC(230) |  | LBS | [14 empty] | 0808 | 809 | 0148 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.230_LBS | 230(11KV #3SC) LBS | SC | D07/11/230/6A5Other |  |  |  | DNP | 509 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 22 | 22kV | 220 | #2SC(220) |  | CB | [14 empty] | 0208 |  | 0063 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.220_CB | 220(23KV #2SC) CB | SC | D07/22/220/CB |  |  |  | DNP | 510 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | 220 | #2SC(220) |  | SCA | [14 empty] | 0209 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.220_SCA | 23KV #2SC 51,51N RY | SC | D07/22/220/SCA |  |  |  | DNP | 511 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | 220 | #2SC(220) |  | UVA | [14 empty] | 0210 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.220_OUVA | 23KV #2SC 27,59RY(欠壓或過壓) | SC | D07/22/220/UVA |  |  |  | DNP | 512 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | 240 | #4SC(240) |  | CB | [14 empty] | 0257 |  | 0159 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.240_CB | 240(23KV #4SC) CB | SC | D07/22/240/CB |  |  |  | DNP | 513 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 22 | 22kV | 240 | #4SC(240) |  | SCA | [14 empty] | 0258 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.240_SCA | 23KV #4SC 51,51N RY | SC | D07/22/240/SCA |  |  |  | DNP | 514 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | 240 | #4SC(240) |  | UVA | [14 empty] | 0259 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.240_OUVA | 23KV #4SC 27,59RY(欠壓或過壓) | SC | D07/22/240/UVA |  |  |  | DNP | 515 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1611BUS | #1BUS |  | VUA | [14 empty] | 0635 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | D07/161/1BUS/BUS_VUA |  |  |  | DNP | 516 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1611BUS | #1BUS |  | 87A | [14 empty] | 0052 | [10 empty] | 161KV_N | [8 empty] | 太鐵DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | D07/161/1BUS/87A |  |  |  | DNP | 517 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1611BUS | #1BUS |  | 87UL | [14 empty] | 0565 |  | 0188 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | D07/161/1BUS/87UL |  |  |  | DNP | 518 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 161 | 161kV | 1612BUS | #2BUS |  | VUA | [14 empty] | 0636 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | D07/161/2BUS/BUS_VUA |  |  |  | DNP | 519 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1612BUS | #2BUS |  | 87A | [14 empty] | 0053 | [10 empty] | 161KV_N | [8 empty] | 太鐵DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | D07/161/2BUS/87A |  |  |  | DNP | 520 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1612BUS | #2BUS |  | 87UL | [14 empty] | 0566 |  | 0189 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | D07/161/2BUS/87UL |  |  |  | DNP | 521 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 22 | 22kV | 11_ | 11/ |  | CBA | [14 empty] | 0559 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | D07/0/ComPoint/CBA |  |  |  | DNP | 522 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | 11_ | 11/ |  | CBF | [14 empty] | 0560 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | D07/0/ComPoint/CBF |  |  |  | DNP | 523 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV |  |  |  | CBA | [14 empty] | 0631 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.161KV_CBA | 161KV斷路器重故障 | OTHER | D07/161/ComPoint/CBA |  |  |  | DNP | 524 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV |  |  |  | CBF | [14 empty] | 0632 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | D07/161/ComPoint/CBF |  |  |  | DNP | 525 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | LINE | LINE |  | RCA | [14 empty] | 0055 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | D07/161/ComPoint/RCA |  |  |  | DNP | 526 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | _SC | 11/ SC |  | 60A | [14 empty] | 0558 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.23KV_SC_60A | 11/23KV SC 60A | OTHER | D07/0/ComPoint/60A |  |  |  | DNP | 527 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | RTU | RTU |  | SupLocal | [14 empty] | 0513 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.RTU_S/L | RTU SUPY/LOCAL | OTHER | D07/0/RTU/RTU_R_L |  |  |  | DNP | 528 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D07 | 太鐵DS | 0 |  | TEST | TEST |  | CB | [14 empty] | 0512 |  | 0000 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.TEST_CB | TEST CB | OTHER | D07/0/RTU/Test_CB |  |  |  | DNP | 529 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  |  |  |  | Fire1 | [14 empty] | 0614 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | D07/0/StaDev/Fire1 |  |  |  | DNP | 530 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  |  |  |  | Fire2 | [14 empty] | 0615 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.火災警報(2) | 火災警報(2) | OTHER | D07/0/StaDev/Fire2 |  |  |  | DNP | 531 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  |  |  |  | Fire3 | [14 empty] | 0616 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.火災警報(3) | 火災警報(3) | OTHER | D07/0/StaDev/Fire3 |  |  |  | DNP | 532 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  |  |  |  | Fire4 | [14 empty] | 0617 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.火災警報(4) | 火災警報(4) | OTHER | D07/0/StaDev/Fire4 |  |  |  | DNP | 533 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  |  |  |  | 火災警報(5) | [14 empty] | 0618 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.火災警報(5) | 火災警報(5) | OTHER | D07/0/StaDev/Fire5 |  |  |  | DNP | 534 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  |  |  |  | 25PFA | [14 empty] | 0369 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER | D07/161/ComPoint/25TA |  |  |  | DNP | 535 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  |  |  |  | 25TA | [14 empty] | 0368 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | D07/161/ComPoint/25PFA |  |  |  | DNP | 536 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  |  |  |  | ACB1 | [14 empty] | 0626 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | D07/0/StaDev/ACB1 |  |  |  | DNP | 537 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ON/OFF | ON
D07 | 太鐵DS | 0 |  |  |  |  | ACB2 | [14 empty] | 0627 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | D07/0/StaDev/ACB2 |  |  |  | DNP | 538 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ON/OFF | ON
D07 | 太鐵DS | 0 |  |  |  |  | ACBA | [14 empty] | 0634 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.所內電源ACBA | 所內電源故障警報 | OTHER | D07/0/StaDev/ACBA |  |  |  | DNP | 539 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 所內電源開關ACB | 所內電源開關ACB |  | ACBT | [14 empty] | 0628 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | D07/0/StaDev/ACBT |  |  |  | DNP | 540 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ON/OFF | OFF
D07 | 太鐵DS | 0 |  |  |  |  | STUV | [14 empty] | 0630 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | D07/0/StaDev/STUV |  |  |  | DNP | 541 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  |  |  |  | CHG1 | [14 empty] | 0637 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.直流充電機故障 | 直流充電機故障 | OTHER | D07/0/StaDev/CHG1 |  |  |  | DNP | 542 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  |  |  |  | DCA | [14 empty] | 0633 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.直流電源DCA | 直流電源故障警報 | OTHER | D07/0/StaDev/DCA |  |  |  | DNP | 543 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  |  |  |  | DCE | [14 empty] | 0638 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.直流電源DCE | 直流電源接地故障警報 | OTHER | D07/0/StaDev/DCE |  |  |  | DNP | 544 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  |  |  |  | CHG2 | [14 empty] | 0651 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | D07/0/StaDev/CHG2 |  |  |  | DNP | 545 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  |  |  |  | CommACF | [14 empty] | 0652 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | D07/0/StaDev/CommACF |  |  |  | DNP | 546 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  |  |  |  | Burglar1 | [14 empty] | 0621 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | D07/0/StaDev/Door3 |  |  |  | DNP | 547 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  |  |  |  | Door1 | [14 empty] | 0619 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.無人化門禁(1) | 無人化門禁(1)圍牆大門 | OTHER | D07/0/StaDev/Door1 |  |  |  | DNP | 548 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
D07 | 太鐵DS | 0 |  |  |  |  | Door2 | [14 empty] | 0620 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.無人化門禁(2) | 無人化門禁(2)建築物大小門 | OTHER | D07/0/StaDev/Door2 |  |  |  | DNP | 549 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
D07 | 太鐵DS | 0 |  | 1520 | 太鐵糠榔二路(1520) |  | 87CFA | [14 empty] | 0538 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.1520_87CFA | 太鐵糠榔二路(1520)87RY通訊故障 | OTHER | D07/161/1520/87CFA |  |  |  | DNP | 550 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 1520 | 太鐵糠榔二路(1520) |  | RYFA | [14 empty] | 0539 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.1520_RYFA | 太鐵糠榔二路(1520)數位電驛故障 | OTHER | D07/161/1520/RYFA |  |  |  | DNP | 551 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 1530 | 北回太鐵紅線(1530) |  | 87CFA | [14 empty] | 0540 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.1530_87CFA | 北回太鐵紅線(1530)87RY通訊故障 | OTHER | D07/161/1530/87CFA |  |  |  | DNP | 552 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 1530 | 北回太鐵紅線(1530) |  | RYFA | [14 empty] | 0541 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.1530_RYFA | 北回太鐵紅線(1530)數位電驛故障 | OTHER | D07/161/1530/RYFA |  |  |  | DNP | 553 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 1540 | 北回太鐵白線(1540) |  | 87CFA | [14 empty] | 0542 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.1540_87CFA | 北回太鐵白線(1540)87RY通訊故障 | OTHER | D07/161/1540/87CFA |  |  |  | DNP | 554 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 1540 | 北回太鐵白線(1540) |  | RYFA | [14 empty] | 0543 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.1540_RYFA | 北回太鐵白線(1540)數位電驛故障 | OTHER | D07/161/1540/RYFA |  |  |  | DNP | 555 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 1550 | 後壁太鐵一路(1550) |  | 87CFA | [14 empty] | 0544 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.1550_87CFA | 後壁太鐵一路(1550)87RY通訊故障 | OTHER | D07/161/1550/87CFA |  |  |  | DNP | 556 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 1550 | 後壁太鐵一路(1550) |  | RYFA | [14 empty] | 0545 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.1550_RYFA | 後壁太鐵一路(1550)數位電驛故障 | OTHER | D07/161/1550/RYFA |  |  |  | DNP | 557 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 1560 | 後壁太鐵二路(1560) |  | 87CFA | [14 empty] | 0546 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.1560_87CFA | 後壁太鐵二路(1560)87RY通訊故障 | OTHER | D07/161/1560/87CFA |  |  |  | DNP | 558 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 1560 | 後壁太鐵二路(1560) |  | RYFA | [14 empty] | 0547 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.1560_RYFA | 後壁太鐵二路(1560)數位電驛故障 | OTHER | D07/161/1560/RYFA |  |  |  | DNP | 559 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | _OSCA | _OSCA |  | 1 | [14 empty] | 0056 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.161KV_OSCA_1 | 161KV示波器啟動警報 | OTHER | D07/161/ComPoint/OSCA |  |  |  | DNP | 560 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | _OSCF | _OSCF |  | 1 | [14 empty] | 0647 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.161KV_OSCF_1 | 161KV示波器故障/缺紙(1) | OTHER | D07/161/ComPoint/OSCF1 |  |  |  | DNP | 561 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | _OSCF | _OSCF | [16 empty] | 0648 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.161KV_OSCF_2 | 161KV示波器故障/缺紙(2) | OTHER | D07/161/ComPoint/OSCF2 |  |  |  | DNP | 562 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 22 | 22kV | 11_ | 11/ |  | LOA | [14 empty] | 0561 | [10 empty] | DDCS2_1 | [8 empty] | 太鐵DS.11/23KV_LOA | 11/23KV饋線復閉失敗閉鎖 | OTHER | D07/0/ComPoint/LOA |  |  |  | DNP | 563 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 310 | #1DTR(310) |  | GDA | [14 empty] | 0068 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.310_GDA | 310開關箱IED RY GDA | OTHER | D07/11/310/GDA |  |  |  | DNP | 564 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 310 | #1DTR(310) |  | PHA2 | [14 empty] | 0067 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.310_PHA2 | 310開關箱IED RY PHA | OTHER | D07/11/310/PHA |  |  |  | DNP | 565 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 320 | #1DTR(320) |  | GDA | [14 empty] | 0072 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.320_GDA | 320開關箱IED RY GDA | OTHER | D07/22/320/GDA |  |  |  | DNP | 566 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 320 | #1DTR(320) |  | PHA2 | [14 empty] | 0071 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.320_PHA2 | 320開關箱IED RY PHA | OTHER | D07/22/320/PHA |  |  |  | DNP | 567 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 330 | #2DTR(330) |  | GDA | [14 empty] | 0084 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.330_GDA | 330開關箱IED RY GDA | OTHER | D07/11/330/GDA |  |  |  | DNP | 568 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 330 | #2DTR(330) |  | PHA2 | [14 empty] | 0083 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.330_PHA2 | 330開關箱IED RY PHA | OTHER | D07/11/330/PHA |  |  |  | DNP | 569 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 340 | #2DTR(340) |  | GDA | [14 empty] | 0088 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.340_GDA | 340開關箱IED RY GDA | OTHER | D07/22/340/GDA |  |  |  | DNP | 570 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 340 | #2DTR(340) |  | PHA2 | [14 empty] | 0087 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.340_PHA2 | 340開關箱IED RY PHA | OTHER | D07/22/340/PHA |  |  |  | DNP | 571 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  |  |  |  | 水位警報(1) | [14 empty] | 0556 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.水位警報(1) | 地下室水位警報(1) | OTHER | D07/0/StaDev/Water1 |  |  |  | DNP | 572 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  |  |  |  | 水位警報(2) | [14 empty] | 0557 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.水位警報(2) | 地下室水位警報(2) | OTHER | D07/0/StaDev/Water2 |  |  |  | DNP | 573 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  |  |  |  | 通信機房溫度 | [14 empty] | 0655 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.通信機房溫度 | 通訊室或控制室溫度警報 | OTHER | D07/0/StaDev/R_Temp |  |  |  | DNP | 574 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  |  |  |  | 蓄油池警報(1) | [14 empty] | 0562 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.蓄油池警報(1) | 蓄油池水位警報(1) | OTHER | D07/0/StaDev/OilLeak1 |  |  |  | DNP | 575 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  |  |  |  | 蓄油池警報(2) | [14 empty] | 0563 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.蓄油池警報(2) | 蓄油池水位警報(2) | OTHER | D07/0/StaDev/OilLeak2 |  |  |  | DNP | 576 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | _OSCA | _OSCA | [16 empty] | 0057 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.161KV_OSCA_2 | 161KV示波器啟動警報(2) | OTHER |  |  |  |  | DNP | 577 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  |  |  |  | PMA | [14 empty] | 0646 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.PMA | 電力量測表計故障 | OTHER | D07/0/StaDev/PMA |  |  |  | DNP | 578 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  |  |  |  | GEN | [14 empty] | 0640 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.GEN | 緊急發電機運轉 | OTHER | D07/0/StaDev/2A5Other |  |  |  | DNP | 579 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ON/OFF | OFF
D07 | 太鐵DS | 161 | 161kV | 1SHR | #1SHR |  | 161#1SHR96PA | [14 empty] | 0114 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.161#1SHR96PA | 161KV #1SHR 機械保護動作 | OTHER | D07/161/1950/96PA |  |  |  | DNP | 580 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1611SHR | #1SHR |  | 187UL | [14 empty] | 0663 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.161#1SHR_187UL | 161KV #1SHR 187RY U/L | OTHER | D07/161/1950/1_87UL1 |  |  |  | DNP | 581 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 161 | 161kV | 1611SHR | #1SHR |  | 287UL | [14 empty] | 0664 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.161#1SHR_287UL | 161KV #1SHR 287RY U/L | OTHER | D07/161/1950/1_87UL2 |  |  |  | DNP | 582 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 161 | 161kV | 1611SHR | #1SHR |  | 51A | [14 empty] | 0116 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.161#1SHR_51A | 161KV #1SHR 51RY | OTHER | D07/161/1950/51A |  |  |  | DNP | 583 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1611SHR | #1SHR |  | 86A | [14 empty] | 0115 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.161#1SHR_86A | 161KV #1SHR 86RY | OTHER | D07/161/1SHR/1A5Other |  |  |  | DNP | 584 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1611SHR | #1SHR |  | 87A | [14 empty] | 0113 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.161#1SHR_87A | 161KV #1SHR 87RY | OTHER | D07/161/1950/87A |  |  |  | DNP | 585 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1611SHR | #1SHR |  | 96B1 | [14 empty] | 0656 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.161#1SHR_96B1 | 161KV #1SHR 96B1 RY | OTHER | D07/161/1950/96B1 |  |  |  | DNP | 586 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1611SHR | #1SHR |  | 96B2 | [14 empty] | 0657 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.161#1SHR_96B2 | 161KV #1SHR 96B2 RY | OTHER | D07/161/1950/96B2 |  |  |  | DNP | 587 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1611SHR | #1SHR |  | 96D | [14 empty] | 0658 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.161#1SHR_96D | 161KV #1SHR 96D RY | OTHER | D07/161/1950/96D |  |  |  | DNP | 588 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1611SHR | #1SHR |  | 96P | [14 empty] | 0659 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.161#1SHR_96P | 161KV #1SHR 96P RY | OTHER | D07/161/1950/96P |  |  |  | DNP | 589 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1611SHR | #1SHR |  | SHRA | [14 empty] | 0661 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.161#1SHR_SRA | 161KV #1SHR 重故障 | OTHER | D07/161/1950/4A5Other |  |  |  | DNP | 590 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1611SHR | #1SHR |  | SRF | [14 empty] | 0660 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.161#1SHR_SRF | 161KV #1SHR 輕故障 | OTHER | D07/161/1950/3A5Other |  |  |  | DNP | 591 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 161_1SHR | 161_1SHR |  | RYFA | [14 empty] | 0662 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.161_1SHR_RYFA | 161KV 1SHR(1950)數位電驛故障 | OTHER | D07/161/1950/RYFA |  |  |  | DNP | 592 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | 1950 | #1SHR(1950) |  | CB | [14 empty] | 0112 |  | 0019 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1950_CB | 1950(161KV #1SHR) CB | OTHER | D07/161/1950/CB |  |  |  | DNP | 593 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1950 | #1SHR(1950) |  | DS1 | 1951 | [13 empty] | 0768 | 769 | 0126 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1951_DS | 1951(161KV #1SHR) DS | OTHER | D07/161/1950/DS1 |  |  |  | DNP | 594 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1950 | #1SHR(1950) |  | DS2 | 1952 | [13 empty] | 0770 | 771 | 0127 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.1952_DS | 1952(161KV #1SHR) DS | OTHER | D07/161/1950/DS2 |  |  |  | DNP | 595 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D07 | 太鐵DS | 161 | 161kV | _BUS | BUS |  | 87CTFA | [14 empty] | 0535 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.161KV_BUS_CTFA | 161KV BUS 87RY CT回路故障 | OTHER | D07/161/ComPoint/12B_CTFA |  |  |  | DNP | 596 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 161 | 161kV | _BUS | BUS |  | RYFA | [14 empty] | 0534 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | D07/161/ComPoint/BUS_RYFA |  |  |  | DNP | 597 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 1DTR | #1DTR |  | 51Z_UL | [14 empty] | 0978 |  | 0264 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.#1DTR_51ZUL | #1DTR 51ZRY U/L | OTHER | D07//1DTR/51Z_UL |  |  |  | DNP | 598 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 0 |  | 1DTR | #1DTR |  | DTR_86A | [14 empty] | 0119 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.#1DTR_86A | #1DTR 86A | OTHER | D07//1DTR/DTR_86A |  |  |  | DNP | 599 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 1DTR | #1DTR |  | 1_87UL1 | [14 empty] | 0976 |  | 0262 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.#1DTR_87UL1 | #1DTR #1 87RY U/L | OTHER | D07//1DTR/1_87UL1 |  |  |  | DNP | 600 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 0 |  | 1DTR | #1DTR |  | 1_87UL2 | [14 empty] | 0977 |  | 0263 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.#1DTR_87UL2 | #1DTR #2 87RY U/L | OTHER | D07//1DTR/1_87UL2 |  |  |  | DNP | 601 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 0 |  | 1DTR | #1DTR |  | RYFA | [14 empty] | 0979 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.#1DTR_RYFA | #1DTR數位電驛故障 | OTHER | D07//1DTR/RYFA |  |  |  | DNP | 602 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 2DTR | #2DTR |  | 51Z_UL | [14 empty] | 0982 |  | 0267 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.#2DTR_51ZUL | #2DTR 51ZRY U/L | OTHER | D07//2DTR/51Z_UL |  |  |  | DNP | 603 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 0 |  | 2DTR | #2DTR |  | DTR_86A | [14 empty] | 0120 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.#2DTR_86A | #2DTR 86A | OTHER | D07//2DTR/DTR_86A |  |  |  | DNP | 604 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | 2DTR | #2DTR |  | 1_87UL1 | [14 empty] | 0980 |  | 0265 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.#2DTR_87UL1 | #2DTR #1 87RY U/L | OTHER | D07//2DTR/1_87UL1 |  |  |  | DNP | 605 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 0 |  | 2DTR | #2DTR |  | 1_87UL2 | [14 empty] | 0981 |  | 0266 | [8 empty] | ADCS_N | [8 empty] | 太鐵DS.#2DTR_87UL2 | #2DTR #2 87RY U/L | OTHER | D07//2DTR/1_87UL2 |  |  |  | DNP | 606 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | USE/LOCK | USE
D07 | 太鐵DS | 0 |  | 2DTR | #2DTR |  | RYFA | [14 empty] | 0983 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.#2DTR_RYFA | #2DTR數位電驛故障 | OTHER | D07//2DTR/RYFA |  |  |  | DNP | 607 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  |  |  |  | RTUA | [14 empty] | 0118 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.RTUA | RTU發生異常 | OTHER | D07/0/RTU/RTUA |  |  |  | DNP | 608 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 0 |  | OLTC | OLTC |  | OLTCA | [14 empty] | 0568 | [10 empty] | ADCS_N | [8 empty] | 太鐵DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | D07/0/ComPoint/OLTC_A |  |  |  | DNP | 609 | DNPDIPoint | DS053 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D07 | 太鐵DS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 610 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 11 | 11kV | 230_SC | #3SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.230_SC_CAP | 11KV#3SC 容量 | SC | [5 empty] | 611 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 22 | 22kV | 220_SC | #2SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.220_SC_CAP | 23KV#2SC 容量 | SC | [5 empty] | 612 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 22 | 22kV | 240_SC | #4SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 太鐵DS.240_SC_CAP | 23KV#4SC 容量 | SC | [5 empty] | 613 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D07 | 太鐵DS | 161 | 161kV | 1510 | 太鐵糠榔一路(1510) |  | LE0 | 1510LE | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.1510LE | 1510LE (非取樣點) | LINE161 | D07/161/1510/LE0 |  |  |  |  | 614 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1510 | 太鐵糠榔一路(1510) |  | BE0 | 1510BE | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.1510BE | 1510BE (非取樣點) | LINE161 | D07/161/1510/BE0 |  |  |  |  | 615 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1520 | 太鐵糠榔二路(1520) |  | LE0 | 1520LE | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.1520LE | 1520LE (非取樣點) | LINE161 | D07/161/1520/LE0 |  |  |  |  | 616 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1520 | 太鐵糠榔二路(1520) |  | BE0 | 1520BE | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.1520BE | 1520BE (非取樣點) | LINE161 | D07/161/1520/BE0 |  |  |  |  | 617 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1530 | 北回太鐵紅線(1530) |  | LE0 | 1530LE | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.1530LE | 1530LE (非取樣點) | LINE161 | D07/161/1530/LE0 |  |  |  |  | 618 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1530 | 北回太鐵紅線(1530) |  | BE0 | 1530BE | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.1530BE | 1530BE (非取樣點) | LINE161 | D07/161/1530/BE0 |  |  |  |  | 619 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1540 | 北回太鐵白線(1540) |  | LE0 | 1540LE | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.1540LE | 1540LE (非取樣點) | LINE161 | D07/161/1540/LE0 |  |  |  |  | 620 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1540 | 北回太鐵白線(1540) |  | BE0 | 1540BE | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.1540BE | 1540BE (非取樣點) | LINE161 | D07/161/1540/BE0 |  |  |  |  | 621 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1550 | 後壁太鐵一路(1550) |  | LE0 | 1550LE | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.1550LE | 1550LE (非取樣點) | LINE161 | D07/161/1550/LE0 |  |  |  |  | 622 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1550 | 後壁太鐵一路(1550) |  | BE0 | 1550BE | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.1550BE | 1550BE (非取樣點) | LINE161 | D07/161/1550/BE0 |  |  |  |  | 623 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1560 | 後壁太鐵二路(1560) |  | LE0 | 1560LE | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.1560LE | 1560LE (非取樣點) | LINE161 | D07/161/1560/LE0 |  |  |  |  | 624 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1560 | 後壁太鐵二路(1560) |  | BE0 | 1560BE | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.1560BE | 1560BE (非取樣點) | LINE161 | D07/161/1560/BE0 |  |  |  |  | 625 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | JV21 | JV21_DS |  | DS1 | JV21_DS | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV21_DS | JV21_DS (非取樣點) | FEEDER | D07/11/JV21/DS |  |  |  |  | 626 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | JV21 | JV21_ES |  | LE0 | JV21_ES | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV21_ES | JV21_ES (非取樣點) | FEEDER | D07/11/JV21/ES |  |  |  |  | 627 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | JV22 | JV22_DS |  | DS1 | JV22_DS | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV22_DS | JV22_DS (非取樣點) | FEEDER | D07/11/JV22/DS |  |  |  |  | 628 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | JV22 | JV22_ES |  | LE0 | JV22_ES | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV22_ES | JV22_ES (非取樣點) | FEEDER | D07/11/JV22/ES |  |  |  |  | 629 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | JV23 | JV23_DS |  | DS1 | JV23_DS | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV23_DS | JV23_DS (非取樣點) | FEEDER | D07/11/JV23/DS |  |  |  |  | 630 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | JV23 | JV23_ES |  | LE0 | JV23_ES | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV23_ES | JV23_ES (非取樣點) | FEEDER | D07/11/JV23/ES |  |  |  |  | 631 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | JV24 | JV24_DS |  | DS1 | JV24_DS | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV24_DS | JV24_DS (非取樣點) | FEEDER | D07/11/JV24/DS |  |  |  |  | 632 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | JV24 | JV24_ES |  | LE0 | JV24_ES | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV24_ES | JV24_ES (非取樣點) | FEEDER | D07/11/JV24/ES |  |  |  |  | 633 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | JV25 | JV25_DS |  | DS1 | JV25_DS | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV25_DS | JV25_DS (非取樣點) | FEEDER | D07/11/JV25/DS |  |  |  |  | 634 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | JV25 | JV25_ES |  | LE0 | JV25_ES | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV25_ES | JV25_ES (非取樣點) | FEEDER | D07/11/JV25/ES |  |  |  |  | 635 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | JV31 | JV31_DS |  | DS1 | JV31_DS | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV31_DS | JV31_DS (非取樣點) | FEEDER | D07/11/JV31/DS |  |  |  |  | 636 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | JV31 | JV31_ES |  | LE0 | JV31_ES | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV31_ES | JV31_ES (非取樣點) | FEEDER | D07/11/JV31/ES |  |  |  |  | 637 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | JV32 | JV32_DS |  | DS1 | JV32_DS | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV32_DS | JV32_DS (非取樣點) | FEEDER | D07/11/JV32/DS |  |  |  |  | 638 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | JV32 | JV32_ES |  | LE0 | JV32_ES | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV32_ES | JV32_ES (非取樣點) | FEEDER | D07/11/JV32/ES |  |  |  |  | 639 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | JV33 | JV33_DS |  | DS1 | JV33_DS | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV33_DS | JV33_DS (非取樣點) | FEEDER | D07/11/JV33/DS |  |  |  |  | 640 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | JV33 | JV33_ES |  | LE0 | JV33_ES | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV33_ES | JV33_ES (非取樣點) | FEEDER | D07/11/JV33/ES |  |  |  |  | 641 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | JV34 | JV34_DS |  | DS1 | JV34_DS | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV34_DS | JV34_DS (非取樣點) | FEEDER | D07/11/JV34/DS |  |  |  |  | 642 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | JV34 | JV34_ES |  | LE0 | JV34_ES | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV34_ES | JV34_ES (非取樣點) | FEEDER | D07/11/JV34/ES |  |  |  |  | 643 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | JV35 | JV35_DS |  | DS1 | JV35_DS | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV35_DS | JV35_DS (非取樣點) | FEEDER | D07/11/JV35/DS |  |  |  |  | 644 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | JV35 | JV35_ES |  | LE0 | JV35_ES | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV35_ES | JV35_ES (非取樣點) | FEEDER | D07/11/JV35/ES |  |  |  |  | 645 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | JV56 | JV56_DS |  | DS1 | JV56_DS | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV56_DS | JV56_DS (非取樣點) | FEEDER | D07/22/JV56/DS |  |  |  |  | 646 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | JV56 | JV56_ES |  | LE0 | JV56_ES | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV56_ES | JV56_ES (非取樣點) | FEEDER | D07/22/JV56/ES |  |  |  |  | 647 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | JV57 | JV57_DS |  | DS1 | JV57_DS | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV57_DS | JV57_DS (非取樣點) | FEEDER | D07/22/JV57/DS |  |  |  |  | 648 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | JV57 | JV57_ES |  | LE0 | JV57_ES | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV57_ES | JV57_ES (非取樣點) | FEEDER | D07/22/JV57/ES |  |  |  |  | 649 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | JV58 | JV58_DS |  | DS1 | JV58_DS | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV58_DS | JV58_DS (非取樣點) | FEEDER | D07/22/JV58/DS |  |  |  |  | 650 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | JV58 | JV58_ES |  | LE0 | JV58_ES | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV58_ES | JV58_ES (非取樣點) | FEEDER | D07/22/JV58/ES |  |  |  |  | 651 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | JV59 | JV59_DS |  | DS1 | JV59_DS | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV59_DS | JV59_DS (非取樣點) | FEEDER | D07/22/JV59/DS |  |  |  |  | 652 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | JV59 | JV59_ES |  | LE0 | JV59_ES | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV59_ES | JV59_ES (非取樣點) | FEEDER | D07/22/JV59/ES |  |  |  |  | 653 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | JV60 | JV60_DS |  | DS1 | JV60_DS | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV60_DS | JV60_DS (非取樣點) | FEEDER | D07/22/JV60/DS |  |  |  |  | 654 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | JV60 | JV60_ES |  | LE0 | JV60_ES | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV60_ES | JV60_ES (非取樣點) | FEEDER | D07/22/JV60/ES |  |  |  |  | 655 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | JV66 | JV66_DS |  | DS1 | JV66_DS | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV66_DS | JV66_DS (非取樣點) | FEEDER | D07/22/JV66/DS |  |  |  |  | 656 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | JV66 | JV66_ES |  | LE0 | JV66_ES | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV66_ES | JV66_ES (非取樣點) | FEEDER | D07/22/JV66/ES |  |  |  |  | 657 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | JV67 | JV67_DS |  | DS1 | JV67_DS | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV67_DS | JV67_DS (非取樣點) | FEEDER | D07/22/JV67/DS |  |  |  |  | 658 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | JV67 | JV67_ES |  | LE0 | JV67_ES | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV67_ES | JV67_ES (非取樣點) | FEEDER | D07/22/JV67/ES |  |  |  |  | 659 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | JV68 | JV68_DS |  | DS1 | JV68_DS | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV68_DS | JV68_DS (非取樣點) | FEEDER | D07/22/JV68/DS |  |  |  |  | 660 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | JV68 | JV68_ES |  | LE0 | JV68_ES | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV68_ES | JV68_ES (非取樣點) | FEEDER | D07/22/JV68/ES |  |  |  |  | 661 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | JV69 | JV69_DS |  | DS1 | JV69_DS | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV69_DS | JV69_DS (非取樣點) | FEEDER | D07/22/JV69/DS |  |  |  |  | 662 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | JV69 | JV69_ES |  | LE0 | JV69_ES | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV69_ES | JV69_ES (非取樣點) | FEEDER | D07/22/JV69/ES |  |  |  |  | 663 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | JV70 | JV70_DS |  | DS1 | JV70_DS | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV70_DS | JV70_DS (非取樣點) | FEEDER | D07/22/JV70/DS |  |  |  |  | 664 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | JV70 | JV70_ES |  | LE0 | JV70_ES | [24 empty] | DDCS2_1 | [8 empty] | 太鐵DS.JV70_ES | JV70_ES (非取樣點) | FEEDER | D07/22/JV70/ES |  |  |  |  | 665 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | 100 | TIE(100) |  | E1 | 101E | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.101E | 101E (非取樣點) | TIE | D07/11/100/E1 |  |  |  |  | 666 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | 100 | TIE(100) |  | E2 | 102E | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.102E | 102E (非取樣點) | TIE | D07/11/100/E2 |  |  |  |  | 667 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | 101 | 101 |  | 101 | 101 | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.101 | 101 (非取樣點) | TIE | D07/11/100/D1 |  |  |  |  | 668 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | 102 | 102 |  | 102 | 102 | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.102 | 102 (非取樣點) | TIE | D07/11/100/D2 |  |  |  |  | 669 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.1501E | 1501E (非取樣點) | TIE | D07/161/1500/E1 |  |  |  |  | 670 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.1502E | 1502E (非取樣點) | TIE | D07/161/1500/E2 |  |  |  |  | 671 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | 200 | TIE(200) |  | E1 | 201E | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.201E | 201E (非取樣點) | TIE | D07/22/200/E1 |  |  |  |  | 672 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | 200 | TIE(200) |  | E2 | 202E | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.202E | 202E (非取樣點) | TIE | D07/22/200/E2 |  |  |  |  | 673 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | 201 | 201 |  | 201 | 201 | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.201 | 201 (非取樣點) | TIE | D07/22/200/D1 |  |  |  |  | 674 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | 202 | 202 |  | 202 | 202 | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.202 | 202 (非取樣點) | TIE | D07/22/200/D2 |  |  |  |  | 675 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | 391 | 391 |  | 391 | 391 | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.391 | 391 (非取樣點) | OTHER | D07/11/390/D1 |  |  |  |  | 676 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | 391E | 391E |  | 391E | 391E | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.391E | 391E (非取樣點) | OTHER | D07/11/390/E1 |  |  |  |  | 677 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | 491 | 491 |  | 491 | 491 | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.491 | 491 (非取樣點) | OTHER | D07/22/490/D1 |  |  |  |  | 678 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | 491E | 491E |  | 491E | 491E | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.491E | 491E (非取樣點) | OTHER | D07/22/490/E1 |  |  |  |  | 679 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | 1750TE | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.1750TE | 1750TE (非取樣點) | MTR | D07/161/1750/TE0 |  |  |  |  | 680 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | 1750BE | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.1750BE | 1750BE (非取樣點) | MTR | D07/161/1750/BE0 |  |  |  |  | 681 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | 311 | 311 |  | 311 | 311 | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.311 | 311 (非取樣點) | MTR | D07/11/310/D1 |  |  |  |  | 682 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | 310 | #1DTR(310) |  | E1 | 311E | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.311E | 311E (非取樣點) | MTR | D07/11/310/E1 |  |  |  |  | 683 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | 321 | 321 |  | 321 | 321 | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.321 | 321 (非取樣點) | MTR | D07/22/320/D1 |  |  |  |  | 684 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | 320 | #1DTR(320) |  | E1 | 321E | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.321E | 321E (非取樣點) | MTR | D07/22/320/E1 |  |  |  |  | 685 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | 1760TE | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.1760TE | 1760TE (非取樣點) | MTR | D07/161/1760/TE0 |  |  |  |  | 686 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | 1760BE | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.1760BE | 1760BE (非取樣點) | MTR | D07/161/1760/BE0 |  |  |  |  | 687 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | 331 | 331 |  | 331 | 331 | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.331 | 331 (非取樣點) | MTR | D07/11/330/D1 |  |  |  |  | 688 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | 330 | #2DTR(330) |  | E1 | 331E | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.331E | 331E (非取樣點) | MTR | D07/11/330/E1 |  |  |  |  | 689 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | 341 | 341 |  | 341 | 341 | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.341 | 341 (非取樣點) | MTR | D07/22/340/D1 |  |  |  |  | 690 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | 340 | #2DTR(340) |  | E1 | 341E | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.341E | 341E (非取樣點) | MTR | D07/22/340/E1 |  |  |  |  | 691 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | 211E | 211E |  | 211E | 211E | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.211E | 211E (非取樣點) | SC | D07/11/210/E1 |  |  |  |  | 692 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | 211 | 211 |  | 211 | 211 | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.211 | 211 (非取樣點) | SC | D07/11/210/D1 |  |  |  |  | 693 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | 231E | 231E |  | 231E | 231E | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.231E | 231E (非取樣點) | SC | D07/11/230/E1 |  |  |  |  | 694 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | 231 | 231 |  | 231 | 231 | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.231 | 231 (非取樣點) | SC | D07/11/230/D1 |  |  |  |  | 695 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | 221E | 221E |  | 221E | 221E | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.221E | 221E (非取樣點) | SC | D07/22/220/E1 |  |  |  |  | 696 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | 221 | 221 |  | 221 | 221 | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.221 | 221 (非取樣點) | SC | D07/22/220/D1 |  |  |  |  | 697 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | 241E | 241E |  | 241E | 241E | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.241E | 241E (非取樣點) | SC | D07/22/240/E1 |  |  |  |  | 698 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | 241 | 241 |  | 241 | 241 | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.241 | 241 (非取樣點) | SC | D07/22/240/D1 |  |  |  |  | 699 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | 15B1E | 15B1E |  | BE1 | 15B1E | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.15B1E | 15B1E (非取樣點) | BUS | D07/161/161B1E/BE1 |  |  |  |  | 700 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | 15B2E | 15B2E |  | BE2 | 15B2E | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.15B2E | 15B2E (非取樣點) | BUS | D07/161/161B2E/BE2 |  |  |  |  | 701 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 702 | NotelDIPoint | [38 empty] | START/STOP | STOP
D07 | 太鐵DS | 0 |  |  |  |  | 1950BE | 1950BE | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.1950BE | 1950BE(非取樣點) | OTHER | D07/161/1950/BE0 |  |  |  |  | 703 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  |  |  |  | 1950RE | 1950RE | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.1950RE | 1950RE(非取樣點) | OTHER | D07/161/1950/RE0 |  |  |  |  | 704 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | 1ABUS | 1ABUS |  | PTD | 1ABUS_PTD | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.1ABUS_PTD | #1ABUS_PTD(非取樣點) | OTHER | [5 empty] | 705 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | 1ABUS | 1ABUS |  | PTE | 1ABUS_PTE | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.1ABUS_PTE | #1ABUS_PTE(非取樣點) | OTHER | [5 empty] | 706 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | 1BBUS | 1BBUS |  | PTD | 1BBUS_PTD | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.1BBUS_PTD | #1BBUS_PTD(非取樣點) | OTHER | [5 empty] | 707 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | 1BBUS | 1BBUS |  | PTE | 1BBUS_PTE | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.1BBUS_PTE | #1BBUS_PTE(非取樣點) | OTHER | [5 empty] | 708 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | 2ABUS | 2ABUS |  | PTD | 2ABUS_PTD | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.2ABUS_PTD | #2ABUS_PTD(非取樣點) | OTHER | [5 empty] | 709 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | 2ABUS | 2ABUS |  | PTE | 2ABUS_PTE | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.2ABUS_PTE | #2ABUS_PTE(非取樣點) | OTHER | [5 empty] | 710 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D07 | 太鐵DS | 0 |  | 2BBUS | 2BBUS |  | PTD | 2BBUS_PTD | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.2BBUS_PTD | #2BBUS_PTD(非取樣點) | OTHER | [5 empty] | 711 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D07 | 太鐵DS | 0 |  | 2BBUS | 2BBUS |  | PTE | 2BBUS_PTE | [24 empty] | ADCS_N | [8 empty] | 太鐵DS.2BBUS_PTE | #2BBUS_PTE(非取樣點) | OTHER | [5 empty] | 712 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo