## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D08 | 斗南DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_A1 | [8 empty] | 斗南DS.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 2 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_A1 | [8 empty] | 斗南DS.1510BE | 1510BE (非取樣點) | LINE161 | [5 empty] | 3 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_A1 | [8 empty] | 斗南DS.1520LE | 1520LE (非取樣點) | LINE161 | [5 empty] | 4 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_A1 | [8 empty] | 斗南DS.1520BE | 1520BE (非取樣點) | LINE161 | [5 empty] | 5 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 161 | 161kV | 1530 | 雲林～斗南線(1530) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_A1 | [8 empty] | 斗南DS.1530LE | 1530LE (非取樣點) | LINE161 | [5 empty] | 6 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 161 | 161kV | 1530 | 雲林～斗南線(1530) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_A1 | [8 empty] | 斗南DS.1530BE | 1530BE (非取樣點) | LINE161 | [5 empty] | 7 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 161 | 161kV | 1540 | 斗南～北勢線(1540) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_A1 | [8 empty] | 斗南DS.1540LE | 1540LE (非取樣點) | LINE161 | [5 empty] | 8 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 161 | 161kV | 1540 | 斗南～北勢線(1540) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_A1 | [8 empty] | 斗南DS.1540BE | 1540BE (非取樣點) | LINE161 | [5 empty] | 9 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_A1 | [8 empty] | 斗南DS.1501E | 1501E (非取樣點) | TIE | [5 empty] | 10 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_A1 | [8 empty] | 斗南DS.1502E | 1502E (非取樣點) | TIE | [5 empty] | 11 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_A1 | [8 empty] | 斗南DS.1760TE | 1760TE (非取樣點) | MTR | [5 empty] | 12 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_A1 | [8 empty] | 斗南DS.1760BE | 1760BE (非取樣點) | MTR | [5 empty] | 13 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | D1 | 331(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D08_A1 | [8 empty] | 斗南DS.331 | 331 (非取樣點) | MTR | [5 empty] | 14 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | E1 | 331E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D08_A1 | [8 empty] | 斗南DS.331E | 331E (非取樣點) | MTR | [5 empty] | 15 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | D1 | 341(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D08_A1 | [8 empty] | 斗南DS.341 | 341 (非取樣點) | MTR | [5 empty] | 16 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | E1 | 341E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D08_A1 | [8 empty] | 斗南DS.341E | 341E (非取樣點) | MTR | [5 empty] | 17 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_A1 | [8 empty] | 斗南DS.1770TE | 1770TE (非取樣點) | MTR | [5 empty] | 18 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_A1 | [8 empty] | 斗南DS.1770BE | 1770BE (非取樣點) | MTR | [5 empty] | 19 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | D1 | 351(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D08_A1 | [8 empty] | 斗南DS.351 | 351 (非取樣點) | MTR | [5 empty] | 20 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | E1 | 351E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D08_A1 | [8 empty] | 斗南DS.351E | 351E (非取樣點) | MTR | [5 empty] | 21 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 11 | 11kV | 360 | #3DTR(B)(360) |  | D1 | 361(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D08_A1 | [8 empty] | 斗南DS.361 | 361 (非取樣點) | MTR | [5 empty] | 22 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | 360 | #3DTR(B)(360) |  | E1 | 361E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D08_A1 | [8 empty] | 斗南DS.361E | 361E (非取樣點) | MTR | [5 empty] | 23 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 11 | 11kV | 390 | #1SSTR(390) |  | D1 | 391(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D08_A1 | [8 empty] | 斗南DS.391 | 391 (非取樣點) | OTHER | [5 empty] | 24 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | 390 | #1SSTR(390) |  | E1 | 391E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D08_A1 | [8 empty] | 斗南DS.391E | 391E (非取樣點) | OTHER | [5 empty] | 25 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 22 | 22kV | XW61 | 南六一線(XW61) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW61_DS | XW61_DS (非取樣點) | FEEDER | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | XW61 | 南六一線(XW61) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW61_ES | XW61_ES (非取樣點) | FEEDER | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 22 | 22kV | XW62 | 南六二線(XW62) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW62_DS | XW62_DS (非取樣點) | FEEDER | [5 empty] | 28 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | XW62 | 南六二線(XW62) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW62_ES | XW62_ES (非取樣點) | FEEDER | [5 empty] | 29 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 22 | 22kV | XW63 | 南六三線(XW63) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW63_DS | XW63_DS (非取樣點) | FEEDER | [5 empty] | 30 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | XW63 | 南六三線(XW63) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW63_ES | XW63_ES (非取樣點) | FEEDER | [5 empty] | 31 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 22 | 22kV | XW64 | 南六四線(XW64) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW64_DS | XW64_DS (非取樣點) | FEEDER | [5 empty] | 32 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | XW64 | 南六四線(XW64) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW64_ES | XW64_ES (非取樣點) | FEEDER | [5 empty] | 33 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 22 | 22kV | XW65 | 南六五線(XW65) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW65_DS | XW65_DS (非取樣點) | FEEDER | [5 empty] | 34 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | XW65 | 南六五線(XW65) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW65_ES | XW65_ES (非取樣點) | FEEDER | [5 empty] | 35 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 11 | 11kV | XW31 | 南十一線(XW31) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW31_DS | XW31_DS (非取樣點) | FEEDER | [5 empty] | 36 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | XW31 | 南十一線(XW31) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW31_ES | XW31_ES (非取樣點) | FEEDER | [5 empty] | 37 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 11 | 11kV | XW32 | 南十二線(XW32) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW32_DS | XW32_DS (非取樣點) | FEEDER | [5 empty] | 38 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | XW32 | 南十二線(XW32) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW32_ES | XW32_ES (非取樣點) | FEEDER | [5 empty] | 39 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 22 | 22kV | 230 | #3SC(230) |  | E1 | 231E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D08_A1 | [8 empty] | 斗南DS.231E | 231E (非取樣點) | SC | [5 empty] | 40 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 22 | 22kV | 230 | #3SC(230) |  | ES | 230_ES | DEL | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D08_A1 | [16 empty] | 41 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D08 | 斗南DS | 22 | 22kV | 230 | #3SC(230) |  | D1 | 231(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D08_A1 | [8 empty] | 斗南DS.231 | 231 (非取樣點) | SC | [5 empty] | 42 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | 300 | TIE(300) |  | D1 | 301(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D08_A1 | [8 empty] | 斗南DS.301 | 301 (非取樣點) | TIE | [5 empty] | 43 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | 300 | TIE(300) |  | D2 | 302(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D08_A1 | [8 empty] | 斗南DS.302 | 302 (非取樣點) | TIE | [5 empty] | 44 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | 300 | TIE(300) |  | E1 | 301E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D08_A1 | [8 empty] | 斗南DS.301E | 301E(非取樣點) | OTHER | [5 empty] | 45 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 22 | 22kV | 300 | TIE(300) |  | E2 | 302E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D08_A1 | [8 empty] | 斗南DS.302E | 302E(非取樣點) | OTHER | [5 empty] | 46 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 11 | 11kV | 490 | #2SSTR(490) |  | D1 | 491(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D08_A1 | [8 empty] | 斗南DS.491 | 491 (非取樣點) | OTHER | [5 empty] | 47 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | 490 | #2SSTR(490) |  | E1 | 491E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D08_A1 | [8 empty] | 斗南DS.491E | 491E (非取樣點) | OTHER | [5 empty] | 48 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 11 | 11kV | XW33 | 南十三線(XW33) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW33_DS | XW33_DS (非取樣點) | FEEDER | [5 empty] | 49 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | XW33 | 南十三線(XW33) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW33_ES | XW33_ES (非取樣點) | FEEDER | [5 empty] | 50 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 11 | 11kV | XW34 | 南十四線(XW34) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW34_DS | XW34_DS (非取樣點) | FEEDER | [5 empty] | 51 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | XW34 | 南十四線(XW34) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW34_ES | XW34_ES (非取樣點) | FEEDER | [5 empty] | 52 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 11 | 11kV | XW35 | 南十五線(XW35) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW35_DS | XW35_DS (非取樣點) | FEEDER | [5 empty] | 53 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | XW35 | 南十五線(XW35) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW35_ES | XW35_ES (非取樣點) | FEEDER | [5 empty] | 54 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 22 | 22kV | XW71 | 南七十一線(XW71) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW71_DS | XW71_DS (非取樣點) | FEEDER | [5 empty] | 55 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | XW71 | 南七十一線(XW71) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW71_ES | XW71_ES (非取樣點) | FEEDER | [5 empty] | 56 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 22 | 22kV | XW72 | 南七十二線(XW72) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW72_DS | XW72_DS (非取樣點) | FEEDER | [5 empty] | 57 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | XW72 | 南七十二線(XW72) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW72_ES | XW72_ES (非取樣點) | FEEDER | [5 empty] | 58 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 11 | 11kV | 240 | #4SC(240) |  | E1 | 241E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D08_A1 | [8 empty] | 斗南DS.241E | 241E (非取樣點) | SC | [5 empty] | 59 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 11 | 11kV | 240 | #4SC(240) |  | DS1 | 241(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D08_A1 | [8 empty] | 斗南DS.241 | 241 (非取樣點) | SC | [5 empty] | 60 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | 400 | TIE(400) |  | D1 | 401(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D08_A1 | [8 empty] | 斗南DS.401 | 401 (非取樣點) | TIE | [5 empty] | 61 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | 400 | TIE(400) |  | D2 | 402(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D08_A1 | [8 empty] | 斗南DS.402 | 402 (非取樣點) | TIE | [5 empty] | 62 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | 400 | TIE(400) |  | E1 | 401E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D08_A1 | [8 empty] | 斗南DS.401E | 401E(非取樣點) | OTHER | [5 empty] | 63 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 11 | 11kV | 400 | TIE(400) |  | E2 | 402E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D08_A1 | [8 empty] | 斗南DS.402E | 402E(非取樣點) | OTHER | [5 empty] | 64 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 22 | 22kV | XW73 | 南七十三線(XW73) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW73_DS | XW73_DS (非取樣點) | FEEDER | [5 empty] | 65 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | XW73 | 南七十三線(XW73) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW73_ES | XW73_ES (非取樣點) | FEEDER | [5 empty] | 66 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 22 | 22kV | XW74 | 南七十四線(XW74) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW74_DS | XW74_DS (非取樣點) | FEEDER | [5 empty] | 67 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | XW74 | 南七十四線(XW74) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW74_ES | XW74_ES (非取樣點) | FEEDER | [5 empty] | 68 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 22 | 22kV | XW75 | 南七十五線(XW75) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW75_DS | XW75_DS (非取樣點) | FEEDER | [5 empty] | 69 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | XW75 | 南七十五線(XW75) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW75_ES | XW75_ES (非取樣點) | FEEDER | [5 empty] | 70 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 11 | 11kV | XW36 | 南十六線(XW36) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW36_DS | XW36_DS (非取樣點) | FEEDER | [5 empty] | 71 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | XW36 | 南十六線(XW36) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW36_ES | XW36_ES (非取樣點) | FEEDER | [5 empty] | 72 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 22 | 22kV | 250 | #5SC(250) |  | E1 | 251E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D08_A1 | [8 empty] | 斗南DS.251E | 251E (非取樣點) | SC | [5 empty] | 73 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 22 | 22kV | 250 | #5SC(250) |  | ES | 250_ES | DEL | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D08_A1 | [16 empty] | 74 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D08 | 斗南DS | 22 | 22kV | 250 | #5SC(250) |  | D1 | 251(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D08_A1 | [8 empty] | 斗南DS.251 | 251 (非取樣點) | SC | [5 empty] | 75 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | XW37 | 南十七線(XW37) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW37_DS | XW37_DS (非取樣點) | FEEDER | [5 empty] | 76 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | XW37 | 南十七線(XW37) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW37_ES | XW37_ES (非取樣點) | FEEDER | [5 empty] | 77 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 11 | 11kV | XW38 | 南十八線(XW38) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW38_DS | XW38_DS (非取樣點) | FEEDER | [5 empty] | 78 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | XW38 | 南十八線(XW38) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW38_ES | XW38_ES (非取樣點) | FEEDER | [5 empty] | 79 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 11 | 11kV | XW39 | 南十九線(XW39) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW39_DS | XW39_DS (非取樣點) | FEEDER | [5 empty] | 80 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | XW39 | 南十九線(XW39) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW39_ES | XW39_ES (非取樣點) | FEEDER | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 11 | 11kV | XW40 | 南二十線(XW40) |  | DS | (非取樣點) | Element(ADD) | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW39_DS | XW39_DS (非取樣點) | FEEDER | [5 empty] | 80 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | XW40 | 南二十線(XW40) |  | ES | (非取樣點) | Element(ADD) | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D08_D1 | [8 empty] | 斗南DS.XW39_ES | XW39_ES (非取樣點) | FEEDER | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 11 | 11kV | 260 | #6SC(260) |  | E1 | 261E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D08_A1 | [8 empty] | 斗南DS.261E | 261E (非取樣點) | SC | [5 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 11 | 11kV | 260 | #6SC(260) |  | DS1 | 261(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D08_A1 | [8 empty] | 斗南DS.261 | 261 (非取樣點) | SC | [5 empty] | 83 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | 15B1E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aahz | B2/D08_A1 | [8 empty] | 斗南DS.15B1E | 15B1E (非取樣點) | BUS | [5 empty] | 84 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | 15B2E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/2Bus | [13 empty] | aahz | B2/D08_A1 | [8 empty] | 斗南DS.15B2E | 15B2E (非取樣點) | BUS | [5 empty] | 85 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | RTU | RTU |  | ADCL1 |  |  | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | [5 empty] | 86 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 0 |  | RTU | RTU |  | ADCH1 |  |  | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.1 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | [5 empty] | 87 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 161 | 161kV | 1BUS | #1BUS |  | V |  | B3 | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 161KV #1BUS | KV | 161KV #1BUS 電壓 | kV_-210_210(-2000_2000) | aaa | B2/D08_A1 | [8 empty] | 斗南DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | [5 empty] | 88 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D08 | 斗南DS | 161 | 161kV | 2BUS | #2BUS |  | V |  | B3 | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0003 |  |  | 1-83 |  |  | 161KV #2BUS | KV | 161KV #2BUS 電壓 | kV_-210_210(-2000_2000) | aab | B2/D08_A1 | [8 empty] | 斗南DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | [5 empty] | 89 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D08 | 斗南DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | 1510 | MW | 虎菁一路 (1510)瓦 | MW_-560_560(-2000_2000) |  | B2/D08_A1 | [8 empty] | 斗南DS.1510_MW | 斗南虎菁一路 MW | LINE161 | [5 empty] | 90 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D08 | 斗南DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | 1510 | MVAR | 虎菁一路 (1510)乏 | MVAR_-560_560(-2000_2000) |  | B2/D08_A1 | [8 empty] | 斗南DS.1510_MVAR | 斗南虎菁一路 MVAR | LINE161 | [5 empty] | 91 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D08 | 斗南DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0012 |  |  | 1-8C |  |  | 1520 | MW | 虎菁二路(1520) 瓦 | MW_-560_560(-2000_2000) |  | B2/D08_A1 | [8 empty] | 斗南DS.1520_MW | 斗南虎菁二路 MW | LINE161 | [5 empty] | 92 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D08 | 斗南DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0013 |  |  | 1-8D |  |  | 1520 | MVAR | 虎菁二路(1520) 乏 | MVAR_-560_560(-2000_2000) |  | B2/D08_A1 | [8 empty] | 斗南DS.1520_MVAR | 斗南虎菁二路 MVAR | LINE161 | [5 empty] | 93 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D08 | 斗南DS | 161 | 161kV | 1530 | 雲林～斗南線(1530) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0014 |  |  | 1-8E |  |  | 1530 | MW | 雲林斗南線 (1530) 瓦 | MW_-560_560(-2000_2000) |  | B2/D08_A1 | [8 empty] | 斗南DS.1530_MW | 雲林斗南線 MW | LINE161 | [5 empty] | 94 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D08 | 斗南DS | 161 | 161kV | 1530 | 雲林～斗南線(1530) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0015 |  |  | 1-8F |  |  | 1530 | MVAR | 雲林斗南線 (1530) 乏 | MVAR_-560_560(-2000_2000) |  | B2/D08_A1 | [8 empty] | 斗南DS.1530_MVAR | 雲林斗南線 MVAR | LINE161 | [5 empty] | 95 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D08 | 斗南DS | 161 | 161kV | 1540 | 斗南～北勢線(1540) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0016 |  |  | 1-90 |  |  | 1540 | MW | 斗南北勢線 (1540) 瓦 | MW_-560_560(-2000_2000) |  | B2/D08_A1 | [8 empty] | 斗南DS.1540_MW | 斗南北勢線 MW | LINE161 | [5 empty] | 96 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D08 | 斗南DS | 161 | 161kV | 1540 | 斗南～北勢線(1540) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0017 |  |  | 1-91 |  |  | 1540 | MVAR | 斗南北勢線 (1540) 乏 | MVAR_-560_560(-2000_2000) |  | B2/D08_A1 | [8 empty] | 斗南DS.1540_MVAR | 斗南北勢線 MVAR | LINE161 | [5 empty] | 97 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D08 | 斗南DS | 0 |  | StaDev | 所內設施 |  | DCV_P |  |  | MvMoment | 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | DCV | 65 | DC-P電壓 | kV_-150_150(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.直流P電源電壓 | 直流P電源電壓 | OTHER | [5 empty] | 98 |  |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 | 0.01 | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D08 | 斗南DS | 0 |  | StaDev | 所內設施 |  | DCV_N |  |  | MvMoment | 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | DCV | -65 | DC-N電壓 | kV_-150_150(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.直流N電源電壓 | 直流N電源電壓 | OTHER | [5 empty] | 99 |  |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 | 0.01 | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D08 | 斗南DS | 161 | 161kV | 1500 | TIE(1500) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | 1500 | A | TIE (1500) R相電流 | A_-2000_2000(-2000_2000) |  | B2/D08_A1 | [8 empty] | 斗南DS.1500TIE_AMP | 1500TIE AMP | TIE | [5 empty] | 100 |  |  |  |  | AI | [5 empty] | C20R1600 | 1520 | 1600 | 1760 | 1968 | 2.27 | -1520 | -1600 | -1760 | -1968 | 1 | 0.01 | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS |  |  | 2DTR | #2DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0024 |  |  | 1-98 |  |  | #2MTR | ℃ | #2MTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/D08_A1 | [8 empty] | 斗南DS.#2DTR_OIL | #2DTR 油溫 | MTR | [5 empty] | 101 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D08 | 斗南DS |  |  | 2DTR(A) | #2DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | #2ATR | ℃ | #2ATR 二次側線溫 | COIL_-120_120(-2000_2000) |  | B1/D08_A1 | [8 empty] | 斗南DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | [5 empty] | 102 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D08 | 斗南DS |  |  | 2DTR(B) | #2DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | #2BTR | ℃ | #2BTR 二次側線溫 | COIL_-120_120(-2000_2000) |  | B1/D08_A1 | [8 empty] | 斗南DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | [5 empty] | 103 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D08 | 斗南DS |  |  | 2DTR(A) | #2DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0027 |  | 0081 | 1-9B |  | 1-51 | #2ATR | 升/降 | #2ATR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D08_A1 | [8 empty] | 斗南DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | [5 empty] | 104 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D08 | 斗南DS |  |  | 2DTR(B) | #2DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0028 |  | 0083 | 1-9C |  | 1-53 | #2BTR | 升/降 | #2BTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D08_A1 | [8 empty] | 斗南DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | [5 empty] | 105 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D08 | 斗南DS |  |  | 3DTR | #3DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | #3MTR | ℃ | #3MTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/D08_A1 | [8 empty] | 斗南DS.#3DTR_OIL | #3DTR 油溫 | MTR | [5 empty] | 106 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D08 | 斗南DS |  |  | 3DTR(A) | #3DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | #3ATR | ℃ | #3ATR 二次側線溫 | COIL_-120_120(-2000_2000) |  | B1/D08_A1 | [8 empty] | 斗南DS.#3DTR(A)_COIL | #3DTR(A) 線溫 | MTR | [5 empty] | 107 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D08 | 斗南DS |  |  | 3DTR(B) | #3DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | #3BTR | ℃ | #3BTR 二次側線溫 | COIL_-120_120(-2000_2000) |  | B1/D08_A1 | [8 empty] | 斗南DS.#3DTR(B)_COIL | #3DTR(B) 線溫 | MTR | [5 empty] | 108 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D08 | 斗南DS |  |  | 3DTR(A) | #3DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0032 |  | 0085 | 1-A0 |  | 1-55 | #3ATR | 升/降 | #3ATR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D08_A1 | [8 empty] | 斗南DS.#3DTR(A)_TAP | #3DTR(A) OLTC TAP | MTR | [5 empty] | 109 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D08 | 斗南DS |  |  | 3DTR(B) | #3DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0033 |  | 0087 | 1-A1 |  | 1-57 | #3BTR | 升/降 | #3BTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D08_A1 | [8 empty] | 斗南DS.#3DTR(B)_TAP | #3DTR(B) OLTC TAP | MTR | [5 empty] | 110 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D08 | 斗南DS | 0 |  | RTU | RTU |  | ADCL2 |  |  | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | [5 empty] | 111 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 0 |  | RTU | RTU |  | ADCH2 |  |  | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.2 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | [5 empty] | 112 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW61 | 南六一線(XW61) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | F9 | KVAR | XW61 南六一線 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南六一線KVAR | 23KV南六一線 KVAR | FEEDER | [5 empty] | 113 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW61 | 南六一線(XW61) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | F9 | A | XW61 南六一線 R相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南六一線A1 | 23KV南六一線 R相AMP | FEEDER | [5 empty] | 114 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW61 | 南六一線(XW61) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | F9 | A | XW61 南六一線 S相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南六一線A2 | 23KV南六一線 S相AMP | FEEDER | [5 empty] | 115 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW61 | 南六一線(XW61) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | F9 | A | XW61 南六一線 T相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南六一線A3 | 23KV南六一線 T相AMP | FEEDER | [5 empty] | 116 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW61 | 南六一線(XW61) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | F9 | A | XW61 南六一線 N相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南六一線A0 | 23KV南六一線 N相AMP | FEEDER | [5 empty] | 117 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW62 | 南六二線(XW62) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | F10 | KVAR | XW62 南六二線 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南六二線KVAR | 23KV南六二線 KVAR | FEEDER | [5 empty] | 118 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW62 | 南六二線(XW62) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | F10 | A | XW62 南六二線 R相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南六二線A1 | 23KV南六二線 R相AMP | FEEDER | [5 empty] | 119 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW62 | 南六二線(XW62) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | F10 | A | XW62 南六二線 S相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南六二線A2 | 23KV南六二線 S相AMP | FEEDER | [5 empty] | 120 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW62 | 南六二線(XW62) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | F10 | A | XW62 南六二線 T相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南六二線A3 | 23KV南六二線 T相AMP | FEEDER | [5 empty] | 121 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW62 | 南六二線(XW62) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | F10 | A | XW62 南六二線 N相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南六二線A0 | 23KV南六二線 N相AMP | FEEDER | [5 empty] | 122 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 100 | TIE(100) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0098 |  |  | 1-E2 |  |  | TIE2A | A | TIE2A 100 R相電流 (SPARE) |  |  | B3/D08_A1 | [16 empty] | 123 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D08 | 斗南DS | 22 | 22kV | 100 | TIE(100) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | TIE2A | A | TIE2A 100 S相電流 (SPARE) |  |  | B3/D08_A1 | [16 empty] | 124 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D08 | 斗南DS | 22 | 22kV | 100 | TIE(100) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | TIE2A | A | TIE2A 100 T相電流 (SPARE) |  |  | B3/D08_A1 | [16 empty] | 125 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D08 | 斗南DS | 22 | 22kV | XW63 | 南六三線(XW63) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0101 |  |  | 1-E5 |  |  | F11 | KVAR | XW63 南六三線 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南六三線KVAR | 23KV南六三線 KVAR | FEEDER | [5 empty] | 126 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW63 | 南六三線(XW63) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | F11 | A | XW63 南六三線 R相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南六三線A1 | 23KV南六三線 R相AMP | FEEDER | [5 empty] | 127 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW63 | 南六三線(XW63) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | F11 | A | XW63 南六三線 S相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南六三線A2 | 23KV南六三線 S相AMP | FEEDER | [5 empty] | 128 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW63 | 南六三線(XW63) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | F11 | A | XW63 南六三線 T相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南六三線A3 | 23KV南六三線 T相AMP | FEEDER | [5 empty] | 129 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW63 | 南六三線(XW63) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | F11 | A | XW63 南六三線 N相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南六三線A0 | 23KV南六三線 N相AMP | FEEDER | [5 empty] | 130 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW64 | 南六四線(XW64) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | F12 | KVAR | XW64 南六四線 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南六四線KVAR | 23KV南六四線 KVAR | FEEDER | [5 empty] | 131 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW64 | 南六四線(XW64) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | F12 | A | XW64 南六四線 R相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南六四線A1 | 23KV南六四線 R相AMP | FEEDER | [5 empty] | 132 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW64 | 南六四線(XW64) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | F12 | A | XW64 南六四線 S相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南六四線A2 | 23KV南六四線 S相AMP | FEEDER | [5 empty] | 133 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW64 | 南六四線(XW64) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | F12 | A | XW64 南六四線 T相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南六四線A3 | 23KV南六四線 T相AMP | FEEDER | [5 empty] | 134 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW64 | 南六四線(XW64) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | F12 | A | XW64 南六四線 N相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南六四線A0 | 23KV南六四線 N相AMP | FEEDER | [5 empty] | 135 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW65 | 南六五線(XW65) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | F13 | KVAR | XW65 南六五線 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南六五線KVAR | 23KV南六五線 KVAR | FEEDER | [5 empty] | 136 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW65 | 南六五線(XW65) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | F13 | A | XW65 南六五線 R相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南六五線A1 | 23KV南六五線 R相AMP | FEEDER | [5 empty] | 137 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW65 | 南六五線(XW65) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | F13 | A | XW65 南六五線 S相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南六五線A2 | 23KV南六五線 S相AMP | FEEDER | [5 empty] | 138 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW65 | 南六五線(XW65) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | F13 | A | XW65 南六五線 T相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南六五線A3 | 23KV南六五線 T相AMP | FEEDER | [5 empty] | 139 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW65 | 南六五線(XW65) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | F13 | A | XW65 南六五線 N相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南六五線A0 | 23KV南六五線 N相AMP | FEEDER | [5 empty] | 140 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW31 | 南十一線(XW31) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | F14 | KVAR | XW31 南十一線 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十一線KVAR | 11KV南十一線 KVAR | FEEDER | [5 empty] | 141 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW31 | 南十一線(XW31) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | F14 | A | XW31 南十一線 R相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十一線A1 | 11KV南十一線 R相AMP | FEEDER | [5 empty] | 142 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW31 | 南十一線(XW31) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | F14 | A | XW31 南十一線 S相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十一線A2 | 11KV南十一線 S相AMP | FEEDER | [5 empty] | 143 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW31 | 南十一線(XW31) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | F14 | A | XW31 南十一線 T相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十一線A3 | 11KV南十一線 T相AMP | FEEDER | [5 empty] | 144 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW31 | 南十一線(XW31) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | F14 | A | XW31 南十一線 N相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十一線A0 | 11KV南十一線 N相AMP | FEEDER | [5 empty] | 145 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW32 | 南十二線(XW32) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | F15 | KVAR | XW32 南十二線 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十二線KVAR | 11KV南十二線 KVAR | FEEDER | [5 empty] | 146 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW32 | 南十二線(XW32) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | F15 | A | XW32 南十二線 R相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十二線A1 | 11KV南十二線 R相AMP | FEEDER | [5 empty] | 147 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW32 | 南十二線(XW32) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | F15 | A | XW32 南十二線 S相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十二線A2 | 11KV南十二線 S相AMP | FEEDER | [5 empty] | 148 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW32 | 南十二線(XW32) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | F15 | A | XW32 南十二線 T相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十二線A3 | 11KV南十二線 T相AMP | FEEDER | [5 empty] | 149 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW32 | 南十二線(XW32) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | F15 | A | XW32 南十二線 N相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十二線A0 | 11KV南十二線 N相AMP | FEEDER | [5 empty] | 150 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | M2A | MW | M2A 330 瓦 | MW_-108_108(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | [5 empty] | 151 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.216 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | M2A | KVAR | M2A 330 乏 | MVAR_-72_72(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | [5 empty] | 152 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D08 | 斗南DS | 0 |  | RTU | RTU |  | ADCL3 |  |  | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.3 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | [5 empty] | 153 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 0 |  | RTU | RTU |  | ADCH3 |  |  | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.3 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | [5 empty] | 154 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | M2A | A | M2A 330 R相電流 | A_-3000_3000(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | [5 empty] | 155 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | M2A | A | M2A 330 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | [5 empty] | 156 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | M2A | A | M2A 330 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | [5 empty] | 157 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 2ABUS | #2ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0133 |  |  | 2-85 |  |  | M2A | KV | #2A PT | kV_-18_18(-2000_2000) | aaa | B3/D08_A1 | [8 empty] | 斗南DS.23KV#2ABUS_KV | 23KV #2ABUS KV | BUS | [5 empty] | 158 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D08 | 斗南DS | 11 | 11kV | 200 | TIE(200) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | TIE2B | A | TIE2B 200 R相電流 (SPARE) |  |  | B3/D08_A1 | [16 empty] | 159 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D08 | 斗南DS | 11 | 11kV | 200 | TIE(200) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0135 |  |  | 2-87 |  |  | TIE2B | A | TIE2B 200 S相電流 (SPARE) |  |  | B3/D08_A1 | [16 empty] | 160 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D08 | 斗南DS | 11 | 11kV | 200 | TIE(200) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0136 |  |  | 2-88 |  |  | TIE2B | A | TIE2B 200 T相電流 (SPARE) |  |  | B3/D08_A1 | [16 empty] | 161 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D08 | 斗南DS | 22 | 22kV | 300 | TIE(300) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0137 |  |  | 2-89 |  |  | TIE2C | A | TIE2C 300 R相電流 | A_-2000_2000(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.23KV_300_A1 | 23KV 300 R相AMP | TIE | [5 empty] | 162 |  |  |  |  | AI | [5 empty] | C20R0750 | 712.5 | 750 | 825 | 922.5 | 0.45 | -712.5 | -750 | -825 | -922.5 | 1 | 0.01 | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 300 | TIE(300) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0138 |  |  | 2-8A |  |  | TIE2C | A | TIE2C 300 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.23KV_300_A2 | 23KV 300 S相AMP | TIE | [5 empty] | 163 |  |  |  |  | AI | [5 empty] | C20R0750 | 712.5 | 750 | 825 | 922.5 | 0.45 | -712.5 | -750 | -825 | -922.5 | 1 | 0.01 | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 300 | TIE(300) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0139 |  |  | 2-8B |  |  | TIE2C | A | TIE2C 300 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.23KV_300_A3 | 23KV 300 T相AMP | TIE | [5 empty] | 164 |  |  |  |  | AI | [5 empty] | C20R0750 | 712.5 | 750 | 825 | 922.5 | 0.45 | -712.5 | -750 | -825 | -922.5 | 1 | 0.01 | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW33 | 南十三線(XW33) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0140 |  |  | 2-8C |  |  | F16 | KVAR | XW33 南十三線 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十三線KVAR | 11KV南十三線 KVAR | FEEDER | [5 empty] | 165 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW33 | 南十三線(XW33) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0141 |  |  | 2-8D |  |  | F16 | A | XW33 南十三線 R相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十三線A1 | 11KV南十三線 R相AMP | FEEDER | [5 empty] | 166 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW33 | 南十三線(XW33) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0142 |  |  | 2-8E |  |  | F16 | A | XW33 南十三線 S相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十三線A2 | 11KV南十三線 S相AMP | FEEDER | [5 empty] | 167 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW33 | 南十三線(XW33) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0143 |  |  | 2-8F |  |  | F16 | A | XW33 南十三線 T相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十三線A3 | 11KV南十三線 T相AMP | FEEDER | [5 empty] | 168 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW33 | 南十三線(XW33) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0144 |  |  | 2-90 |  |  | F16 | A | XW33 南十三線 N相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十三線A0 | 11KV南十三線 N相AMP | FEEDER | [5 empty] | 169 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW34 | 南十四線(XW34) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0145 |  |  | 2-91 |  |  | F17 | KVAR | XW34 南十四線 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十四線KVAR | 11KV南十四線 KVAR | FEEDER | [5 empty] | 170 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW34 | 南十四線(XW34) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0146 |  |  | 2-92 |  |  | F17 | A | XW34 南十四線 R相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十四線A1 | 11KV南十四線 R相AMP | FEEDER | [5 empty] | 171 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW34 | 南十四線(XW34) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0147 |  |  | 2-93 |  |  | F17 | A | XW34 南十四線 S相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十四線A2 | 11KV南十四線 S相AMP | FEEDER | [5 empty] | 172 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW34 | 南十四線(XW34) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0148 |  |  | 2-94 |  |  | F17 | A | XW34 南十四線 T相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十四線A3 | 11KV南十四線 T相AMP | FEEDER | [5 empty] | 173 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW34 | 南十四線(XW34) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0149 |  |  | 2-95 |  |  | F17 | A | XW34 南十四線 N相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十四線A0 | 11KV南十四線 N相AMP | FEEDER | [5 empty] | 174 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW35 | 南十五線(XW35) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0150 |  |  | 2-96 |  |  | F18 | KVAR | XW35 南十五線 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十五線KVAR | 11KV南十五線 KVAR | FEEDER | [5 empty] | 175 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW35 | 南十五線(XW35) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0151 |  |  | 2-97 |  |  | F18 | A | XW35 南十五線 R相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十五線A1 | 11KV南十五線 R相AMP | FEEDER | [5 empty] | 176 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW35 | 南十五線(XW35) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0152 |  |  | 2-98 |  |  | F18 | A | XW35 南十五線 S相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十五線A2 | 11KV南十五線 S相AMP | FEEDER | [5 empty] | 177 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW35 | 南十五線(XW35) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0153 |  |  | 2-99 |  |  | F18 | A | XW35 南十五線 T相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十五線A3 | 11KV南十五線 T相AMP | FEEDER | [5 empty] | 178 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW35 | 南十五線(XW35) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0154 |  |  | 2-9A |  |  | F18 | A | XW35 南十五線 N相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十五線A0 | 11KV南十五線 N相AMP | FEEDER | [5 empty] | 179 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW71 | 南七十一線(XW71) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0155 |  |  | 2-9B |  |  | F19 | KVAR | XW71 南七十一線 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南七一線KVAR | 23KV南七一線 KVAR | FEEDER | [5 empty] | 180 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW71 | 南七十一線(XW71) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0156 |  |  | 2-9C |  |  | F19 | A | XW71 南七十一線 R相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南七一線A1 | 23KV南七一線 R相AMP | FEEDER | [5 empty] | 181 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW71 | 南七十一線(XW71) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0157 |  |  | 2-9D |  |  | F19 | A | XW71 南七十一線 S相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南七一線A2 | 23KV南七一線 S相AMP | FEEDER | [5 empty] | 182 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW71 | 南七十一線(XW71) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0158 |  |  | 2-9E |  |  | F19 | A | XW71 南七十一線 T相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南七一線A3 | 23KV南七一線 T相AMP | FEEDER | [5 empty] | 183 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW71 | 南七十一線(XW71) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0159 |  |  | 2-9F |  |  | F19 | A | XW71 南七十一線 N相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南七一線A0 | 23KV南七一線 N相AMP | FEEDER | [5 empty] | 184 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW72 | 南七十二線(XW72) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0160 |  |  | 2-A0 |  |  | F20 | KVAR | XW72 南七十二線 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南七二線KVAR | 23KV南七二線 KVAR | FEEDER | [5 empty] | 185 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW72 | 南七十二線(XW72) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0161 |  |  | 2-A1 |  |  | F20 | A | XW72 南七十二線 R相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南七二線A1 | 23KV南七二線 R相AMP | FEEDER | [5 empty] | 186 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW72 | 南七十二線(XW72) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0162 |  |  | 2-A2 |  |  | F20 | A | XW72 南七十二線 S相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南七二線A2 | 23KV南七二線 S相AMP | FEEDER | [5 empty] | 187 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW72 | 南七十二線(XW72) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0163 |  |  | 2-A3 |  |  | F20 | A | XW72 南七十二線T相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南七二線A3 | 23KV南七二線 T相AMP | FEEDER | [5 empty] | 188 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW72 | 南七十二線(XW72) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0164 |  |  | 2-A4 |  |  | F20 | A | XW72 南七十二線 N相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南七二線A0 | 23KV南七二線 N相AMP | FEEDER | [5 empty] | 189 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0165 |  |  | 2-A5 |  |  | M2B | MW | M2B 340 瓦 | MW_-54_54(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | [5 empty] | 190 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0166 |  |  | 2-A6 |  |  | M2B | KVAR | M2B 340 乏 | MVAR_-36_36(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | [5 empty] | 191 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0167 |  |  | 2-A7 |  |  | M2B | A | M2B 340 R相電流 | A_-3000_3000(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | [5 empty] | 192 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0168 |  |  | 2-A8 |  |  | M2B | A | M2B 340 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | [5 empty] | 193 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0169 |  |  | 2-A9 |  |  | M2B | A | M2B 340 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | [5 empty] | 194 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 2BBUS | #2BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0170 |  |  | 2-AA |  |  | M2B | KV | #2B PT | kV_-9_9(-2000_2000) | baa | B3/D08_A1 | [8 empty] | 斗南DS.11KV#2BBUS_KV | 11KV #2BBUS KV | BUS | [5 empty] | 195 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D08 | 斗南DS | 11 | 11kV | 400 | TIE(400) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0171 |  |  | 2-AB |  |  | TIE2D | A | TIE2D 400 R相電流 | A_-2000_2000(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.11KV_400_A1 | 11KV 400 R相AMP | TIE | [5 empty] | 196 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 400 | TIE(400) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0172 |  |  | 2-AC |  |  | TIE2D | A | TIE2D 400 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.11KV_400_A2 | 11KV 400 S相AMP | TIE | [5 empty] | 197 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 400 | TIE(400) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0173 |  |  | 2-AD |  |  | TIE2D | A | TIE2D 400 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.11KV_400_A3 | 11KV 400 T相AMP | TIE | [5 empty] | 198 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW73 | 南七十三線(XW73) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0174 |  |  | 2-AE |  |  | F21 | KVAR | XW73 南七十三線 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南七三線KVAR | 23KV南七三線 KVAR | FEEDER | [5 empty] | 199 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW73 | 南七十三線(XW73) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0175 |  |  | 2-AF |  |  | F21 | A | XW73 南七十三線 R相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南七三線A1 | 23KV南七三線 R相AMP | FEEDER | [5 empty] | 200 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW73 | 南七十三線(XW73) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0176 |  |  | 2-B0 |  |  | F21 | A | XW73 南七十三線 S相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南七三線A2 | 23KV南七三線 S相AMP | FEEDER | [5 empty] | 201 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW73 | 南七十三線(XW73) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0177 |  |  | 2-B1 |  |  | F21 | A | XW73 南七十三線 T相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南七三線A3 | 23KV南七三線 T相AMP | FEEDER | [5 empty] | 202 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW73 | 南七十三線(XW73) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0178 |  |  | 2-B2 |  |  | F21 | A | XW73 南七十三線 N相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南七三線A0 | 23KV南七三線 N相AMP | FEEDER | [5 empty] | 203 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW74 | 南七十四線(XW74) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0179 |  |  | 2-B3 |  |  | F22 | KVAR | XW74 南七十四線 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南七四線KVAR | 23KV南七四線 KVAR | FEEDER | [5 empty] | 204 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW74 | 南七十四線(XW74) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0180 |  |  | 2-B4 |  |  | F22 | A | XW74 南七十四線 R相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南七四線A1 | 23KV南七四線 R相AMP | FEEDER | [5 empty] | 205 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW74 | 南七十四線(XW74) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0181 |  |  | 2-B5 |  |  | F22 | A | XW74 南七十四線 S相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南七四線A2 | 23KV南七四線 S相AMP | FEEDER | [5 empty] | 206 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW74 | 南七十四線(XW74) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0182 |  |  | 2-B6 |  |  | F22 | A | XW74 南七十四線 T相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南七四線A3 | 23KV南七四線 T相AMP | FEEDER | [5 empty] | 207 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW74 | 南七十四線(XW74) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0183 |  |  | 2-B7 |  |  | F22 | A | XW74 南七十四線 N相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南七四線A0 | 23KV南七四線 N相AMP | FEEDER | [5 empty] | 208 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW75 | 南七十五線(XW75) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0184 |  |  | 2-B8 |  |  | F23 | KVAR | XW75 南七十五線 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南七五線KVAR | 23KV南七五線 KVAR | FEEDER | [5 empty] | 209 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW75 | 南七十五線(XW75) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0185 |  |  | 2-B9 |  |  | F23 | A | XW75 南七十五線 R相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南七五線A1 | 23KV南七五線 R相AMP | FEEDER | [5 empty] | 210 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW75 | 南七十五線(XW75) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0186 |  |  | 2-BA |  |  | F23 | A | XW75 南七十五線 S相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南七五線A2 | 23KV南七五線 S相AMP | FEEDER | [5 empty] | 211 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW75 | 南七十五線(XW75) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0187 |  |  | 2-BB |  |  | F23 | A | XW75 南七十五線 T相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南七五線A3 | 23KV南七五線 T相AMP | FEEDER | [5 empty] | 212 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | XW75 | 南七十五線(XW75) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0188 |  |  | 2-BC |  |  | F23 | A | XW75 南七十五線 N相電流 | A_-600_600(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南七五線A0 | 23KV南七五線 N相AMP | FEEDER | [5 empty] | 213 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW36 | 南十六線(XW36) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0189 |  |  | 2-BD |  |  | F24 | KVAR | XW36 南十六線 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十六線KVAR | 11KV南十六線 KVAR | FEEDER | [5 empty] | 214 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW36 | 南十六線(XW36) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0190 |  |  | 2-BE |  |  | F24 | A | XW36 南十六線 R相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十六線A1 | 11KV南十六線 R相AMP | FEEDER | [5 empty] | 215 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW36 | 南十六線(XW36) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0191 |  |  | 2-BF |  |  | F24 | A | XW36 南十六線 S相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十六線A2 | 11KV南十六線 S相AMP | FEEDER | [5 empty] | 216 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 0 |  | RTU | RTU |  | ADCL4 |  |  | MvMoment | No4 AI參考點 10% |  | Y |  | AI | [6 empty] | 0192 |  |  | 2-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.4 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | [5 empty] | 217 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 0 |  | RTU | RTU |  | ADCH4 |  |  | MvMoment | No4 AI參考點 90% |  | Y |  | AI | [6 empty] | 0193 |  |  | 2-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.4 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | [5 empty] | 218 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW36 | 南十六線(XW36) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0194 |  |  | 2-C2 |  |  | F24 | A | XW36 南十六線 T相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十六線A3 | 11KV南十六線 T相AMP | FEEDER | [5 empty] | 219 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW36 | 南十六線(XW36) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0195 |  |  | 2-C3 |  |  | F24 | A | XW36 南十六線 N相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十六線A0 | 11KV南十六線 N相AMP | FEEDER | [5 empty] | 220 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0196 |  |  | 2-C4 |  |  | M3A | MW | M3A 350 瓦 | MW_-108_108(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.#3DTR(A)_MW | #3DTR二次側(A) MW | MTR | [5 empty] | 221 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.216 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0197 |  |  | 2-C5 |  |  | M3A | KVAR | M3A 350 乏 | MVAR_-72_72(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.#3DTR(A)_MVAR | #3DTR二次側(A) MVAR | MTR | [5 empty] | 222 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0198 |  |  | 2-C6 |  |  | M3A | A | M3A 350 R相電流 | A_-3000_3000(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.#3DTR(A)_A1 | #3DTR二次側(A) R相AMP | MTR | [5 empty] | 223 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0199 |  |  | 2-C7 |  |  | M3A | A | M3A 350 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.#3DTR(A)_A2 | #3DTR二次側(A) S相AMP | MTR | [5 empty] | 224 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0200 |  |  | 2-C8 |  |  | M3A | A | M3A 350 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.#3DTR(A)_A3 | #3DTR二次側(A) T相AMP | MTR | [5 empty] | 225 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 3ABUS | #3ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0201 |  |  | 2-C9 |  |  | M3A | KV | #3A PT | kV_-18_18(-2000_2000) | aba | B3/D08_A1 | [8 empty] | 斗南DS.23KV#3ABUS_KV | 23KV #3ABUS KV | BUS | [5 empty] | 226 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D08 | 斗南DS | 11 | 11kV | XW37 | 南十七線(XW37) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0202 |  |  | 2-CA |  |  | F25 | KVAR | XW37 南十七線 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十七線KVAR | 11KV南十七線 KVAR | FEEDER | [5 empty] | 227 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW37 | 南十七線(XW37) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0203 |  |  | 2-CB |  |  | F25 | A | XW37 南十七線 R相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十七線A1 | 11KV南十七線 R相AMP | FEEDER | [5 empty] | 228 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW37 | 南十七線(XW37) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0204 |  |  | 2-CC |  |  | F25 | A | XW37 南十七線 S相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十七線A2 | 11KV南十七線 S相AMP | FEEDER | [5 empty] | 229 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW37 | 南十七線(XW37) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0205 |  |  | 2-CD |  |  | F25 | A | XW37 南十七線 T相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十七線A3 | 11KV南十七線 T相AMP | FEEDER | [5 empty] | 230 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW37 | 南十七線(XW37) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0206 |  |  | 2-CE |  |  | F25 | A | XW37 南十七線 N相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十七線A0 | 11KV南十七線 N相AMP | FEEDER | [5 empty] | 231 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW38 | 南十八線(XW38) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0207 |  |  | 2-CF |  |  | F26 | KVAR | XW38 南十八線 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十八線KVAR | 11KV南十八線 KVAR | FEEDER | [5 empty] | 232 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW38 | 南十八線(XW38) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0208 |  |  | 2-D0 |  |  | F26 | A | XW38 南十八線 R相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十八線A1 | 11KV南十八線 R相AMP | FEEDER | [5 empty] | 233 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW38 | 南十八線(XW38) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0209 |  |  | 2-D1 |  |  | F26 | A | XW38 南十八線 S相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十八線A2 | 11KV南十八線 S相AMP | FEEDER | [5 empty] | 234 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW38 | 南十八線(XW38) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0210 |  |  | 2-D2 |  |  | F26 | A | XW38 南十八線 T相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十八線A3 | 11KV南十八線 T相AMP | FEEDER | [5 empty] | 235 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW38 | 南十八線(XW38) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0211 |  |  | 2-D3 |  |  | F26 | A | XW38 南十八線 N相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十八線A0 | 11KV南十八線 N相AMP | FEEDER | [5 empty] | 236 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW39 | 南十九線(XW39) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0212 |  |  | 2-D4 |  |  | F27 | KVAR | XW39 南十九線 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十九線KVAR | 11KV南十九線 KVAR | FEEDER | [5 empty] | 237 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW39 | 南十九線(XW39) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0213 |  |  | 2-D5 |  |  | F27 | A | XW39 南十九線 R相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十九線A1 | 11KV南十九線 R相AMP | FEEDER | [5 empty] | 238 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW39 | 南十九線(XW39) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0214 |  |  | 2-D6 |  |  | F27 | A | XW39 南十九線 S相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十九線A2 | 11KV南十九線 S相AMP | FEEDER | [5 empty] | 239 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW39 | 南十九線(XW39) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0215 |  |  | 2-D7 |  |  | F27 | A | XW39 南十九線 T相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十九線A3 | 11KV南十九線 T相AMP | FEEDER | [5 empty] | 240 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW39 | 南十九線(XW39) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0216 |  |  | 2-D8 |  |  | F27 | A | XW39 南十九線 N相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南十九線A0 | 11KV南十九線 N相AMP | FEEDER | [5 empty] | 241 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW39 | 南十九線(XW39) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BBus | L/XW39/T1 |  |  | 0239 |  | 0055 | 1-1D-07 |  | 1-37 | F27 | ON/OFF | XW39 南十九線 CB 52AS |  | bbeb | B2/D08_D1 | [8 empty] | 斗南DS.XW39_CB | XW39(11KV南十九線) CB | FEEDER | [5 empty] | 394 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | XW39 | 南十九線(XW39) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0240 |  |  | 1-1E-00 |  |  | F27 | PHA | XW39 南十九線 RY PHA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW39_PHA | 11KV南十九線(XW39) 相間RY | FEEDER | [5 empty] | 395 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW39 | 南十九線(XW39) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0241 |  |  | 1-1E-01 |  |  | F27 | GDA | XW39 南十九線 RY GDA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW39_GDA | 11KV南十九線(XW39) 接地RY | FEEDER | [5 empty] | 396 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW39 | 南十九線(XW39) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0823 |  | 0180 | 2-33-07 |  | 2-34 | Locate Empty | ON/OFF | XW39 南十九線 F27 79S |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW39_79UL | 11KV南十九線(XW39) 79RY U/L | FEEDER | [5 empty] | 540 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS | 11 | 11kV | XW39 | 南十九線(XW39) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0824 |  | 0181 | 2-33-08 |  | 2-35 | Locate Empty | ON/OFF | XW39 南十九線 F27 51NS |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW39_LCO_TAP | 11KV南十九線(XW39) LCO TAP | FEEDER | [5 empty] | 541 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D08 | 斗南DS | 11 | 11kV | 360 | #3DTR(B)(360) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0222 |  |  | 2-DE |  |  | M3B | MW | M3B 360 瓦 | MW_-54_54(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.#3DTR(B)_MW | #3DTR二次側(B) MW | MTR | [5 empty] | 247 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 360 | #3DTR(B)(360) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0223 |  |  | 2-DF |  |  | M3B | KVAR | M3B 360 乏 | MVAR_-36_36(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.#3DTR(B)_MVAR | #3DTR二次側(B) MVAR | MTR | [5 empty] | 248 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 360 | #3DTR(B)(360) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0224 |  |  | 2-E0 |  |  | M3B | A | M3B 360 R相電流 | A_-3000_3000(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.#3DTR(B)_A1 | #3DTR二次側(B) R相AMP | MTR | [5 empty] | 249 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 360 | #3DTR(B)(360) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0225 |  |  | 2-E1 |  |  | M3B | A | M3B 360 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.#3DTR(B)_A2 | #3DTR二次側(B) S相AMP | MTR | [5 empty] | 250 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 360 | #3DTR(B)(360) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0226 |  |  | 2-E2 |  |  | M3B | A | M3B 360 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D08_A1 | [8 empty] | 斗南DS.#3DTR(B)_A3 | #3DTR二次側(B) T相AMP | MTR | [5 empty] | 251 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 3BBUS | #3BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0227 |  |  | 2-E3 |  |  | M3B | KV | #3B PT | kV_-9_9(-2000_2000) | bba | B3/D08_A1 | [8 empty] | 斗南DS.11KV#3BBUS_KV | 11KV #3BBUS KV | BUS | [5 empty] | 252 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D08 | 斗南DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D08D241/T1 |  | 0015 |  | 0004 | 1-01-07 |  | 1-04 | 1510 | ON/OFF | 虎菁一路(1510 CB) 52AS |  | aaaa | B2/D08_A1 | [8 empty] | 斗南DS.1510_CB | 1510(斗南虎菁一路) CB | LINE161 | [5 empty] | 253 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-02-00 |  |  | 1510 | 87A | 虎菁一路(1510 RY) 87A |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1510_87A | 斗南虎菁一路(1510) 87RY | LINE161 | [5 empty] | 254 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 |  |  | 1-02-02 |  |  | 1510 | PHA | 虎菁一路(1510 RY) PHA |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1510_PHA | 斗南虎菁一路(1510) 相間RY | LINE161 | [5 empty] | 255 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0019 |  |  | 1-02-03 |  |  | 1510 | GDA | 虎菁一路(1510 RY) GDA |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1510_GDA | 斗南虎菁一路(1510) 接地RY | LINE161 | [5 empty] | 256 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D08D242/T1 |  | 0020 |  | 0005 | 1-02-04 |  | 1-05 | 1520 | ON/OFF | 虎菁二路(1520 CB) 52AS |  | aaba | B2/D08_A1 | [8 empty] | 斗南DS.1520_CB | 1520(斗南虎菁二路) CB | LINE161 | [5 empty] | 257 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-05 |  |  | 1520 | 87A | 虎菁二路(1520 RY) 87A |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1520_87A | 斗南虎菁二路(1520) 87RY | LINE161 | [5 empty] | 258 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0023 |  |  | 1-02-07 |  |  | 1520 | PHA | 虎菁二路(1520 RY) PHA |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1520_PHA | 斗南虎菁二路(1520) 相間RY | LINE161 | [5 empty] | 259 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0024 |  |  | 1-03-00 |  |  | 1520 | GDA | 虎菁二路(1520 RY) GDA |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1520_GDA | 斗南虎菁二路(1520) 接地RY | LINE161 | [5 empty] | 260 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1530 | 雲林～斗南線(1530) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P03D08/T2 |  | 0025 |  | 0006 | 1-03-01 |  | 1-06 | 1530 | ON/OFF | 雲林斗南線 (1530 CB) 52AS |  | aaea | B2/D08_A1 | [8 empty] | 斗南DS.1530_CB | 1530(雲林斗南線) CB | LINE161 | [5 empty] | 261 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 161 | 161kV | 1530 | 雲林～斗南線(1530) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0026 |  |  | 1-03-02 |  |  | 1530 | 87A | 雲林斗南線 (1530 RY) 87A |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1530_87A | 雲林斗南線(1530) 87RY | LINE161 | [5 empty] | 262 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1530 | 雲林～斗南線(1530) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0028 |  |  | 1-03-04 |  |  | 1530 | PHA | 雲林斗南線 (1530 RY) PHA |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1530_PHA | 雲林斗南線(1530) 相間RY | LINE161 | [5 empty] | 263 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1530 | 雲林～斗南線(1530) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0029 |  |  | 1-03-05 |  |  | 1530 | GDA | 雲林斗南線 (1530 RY) GDA |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1530_GDA | 雲林斗南線(1530) 接地RY | LINE161 | [5 empty] | 264 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1540 | 斗南～北勢線(1540) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D08D10/T1 |  | 0030 |  | 0007 | 1-03-06 |  | 1-07 | 1540 | ON/OFF | 斗南北勢線(1540 CB) 52AS |  | aaga | B2/D08_A1 | [8 empty] | 斗南DS.1540_CB | 1540(斗南北勢線) CB | LINE161 | [5 empty] | 265 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 161 | 161kV | 1540 | 斗南～北勢線(1540) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0031 |  |  | 1-03-07 |  |  | 1540 | 87A1 | 斗南北勢線 (1540 RY) 87A1 |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1540_87A1 | 斗南北勢線(1540)第一套87RY | OTHER | [5 empty] | 266 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1540 | 斗南～北勢線(1540) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0033 |  |  | 1-04-01 |  |  | 1540 | PHA | 斗南北勢線 (1540 RY) PHA |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1540_PHA | 斗南北勢線(1540) 相間RY | LINE161 | [5 empty] | 267 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1540 | 斗南～北勢線(1540) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0034 |  |  | 1-04-02 |  |  | 1540 | GDA | 斗南北勢線 (1540 RY) GDA |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1540_GDA | 斗南北勢線(1540) 接地RY | LINE161 | [5 empty] | 268 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1540 | 斗南～北勢線(1540) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0035 |  |  | 1-04-03 |  |  | 1540 | 87A2 | 斗南北勢線 (1540 RY) 87A2 |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1540_87A2 | 斗南北勢線(1540)第二套87RY | OTHER | [5 empty] | 269 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0040 |  | 0009 | 1-05-00 |  | 1-09 | 1500 | ON/OFF | 1500 CB 52AS |  | aacz | B2/D08_A1 | [8 empty] | 斗南DS.1500_CB | 1500(TIE) CB | TIE | [5 empty] | 270 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0041 |  |  | 1-05-01 |  |  | 1500 | 50RY | 1500 RY 50A |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1500_50A | 161KV TIE(1500) 50RY | TIE | [5 empty] | 271 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0042 |  |  | 1-05-02 |  |  | 161KV BUS | 87B1A | 161KV #1BUS 87A |  |  | B2/D08_A1 | [8 empty] | 斗南DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | [5 empty] | 272 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0043 |  |  | 1-05-03 |  |  | 161KV BUS | 87B2A | 161KV #2BUS 87A |  |  | B2/D08_A1 | [8 empty] | 斗南DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | [5 empty] | 273 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0044 |  |  | 1-05-04 |  |  | OSCA | A/N | 161KV示波器啟動警報OSCA |  |  | B3/D08_A1 | [8 empty] | 斗南DS.161KV_OSCA | 161KV示波器啟動警報 | OTHER | [5 empty] | 274 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0045 |  |  | 1-05-05 |  |  | 79RY |  | 161KV RCA |  |  | B3/D08_A1 | [8 empty] | 斗南DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | [5 empty] | 275 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2DTR |  | 0062 |  | 0011 | 1-07-06 |  | 1-0B | #2MTR | ON/OFF | NO.2 TR 1760 CB 52AS |  | aadb | ELEM/D08_A1 | [8 empty] | 斗南DS.1760_CB | 1760(#2DTR) CB | MTR | [5 empty] | 282 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS |  |  | 1DTR | #1DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0049 |  |  | 1-06-01 |  |  | #1MTR | 87A | NO.1 TR 87 RY 87A |  |  | B1/D08_A1 | [16 empty] | 277 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D08 | 斗南DS |  |  | 1DTR | #1DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0050 |  |  | 1-06-02 |  |  | #1MTR | 96PA | NO.1 TR 機械保護動作(96PA) |  |  | B1/D08_A1 | [16 empty] | 278 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D08 | 斗南DS |  |  | 1DTR | #1DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0051 |  |  | 1-06-03 |  |  | #1MTR | 51ZA | NO.1 TR 51Z RY 51ZA |  |  | B1/D08_A1 | [16 empty] | 279 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D08 | 斗南DS | 161 | 161kV | 1750 | #1DTR(1750) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | 1750 | PHA | NO.1 TR(一次側) 1750 PHA |  |  | B2/D08_A1 | [16 empty] | 280 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D08 | 斗南DS | 161 | 161kV | 1750 | #1DTR(1750) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0053 |  |  | 1-06-05 |  |  | 1750 | GDA | NO.1 TR(一次側) 1750 GDA |  |  | B2/D08_A1 | [16 empty] | 281 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D08 | 斗南DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | T/2DTR(A) |  |  | 0070 |  | 0035 | 1-08-06 |  | 1-23 | M2A | ON/OFF | M2A 330 CB 52AS |  | aaca | ELEM/D08_A1 | [8 empty] | 斗南DS.330_CB | 330(#2DTR) CB | MTR | [5 empty] | 290 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS |  |  | 2DTR | #2DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0063 |  |  | 1-07-07 |  |  | #2MTR | 87A | NO.2 TR 87 RY 87A |  |  | B1/D08_A1 | [8 empty] | 斗南DS.#2DTR_87A | #2DTR 87RY | MTR | [5 empty] | 283 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS |  |  | 2DTR | #2DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0064 |  |  | 1-08-00 |  |  | #2MTR | 96PA | NO.2 TR 機械保護動作(96PA) |  |  | B1/D08_A1 | [8 empty] | 斗南DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | [5 empty] | 284 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS |  |  | 2DTR | #2DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0065 |  |  | 1-08-01 |  |  | #2MTR | 51ZA | NO.2 TR 51Z RY 51ZA |  |  | B1/D08_A1 | [8 empty] | 斗南DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | [5 empty] | 285 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1760 | #2DTR(1760) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0066 |  |  | 1-08-02 |  |  | 1760 | PHA | NO.2 TR(一次側) 1760 PHA |  |  | B2/D08_A1 | [8 empty] | 斗南DS.#2DTR_51A | #2DTR 51RY | MTR | [5 empty] | 286 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1760 | #2DTR(1760) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0067 |  |  | 1-08-03 |  |  | 1760 | GDA | NO.2 TR(一次側) 1760 GDA |  |  | B2/D08_A1 | [8 empty] | 斗南DS.#2DTR_51NA | #2DTR 51N RY | MTR | [5 empty] | 287 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 |  |  | 1-08-04 |  |  | M2A | PHA | M2A 330 3φ51 RY PHA |  |  | B3/D08_A1 | [8 empty] | 斗南DS.330_51A | #2DTR二次側(330) 51RY | MTR | [5 empty] | 288 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 |  |  | 1-08-05 |  |  | M2B | PHA | M2B 340 3φ51 RY PHA |  |  | B3/D08_A1 | [8 empty] | 斗南DS.340_51A | #2DTR二次側(340) 51RY | MTR | [5 empty] | 289 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | T/2DTR(B) |  |  | 0073 |  | 0045 | 1-09-01 |  | 1-2D | M2B | ON/OFF | M2B 340 CB 52AS |  | baca | ELEM/D08_A1 | [8 empty] | 斗南DS.340_CB | 340(#2DTR) CB | MTR | [5 empty] | 293 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0071 |  |  | 1-08-07 |  |  | M2A | PHA | M2A 330 RY PHA |  |  | B3/D08_A1 | [8 empty] | 斗南DS.330_PHA2 | 330開關箱IED RY PHA | OTHER | [5 empty] | 291 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0072 |  |  | 1-09-00 |  |  | M2A | GDA | M2A 330 RY GDA |  |  | B3/D08_A1 | [8 empty] | 斗南DS.330_GDA | 330開關箱IED RY GDA | OTHER | [5 empty] | 292 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/3DTR |  | 0076 |  | 0012 | 1-09-04 |  | 1-0C | #3MTR | ON/OFF | NO.3 TR 1770 CB 52AS |  | aafb | ELEM/D08_A1 | [8 empty] | 斗南DS.1770_CB | 1770(#3DTR) CB | MTR | [5 empty] | 296 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-09-02 |  |  | M2B | PHA | M2B 340 RY PHA |  |  | B3/D08_A1 | [8 empty] | 斗南DS.340_PHA2 | 340開關箱IED RY PHA | OTHER | [5 empty] | 294 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0075 |  |  | 1-09-03 |  |  | M2B | GDA | M2B 340 RY GDA |  |  | B3/D08_A1 | [8 empty] | 斗南DS.340_GDA | 340開關箱IED RY GDA | OTHER | [5 empty] | 295 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3ABus | T/3DTR(A) |  |  | 0084 |  | 0052 | 1-0A-04 |  | 1-34 | M3A | ON/OFF | M3A 350 CB 52AS |  | abha | ELEM/D08_A1 | [8 empty] | 斗南DS.350_CB | 350(#3DTR) CB | MTR | [5 empty] | 304 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS |  |  | 3DTR | #3DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0077 |  |  | 1-09-05 |  |  | #3MTR | 87A | NO.3 TR 87 RY 87A |  |  | B1/D08_A1 | [8 empty] | 斗南DS.#3DTR_87A | #3DTR 87RY | MTR | [5 empty] | 297 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS |  |  | 3DTR | #3DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0078 |  |  | 1-09-06 |  |  | #3MTR | 96PA | NO.3 TR 機械保護動作(96PA) |  |  | B1/D08_A1 | [8 empty] | 斗南DS.#3DTR_96PA | #3DTR 機械保護動作 | MTR | [5 empty] | 298 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS |  |  | 3DTR | #3DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0079 |  |  | 1-09-07 |  |  | #3MTR | 51ZA | NO.3 TR 51Z RY 51ZA |  |  | B1/D08_A1 | [8 empty] | 斗南DS.#3DTR_51ZA | #3DTR 51Z RY | MTR | [5 empty] | 299 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS |  |  | 3DTR | #3DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0080 |  |  | 1-0A-00 |  |  | 1770 | PHA | NO.3 TR(一次側) 1770 PHA |  |  | B1/D08_A1 | [8 empty] | 斗南DS.#3DTR_51A | #3DTR 51RY | MTR | [5 empty] | 300 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS |  |  | 3DTR | #3DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0081 |  |  | 1-0A-01 |  |  | 1770 | GDA | NO.3 TR(一次側) 1770 GDA |  |  | B1/D08_A1 | [8 empty] | 斗南DS.#3DTR_51NA | #3DTR 51N RY | MTR | [5 empty] | 301 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0082 |  |  | 1-0A-02 |  |  | M3A | PHA | M3A 350 3φ51 RY PHA |  |  | B3/D08_A1 | [8 empty] | 斗南DS.350_51A | #3DTR二次側(350) 51RY | MTR | [5 empty] | 302 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | 360 | #3DTR(B)(360) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0083 |  |  | 1-0A-03 |  |  | M3B | PHA | M3B 360 3φ51 RY PHA |  |  | B3/D08_A1 | [8 empty] | 斗南DS.360_51A | #3DTR二次側(360) 51RY | MTR | [5 empty] | 303 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | 360 | #3DTR(B)(360) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3BBus | T/3DTR(B) |  |  | 0087 |  | 0058 | 1-0A-07 |  | 1-3A | M3B | ON/OFF | M3B 360 CB 52AS |  | bbha | ELEM/D08_A1 | [8 empty] | 斗南DS.360_CB | 360(#3DTR) CB | MTR | [5 empty] | 307 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0085 |  |  | 1-0A-05 |  |  | M3A | PHA | M3A 350 RY PHA |  |  | B3/D08_A1 | [8 empty] | 斗南DS.350_PHA2 | 350開關箱IED RY PHA | OTHER | [5 empty] | 305 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0086 |  |  | 1-0A-06 |  |  | M3A | GDA | M3A 350 RY GDA |  |  | B3/D08_A1 | [8 empty] | 斗南DS.350_GDA | 350開關箱IED RY GDA | OTHER | [5 empty] | 306 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | 390 | #1SSTR(390) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | T/1SSTR |  |  | 0128 |  | 0013 | 1-10-00 |  | 1-0D | #1SSTR | ON/OFF | #1SSTR 390 CB 52AS |  | bajb | B3/D08_A1 | [8 empty] | 斗南DS.390_CB | 390(#1SSTR) CB | OTHER | [5 empty] | 313 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | 360 | #3DTR(B)(360) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0088 |  |  | 1-0B-00 |  |  | M3B | PHA | M3B 360 RY PHA |  |  | B3/D08_A1 | [8 empty] | 斗南DS.360_PHA2 | 360開關箱IED RY PHA | OTHER | [5 empty] | 308 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | 360 | #3DTR(B)(360) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0089 |  |  | 1-0B-01 |  |  | M3B | GDA | M3B 360 RY GDA |  |  | B3/D08_A1 | [8 empty] | 斗南DS.360_GDA | 360開關箱IED RY GDA | OTHER | [5 empty] | 309 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | RTU | RTU |  | RTU_MCT |  |  | Status | RTU Master Ry | Open/Close | Y | E | DI-SP | [6 empty] | 0090 |  |  | 1-0B-02 |  |  | 161RTU | MCT_ SOE | RTU MASTER RY SOE |  |  | B3/D08_A1 | [16 empty] | 310 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D08 | 斗南DS |  |  | 2DTR | #2DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0091 |  |  | 1-0B-03 |  |  | 86A |  | #2 DTR. 86A |  |  | B1/D08_A1 | [8 empty] | 斗南DS.#2DTR_86A | #2DTR 86A | OTHER | [5 empty] | 311 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D08 | 斗南DS |  |  | 3DTR | #3DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0092 |  |  | 1-0B-04 |  |  | 86A |  | #3 DTR. 86A |  |  | B1/D08_A1 | [8 empty] | 斗南DS.#3DTR_86A | #3DTR 86A | OTHER | [5 empty] | 312 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW61 | 南六一線(XW61) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/XW61/T1 |  |  | 0161 |  | 0026 | 1-14-01 |  | 1-1A | F9 | ON/OFF | XW61 南六一線 CB 52AS |  | aaeb | B2/D08_D1 | [8 empty] | 斗南DS.XW61_CB | XW61(23KV南六一線) CB | FEEDER | [5 empty] | 316 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | 390 | #1SSTR(390) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0129 |  |  | 1-10-01 |  |  | #1SSTR | PHA | #1SSTR 390 RY PHA |  |  | B3/D08_A1 | [8 empty] | 斗南DS.#1SSTR_51A | #1SSTR 51RY | OTHER | [5 empty] | 314 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | 390 | #1SSTR(390) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-10-02 |  |  | #1SSTR | GDA | #1SSTR 390 RY GDA |  |  | B3/D08_A1 | [8 empty] | 斗南DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | [5 empty] | 315 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW62 | 南六二線(XW62) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/XW62/T1 |  |  | 0164 |  | 0027 | 1-14-04 |  | 1-1B | F10 | ON/OFF | XW62 南六二線 CB 52AS |  | aafb | B2/D08_D1 | [8 empty] | 斗南DS.XW62_CB | XW62(23KV南六二線) CB | FEEDER | [5 empty] | 319 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | XW61 | 南六一線(XW61) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0162 |  |  | 1-14-02 |  |  | F9 | PHA | XW61 南六一線 RY PHA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW61_PHA | 23KV南六一線(XW61) 相間RY | FEEDER | [5 empty] | 317 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW61 | 南六一線(XW61) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0163 |  |  | 1-14-03 |  |  | F9 | GDA | XW61 南六一線 RY GDA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW61_GDA | 23KV南六一線(XW61) 接地RY | FEEDER | [5 empty] | 318 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | 100 | TIE(100) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | L/TIE-2A |  |  | 0167 |  | 0028 | 1-14-07 |  | 1-1C | #2A TIE | ON/OFF | #2A TIE 100 CB 52AS(SPARE) |  | aaab | B3/D08_A1 | [16 empty] | 322 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D08 | 斗南DS | 22 | 22kV | XW62 | 南六二線(XW62) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0165 |  |  | 1-14-05 |  |  | F10 | PHA | XW62 南六二線 RY PHA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW62_PHA | 23KV南六二線(XW62) 相間RY | FEEDER | [5 empty] | 320 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW62 | 南六二線(XW62) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0166 |  |  | 1-14-06 |  |  | F10 | GDA | XW62 南六二線 RY GDA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW62_GDA | 23KV南六二線(XW62) 接地RY | FEEDER | [5 empty] | 321 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW63 | 南六三線(XW63) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/XW63/T1 |  |  | 0170 |  | 0029 | 1-15-02 |  | 1-1D | F11 | ON/OFF | XW63 南六三線 CB 52AS |  | aagb | B2/D08_D1 | [8 empty] | 斗南DS.XW63_CB | XW63(23KV南六三線) CB | FEEDER | [5 empty] | 325 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | XW64 | 南六四線(XW64) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/XW64/T1 |  |  | 0173 |  | 0030 | 1-15-05 |  | 1-1E | F12 | ON/OFF | XW64 南六四線 CB 52AS |  | aahb | B2/D08_D1 | [8 empty] | 斗南DS.XW64_CB | XW64(23KV南六四線) CB | FEEDER | [5 empty] | 328 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | XW65 | 南六五線(XW65) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/XW65/T1 |  |  | 0176 |  | 0031 | 1-16-00 |  | 1-1F | F13 | ON/OFF | XW65 南六五線 CB 52AS |  | aaib | B2/D08_D1 | [8 empty] | 斗南DS.XW65_CB | XW65(23KV南六五線) CB | FEEDER | [5 empty] | 331 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | 100 | TIE(100) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0168 |  |  | 1-15-00 |  |  | #2A TIE | PHA | #2A TIE 100 RY PHA(SPARE) |  |  | B3/D08_A1 | [16 empty] | 323 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D08 | 斗南DS | 22 | 22kV | 100 | TIE(100) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0169 |  |  | 1-15-01 |  |  | #2A TIE | GDA | #2A TIE 100 RY GDA(SPARE) |  |  | B3/D08_A1 | [16 empty] | 324 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D08 | 斗南DS | 11 | 11kV | XW31 | 南十一線(XW31) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/XW31/T1 |  |  | 0179 |  | 0032 | 1-16-03 |  | 1-20 | F14 | ON/OFF | XW31 南十一線 CB 52AS |  | baeb | B2/D08_D1 | [8 empty] | 斗南DS.XW31_CB | XW31(11KV南十一線) CB | FEEDER | [5 empty] | 334 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | XW63 | 南六三線(XW63) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0171 |  |  | 1-15-03 |  |  | F11 | PHA | XW63 南六三線 RY PHA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW63_PHA | 23KV南六三線(XW63) 相間RY | FEEDER | [5 empty] | 326 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW63 | 南六三線(XW63) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0172 |  |  | 1-15-04 |  |  | F11 | GDA | XW63 南六三線 RY GDA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW63_GDA | 23KV南六三線(XW63) 接地RY | FEEDER | [5 empty] | 327 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW32 | 南十二線(XW32) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/XW32/T1 |  |  | 0182 |  | 0033 | 1-16-06 |  | 1-21 | F15 | ON/OFF | XW32 南十二線 CB 52AS |  | bafb | B2/D08_D1 | [8 empty] | 斗南DS.XW32_CB | XW32(11KV南十二線) CB | FEEDER | [5 empty] | 337 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | XW64 | 南六四線(XW64) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0174 |  |  | 1-15-06 |  |  | F12 | PHA | XW64 南六四線 RY PHA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW64_PHA | 23KV南六四線(XW64) 相間RY | FEEDER | [5 empty] | 329 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW64 | 南六四線(XW64) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0175 |  |  | 1-15-07 |  |  | F12 | GDA | XW64 南六四線 RY GDA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW64_GDA | 23KV南六四線(XW64) 接地RY | FEEDER | [5 empty] | 330 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | 230 | #3SC(230) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | C/3SC |  |  | 0185 |  | 0034 | 1-17-01 |  | 1-22 | #2ASC | ON/OFF | #3SC 230 CB 52AS |  | aadb | B3/D08_A1 | [8 empty] | 斗南DS.230_CB | 230(23KV #3SC) CB | SC | [5 empty] | 340 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | XW65 | 南六五線(XW65) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0177 |  |  | 1-16-01 |  |  | F13 | PHA | XW65 南六五線 RY PHA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW65_PHA | 23KV南六五線(XW65) 相間RY | FEEDER | [5 empty] | 332 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW65 | 南六五線(XW65) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0178 |  |  | 1-16-02 |  |  | F13 | GDA | XW65 南六五線 RY GDA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW65_GDA | 23KV南六五線(XW65) 接地RY | FEEDER | [5 empty] | 333 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | 300 | TIE(300) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/2ABus | B/3ABus |  |  | 0188 |  | 0036 | 1-17-04 |  | 1-24 | #2C TIE | ON/OFF | #2C TIE 300 CB 52AS |  | aajb | B3/D08_A1 | [8 empty] | 斗南DS.300_CB | 300(TIE) CB | TIE | [5 empty] | 343 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 11 | 11kV | XW31 | 南十一線(XW31) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0180 |  |  | 1-16-04 |  |  | F14 | PHA | XW31 南十一線 RY PHA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW31_PHA | 11KV南十一線(XW31) 相間RY | FEEDER | [5 empty] | 335 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW31 | 南十一線(XW31) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0181 |  |  | 1-16-05 |  |  | F14 | GDA | XW31 南十一線 RY GDA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW31_GDA | 11KV南十一線(XW31) 接地RY | FEEDER | [5 empty] | 336 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | 200 | TIE(200) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | L/TIE-2B |  |  | 0191 |  | 0037 | 1-17-07 |  | 1-25 | #2B TIE | ON/OFF | #2B TIE 200 CB 52AS(SPARE) |  | baab | B3/D08_A1 | [16 empty] | 346 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D08 | 斗南DS | 11 | 11kV | XW32 | 南十二線(XW32) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0183 |  |  | 1-16-07 |  |  | F15 | PHA | XW32 南十二線 RY PHA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW32_PHA | 11KV南十二線(XW32) 相間RY | FEEDER | [5 empty] | 338 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW32 | 南十二線(XW32) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0184 |  |  | 1-17-00 |  |  | F15 | GDA | XW32 南十二線 RY GDA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW32_GDA | 11KV南十二線(XW32) 接地RY | FEEDER | [5 empty] | 339 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | 490 | #2SSTR(490) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3BBus | T/2SSTR |  |  | 0194 |  | 0038 | 1-18-02 |  | 1-26 | #2SSTR | ON/OFF | #2SSTR 490 CB 52AS |  | bbib | B3/D08_A1 | [8 empty] | 斗南DS.490_CB | 490(#2SSTR) CB | OTHER | [5 empty] | 349 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | 230 | #3SC(230) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0186 |  |  | 1-17-02 |  |  | #2ASC | SCA | #3SC 230 RY SCA |  |  | B3/D08_A1 | [8 empty] | 斗南DS.230_SCA | 23KV #3SC 51,51N RY | SC | [5 empty] | 341 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | 230 | #3SC(230) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0187 |  |  | 1-17-03 |  |  | #2ASC | UVA | #3SC 230 RY UVA |  |  | B3/D08_A1 | [8 empty] | 斗南DS.230_UVA | 23KV #3SC 27RY(欠壓) | SC | [5 empty] | 342 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW33 | 南十三線(XW33) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/XW33/T1 |  |  | 0197 |  | 0039 | 1-18-05 |  | 1-27 | F16 | ON/OFF | XW33 南十三線 CB 52AS |  | bagb | B2/D08_D1 | [8 empty] | 斗南DS.XW33_CB | XW33(11KV南十三線) CB | FEEDER | [5 empty] | 352 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | 300 | TIE(300) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0189 |  |  | 1-17-05 |  |  | #2C TIE | PHA | #2C TIE 300 RY PHA |  |  | B3/D08_A1 | [8 empty] | 斗南DS.300_51A | 23KV TIE(300) 51RY | TIE | [5 empty] | 344 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | 300 | TIE(300) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0190 |  |  | 1-17-06 |  |  | #2C TIE | GDA | #2C TIE 300 RY GDA |  |  | B3/D08_A1 | [8 empty] | 斗南DS.300_51NA | 23KV TIE(300) 51N RY | TIE | [5 empty] | 345 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW34 | 南十四線(XW34) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/XW34/T1 |  |  | 0200 |  | 0040 | 1-19-00 |  | 1-28 | F17 | ON/OFF | XW34 南十四線 CB 52AS |  | bahb | B2/D08_D1 | [8 empty] | 斗南DS.XW34_CB | XW34(11KV南十四線) CB | FEEDER | [5 empty] | 355 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | 200 | TIE(200) |  | D1 | 201 | ADD | Status | D1 | Close/Open | Y | 1 | DI-SP | [6 empty] | 0191 |  | 0037 | 1-17-07 |  | 1-25 | #2B TIE | ON/OFF | #2B TIE 200 CB 52AS(SPARE) |  | baab | B3/D08_A1 | [16 empty] | 346 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D08 | 斗南DS | 11 | 11kV | 200 | TIE(200) |  | E1 | 201E | ADD | Status | E1 | Close/Open | Y | 1 | DI-SP | [6 empty] | 0191 |  | 0037 | 1-17-07 |  | 1-25 | #2B TIE | ON/OFF | #2B TIE 200 CB 52AS(SPARE) |  | baab | B3/D08_A1 | [16 empty] | 346 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D08 | 斗南DS | 11 | 11kV | 200 | TIE(200) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0192 |  |  | 1-18-00 |  |  | #2B TIE | PHA | #2B TIE 200 RY PHA(SPARE) |  |  | B3/D08_A1 | [16 empty] | 347 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D08 | 斗南DS | 11 | 11kV | 200 | TIE(200) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0193 |  |  | 1-18-01 |  |  | #2B TIE | GDA | #2B TIE 200 RY GDA(SPARE) |  |  | B3/D08_A1 | [16 empty] | 348 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D08 | 斗南DS | 11 | 11kV | XW35 | 南十五線(XW35) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/XW35/T1 |  |  | 0203 |  | 0041 | 1-19-03 |  | 1-29 | F18 | ON/OFF | XW35 南十五線 CB 52AS |  | baib | B2/D08_D1 | [8 empty] | 斗南DS.XW35_CB | XW35(11KV南十五線) CB | FEEDER | [5 empty] | 358 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | 490 | #2SSTR(490) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0195 |  |  | 1-18-03 |  |  | #2SSTR | PHA | #2SSTR 490 RY PHA |  |  | B3/D08_A1 | [8 empty] | 斗南DS.#2SSTR_51A | #2SSTR 51RY | OTHER | [5 empty] | 350 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | 490 | #2SSTR(490) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0196 |  |  | 1-18-04 |  |  | #2SSTR | GDA | #2SSTR 490 RY GDA |  |  | B3/D08_A1 | [8 empty] | 斗南DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | [5 empty] | 351 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW71 | 南七十一線(XW71) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3ABus | L/XW71/T1 |  |  | 0206 |  | 0042 | 1-19-06 |  | 1-2A | F19 | ON/OFF | XW71 南七十一線 CB 52AS |  | abab | B2/D08_D1 | [8 empty] | 斗南DS.XW71_CB | XW71(23KV南七一線) CB | FEEDER | [5 empty] | 361 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | XW33 | 南十三線(XW33) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0198 |  |  | 1-18-06 |  |  | F16 | PHA | XW33 南十三線 RY PHA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW33_PHA | 11KV南十三線(XW33) 相間RY | FEEDER | [5 empty] | 353 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW33 | 南十三線(XW33) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0199 |  |  | 1-18-07 |  |  | F16 | GDA | XW33 南十三線 RY GDA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW33_GDA | 11KV南十三線(XW33) 接地RY | FEEDER | [5 empty] | 354 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW72 | 南七十二線(XW72) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3ABus | L/XW72/T1 |  |  | 0209 |  | 0043 | 1-1A-01 |  | 1-2B | F20 | ON/OFF | XW72 南七十二線 CB 52AS |  | abbb | B2/D08_D1 | [8 empty] | 斗南DS.XW72_CB | XW72(23KV南七二線) CB | FEEDER | [5 empty] | 364 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | XW34 | 南十四線(XW34) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0201 |  |  | 1-19-01 |  |  | F17 | PHA | XW34 南十四線 RY PHA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW34_PHA | 11KV南十四線(XW34) 相間RY | FEEDER | [5 empty] | 356 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW34 | 南十四線(XW34) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0202 |  |  | 1-19-02 |  |  | F17 | GDA | XW34 南十四線 RY GDA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW34_GDA | 11KV南十四線(XW34) 接地RY | FEEDER | [5 empty] | 357 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | 240 | #4SC(240) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | A/LBS240^C/4SC(A) |  |  | 0212 |  | 0044 | 1-1A-04 |  | 1-2C | #2BSC | ON/OFF | #4SC 240 CB 52AS |  | badb | B3/D08_A1 | [8 empty] | 斗南DS.240_CB | 240(11KV #4SC) CB | SC | [5 empty] | 367 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | XW35 | 南十五線(XW35) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0204 |  |  | 1-19-04 |  |  | F18 | PHA | XW35 南十五線 RY PHA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW35_PHA | 11KV南十五線(XW35) 相間RY | FEEDER | [5 empty] | 359 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW35 | 南十五線(XW35) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0205 |  |  | 1-19-05 |  |  | F18 | GDA | XW35 南十五線 RY GDA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW35_GDA | 11KV南十五線(XW35) 接地RY | FEEDER | [5 empty] | 360 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | 400 | TIE(400) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/2BBus | B/3BBus |  |  | 0215 |  | 0046 | 1-1A-07 |  | 1-2E | #2DTIE | ON/OFF | #2DTIE 400 CB 52AS |  | bakb | B3/D08_A1 | [8 empty] | 斗南DS.400_CB | 400(TIE) CB | TIE | [5 empty] | 370 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 22 | 22kV | XW71 | 南七十一線(XW71) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0207 |  |  | 1-19-07 |  |  | F19 | PHA | XW71 南七十一線 RY PHA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW71_PHA | 23KV南七一線(XW71) 相間RY | FEEDER | [5 empty] | 362 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW71 | 南七十一線(XW71) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0208 |  |  | 1-1A-00 |  |  | F19 | GDA | XW71 南七十一線 RY GDA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW71_GDA | 23KV南七一線(XW71) 接地RY | FEEDER | [5 empty] | 363 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW73 | 南七十三線(XW73) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3ABus | L/XW73/T1 |  |  | 0218 |  | 0047 | 1-1B-02 |  | 1-2F | F21 | ON/OFF | XW73 南七十三線 CB 52AS |  | abdb | B2/D08_D1 | [8 empty] | 斗南DS.XW73_CB | XW73(23KV南七三線) CB | FEEDER | [5 empty] | 373 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | XW72 | 南七十二線(XW72) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0210 |  |  | 1-1A-02 |  |  | F20 | PHA | XW72 南七十二線 RY PHA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW72_PHA | 23KV南七二線(XW72) 相間RY | FEEDER | [5 empty] | 365 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW72 | 南七十二線(XW72) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0211 |  |  | 1-1A-03 |  |  | F20 | GDA | XW72 南七十二線 RY GDA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW72_GDA | 23KV南七二線(XW72) 接地RY | FEEDER | [5 empty] | 366 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW74 | 南七十四線(XW74) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3ABus | L/XW74/T1 |  |  | 0221 |  | 0048 | 1-1B-05 |  | 1-30 | F22 | ON/OFF | XW74 南七十四線 CB 52AS |  | abeb | B2/D08_D1 | [8 empty] | 斗南DS.XW74_CB | XW74(23KV南七四線) CB | FEEDER | [5 empty] | 376 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | 240 | #4SC(240) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0213 |  |  | 1-1A-05 |  |  | #2BSC | SCA | #4SC 240 RY SCA |  |  | B3/D08_A1 | [8 empty] | 斗南DS.240_SCA | 11KV #4SC 51,51N RY | SC | [5 empty] | 368 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | 240 | #4SC(240) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0214 |  |  | 1-1A-06 |  |  | #2BSC | UVA | #4SC 240 RY UVA |  |  | B3/D08_A1 | [8 empty] | 斗南DS.240_UVA | 11KV #4SC 27RY(欠壓) | SC | [5 empty] | 369 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW75 | 南七十五線(XW75) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3ABus | L/XW75/T1 |  |  | 0224 |  | 0049 | 1-1C-00 |  | 1-31 | F23 | ON/OFF | XW75 南七十五線 CB 52AS |  | abfb | B2/D08_D1 | [8 empty] | 斗南DS.XW75_CB | XW75(23KV南七五線) CB | FEEDER | [5 empty] | 379 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | 400 | TIE(400) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0216 |  |  | 1-1B-00 |  |  | #2DTIE | PHA | #2DTIE 400 RY PHA |  |  | B3/D08_A1 | [8 empty] | 斗南DS.400_51A | 11KV TIE(400) 51RY | TIE | [5 empty] | 371 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | 400 | TIE(400) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0217 |  |  | 1-1B-01 |  |  | #2DTIE | GDA | #2DTIE 400 RY GDA |  |  | B3/D08_A1 | [8 empty] | 斗南DS.400_51NA | 11KV TIE(400) 51N RY | TIE | [5 empty] | 372 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW36 | 南十六線(XW36) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BBus | L/XW36/T1 |  |  | 0227 |  | 0050 | 1-1C-03 |  | 1-32 | F24 | ON/OFF | XW36 南十六線 CB 52AS |  | bbab | B2/D08_D1 | [8 empty] | 斗南DS.XW36_CB | XW36(11KV南十六線) CB | FEEDER | [5 empty] | 382 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | XW73 | 南七十三線(XW73) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0219 |  |  | 1-1B-03 |  |  | F21 | PHA | XW73 南七十三線 RY PHA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW73_PHA | 23KV南七三線(XW73) 相間RY | FEEDER | [5 empty] | 374 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW73 | 南七十三線(XW73) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0220 |  |  | 1-1B-04 |  |  | F21 | GDA | XW73 南七十三線 RY GDA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW73_GDA | 23KV南七三線(XW73) 接地RY | FEEDER | [5 empty] | 375 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | 250 | #5SC(250) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3ABus | C/5SC |  |  | 0230 |  | 0051 | 1-1C-06 |  | 1-33 | #3ASC | ON/OFF | #5SC 250 CB 52AS |  | abgb | B3/D08_A1 | [8 empty] | 斗南DS.250_CB | 250(23KV #5SC) CB | SC | [5 empty] | 385 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | XW74 | 南七十四線(XW74) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0222 |  |  | 1-1B-06 |  |  | F22 | PHA | XW74 南七十四線 RY PHA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW74_PHA | 23KV南七四線(XW74) 相間RY | FEEDER | [5 empty] | 377 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW74 | 南七十四線(XW74) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0223 |  |  | 1-1B-07 |  |  | F22 | GDA | XW74 南七十四線 RY GDA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW74_GDA | 23KV南七四線(XW74) 接地RY | FEEDER | [5 empty] | 378 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW37 | 南十七線(XW37) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BBus | L/XW37/T1 |  |  | 0233 |  | 0053 | 1-1D-01 |  | 1-35 | F25 | ON/OFF | XW37 南十七線 CB 52AS |  | bbbb | B2/D08_D1 | [8 empty] | 斗南DS.XW37_CB | XW37(11KV南十七線) CB | FEEDER | [5 empty] | 388 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | XW75 | 南七十五線(XW75) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0225 |  |  | 1-1C-01 |  |  | F23 | PHA | XW75 南七十五線 RY PHA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW75_PHA | 23KV南七五線(XW75) 相間RY | FEEDER | [5 empty] | 380 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW75 | 南七十五線(XW75) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0226 |  |  | 1-1C-02 |  |  | F23 | GDA | XW75 南七十五線 RY GDA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW75_GDA | 23KV南七五線(XW75) 接地RY | FEEDER | [5 empty] | 381 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW38 | 南十八線(XW38) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BBus | L/XW38/T1 |  |  | 0236 |  | 0054 | 1-1D-04 |  | 1-36 | F26 | ON/OFF | XW38 南十八線 CB 52AS |  | bbdb | B2/D08_D1 | [8 empty] | 斗南DS.XW38_CB | XW38(11KV南十八線) CB | FEEDER | [5 empty] | 391 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | XW36 | 南十六線(XW36) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0228 |  |  | 1-1C-04 |  |  | F24 | PHA | XW36 南十六線 RY PHA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW36_PHA | 11KV南十六線(XW36) 相間RY | FEEDER | [5 empty] | 383 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW36 | 南十六線(XW36) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0229 |  |  | 1-1C-05 |  |  | F24 | GDA | XW36 南十六線 RY GDA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW36_GDA | 11KV南十六線(XW36) 接地RY | FEEDER | [5 empty] | 384 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW40 | 南二十線(XW40) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BBus | L/XW40/T1 |  |  | 0242 |  | 0056 | 1-1E-02 |  | 1-38 | F28 | ON/OFF | XW40 南二十線 CB 52AS |  | bbfb | B2/D08_D1 | [8 empty] | 斗南DS.XW40_CB | XW40(11KV南二十線) CB | FEEDER | [5 empty] | 397 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | 250 | #5SC(250) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0231 |  |  | 1-1C-07 |  |  | #3ASC | SCA | #5SC 250 RY SCA |  |  | B3/D08_A1 | [8 empty] | 斗南DS.250_SCA | 23KV #5SC 51,51N RY | SC | [5 empty] | 386 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | 250 | #5SC(250) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0232 |  |  | 1-1D-00 |  |  | #3ASC | UVA | #5SC 250 RY UVA |  |  | B3/D08_A1 | [8 empty] | 斗南DS.250_UVA | 23KV #5SC 27RY(欠壓) | SC | [5 empty] | 387 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | 260 | #6SC(260) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3BBus | A/LBS260^C/6SC(A) |  |  | 0245 |  | 0057 | 1-1E-05 |  | 1-39 | #3BSC | ON/OFF | #6SC 260 CB 52AS |  | bbgb | B3/D08_A1 | [8 empty] | 斗南DS.260_CB | 260(11KV #6SC) CB | SC | [5 empty] | 400 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | XW37 | 南十七線(XW37) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0234 |  |  | 1-1D-02 |  |  | F25 | PHA | XW37 南十七線 RY PHA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW37_PHA | 11KV南十七線(XW37) 相間RY | FEEDER | [5 empty] | 389 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW37 | 南十七線(XW37) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0235 |  |  | 1-1D-03 |  |  | F25 | GDA | XW37 南十七線 RY GDA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW37_GDA | 11KV南十七線(XW37) 接地RY | FEEDER | [5 empty] | 390 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS |  |  | 2DTR | #2DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0570 |  |  | 1-33-10 |  |  | Locate Empty | A/N | NO.2 TR 2TRA |  | a | B1/D08_A1 | [8 empty] | 斗南DS.#2DTR_TRA | #2DTR 重故障 | MTR | [5 empty] | 434 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW38 | 南十八線(XW38) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0237 |  |  | 1-1D-05 |  |  | F26 | PHA | XW38 南十八線 RY PHA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW38_PHA | 11KV南十八線(XW38) 相間RY | FEEDER | [5 empty] | 392 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW38 | 南十八線(XW38) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0238 |  |  | 1-1D-06 |  |  | F26 | GDA | XW38 南十八線 RY GDA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW38_GDA | 11KV南十八線(XW38) 接地RY | FEEDER | [5 empty] | 393 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW40 | 南二十線(XW40) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0217 |  |  | 2-D9 |  |  | F28 | KVAR | XW40 南二十線 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南二十線KVAR | 11KV南二十線 KVAR | FEEDER | [5 empty] | 242 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW40 | 南二十線(XW40) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0218 |  |  | 2-DA |  |  | F28 | A | XW40 南二十線 R相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南二十線A1 | 11KV南二十線 R相AMP | FEEDER | [5 empty] | 243 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW40 | 南二十線(XW40) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0219 |  |  | 2-DB |  |  | F28 | A | XW40 南二十線 S相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南二十線A2 | 11KV南二十線 S相AMP | FEEDER | [5 empty] | 244 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW40 | 南二十線(XW40) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0220 |  |  | 2-DC |  |  | F28 | A | XW40 南二十線 T相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南二十線A3 | 11KV南二十線 T相AMP | FEEDER | [5 empty] | 245 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | XW40 | 南二十線(XW40) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0221 |  |  | 2-DD |  |  | F28 | A | XW40 南二十線 N相電流 | A_-500_500(-2000_2000) |  | B2/D08_D1 | [8 empty] | 斗南DS.南二十線A0 | 11KV南二十線 N相AMP | FEEDER | [5 empty] | 246 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS |  |  | 3DTR | #3DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0582 |  |  | 1-34-06 |  |  | Locate Empty | A/N | NO.3 TR 3TRA |  | a | B1/D08_A1 | [8 empty] | 斗南DS.#3DTR_TRA | #3DTR 重故障 | MTR | [5 empty] | 445 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/1DTR |  | 0048 |  | 0010 | 1-06-00 |  | 1-0A | #1MTR | ON/OFF | NO.1 TR 1750 CB 52AS |  | not found | ELEM/D08_A1 | [16 empty] | 276 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D08 | 斗南DS | 11 | 11kV | 260 | #6SC(260) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0246 |  |  | 1-1E-06 |  |  | #3BSC | SCA | #6SC 260 RY SCA |  |  | B3/D08_A1 | [8 empty] | 斗南DS.260_SCA | 11KV #6SC 51,51N RY | SC | [5 empty] | 401 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | 260 | #6SC(260) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0247 |  |  | 1-1E-07 |  |  | #3BSC | UVA | #6SC 260 RY UVA |  |  | B3/D08_A1 | [8 empty] | 斗南DS.260_UVA | 11KV #6SC 27RY(欠壓) | SC | [5 empty] | 402 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | 360 | #3DTR(B)(360) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0248 |  | 0059 | 1-1F-00 |  | 1-3B | D3B | 81A | D3B 360 CB 81 RY 動作 |  |  | B3/D08_A1 | [8 empty] | 斗南DS.81RY_A/S(1) | 360低頻電驛動作/復歸 | OTHER | [5 empty] | 403 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
D08 | 斗南DS | 11 | 11kV | XW33 | 南十三線(XW33) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0249 |  |  | 1-1F-01 |  |  | F16 | 81A | XW33 南十三線 81 RY 動作 |  |  | B2/D08_D1 | [8 empty] | 斗南DS.81RY_A/S(2) | XW33低頻電驛動作/復歸 | OTHER | [5 empty] | 404 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
D08 | 斗南DS | 11 | 11kV | XW34 | 南十四線(XW34) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0250 |  |  | 1-1F-02 |  |  | F17 | 81A | XW34 南十四線 81 RY 動作 |  |  | B2/D08_D1 | [8 empty] | 斗南DS.81RY_A/S(3) | XW34低頻電驛動作/復歸 | OTHER | [5 empty] | 405 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
D08 | 斗南DS | 11 | 11kV | XW35 | 南十五線(XW35) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0251 |  |  | 1-1F-03 |  |  | F18 | 81A | XW35 南十五線 81 RY 動作 |  |  | B2/D08_D1 | [8 empty] | 斗南DS.81RY_A/S(4) | XW35低頻電驛動作/復歸 | OTHER | [5 empty] | 406 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
D08 | 斗南DS | 11 | 11kV | ComPoint |  |  | OLTC_A |  |  | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0252 |  | 0184 | 1-1F-04 |  | 2-38 | #2B DTR | ON/OFF | #2BDTR OLTC TAP連動 |  |  | B3/D08_A1 | [8 empty] | 斗南DS.2BOLTC_TAP連動 | #2BDTR OLTC TAP連動,請確認處理 | OTHER | [5 empty] | 407 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0512 |  | 0000 | 1-30-00 |  | 1-00 | Locate Empty | ON/OFF | TEST CB ON/OFF |  |  | ELEM/ALL | [8 empty] | 斗南DS.TEST_CB | TEST CB | OTHER | [5 empty] | 408 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | RTU | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0513 |  |  | 1-30-01 |  |  | Locate Empty | ON/OFF | L/R STATUS ON/OFF |  |  | ELEM/D08_A1 | [8 empty] | 斗南DS.RTU_S/L | RTU SUPY/LOCAL | OTHER | [5 empty] | 409 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
D08 | 斗南DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0520 |  | 0068 | 1-30-08 |  | 1-44 | Locate Empty | USE/LOCK | 虎菁一路(1510) 87S |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1510_87UL | 斗南虎菁一路(1510) 87RY U/L | LINE161 | [5 empty] | 410 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0521 |  | 0069 | 1-30-09 |  | 1-45 | Locate Empty | USE/LOCK | 虎菁一路(1510) 79S |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1510_79UL | 斗南虎菁一路(1510) 79RY U/L | LINE161 | [5 empty] | 411 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0522 |  | 0070 | 1-30-10 |  | 1-46 | Locate Empty | USE/LOCK | 虎菁二路(1520) 87S |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1520_87UL | 斗南虎菁二路(1520) 87RY U/L | LINE161 | [5 empty] | 412 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0523 |  | 0071 | 1-30-11 |  | 1-47 | Locate Empty | USE/LOCK | 虎菁二路(1520) 79S |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1520_79UL | 斗南虎菁二路(1520) 79RY U/L | LINE161 | [5 empty] | 413 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS | 161 | 161kV | 1530 | 雲林～斗南線(1530) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0524 |  | 0072 | 1-30-12 |  | 1-48 | Locate Empty | USE/LOCK | 雲林斗南線 (1530) 87S |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1530_87UL | 雲林斗南線(1530) 87RY U/L | LINE161 | [5 empty] | 414 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS | 161 | 161kV | 1530 | 雲林～斗南線(1530) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0525 |  | 0073 | 1-30-13 |  | 1-49 | Locate Empty | USE/LOCK | 雲林斗南線 (1530) 79S |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1530_79UL | 雲林斗南線(1530) 79RY U/L | LINE161 | [5 empty] | 415 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS | 161 | 161kV | 1540 | 斗南～北勢線(1540) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0526 |  | 0074 | 1-30-14 |  | 1-4A | Locate Empty | USE/LOCK | 斗南北勢線 (1540) 87RY UL1 |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1540_87UL1 | 斗南北勢線(1540)#1 87RY U/L | OTHER | [5 empty] | 416 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS | 161 | 161kV | 1540 | 斗南～北勢線(1540) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0527 |  | 0075 | 1-30-15 |  | 1-4B | Locate Empty | USE/LOCK | 斗南北勢線 (1540) 79RY U/L |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1540_79UL | 斗南北勢線(1540) 79RY U/L | LINE161 | [5 empty] | 417 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS | 161 | 161kV | 1540 | 斗南～北勢線(1540) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0528 |  | 0062 | 1-31-00 |  | 1-3E | Locate Empty | USE/LOCK | 斗南北勢線 (1540) 87RY UL2 |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1540_87UL2 | 斗南北勢線(1540)#2 87RY U/L | OTHER | [5 empty] | 418 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0539 |  |  | 1-31-11 |  |  | Locate Empty |  | 虎菁一路(1510) RYFA |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1510_RYFA | 斗南虎菁一路(1510)數位電驛故障 | OTHER | [5 empty] | 419 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0540 |  |  | 1-31-12 |  |  | Locate Empty |  | 虎菁一路(1510) 87CFA |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1510_87CFA | 斗南虎菁一路(1510)87RY通訊故障 | OTHER | [5 empty] | 420 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0542 |  |  | 1-31-14 |  |  | Locate Empty |  | 虎菁二路(1520) RYFA |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1520_RYFA | 斗南虎菁二路(1520)數位電驛故障 | OTHER | [5 empty] | 421 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0543 |  |  | 1-31-15 |  |  | Locate Empty |  | 虎菁二路(1520) 87CFA |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1520_87CFA | 斗南虎菁二路(1520)87RY通訊故障 | OTHER | [5 empty] | 422 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1530 | 雲林～斗南線(1530) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0545 |  |  | 1-32-01 |  |  | Locate Empty | 87CFA | 雲林斗南線 (1530) 87RY通訊故障 |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1530_87CFA | 雲林斗南線(1530) 87RY通訊故障 | OTHER | [5 empty] | 423 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1530 | 雲林～斗南線(1530) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0546 |  |  | 1-32-02 |  |  | Locate Empty | RYFA | 雲林斗南線 (1530) 數位電驛故障 |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1530_RYFA | 雲林斗南線(1530) 數位電驛故障 | OTHER | [5 empty] | 424 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1540 | 斗南～北勢線(1540) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0548 |  |  | 1-32-04 |  |  | Locate Empty | 87CFA | 斗南北勢線 (1540) 87RY通訊故障 |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1540_87CFA | 斗南北勢線(1540))87RY通訊故障 | OTHER | [5 empty] | 425 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1540 | 斗南～北勢線(1540) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0549 |  |  | 1-32-05 |  |  | Locate Empty | RYFA | 斗南北勢線 (1540) 數位電驛故障 |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1540_RYFA | 斗南北勢線(1540)數位電驛故障 | OTHER | [5 empty] | 426 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0552 |  | 0064 | 1-32-08 |  | 1-40 | #1 BUS | ON/OFF | 161KV #1 BUS╴87UL |  |  | B2/D08_A1 | [8 empty] | 斗南DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | [5 empty] | 427 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS | 161 | 161kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0553 |  | 0065 | 1-32-09 |  | 1-41 | #2 BUS | ON/OFF | 161KV #2 BUS╴87UL |  |  | B2/D08_A1 | [8 empty] | 斗南DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | [5 empty] | 428 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS |  |  | 2DTR(A) | #2DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0565 |  |  | 1-33-05 |  |  | Locate Empty | ON/OFF | NO.2 TR(A) 243R1S3 S/L |  | c | B1/D08_A1 | [8 empty] | 斗南DS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | [5 empty] | 429 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D08 | 斗南DS |  |  | 2DTR(A) | #2DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0566 |  | 0080 | 1-33-06 |  | 1-50 | Locate Empty | ON/OFF | NO.2 TR(A) 2AXS1 A/M |  |  | B1/D08_A1 | [8 empty] | 斗南DS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | [5 empty] | 430 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D08 | 斗南DS |  |  | 2DTR(B) | #2DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0567 |  |  | 1-33-07 |  |  | Locate Empty | ON/OFF | NO.2 TR(B) 243R2S3 S/L |  | b | B1/D08_A1 | [8 empty] | 斗南DS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | [5 empty] | 431 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D08 | 斗南DS |  |  | 2DTR(B) | #2DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0568 |  | 0082 | 1-33-08 |  | 1-52 | Locate Empty | ON/OFF | NO.2 TR(B) 2BXS2 A/M |  |  | B1/D08_A1 | [8 empty] | 斗南DS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | [5 empty] | 432 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D08 | 斗南DS |  |  | 2DTR | #2DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0569 |  |  | 1-33-09 |  |  | Locate Empty | A/N | NO.2 TR 2TRF |  |  | B1/D08_A1 | [8 empty] | 斗南DS.#2DTR_TRF | #2DTR 輕故障 | MTR | [5 empty] | 433 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | 100 | TIE(100) |  | D1 | 101 | ADD | Status | D1 | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | L/TIE-2A |  |  | 0167 |  | 0028 | 1-14-07 |  | 1-1C | #2A TIE | ON/OFF | #2A TIE 100 CB 52AS(SPARE) |  | aaab | B3/D08_A1 | [16 empty] | 322 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D08 | 斗南DS |  |  | 2DTR | #2DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0571 |  |  | 1-33-11 |  |  | Locate Empty | A/N | NO.2 TR 296B1 |  |  | B1/D08_A1 | [8 empty] | 斗南DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | [5 empty] | 435 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D08 | 斗南DS |  |  | 2DTR | #2DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0572 |  |  | 1-33-12 |  |  | Locate Empty | A/N | NO.2 TR 296B2 |  |  | B1/D08_A1 | [8 empty] | 斗南DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | [5 empty] | 436 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D08 | 斗南DS |  |  | 2DTR | #2DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0573 |  |  | 1-33-13 |  |  | Locate Empty | A/N | NO.2 TR 296D |  |  | B1/D08_A1 | [8 empty] | 斗南DS.#2DTR_96D | #2DTR 96D RY | MTR | [5 empty] | 437 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D08 | 斗南DS |  |  | 2DTR | #2DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0574 |  |  | 1-33-14 |  |  | Locate Empty | A/N | NO.2 TR 296P |  |  | B1/D08_A1 | [8 empty] | 斗南DS.#2DTR_96P | #2DTR 96P RY | MTR | [5 empty] | 438 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D08 | 斗南DS |  |  | 2DTR | #2DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0575 |  |  | 1-33-15 |  |  | Locate Empty | A/N | NO.2 TR 263Q |  |  | B1/D08_A1 | [8 empty] | 斗南DS.#2DTR_63Q | #2DTR 63Q RY | MTR | [5 empty] | 439 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D08 | 斗南DS |  |  | 3DTR(A) | #3DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0577 |  |  | 1-34-01 |  |  | Locate Empty | ON/OFF | NO.3 TR(A) 343R1S3 S/L |  | c | B1/D08_A1 | [8 empty] | 斗南DS.#3DTR(A)_S/L | #3DTR(A) OLTC S/L | MTR | [5 empty] | 440 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D08 | 斗南DS |  |  | 3DTR(A) | #3DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0578 |  | 0084 | 1-34-02 |  | 1-54 | Locate Empty | ON/OFF | NO.3 TR(A) 3AXS1 A/M |  |  | B1/D08_A1 | [8 empty] | 斗南DS.#3DTR(A)_A/M | #3DTR(A) OLTC A/M | MTR | [5 empty] | 441 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D08 | 斗南DS |  |  | 3DTR(B) | #3DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0579 |  |  | 1-34-03 |  |  | Locate Empty | ON/OFF | NO.3 TR(B) 343R2S3 S/L |  | b | B1/D08_A1 | [8 empty] | 斗南DS.#3DTR(B)_S/L | #3DTR(B) OLTC S/L | MTR | [5 empty] | 442 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D08 | 斗南DS |  |  | 3DTR(B) | #3DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0580 |  | 0086 | 1-34-04 |  | 1-56 | Locate Empty | ON/OFF | NO.3 TR(B) 3BXS2 A/M |  |  | B1/D08_A1 | [8 empty] | 斗南DS.#3DTR(B)_A/M | #3DTR(B) OLTC A/M | MTR | [5 empty] | 443 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D08 | 斗南DS |  |  | 3DTR | #3DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0581 |  |  | 1-34-05 |  |  | Locate Empty | A/N | NO.3 TR 3TRF |  |  | B1/D08_A1 | [8 empty] | 斗南DS.#3DTR_TRF | #3DTR 輕故障 | MTR | [5 empty] | 444 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | 100 | TIE(100) |  | E1 | 101E | ADD | Status | E1 | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | L/TIE-2A |  |  | 0167 |  | 0028 | 1-14-07 |  | 1-1C | #2A TIE | ON/OFF | #2A TIE 100 CB 52AS(SPARE) |  | aaab | B3/D08_A1 | [16 empty] | 322 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D08 | 斗南DS |  |  | 3DTR | #3DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0583 |  |  | 1-34-07 |  |  | Locate Empty | A/N | NO.3 TR 396B1 |  |  | B1/D08_A1 | [8 empty] | 斗南DS.#3DTR_96B1 | #3DTR 96B1 RY | MTR | [5 empty] | 446 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D08 | 斗南DS |  |  | 3DTR | #3DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0584 |  |  | 1-34-08 |  |  | Locate Empty | A/N | NO.3 TR 396B2 |  |  | B1/D08_A1 | [8 empty] | 斗南DS.#3DTR_96B2 | #3DTR 96B2 RY | MTR | [5 empty] | 447 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D08 | 斗南DS |  |  | 3DTR | #3DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0585 |  |  | 1-34-09 |  |  | Locate Empty | A/N | NO.3 TR 396D |  |  | B1/D08_A1 | [8 empty] | 斗南DS.#3DTR_96D | #3DTR 96D RY | MTR | [5 empty] | 448 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D08 | 斗南DS |  |  | 3DTR | #3DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0586 |  |  | 1-34-10 |  |  | Locate Empty | A/N | NO.3 TR 396P |  |  | B1/D08_A1 | [8 empty] | 斗南DS.#3DTR_96P | #3DTR 96P RY | MTR | [5 empty] | 449 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D08 | 斗南DS |  |  | 3DTR | #3DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0587 |  |  | 1-34-11 |  |  | Locate Empty | A/N | NO.3 TR 363Q |  |  | B1/D08_A1 | [8 empty] | 斗南DS.#3DTR_63Q | #3DTR 63Q RY | MTR | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | ComPoint |  |  | OLTC_A |  |  | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0588 |  |  | 1-34-12 |  |  | OLTC | OLTCA | OLTC 15分鐘內連動3次警報 |  |  | B3/D08_A1 | [8 empty] | 斗南DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | [5 empty] | 451 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | ComPoint |  |  | BUS_RYFA |  |  | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0589 |  |  | 1-34-13 |  |  | BUS | A/N | 161KV BUS數位電驛故障 |  |  | B3/D08_A1 | [8 empty] | 斗南DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | [5 empty] | 452 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | ComPoint |  |  | 12B_CTFA | BUS_87CTFA | Element | Status | #1#2 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0590 |  |  | 1-34-14 |  |  | BUS | A/N | 161KV BUS 87RY CT 迴路故障 |  |  | B3/D08_A1 | [8 empty] | 斗南DS.161KV_BUS_CTFA | 161KV BUS 87RY CT回路故障 | OTHER | [5 empty] | 453 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | StaDev | 所內設施 |  | GEN | 緊急發電機運轉 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0591 |  |  | 1-34-15 |  |  | Locate Empty | ON/OFF | 緊急發電機運轉 |  |  | B3/D08_A1 | [8 empty] | 斗南DS.GEN | 緊急發電機運轉 | OTHER | [5 empty] | 454 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ON/OFF | OFF
D08 | 斗南DS | 0 |  | StaDev | 所內設施 |  | Fire1 | 受信總機 |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0592 |  |  | 1-35-00 |  |  | 火災警報(1) | A/N | 火災警報(1)受信總機 |  |  | B3/D08_A1 | [8 empty] | 斗南DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | [5 empty] | 455 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | StaDev | 所內設施 |  | Fire2 | (SPARE) |  | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0593 |  |  | 1-35-01 |  |  | 火災警報(2) | A/N | 火災警報(2) (SPARE) |  |  | B3/D08_A1 | [8 empty] | 斗南DS.火災警報(2) | 火災警報(2) SPARE | OTHER | [5 empty] | 456 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | StaDev | 所內設施 |  | Fire3 | (SPARE) |  | Status | 火災警報3 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0594 |  |  | 1-35-02 |  |  | 火災警報(3) | A/N | 火災警報(3) (SPARE) |  |  | B3/D08_A1 | [8 empty] | 斗南DS.火災警報(3) | 火災警報(3) SPARE | OTHER | [5 empty] | 457 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | StaDev | 所內設施 |  | Burglar1 | 保全防盜 |  | Status | 無人化防盜1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0595 |  |  | 1-35-03 |  |  | Locate Empty | A/N | 無人化防盜 (一) 保全防盜 |  |  | B3/D08_A1 | [8 empty] | 斗南DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | [5 empty] | 458 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | StaDev | 所內設施 |  | Burglar2 | (SPARE) |  | Status | 無人化防盜2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0596 |  |  | 1-35-04 |  |  | Locate Empty | A/N | 無人化防盜 (二) (SPARE) |  |  | B3/D08_A1 | [16 empty] | 459 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D08 | 斗南DS | 0 |  | StaDev | 所內設施 |  | Burglar3 | (SPARE) |  | Status | 無人化防盜3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0597 |  |  | 1-35-05 |  |  | Locate Empty | A/N | 無人化防盜 (三) (SPARE) |  |  | B3/D08_A1 | [16 empty] | 460 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D08 | 斗南DS | 0 |  | StaDev | 所內設施 |  | Door1 | 一樓大門門禁 |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0598 |  |  | 1-35-06 |  |  | Locate Empty | A/N | 無人化門禁 (一) 一樓大門門禁 |  |  | B3/D08_A1 | [8 empty] | 斗南DS.無人化門禁(1) | 無人化門禁(1)建築物大門 | OTHER | [5 empty] | 461 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | StaDev | 所內設施 |  | Door2 | 控制室門禁 |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0599 |  |  | 1-35-07 |  |  | Locate Empty | A/N | 無人化門禁 (二) 控制室門禁 |  |  | B3/D08_A1 | [8 empty] | 斗南DS.無人化門禁(2) | 無人化門禁(2)控制室大門 | OTHER | [5 empty] | 462 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | StaDev | 所內設施 |  | Door3 | (SPARE) |  | Status | 無人化門禁3 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0600 |  |  | 1-35-08 |  |  | Locate Empty | A/N | 無人化門禁 (三) (SPARE) |  |  | B3/D08_A1 | [16 empty] | 463 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D08 | 斗南DS | 0 |  | StaDev | 所內設施 |  | Lights1 |  |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0601 |  | 0060 | 1-35-09 |  | 1-3C | Locate Empty | ON/OFF | 無人化開關場照明 (A)(SPARE) |  |  | B3/D08_A1 | [16 empty] | 464 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D08 | 斗南DS | 0 |  | StaDev | 所內設施 |  | Lights2 |  |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0602 |  | 0061 | 1-35-10 |  | 1-3D | Locate Empty | ON/OFF | 無人化開關場照明 (B)(SPARE) |  |  | B3/D08_A1 | [16 empty] | 465 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D08 | 斗南DS | 0 |  | ComPoint |  |  | OPA |  |  | Status | 充油電纜低壓警報 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0603 |  |  | 1-35-11 |  |  | Locate Empty | A/N | OPA 充油電纜警報(SPARE) |  |  | B3/D08_A1 | [16 empty] | 466 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D08 | 斗南DS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0604 |  |  | 1-35-12 |  |  | Locate Empty | ON/OFF | 所內電源 ACB1 |  |  | B3/D08_A1 | [8 empty] | 斗南DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | [5 empty] | 467 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D08 | 斗南DS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0605 |  |  | 1-35-13 |  |  | Locate Empty | ON/OFF | 所內電源 ACB2 |  |  | B3/D08_A1 | [8 empty] | 斗南DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | [5 empty] | 468 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D08 | 斗南DS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0606 |  |  | 1-35-14 |  |  | Locate Empty | A/N | STUV 所內欠壓警報 |  |  | ELEM/D08_A1 | [8 empty] | 斗南DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | [5 empty] | 469 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0607 |  |  | 1-35-15 |  |  | Locate Empty | A/N | VUA1 #1 BUS 電壓電驛 |  |  | B2/D08_A1 | [8 empty] | 斗南DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | [5 empty] | 470 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0608 |  |  | 1-36-00 |  |  | Locate Empty | A/N | VUA2 #2 BUS 電壓電驛 |  |  | B2/D08_A1 | [8 empty] | 斗南DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | [5 empty] | 471 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0609 |  |  | 1-36-01 |  |  | Locate Empty | A/N | DCA 直流電源故障 |  |  | ELEM/D08_A1 | [8 empty] | 斗南DS.直流電源DCA | 直流電源故障警報 | OTHER | [5 empty] | 472 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0610 |  |  | 1-36-02 |  |  | Locate Empty | A/N | CHG1變電設備充電機故障 |  |  | B3/D08_A1 | [8 empty] | 斗南DS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | [5 empty] | 473 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0611 |  |  | 1-36-03 |  |  | 161KV TIE | 測試/正常 | 161KV TIE (1500)50RY 測試/正常 |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | [5 empty] | 474 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Test | Test | 1 |  |  | TEST/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0612 |  |  | 1-36-04 |  |  | Locate Empty | A/N | DCE 直流電源接地 |  |  | ELEM/D08_A1 | [8 empty] | 斗南DS.直流電源DCE | 直流電源接地故障警報 | OTHER | [5 empty] | 475 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | ComPoint |  |  | COMT |  |  | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0613 |  |  | 1-36-05 |  |  | Locate Empty | A/N | COMT 空壓機超時運轉(SPARE) |  |  | B3/D08_A1 | [16 empty] | 476 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D08 | 斗南DS | 161 | 161kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0614 |  |  | 1-36-06 |  |  | Locate Empty | A/N | 161KV CBA 重故障 |  |  | B3/D08_A1 | [8 empty] | 斗南DS.161KV_CBA | 161KV斷路器重故障 | OTHER | [5 empty] | 477 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0615 |  |  | 1-36-07 |  |  | Locate Empty | A/N | 161KV CBF 輕故障 |  |  | B3/D08_A1 | [8 empty] | 斗南DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | [5 empty] | 478 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | StaDev | 所內設施 |  | Water1 |  |  | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0616 |  |  | 1-36-08 |  |  | Locate Empty | A/N | OW1 地下室第一段水位警報 |  |  | B3/D08_A1 | [8 empty] | 斗南DS.水位警報(1) | 地下室水位警報(1) | OTHER | [5 empty] | 479 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | StaDev | 所內設施 |  | Water2 |  |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0617 |  |  | 1-36-09 |  |  | Locate Empty | A/N | OW2 地下室第二段水位警報 |  |  | B3/D08_A1 | [8 empty] | 斗南DS.水位警報(2) | 地下室水位警報(2) | OTHER | [5 empty] | 480 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0618 |  |  | 1-36-10 |  |  | Locate Empty | A/N | ACBA 所內用電ACB TRIP |  |  | B3/D08_A1 | [8 empty] | 斗南DS.所內電源ACBA | 所內電源故障警報 | OTHER | [5 empty] | 481 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | StaDev | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0619 |  |  | 1-36-11 |  |  | Locate Empty | A/N | PSF 變電所其他輕故障(SPARE) |  |  | B3/D08_A1 | [8 empty] | 斗南DS.其他重故障 | 變電所內其他重故障 | OTHER | [5 empty] | 482 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | StaDev | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0620 |  |  | 1-36-12 |  |  | Locate Empty | A/N | PSA 變電所其他重故障(SPARE) |  |  | B3/D08_A1 | [8 empty] | 斗南DS.其他輕故障 | 變電所內其他輕故障 | OTHER | [5 empty] | 483 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | StaDev | 所內設施 |  | AIRCON |  |  | Status | 冷氣跳脫 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0621 |  |  | 1-36-13 |  |  | Locate Empty | A/N | 冷氣空調機警報 |  |  | B3/D08_A1 | [8 empty] | 斗南DS.空調機故障 | 空調機故障或電源跳脫 | OTHER | [5 empty] | 484 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | NORMAL/FAULT | NORMAL
D08 | 斗南DS | 0 |  | ComPoint |  |  | 60A |  |  | Status | 電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0622 |  |  | 1-36-14 |  |  | Locate Empty | A/N | 60A 60電驛故障 |  |  | B3/D08_A1 | [8 empty] | 斗南DS.23KV_SC_60A | 23/11KV SC 60A | OTHER | [5 empty] | 485 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | StaDev | 所內設施 |  | OilLeak1 |  |  | Status | 洩油池水位警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0623 |  |  | 1-36-15 |  |  | Locate Empty | A/N | WPF 集油池水位警報1 |  |  | B3/D08_A1 | [8 empty] | 斗南DS.集油池警報(1) | 集油池警報(1) | OTHER | [5 empty] | 486 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | StaDev | 所內設施 |  | OilLeak2 |  |  | Status | 洩油池水位警報2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0624 |  |  | 1-37-00 |  |  | Locate Empty | A/N | WPF 集油池水位警報2 |  |  | B3/D08_A1 | [8 empty] | 斗南DS.集油池警報(2) | 集油池警報(2) | OTHER | [5 empty] | 487 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0625 |  |  | 1-37-01 |  |  | Locate Empty | A/N | 通訊充電機故障 |  |  | B3/D08_A1 | [8 empty] | 斗南DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | [5 empty] | 488 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0626 |  |  | 1-37-02 |  |  | Locate Empty | A/N | ACFA 通訊設備AC故障 |  |  | B3/D08_A1 | [8 empty] | 斗南DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | [5 empty] | 489 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | StaDev | 所內設施 |  | R_Temp |  |  | Status | 溫度警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0629 |  |  | 1-37-05 |  |  | Locate Empty | A/N | 通信室溫控警報 |  |  | B3/D08_A1 | [8 empty] | 斗南DS.通信機房溫度 | 通信機房溫度警報 | OTHER | [5 empty] | 490 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0630 |  |  | 1-37-06 |  |  | OSCF | A/N | 161KV示波器缺紙或故障警報OSCF |  |  | B3/D08_A1 | [8 empty] | 斗南DS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | [5 empty] | 491 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | ComPoint |  |  | GRZ100 |  |  | Status | 電驛GRZ100閉鎖 | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0631 |  |  | 1-37-07 |  |  | BVS盤 | LOCK/USE | 本所各GRZ100 Ry U/L |  |  | B3/D08_A1 | [8 empty] | 斗南DS.BVS_RY | BVS GRZ100 RY U/L | OTHER | [5 empty] | 492 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | LOCK/USE | USE
D08 | 斗南DS |  |  | 2DTR | #2DTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0632 |  | 0192 | 1-37-08 |  |  | #2DTR | U/L | #2DTR #1 87RY U/L |  |  | B1/D08_A1 | [8 empty] | 斗南DS.#2DTR_87UL1 | #2DTR #1 87RY U/L | OTHER |  | CDC_Cmd_EMPTY |  |  |  | 493 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS |  |  | 2DTR | #2DTR |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0633 |  | 0193 | 1-37-09 |  |  | #2DTR | U/L | #2DTR #2 87RY U/L |  |  | B1/D08_A1 | [8 empty] | 斗南DS.#2DTR_87UL2 | #2DTR #2 87RY U/L | OTHER |  | CDC_Cmd_EMPTY |  |  |  | 494 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS |  |  | 2DTR | #2DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0634 |  | 0194 | 1-37-10 |  |  | #2DTR | U/L | #2DTR 51Z RY U/L |  |  | B1/D08_A1 | [8 empty] | 斗南DS.#2DTR_51ZUL | #2DTR 51ZRY U/L | OTHER |  | CDC_Cmd_EMPTY |  |  |  | 495 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS |  |  | 2DTR | #2DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0635 |  |  | 1-37-11 |  |  | #2DTR | RYFA | #2DTR. 數位電驛故障 |  |  | B1/D08_A1 | [8 empty] | 斗南DS.#2DTR_RYFA | #2DTR數位電驛故障 | OTHER | [5 empty] | 496 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D08 | 斗南DS |  |  | 3DTR | #3DTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0636 |  | 0195 | 1-37-12 |  |  | #3DTR | U/L | #3DTR #1 87RY U/L |  |  | B1/D08_A1 | [8 empty] | 斗南DS.#3DTR_87UL1 | #3DTR #1 87RY U/L | OTHER |  | CDC_Cmd_EMPTY |  |  |  | 497 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS |  |  | 3DTR | #3DTR |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0637 |  | 0196 | 1-37-13 |  |  | #3DTR | U/L | #3DTR #2 87RY U/L |  |  | B1/D08_A1 | [8 empty] | 斗南DS.#3DTR_87UL2 | #3DTR #2 87RY U/L | OTHER |  | CDC_Cmd_EMPTY |  |  |  | 498 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS |  |  | 3DTR | #3DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0638 |  | 0197 | 1-37-14 |  |  | #3DTR | U/L | #3DTR 51Z RY U/L |  |  | B1/D08_A1 | [8 empty] | 斗南DS.#3DTR_51ZUL | #3DTR 51ZRY U/L | OTHER |  | CDC_Cmd_EMPTY |  |  |  | 499 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS |  |  | 3DTR | #3DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0639 |  |  | 1-37-15 |  |  | #3DTR | RYFA | #3DTR. 數位電驛故障 |  |  | B1/D08_A1 | [8 empty] | 斗南DS.#3DTR_RYFA | #3DTR數位電驛故障 | OTHER | [5 empty] | 500 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0768 |  |  | 2-30-00 |  |  | Locate Empty | A/N | 23KV CBA |  |  | B3/D08_A1 | [8 empty] | 斗南DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | [5 empty] | 501 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0769 |  |  | 2-30-01 |  |  | Locate Empty | A/N | 23KV CBF |  |  | B3/D08_A1 | [8 empty] | 斗南DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | [5 empty] | 502 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | ComPoint |  |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0770 |  |  | 2-30-02 |  |  | Locate Empty | A/N | 23KV LOA |  |  | B3/D08_A1 | [8 empty] | 斗南DS.FEEDER_RCA | 饋線復閉電驛動作 | OTHER | [5 empty] | 503 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW61 | 南六一線(XW61) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0787 |  | 0144 | 2-31-03 |  | 2-10 | Locate Empty | ON/OFF | XW61 南六一線 F9 79S |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW61_79UL | 23KV南六一線(XW61) 79RY U/L | FEEDER | [5 empty] | 504 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS | 22 | 22kV | XW61 | 南六一線(XW61) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0788 |  | 0145 | 2-31-04 |  | 2-11 | Locate Empty | ON/OFF | XW61 南六一線 F9 51NS |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW61_LCO_TAP | 23KV南六一線(XW61) LCO TAP | FEEDER | [5 empty] | 505 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D08 | 斗南DS | 22 | 22kV | XW62 | 南六二線(XW62) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0789 |  | 0146 | 2-31-05 |  | 2-12 | Locate Empty | ON/OFF | XW62 南六二線 F10 79S |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW62_79UL | 23KV南六二線(XW62) 79RY U/L | FEEDER | [5 empty] | 506 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS | 22 | 22kV | XW62 | 南六二線(XW62) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0790 |  | 0147 | 2-31-06 |  | 2-13 | Locate Empty | ON/OFF | XW62 南六二線 F10 51NS |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW62_LCO_TAP | 23KV南六二線(XW62) LCO TAP | FEEDER | [5 empty] | 507 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D08 | 斗南DS | 22 | 22kV | XW63 | 南六三線(XW63) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0791 |  | 0148 | 2-31-07 |  | 2-14 | Locate Empty | ON/OFF | XW63 南六三線 F11 79S |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW63_79UL | 23KV南六三線(XW63) 79RY U/L | FEEDER | [5 empty] | 508 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS | 22 | 22kV | XW63 | 南六三線(XW63) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0792 |  | 0149 | 2-31-08 |  | 2-15 | Locate Empty | ON/OFF | XW63 南六三線 F11 51NS |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW63_LCO_TAP | 23KV南六三線(XW63) LCO TAP | FEEDER | [5 empty] | 509 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D08 | 斗南DS | 22 | 22kV | XW64 | 南六四線(XW64) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0793 |  | 0150 | 2-31-09 |  | 2-16 | Locate Empty | ON/OFF | XW64 南六四線 F12 79S |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW64_79UL | 23KV南六四線(XW64) 79RY U/L | FEEDER | [5 empty] | 510 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS | 22 | 22kV | XW64 | 南六四線(XW64) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0794 |  | 0151 | 2-31-10 |  | 2-17 | Locate Empty | ON/OFF | XW64 南六四線 F12 51NS |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW64_LCO_TAP | 23KV南六四線(XW64) LCO TAP | FEEDER | [5 empty] | 511 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D08 | 斗南DS | 22 | 22kV | XW65 | 南六五線(XW65) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0795 |  | 0152 | 2-31-11 |  | 2-18 | Locate Empty | ON/OFF | XW65 南六五線 F13 79S |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW65_79UL | 23KV南六五線(XW65) 79RY U/L | FEEDER | [5 empty] | 512 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS | 22 | 22kV | XW65 | 南六五線(XW65) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0796 |  | 0153 | 2-31-12 |  | 2-19 | Locate Empty | ON/OFF | XW65 南六五線 F13 51NS |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW65_LCO_TAP | 23KV南六五線(XW65) LCO TAP | FEEDER | [5 empty] | 513 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D08 | 斗南DS | 11 | 11kV | XW31 | 南十一線(XW31) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0797 |  | 0154 | 2-31-13 |  | 2-1A | Locate Empty | ON/OFF | XW31 南十一線 F14 79S |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW31_79UL | 11KV南十一線(XW31) 79RY U/L | FEEDER | [5 empty] | 514 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS | 11 | 11kV | XW31 | 南十一線(XW31) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0798 |  | 0155 | 2-31-14 |  | 2-1B | Locate Empty | ON/OFF | XW31 南十一線 F14 51NS |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW31_LCO_TAP | 11KV南十一線(XW31) LCO TAP | FEEDER | [5 empty] | 515 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D08 | 斗南DS | 11 | 11kV | XW32 | 南十二線(XW32) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0799 |  | 0156 | 2-31-15 |  | 2-1C | Locate Empty | ON/OFF | XW32 南十二線 F15 79S |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW32_79UL | 11KV南十二線(XW32) 79RY U/L | FEEDER | [5 empty] | 516 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS | 11 | 11kV | XW32 | 南十二線(XW32) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0800 |  | 0157 | 2-32-00 |  | 2-1D | Locate Empty | ON/OFF | XW32 南十二線 F15 51NS |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW32_LCO_TAP | 11KV南十二線(XW32) LCO TAP | FEEDER | [5 empty] | 517 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D08 | 斗南DS | 11 | 11kV | XW33 | 南十三線(XW33) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0801 |  | 0158 | 2-32-01 |  | 2-1E | Locate Empty | ON/OFF | XW33 南十三線 F16 79S |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW33_79UL | 11KV南十三線(XW33) 79RY U/L | FEEDER | [5 empty] | 518 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS | 11 | 11kV | XW33 | 南十三線(XW33) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0802 |  | 0159 | 2-32-02 |  | 2-1F | Locate Empty | ON/OFF | XW33 南十三線 F16 51NS |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW33_LCO_TAP | 11KV南十三線(XW33) LCO TAP | FEEDER | [5 empty] | 519 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D08 | 斗南DS | 11 | 11kV | XW34 | 南十四線(XW34) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0803 |  | 0160 | 2-32-03 |  | 2-20 | Locate Empty | ON/OFF | XW34 南十四線 F17 79S |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW34_79UL | 11KV南十四線(XW34) 79RY U/L | FEEDER | [5 empty] | 520 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS | 11 | 11kV | XW34 | 南十四線(XW34) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0804 |  | 0161 | 2-32-04 |  | 2-21 | Locate Empty | ON/OFF | XW34 南十四線 F17 51NS |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW34_LCO_TAP | 11KV南十四線(XW34) LCO TAP | FEEDER | [5 empty] | 521 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D08 | 斗南DS | 11 | 11kV | XW35 | 南十五線(XW35) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0805 |  | 0162 | 2-32-05 |  | 2-22 | Locate Empty | ON/OFF | XW35 南十五線 F18 79S |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW35_79UL | 11KV南十五線(XW35) 79RY U/L | FEEDER | [5 empty] | 522 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS | 11 | 11kV | XW35 | 南十五線(XW35) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0806 |  | 0163 | 2-32-06 |  | 2-23 | Locate Empty | ON/OFF | XW35 南十五線 F18 51NS |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW35_LCO_TAP | 11KV南十五線(XW35) LCO TAP | FEEDER | [5 empty] | 523 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D08 | 斗南DS | 22 | 22kV | XW71 | 南七十一線(XW71) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0807 |  | 0164 | 2-32-07 |  | 2-24 | Locate Empty | ON/OFF | XW71 南七十一線 F19 79S |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW71_79UL | 23KV南七一線(XW71) 79RY U/L | FEEDER | [5 empty] | 524 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS | 22 | 22kV | XW71 | 南七十一線(XW71) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0808 |  | 0165 | 2-32-08 |  | 2-25 | Locate Empty | ON/OFF | XW71 南七十一線 F19 51NS |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW71_LCO_TAP | 23KV南七一線(XW71) LCO TAP | FEEDER | [5 empty] | 525 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D08 | 斗南DS | 22 | 22kV | XW72 | 南七十二線(XW72) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0809 |  | 0166 | 2-32-09 |  | 2-26 | Locate Empty | ON/OFF | XW72 南七十二線 F20 79S |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW72_79UL | 23KV南七二線(XW72) 79RY U/L | FEEDER | [5 empty] | 526 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS | 22 | 22kV | XW72 | 南七十二線(XW72) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0810 |  | 0167 | 2-32-10 |  | 2-27 | Locate Empty | ON/OFF | XW72 南七十二線 F20 51NS |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW72_LCO_TAP | 23KV南七二線(XW72) LCO TAP | FEEDER | [5 empty] | 527 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D08 | 斗南DS | 22 | 22kV | XW73 | 南七十三線(XW73) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0811 |  | 0168 | 2-32-11 |  | 2-28 | Locate Empty | ON/OFF | XW73 南七十三線 F21 79S |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW73_79UL | 23KV南七三線(XW73) 79RY U/L | FEEDER | [5 empty] | 528 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS | 22 | 22kV | XW73 | 南七十三線(XW73) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0812 |  | 0169 | 2-32-12 |  | 2-29 | Locate Empty | ON/OFF | XW73 南七十三線 F21 51NS |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW73_LCO_TAP | 23KV南七三線(XW73) LCO TAP | FEEDER | [5 empty] | 529 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D08 | 斗南DS | 22 | 22kV | XW74 | 南七十四線(XW74) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0813 |  | 0170 | 2-32-13 |  | 2-2A | Locate Empty | ON/OFF | XW74 南七十四線 F22 79S |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW74_79UL | 23KV南七四線(XW74) 79RY U/L | FEEDER | [5 empty] | 530 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS | 22 | 22kV | XW74 | 南七十四線(XW74) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0814 |  | 0171 | 2-32-14 |  | 2-2B | Locate Empty | ON/OFF | XW74 南七十四線 F22 51NS |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW74_LCO_TAP | 23KV南七四線(XW74) LCO TAP | FEEDER | [5 empty] | 531 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D08 | 斗南DS | 22 | 22kV | XW75 | 南七十五線(XW75) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0815 |  | 0172 | 2-32-15 |  | 2-2C | Locate Empty | ON/OFF | XW75 南七十五線 F23 79S |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW75_79UL | 23KV南七五線(XW75) 79RY U/L | FEEDER | [5 empty] | 532 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS | 22 | 22kV | XW75 | 南七十五線(XW75) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0816 |  | 0173 | 2-33-00 |  | 2-2D | Locate Empty | ON/OFF | XW75 南七十五線 F23 51NS |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW75_LCO_TAP | 23KV南七五線(XW75) LCO TAP | FEEDER | [5 empty] | 533 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D08 | 斗南DS | 11 | 11kV | XW36 | 南十六線(XW36) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0817 |  | 0174 | 2-33-01 |  | 2-2E | Locate Empty | ON/OFF | XW36 南十六線 F24 79S |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW36_79UL | 11KV南十六線(XW36) 79RY U/L | FEEDER | [5 empty] | 534 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS | 11 | 11kV | XW36 | 南十六線(XW36) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0818 |  | 0175 | 2-33-02 |  | 2-2F | Locate Empty | ON/OFF | XW36 南十六線 F24 51NS |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW36_LCO_TAP | 11KV南十六線(XW36) LCO TAP | FEEDER | [5 empty] | 535 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D08 | 斗南DS | 11 | 11kV | XW37 | 南十七線(XW37) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0819 |  | 0176 | 2-33-03 |  | 2-30 | Locate Empty | ON/OFF | XW37 南十七線 F25 79S |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW37_79UL | 11KV南十七線(XW37) 79RY U/L | FEEDER | [5 empty] | 536 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS | 11 | 11kV | XW37 | 南十七線(XW37) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0820 |  | 0177 | 2-33-04 |  | 2-31 | Locate Empty | ON/OFF | XW37 南十七線 F25 51NS |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW37_LCO_TAP | 11KV南十七線(XW37) LCO TAP | FEEDER | [5 empty] | 537 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D08 | 斗南DS | 11 | 11kV | XW38 | 南十八線(XW38) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0821 |  | 0178 | 2-33-05 |  | 2-32 | Locate Empty | ON/OFF | XW38 南十八線 F26 79S |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW38_79UL | 11KV南十八線(XW38) 79RY U/L | FEEDER | [5 empty] | 538 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS | 11 | 11kV | XW38 | 南十八線(XW38) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0822 |  | 0179 | 2-33-06 |  | 2-33 | Locate Empty | ON/OFF | XW38 南十八線 F26 51NS |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW38_LCO_TAP | 11KV南十八線(XW38) LCO TAP | FEEDER | [5 empty] | 539 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D08 | 斗南DS | 11 | 11kV | XW40 | 南二十線(XW40) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0243 |  |  | 1-1E-03 |  |  | F28 | PHA | XW40 南二十線 RY PHA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW40_PHA | 11KV南二十線(XW40) 相間RY | FEEDER | [5 empty] | 398 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW40 | 南二十線(XW40) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0244 |  |  | 1-1E-04 |  |  | F28 | GDA | XW40 南二十線 RY GDA |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW40_GDA | 11KV南二十線(XW40) 接地RY | FEEDER | [5 empty] | 399 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW40 | 南二十線(XW40) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0825 |  | 0182 | 2-33-09 |  | 2-36 | Locate Empty | ON/OFF | XW40 南二十線 F28 79S |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW40_79UL | 11KV南二十線(XW40) 79RY U/L | FEEDER | [5 empty] | 542 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D08 | 斗南DS | 11 | 11kV | XW40 | 南二十線(XW40) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0826 |  | 0183 | 2-33-10 |  | 2-37 | Locate Empty | ON/OFF | XW40 南二十線 F28 51NS |  |  | B2/D08_D1 | [8 empty] | 斗南DS.XW40_LCO_TAP | 11KV南二十線(XW40) LCO TAP | FEEDER | [5 empty] | 543 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D08 | 斗南DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | DS1 | 1511 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0664 | 665 | 0100 | 1-39-08 | 1-39-09 | 1-64 | Locate Empty | ON/OFF | 虎菁一路(1511 DS) AS |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1511_DS | 1511(斗南虎菁一路) DS | LINE161 | [5 empty] | 544 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D08 | 斗南DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | DS2 | 1512 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0666 | 667 | 0101 | 1-39-10 | 1-39-11 | 1-65 | Locate Empty | ON/OFF | 虎菁一路(1512 DS) AS |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1512_DS | 1512(斗南虎菁一路) DS | LINE161 | [5 empty] | 545 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D08 | 斗南DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | DS3 | 1513 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0668 | 669 | 0102 | 1-39-12 | 1-39-13 | 1-66 | Locate Empty | ON/OFF | 虎菁一路(1513 DS) AS |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1513_DS | 1513(斗南虎菁一路) DS | LINE161 | [5 empty] | 546 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D08 | 斗南DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | ES3 | 1513E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0670 | 671 | 0103 | 1-39-14 | 1-39-15 | 1-67 | Locate Empty | ON/OFF | 虎菁一路(1513E ES) AS |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1513E_ES | 1513E(斗南虎菁一路) ES | LINE161 | [5 empty] | 547 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D08 | 斗南DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | DS1 | 1521 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0672 | 673 | 0104 | 1-3A-00 | 1-3A-01 | 1-68 | Locate Empty | ON/OFF | 虎菁二路(1521 DS) AS |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1521_DS | 1521(斗南虎菁二路) DS | LINE161 | [5 empty] | 548 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D08 | 斗南DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | DS2 | 1522 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0674 | 675 | 0105 | 1-3A-02 | 1-3A-03 | 1-69 | Locate Empty | ON/OFF | 虎菁二路(1522 DS) AS |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1522_DS | 1522(斗南虎菁二路) DS | LINE161 | [5 empty] | 549 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D08 | 斗南DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | DS3 | 1523 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0676 | 677 | 0106 | 1-3A-04 | 1-3A-05 | 1-6A | Locate Empty | ON/OFF | 虎菁二路(1523 DS) AS |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1523_DS | 1523(斗南虎菁二路) DS | LINE161 | [5 empty] | 550 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D08 | 斗南DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | ES3 | 1523E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0678 | 679 | 0107 | 1-3A-06 | 1-3A-07 | 1-6B | Locate Empty | ON/OFF | 虎菁二路(1523E ES) AS |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1523E_ES | 1523E(斗南虎菁二路) ES | LINE161 | [5 empty] | 551 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D08 | 斗南DS | 161 | 161kV | 1530 | 雲林～斗南線(1530) |  | DS1 | 1531 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0680 | 681 | 0108 | 1-3A-08 | 1-3A-09 | 1-6C | Locate Empty | ON/OFF | 雲林斗南線 (1531 DS) AS |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1531_DS | 1531(雲林斗南線) DS | LINE161 | [5 empty] | 552 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D08 | 斗南DS | 161 | 161kV | 1530 | 雲林～斗南線(1530) |  | DS2 | 1532 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0682 | 683 | 0109 | 1-3A-10 | 1-3A-11 | 1-6D | Locate Empty | ON/OFF | 雲林斗南線 (1532 DS) AS |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1532_DS | 1532(雲林斗南線) DS | LINE161 | [5 empty] | 553 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D08 | 斗南DS | 161 | 161kV | 1530 | 雲林～斗南線(1530) |  | DS3 | 1533 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0684 | 685 | 0110 | 1-3A-12 | 1-3A-13 | 1-6E | Locate Empty | ON/OFF | 雲林斗南線 (1533 DS) AS |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1533_DS | 1533(雲林斗南線) DS | LINE161 | [5 empty] | 554 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D08 | 斗南DS | 161 | 161kV | 1530 | 雲林～斗南線(1530) |  | ES3 | 1533E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0686 | 687 | 0111 | 1-3A-14 | 1-3A-15 | 1-6F | Locate Empty | ON/OFF | 雲林斗南線 (1533E DS) AS |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1533E_ES | 1533E(雲林斗南線) ES | LINE161 | [5 empty] | 555 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D08 | 斗南DS | 161 | 161kV | 1540 | 斗南～北勢線(1540) |  | DS1 | 1541 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0688 | 689 | 0112 | 1-3B-00 | 1-3B-01 | 1-70 | Locate Empty | ON/OFF | 斗南北勢線 (1541 DS) AS |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1541_DS | 1541(斗南北勢線) DS | LINE161 | [5 empty] | 556 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D08 | 斗南DS | 161 | 161kV | 1540 | 斗南～北勢線(1540) |  | DS2 | 1542 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0690 | 691 | 0113 | 1-3B-02 | 1-3B-03 | 1-71 | Locate Empty | ON/OFF | 斗南北勢線 (1542 DS) AS |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1542_DS | 1542(斗南北勢線) DS | LINE161 | [5 empty] | 557 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D08 | 斗南DS | 161 | 161kV | 1540 | 斗南～北勢線(1540) |  | DS3 | 1543 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0692 | 693 | 0114 | 1-3B-04 | 1-3B-05 | 1-72 | Locate Empty | ON/OFF | 斗南北勢線 (1543 DS) AS |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1543_DS | 1543(斗南北勢線) DS | LINE161 | [5 empty] | 558 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D08 | 斗南DS | 161 | 161kV | 1540 | 斗南～北勢線(1540) |  | ES3 | 1543E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0694 | 695 | 0115 | 1-3B-06 | 1-3B-07 | 1-73 | Locate Empty | ON/OFF | 斗南北勢線 (1543E DS) AS |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1543E_ES | 1543E(斗南北勢線) ES | LINE161 | [5 empty] | 559 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D08 | 斗南DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0704 | 705 | 0120 | 1-3C-00 | 1-3C-01 | 1-78 | Locate Empty | ON/OFF | TIE (1501 DS) AS |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1501_DS | 1501(TIE) DS | TIE | [5 empty] | 560 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D08 | 斗南DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0706 | 707 | 0121 | 1-3C-02 | 1-3C-03 | 1-79 | Locate Empty | ON/OFF | TIE (1502 DS) AS |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1502_DS | 1502(TIE) DS | TIE | [5 empty] | 561 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D08 | 斗南DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0708 | 709 | 0122 | 1-3C-04 | 1-3C-05 | 1-7A | Locate Empty | ON/OFF | NO.1 TR(1751 DS) AS |  |  | B2/D08_A1 | [16 empty] | 562 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D08 | 斗南DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0710 | 711 | 0123 | 1-3C-06 | 1-3C-07 | 1-7B | Locate Empty | ON/OFF | NO.1 TR(1752 DS) AS |  |  | B2/D08_A1 | [16 empty] | 563 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D08 | 斗南DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0712 | 713 | 0124 | 1-3C-08 | 1-3C-09 | 1-7C | Locate Empty | ON/OFF | NO.2 TR(1761 DS) AS |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1761_DS | 1761(#2DTR) DS | MTR | [5 empty] | 564 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D08 | 斗南DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0714 | 715 | 0125 | 1-3C-10 | 1-3C-11 | 1-7D | Locate Empty | ON/OFF | NO.2 TR(1762 DS) AS |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1762_DS | 1762(#2DTR) DS | MTR | [5 empty] | 565 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D08 | 斗南DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0716 | 717 | 0126 | 1-3C-12 | 1-3C-13 | 1-7E | Locate Empty | ON/OFF | NO.3 TR(1771 DS) AS |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1771_DS | 1771(#3DTR) DS | MTR | [5 empty] | 566 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D08 | 斗南DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0718 | 719 | 0127 | 1-3C-14 | 1-3C-15 | 1-7F | Locate Empty | ON/OFF | NO.3 TR(1772 DS) AS |  |  | B2/D08_A1 | [8 empty] | 斗南DS.1772_DS | 1772(#3DTR) DS | MTR | [5 empty] | 567 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D08 | 斗南DS | 11 | 11kV | LBS240 | #4SC(240) |  | LBS |  |  | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/240 | C/4SC(B) |  |  | 0866 | 867 |  | 2-36-02 | 2-36-03 |  | Locate Empty | ON/OFF | #4SC-2B LBS AS |  |  | B3/D08_A1 | [8 empty] | 斗南DS.240_LBS | 240(11KV #4SC) LBS | SC | [5 empty] | 568 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D08 | 斗南DS | 11 | 11kV | LBS260 | #6SC(260) |  | LBS |  |  | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/260 | C/6SC(B) |  |  | 0870 | 871 |  | 2-36-06 | 2-36-07 |  | Locate Empty | ON/OFF | #6SC-3B LBS AS |  |  | B3/D08_A1 | [8 empty] | 斗南DS.260_LBS | 260(11KV #6SC) LBS | SC | [5 empty] | 569 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D08 | 斗南DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | 1760TE(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_A1 | [8 empty] | 斗南DS.1750TE | 1750TE (非取樣點) | MTR | [5 empty] | 12 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D08 | 斗南DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | 1760BE(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D08_A1 | [8 empty] | 斗南DS.1750BE | 1750BE (非取樣點) | MTR | [5 empty] | 13 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
D08 | 斗南DS | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/D08_A1 | [12 empty] | 斗南DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: D08/161/1BUS/V; OPRD2: D08/161/2BUS/V
D08 | 斗南DS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/D08_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: D08/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
D08 | 斗南DS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/D08_A1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_4 | OPRD1: D08/161/1510/MW; OPRD2: D08/161/1520/MW; OPRD3: D08/161/1530/MW; OPRD4: D08/161/1540/MW
D08 | 斗南DS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/D08_A1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: D08/0/CalcPoint/OPRN2_MW
D08 | 斗南DS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/D08_A1 | [17 empty] | none
D08 | 斗南DS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/D08_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: D08/0/CalcPoint/OPRN1; OPRD2: D08/0/CalcPoint/OPRN2; OPRD3: D08/0/CalcPoint/PRFL_UL
D08 | 斗南DS |  |  | 2DTR | 2DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D08_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D08/22/330/I_R; OPRD2: D08/11/340/I_R
D08 | 斗南DS |  |  | 2DTR | 2DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D08_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D08/22/330/I_S; OPRD2: D08/11/340/I_S
D08 | 斗南DS |  |  | 2DTR | 2DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D08_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D08/22/330/I_T; OPRD2: D08/11/340/I_T
D08 | 斗南DS |  |  | 3DTR | 3DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D08_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D08/22/350/I_R; OPRD2: D08/11/360/I_R
D08 | 斗南DS |  |  | 3DTR | 3DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D08_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D08/22/350/I_S; OPRD2: D08/11/360/I_S
D08 | 斗南DS |  |  | 3DTR | 3DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D08_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D08/22/350/I_T; OPRD2: D08/11/360/I_T
D08 | 斗南DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D08_A1 | [12 empty] | 斗南DS.1510_AMP | 斗南虎菁一路 AMP | LINE161 | AMP_CAL | C20R2000 | amp_cal | OPRD1: D08/161/1510/MW; OPRD2: D08/161/1510/MVAR; OPRD3: D08/0/CalcPoint/Vbs4
D08 | 斗南DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D08_A1 | [12 empty] | 斗南DS.1520_AMP | 斗南虎菁二路 AMP | LINE161 | AMP_CAL | C20R2000 | amp_cal | OPRD1: D08/161/1520/MW; OPRD2: D08/161/1520/MVAR; OPRD3: D08/0/CalcPoint/Vbs4
D08 | 斗南DS | 161 | 161kV | 1530 | 雲林～斗南線(1530) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D08_A1 | [12 empty] | 斗南DS.1530_AMP | 雲林斗南線 AMP | LINE161 | AMP_CAL | C20R2000 | amp_cal | OPRD1: D08/161/1530/MW; OPRD2: D08/161/1530/MVAR; OPRD3: D08/0/CalcPoint/Vbs4
D08 | 斗南DS | 161 | 161kV | 1540 | 斗南～北勢線(1540) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D08_A1 | [12 empty] | 斗南DS.1540_AMP | 斗南北勢線 AMP | LINE161 | AMP_CAL | C20R2000 | amp_cal | OPRD1: D08/161/1540/MW; OPRD2: D08/161/1540/MVAR; OPRD3: D08/0/CalcPoint/Vbs4
D08 | 斗南DS | 11 | 11kV | 2BBUS | #2BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D08_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D08/11/2BBUS/V
D08 | 斗南DS | 11 | 11kV | 3BBUS | #3BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D08_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D08/11/3BBUS/V
D08 | 斗南DS | 22 | 22kV | 2ABUS | #2ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D08_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D08/22/2ABUS/V
D08 | 斗南DS | 22 | 22kV | 3ABUS | #3ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D08_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D08/22/3ABUS/V
D08 | 斗南DS |  |  | 2DTR(A) | #2DTR(A) |  | TR_PERM | [9 empty] | B1/D08_A1 | [12 empty] | 斗南DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D08//2DTR(A)/SupLocal; OPRD2: D08//2DTR(A)/Tap Chan
D08 | 斗南DS |  |  | 2DTR(B) | #2DTR(B) |  | TR_PERM | [9 empty] | B1/D08_A1 | [12 empty] | 斗南DS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D08//2DTR(B)/SupLocal; OPRD2: D08//2DTR(B)/Tap Chan
D08 | 斗南DS |  |  | 3DTR(A) | #3DTR(A) |  | TR_PERM | [9 empty] | B1/D08_A1 | [12 empty] | 斗南DS.#3DTR(A)_PERM | #3DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D08//3DTR(A)/SupLocal; OPRD2: D08//3DTR(A)/Tap Chan
D08 | 斗南DS |  |  | 3DTR(B) | #3DTR(B) |  | TR_PERM | [9 empty] | B1/D08_A1 | [12 empty] | 斗南DS.#3DTR(B)_PERM | #3DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D08//3DTR(B)/SupLocal; OPRD2: D08//3DTR(B)/Tap Chan
D08 | 斗南DS | 11 | 11kV | XW31 | 南十一線(XW31) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D08/11/2BBUS/V; OPRD2: D08/11/XW31/I_R; OPRD3: D08/11/XW31/I_S; OPRD4: D08/11/XW31/I_T
D08 | 斗南DS | 11 | 11kV | XW32 | 南十二線(XW32) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D08/11/2BBUS/V; OPRD2: D08/11/XW32/I_R; OPRD3: D08/11/XW32/I_S; OPRD4: D08/11/XW32/I_T
D08 | 斗南DS | 11 | 11kV | XW33 | 南十三線(XW33) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D08/11/2BBUS/V; OPRD2: D08/11/XW33/I_R; OPRD3: D08/11/XW33/I_S; OPRD4: D08/11/XW33/I_T
D08 | 斗南DS | 11 | 11kV | XW34 | 南十四線(XW34) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D08/11/2BBUS/V; OPRD2: D08/11/XW34/I_R; OPRD3: D08/11/XW34/I_S; OPRD4: D08/11/XW34/I_T
D08 | 斗南DS | 11 | 11kV | XW35 | 南十五線(XW35) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D08/11/2BBUS/V; OPRD2: D08/11/XW35/I_R; OPRD3: D08/11/XW35/I_S; OPRD4: D08/11/XW35/I_T
D08 | 斗南DS | 11 | 11kV | XW36 | 南十六線(XW36) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D08/11/3BBUS/V; OPRD2: D08/11/XW36/I_R; OPRD3: D08/11/XW36/I_S; OPRD4: D08/11/XW36/I_T
D08 | 斗南DS | 11 | 11kV | XW37 | 南十七線(XW37) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D08/11/3BBUS/V; OPRD2: D08/11/XW37/I_R; OPRD3: D08/11/XW37/I_S; OPRD4: D08/11/XW37/I_T
D08 | 斗南DS | 11 | 11kV | XW38 | 南十八線(XW38) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D08/11/3BBUS/V; OPRD2: D08/11/XW38/I_R; OPRD3: D08/11/XW38/I_S; OPRD4: D08/11/XW38/I_T
D08 | 斗南DS | 11 | 11kV | XW39 | 南十九線(XW39) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D08/11/3BBUS/V; OPRD2: D08/11/XW39/I_R; OPRD3: D08/11/XW39/I_S; OPRD4: D08/11/XW39/I_T
D08 | 斗南DS | 11 | 11kV | XW41 | 南二十線(XW41) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D08/11/3BBUS/V; OPRD2: D08/11/XW41/I_R; OPRD3: D08/11/XW41/I_S; OPRD4: D08/11/XW41/I_T
D08 | 斗南DS | 22 | 22kV | XW61 | 南六一線(XW61) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D08/22/2ABUS/V; OPRD2: D08/22/XW61/I_R; OPRD3: D08/22/XW61/I_S; OPRD4: D08/22/XW61/I_T
D08 | 斗南DS | 22 | 22kV | XW62 | 南六二線(XW62) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D08/22/2ABUS/V; OPRD2: D08/22/XW62/I_R; OPRD3: D08/22/XW62/I_S; OPRD4: D08/22/XW62/I_T
D08 | 斗南DS | 22 | 22kV | XW63 | 南六三線(XW63) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D08/22/2ABUS/V; OPRD2: D08/22/XW63/I_R; OPRD3: D08/22/XW63/I_S; OPRD4: D08/22/XW63/I_T
D08 | 斗南DS | 22 | 22kV | XW64 | 南六四線(XW64) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D08/22/2ABUS/V; OPRD2: D08/22/XW64/I_R; OPRD3: D08/22/XW64/I_S; OPRD4: D08/22/XW64/I_T
D08 | 斗南DS | 22 | 22kV | XW65 | 南六五線(XW65) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D08/22/2ABUS/V; OPRD2: D08/22/XW65/I_R; OPRD3: D08/22/XW65/I_S; OPRD4: D08/22/XW65/I_T
D08 | 斗南DS | 22 | 22kV | XW71 | 南七十一線(XW71) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D08/22/3ABUS/V; OPRD2: D08/22/XW71/I_R; OPRD3: D08/22/XW71/I_S; OPRD4: D08/22/XW71/I_T
D08 | 斗南DS | 22 | 22kV | XW72 | 南七十二線(XW72) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D08/22/3ABUS/V; OPRD2: D08/22/XW72/I_R; OPRD3: D08/22/XW72/I_S; OPRD4: D08/22/XW72/I_T
D08 | 斗南DS | 22 | 22kV | XW73 | 南七十三線(XW73) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D08/22/3ABUS/V; OPRD2: D08/22/XW73/I_R; OPRD3: D08/22/XW73/I_S; OPRD4: D08/22/XW73/I_T
D08 | 斗南DS | 22 | 22kV | XW74 | 南七十四線(XW74) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D08/22/3ABUS/V; OPRD2: D08/22/XW74/I_R; OPRD3: D08/22/XW74/I_S; OPRD4: D08/22/XW74/I_T
D08 | 斗南DS | 22 | 22kV | XW75 | 南七十五線(XW75) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D08/22/3ABUS/V; OPRD2: D08/22/XW75/I_R; OPRD3: D08/22/XW75/I_S; OPRD4: D08/22/XW75/I_T
D08 | 斗南DS | 11 | 11kV | XW31 | 南十一線(XW31) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D08/11/XW31/kVA; OPRD2: D08/11/XW31/KVAR
D08 | 斗南DS | 11 | 11kV | XW32 | 南十二線(XW32) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D08/11/XW32/kVA; OPRD2: D08/11/XW32/KVAR
D08 | 斗南DS | 11 | 11kV | XW33 | 南十三線(XW33) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D08/11/XW33/kVA; OPRD2: D08/11/XW33/KVAR
D08 | 斗南DS | 11 | 11kV | XW34 | 南十四線(XW34) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D08/11/XW34/kVA; OPRD2: D08/11/XW34/KVAR
D08 | 斗南DS | 11 | 11kV | XW35 | 南十五線(XW35) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D08/11/XW35/kVA; OPRD2: D08/11/XW35/KVAR
D08 | 斗南DS | 11 | 11kV | XW36 | 南十六線(XW36) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D08/11/XW36/kVA; OPRD2: D08/11/XW36/KVAR
D08 | 斗南DS | 11 | 11kV | XW37 | 南十七線(XW37) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D08/11/XW37/kVA; OPRD2: D08/11/XW37/KVAR
D08 | 斗南DS | 11 | 11kV | XW38 | 南十八線(XW38) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D08/11/XW38/kVA; OPRD2: D08/11/XW38/KVAR
D08 | 斗南DS | 11 | 11kV | XW39 | 南十九線(XW39) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D08/11/XW39/kVA; OPRD2: D08/11/XW39/KVAR
D08 | 斗南DS | 11 | 11kV | XW41 | 南二十線(XW41) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D08/11/XW41/kVA; OPRD2: D08/11/XW41/KVAR
D08 | 斗南DS | 22 | 22kV | XW61 | 南六一線(XW61) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D08/22/XW61/kVA; OPRD2: D08/22/XW61/KVAR
D08 | 斗南DS | 22 | 22kV | XW62 | 南六二線(XW62) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D08/22/XW62/kVA; OPRD2: D08/22/XW62/KVAR
D08 | 斗南DS | 22 | 22kV | XW63 | 南六三線(XW63) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D08/22/XW63/kVA; OPRD2: D08/22/XW63/KVAR
D08 | 斗南DS | 22 | 22kV | XW64 | 南六四線(XW64) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D08/22/XW64/kVA; OPRD2: D08/22/XW64/KVAR
D08 | 斗南DS | 22 | 22kV | XW65 | 南六五線(XW65) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D08/22/XW65/kVA; OPRD2: D08/22/XW65/KVAR
D08 | 斗南DS | 22 | 22kV | XW71 | 南七十一線(XW71) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D08/22/XW71/kVA; OPRD2: D08/22/XW71/KVAR
D08 | 斗南DS | 22 | 22kV | XW72 | 南七十二線(XW72) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D08/22/XW72/kVA; OPRD2: D08/22/XW72/KVAR
D08 | 斗南DS | 22 | 22kV | XW73 | 南七十三線(XW73) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D08/22/XW73/kVA; OPRD2: D08/22/XW73/KVAR
D08 | 斗南DS | 22 | 22kV | XW74 | 南七十四線(XW74) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D08/22/XW74/kVA; OPRD2: D08/22/XW74/KVAR
D08 | 斗南DS | 22 | 22kV | XW75 | 南七十五線(XW75) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D08_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D08/22/XW75/kVA; OPRD2: D08/22/XW75/KVAR
D08 | 斗南DS | 11 | 11kV | 240 | #4SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D08_A1 | [12 empty] | 斗南DS.240_SC_MVAR | 11KV#4SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D08/11/240/CB; OPRD2: 6.9; OPRD3: 0
D08 | 斗南DS | 11 | 11kV | 260 | #6SC(260) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D08_A1 | [12 empty] | 斗南DS.260_SC_MVAR | 11KV#6SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D08/11/260/CB; OPRD2: 6.9; OPRD3: 0
D08 | 斗南DS | 22 | 22kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D08_A1 | [12 empty] | 斗南DS.230_SC_MVAR | 23KV#3SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D08/22/230/CB; OPRD2: 13.8; OPRD3: 0
D08 | 斗南DS | 22 | 22kV | 250 | #5SC(250) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D08_A1 | [12 empty] | 斗南DS.250_SC_MVAR | 23KV#5SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D08/22/250/CB; OPRD2: 13.8; OPRD3: 0
D08 | 斗南DS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/D08_A1 | [12 empty] | 斗南DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_10 |  | com_alarm_35 | D08//1DTR/96PA | D08//1DTR/51ZA | D08//1DTR/87A | D08//2DTR/96D | D08//2DTR/63Q | D08//2DTR/51ZA | D08//2DTR/96B1 | D08//2DTR/TRA | D08//2DTR/96B2 | D08//2DTR/87A | D08//2DTR/96PA | D08//3DTR/63Q | D08//3DTR/GDA | D08//3DTR/PHA | D08//3DTR/96D | D08//3DTR/TRA | D08//3DTR/96B1 | D08//3DTR/96B2 | D08//3DTR/51ZA | D08//3DTR/87A | D08//3DTR/96PA | D08/11/340/GDA | D08/11/340/PHA | D08/11/360/GDA | D08/11/360/PHA | D08/161/1750/GDA | D08/161/1750/PHA | D08/161/1760/GDA | D08/161/1760/PHA | D08/161/1BUS/87A | D08/161/2BUS/87A | D08/22/330/GDA | D08/22/330/PHA | D08/22/350/GDA | D08/22/350/PHA
D08 | 斗南DS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/D08_A1 | [12 empty] | 斗南DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | STATION_FAULT_2 |  | com_alarm_2 | OPRD1: D08//2DTR/TRF; OPRD2: D08//3DTR/TRF
D08 | 斗南DS | 161 | 161kV | 1750_D1 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D08_D1 | [17 empty] | lamp2CC | OPRD1: D08/161/1750/CB
D08 | 斗南DS | 161 | 161kV | 1760_D1 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D08_D1 | [17 empty] | lamp2CC | OPRD1: D08/161/1760/CB
D08 | 斗南DS | 22 | 22kV | 330_D1 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D08_D1 | [17 empty] | lamp2CC | OPRD1: D08/22/330/CB
D08 | 斗南DS | 11 | 11kV | 340_D1 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D08_D1 | [17 empty] | lamp2CC | OPRD1: D08/11/340/CB
D08 | 斗南DS | 161 | 161kV | 1770_D1 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D08_D1 | [17 empty] | lamp2CC | OPRD1: D08/161/1770/CB
D08 | 斗南DS | 22 | 22kV | 350_D1 | #3DTR(A)(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D08_D1 | [17 empty] | lamp2CC | OPRD1: D08/22/350/CB
D08 | 斗南DS | 11 | 11kV | 360_D1 | #3DTR(B)(360) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D08_D1 | [17 empty] | lamp2CC | OPRD1: D08/11/360/CB
D08 | 斗南DS | 0 |  | RTU_D1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/D08_D1 | [17 empty] | lamp2CC | OPRD1: D08/0/RTU/RTU_R_L
D08 | 斗南DS | 0 |  | StaDev_D1 | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/D08_D1 | [17 empty] | lamp2CC | OPRD1: D08/0/StaDev/STUV
D08 | 斗南DS | 0 |  | StaDev_D1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D08_D1 | [17 empty] | lamp2CC | OPRD1: D08/0/StaDev/DCA
D08 | 斗南DS | 0 |  | StaDev_D1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D08_D1 | [17 empty] | lamp2CC | OPRD1: D08/0/StaDev/DCE

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D08 | 斗南DS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 斗南DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | D08/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
D08 | 斗南DS | 161 | 161kV | 1530 | 雲林斗南線(1530) |  | I | [25 empty] | ADCS_N | [8 empty] | 斗南DS.1530_AMP | 雲林斗南線 AMP | LINE161 | D08/161/1530/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000
D08 | 斗南DS | 161 | 161kV | 1540 | 斗南北勢線(1540) |  | I | [25 empty] | ADCS_N | [8 empty] | 斗南DS.1540_AMP | 斗南北勢線 AMP | LINE161 | D08/161/1540/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南二十線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南二十線KVA | 11KV南二十線KVA | FEEDER |  |  | KVA_CAL |  |  | 5 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南二十線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南二十線KW | 11KV南二十線KW | FEEDER |  |  | KW_CAL |  |  | 6 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南十一線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南十一線KVA | 11KV南十一線KVA | FEEDER |  |  | KVA_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南十一線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南十一線KW | 11KV南十一線KW | FEEDER |  |  | KW_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南十七線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南十七線KVA | 11KV南十七線KVA | FEEDER |  |  | KVA_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南十七線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南十七線KW | 11KV南十七線KW | FEEDER |  |  | KW_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南十九線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南十九線KVA | 11KV南十九線KVA | FEEDER |  |  | KVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南十九線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南十九線KW | 11KV南十九線KW | FEEDER |  |  | KW_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南十二線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南十二線KVA | 11KV南十二線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南十二線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南十二線KW | 11KV南十二線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南十八線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南十八線KVA | 11KV南十八線KVA | FEEDER |  |  | KVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南十八線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南十八線KW | 11KV南十八線KW | FEEDER |  |  | KW_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南十三線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南十三線KVA | 11KV南十三線KVA | FEEDER |  |  | KVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南十三線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南十三線KW | 11KV南十三線KW | FEEDER |  |  | KW_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南十五線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南十五線KVA | 11KV南十五線KVA | FEEDER |  |  | KVA_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南十五線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南十五線KW | 11KV南十五線KW | FEEDER |  |  | KW_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南十六線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南十六線KVA | 11KV南十六線KVA | FEEDER |  |  | KVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南十六線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南十六線KW | 11KV南十六線KW | FEEDER |  |  | KW_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南十四線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南十四線KVA | 11KV南十四線KVA | FEEDER |  |  | KVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南十四線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南十四線KW | 11KV南十四線KW | FEEDER |  |  | KW_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南七一線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南七一線KVA | 23KV南七一線KVA | FEEDER |  |  | KVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南七一線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南七一線KW | 23KV南七一線KW | FEEDER |  |  | KW_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南七二線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南七二線KVA | 23KV南七二線KVA | FEEDER |  |  | KVA_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南七二線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南七二線KW | 23KV南七二線KW | FEEDER |  |  | KW_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南七三線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南七三線KVA | 23KV南七三線KVA | FEEDER |  |  | KVA_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南七三線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南七三線KW | 23KV南七三線KW | FEEDER |  |  | KW_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南七五線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南七五線KVA | 23KV南七五線KVA | FEEDER |  |  | KVA_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南七五線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南七五線KW | 23KV南七五線KW | FEEDER |  |  | KW_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南七四線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南七四線KVA | 23KV南七四線KVA | FEEDER |  |  | KVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南七四線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南七四線KW | 23KV南七四線KW | FEEDER |  |  | KW_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南六一線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南六一線KVA | 23KV南六一線KVA | FEEDER |  |  | KVA_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南六一線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南六一線KW | 23KV南六一線KW | FEEDER |  |  | KW_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南六二線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南六二線KVA | 23KV南六二線KVA | FEEDER |  |  | KVA_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南六二線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南六二線KW | 23KV南六二線KW | FEEDER |  |  | KW_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南六三線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南六三線KVA | 23KV南六三線KVA | FEEDER |  |  | KVA_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南六三線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南六三線KW | 23KV南六三線KW | FEEDER |  |  | KW_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南六五線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南六五線KVA | 23KV南六五線KVA | FEEDER |  |  | KVA_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南六五線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南六五線KW | 23KV南六五線KW | FEEDER |  |  | KW_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南六四線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南六四線KVA | 23KV南六四線KVA | FEEDER |  |  | KVA_CAL |  |  | 43 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  |  |  |  | 南六四線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.南六四線KW | 23KV南六四線KW | FEEDER |  |  | KW_CAL |  |  | 44 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 11 | 11kV | 240_SC | #4SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 斗南DS.240_SC_MVAR | 11KV#4SC MVAR | SC | D08/11/240/MVAR |  | SC_LBS_11 |  |  | 45 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 11 | 11kV | 260_SC | #6SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 斗南DS.260_SC_MVAR | 11KV#6SC MVAR | SC | D08/11/260/MVAR |  | SC_LBS_11 |  |  | 46 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 22 | 22kV | 230_SC | #3SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 斗南DS.230_SC_MVAR | 23KV#3SC MVAR | SC | D08/22/230/MVAR |  | SC_CAL_23 |  |  | 47 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 22 | 22kV | 250_SC | #5SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 斗南DS.250_SC_MVAR | 23KV#5SC MVAR | SC | D08/22/250/MVAR |  | SC_CAL_23 |  |  | 48 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  | TRTOT | 斗南主變瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 斗南DS.TRTOT_MW | 斗南主變瞬時供電量 MW |  |  |  | MTR_PQ_CAL |  |  | 49 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  | TRTOT | 斗南主變瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 斗南DS.TRTOT_MVAR | 斗南主變瞬時供電量 MVAR |  |  |  | MTR_PQ_CAL |  |  | 50 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 斗南DS.#2DTR(A)_MVA | #2DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 51 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D08 | 斗南DS | 0 |  | 2DTR(A) | #2DTR(A) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 斗南DS.#2DTR(A)_LOAD | #2DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 52 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D08 | 斗南DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PF | [25 empty] | ADCS_N | [8 empty] | 斗南DS.#2DTR(A)_PF | #2DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 53 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D08 | 斗南DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 斗南DS.#2DTR(B)_MVA | #2DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 54 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D08 | 斗南DS | 0 |  | 2DTR(B) | #2DTR(B) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 斗南DS.#2DTR(B)_LOAD | #2DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 55 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D08 | 斗南DS | 0 |  | 2DTR(B) | #2DTR(B) |  | PF | [25 empty] | ADCS_N | [8 empty] | 斗南DS.#2DTR(B)_PF | #2DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 56 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D08 | 斗南DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 斗南DS.#3DTR(A)_MVA | #3DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 57 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D08 | 斗南DS | 0 |  | 3DTR(A) | #3DTR(A) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 斗南DS.#3DTR(A)_LOAD | #3DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 58 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D08 | 斗南DS | 0 |  | 3DTR(A) | #3DTR(A) |  | PF | [25 empty] | ADCS_N | [8 empty] | 斗南DS.#3DTR(A)_PF | #3DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 59 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D08 | 斗南DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 斗南DS.#3DTR(B)_MVA | #3DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 60 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D08 | 斗南DS | 0 |  | 3DTR(B) | #3DTR(B) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 斗南DS.#3DTR(B)_LOAD | #3DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 61 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D08 | 斗南DS | 0 |  | 3DTR(B) | #3DTR(B) |  | PF | [25 empty] | ADCS_N | [8 empty] | 斗南DS.#3DTR(B)_PF | #3DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 62 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D08 | 斗南DS | 0 |  | 2DTR | #2DTR |  | MW | [25 empty] | ADCS_N | [8 empty] | 斗南DS.#2DTR_MW | #2DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 63 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  | 2DTR | #2DTR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 斗南DS.#2DTR_MVAR | #2DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 64 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  | 2DTR | #2DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 斗南DS.#2DTR_MVA | #2DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 65 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D08 | 斗南DS | 0 |  | 2DTR | #2DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 斗南DS.#2DTR_LOAD | #2DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 66 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D08 | 斗南DS | 0 |  | 3DTR | #3DTR |  | MW | [25 empty] | ADCS_N | [8 empty] | 斗南DS.#3DTR_MW | #3DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 67 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  | 3DTR | #3DTR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 斗南DS.#3DTR_MVAR | #3DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 68 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  | 3DTR | #3DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 斗南DS.#3DTR_MVA | #3DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 69 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D08 | 斗南DS | 0 |  | 3DTR | #3DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 斗南DS.#3DTR_LOAD | #3DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 70 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D08 | 斗南DS | 161 | 161kV | 1510 | 斗南虎菁一路(1510) |  | I | [25 empty] | ADCS_N | [8 empty] | 斗南DS.1510_AMP | 斗南虎菁一路 AMP | LINE161 | D08/161/1510/I |  | AMP_CAL |  |  | 71 | CalcAIPoint | [21 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000
D08 | 斗南DS | 161 | 161kV | 1520 | 斗南虎菁二路(1520) |  | I | [25 empty] | ADCS_N | [8 empty] | 斗南DS.1520_AMP | 斗南虎菁二路 AMP | LINE161 | D08/161/1520/I |  | AMP_CAL |  |  | 72 | CalcAIPoint | [21 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000
D08 | 斗南DS | 0 |  | 300_CB | 300(300_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.300_CB_1 | 300 CB (D1) | TIE |  |  | AD_LAMP_DD_1 |  |  | 73 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | 400_CB | 400(400_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.400_CB_1 | 400 CB (D1) | TIE |  |  | AD_LAMP_DD_1 |  |  | 74 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | 1760_CB | #2DTR(1760_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.1760_CB_1 | 1760(#2DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 75 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | 330_CB | #2DTR(330_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.330_CB_1 | 330(#2DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 76 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | 340_CB | #2DTR(340_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.340_CB_1 | 340(#2DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 77 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | 1770_CB | #3DTR(1770_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.1770_CB_1 | 1770(#3DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 78 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | 350_CB | #3DTR(350_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.350_CB_1 | 350(#3DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 79 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | 360_CB | #3DTR(360_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.360_CB_1 | 360(#3DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 80 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | 240_CB | #4SC(240_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.240_CB_1 | 240(11KV #4SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 81 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | 260_CB | #6SC(260_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.260_CB_1 | 260(11KV #6SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 82 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | 230_CB | #3SC(230_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.230_CB_1 | 230(23KV #3SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 83 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | 250_CB | #5SC(250_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.250_CB_1 | 250(23KV #5SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 84 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | 11__CBA | 11/斷路器重故障(11__CBA) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.11/23KV_CBA_1 | 11/23KV斷路器重故障 (D1) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 85 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | 11__CBF | 11/斷路器輕故障(11__CBF) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.11/23KV_CBF_1 | 11/23KV斷路器輕故障 (D1) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 86 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | RTU_S_L | RTU |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.RTU_S/L_1 | RTU SUPY/LOCAL (D1) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 87 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D08 | 斗南DS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_N | [8 empty] | 斗南DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | D08/0/CalcPoint/SUBA |  | STATION_FAULT_10 |  |  | 88 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 變電所輕故障點燈 | 變電所輕故障點燈 |  | SUBF | [25 empty] | ADCS_N | [8 empty] | 斗南DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | D08/0/CalcPoint/SUBF |  | STATION_FAULT_2 |  |  | 89 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.變電所重故障_1 | 變電所重故障點燈 (D1) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 90 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.變電所輕故障_1 | 變電所輕故障點燈 (D1) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 91 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1530_AMP | 雲林斗南線 | [27 empty] | ADCS_N | [8 empty] | 斗南DS.1530_AMP_A | 雲林斗南線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 92 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D08 | 斗南DS | 161 | 161kV | 1540_AMP | 斗南北勢線 | [27 empty] | ADCS_N | [8 empty] | 斗南DS.1540_AMP_A | 斗南北勢線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 93 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D08 | 斗南DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PERM | [25 empty] | ADCS_N | [8 empty] | 斗南DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | D08//2DTR(A)/TR_PERM |  | DTR_PERM |  |  | 94 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D08 | 斗南DS | 0 |  | 2DTR(B) | #2DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 斗南DS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | D08//2DTR(B)/TR_PERM |  | DTR_PERM |  |  | 95 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D08 | 斗南DS | 0 |  | 3DTR(A) | #3DTR(A) |  | PERM | [25 empty] | ADCS_N | [8 empty] | 斗南DS.#3DTR(A)_PERM | #3DTR(A) TAP PERMISSION POINT | MTR | D08//3DTR(A)/TR_PERM |  | DTR_PERM |  |  | 96 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D08 | 斗南DS | 0 |  | 3DTR(B) | #3DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 斗南DS.#3DTR(B)_PERM | #3DTR TAP PERMISSION POINT | MTR | D08//3DTR(B)/TR_PERM |  | DTR_PERM |  |  | 97 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D08 | 斗南DS | 0 |  | 2DTR_MVA | #2DTR | [27 empty] | ADCS_N | [8 empty] | 斗南DS.#2DTR_MVA_A | #2DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 98 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D08 | 斗南DS | 0 |  | 2DTR_MVA | #2DTR(A) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.#2DTR_MVA_1 | #2DTR(A) MVA 點燈 (D1) | MTR |  |  | MAP_SET |  |  | 99 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D08 | 斗南DS | 0 |  | 2DTR_MVA | #2DTR(B) | [27 empty] | DDCS1_1 | [8 empty] | 斗南DS.#2DTR_MVA_2 | #2DTR(B) MVA 點燈 (D1) | MTR |  |  | MAP_SET |  |  | 100 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
D08 | 斗南DS | 0 |  | 3DTR_MVA | #3DTR | [27 empty] | ADCS_N | [8 empty] | 斗南DS.#3DTR_MVA_A | #3DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 101 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D08 | 斗南DS | 0 |  | 3DTR_MVA | #3DTR |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.#3DTR_MVA_1 | #3DTR MVA 點燈 (D1) | MTR |  |  | MAP_SET |  |  | 102 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D08 | 斗南DS | 0 |  | 3DTR_MVA | #3DTR(B) | [27 empty] | DDCS1_1 | [8 empty] | 斗南DS.#3DTR_MVA_2 | #3DTR(B) MVA 點燈 (D1) | MTR |  |  | MAP_SET |  |  | 103 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
D08 | 斗南DS | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_N | [8 empty] | 斗南DS.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_DS |  |  | 104 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 81RY_A_S(1) | 360低頻電驛動作/復歸 |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗南DS.81RY_A/S(1)_1 | 360低頻電驛動作/復歸 (D1) | OTHER |  |  | AD_LAMP_DD_7 |  |  | 105 | CalcDIPoint | [38 empty] | TRIP/RESET | RESET
D08 | 斗南DS | 161 | 161kV | 1510_AMP | 斗南虎菁一路 | [27 empty] | ADCS_N | [8 empty] | 斗南DS.1510_AMP_A | 斗南虎菁一路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 106 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D08 | 斗南DS | 161 | 161kV | 1520_AMP | 斗南虎菁二路 | [27 empty] | ADCS_N | [8 empty] | 斗南DS.1520_AMP_A | 斗南虎菁二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 107 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D08 | 斗南DS | 0 |  | 2ABUS | #2ABUS |  | 23KV#2ABUSC | [25 empty] | CDCS | [8 empty] | 斗南DS.23KV#2ABUSC | #2ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 108 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D08 | 斗南DS | 0 |  | 2BBUS | #2BBUS |  | 11KV#2BBUSC | [25 empty] | CDCS | [8 empty] | 斗南DS.11KV#2BBUSC | #2BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 109 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D08 | 斗南DS | 0 |  | 3ABUS | #3ABUS |  | 23KV#3ABUSC | [25 empty] | CDCS | [8 empty] | 斗南DS.23KV#3ABUSC | #3ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 110 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D08 | 斗南DS | 0 |  | 3BBUS | #3BBUS |  | 11KV#3BBUSC | [25 empty] | CDCS | [8 empty] | 斗南DS.11KV#3BBUSC | #3BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 111 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D08 | 斗南DS | 0 |  | TAP_OVER | TAP |  | SET | [25 empty] | ADCS_N | [8 empty] | 斗南DS.TAP_OVER_SET | TAP OVER HI/LO ALARM | MTR |  |  | 5000_CB_T4 |  |  | 112 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D08 | 斗南DS | 0 |  | BUS_OVER | BUS |  | SET | [25 empty] | ADCS_N | [8 empty] | 斗南DS.BUS_OVER_SET | BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B4 |  |  | 113 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D08 | 斗南DS | 0 |  | 5000 | 虛擬5000 |  | CB動作 | [25 empty] | ADCS_N | [8 empty] | 斗南DS.5000_CB動作 | 虛擬5000 CB動作,請查明原因處理 | MTR |  |  | 5000_CB_M |  |  | 114 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | 注意OLTC | 注意OLTC |  | BUS電壓異常 | [25 empty] | ADCS_N | [8 empty] | 斗南DS.BUS電壓異常 | 注意OLTC Tap位置,並將RPDC閉鎖 | OTHER |  |  | STATION_FAULT_1 |  |  | 115 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | D08/0/RTU/ADCH1 |  |  |  | CDC | 116 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | D08/0/RTU/ADCH2 |  |  |  | CDC | 117 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | D08/0/RTU/ADCH3 |  |  |  | CDC | 118 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 0 |  | AI | AI |  | ADCH4 | [17 empty] | 2-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | D08/0/RTU/ADCH4 |  |  |  | CDC | 119 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | D08/0/RTU/ADCL1 |  |  |  | CDC | 120 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | D08/0/RTU/ADCL2 |  |  |  | CDC | 121 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | D08/0/RTU/ADCL3 |  |  |  | CDC | 122 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 0 |  | AI | AI |  | ADCL4 | [17 empty] | 2-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | D08/0/RTU/ADCL4 |  |  |  | CDC | 123 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 161 | 161kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | D08/161/1BUS/V |  |  |  | CDC | 124 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D08 | 斗南DS | 161 | 161kV | 2BUS | #2BUS |  | V | [17 empty] | 1-83 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | D08/161/2BUS/V |  |  |  | CDC | 125 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D08 | 斗南DS | 11 | 11kV | 2BBUS | #2BBUS |  | V | [17 empty] | 2-AA | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.11KV#2BBUS_KV | 11KV #2BBUS KV | BUS | D08/11/2BBUS/V |  |  |  | CDC | 126 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D08 | 斗南DS | 11 | 11kV | 3BBUS | #3BBUS |  | V | [17 empty] | 2-E3 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.11KV#3BBUS_KV | 11KV #3BBUS KV | BUS | D08/11/3BBUS/V |  |  |  | CDC | 127 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D08 | 斗南DS | 22 | 22kV | 2ABUS | #2ABUS |  | V | [17 empty] | 2-85 | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.23KV#2ABUS_KV | 23KV #2ABUS KV | BUS | D08/22/2ABUS/V |  |  |  | CDC | 128 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D08 | 斗南DS | 22 | 22kV | 3ABUS | #3ABUS |  | V | [17 empty] | 2-C9 | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.23KV#3ABUS_KV | 23KV #3ABUS KV | BUS | D08/22/3ABUS/V |  |  |  | CDC | 129 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D08 | 斗南DS | 161 | 161kV | 1530 | 雲林斗南線(1530) |  | MW | [17 empty] | 1-8E | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.1530_MW | 雲林斗南線 MW | LINE161 | D08/161/1530/MW |  |  |  | CDC | 130 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D08 | 斗南DS | 161 | 161kV | 1530 | 雲林斗南線(1530) |  | MVAR | [17 empty] | 1-8F | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.1530_MVAR | 雲林斗南線 MVAR | LINE161 | D08/161/1530/MVAR |  |  |  | CDC | 131 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D08 | 斗南DS | 161 | 161kV | 1540 | 斗南北勢線(1540) |  | MW | [17 empty] | 1-90 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.1540_MW | 斗南北勢線 MW | LINE161 | D08/161/1540/MW |  |  |  | CDC | 132 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D08 | 斗南DS | 161 | 161kV | 1540 | 斗南北勢線(1540) |  | MVAR | [17 empty] | 1-91 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.1540_MVAR | 斗南北勢線 MVAR | LINE161 | D08/161/1540/MVAR |  |  |  | CDC | 133 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南二十線 | 南二十線 |  | 南二十線KVAR | [17 empty] | 2-D9 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南二十線KVAR | 11KV南二十線 KVAR | FEEDER | D08/11/XW41/KVAR |  |  |  | CDC | 134 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南二十線 | 南二十線 |  | 南二十線A1 | [17 empty] | 2-DA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南二十線A1 | 11KV南二十線 R相AMP | FEEDER | D08/11/XW41/I_R |  |  |  | CDC | 135 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南二十線 | 南二十線 |  | 南二十線A2 | [17 empty] | 2-DB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南二十線A2 | 11KV南二十線 S相AMP | FEEDER | D08/11/XW41/I_S |  |  |  | CDC | 136 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南二十線 | 南二十線 |  | 南二十線A3 | [17 empty] | 2-DC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南二十線A3 | 11KV南二十線 T相AMP | FEEDER | D08/11/XW41/I_T |  |  |  | CDC | 137 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南二十線 | 南二十線 |  | 南二十線A0 | [17 empty] | 2-DD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南二十線A0 | 11KV南二十線 N相AMP | FEEDER | D08/11/XW41/I_N |  |  |  | CDC | 138 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十一線 | 南十一線 |  | 南十一線KVAR | [17 empty] | 1-F4 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十一線KVAR | 11KV南十一線 KVAR | FEEDER | D08/11/XW31/KVAR |  |  |  | CDC | 139 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十一線 | 南十一線 |  | 南十一線A1 | [17 empty] | 1-F5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十一線A1 | 11KV南十一線 R相AMP | FEEDER | D08/11/XW31/I_R |  |  |  | CDC | 140 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十一線 | 南十一線 |  | 南十一線A2 | [17 empty] | 1-F6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十一線A2 | 11KV南十一線 S相AMP | FEEDER | D08/11/XW31/I_S |  |  |  | CDC | 141 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十一線 | 南十一線 |  | 南十一線A3 | [17 empty] | 1-F7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十一線A3 | 11KV南十一線 T相AMP | FEEDER | D08/11/XW31/I_T |  |  |  | CDC | 142 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十一線 | 南十一線 |  | 南十一線A0 | [17 empty] | 1-F8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十一線A0 | 11KV南十一線 N相AMP | FEEDER | D08/11/XW31/I_N |  |  |  | CDC | 143 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十七線 | 南十七線 |  | 南十七線KVAR | [17 empty] | 2-CA | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十七線KVAR | 11KV南十七線 KVAR | FEEDER | D08/11/XW37/KVAR |  |  |  | CDC | 144 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十七線 | 南十七線 |  | 南十七線A1 | [17 empty] | 2-CB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十七線A1 | 11KV南十七線 R相AMP | FEEDER | D08/11/XW37/I_R |  |  |  | CDC | 145 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十七線 | 南十七線 |  | 南十七線A2 | [17 empty] | 2-CC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十七線A2 | 11KV南十七線 S相AMP | FEEDER | D08/11/XW37/I_S |  |  |  | CDC | 146 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十七線 | 南十七線 |  | 南十七線A3 | [17 empty] | 2-CD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十七線A3 | 11KV南十七線 T相AMP | FEEDER | D08/11/XW37/I_T |  |  |  | CDC | 147 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十七線 | 南十七線 |  | 南十七線A0 | [17 empty] | 2-CE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十七線A0 | 11KV南十七線 N相AMP | FEEDER | D08/11/XW37/I_N |  |  |  | CDC | 148 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十九線 | 南十九線 |  | 南十九線KVAR | [17 empty] | 2-D4 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十九線KVAR | 11KV南十九線 KVAR | FEEDER | D08/11/XW39/KVAR |  |  |  | CDC | 149 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十九線 | 南十九線 |  | 南十九線A1 | [17 empty] | 2-D5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十九線A1 | 11KV南十九線 R相AMP | FEEDER | D08/11/XW39/I_R |  |  |  | CDC | 150 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十九線 | 南十九線 |  | 南十九線A2 | [17 empty] | 2-D6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十九線A2 | 11KV南十九線 S相AMP | FEEDER | D08/11/XW39/I_S |  |  |  | CDC | 151 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十九線 | 南十九線 |  | 南十九線A3 | [17 empty] | 2-D7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十九線A3 | 11KV南十九線 T相AMP | FEEDER | D08/11/XW39/I_T |  |  |  | CDC | 152 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十九線 | 南十九線 |  | 南十九線A0 | [17 empty] | 2-D8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十九線A0 | 11KV南十九線 N相AMP | FEEDER | D08/11/XW39/I_N |  |  |  | CDC | 153 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十二線 | 南十二線 |  | 南十二線KVAR | [17 empty] | 1-F9 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十二線KVAR | 11KV南十二線 KVAR | FEEDER | D08/11/XW32/KVAR |  |  |  | CDC | 154 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十二線 | 南十二線 |  | 南十二線A1 | [17 empty] | 1-FA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十二線A1 | 11KV南十二線 R相AMP | FEEDER | D08/11/XW32/I_R |  |  |  | CDC | 155 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十二線 | 南十二線 |  | 南十二線A2 | [17 empty] | 1-FB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十二線A2 | 11KV南十二線 S相AMP | FEEDER | D08/11/XW32/I_S |  |  |  | CDC | 156 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十二線 | 南十二線 |  | 南十二線A3 | [17 empty] | 1-FC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十二線A3 | 11KV南十二線 T相AMP | FEEDER | D08/11/XW32/I_T |  |  |  | CDC | 157 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十二線 | 南十二線 |  | 南十二線A0 | [17 empty] | 1-FD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十二線A0 | 11KV南十二線 N相AMP | FEEDER | D08/11/XW32/I_N |  |  |  | CDC | 158 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十八線 | 南十八線 |  | 南十八線KVAR | [17 empty] | 2-CF | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十八線KVAR | 11KV南十八線 KVAR | FEEDER | D08/11/XW38/KVAR |  |  |  | CDC | 159 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十八線 | 南十八線 |  | 南十八線A1 | [17 empty] | 2-D0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十八線A1 | 11KV南十八線 R相AMP | FEEDER | D08/11/XW38/I_R |  |  |  | CDC | 160 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十八線 | 南十八線 |  | 南十八線A2 | [17 empty] | 2-D1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十八線A2 | 11KV南十八線 S相AMP | FEEDER | D08/11/XW38/I_S |  |  |  | CDC | 161 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十八線 | 南十八線 |  | 南十八線A3 | [17 empty] | 2-D2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十八線A3 | 11KV南十八線 T相AMP | FEEDER | D08/11/XW38/I_T |  |  |  | CDC | 162 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十八線 | 南十八線 |  | 南十八線A0 | [17 empty] | 2-D3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十八線A0 | 11KV南十八線 N相AMP | FEEDER | D08/11/XW38/I_N |  |  |  | CDC | 163 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十三線 | 南十三線 |  | 南十三線KVAR | [17 empty] | 2-8C | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十三線KVAR | 11KV南十三線 KVAR | FEEDER | D08/11/XW33/KVAR |  |  |  | CDC | 164 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十三線 | 南十三線 |  | 南十三線A1 | [17 empty] | 2-8D | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十三線A1 | 11KV南十三線 R相AMP | FEEDER | D08/11/XW33/I_R |  |  |  | CDC | 165 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十三線 | 南十三線 |  | 南十三線A2 | [17 empty] | 2-8E | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十三線A2 | 11KV南十三線 S相AMP | FEEDER | D08/11/XW33/I_S |  |  |  | CDC | 166 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十三線 | 南十三線 |  | 南十三線A3 | [17 empty] | 2-8F | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十三線A3 | 11KV南十三線 T相AMP | FEEDER | D08/11/XW33/I_T |  |  |  | CDC | 167 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十三線 | 南十三線 |  | 南十三線A0 | [17 empty] | 2-90 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十三線A0 | 11KV南十三線 N相AMP | FEEDER | D08/11/XW33/I_N |  |  |  | CDC | 168 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十五線 | 南十五線 |  | 南十五線KVAR | [17 empty] | 2-96 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十五線KVAR | 11KV南十五線 KVAR | FEEDER | D08/11/XW35/KVAR |  |  |  | CDC | 169 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十五線 | 南十五線 |  | 南十五線A1 | [17 empty] | 2-97 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十五線A1 | 11KV南十五線 R相AMP | FEEDER | D08/11/XW35/I_R |  |  |  | CDC | 170 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十五線 | 南十五線 |  | 南十五線A2 | [17 empty] | 2-98 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十五線A2 | 11KV南十五線 S相AMP | FEEDER | D08/11/XW35/I_S |  |  |  | CDC | 171 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十五線 | 南十五線 |  | 南十五線A3 | [17 empty] | 2-99 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十五線A3 | 11KV南十五線 T相AMP | FEEDER | D08/11/XW35/I_T |  |  |  | CDC | 172 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十五線 | 南十五線 |  | 南十五線A0 | [17 empty] | 2-9A | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十五線A0 | 11KV南十五線 N相AMP | FEEDER | D08/11/XW35/I_N |  |  |  | CDC | 173 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十六線 | 南十六線 |  | 南十六線KVAR | [17 empty] | 2-BD | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十六線KVAR | 11KV南十六線 KVAR | FEEDER | D08/11/XW36/KVAR |  |  |  | CDC | 174 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十六線 | 南十六線 |  | 南十六線A1 | [17 empty] | 2-BE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十六線A1 | 11KV南十六線 R相AMP | FEEDER | D08/11/XW36/I_R |  |  |  | CDC | 175 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十六線 | 南十六線 |  | 南十六線A2 | [17 empty] | 2-BF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十六線A2 | 11KV南十六線 S相AMP | FEEDER | D08/11/XW36/I_S |  |  |  | CDC | 176 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十六線 | 南十六線 |  | 南十六線A3 | [17 empty] | 2-C2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十六線A3 | 11KV南十六線 T相AMP | FEEDER | D08/11/XW36/I_T |  |  |  | CDC | 177 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十六線 | 南十六線 |  | 南十六線A0 | [17 empty] | 2-C3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十六線A0 | 11KV南十六線 N相AMP | FEEDER | D08/11/XW36/I_N |  |  |  | CDC | 178 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十四線 | 南十四線 |  | 南十四線KVAR | [17 empty] | 2-91 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十四線KVAR | 11KV南十四線 KVAR | FEEDER | D08/11/XW34/KVAR |  |  |  | CDC | 179 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十四線 | 南十四線 |  | 南十四線A1 | [17 empty] | 2-92 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十四線A1 | 11KV南十四線 R相AMP | FEEDER | D08/11/XW34/I_R |  |  |  | CDC | 180 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十四線 | 南十四線 |  | 南十四線A2 | [17 empty] | 2-93 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十四線A2 | 11KV南十四線 S相AMP | FEEDER | D08/11/XW34/I_S |  |  |  | CDC | 181 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十四線 | 南十四線 |  | 南十四線A3 | [17 empty] | 2-94 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十四線A3 | 11KV南十四線 T相AMP | FEEDER | D08/11/XW34/I_T |  |  |  | CDC | 182 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | 南十四線 | 南十四線 |  | 南十四線A0 | [17 empty] | 2-95 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南十四線A0 | 11KV南十四線 N相AMP | FEEDER | D08/11/XW34/I_N |  |  |  | CDC | 183 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南七一線 | 南七一線 |  | 南七一線KVAR | [17 empty] | 2-9B | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南七一線KVAR | 23KV南七一線 KVAR | FEEDER | D08/22/XW71/KVAR |  |  |  | CDC | 184 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南七一線 | 南七一線 |  | 南七一線A1 | [17 empty] | 2-9C | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南七一線A1 | 23KV南七一線 R相AMP | FEEDER | D08/22/XW71/I_R |  |  |  | CDC | 185 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南七一線 | 南七一線 |  | 南七一線A2 | [17 empty] | 2-9D | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南七一線A2 | 23KV南七一線 S相AMP | FEEDER | D08/22/XW71/I_S |  |  |  | CDC | 186 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南七一線 | 南七一線 |  | 南七一線A3 | [17 empty] | 2-9E | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南七一線A3 | 23KV南七一線 T相AMP | FEEDER | D08/22/XW71/I_T |  |  |  | CDC | 187 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南七一線 | 南七一線 |  | 南七一線A0 | [17 empty] | 2-9F | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南七一線A0 | 23KV南七一線 N相AMP | FEEDER | D08/22/XW71/I_N |  |  |  | CDC | 188 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南七二線 | 南七二線 |  | 南七二線KVAR | [17 empty] | 2-A0 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南七二線KVAR | 23KV南七二線 KVAR | FEEDER | D08/22/XW72/KVAR |  |  |  | CDC | 189 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南七二線 | 南七二線 |  | 南七二線A1 | [17 empty] | 2-A1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南七二線A1 | 23KV南七二線 R相AMP | FEEDER | D08/22/XW72/I_R |  |  |  | CDC | 190 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南七二線 | 南七二線 |  | 南七二線A2 | [17 empty] | 2-A2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南七二線A2 | 23KV南七二線 S相AMP | FEEDER | D08/22/XW72/I_S |  |  |  | CDC | 191 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南七二線 | 南七二線 |  | 南七二線A3 | [17 empty] | 2-A3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南七二線A3 | 23KV南七二線 T相AMP | FEEDER | D08/22/XW72/I_T |  |  |  | CDC | 192 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南七二線 | 南七二線 |  | 南七二線A0 | [17 empty] | 2-A4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南七二線A0 | 23KV南七二線 N相AMP | FEEDER | D08/22/XW72/I_N |  |  |  | CDC | 193 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南七三線 | 南七三線 |  | 南七三線KVAR | [17 empty] | 2-AE | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南七三線KVAR | 23KV南七三線 KVAR | FEEDER | D08/22/XW73/KVAR |  |  |  | CDC | 194 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南七三線 | 南七三線 |  | 南七三線A1 | [17 empty] | 2-AF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南七三線A1 | 23KV南七三線 R相AMP | FEEDER | D08/22/XW73/I_R |  |  |  | CDC | 195 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南七三線 | 南七三線 |  | 南七三線A2 | [17 empty] | 2-B0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南七三線A2 | 23KV南七三線 S相AMP | FEEDER | D08/22/XW73/I_S |  |  |  | CDC | 196 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南七三線 | 南七三線 |  | 南七三線A3 | [17 empty] | 2-B1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南七三線A3 | 23KV南七三線 T相AMP | FEEDER | D08/22/XW73/I_T |  |  |  | CDC | 197 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南七三線 | 南七三線 |  | 南七三線A0 | [17 empty] | 2-B2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南七三線A0 | 23KV南七三線 N相AMP | FEEDER | D08/22/XW73/I_N |  |  |  | CDC | 198 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南七五線 | 南七五線 |  | 南七五線KVAR | [17 empty] | 2-B8 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南七五線KVAR | 23KV南七五線 KVAR | FEEDER | D08/22/XW75/KVAR |  |  |  | CDC | 199 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南七五線 | 南七五線 |  | 南七五線A1 | [17 empty] | 2-B9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南七五線A1 | 23KV南七五線 R相AMP | FEEDER | D08/22/XW75/I_R |  |  |  | CDC | 200 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南七五線 | 南七五線 |  | 南七五線A2 | [17 empty] | 2-BA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南七五線A2 | 23KV南七五線 S相AMP | FEEDER | D08/22/XW75/I_S |  |  |  | CDC | 201 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南七五線 | 南七五線 |  | 南七五線A3 | [17 empty] | 2-BB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南七五線A3 | 23KV南七五線 T相AMP | FEEDER | D08/22/XW75/I_T |  |  |  | CDC | 202 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南七五線 | 南七五線 |  | 南七五線A0 | [17 empty] | 2-BC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南七五線A0 | 23KV南七五線 N相AMP | FEEDER | D08/22/XW75/I_N |  |  |  | CDC | 203 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南七四線 | 南七四線 |  | 南七四線KVAR | [17 empty] | 2-B3 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南七四線KVAR | 23KV南七四線 KVAR | FEEDER | D08/22/XW74/KVAR |  |  |  | CDC | 204 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南七四線 | 南七四線 |  | 南七四線A1 | [17 empty] | 2-B4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南七四線A1 | 23KV南七四線 R相AMP | FEEDER | D08/22/XW74/I_R |  |  |  | CDC | 205 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南七四線 | 南七四線 |  | 南七四線A2 | [17 empty] | 2-B5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南七四線A2 | 23KV南七四線 S相AMP | FEEDER | D08/22/XW74/I_S |  |  |  | CDC | 206 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南七四線 | 南七四線 |  | 南七四線A3 | [17 empty] | 2-B6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南七四線A3 | 23KV南七四線 T相AMP | FEEDER | D08/22/XW74/I_T |  |  |  | CDC | 207 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南七四線 | 南七四線 |  | 南七四線A0 | [17 empty] | 2-B7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南七四線A0 | 23KV南七四線 N相AMP | FEEDER | D08/22/XW74/I_N |  |  |  | CDC | 208 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南六一線 | 南六一線 |  | 南六一線KVAR | [17 empty] | 1-D8 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南六一線KVAR | 23KV南六一線 KVAR | FEEDER | D08/22/XW61/KVAR |  |  |  | CDC | 209 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南六一線 | 南六一線 |  | 南六一線A1 | [17 empty] | 1-D9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南六一線A1 | 23KV南六一線 R相AMP | FEEDER | D08/22/XW61/I_R |  |  |  | CDC | 210 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南六一線 | 南六一線 |  | 南六一線A2 | [17 empty] | 1-DA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南六一線A2 | 23KV南六一線 S相AMP | FEEDER | D08/22/XW61/I_S |  |  |  | CDC | 211 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南六一線 | 南六一線 |  | 南六一線A3 | [17 empty] | 1-DB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南六一線A3 | 23KV南六一線 T相AMP | FEEDER | D08/22/XW61/I_T |  |  |  | CDC | 212 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南六一線 | 南六一線 |  | 南六一線A0 | [17 empty] | 1-DC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南六一線A0 | 23KV南六一線 N相AMP | FEEDER | D08/22/XW61/I_N |  |  |  | CDC | 213 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南六二線 | 南六二線 |  | 南六二線KVAR | [17 empty] | 1-DD | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南六二線KVAR | 23KV南六二線 KVAR | FEEDER | D08/22/XW62/KVAR |  |  |  | CDC | 214 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南六二線 | 南六二線 |  | 南六二線A1 | [17 empty] | 1-DE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南六二線A1 | 23KV南六二線 R相AMP | FEEDER | D08/22/XW62/I_R |  |  |  | CDC | 215 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南六二線 | 南六二線 |  | 南六二線A2 | [17 empty] | 1-DF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南六二線A2 | 23KV南六二線 S相AMP | FEEDER | D08/22/XW62/I_S |  |  |  | CDC | 216 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南六二線 | 南六二線 |  | 南六二線A3 | [17 empty] | 1-E0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南六二線A3 | 23KV南六二線 T相AMP | FEEDER | D08/22/XW62/I_T |  |  |  | CDC | 217 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南六二線 | 南六二線 |  | 南六二線A0 | [17 empty] | 1-E1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南六二線A0 | 23KV南六二線 N相AMP | FEEDER | D08/22/XW62/I_N |  |  |  | CDC | 218 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南六三線 | 南六三線 |  | 南六三線KVAR | [17 empty] | 1-E5 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南六三線KVAR | 23KV南六三線 KVAR | FEEDER | D08/22/XW63/KVAR |  |  |  | CDC | 219 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南六三線 | 南六三線 |  | 南六三線A1 | [17 empty] | 1-E6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南六三線A1 | 23KV南六三線 R相AMP | FEEDER | D08/22/XW63/I_R |  |  |  | CDC | 220 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南六三線 | 南六三線 |  | 南六三線A2 | [17 empty] | 1-E7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南六三線A2 | 23KV南六三線 S相AMP | FEEDER | D08/22/XW63/I_S |  |  |  | CDC | 221 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南六三線 | 南六三線 |  | 南六三線A3 | [17 empty] | 1-E8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南六三線A3 | 23KV南六三線 T相AMP | FEEDER | D08/22/XW63/I_T |  |  |  | CDC | 222 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南六三線 | 南六三線 |  | 南六三線A0 | [17 empty] | 1-E9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南六三線A0 | 23KV南六三線 N相AMP | FEEDER | D08/22/XW63/I_N |  |  |  | CDC | 223 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南六五線 | 南六五線 |  | 南六五線KVAR | [17 empty] | 1-EF | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南六五線KVAR | 23KV南六五線 KVAR | FEEDER | D08/22/XW65/KVAR |  |  |  | CDC | 224 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南六五線 | 南六五線 |  | 南六五線A1 | [17 empty] | 1-F0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南六五線A1 | 23KV南六五線 R相AMP | FEEDER | D08/22/XW65/I_R |  |  |  | CDC | 225 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南六五線 | 南六五線 |  | 南六五線A2 | [17 empty] | 1-F1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南六五線A2 | 23KV南六五線 S相AMP | FEEDER | D08/22/XW65/I_S |  |  |  | CDC | 226 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南六五線 | 南六五線 |  | 南六五線A3 | [17 empty] | 1-F2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南六五線A3 | 23KV南六五線 T相AMP | FEEDER | D08/22/XW65/I_T |  |  |  | CDC | 227 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南六五線 | 南六五線 |  | 南六五線A0 | [17 empty] | 1-F3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南六五線A0 | 23KV南六五線 N相AMP | FEEDER | D08/22/XW65/I_N |  |  |  | CDC | 228 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南六四線 | 南六四線 |  | 南六四線KVAR | [17 empty] | 1-EA | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南六四線KVAR | 23KV南六四線 KVAR | FEEDER | D08/22/XW64/KVAR |  |  |  | CDC | 229 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南六四線 | 南六四線 |  | 南六四線A1 | [17 empty] | 1-EB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南六四線A1 | 23KV南六四線 R相AMP | FEEDER | D08/22/XW64/I_R |  |  |  | CDC | 230 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南六四線 | 南六四線 |  | 南六四線A2 | [17 empty] | 1-EC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南六四線A2 | 23KV南六四線 S相AMP | FEEDER | D08/22/XW64/I_S |  |  |  | CDC | 231 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南六四線 | 南六四線 |  | 南六四線A3 | [17 empty] | 1-ED | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南六四線A3 | 23KV南六四線 T相AMP | FEEDER | D08/22/XW64/I_T |  |  |  | CDC | 232 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | 南六四線 | 南六四線 |  | 南六四線A0 | [17 empty] | 1-EE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗南DS.南六四線A0 | 23KV南六四線 N相AMP | FEEDER | D08/22/XW64/I_N |  |  |  | CDC | 233 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 0 |  | 1500TIE | 1500TIE |  | I | [17 empty] | 1-94 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.1500TIE_AMP | 1500TIE AMP | TIE | D08/161/1500/I_R |  |  |  | CDC | 234 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | _400 | 400 |  | I_R | [17 empty] | 2-AB | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.11KV_400_A1 | 11KV 400 R相AMP | TIE | D08/11/400/I_R |  |  |  | CDC | 235 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | _400 | 400 |  | I_S | [17 empty] | 2-AC | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.11KV_400_A2 | 11KV 400 S相AMP | TIE | D08/11/400/I_S |  |  |  | CDC | 236 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 11 | 11kV | _400 | 400 |  | I_T | [17 empty] | 2-AD | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.11KV_400_A3 | 11KV 400 T相AMP | TIE | D08/11/400/I_T |  |  |  | CDC | 237 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | _300 | 300 |  | I_R | [17 empty] | 2-89 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.23KV_300_A1 | 23KV 300 R相AMP | TIE | D08/22/300/I_R |  |  |  | CDC | 238 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | _300 | 300 |  | I_S | [17 empty] | 2-8A | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.23KV_300_A2 | 23KV 300 S相AMP | TIE | D08/22/300/I_S |  |  |  | CDC | 239 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 22 | 22kV | _300 | 300 |  | I_T | [17 empty] | 2-8B | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.23KV_300_A3 | 23KV 300 T相AMP | TIE | D08/22/300/I_T |  |  |  | CDC | 240 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 0 |  |  |  |  | DCV_N | [17 empty] | 1-93 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.直流N電源電壓 | 直流N電源電壓 | OTHER | D08/0/StaDev/DCV_N |  |  |  | CDC | 241 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D08 | 斗南DS | 0 |  |  |  |  | DCV_P | [17 empty] | 1-92 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.直流P電源電壓 | 直流P電源電壓 | OTHER | D08/0/StaDev/DCV_P |  |  |  | CDC | 242 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D08 | 斗南DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MW | [17 empty] | 1-FE | [5 empty] | MW_-108_108(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | D08/22/330/KW |  |  |  | CDC | 243 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D08 | 斗南DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVAR | [17 empty] | 1-FF | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | D08/22/330/KVAR |  |  |  | CDC | 244 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D08 | 斗南DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_R | [17 empty] | 2-82 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | D08/22/330/I_R |  |  |  | CDC | 245 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_S | [17 empty] | 2-83 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | D08/22/330/I_S |  |  |  | CDC | 246 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_T | [17 empty] | 2-84 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | D08/22/330/I_T |  |  |  | CDC | 247 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 0 |  | 2DTR | #2DTR |  | OilTemp | [17 empty] | 1-98 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.#2DTR_OIL | #2DTR 油溫 | MTR | D08//2DTR/OilTemp |  |  |  | CDC | 248 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D08 | 斗南DS | 0 |  | 2DTR(A) | #2DTR(A) |  | CoilTemp | [17 empty] | 1-99 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | D08//2DTR(A)/CoilTemp |  |  |  | CDC | 249 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D08 | 斗南DS | 0 |  | 2DTR(A) | #2DTR(A) |  | TapPosMv | [17 empty] | 1-9B |  | 1-51 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 斗南DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | D08//2DTR(A)/TapPosMv |  |  |  | CDC | 250 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D08 | 斗南DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MW | [17 empty] | 2-A5 | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | D08/11/340/KW |  |  |  | CDC | 251 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D08 | 斗南DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVAR | [17 empty] | 2-A6 | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | D08/11/340/KVAR |  |  |  | CDC | 252 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D08 | 斗南DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_R | [17 empty] | 2-A7 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | D08/11/340/I_R |  |  |  | CDC | 253 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_S | [17 empty] | 2-A8 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | D08/11/340/I_S |  |  |  | CDC | 254 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_T | [17 empty] | 2-A9 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | D08/11/340/I_T |  |  |  | CDC | 255 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 0 |  | 2DTR(B) | #2DTR(B) |  | CoilTemp | [17 empty] | 1-9A | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | D08//2DTR(B)/CoilTemp |  |  |  | CDC | 256 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D08 | 斗南DS | 0 |  | 2DTR(B) | #2DTR(B) |  | TapPosMv | [17 empty] | 1-9C |  | 1-53 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 斗南DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | D08//2DTR(B)/TapPosMv |  |  |  | CDC | 257 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D08 | 斗南DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | MW | [17 empty] | 2-C4 | [5 empty] | MW_-108_108(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.#3DTR(A)_MW | #3DTR二次側(A) MW | MTR | D08/22/350/KW |  |  |  | CDC | 258 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D08 | 斗南DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | MVAR | [17 empty] | 2-C5 | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.#3DTR(A)_MVAR | #3DTR二次側(A) MVAR | MTR | D08/22/350/KVAR |  |  |  | CDC | 259 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D08 | 斗南DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | I_R | [17 empty] | 2-C6 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.#3DTR(A)_A1 | #3DTR二次側(A) R相AMP | MTR | D08/22/350/I_R |  |  |  | CDC | 260 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | I_S | [17 empty] | 2-C7 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.#3DTR(A)_A2 | #3DTR二次側(A) S相AMP | MTR | D08/22/350/I_S |  |  |  | CDC | 261 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | I_T | [17 empty] | 2-C8 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.#3DTR(A)_A3 | #3DTR二次側(A) T相AMP | MTR | D08/22/350/I_T |  |  |  | CDC | 262 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 0 |  | 3DTR | #3DTR |  | OilTemp | [17 empty] | 1-9D | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.#3DTR_OIL | #3DTR 油溫 | MTR | D08//3DTR/OilTemp |  |  |  | CDC | 263 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D08 | 斗南DS | 0 |  | 3DTR(A) | #3DTR(A) |  | CoilTemp | [17 empty] | 1-9E | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.#3DTR(A)_COIL | #3DTR(A) 線溫 | MTR | D08//3DTR(A)/CoilTemp |  |  |  | CDC | 264 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D08 | 斗南DS | 0 |  | 3DTR(A) | #3DTR(A) |  | TapPosMv | [17 empty] | 1-A0 |  | 1-55 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 斗南DS.#3DTR(A)_TAP | #3DTR(A) OLTC TAP | MTR | D08//3DTR(A)/TapPosMv |  |  |  | CDC | 265 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D08 | 斗南DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | MW | [17 empty] | 2-DE | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.#3DTR(B)_MW | #3DTR二次側(B) MW | MTR | D08/11/360/KW |  |  |  | CDC | 266 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D08 | 斗南DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | MVAR | [17 empty] | 2-DF | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.#3DTR(B)_MVAR | #3DTR二次側(B) MVAR | MTR | D08/11/360/KVAR |  |  |  | CDC | 267 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D08 | 斗南DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | I_R | [17 empty] | 2-E0 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.#3DTR(B)_A1 | #3DTR二次側(B) R相AMP | MTR | D08/11/360/I_R |  |  |  | CDC | 268 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | I_S | [17 empty] | 2-E1 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.#3DTR(B)_A2 | #3DTR二次側(B) S相AMP | MTR | D08/11/360/I_S |  |  |  | CDC | 269 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | I_T | [17 empty] | 2-E2 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.#3DTR(B)_A3 | #3DTR二次側(B) T相AMP | MTR | D08/11/360/I_T |  |  |  | CDC | 270 | GENERICAIPoint | DS040_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D08 | 斗南DS | 0 |  | 3DTR(B) | #3DTR(B) |  | CoilTemp | [17 empty] | 1-9F | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.#3DTR(B)_COIL | #3DTR(B) 線溫 | MTR | D08//3DTR(B)/CoilTemp |  |  |  | CDC | 271 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D08 | 斗南DS | 0 |  | 3DTR(B) | #3DTR(B) |  | TapPosMv | [17 empty] | 1-A1 |  | 1-57 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 斗南DS.#3DTR(B)_TAP | #3DTR(B) OLTC TAP | MTR | D08//3DTR(B)/TapPosMv |  |  |  | CDC | 272 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D08 | 斗南DS | 161 | 161kV | 1510 | 斗南虎菁一路(1510) |  | MW | [17 empty] | 1-8A | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.1510_MW | 斗南虎菁一路 MW | LINE161 | D08/161/1510/MW |  |  |  | CDC | 273 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D08 | 斗南DS | 161 | 161kV | 1510 | 斗南虎菁一路(1510) |  | MVAR | [17 empty] | 1-8B | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.1510_MVAR | 斗南虎菁一路 MVAR | LINE161 | D08/161/1510/MVAR |  |  |  | CDC | 274 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D08 | 斗南DS | 161 | 161kV | 1520 | 斗南虎菁二路(1520) |  | MW | [17 empty] | 1-8C | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.1520_MW | 斗南虎菁二路 MW | LINE161 | D08/161/1520/MW |  |  |  | CDC | 275 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D08 | 斗南DS | 161 | 161kV | 1520 | 斗南虎菁二路(1520) |  | MVAR | [17 empty] | 1-8D | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 斗南DS.1520_MVAR | 斗南虎菁二路 MVAR | LINE161 | D08/161/1520/MVAR |  |  |  | CDC | 276 | GENERICAIPoint | DS040_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D08 | 斗南DS | 161 | 161kV | 1530 | 雲林斗南線(1530) |  | PHA | [17 empty] | 1-03-04 | [7 empty] | 161KV_N | [8 empty] | 斗南DS.1530_PHA | 雲林斗南線(1530) 相間RY | LINE161 | D08/161/1530/PHA |  |  |  | CDC | 277 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1530 | 雲林斗南線(1530) |  | GDA | [17 empty] | 1-03-05 | [7 empty] | 161KV_N | [8 empty] | 斗南DS.1530_GDA | 雲林斗南線(1530) 接地RY | LINE161 | D08/161/1530/GDA |  |  |  | CDC | 278 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1530 | 雲林斗南線(1530) |  | CB | [17 empty] | 1-03-01 |  | 1-06 | [5 empty] | 161KV_N | [8 empty] | 斗南DS.1530_CB | 1530(雲林斗南線) CB | LINE161 | D08/161/1530/CB |  |  |  | CDC | 279 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 161 | 161kV | 1530 | 雲林斗南線(1530) |  | 79UL | [17 empty] | 1-30-13 |  | 1-49 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.1530_79UL | 雲林斗南線(1530) 79RY U/L | LINE161 | D08/161/1530/79UL |  |  |  | CDC | 280 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 161 | 161kV | 1530 | 雲林斗南線(1530) |  | DS1 | 1531 | [16 empty] | 1-3A-08 | 1-3A-09 | 1-6C | [5 empty] | ADCS_N | [8 empty] | 斗南DS.1531_DS | 1531(雲林斗南線) DS | LINE161 | D08/161/1530/DS1 |  |  |  | CDC | 281 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D08 | 斗南DS | 161 | 161kV | 1530 | 雲林斗南線(1530) |  | DS2 | 1532 | [16 empty] | 1-3A-10 | 1-3A-11 | 1-6D | [5 empty] | ADCS_N | [8 empty] | 斗南DS.1532_DS | 1532(雲林斗南線) DS | LINE161 | D08/161/1530/DS2 |  |  |  | CDC | 282 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D08 | 斗南DS | 161 | 161kV | 1530 | 雲林斗南線(1530) |  | DS3 | 1533 | [16 empty] | 1-3A-12 | 1-3A-13 | 1-6E | [5 empty] | ADCS_N | [8 empty] | 斗南DS.1533_DS | 1533(雲林斗南線) DS | LINE161 | D08/161/1530/DS3 |  |  |  | CDC | 283 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D08 | 斗南DS | 161 | 161kV | 1530 | 雲林斗南線(1530) |  | E3 | 1533E | [16 empty] | 1-3A-14 | 1-3A-15 | 1-6F | [5 empty] | ADCS_N | [8 empty] | 斗南DS.1533E_ES | 1533E(雲林斗南線) ES | LINE161 | D08/161/1530/ES3 |  |  |  | CDC | 284 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D08 | 斗南DS | 161 | 161kV | 1540 | 斗南北勢線(1540) |  | PHA | [17 empty] | 1-04-01 | [7 empty] | 161KV_N | [8 empty] | 斗南DS.1540_PHA | 斗南北勢線(1540) 相間RY | LINE161 | D08/161/1540/PHA |  |  |  | CDC | 285 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1540 | 斗南北勢線(1540) |  | GDA | [17 empty] | 1-04-02 | [7 empty] | 161KV_N | [8 empty] | 斗南DS.1540_GDA | 斗南北勢線(1540) 接地RY | LINE161 | D08/161/1540/GDA |  |  |  | CDC | 286 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1540 | 斗南北勢線(1540) |  | CB | [17 empty] | 1-03-06 |  | 1-07 | [5 empty] | 161KV_N | [8 empty] | 斗南DS.1540_CB | 1540(斗南北勢線) CB | LINE161 | D08/161/1540/CB |  |  |  | CDC | 287 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 161 | 161kV | 1540 | 斗南北勢線(1540) |  | 79UL | [17 empty] | 1-30-15 |  | 1-4B | [5 empty] | ADCS_N | [8 empty] | 斗南DS.1540_79UL | 斗南北勢線(1540) 79RY U/L | LINE161 | D08/161/1540/79UL |  |  |  | CDC | 288 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 161 | 161kV | 1540 | 斗南北勢線(1540) |  | DS1 | 1541 | [16 empty] | 1-3B-00 | 1-3B-01 | 1-70 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.1541_DS | 1541(斗南北勢線) DS | LINE161 | D08/161/1540/DS1 |  |  |  | CDC | 289 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D08 | 斗南DS | 161 | 161kV | 1540 | 斗南北勢線(1540) |  | DS2 | 1542 | [16 empty] | 1-3B-02 | 1-3B-03 | 1-71 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.1542_DS | 1542(斗南北勢線) DS | LINE161 | D08/161/1540/DS2 |  |  |  | CDC | 290 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D08 | 斗南DS | 161 | 161kV | 1540 | 斗南北勢線(1540) |  | DS3 | 1543 | [16 empty] | 1-3B-04 | 1-3B-05 | 1-72 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.1543_DS | 1543(斗南北勢線) DS | LINE161 | D08/161/1540/DS3 |  |  |  | CDC | 291 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D08 | 斗南DS | 161 | 161kV | 1540 | 斗南北勢線(1540) |  | E3 | 1543E | [16 empty] | 1-3B-06 | 1-3B-07 | 1-73 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.1543E_ES | 1543E(斗南北勢線) ES | LINE161 | D08/161/1540/ES3 |  |  |  | CDC | 292 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D08 | 斗南DS | 11 | 11kV | XW31 | 南十一線(XW31) |  | PHA | [17 empty] | 1-16-04 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW31_PHA | 11KV南十一線(XW31) 相間RY | FEEDER | D08/11/XW31/PHA |  |  |  | CDC | 293 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW31 | 南十一線(XW31) |  | GDA | [17 empty] | 1-16-05 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW31_GDA | 11KV南十一線(XW31) 接地RY | FEEDER | D08/11/XW31/GDA |  |  |  | CDC | 294 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW31 | 南十一線(XW31) 79RY |  | 79UL | [17 empty] | 2-31-13 |  | 2-1A | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW31_79UL | 11KV南十一線(XW31) 79RY U/L | FEEDER | D08/11/XW31/79UL |  |  |  | CDC | 295 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 11 | 11kV | XW31_LCO | 南十一線(XW31) LCO |  | TapPosMv | [17 empty] | 2-31-14 |  | 2-1B | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW31_LCO_TAP | 11KV南十一線(XW31) LCO TAP | FEEDER | D08/11/XW31/ADJ |  |  |  | CDC | 296 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D08 | 斗南DS | 11 | 11kV | XW31 | XW31(11KV南十一線) |  | CB | [17 empty] | 1-16-03 |  | 1-20 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW31_CB | XW31(11KV南十一線) CB | FEEDER | D08/11/XW31/CB |  |  |  | CDC | 297 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | XW32 | 南十二線(XW32) |  | PHA | [17 empty] | 1-16-07 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW32_PHA | 11KV南十二線(XW32) 相間RY | FEEDER | D08/11/XW32/PHA |  |  |  | CDC | 298 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW32 | 南十二線(XW32) |  | GDA | [17 empty] | 1-17-00 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW32_GDA | 11KV南十二線(XW32) 接地RY | FEEDER | D08/11/XW32/GDA |  |  |  | CDC | 299 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW32 | 南十二線(XW32) 79RY |  | 79UL | [17 empty] | 2-31-15 |  | 2-1C | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW32_79UL | 11KV南十二線(XW32) 79RY U/L | FEEDER | D08/11/XW32/79UL |  |  |  | CDC | 300 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 11 | 11kV | XW32_LCO | 南十二線(XW32) LCO |  | TapPosMv | [17 empty] | 2-32-00 |  | 2-1D | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW32_LCO_TAP | 11KV南十二線(XW32) LCO TAP | FEEDER | D08/11/XW32/ADJ |  |  |  | CDC | 301 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D08 | 斗南DS | 11 | 11kV | XW32 | XW32(11KV南十二線) |  | CB | [17 empty] | 1-16-06 |  | 1-21 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW32_CB | XW32(11KV南十二線) CB | FEEDER | D08/11/XW32/CB |  |  |  | CDC | 302 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | XW33 | 南十三線(XW33) |  | PHA | [17 empty] | 1-18-06 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW33_PHA | 11KV南十三線(XW33) 相間RY | FEEDER | D08/11/XW33/PHA |  |  |  | CDC | 303 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW33 | 南十三線(XW33) |  | GDA | [17 empty] | 1-18-07 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW33_GDA | 11KV南十三線(XW33) 接地RY | FEEDER | D08/11/XW33/GDA |  |  |  | CDC | 304 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW33 | 南十三線(XW33) 79RY |  | 79UL | [17 empty] | 2-32-01 |  | 2-1E | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW33_79UL | 11KV南十三線(XW33) 79RY U/L | FEEDER | D08/11/XW33/79UL |  |  |  | CDC | 305 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 11 | 11kV | XW33_LCO | 南十三線(XW33) LCO |  | TapPosMv | [17 empty] | 2-32-02 |  | 2-1F | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW33_LCO_TAP | 11KV南十三線(XW33) LCO TAP | FEEDER | D08/11/XW33/ADJ |  |  |  | CDC | 306 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D08 | 斗南DS | 11 | 11kV | XW33 | XW33(11KV南十三線) |  | CB | [17 empty] | 1-18-05 |  | 1-27 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW33_CB | XW33(11KV南十三線) CB | FEEDER | D08/11/XW33/CB |  |  |  | CDC | 307 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | XW34 | 南十四線(XW34) |  | PHA | [17 empty] | 1-19-01 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW34_PHA | 11KV南十四線(XW34) 相間RY | FEEDER | D08/11/XW34/PHA |  |  |  | CDC | 308 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW34 | 南十四線(XW34) |  | GDA | [17 empty] | 1-19-02 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW34_GDA | 11KV南十四線(XW34) 接地RY | FEEDER | D08/11/XW34/GDA |  |  |  | CDC | 309 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW34 | 南十四線(XW34) 79RY |  | 79UL | [17 empty] | 2-32-03 |  | 2-20 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW34_79UL | 11KV南十四線(XW34) 79RY U/L | FEEDER | D08/11/XW34/79UL |  |  |  | CDC | 310 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 11 | 11kV | XW34_LCO | 南十四線(XW34) LCO |  | TapPosMv | [17 empty] | 2-32-04 |  | 2-21 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW34_LCO_TAP | 11KV南十四線(XW34) LCO TAP | FEEDER | D08/11/XW34/ADJ |  |  |  | CDC | 311 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D08 | 斗南DS | 11 | 11kV | XW34 | XW34(11KV南十四線) |  | CB | [17 empty] | 1-19-00 |  | 1-28 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW34_CB | XW34(11KV南十四線) CB | FEEDER | D08/11/XW34/CB |  |  |  | CDC | 312 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | XW35 | 南十五線(XW35) |  | PHA | [17 empty] | 1-19-04 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW35_PHA | 11KV南十五線(XW35) 相間RY | FEEDER | D08/11/XW35/PHA |  |  |  | CDC | 313 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW35 | 南十五線(XW35) |  | GDA | [17 empty] | 1-19-05 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW35_GDA | 11KV南十五線(XW35) 接地RY | FEEDER | D08/11/XW35/GDA |  |  |  | CDC | 314 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW35 | 南十五線(XW35) 79RY |  | 79UL | [17 empty] | 2-32-05 |  | 2-22 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW35_79UL | 11KV南十五線(XW35) 79RY U/L | FEEDER | D08/11/XW35/79UL |  |  |  | CDC | 315 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 11 | 11kV | XW35_LCO | 南十五線(XW35) LCO |  | TapPosMv | [17 empty] | 2-32-06 |  | 2-23 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW35_LCO_TAP | 11KV南十五線(XW35) LCO TAP | FEEDER | D08/11/XW35/ADJ |  |  |  | CDC | 316 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D08 | 斗南DS | 11 | 11kV | XW35 | XW35(11KV南十五線) |  | CB | [17 empty] | 1-19-03 |  | 1-29 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW35_CB | XW35(11KV南十五線) CB | FEEDER | D08/11/XW35/CB |  |  |  | CDC | 317 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | XW36 | 南十六線(XW36) |  | PHA | [17 empty] | 1-1C-04 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW36_PHA | 11KV南十六線(XW36) 相間RY | FEEDER | D08/11/XW36/PHA |  |  |  | CDC | 318 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW36 | 南十六線(XW36) |  | GDA | [17 empty] | 1-1C-05 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW36_GDA | 11KV南十六線(XW36) 接地RY | FEEDER | D08/11/XW36/GDA |  |  |  | CDC | 319 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW36 | 南十六線(XW36) 79RY |  | 79UL | [17 empty] | 2-33-01 |  | 2-2E | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW36_79UL | 11KV南十六線(XW36) 79RY U/L | FEEDER | D08/11/XW36/79UL |  |  |  | CDC | 320 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 11 | 11kV | XW36_LCO | 南十六線(XW36) LCO |  | TapPosMv | [17 empty] | 2-33-02 |  | 2-2F | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW36_LCO_TAP | 11KV南十六線(XW36) LCO TAP | FEEDER | D08/11/XW36/ADJ |  |  |  | CDC | 321 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D08 | 斗南DS | 11 | 11kV | XW36 | XW36(11KV南十六線) |  | CB | [17 empty] | 1-1C-03 |  | 1-32 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW36_CB | XW36(11KV南十六線) CB | FEEDER | D08/11/XW36/CB |  |  |  | CDC | 322 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | XW37 | 南十七線(XW37) |  | PHA | [17 empty] | 1-1D-02 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW37_PHA | 11KV南十七線(XW37) 相間RY | FEEDER | D08/11/XW37/PHA |  |  |  | CDC | 323 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW37 | 南十七線(XW37) |  | GDA | [17 empty] | 1-1D-03 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW37_GDA | 11KV南十七線(XW37) 接地RY | FEEDER | D08/11/XW37/GDA |  |  |  | CDC | 324 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW37 | 南十七線(XW37) 79RY |  | 79UL | [17 empty] | 2-33-03 |  | 2-30 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW37_79UL | 11KV南十七線(XW37) 79RY U/L | FEEDER | D08/11/XW37/79UL |  |  |  | CDC | 325 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 11 | 11kV | XW37_LCO | 南十七線(XW37) LCO |  | TapPosMv | [17 empty] | 2-33-04 |  | 2-31 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW37_LCO_TAP | 11KV南十七線(XW37) LCO TAP | FEEDER | D08/11/XW37/ADJ |  |  |  | CDC | 326 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D08 | 斗南DS | 11 | 11kV | XW37 | XW37(11KV南十七線) |  | CB | [17 empty] | 1-1D-01 |  | 1-35 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW37_CB | XW37(11KV南十七線) CB | FEEDER | D08/11/XW37/CB |  |  |  | CDC | 327 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | XW38 | 南十八線(XW38) |  | PHA | [17 empty] | 1-1D-05 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW38_PHA | 11KV南十八線(XW38) 相間RY | FEEDER | D08/11/XW38/PHA |  |  |  | CDC | 328 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW38 | 南十八線(XW38) |  | GDA | [17 empty] | 1-1D-06 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW38_GDA | 11KV南十八線(XW38) 接地RY | FEEDER | D08/11/XW38/GDA |  |  |  | CDC | 329 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW38 | 南十八線(XW38) 79RY |  | 79UL | [17 empty] | 2-33-05 |  | 2-32 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW38_79UL | 11KV南十八線(XW38) 79RY U/L | FEEDER | D08/11/XW38/79UL |  |  |  | CDC | 330 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 11 | 11kV | XW38_LCO | 南十八線(XW38) LCO |  | TapPosMv | [17 empty] | 2-33-06 |  | 2-33 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW38_LCO_TAP | 11KV南十八線(XW38) LCO TAP | FEEDER | D08/11/XW38/ADJ |  |  |  | CDC | 331 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D08 | 斗南DS | 11 | 11kV | XW38 | XW38(11KV南十八線) |  | CB | [17 empty] | 1-1D-04 |  | 1-36 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW38_CB | XW38(11KV南十八線) CB | FEEDER | D08/11/XW38/CB |  |  |  | CDC | 332 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | XW39 | 南十九線(XW39) |  | PHA | [17 empty] | 1-1E-00 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW39_PHA | 11KV南十九線(XW39) 相間RY | FEEDER | D08/11/XW39/PHA |  |  |  | CDC | 333 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW39 | 南十九線(XW39) |  | GDA | [17 empty] | 1-1E-01 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW39_GDA | 11KV南十九線(XW39) 接地RY | FEEDER | D08/11/XW39/GDA |  |  |  | CDC | 334 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW39 | 南十九線(XW39) 79RY |  | 79UL | [17 empty] | 2-33-07 |  | 2-34 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW39_79UL | 11KV南十九線(XW39) 79RY U/L | FEEDER | D08/11/XW39/79UL |  |  |  | CDC | 335 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 11 | 11kV | XW39_LCO | 南十九線(XW39) LCO |  | TapPosMv | [17 empty] | 2-33-08 |  | 2-35 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW39_LCO_TAP | 11KV南十九線(XW39) LCO TAP | FEEDER | D08/11/XW39/ADJ |  |  |  | CDC | 336 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D08 | 斗南DS | 11 | 11kV | XW39 | XW39(11KV南十九線) |  | CB | [17 empty] | 1-1D-07 |  | 1-37 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW39_CB | XW39(11KV南十九線) CB | FEEDER | D08/11/XW39/CB |  |  |  | CDC | 337 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | XW40 | 南二十線(XW40) |  | PHA | [17 empty] | 1-1E-03 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW40_PHA | 11KV南二十線(XW40) 相間RY | FEEDER | D08/11/XW41/PHA |  |  |  | CDC | 338 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW40 | 南二十線(XW40) |  | GDA | [17 empty] | 1-1E-04 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW40_GDA | 11KV南二十線(XW40) 接地RY | FEEDER | D08/11/XW41/GDA |  |  |  | CDC | 339 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | XW40 | 南二十線(XW40) 79RY |  | 79UL | [17 empty] | 2-33-09 |  | 2-36 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW40_79UL | 11KV南二十線(XW40) 79RY U/L | FEEDER | D08/11/XW41/79UL |  |  |  | CDC | 340 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 11 | 11kV | XW40_LCO | 南二十線(XW40) LCO |  | TapPosMv | [17 empty] | 2-33-10 |  | 2-37 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW40_LCO_TAP | 11KV南二十線(XW40) LCO TAP | FEEDER | D08/11/XW41/ADJ |  |  |  | CDC | 341 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D08 | 斗南DS | 11 | 11kV | XW40 | XW40(11KV南二十線) |  | CB | [17 empty] | 1-1E-02 |  | 1-38 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW40_CB | XW40(11KV南二十線) CB | FEEDER | D08/11/XW41/CB |  |  |  | CDC | 342 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | XW61 | 南六一線(XW61) |  | PHA | [17 empty] | 1-14-02 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW61_PHA | 23KV南六一線(XW61) 相間RY | FEEDER | D08/22/XW61/PHA |  |  |  | CDC | 343 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW61 | 南六一線(XW61) |  | GDA | [17 empty] | 1-14-03 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW61_GDA | 23KV南六一線(XW61) 接地RY | FEEDER | D08/22/XW61/GDA |  |  |  | CDC | 344 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW61 | 南六一線(XW61) 79RY |  | 79UL | [17 empty] | 2-31-03 |  | 2-10 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW61_79UL | 23KV南六一線(XW61) 79RY U/L | FEEDER | D08/22/XW61/79UL |  |  |  | CDC | 345 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 22 | 22kV | XW61_LCO | 南六一線(XW61) LCO |  | TapPosMv | [17 empty] | 2-31-04 |  | 2-11 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW61_LCO_TAP | 23KV南六一線(XW61) LCO TAP | FEEDER | D08/22/XW61/ADJ |  |  |  | CDC | 346 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D08 | 斗南DS | 22 | 22kV | XW61 | XW61(23KV南六一線) |  | CB | [17 empty] | 1-14-01 |  | 1-1A | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW61_CB | XW61(23KV南六一線) CB | FEEDER | D08/22/XW61/CB |  |  |  | CDC | 347 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | XW62 | 南六二線(XW62) |  | PHA | [17 empty] | 1-14-05 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW62_PHA | 23KV南六二線(XW62) 相間RY | FEEDER | D08/22/XW62/PHA |  |  |  | CDC | 348 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW62 | 南六二線(XW62) |  | GDA | [17 empty] | 1-14-06 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW62_GDA | 23KV南六二線(XW62) 接地RY | FEEDER | D08/22/XW62/GDA |  |  |  | CDC | 349 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW62 | 南六二線(XW62) 79RY |  | 79UL | [17 empty] | 2-31-05 |  | 2-12 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW62_79UL | 23KV南六二線(XW62) 79RY U/L | FEEDER | D08/22/XW62/79UL |  |  |  | CDC | 350 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 22 | 22kV | XW62_LCO | 南六二線(XW62) LCO |  | TapPosMv | [17 empty] | 2-31-06 |  | 2-13 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW62_LCO_TAP | 23KV南六二線(XW62) LCO TAP | FEEDER | D08/22/XW62/ADJ |  |  |  | CDC | 351 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D08 | 斗南DS | 22 | 22kV | XW62 | XW62(23KV南六二線) |  | CB | [17 empty] | 1-14-04 |  | 1-1B | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW62_CB | XW62(23KV南六二線) CB | FEEDER | D08/22/XW62/CB |  |  |  | CDC | 352 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | XW63 | 南六三線(XW63) |  | PHA | [17 empty] | 1-15-03 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW63_PHA | 23KV南六三線(XW63) 相間RY | FEEDER | D08/22/XW63/PHA |  |  |  | CDC | 353 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW63 | 南六三線(XW63) |  | GDA | [17 empty] | 1-15-04 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW63_GDA | 23KV南六三線(XW63) 接地RY | FEEDER | D08/22/XW63/GDA |  |  |  | CDC | 354 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW63 | 南六三線(XW63) 79RY |  | 79UL | [17 empty] | 2-31-07 |  | 2-14 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW63_79UL | 23KV南六三線(XW63) 79RY U/L | FEEDER | D08/22/XW63/79UL |  |  |  | CDC | 355 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 22 | 22kV | XW63_LCO | 南六三線(XW63) LCO |  | TapPosMv | [17 empty] | 2-31-08 |  | 2-15 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW63_LCO_TAP | 23KV南六三線(XW63) LCO TAP | FEEDER | D08/22/XW63/ADJ |  |  |  | CDC | 356 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D08 | 斗南DS | 22 | 22kV | XW63 | XW63(23KV南六三線) |  | CB | [17 empty] | 1-15-02 |  | 1-1D | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW63_CB | XW63(23KV南六三線) CB | FEEDER | D08/22/XW63/CB |  |  |  | CDC | 357 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | XW64 | 南六四線(XW64) |  | PHA | [17 empty] | 1-15-06 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW64_PHA | 23KV南六四線(XW64) 相間RY | FEEDER | D08/22/XW64/PHA |  |  |  | CDC | 358 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW64 | 南六四線(XW64) |  | GDA | [17 empty] | 1-15-07 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW64_GDA | 23KV南六四線(XW64) 接地RY | FEEDER | D08/22/XW64/GDA |  |  |  | CDC | 359 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW64 | 南六四線(XW64) 79RY |  | 79UL | [17 empty] | 2-31-09 |  | 2-16 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW64_79UL | 23KV南六四線(XW64) 79RY U/L | FEEDER | D08/22/XW64/79UL |  |  |  | CDC | 360 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 22 | 22kV | XW64_LCO | 南六四線(XW64) LCO |  | TapPosMv | [17 empty] | 2-31-10 |  | 2-17 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW64_LCO_TAP | 23KV南六四線(XW64) LCO TAP | FEEDER | D08/22/XW64/ADJ |  |  |  | CDC | 361 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D08 | 斗南DS | 22 | 22kV | XW64 | XW64(23KV南六四線) |  | CB | [17 empty] | 1-15-05 |  | 1-1E | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW64_CB | XW64(23KV南六四線) CB | FEEDER | D08/22/XW64/CB |  |  |  | CDC | 362 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | XW65 | 南六五線(XW65) |  | PHA | [17 empty] | 1-16-01 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW65_PHA | 23KV南六五線(XW65) 相間RY | FEEDER | D08/22/XW65/PHA |  |  |  | CDC | 363 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW65 | 南六五線(XW65) |  | GDA | [17 empty] | 1-16-02 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW65_GDA | 23KV南六五線(XW65) 接地RY | FEEDER | D08/22/XW65/GDA |  |  |  | CDC | 364 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW65 | 南六五線(XW65) 79RY |  | 79UL | [17 empty] | 2-31-11 |  | 2-18 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW65_79UL | 23KV南六五線(XW65) 79RY U/L | FEEDER | D08/22/XW65/79UL |  |  |  | CDC | 365 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 22 | 22kV | XW65_LCO | 南六五線(XW65) LCO |  | TapPosMv | [17 empty] | 2-31-12 |  | 2-19 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW65_LCO_TAP | 23KV南六五線(XW65) LCO TAP | FEEDER | D08/22/XW65/ADJ |  |  |  | CDC | 366 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D08 | 斗南DS | 22 | 22kV | XW65 | XW65(23KV南六五線) |  | CB | [17 empty] | 1-16-00 |  | 1-1F | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW65_CB | XW65(23KV南六五線) CB | FEEDER | D08/22/XW65/CB |  |  |  | CDC | 367 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | XW71 | 南七一線(XW71) |  | PHA | [17 empty] | 1-19-07 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW71_PHA | 23KV南七一線(XW71) 相間RY | FEEDER | D08/22/XW71/PHA |  |  |  | CDC | 368 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW71 | 南七一線(XW71) |  | GDA | [17 empty] | 1-1A-00 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW71_GDA | 23KV南七一線(XW71) 接地RY | FEEDER | D08/22/XW71/GDA |  |  |  | CDC | 369 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW71 | 南七一線(XW71) 79RY |  | 79UL | [17 empty] | 2-32-07 |  | 2-24 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW71_79UL | 23KV南七一線(XW71) 79RY U/L | FEEDER | D08/22/XW71/79UL |  |  |  | CDC | 370 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 22 | 22kV | XW71_LCO | 南七一線(XW71) LCO |  | TapPosMv | [17 empty] | 2-32-08 |  | 2-25 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW71_LCO_TAP | 23KV南七一線(XW71) LCO TAP | FEEDER | D08/22/XW71/ADJ |  |  |  | CDC | 371 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D08 | 斗南DS | 22 | 22kV | XW71 | XW71(23KV南七一線) |  | CB | [17 empty] | 1-19-06 |  | 1-2A | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW71_CB | XW71(23KV南七一線) CB | FEEDER | D08/22/XW71/CB |  |  |  | CDC | 372 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | XW72 | 南七二線(XW72) |  | PHA | [17 empty] | 1-1A-02 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW72_PHA | 23KV南七二線(XW72) 相間RY | FEEDER | D08/22/XW72/PHA |  |  |  | CDC | 373 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW72 | 南七二線(XW72) |  | GDA | [17 empty] | 1-1A-03 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW72_GDA | 23KV南七二線(XW72) 接地RY | FEEDER | D08/22/XW72/GDA |  |  |  | CDC | 374 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW72 | 南七二線(XW72) 79RY |  | 79UL | [17 empty] | 2-32-09 |  | 2-26 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW72_79UL | 23KV南七二線(XW72) 79RY U/L | FEEDER | D08/22/XW72/79UL |  |  |  | CDC | 375 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 22 | 22kV | XW72_LCO | 南七二線(XW72) LCO |  | TapPosMv | [17 empty] | 2-32-10 |  | 2-27 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW72_LCO_TAP | 23KV南七二線(XW72) LCO TAP | FEEDER | D08/22/XW72/ADJ |  |  |  | CDC | 376 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D08 | 斗南DS | 22 | 22kV | XW72 | XW72(23KV南七二線) |  | CB | [17 empty] | 1-1A-01 |  | 1-2B | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW72_CB | XW72(23KV南七二線) CB | FEEDER | D08/22/XW72/CB |  |  |  | CDC | 377 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | XW73 | 南七三線(XW73) |  | PHA | [17 empty] | 1-1B-03 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW73_PHA | 23KV南七三線(XW73) 相間RY | FEEDER | D08/22/XW73/PHA |  |  |  | CDC | 378 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW73 | 南七三線(XW73) |  | GDA | [17 empty] | 1-1B-04 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW73_GDA | 23KV南七三線(XW73) 接地RY | FEEDER | D08/22/XW73/GDA |  |  |  | CDC | 379 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW73 | 南七三線(XW73) 79RY |  | 79UL | [17 empty] | 2-32-11 |  | 2-28 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW73_79UL | 23KV南七三線(XW73) 79RY U/L | FEEDER | D08/22/XW73/79UL |  |  |  | CDC | 380 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 22 | 22kV | XW73_LCO | 南七三線(XW73) LCO |  | TapPosMv | [17 empty] | 2-32-12 |  | 2-29 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW73_LCO_TAP | 23KV南七三線(XW73) LCO TAP | FEEDER | D08/22/XW73/ADJ |  |  |  | CDC | 381 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D08 | 斗南DS | 22 | 22kV | XW73 | XW73(23KV南七三線) |  | CB | [17 empty] | 1-1B-02 |  | 1-2F | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW73_CB | XW73(23KV南七三線) CB | FEEDER | D08/22/XW73/CB |  |  |  | CDC | 382 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | XW74 | 南七四線(XW74) |  | PHA | [17 empty] | 1-1B-06 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW74_PHA | 23KV南七四線(XW74) 相間RY | FEEDER | D08/22/XW74/PHA |  |  |  | CDC | 383 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW74 | 南七四線(XW74) |  | GDA | [17 empty] | 1-1B-07 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW74_GDA | 23KV南七四線(XW74) 接地RY | FEEDER | D08/22/XW74/GDA |  |  |  | CDC | 384 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW74 | 南七四線(XW74) 79RY |  | 79UL | [17 empty] | 2-32-13 |  | 2-2A | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW74_79UL | 23KV南七四線(XW74) 79RY U/L | FEEDER | D08/22/XW74/79UL |  |  |  | CDC | 385 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 22 | 22kV | XW74_LCO | 南七四線(XW74) LCO |  | TapPosMv | [17 empty] | 2-32-14 |  | 2-2B | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW74_LCO_TAP | 23KV南七四線(XW74) LCO TAP | FEEDER | D08/22/XW74/ADJ |  |  |  | CDC | 386 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D08 | 斗南DS | 22 | 22kV | XW74 | XW74(23KV南七四線) |  | CB | [17 empty] | 1-1B-05 |  | 1-30 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW74_CB | XW74(23KV南七四線) CB | FEEDER | D08/22/XW74/CB |  |  |  | CDC | 387 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | XW75 | 南七五線(XW75) |  | PHA | [17 empty] | 1-1C-01 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW75_PHA | 23KV南七五線(XW75) 相間RY | FEEDER | D08/22/XW75/PHA |  |  |  | CDC | 388 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW75 | 南七五線(XW75) |  | GDA | [17 empty] | 1-1C-02 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW75_GDA | 23KV南七五線(XW75) 接地RY | FEEDER | D08/22/XW75/GDA |  |  |  | CDC | 389 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | XW75 | 南七五線(XW75) 79RY |  | 79UL | [17 empty] | 2-32-15 |  | 2-2C | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW75_79UL | 23KV南七五線(XW75) 79RY U/L | FEEDER | D08/22/XW75/79UL |  |  |  | CDC | 390 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 22 | 22kV | XW75_LCO | 南七五線(XW75) LCO |  | TapPosMv | [17 empty] | 2-33-00 |  | 2-2D | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW75_LCO_TAP | 23KV南七五線(XW75) LCO TAP | FEEDER | D08/22/XW75/ADJ |  |  |  | CDC | 391 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D08 | 斗南DS | 22 | 22kV | XW75 | XW75(23KV南七五線) |  | CB | [17 empty] | 1-1C-00 |  | 1-31 | [5 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW75_CB | XW75(23KV南七五線) CB | FEEDER | D08/22/XW75/CB |  |  |  | CDC | 392 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [17 empty] | 1-05-00 |  | 1-09 | [5 empty] | 161KV_N | [8 empty] | 斗南DS.1500_CB | 1500(TIE) CB | TIE | D08/161/1500/CB |  |  |  | CDC | 393 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | 1500 | TIE(1500) |  | 50A | [17 empty] | 1-05-01 | [7 empty] | 161KV_N | [8 empty] | 斗南DS.1500_50A | 161KV TIE(1500) 50RY | TIE | D08/161/1500/50A |  |  |  | CDC | 394 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [16 empty] | 1-3C-00 | 1-3C-01 | 1-78 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.1501_DS | 1501(TIE) DS | TIE | D08/161/1500/DS1 |  |  |  | CDC | 395 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D08 | 斗南DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [16 empty] | 1-3C-02 | 1-3C-03 | 1-79 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.1502_DS | 1502(TIE) DS | TIE | D08/161/1500/DS2 |  |  |  | CDC | 396 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D08 | 斗南DS | 0 |  | 300 | TIE(300) |  | CB | [17 empty] | 1-17-04 |  | 1-24 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.300_CB | 300(TIE) CB | TIE | D08/22/300/CB |  |  |  | CDC | 397 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | 300 | TIE(300) |  | 51A | [17 empty] | 1-17-05 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.300_51A | 23KV TIE(300) 51RY | TIE | D08/22/300/PHA |  |  |  | CDC | 398 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 300 | TIE(300) |  | 51NA | [17 empty] | 1-17-06 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.300_51NA | 23KV TIE(300) 51N RY | TIE | D08/22/300/GDA |  |  |  | CDC | 399 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 400 | TIE(400) |  | CB | [17 empty] | 1-1A-07 |  | 1-2E | [5 empty] | ADCS_N | [8 empty] | 斗南DS.400_CB | 400(TIE) CB | TIE | D08/11/400/CB |  |  |  | CDC | 400 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | 400 | TIE(400) |  | 51A | [17 empty] | 1-1B-00 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.400_51A | 11KV TIE(400) 51RY | TIE | D08/11/400/PHA |  |  |  | CDC | 401 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 400 | TIE(400) |  | 51NA | [17 empty] | 1-1B-01 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.400_51NA | 11KV TIE(400) 51N RY | TIE | D08/11/400/GDA |  |  |  | CDC | 402 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 390 | #1SSTR(390) |  | CB | [17 empty] | 1-10-00 |  | 1-0D | [5 empty] | 161KV_N | [8 empty] | 斗南DS.390_CB | 390(#1SSTR) CB | OTHER | D08/11/390/CB |  |  |  | CDC | 403 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | 1SSTR | #1SSTR |  | 51A | [17 empty] | 1-10-01 | [7 empty] | 161KV_N | [8 empty] | 斗南DS.#1SSTR_51A | #1SSTR 51RY | OTHER | D08/11/390/PHA |  |  |  | CDC | 404 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 1SSTR | #1SSTR |  | 51NA | [17 empty] | 1-10-02 | [7 empty] | 161KV_N | [8 empty] | 斗南DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | D08/11/390/GDA |  |  |  | CDC | 405 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 490 | #2SSTR(490) |  | CB | [17 empty] | 1-18-02 |  | 1-26 | [5 empty] | 161KV_N | [8 empty] | 斗南DS.490_CB | 490(#2SSTR) CB | OTHER | D08/11/490/CB |  |  |  | CDC | 406 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | 2SSTR | #2SSTR |  | 51A | [17 empty] | 1-18-03 | [7 empty] | 161KV_N | [8 empty] | 斗南DS.#2SSTR_51A | #2SSTR 51RY | OTHER | D08/11/490/PHA |  |  |  | CDC | 407 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 2SSTR | #2SSTR |  | 51NA | [17 empty] | 1-18-04 | [7 empty] | 161KV_N | [8 empty] | 斗南DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | D08/11/490/GDA |  |  |  | CDC | 408 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB | [17 empty] | 1-07-06 |  | 1-0B | [5 empty] | 161KV_N | [8 empty] | 斗南DS.1760_CB | 1760(#2DTR) CB | MTR | D08/161/1760/CB |  |  |  | CDC | 409 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | 330 | #2DTR(330) |  | CB | [17 empty] | 1-08-06 |  | 1-23 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.330_CB | 330(#2DTR) CB | MTR | D08/22/330/CB |  |  |  | CDC | 410 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | 340 | #2DTR(340) |  | CB | [17 empty] | 1-09-01 |  | 1-2D | [5 empty] | ADCS_N | [8 empty] | 斗南DS.340_CB | 340(#2DTR) CB | MTR | D08/11/340/CB |  |  |  | CDC | 411 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | 330 | #2DTR(330) |  | 51A | [17 empty] | 1-08-04 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.330_51A | #2DTR二次側(330) 51RY | MTR | D08/22/330/51A |  |  |  | CDC | 412 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 340 | #2DTR(340) |  | 51A | [17 empty] | 1-08-05 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.340_51A | #2DTR二次側(340) 51RY | MTR | D08/11/340/51A |  |  |  | CDC | 413 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 | [16 empty] | 1-3C-08 | 1-3C-09 | 1-7C | [5 empty] | ADCS_N | [8 empty] | 斗南DS.1761_DS | 1761(#2DTR) DS | MTR | D08/161/1760/DS1 |  |  |  | CDC | 414 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D08 | 斗南DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 | [16 empty] | 1-3C-10 | 1-3C-11 | 1-7D | [5 empty] | ADCS_N | [8 empty] | 斗南DS.1762_DS | 1762(#2DTR) DS | MTR | D08/161/1760/DS2 |  |  |  | CDC | 415 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D08 | 斗南DS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB | [17 empty] | 1-09-04 |  | 1-0C | [5 empty] | 161KV_N | [8 empty] | 斗南DS.1770_CB | 1770(#3DTR) CB | MTR | D08/161/1770/CB |  |  |  | CDC | 416 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | 350 | #3DTR(350) |  | CB | [17 empty] | 1-0A-04 |  | 1-34 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.350_CB | 350(#3DTR) CB | MTR | D08/22/350/CB |  |  |  | CDC | 417 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | 360 | #3DTR(360) |  | CB | [17 empty] | 1-0A-07 |  | 1-3A | [5 empty] | ADCS_N | [8 empty] | 斗南DS.360_CB | 360(#3DTR) CB | MTR | D08/11/360/CB |  |  |  | CDC | 418 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | 350 | #3DTR(350) |  | 51A | [17 empty] | 1-0A-02 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.350_51A | #3DTR二次側(350) 51RY | MTR | D08/22/350/51A |  |  |  | CDC | 419 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 360 | #3DTR(360) |  | 51A | [17 empty] | 1-0A-03 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.360_51A | #3DTR二次側(360) 51RY | MTR | D08/11/360/51A |  |  |  | CDC | 420 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 | [16 empty] | 1-3C-12 | 1-3C-13 | 1-7E | [5 empty] | ADCS_N | [8 empty] | 斗南DS.1771_DS | 1771(#3DTR) DS | MTR | D08/161/1770/DS1 |  |  |  | CDC | 421 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D08 | 斗南DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 | [16 empty] | 1-3C-14 | 1-3C-15 | 1-7F | [5 empty] | ADCS_N | [8 empty] | 斗南DS.1772_DS | 1772(#3DTR) DS | MTR | D08/161/1770/DS2 |  |  |  | CDC | 422 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D08 | 斗南DS | 11 | 11kV | 240 | #4SC(240) |  | CB | [17 empty] | 1-1A-04 |  | 1-2C | [5 empty] | ADCS_N | [8 empty] | 斗南DS.240_CB | 240(11KV #4SC) CB | SC | D08/11/240/CB |  |  |  | CDC | 423 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | 240 | #4SC(240) |  | SCA | [17 empty] | 1-1A-05 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.240_SCA | 11KV #4SC 51,51N RY | SC | D08/11/240/SCA |  |  |  | CDC | 424 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | 240 | #4SC(240) |  | UVA | [17 empty] | 1-1A-06 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.240_UVA | 11KV #4SC 27RY(欠壓) | SC | D08/11/240/UVA |  |  |  | CDC | 425 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | 240 | #4SC(240) |  | LBS | [17 empty] | 2-36-02 | 2-36-03 | 2-3B | [5 empty] | ADCS_N | [8 empty] | 斗南DS.240_LBS | 240(11KV #4SC) LBS | SC | D08/11/240/LBS |  |  |  | CDC | 426 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D08 | 斗南DS | 11 | 11kV | 260 | #6SC(260) |  | CB | [17 empty] | 1-1E-05 |  | 1-39 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.260_CB | 260(11KV #6SC) CB | SC | D08/11/260/CB |  |  |  | CDC | 427 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 11 | 11kV | 260 | #6SC(260) |  | SCA | [17 empty] | 1-1E-06 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.260_SCA | 11KV #6SC 51,51N RY | SC | D08/11/260/SCA |  |  |  | CDC | 428 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | 260 | #6SC(260) |  | UVA | [17 empty] | 1-1E-07 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.260_UVA | 11KV #6SC 27RY(欠壓) | SC | D08/11/260/UVA |  |  |  | CDC | 429 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | 260 | #6SC(260) |  | LBS | [17 empty] | 2-36-06 | 2-36-07 | 2-3D | [5 empty] | ADCS_N | [8 empty] | 斗南DS.260_LBS | 260(11KV #6SC) LBS | SC | D08/11/260/LBS |  |  |  | CDC | 430 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D08 | 斗南DS | 22 | 22kV | 230 | #3SC(230) |  | CB | [17 empty] | 1-17-01 |  | 1-22 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.230_CB | 230(23KV #3SC) CB | SC | D08/22/230/CB |  |  |  | CDC | 431 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | 230 | #3SC(230) |  | SCA | [17 empty] | 1-17-02 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.230_SCA | 23KV #3SC 51,51N RY | SC | D08/22/230/SCA |  |  |  | CDC | 432 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | 230 | #3SC(230) |  | UVA | [17 empty] | 1-17-03 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.230_UVA | 23KV #3SC 27RY(欠壓) | SC | D08/22/230/UVA |  |  |  | CDC | 433 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | 250 | #5SC(250) |  | CB | [17 empty] | 1-1C-06 |  | 1-33 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.250_CB | 250(23KV #5SC) CB | SC | D08/22/250/CB |  |  |  | CDC | 434 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 22 | 22kV | 250 | #5SC(250) |  | SCA | [17 empty] | 1-1C-07 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.250_SCA | 23KV #5SC 51,51N RY | SC | D08/22/250/SCA |  |  |  | CDC | 435 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | 250 | #5SC(250) |  | UVA | [17 empty] | 1-1D-00 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.250_UVA | 23KV #5SC 27RY(欠壓) | SC | D08/22/250/UVA |  |  |  | CDC | 436 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1611BUS | #1BUS |  | VUA | [17 empty] | 1-35-15 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | D08/161/1BUS/BUS_VUA |  |  |  | CDC | 437 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1611BUS | #1BUS |  | 87A | [17 empty] | 1-05-02 | [7 empty] | 161KV_N | [8 empty] | 斗南DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | D08/161/1BUS/87A |  |  |  | CDC | 438 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1611BUS | #1BUS |  | 87UL | [17 empty] | 1-32-08 |  | 1-40 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | D08/161/1BUS/87UL |  |  |  | CDC | 439 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 161 | 161kV | 1612BUS | #2BUS |  | VUA | [17 empty] | 1-36-00 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | D08/161/2BUS/BUS_VUA |  |  |  | CDC | 440 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1612BUS | #2BUS |  | 87A | [17 empty] | 1-05-03 | [7 empty] | 161KV_N | [8 empty] | 斗南DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | D08/161/2BUS/87A |  |  |  | CDC | 441 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1612BUS | #2BUS |  | 87UL | [17 empty] | 1-32-09 |  | 1-41 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | D08/161/2BUS/87UL |  |  |  | CDC | 442 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 22 | 22kV | 11_ | 11/ |  | CBA | [17 empty] | 2-30-00 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | D08/0/ComPoint/CBA |  |  |  | CDC | 443 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | 11_ | 11/ |  | CBF | [17 empty] | 2-30-01 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | D08/0/ComPoint/CBF |  |  |  | CDC | 444 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV |  |  |  | CBA | [17 empty] | 1-36-06 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.161KV_CBA | 161KV斷路器重故障 | OTHER | D08/161/ComPoint/CBA |  |  |  | CDC | 445 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV |  |  |  | CBF | [17 empty] | 1-36-07 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | D08/161/ComPoint/CBF |  |  |  | CDC | 446 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV |  |  |  | OSCA | [17 empty] | 1-05-04 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.161KV_OSCA | 161KV示波器啟動警報 | OTHER | D08/161/ComPoint/OSCA |  |  |  | CDC | 447 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | LINE | LINE |  | RCA | [17 empty] | 1-05-05 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | D08/161/ComPoint/RCA |  |  |  | CDC | 448 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 22 | 22kV | _SC | 23/ SC |  | 60A | [17 empty] | 1-36-14 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.23KV_SC_60A | 23/11KV SC 60A | OTHER | D08/0/ComPoint/60A |  |  |  | CDC | 449 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | FEEDER | FEEDER |  | RCA | [17 empty] | 2-30-02 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.FEEDER_RCA | 饋線復閉電驛動作 | OTHER | D08/0/ComPoint/LOA |  |  |  | CDC | 450 | GENERICDIPoint | DS040_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.RTU_S/L | RTU SUPY/LOCAL | OTHER | D08/0/RTU/RTU_R_L |  |  |  | CDC | 451 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D08 | 斗南DS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.TEST_CB | TEST CB | OTHER | D08/0/RTU/Test_CB |  |  |  | CDC | 452 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  |  |  |  | Fire1 | [17 empty] | 1-35-00 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | D08/0/StaDev/Fire1 |  |  |  | CDC | 453 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 火災警報(2) | 火災警報(2) |  | Fire2 | [17 empty] | 1-35-01 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.火災警報(2) | 火災警報(2) SPARE | OTHER | D08/0/StaDev/Fire2 |  |  |  | CDC | 454 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 火災警報(3) | 火災警報(3) |  | Fire3 | [17 empty] | 1-35-02 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.火災警報(3) | 火災警報(3) SPARE | OTHER | D08/0/StaDev/Fire3 |  |  |  | CDC | 455 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  |  |  |  | SUBA | [17 empty] | 1-36-11 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.其他重故障 | 變電所內其他重故障 | OTHER | D08/0/StaDev/PSF |  |  |  | CDC | 456 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  |  |  |  | SUBF | [17 empty] | 1-36-12 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.其他輕故障 | 變電所內其他輕故障 | OTHER | D08/0/StaDev/PSA |  |  |  | CDC | 457 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  |  |  |  | ACB1 | [17 empty] | 1-35-12 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | D08/0/StaDev/ACB1 |  |  |  | CDC | 458 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
D08 | 斗南DS | 0 |  |  |  |  | ACB2 | [17 empty] | 1-35-13 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | D08/0/StaDev/ACB2 |  |  |  | CDC | 459 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
D08 | 斗南DS | 0 |  |  |  |  | ACBA | [17 empty] | 1-36-10 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.所內電源ACBA | 所內電源故障警報 | OTHER | D08/0/StaDev/ACBA |  |  |  | CDC | 460 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  |  |  |  | STUV | [17 empty] | 1-35-14 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | D08/0/StaDev/STUV |  |  |  | CDC | 461 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-36-02 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | D08/0/StaDev/CHG1 |  |  |  | CDC | 462 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  |  |  |  | DCA | [17 empty] | 1-36-01 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.直流電源DCA | 直流電源故障警報 | OTHER | D08/0/StaDev/DCA |  |  |  | CDC | 463 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  |  |  |  | DCE | [17 empty] | 1-36-04 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.直流電源DCE | 直流電源接地故障警報 | OTHER | D08/0/StaDev/DCE |  |  |  | CDC | 464 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-37-01 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | D08/0/StaDev/CHG2 |  |  |  | CDC | 465 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  |  |  |  | CommACF | [17 empty] | 1-37-02 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | D08/0/StaDev/CommACF |  |  |  | CDC | 466 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  |  |  |  | Burglar1 | [17 empty] | 1-35-03 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | D08/0/StaDev/Burglar1 |  |  |  | CDC | 467 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  |  |  |  | Door1 | [17 empty] | 1-35-06 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.無人化門禁(1) | 無人化門禁(1)建築物大門 | OTHER | D08/0/StaDev/Door1 |  |  |  | CDC | 468 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  |  |  |  | Door2 | [17 empty] | 1-35-07 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.無人化門禁(2) | 無人化門禁(2)控制室大門 | OTHER | D08/0/StaDev/Door2 |  |  |  | CDC | 469 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | 330 | #2DTR(330) |  | GDA | [17 empty] | 1-09-00 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.330_GDA | 330開關箱IED RY GDA | OTHER | D08/22/330/GDA |  |  |  | CDC | 470 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 330 | #2DTR(330) |  | PHA2 | [17 empty] | 1-08-07 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.330_PHA2 | 330開關箱IED RY PHA | OTHER | D08/22/330/PHA |  |  |  | CDC | 471 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 340 | #2DTR(340) |  | GDA | [17 empty] | 1-09-03 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.340_GDA | 340開關箱IED RY GDA | OTHER | D08/11/340/GDA |  |  |  | CDC | 472 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 340 | #2DTR(340) |  | PHA2 | [17 empty] | 1-09-02 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.340_PHA2 | 340開關箱IED RY PHA | OTHER | D08/11/340/PHA |  |  |  | CDC | 473 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 350 | #3DTR(350) |  | GDA | [17 empty] | 1-0A-06 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.350_GDA | 350開關箱IED RY GDA | OTHER | D08/22/350/GDA |  |  |  | CDC | 474 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 350 | #3DTR(350) |  | PHA2 | [17 empty] | 1-0A-05 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.350_PHA2 | 350開關箱IED RY PHA | OTHER | D08/22/350/PHA |  |  |  | CDC | 475 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 360 | #3DTR(360) |  | GDA | [17 empty] | 1-0B-01 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.360_GDA | 360開關箱IED RY GDA | OTHER | D08/11/360/GDA |  |  |  | CDC | 476 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 360 | #3DTR(360) |  | PHA2 | [17 empty] | 1-0B-00 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.360_PHA2 | 360開關箱IED RY PHA | OTHER | D08/11/360/PHA |  |  |  | CDC | 477 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 0 |  |  |  |  | 水位警報(1) | [17 empty] | 1-36-08 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.水位警報(1) | 地下室水位警報(1) | OTHER | D08/0/StaDev/Water1 |  |  |  | CDC | 478 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  |  |  |  | 水位警報(2) | [17 empty] | 1-36-09 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.水位警報(2) | 地下室水位警報(2) | OTHER | D08/0/StaDev/Water2 |  |  |  | CDC | 479 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  |  |  |  | 空調機故障 | [17 empty] | 1-36-13 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.空調機故障 | 空調機故障或電源跳脫 | OTHER | D08/0/StaDev/AIRCON |  |  |  | CDC | 480 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | NORMAL/FAULT | NORMAL
D08 | 斗南DS | 0 |  |  |  |  | 集油池警報(1) | [17 empty] | 1-36-15 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.集油池警報(1) | 集油池警報(1) | OTHER | D08/0/StaDev/OilLeak1 |  |  |  | CDC | 481 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  |  |  |  | 集油池警報(2) | [17 empty] | 1-37-00 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.集油池警報(2) | 集油池警報(2) | OTHER | D08/0/StaDev/OilLeak2 |  |  |  | CDC | 482 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 2DTR | #2DTR |  | 51A | [17 empty] | 1-08-02 | [7 empty] | 161KV_N | [8 empty] | 斗南DS.#2DTR_51A | #2DTR 51RY | MTR | D08/161/1760/PHA |  |  |  | CDC | 483 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 2DTR | #2DTR |  | 51NA | [17 empty] | 1-08-03 | [7 empty] | 161KV_N | [8 empty] | 斗南DS.#2DTR_51NA | #2DTR 51N RY | MTR | D08/161/1760/GDA |  |  |  | CDC | 484 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 2DTR | #2DTR |  | 51ZA | [17 empty] | 1-08-01 | [7 empty] | 161KV_N | [8 empty] | 斗南DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | D08//2DTR/51ZA |  |  |  | CDC | 485 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 2DTR | #2DTR |  | 87A | [17 empty] | 1-07-07 | [7 empty] | 161KV_N | [8 empty] | 斗南DS.#2DTR_87A | #2DTR 87RY | MTR | D08//2DTR/87A |  |  |  | CDC | 486 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 2DTR | #2DTR |  | 96PA | [17 empty] | 1-08-00 | [7 empty] | 161KV_N | [8 empty] | 斗南DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | D08//2DTR/96PA |  |  |  | CDC | 487 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 2DTR | #2DTR |  | 96D | [17 empty] | 1-33-13 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.#2DTR_96D | #2DTR 96D RY | MTR | D08//2DTR/96D |  |  |  | CDC | 488 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 2DTR | #2DTR |  | 96P | [17 empty] | 1-33-14 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.#2DTR_96P | #2DTR 96P RY | MTR | D08//2DTR/96P |  |  |  | CDC | 489 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 2DTR | #2DTR |  | 63Q | [17 empty] | 1-33-15 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.#2DTR_63Q | #2DTR 63Q RY | MTR | D08//2DTR/63Q |  |  |  | CDC | 490 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 2DTR | #2DTR |  | 96B1 | [17 empty] | 1-33-11 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | D08//2DTR/96B1 |  |  |  | CDC | 491 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 2DTR | #2DTR |  | 96B2 | [17 empty] | 1-33-12 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | D08//2DTR/96B2 |  |  |  | CDC | 492 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 2DTR | #2DTR |  | TRA | [17 empty] | 1-33-10 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.#2DTR_TRA | #2DTR 重故障 | MTR | D08//2DTR/TRA |  |  |  | CDC | 493 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 2DTR | #2DTR |  | TRF | [17 empty] | 1-33-09 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.#2DTR_TRF | #2DTR 輕故障 | MTR | D08//2DTR/TRF |  |  |  | CDC | 494 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 2DTR(A) | #2DTR(A) |  | SupLocal | [17 empty] | 1-33-05 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | D08//2DTR(A)/SupLocal |  |  |  | CDC | 495 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D08 | 斗南DS | 0 |  | 2DTR(A) | #2DTR(A) |  | A_M | [17 empty] | 1-33-06 |  | 1-50 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | D08//2DTR(A)/Tap Chan |  |  |  | CDC | 496 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D08 | 斗南DS | 0 |  | 2DTR(B) | #2DTR(B) |  | SupLocal | [17 empty] | 1-33-07 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | D08//2DTR(B)/SupLocal |  |  |  | CDC | 497 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D08 | 斗南DS | 0 |  | 2DTR(B) | #2DTR(B) |  | A_M | [17 empty] | 1-33-08 |  | 1-52 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | D08//2DTR(B)/Tap Chan |  |  |  | CDC | 498 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D08 | 斗南DS | 0 |  | 3DTR | #3DTR |  | 51A | [17 empty] | 1-0A-00 | [7 empty] | 161KV_N | [8 empty] | 斗南DS.#3DTR_51A | #3DTR 51RY | MTR | D08//3DTR/PHA |  |  |  | CDC | 499 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 3DTR | #3DTR |  | 51NA | [17 empty] | 1-0A-01 | [7 empty] | 161KV_N | [8 empty] | 斗南DS.#3DTR_51NA | #3DTR 51N RY | MTR | D08//3DTR/GDA |  |  |  | CDC | 500 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 3DTR | #3DTR |  | 51ZA | [17 empty] | 1-09-07 | [7 empty] | 161KV_N | [8 empty] | 斗南DS.#3DTR_51ZA | #3DTR 51Z RY | MTR | D08//3DTR/51ZA |  |  |  | CDC | 501 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 3DTR | #3DTR |  | 87A | [17 empty] | 1-09-05 | [7 empty] | 161KV_N | [8 empty] | 斗南DS.#3DTR_87A | #3DTR 87RY | MTR | D08//3DTR/87A |  |  |  | CDC | 502 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 3DTR | #3DTR |  | 96PA | [17 empty] | 1-09-06 | [7 empty] | 161KV_N | [8 empty] | 斗南DS.#3DTR_96PA | #3DTR 機械保護動作 | MTR | D08//3DTR/96PA |  |  |  | CDC | 503 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 3DTR | #3DTR |  | 96D | [17 empty] | 1-34-09 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.#3DTR_96D | #3DTR 96D RY | MTR | D08//3DTR/96D |  |  |  | CDC | 504 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 3DTR | #3DTR |  | 96P | [17 empty] | 1-34-10 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.#3DTR_96P | #3DTR 96P RY | MTR | D08//3DTR/96P |  |  |  | CDC | 505 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 3DTR | #3DTR |  | 63Q | [17 empty] | 1-34-11 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.#3DTR_63Q | #3DTR 63Q RY | MTR | D08//3DTR/63Q |  |  |  | CDC | 506 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 3DTR | #3DTR |  | 96B1 | [17 empty] | 1-34-07 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.#3DTR_96B1 | #3DTR 96B1 RY | MTR | D08//3DTR/96B1 |  |  |  | CDC | 507 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 3DTR | #3DTR |  | 96B2 | [17 empty] | 1-34-08 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.#3DTR_96B2 | #3DTR 96B2 RY | MTR | D08//3DTR/96B2 |  |  |  | CDC | 508 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 3DTR | #3DTR |  | TRA | [17 empty] | 1-34-06 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.#3DTR_TRA | #3DTR 重故障 | MTR | D08//3DTR/TRA |  |  |  | CDC | 509 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 3DTR | #3DTR |  | TRF | [17 empty] | 1-34-05 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.#3DTR_TRF | #3DTR 輕故障 | MTR | D08//3DTR/TRF |  |  |  | CDC | 510 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 3DTR(A) | #3DTR(A) |  | SupLocal | [17 empty] | 1-34-01 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.#3DTR(A)_S/L | #3DTR(A) OLTC S/L | MTR | D08//3DTR(A)/SupLocal |  |  |  | CDC | 511 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D08 | 斗南DS | 0 |  | 3DTR(A) | #3DTR(A) |  | A_M | [17 empty] | 1-34-02 |  | 1-54 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.#3DTR(A)_A/M | #3DTR(A) OLTC A/M | MTR | D08//3DTR(A)/Tap Chan |  |  |  | CDC | 512 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D08 | 斗南DS | 0 |  | 3DTR(B) | #3DTR(B) |  | SupLocal | [17 empty] | 1-34-03 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.#3DTR(B)_S/L | #3DTR(B) OLTC S/L | MTR | D08//3DTR(B)/SupLocal |  |  |  | CDC | 513 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D08 | 斗南DS | 0 |  | 3DTR(B) | #3DTR(B) |  | A_M | [17 empty] | 1-34-04 |  | 1-56 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.#3DTR(B)_A/M | #3DTR(B) OLTC A/M | MTR | D08//3DTR(B)/Tap Chan |  |  |  | CDC | 514 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D08 | 斗南DS | 0 |  | 1500TIE | 1500 |  | 50SA | [17 empty] | 1-36-03 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | D08/161/1500/50SA |  |  |  | CDC | 515 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | TEST/NORMAL | NORMAL
D08 | 斗南DS | 0 |  |  |  |  | 通信機房溫度 | [17 empty] | 1-37-05 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.通信機房溫度 | 通信機房溫度警報 | OTHER | D08/0/StaDev/R_Temp |  |  |  | CDC | 516 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV |  |  |  | OSCF | [17 empty] | 1-37-06 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | D08/161/ComPoint/OSCF |  |  |  | CDC | 517 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 81RY | 81RY |  | A/S(1) | [17 empty] | 1-1F-00 |  | 1-3B | [5 empty] | ADCS_N | [8 empty] | 斗南DS.81RY_A/S(1) | 360低頻電驛動作/復歸 | OTHER | D08/11/360/81AS |  |  |  | CDC | 518 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
D08 | 斗南DS | 0 |  | 81RY | 81RY |  | A/S(2) | [17 empty] | 1-1F-01 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.81RY_A/S(2) | XW33低頻電驛動作/復歸 | OTHER | D08/11/XW33/81AS |  |  |  | CDC | 519 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
D08 | 斗南DS | 0 |  | 81RY | 81RY |  | A/S(3) | [17 empty] | 1-1F-02 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.81RY_A/S(3) | XW34低頻電驛動作/復歸 | OTHER | D08/11/XW34/81AS |  |  |  | CDC | 520 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
D08 | 斗南DS | 0 |  | 81RY | 81RY |  | A/S(4) | [17 empty] | 1-1F-03 | [7 empty] | DDCS1_1 | [8 empty] | 斗南DS.81RY_A/S(4) | XW35低頻電驛動作/復歸 | OTHER | D08/11/XW35/81AS |  |  |  | CDC | 521 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
D08 | 斗南DS | 161 | 161kV | 1530 | 雲林斗南線(1530) |  | 87A | [17 empty] | 1-03-02 | [7 empty] | 161KV_N | [8 empty] | 斗南DS.1530_87A | 雲林斗南線(1530) 87RY | LINE161 | D08/161/1530/87A |  |  |  | CDC | 522 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1530 | 雲林斗南線(1530) |  | 87UL | [17 empty] | 1-30-12 |  | 1-48 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.1530_87UL | 雲林斗南線(1530) 87RY U/L | LINE161 | D08/161/1530/87UL |  |  |  | CDC | 523 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 0 |  | 1530 | 雲林斗南線(1530) |  | 87CFA | [17 empty] | 1-32-01 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.1530_87CFA | 雲林斗南線(1530) 87RY通訊故障 | OTHER | D08/161/1530/87CFA |  |  |  | CDC | 524 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 1530 | 雲林斗南線(1530) |  | RYFA | [17 empty] | 1-32-02 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.1530_RYFA | 雲林斗南線(1530) 數位電驛故障 | OTHER | D08/161/1530/RYFA |  |  |  | CDC | 525 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1510 | 斗南虎菁一路(1510) |  | PHA | [17 empty] | 1-02-02 | [7 empty] | 161KV_N | [8 empty] | 斗南DS.1510_PHA | 斗南虎菁一路(1510) 相間RY | LINE161 | D08/161/1510/PHA |  |  |  | CDC | 526 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1510 | 斗南虎菁一路(1510) |  | GDA | [17 empty] | 1-02-03 | [7 empty] | 161KV_N | [8 empty] | 斗南DS.1510_GDA | 斗南虎菁一路(1510) 接地RY | LINE161 | D08/161/1510/GDA |  |  |  | CDC | 527 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1510 | 斗南虎菁一路(1510) |  | 87A | [17 empty] | 1-02-00 | [7 empty] | 161KV_N | [8 empty] | 斗南DS.1510_87A | 斗南虎菁一路(1510) 87RY | LINE161 | D08/161/1510/87A |  |  |  | CDC | 528 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1510 | 斗南虎菁一路(1510) |  | 87UL | [17 empty] | 1-30-08 |  | 1-44 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.1510_87UL | 斗南虎菁一路(1510) 87RY U/L | LINE161 | D08/161/1510/87UL |  |  |  | CDC | 529 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 161 | 161kV | 1510 | 斗南虎菁一路(1510) |  | CB | [17 empty] | 1-01-07 |  | 1-04 | [5 empty] | 161KV_N | [8 empty] | 斗南DS.1510_CB | 1510(斗南虎菁一路) CB | LINE161 | D08/161/1510/CB |  |  |  | CDC | 530 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 161 | 161kV | 1510 | 斗南虎菁一路(1510) |  | 79UL | [17 empty] | 1-30-09 |  | 1-45 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.1510_79UL | 斗南虎菁一路(1510) 79RY U/L | LINE161 | D08/161/1510/79UL |  |  |  | CDC | 531 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 161 | 161kV | 1510 | 斗南虎菁一路(1510) |  | DS1 | 1511 | [16 empty] | 1-39-08 | 1-39-09 | 1-64 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.1511_DS | 1511(斗南虎菁一路) DS | LINE161 | D08/161/1510/DS1 |  |  |  | CDC | 532 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D08 | 斗南DS | 161 | 161kV | 1510 | 斗南虎菁一路(1510) |  | DS2 | 1512 | [16 empty] | 1-39-10 | 1-39-11 | 1-65 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.1512_DS | 1512(斗南虎菁一路) DS | LINE161 | D08/161/1510/DS2 |  |  |  | CDC | 533 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D08 | 斗南DS | 161 | 161kV | 1510 | 斗南虎菁一路(1510) |  | DS3 | 1513 | [16 empty] | 1-39-12 | 1-39-13 | 1-66 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.1513_DS | 1513(斗南虎菁一路) DS | LINE161 | D08/161/1510/DS3 |  |  |  | CDC | 534 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D08 | 斗南DS | 161 | 161kV | 1510 | 斗南虎菁一路(1510) |  | E3 | 1513E | [16 empty] | 1-39-14 | 1-39-15 | 1-67 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.1513E_ES | 1513E(斗南虎菁一路) ES | LINE161 | D08/161/1510/ES3 |  |  |  | CDC | 535 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D08 | 斗南DS | 161 | 161kV | 1520 | 斗南虎菁二路(1520) |  | PHA | [17 empty] | 1-02-07 | [7 empty] | 161KV_N | [8 empty] | 斗南DS.1520_PHA | 斗南虎菁二路(1520) 相間RY | LINE161 | D08/161/1520/PHA |  |  |  | CDC | 536 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1520 | 斗南虎菁二路(1520) |  | GDA | [17 empty] | 1-03-00 | [7 empty] | 161KV_N | [8 empty] | 斗南DS.1520_GDA | 斗南虎菁二路(1520) 接地RY | LINE161 | D08/161/1520/GDA |  |  |  | CDC | 537 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1520 | 斗南虎菁二路(1520) |  | 87A | [17 empty] | 1-02-05 | [7 empty] | 161KV_N | [8 empty] | 斗南DS.1520_87A | 斗南虎菁二路(1520) 87RY | LINE161 | D08/161/1520/87A |  |  |  | CDC | 538 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | 1520 | 斗南虎菁二路(1520) |  | 87UL | [17 empty] | 1-30-10 |  | 1-46 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.1520_87UL | 斗南虎菁二路(1520) 87RY U/L | LINE161 | D08/161/1520/87UL |  |  |  | CDC | 539 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 161 | 161kV | 1520 | 斗南虎菁二路(1520) |  | CB | [17 empty] | 1-02-04 |  | 1-05 | [5 empty] | 161KV_N | [8 empty] | 斗南DS.1520_CB | 1520(斗南虎菁二路) CB | LINE161 | D08/161/1520/CB |  |  |  | CDC | 540 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 161 | 161kV | 1520 | 斗南虎菁二路(1520) |  | 79UL | [17 empty] | 1-30-11 |  | 1-47 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.1520_79UL | 斗南虎菁二路(1520) 79RY U/L | LINE161 | D08/161/1520/79UL |  |  |  | CDC | 541 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 161 | 161kV | 1520 | 斗南虎菁二路(1520) |  | DS1 | 1521 | [16 empty] | 1-3A-00 | 1-3A-01 | 1-68 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.1521_DS | 1521(斗南虎菁二路) DS | LINE161 | D08/161/1520/DS1 |  |  |  | CDC | 542 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D08 | 斗南DS | 161 | 161kV | 1520 | 斗南虎菁二路(1520) |  | DS2 | 1522 | [16 empty] | 1-3A-02 | 1-3A-03 | 1-69 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.1522_DS | 1522(斗南虎菁二路) DS | LINE161 | D08/161/1520/DS2 |  |  |  | CDC | 543 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D08 | 斗南DS | 161 | 161kV | 1520 | 斗南虎菁二路(1520) |  | DS3 | 1523 | [16 empty] | 1-3A-04 | 1-3A-05 | 1-6A | [5 empty] | ADCS_N | [8 empty] | 斗南DS.1523_DS | 1523(斗南虎菁二路) DS | LINE161 | D08/161/1520/DS3 |  |  |  | CDC | 544 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D08 | 斗南DS | 161 | 161kV | 1520 | 斗南虎菁二路(1520) |  | E3 | 1523E | [16 empty] | 1-3A-06 | 1-3A-07 | 1-6B | [5 empty] | ADCS_N | [8 empty] | 斗南DS.1523E_ES | 1523E(斗南虎菁二路) ES | LINE161 | D08/161/1520/ES3 |  |  |  | CDC | 545 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D08 | 斗南DS | 0 |  | 1510 | 斗南虎菁一路(1510) |  | 87CFA | [17 empty] | 1-31-12 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.1510_87CFA | 斗南虎菁一路(1510)87RY通訊故障 | OTHER | D08/161/1510/87CFA |  |  |  | CDC | 546 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 1510 | 斗南虎菁一路(1510) |  | RYFA | [17 empty] | 1-31-11 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.1510_RYFA | 斗南虎菁一路(1510)數位電驛故障 | OTHER | D08/161/1510/RYFA |  |  |  | CDC | 547 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 1520 | 斗南虎菁二路(1520) |  | 87CFA | [17 empty] | 1-31-15 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.1520_87CFA | 斗南虎菁二路(1520)87RY通訊故障 | OTHER | D08/161/1520/87CFA |  |  |  | CDC | 548 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 1520 | 斗南虎菁二路(1520) |  | RYFA | [17 empty] | 1-31-14 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.1520_RYFA | 斗南虎菁二路(1520)數位電驛故障 | OTHER | D08/161/1520/RYFA |  |  |  | CDC | 549 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | BVS | BVS |  | RY | [17 empty] | 1-37-07 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.BVS_RY | BVS GRZ100 RY U/L | OTHER | D08/0/ComPoint/GRZ100 |  |  |  | CDC | 550 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | LOCK/USE | USE
D08 | 斗南DS | 0 |  |  |  |  | GEN | [17 empty] | 1-34-15 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.GEN | 緊急發電機運轉 | OTHER | D08/0/ComPoint/1A5Other |  |  |  | CDC | 551 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D08 | 斗南DS | 0 |  | 1540 | 斗南北勢線(1540) |  | 87A1 | [17 empty] | 1-03-07 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.1540_87A1 | 斗南北勢線(1540)第一套87RY | OTHER | D08/161/1540/87A1 |  |  |  | CDC | 552 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 1540 | 斗南北勢線(1540) |  | 87A2 | [17 empty] | 1-04-03 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.1540_87A2 | 斗南北勢線(1540)第二套87RY | OTHER | D08/161/1540/87A2 |  |  |  | CDC | 553 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 1540 | 斗南北勢線(1540) |  | 87CFA | [17 empty] | 1-32-04 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.1540_87CFA | 斗南北勢線(1540))87RY通訊故障 | OTHER | D08/161/1540/87CFA |  |  |  | CDC | 554 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 1540 | 斗南北勢線(1540) |  | 1_87UL1 | [17 empty] | 1-30-14 |  | 1-4A | [5 empty] | ADCS_N | [8 empty] | 斗南DS.1540_87UL1 | 斗南北勢線(1540)#1 87RY U/L | OTHER | D08/161/1540/1_87UL1 |  |  |  | CDC | 555 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 0 |  | 1540 | 斗南北勢線(1540) |  | 1_87UL2 | [17 empty] | 1-31-00 |  | 1-3E | [5 empty] | ADCS_N | [8 empty] | 斗南DS.1540_87UL2 | 斗南北勢線(1540)#2 87RY U/L | OTHER | D08/161/1540/1_87UL2 |  |  |  | CDC | 556 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 0 |  | 1540 | 斗南北勢線(1540) |  | RYFA | [17 empty] | 1-32-05 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.1540_RYFA | 斗南北勢線(1540)數位電驛故障 | OTHER | D08/161/1540/RYFA |  |  |  | CDC | 557 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | _BUS | BUS |  | 87CTFA | [17 empty] | 1-34-14 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.161KV_BUS_CTFA | 161KV BUS 87RY CT回路故障 | OTHER | D08/161/ComPoint/12B_CTFA |  |  |  | CDC | 558 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 161 | 161kV | _BUS | BUS |  | RYFA | [17 empty] | 1-34-13 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | D08/161/ComPoint/BUS_RYFA |  |  |  | CDC | 559 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 2BOLTC | #2BDTR |  | TAP連動 | [17 empty] | 1-1F-04 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.2BOLTC_TAP連動 | #2BDTR OLTC TAP連動,請確認處理 | OTHER | D08/11/ComPoint/OLTC_A |  |  |  | CDC | 560 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 2DTR | #2DTR |  | 51Z_UL | [17 empty] | 1-37-10 |  | 2-42 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.#2DTR_51ZUL | #2DTR 51ZRY U/L | OTHER | D08//2DTR/51Z_UL |  |  |  | CDC | 561 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 0 |  | 2DTR | #2DTR |  | DTR_86A | [17 empty] | 1-0B-03 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.#2DTR_86A | #2DTR 86A | OTHER | D08//2DTR/DTR_86A |  |  |  | CDC | 562 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 2DTR | #2DTR |  | 1_87UL1 | [17 empty] | 1-37-08 |  | 2-40 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.#2DTR_87UL1 | #2DTR #1 87RY U/L | OTHER | D08//2DTR/1_87UL1 |  |  |  | CDC | 563 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 0 |  | 2DTR | #2DTR |  | 1_87UL2 | [17 empty] | 1-37-09 |  | 2-41 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.#2DTR_87UL2 | #2DTR #2 87RY U/L | OTHER | D08//2DTR/1_87UL2 |  |  |  | CDC | 564 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 0 |  | 2DTR | #2DTR |  | RYFA | [17 empty] | 1-37-11 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.#2DTR_RYFA | #2DTR數位電驛故障 | OTHER | D08//2DTR/RYFA |  |  |  | CDC | 565 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 3DTR | #3DTR |  | 51Z_UL | [17 empty] | 1-37-14 |  | 2-45 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.#3DTR_51ZUL | #3DTR 51ZRY U/L | OTHER | D08//3DTR/51Z_UL |  |  |  | CDC | 566 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 0 |  | 3DTR | #3DTR |  | DTR_86A | [17 empty] | 1-0B-04 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.#3DTR_86A | #3DTR 86A | OTHER | D08//3DTR/DTR_86A |  |  |  | CDC | 567 | GENERICDIPoint | DS040_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | 3DTR | #3DTR |  | 1_87UL1 | [17 empty] | 1-37-12 |  | 2-43 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.#3DTR_87UL1 | #3DTR #1 87RY U/L | OTHER | D08//3DTR/1_87UL1 |  |  |  | CDC | 568 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 0 |  | 3DTR | #3DTR |  | 1_87UL2 | [17 empty] | 1-37-13 |  | 2-44 | [5 empty] | ADCS_N | [8 empty] | 斗南DS.#3DTR_87UL2 | #3DTR #2 87RY U/L | OTHER | D08//3DTR/1_87UL2 |  |  |  | CDC | 569 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D08 | 斗南DS | 0 |  | 3DTR | #3DTR |  | RYFA | [17 empty] | 1-37-15 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.#3DTR_RYFA | #3DTR數位電驛故障 | OTHER | D08//3DTR/RYFA |  |  |  | CDC | 570 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D08 | 斗南DS | 0 |  | OLTC | OLTC |  | OLTCA | [17 empty] | 1-34-12 | [7 empty] | ADCS_N | [8 empty] | 斗南DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | D08/0/ComPoint/OLTC_A |  |  |  | CDC | 571 | GENERICDIPoint | DS040_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D08 | 斗南DS | 11 | 11kV | 240_SC | #4SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 斗南DS.240_SC_CAP | 11KV#4SC 容量 | SC | [5 empty] | 572 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 11 | 11kV | 260_SC | #6SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 斗南DS.260_SC_CAP | 11KV#6SC 容量 | SC | [5 empty] | 573 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 22 | 22kV | 230_SC | #3SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 斗南DS.230_SC_CAP | 23KV#3SC 容量 | SC | [5 empty] | 574 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 22 | 22kV | 250_SC | #5SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 斗南DS.250_SC_CAP | 23KV#5SC 容量 | SC | [5 empty] | 575 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D08 | 斗南DS | 0 |  | TRD | 斗南DS |  | 141 | [25 empty] | TRAIN_AD | [8 empty] | 斗南DS.TRD_141 | 斗南DS NT #2BDTR 11KV_Hi_Limit | [6 empty] | 576 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D08 | 斗南DS | 0 |  | TRD | 斗南DS |  | 142 | [25 empty] | TRAIN_AD | [8 empty] | 斗南DS.TRD_142 | 斗南DS NT #2BDTR 11KV_Lo_Limit | [6 empty] | 577 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D08 | 斗南DS | 0 |  | TRD | 斗南DS |  | 143 | [25 empty] | TRAIN_AD | [8 empty] | 斗南DS.TRD_143 | 斗南DS NT #2ADTR 23KV_Hi_Limit | [6 empty] | 578 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D08 | 斗南DS | 0 |  | TRD | 斗南DS |  | 144 | [25 empty] | TRAIN_AD | [8 empty] | 斗南DS.TRD_144 | 斗南DS NT #2ADTR 23KV_Lo_Limit | [6 empty] | 579 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D08 | 斗南DS | 0 |  | TRD | 斗南DS |  | 145 | [25 empty] | TRAIN_AD | [8 empty] | 斗南DS.TRD_145 | 斗南DS NT #3ADTR 23KV_Hi_Limit | [6 empty] | 580 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D08 | 斗南DS | 0 |  | TRD | 斗南DS |  | 146 | [25 empty] | TRAIN_AD | [8 empty] | 斗南DS.TRD_146 | 斗南DS NT #3ADTR 23KV_Lo_Limit | [6 empty] | 581 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D08 | 斗南DS | 0 |  | TRD | 斗南DS |  | 147 | [25 empty] | TRAIN_AD | [8 empty] | 斗南DS.TRD_147 | 斗南DS NT #3BDTR 11KV_Hi_Limit | [6 empty] | 582 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D08 | 斗南DS | 0 |  | TRD | 斗南DS |  | 148 | [25 empty] | TRAIN_AD | [8 empty] | 斗南DS.TRD_148 | 斗南DS NT #3BDTR 11KV_Lo_Limit | [6 empty] | 583 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D08 | 斗南DS | 161 | 161kV | 1530 | 雲林斗南線(1530) |  | LE0 | 1530LE | [24 empty] | ADCS_N | [8 empty] | 斗南DS.1530LE | 1530LE (非取樣點) | LINE161 | D08/161/1530/LE0 |  |  |  |  | 584 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 161 | 161kV | 1530 | 雲林斗南線(1530) |  | BE0 | 1530BE | [24 empty] | ADCS_N | [8 empty] | 斗南DS.1530BE | 1530BE (非取樣點) | LINE161 | D08/161/1530/BE0 |  |  |  |  | 585 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 161 | 161kV | 1540 | 斗南北勢線(1540) |  | LE0 | 1540LE | [24 empty] | ADCS_N | [8 empty] | 斗南DS.1540LE | 1540LE (非取樣點) | LINE161 | D08/161/1540/LE0 |  |  |  |  | 586 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 161 | 161kV | 1540 | 斗南北勢線(1540) |  | BE0 | 1540BE | [24 empty] | ADCS_N | [8 empty] | 斗南DS.1540BE | 1540BE (非取樣點) | LINE161 | D08/161/1540/BE0 |  |  |  |  | 587 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | XW31 | XW31_DS |  | DS1 | XW31_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW31_DS | XW31_DS (非取樣點) | FEEDER | D08/11/XW31/DS |  |  |  |  | 588 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | XW31 | XW31_ES |  | LE0 | XW31_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW31_ES | XW31_ES (非取樣點) | FEEDER | D08/11/XW31/ES |  |  |  |  | 589 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | XW32 | XW32_DS |  | DS1 | XW32_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW32_DS | XW32_DS (非取樣點) | FEEDER | D08/11/XW32/DS |  |  |  |  | 590 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | XW32 | XW32_ES |  | LE0 | XW32_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW32_ES | XW32_ES (非取樣點) | FEEDER | D08/11/XW32/ES |  |  |  |  | 591 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | XW33 | XW33_DS |  | DS1 | XW33_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW33_DS | XW33_DS (非取樣點) | FEEDER | D08/11/XW33/DS |  |  |  |  | 592 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | XW33 | XW33_ES |  | LE0 | XW33_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW33_ES | XW33_ES (非取樣點) | FEEDER | D08/11/XW33/ES |  |  |  |  | 593 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | XW34 | XW34_DS |  | DS1 | XW34_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW34_DS | XW34_DS (非取樣點) | FEEDER | D08/11/XW34/DS |  |  |  |  | 594 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | XW34 | XW34_ES |  | LE0 | XW34_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW34_ES | XW34_ES (非取樣點) | FEEDER | D08/11/XW34/ES |  |  |  |  | 595 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | XW35 | XW35_DS |  | DS1 | XW35_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW35_DS | XW35_DS (非取樣點) | FEEDER | D08/11/XW35/DS |  |  |  |  | 596 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | XW35 | XW35_ES |  | LE0 | XW35_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW35_ES | XW35_ES (非取樣點) | FEEDER | D08/11/XW35/ES |  |  |  |  | 597 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | XW36 | XW36_DS |  | DS1 | XW36_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW36_DS | XW36_DS (非取樣點) | FEEDER | D08/11/XW36/DS |  |  |  |  | 598 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | XW36 | XW36_ES |  | LE0 | XW36_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW36_ES | XW36_ES (非取樣點) | FEEDER | D08/11/XW36/ES |  |  |  |  | 599 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | XW37 | XW37_DS |  | DS1 | XW37_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW37_DS | XW37_DS (非取樣點) | FEEDER | D08/11/XW37/DS |  |  |  |  | 600 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | XW37 | XW37_ES |  | LE0 | XW37_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW37_ES | XW37_ES (非取樣點) | FEEDER | D08/11/XW37/ES |  |  |  |  | 601 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | XW38 | XW38_DS |  | DS1 | XW38_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW38_DS | XW38_DS (非取樣點) | FEEDER | D08/11/XW38/DS |  |  |  |  | 602 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | XW38 | XW38_ES |  | LE0 | XW38_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW38_ES | XW38_ES (非取樣點) | FEEDER | D08/11/XW38/ES |  |  |  |  | 603 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | XW39 | XW39_DS |  | DS1 | XW39_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW39_DS | XW39_DS (非取樣點) | FEEDER | D08/11/XW39/DS |  |  |  |  | 604 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | XW39 | XW39_ES |  | LE0 | XW39_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW39_ES | XW39_ES (非取樣點) | FEEDER | D08/11/XW39/ES |  |  |  |  | 605 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | XW40 | XW40_DS |  | DS1 | XW40_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW40_DS | XW40_DS (非取樣點) | FEEDER | [5 empty] | 606 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | XW40 | XW40_ES |  | LE0 | XW40_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW40_ES | XW40_ES (非取樣點) | FEEDER | [5 empty] | 607 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | XW61 | XW61_DS |  | DS1 | XW61_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW61_DS | XW61_DS (非取樣點) | FEEDER | D08/22/XW61/DS |  |  |  |  | 608 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | XW61 | XW61_ES |  | LE0 | XW61_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW61_ES | XW61_ES (非取樣點) | FEEDER | D08/22/XW61/ES |  |  |  |  | 609 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | XW62 | XW62_DS |  | DS1 | XW62_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW62_DS | XW62_DS (非取樣點) | FEEDER | D08/22/XW62/DS |  |  |  |  | 610 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | XW62 | XW62_ES |  | LE0 | XW62_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW62_ES | XW62_ES (非取樣點) | FEEDER | D08/22/XW62/ES |  |  |  |  | 611 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | XW63 | XW63_DS |  | DS1 | XW63_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW63_DS | XW63_DS (非取樣點) | FEEDER | D08/22/XW63/DS |  |  |  |  | 612 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | XW63 | XW63_ES |  | LE0 | XW63_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW63_ES | XW63_ES (非取樣點) | FEEDER | D08/22/XW63/ES |  |  |  |  | 613 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | XW64 | XW64_DS |  | DS1 | XW64_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW64_DS | XW64_DS (非取樣點) | FEEDER | D08/22/XW64/DS |  |  |  |  | 614 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | XW64 | XW64_ES |  | LE0 | XW64_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW64_ES | XW64_ES (非取樣點) | FEEDER | D08/22/XW64/ES |  |  |  |  | 615 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | XW65 | XW65_DS |  | DS1 | XW65_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW65_DS | XW65_DS (非取樣點) | FEEDER | D08/22/XW65/DS |  |  |  |  | 616 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | XW65 | XW65_ES |  | LE0 | XW65_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW65_ES | XW65_ES (非取樣點) | FEEDER | D08/22/XW65/ES |  |  |  |  | 617 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | XW71 | XW71_DS |  | DS1 | XW71_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW71_DS | XW71_DS (非取樣點) | FEEDER | D08/22/XW71/DS |  |  |  |  | 618 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | XW71 | XW71_ES |  | LE0 | XW71_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW71_ES | XW71_ES (非取樣點) | FEEDER | D08/22/XW71/ES |  |  |  |  | 619 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | XW72 | XW72_DS |  | DS1 | XW72_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW72_DS | XW72_DS (非取樣點) | FEEDER | D08/22/XW72/DS |  |  |  |  | 620 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | XW72 | XW72_ES |  | LE0 | XW72_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW72_ES | XW72_ES (非取樣點) | FEEDER | D08/22/XW72/ES |  |  |  |  | 621 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | XW73 | XW73_DS |  | DS1 | XW73_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW73_DS | XW73_DS (非取樣點) | FEEDER | D08/22/XW73/DS |  |  |  |  | 622 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | XW73 | XW73_ES |  | LE0 | XW73_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW73_ES | XW73_ES (非取樣點) | FEEDER | D08/22/XW73/ES |  |  |  |  | 623 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | XW74 | XW74_DS |  | DS1 | XW74_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW74_DS | XW74_DS (非取樣點) | FEEDER | D08/22/XW74/DS |  |  |  |  | 624 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | XW74 | XW74_ES |  | LE0 | XW74_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW74_ES | XW74_ES (非取樣點) | FEEDER | D08/22/XW74/ES |  |  |  |  | 625 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | XW75 | XW75_DS |  | DS1 | XW75_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW75_DS | XW75_DS (非取樣點) | FEEDER | D08/22/XW75/DS |  |  |  |  | 626 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | XW75 | XW75_ES |  | LE0 | XW75_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗南DS.XW75_ES | XW75_ES (非取樣點) | FEEDER | D08/22/XW75/ES |  |  |  |  | 627 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [24 empty] | ADCS_N | [8 empty] | 斗南DS.1501E | 1501E (非取樣點) | TIE | D08/161/1500/E1 |  |  |  |  | 628 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [24 empty] | ADCS_N | [8 empty] | 斗南DS.1502E | 1502E (非取樣點) | TIE | D08/161/1500/E2 |  |  |  |  | 629 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | 301 | 301 |  | 301 | 301 | [24 empty] | ADCS_N | [8 empty] | 斗南DS.301 | 301 (非取樣點) | TIE | D08/22/300/D1 |  |  |  |  | 630 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | 302 | 302 |  | 302 | 302 | [24 empty] | ADCS_N | [8 empty] | 斗南DS.302 | 302 (非取樣點) | TIE | D08/22/300/D2 |  |  |  |  | 631 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | 401 | 401 |  | 401 | 401 | [24 empty] | ADCS_N | [8 empty] | 斗南DS.401 | 401 (非取樣點) | TIE | D08/11/400/D1 |  |  |  |  | 632 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | 402 | 402 |  | 402 | 402 | [24 empty] | ADCS_N | [8 empty] | 斗南DS.402 | 402 (非取樣點) | TIE | D08/11/400/D2 |  |  |  |  | 633 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | 391 | 391 |  | 391 | 391 | [24 empty] | ADCS_N | [8 empty] | 斗南DS.391 | 391 (非取樣點) | OTHER | D08/11/390/D1 |  |  |  |  | 634 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | 391E | 391E |  | 391E | 391E | [24 empty] | ADCS_N | [8 empty] | 斗南DS.391E | 391E (非取樣點) | OTHER | D08/11/390/E1 |  |  |  |  | 635 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | 491 | 491 |  | 491 | 491 | [24 empty] | ADCS_N | [8 empty] | 斗南DS.491 | 491 (非取樣點) | OTHER | D08/11/490/D1 |  |  |  |  | 636 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | 491E | 491E |  | 491E | 491E | [24 empty] | ADCS_N | [8 empty] | 斗南DS.491E | 491E (非取樣點) | OTHER | D08/11/490/E1 |  |  |  |  | 637 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | 1760TE | [24 empty] | ADCS_N | [8 empty] | 斗南DS.1760TE | 1760TE (非取樣點) | MTR | D08/161/1760/TE0 |  |  |  |  | 638 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | 1760BE | [24 empty] | ADCS_N | [8 empty] | 斗南DS.1760BE | 1760BE (非取樣點) | MTR | D08/161/1760/BE0 |  |  |  |  | 639 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | 331 | 331 |  | 331 | 331 | [24 empty] | ADCS_N | [8 empty] | 斗南DS.331 | 331 (非取樣點) | MTR | D08/22/330/D1 |  |  |  |  | 640 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | 330 | #2DTR(330) |  | E1 | 331E | [24 empty] | ADCS_N | [8 empty] | 斗南DS.331E | 331E (非取樣點) | MTR | D08/22/330/E1 |  |  |  |  | 641 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | 341 | 341 |  | 341 | 341 | [24 empty] | ADCS_N | [8 empty] | 斗南DS.341 | 341 (非取樣點) | MTR | D08/11/340/D1 |  |  |  |  | 642 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | 340 | #2DTR(340) |  | E1 | 341E | [24 empty] | ADCS_N | [8 empty] | 斗南DS.341E | 341E (非取樣點) | MTR | D08/11/340/E1 |  |  |  |  | 643 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | 1770TE | [24 empty] | ADCS_N | [8 empty] | 斗南DS.1770TE | 1770TE (非取樣點) | MTR | D08/161/1770/TE0 |  |  |  |  | 644 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | 1770BE | [24 empty] | ADCS_N | [8 empty] | 斗南DS.1770BE | 1770BE (非取樣點) | MTR | D08/161/1770/BE0 |  |  |  |  | 645 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | 351 | 351 |  | 351 | 351 | [24 empty] | ADCS_N | [8 empty] | 斗南DS.351 | 351 (非取樣點) | MTR | D08/22/350/D1 |  |  |  |  | 646 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | 350 | #3DTR(350) |  | E1 | 351E | [24 empty] | ADCS_N | [8 empty] | 斗南DS.351E | 351E (非取樣點) | MTR | D08/22/350/E1 |  |  |  |  | 647 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | 361 | 361 |  | 361 | 361 | [24 empty] | ADCS_N | [8 empty] | 斗南DS.361 | 361 (非取樣點) | MTR | D08/11/360/D1 |  |  |  |  | 648 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | 360 | #3DTR(360) |  | E1 | 361E | [24 empty] | ADCS_N | [8 empty] | 斗南DS.361E | 361E (非取樣點) | MTR | D08/11/360/E1 |  |  |  |  | 649 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | 241E | 241E |  | 241E | 241E | [24 empty] | ADCS_N | [8 empty] | 斗南DS.241E | 241E (非取樣點) | SC | D08/11/240/E1 |  |  |  |  | 650 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | 240 | #4SC(240) |  | SC10 | 240SC1 | [24 empty] | ADCS_N | [8 empty] | 斗南DS.240SC1_ES | 240SC1_ES (非取樣點) | SC | [5 empty] | 651 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | 241 | 241 |  | 241 | 241 | [24 empty] | ADCS_N | [8 empty] | 斗南DS.241 | 241 (非取樣點) | SC | D08/11/240/D1 |  |  |  |  | 652 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | 240 | #4SC(240) |  | SC20 | 240SC2 | [24 empty] | ADCS_N | [8 empty] | 斗南DS.240SC2_ES | 240SC2_ES (非取樣點) | SC | [5 empty] | 653 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | 261E | 261E |  | 261E | 261E | [24 empty] | ADCS_N | [8 empty] | 斗南DS.261E | 261E (非取樣點) | SC | D08/11/260/E1 |  |  |  |  | 654 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | 260 | #6SC(260) |  | SC10 | 260SC1 | [24 empty] | ADCS_N | [8 empty] | 斗南DS.260SC1_ES | 260SC1_ES (非取樣點) | SC | [5 empty] | 655 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | 261 | 261 |  | 261 | 261 | [24 empty] | ADCS_N | [8 empty] | 斗南DS.261 | 261 (非取樣點) | SC | D08/11/260/D1 |  |  |  |  | 656 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | 260 | #6SC(260) |  | SC20 | 260SC2 | [24 empty] | ADCS_N | [8 empty] | 斗南DS.260SC2_ES | 260SC2_ES (非取樣點) | SC | [5 empty] | 657 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | 231E | 231E |  | 231E | 231E | [24 empty] | ADCS_N | [8 empty] | 斗南DS.231E | 231E (非取樣點) | SC | D08/22/230/E1 |  |  |  |  | 658 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | 230 | #3SC(230) |  | SC10 | 230SC1 | [24 empty] | ADCS_N | [8 empty] | 斗南DS.230SC1_ES | 230SC1_ES (非取樣點) | SC | [5 empty] | 659 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | 231 | 231 |  | 231 | 231 | [24 empty] | ADCS_N | [8 empty] | 斗南DS.231 | 231 (非取樣點) | SC | D08/22/230/D1 |  |  |  |  | 660 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | 251E | 251E |  | 251E | 251E | [24 empty] | ADCS_N | [8 empty] | 斗南DS.251E | 251E (非取樣點) | SC | D08/22/250/E1 |  |  |  |  | 661 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | 250 | #5SC(250) |  | SC10 | 250SC1 | [24 empty] | ADCS_N | [8 empty] | 斗南DS.250SC1_ES | 250SC1_ES (非取樣點) | SC | [5 empty] | 662 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | 251 | 251 |  | 251 | 251 | [24 empty] | ADCS_N | [8 empty] | 斗南DS.251 | 251 (非取樣點) | SC | D08/22/250/D1 |  |  |  |  | 663 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D08 | 斗南DS | 0 |  | 15B1E | 15B1E |  | BE1 | 15B1E | [24 empty] | ADCS_N | [8 empty] | 斗南DS.15B1E | 15B1E (非取樣點) | BUS | D08/161/161B1E/BE1 |  |  |  |  | 664 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | 15B2E | 15B2E |  | BE2 | 15B2E | [24 empty] | ADCS_N | [8 empty] | 斗南DS.15B2E | 15B2E (非取樣點) | BUS | D08/161/161B2E/BE2 |  |  |  |  | 665 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | ADCS_N | [8 empty] | 斗南DS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 666 | NotelDIPoint | [38 empty] | START/STOP | STOP
D08 | 斗南DS | 0 |  |  |  |  | 301E | 301E | [24 empty] | ADCS_N | [8 empty] | 斗南DS.301E | 301E(非取樣點) | OTHER | D08/22/300/E1 |  |  |  |  | 667 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  |  |  |  | 302E | 302E | [24 empty] | ADCS_N | [8 empty] | 斗南DS.302E | 302E(非取樣點) | OTHER | D08/22/300/E2 |  |  |  |  | 668 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  |  |  |  | 401E | 401E | [24 empty] | ADCS_N | [8 empty] | 斗南DS.401E | 401E(非取樣點) | OTHER | D08/11/400/E1 |  |  |  |  | 669 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  |  |  |  | 402E | 402E | [24 empty] | ADCS_N | [8 empty] | 斗南DS.402E | 402E(非取樣點) | OTHER | D08/11/400/E2 |  |  |  |  | 670 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 161 | 161kV | 1510 | 斗南虎菁一路(1510) |  | LE0 | 1510LE | [24 empty] | ADCS_N | [8 empty] | 斗南DS.1510LE | 1510LE (非取樣點) | LINE161 | D08/161/1510/LE0 |  |  |  |  | 671 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 161 | 161kV | 1510 | 斗南虎菁一路(1510) |  | BE0 | 1510BE | [24 empty] | ADCS_N | [8 empty] | 斗南DS.1510BE | 1510BE (非取樣點) | LINE161 | D08/161/1510/BE0 |  |  |  |  | 672 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 161 | 161kV | 1520 | 斗南虎菁二路(1520) |  | LE0 | 1520LE | [24 empty] | ADCS_N | [8 empty] | 斗南DS.1520LE | 1520LE (非取樣點) | LINE161 | D08/161/1520/LE0 |  |  |  |  | 673 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 161 | 161kV | 1520 | 斗南虎菁二路(1520) |  | BE0 | 1520BE | [24 empty] | ADCS_N | [8 empty] | 斗南DS.1520BE | 1520BE (非取樣點) | LINE161 | D08/161/1520/BE0 |  |  |  |  | 674 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | 2ABUS | 2ABUS |  | PTE | 2ABUS_PTE | [24 empty] | ADCS_N | [8 empty] | 斗南DS.2ABUS_PTE | #2ABUS_PTE(非取樣點) | OTHER | [5 empty] | 675 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | 2BBUS | 2BBUS |  | PTE | 2BBUS_PTE | [24 empty] | ADCS_N | [8 empty] | 斗南DS.2BBUS_PTE | #2BBUS_PTE(非取樣點) | OTHER | [5 empty] | 676 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | 3ABUS | 3ABUS |  | PTE | 3ABUS_PTE | [24 empty] | ADCS_N | [8 empty] | 斗南DS.3ABUS_PTE | #3ABUS_PTE(非取樣點) | OTHER | [5 empty] | 677 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D08 | 斗南DS | 0 |  | 3BBUS | 3BBUS |  | PTE | 3BBUS_PTE | [24 empty] | ADCS_N | [8 empty] | 斗南DS.3BBUS_PTE | #3BBUS_PTE(非取樣點) | OTHER | [5 empty] | 678 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo