## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工～斗工山線(1510) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_A1 | [8 empty] | 斗工DS.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 2 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工～斗工山線(1510) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_A1 | [8 empty] | 斗工DS.1510BE | 1510BE (非取樣點) | LINE161 | [5 empty] | 3 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工～斗工海線(1520) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_A1 | [8 empty] | 斗工DS.1520LE | 1520LE (非取樣點) | LINE161 | [5 empty] | 4 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工～斗工海線(1520) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_A1 | [8 empty] | 斗工DS.1520BE | 1520BE (非取樣點) | LINE161 | [5 empty] | 5 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1540 | 雲林~斗工線(1540) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_A1 | [8 empty] | 斗工DS.1540LE | 1540LE (非取樣點) | LINE161 | [5 empty] | 6 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1540 | 雲林~斗工線(1540) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_A1 | [8 empty] | 斗工DS.1540BE | 1540BE (非取樣點) | LINE161 | [5 empty] | 7 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1530 | 嘉民～斗工紅線(1530) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_A1 | [8 empty] | 斗工DS.1530LE | 1530LE (非取樣點) | LINE161 | [5 empty] | 8 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1530 | 嘉民～斗工紅線(1530) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_A1 | [8 empty] | 斗工DS.1530BE | 1530BE (非取樣點) | LINE161 | [5 empty] | 9 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1550 | 斗工～富喬線(1550) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_A1 | [8 empty] | 斗工DS.1550LE | 1550LE (非取樣點) | LINE161 | [5 empty] | 10 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1550 | 斗工～富喬線(1550) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_A1 | [8 empty] | 斗工DS.1550BE | 1550BE (非取樣點) | LINE161 | [5 empty] | 11 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1610 | 榴中～斗工一路(1610) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_A1 | [8 empty] | 斗工DS.1610LE | 1610LE (非取樣點) | LINE161 | [5 empty] | 12 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1610 | 榴中～斗工一路(1610) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_A1 | [8 empty] | 斗工DS.1610BE | 1610BE (非取樣點) | LINE161 | [5 empty] | 13 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1620 | 榴中～斗工二路(1620) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_A1 | [8 empty] | 斗工DS.1620LE | 1620LE (非取樣點) | LINE161 | [5 empty] | 14 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1620 | 榴中～斗工二路(1620) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_A1 | [8 empty] | 斗工DS.1620BE | 1620BE (非取樣點) | LINE161 | [5 empty] | 15 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_A1 | [8 empty] | 斗工DS.1501E | 1501E (非取樣點) | TIE | [5 empty] | 16 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_A1 | [8 empty] | 斗工DS.1502E | 1502E (非取樣點) | TIE | [5 empty] | 17 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_A1 | [8 empty] | 斗工DS.1750TE | 1750TE (非取樣點) | MTR | [5 empty] | 18 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_A1 | [8 empty] | 斗工DS.1750BE | 1750BE (非取樣點) | MTR | [5 empty] | 19 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | D1 | 311(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D09_A1 | [8 empty] | 斗工DS.311 | 311 (非取樣點) | MTR | [5 empty] | 20 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | E1 | 311E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D09_A1 | [8 empty] | 斗工DS.311E | 311E (非取樣點) | MTR | [5 empty] | 21 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | D1 | 321(非取樣點) | B2 | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D09_A1 | [8 empty] | 斗工DS.321 | 321 (非取樣點) | MTR | [5 empty] | 22 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | E1 | 321E(非取樣點) | B2,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D09_A1 | [8 empty] | 斗工DS.321E | 321E (非取樣點) | MTR | [5 empty] | 23 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_A1 | [8 empty] | 斗工DS.1760TE | 1760TE (非取樣點) | MTR | [5 empty] | 24 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_A1 | [8 empty] | 斗工DS.1760BE | 1760BE (非取樣點) | MTR | [5 empty] | 25 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 22 | 22kV | XU51 | 工五一線(XU51) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU51_DS | XU51_DS (非取樣點) | FEEDER | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | XU51 | 工五一線(XU51) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU51_ES | XU51_ES (非取樣點) | FEEDER | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 22 | 22kV | XU52 | 工五二線(XU52) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU52_DS | XU52_DS (非取樣點) | FEEDER | [5 empty] | 28 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | XU52 | 工五二線(XU52) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU52_ES | XU52_ES (非取樣點) | FEEDER | [5 empty] | 29 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 22 | 22kV | XU53 | 工五三線(XU53) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU53_DS | XU53_DS (非取樣點) | FEEDER | [5 empty] | 30 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | XU53 | 工五三線(XU53) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU53_ES | XU53_ES (非取樣點) | FEEDER | [5 empty] | 31 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 22 | 22kV | XU54 | 工五四線(XU54) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU54_DS | XU54_DS (非取樣點) | FEEDER | [5 empty] | 32 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | XU54 | 工五四線(XU54) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU54_ES | XU54_ES (非取樣點) | FEEDER | [5 empty] | 33 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 22 | 22kV | XU55 | 工五五線(XU55) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU55_DS | XU55_DS (非取樣點) | FEEDER | [5 empty] | 34 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | XU55 | 工五五線(XU55) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU55_ES | XU55_ES (非取樣點) | FEEDER | [5 empty] | 35 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 22 | 22kV | 210 | #1SC(210) |  | E1 | 211E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D09_A1 | [8 empty] | 斗工DS.211E | 211E (非取樣點) | SC | [5 empty] | 36 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 22 | 22kV | 210 | #1SC(210) |  | D1 | 211(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D09_A1 | [8 empty] | 斗工DS.211 | 211 (非取樣點) | SC | [5 empty] | 37 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | 100 | TIE(100) |  | D1 | 101(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D09_A1 | [8 empty] | 斗工DS.101 | 101 (非取樣點) | TIE | [5 empty] | 38 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | 100 | TIE(100) |  | D2 | 102(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D09_A1 | [8 empty] | 斗工DS.102 | 102 (非取樣點) | TIE | [5 empty] | 39 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | 100 | TIE(100) |  | E1 | 101E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D09_A1 | [8 empty] | 斗工DS.101E | 101E(非取樣點) | OTHER | [5 empty] | 40 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 22 | 22kV | 100 | TIE(100) |  | E2 | 102E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D09_A1 | [8 empty] | 斗工DS.102E | 102E(非取樣點) | OTHER | [5 empty] | 41 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 11 | 11kV | XU26 | 工六線(XU26) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU26_DS | XU26_DS (非取樣點) | FEEDER | [5 empty] | 42 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | XU26 | 工六線(XU26) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU26_ES | XU26_ES (非取樣點) | FEEDER | [5 empty] | 43 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 11 | 11kV | XU27 | 工七線(XU27) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU27_DS | XU27_DS (非取樣點) | FEEDER | [5 empty] | 44 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | XU27 | 工七線(XU27) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU27_ES | XU27_ES (非取樣點) | FEEDER | [5 empty] | 45 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 11 | 11kV | XU28 | 工八線(XU28) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU28_DS | XU28_DS (非取樣點) | FEEDER | [5 empty] | 46 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | XU28 | 工八線(XU28) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU28_ES | XU28_ES (非取樣點) | FEEDER | [5 empty] | 47 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 11 | 11kV | XU29 | 工九線(XU29) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU29_DS | XU29_DS (非取樣點) | FEEDER | [5 empty] | 48 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | XU29 | 工九線(XU29) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU29_ES | XU29_ES (非取樣點) | FEEDER | [5 empty] | 49 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 11 | 11kV | XU30 | 工十線(XU30) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU30_DS | XU30_DS (非取樣點) | FEEDER | [5 empty] | 50 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | XU30 | 工十線(XU30) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU30_ES | XU30_ES (非取樣點) | FEEDER | [5 empty] | 51 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 11 | 11kV | 220 | #2SC(220) |  | E1 | 221E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D09_A1 | [8 empty] | 斗工DS.221E | 221E (非取樣點) | SC | [5 empty] | 52 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 11 | 11kV | 220 | #2SC(220) |  | DS1 | 221(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D09_A1 | [8 empty] | 斗工DS.221 | 221 (非取樣點) | SC | [5 empty] | 53 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | 200 | TIE(200) |  | D1 | 201(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D09_A1 | [8 empty] | 斗工DS.201 | 201 (非取樣點) | TIE | [5 empty] | 54 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | 200 | TIE(200) |  | E1 | 201E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D09_A1 | [8 empty] | 斗工DS.201E | 201E(非取樣點) | OTHER | [5 empty] | 55 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 11 | 11kV | 200 | TIE(200) |  | D2 | 202(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D09_A1 | [8 empty] | 斗工DS.202 | 202 (非取樣點) | TIE | [5 empty] | 56 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | 200 | TIE(200) |  | E2 | 202E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D09_A1 | [8 empty] | 斗工DS.202E | 202E(非取樣點) | OTHER | [5 empty] | 57 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 11 | 11kV | 390 | #1SSTR(390) |  | D1 | 391(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D09_A1 | [8 empty] | 斗工DS.391 | 391 (非取樣點) | OTHER | [5 empty] | 58 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | 390 | #1SSTR(390) |  | E1 | 391E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D09_A1 | [8 empty] | 斗工DS.391E | 391E(非取樣點)(非取樣點) | OTHER | [5 empty] | 59 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 22 | 22kV | XU61 | 工六一線(XU61) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU61_DS | XU61_DS (非取樣點) | FEEDER | [5 empty] | 60 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | XU61 | 工六一線(XU61) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU61_ES | XU61_ES (非取樣點) | FEEDER | [5 empty] | 61 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 22 | 22kV | XU62 | 工六二線(XU62) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU62_DS | XU62_DS (非取樣點) | FEEDER | [5 empty] | 62 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | XU62 | 工六二線(XU62) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU62_ES | XU62_ES (非取樣點) | FEEDER | [5 empty] | 63 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 22 | 22kV | XU63 | 工六三線(XU63) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU63_DS | XU63_DS (非取樣點) | FEEDER | [5 empty] | 64 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | XU63 | 工六三線(XU63) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU63_ES | XU63_ES (非取樣點) | FEEDER | [5 empty] | 65 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 22 | 22kV | XU64 | 工六四線(XU64) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU64_DS | XU64_DS (非取樣點) | FEEDER | [5 empty] | 66 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | XU64 | 工六四線(XU64) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU64_ES | XU64_ES (非取樣點) | FEEDER | [5 empty] | 67 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 22 | 22kV | XU65 | 工六五線(XU65) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU65_DS | XU65_DS (非取樣點) | FEEDER | [5 empty] | 68 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | XU65 | 工六五線(XU65) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU65_ES | XU65_ES (非取樣點) | FEEDER | [5 empty] | 69 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 22 | 22kV | 300 | TIE(300) |  | D1 | 301(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D09_A1 | [8 empty] | 斗工DS.301 | 301 (非取樣點) | TIE | [5 empty] | 70 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | 300 | TIE(300) |  | E1 | 301E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D09_A1 | [8 empty] | 斗工DS.301E | 301E(非取樣點) | OTHER | [5 empty] | 71 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 22 | 22kV | 230 | #3SC(230) |  | E1 | 231E(非取樣點) | B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D09_A1 | [8 empty] | 斗工DS.231E | 231E (非取樣點) | SC | [5 empty] | 72 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 22 | 22kV | 230 | #3SC(230) |  | D1 | 231(非取樣點) | B3 | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D09_A1 | [8 empty] | 斗工DS.231 | 231 (非取樣點) | SC | [5 empty] | 73 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | 490 | #1SSTR(490) |  | D1 | 491(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D09_A1 | [8 empty] | 斗工DS.491 | 491 (非取樣點) | OTHER | [5 empty] | 74 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | 490 | #1SSTR(490) |  | E1 | 491E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D09_A1 | [8 empty] | 斗工DS.491E | 491E(非取樣點)(非取樣點) | OTHER | [5 empty] | 75 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 11 | 11kV | XU36 | 工十六線(XU36) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU36_DS | XU36_DS (非取樣點) | FEEDER | [5 empty] | 76 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | XU36 | 工十六線(XU36) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU36_ES | XU36_ES (非取樣點) | FEEDER | [5 empty] | 77 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 11 | 11kV | XU37 | 工十七線(XU37) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU37_DS | XU37_DS (非取樣點) | FEEDER | [5 empty] | 78 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | XU37 | 工十七線(XU37) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU37_ES | XU37_ES (非取樣點) | FEEDER | [5 empty] | 79 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 11 | 11kV | XU38 | 工十八線(XU38) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU38_DS | XU38_DS (非取樣點) | FEEDER | [5 empty] | 80 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | XU38 | 工十八線(XU38) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU38_ES | XU38_ES (非取樣點) | FEEDER | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 11 | 11kV | XU39 | 工十九線(XU39) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU39_DS | XU39_DS (非取樣點) | FEEDER | [5 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | XU39 | 工十九線(XU39) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU39_ES | XU39_ES (非取樣點) | FEEDER | [5 empty] | 83 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 11 | 11kV | XU40 | 工二十線(XU40) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU40_DS | XU40_DS (非取樣點) | FEEDER | [5 empty] | 84 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | XU40 | 工二十線(XU40) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D09_D1 | [8 empty] | 斗工DS.XU40_ES | XU40_ES (非取樣點) | FEEDER | [5 empty] | 85 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 11 | 11kV | 240 | #4SC(240) |  | E1 | 241E(非取樣點) | B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D09_A1 | [8 empty] | 斗工DS.241E | 241E (非取樣點) | SC | [5 empty] | 86 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 11 | 11kV | 240 | #4SC(240) |  | DS1 | 241(非取樣點) | B3 | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D09_A1 | [8 empty] | 斗工DS.241 | 241 (非取樣點) | SC | [5 empty] | 87 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | 400 | TIE(400) |  | D1 | 401(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D09_A1 | [8 empty] | 斗工DS.401 | 401 (非取樣點) | TIE | [5 empty] | 88 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | 400 | TIE(400) |  | E1 | 401E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D09_A1 | [8 empty] | 斗工DS.401E | 401E(非取樣點) | OTHER | [5 empty] | 89 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | 15B1E(非取樣點) | B2,B2,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aaaz | B2/D09_A1 | [8 empty] | 斗工DS.15B1E | 15B1E (非取樣點) | BUS | [5 empty] | 90 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | 15B2E(非取樣點) | B2,B2,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/2Bus | [13 empty] | aaaz | B2/D09_A1 | [8 empty] | 斗工DS.15B2E | 15B2E (非取樣點) | BUS | [5 empty] | 91 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0512 |  | 0000 | 1-30-00 |  | 1-00 | TEST CB | ON/OFF | TEST CB |  |  | ELEM/ALL | [8 empty] | 斗工DS.TEST_CB | TEST CB | OTHER | [5 empty] | 92 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工～斗工山線(1510) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/T14D09M/T2 |  | 0000 |  | 0001 | 1-00-00 |  | 1-01 | 1510 | ON/OFF | 鉅工斗工山線 1510 CB |  | aaca | B2/D09_A1 | [8 empty] | 斗工DS.1510_CB | 1510(鉅工山線) CB | LINE161 | [5 empty] | 93 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工～斗工海線(1520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/T14D09O/T2 |  | 0005 |  | 0002 | 1-00-05 |  | 1-02 | 1520 | ON/OFF | 鉅工斗工海線 1520 CB |  | aada | B2/D09_A1 | [8 empty] | 斗工DS.1520_CB | 1520(鉅工海線) CB | LINE161 | [5 empty] | 94 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 161 | 161kV | 1540 | 雲林~斗工線(1540) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P03D09/T2 |  | 0010 |  | 0003 | 1-01-02 |  | 1-03 | 1540 | ON/OFF | 雲林斗工線 1540 CB |  | aaga | B2/D09_A1 | [8 empty] | 斗工DS.1540_CB | 1540(雲林斗工線) CB | LINE161 | [5 empty] | 95 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 161 | 161kV | 1530 | 嘉民～斗工紅線(1530) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/E03D09R/T2 |  | 0015 |  | 0004 | 1-01-07 |  | 1-04 | 1530 | ON/OFF | 嘉民斗工紅線 1530 CB |  | aaha | B2/D09_A1 | [8 empty] | 斗工DS.1530_CB | 1530(嘉民斗工紅線) CB | LINE161 | [5 empty] | 96 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 161 | 161kV | 1550 | 斗工～富喬線(1550) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D09C61/T1 |  | 0020 |  | 0005 | 1-02-04 |  | 1-05 | 1550 | ON/OFF | 斗工富喬線 1550 CB |  | aaia | B2/D09_A1 | [8 empty] | 斗工DS.1550_CB | 1550(富喬線) CB | LINE161 | [5 empty] | 97 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 161 | 161kV | 1610 | 榴中～斗工一路(1610) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D11D091/T2 |  | 0035 |  | 0008 | 1-04-03 |  | 1-08 | 1610 | ON/OFF | 榴中斗工一路 1610 CB |  | aala | B2/D09_A1 | [8 empty] | 斗工DS.1610_CB | 1610(榴中斗工一路) CB | LINE161 | [5 empty] | 98 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 161 | 161kV | 1620 | 榴中～斗工二路(1620) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D11D092/T2 |  | 0040 |  | 0009 | 1-05-00 |  | 1-09 | 1620 | ON/OFF | 榴中斗工二路 1620 CB |  | aama | B2/D09_A1 | [8 empty] | 斗工DS.1620_CB | 1620(榴中斗工二路) CB | LINE161 | [5 empty] | 99 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0051 |  | 0011 | 1-06-03 |  | 1-0B | 1500 | ON/OFF | 161KV TIE 1500 CB |  | aaez | B2/D09_A1 | [8 empty] | 斗工DS.1500_CB | 1500(TIE) CB | TIE | [5 empty] | 100 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/1DTR |  | 0057 |  | 0012 | 1-07-01 |  | 1-0C | 1750 | ON/OFF | #1DTR 1750 CB |  | aabb | ELEM/D09_A1 | [8 empty] | 斗工DS.1750_CB | 1750(#1DTR) CB | MTR | [5 empty] | 101 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2DTR |  | 0067 |  | 0013 | 1-08-03 |  | 1-0D | 1760 | ON/OFF | #2DTR 1760 CB |  | aafb | ELEM/D09_A1 | [8 empty] | 斗工DS.1760_CB | 1760(#2DTR) CB | MTR | [5 empty] | 102 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | T/1DTR(A) |  |  | 0063 |  | 0016 | 1-07-07 |  | 1-10 | 310 | ON/OFF | #1DTR 1A 310 CB |  | aaba | ELEM/D09_A1 | [8 empty] | 斗工DS.310_CB | 310(#1DTR) CB | MTR | [5 empty] | 103 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | 210 | #1SC(210) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | C/1SC |  |  | 0143 |  | 0017 | 1-11-07 |  | 1-11 | 210 #1SC | ON/OFF | #1SC 210 #1SC CB |  | aacb | B3/D09_A1 | [8 empty] | 斗工DS.210_CB | 210(23KV #1SC) CB | SC | [5 empty] | 104 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | XU51 | 工五一線(XU51) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/XU51/T1 |  |  | 0128 |  | 0018 | 1-10-00 |  | 1-12 | F1 | ON/OFF | F1 CB 工五一線 XU51 |  | aadb | B2/D09_D1 | [8 empty] | 斗工DS.XU51_CB | XU51(23KV工五一線) CB | FEEDER | [5 empty] | 105 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | XU52 | 工五二線(XU52) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/XU52/T1 |  |  | 0131 |  | 0019 | 1-10-03 |  | 1-13 | F2 | ON/OFF | F2 CB 工五二線 XU52 |  | aaeb | B2/D09_D1 | [8 empty] | 斗工DS.XU52_CB | XU52(23KV工五二線) CB | FEEDER | [5 empty] | 106 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | XU53 | 工五三線(XU53) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/XU53/T1 |  |  | 0134 |  | 0020 | 1-10-06 |  | 1-14 | F3 | ON/OFF | F3 CB 工五三線 XU53 |  | aafb | B2/D09_D1 | [8 empty] | 斗工DS.XU53_CB | XU53(23KV工五三線) CB | FEEDER | [5 empty] | 107 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | XU54 | 工五四線(XU54) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/XU54/T1 |  |  | 0137 |  | 0021 | 1-11-01 |  | 1-15 | F4 | ON/OFF | F4 CB 工五四線 XU54 |  | aagb | B2/D09_D1 | [8 empty] | 斗工DS.XU54_CB | XU54(23KV工五四線) CB | FEEDER | [5 empty] | 108 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | XU55 | 工五五線(XU55) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/XU55/T1 |  |  | 0140 |  | 0022 | 1-11-04 |  | 1-16 | F5 | ON/OFF | F5 CB 工五五線 XU55 |  | aahb | B2/D09_D1 | [8 empty] | 斗工DS.XU55_CB | XU55(23KV工五五線) CB | FEEDER | [5 empty] | 109 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | 100 | TIE(100) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/1ABus | B/2A1Bus |  |  | 0146 |  | 0023 | 1-12-02 |  | 1-17 | 100 | ON/OFF | #1TIE 1A 100 CB |  | aaib | B3/D09_A1 | [8 empty] | 斗工DS.100_CB | 100(TIE) CB | TIE | [5 empty] | 110 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 11 | 11kV | 390 | #1SSTR(390) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | T/1SSTR |  |  | 0170 |  | 0024 | 1-15-02 |  | 1-18 | 390 | ON/OFF | #1SSTR CB |  | babb | B3/D09_A1 | [8 empty] | 斗工DS.390_CB | 390(#1SSTR) CB | OTHER | [5 empty] | 111 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | T/1DTR(B) |  |  | 0065 |  | 0025 | 1-08-01 |  | 1-19 | 320 | ON/OFF | #1DTR 1B 320 CB |  | baca | ELEM/D09_A1 | [8 empty] | 斗工DS.320_CB | 320(#1DTR) CB | MTR | [5 empty] | 112 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | 220 | #2SC(220) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | A/LBS220^C/2SC(A) |  |  | 0164 |  | 0026 | 1-14-04 |  | 1-1A | 220 #2SC | ON/OFF | #2SC 220 #2SC CB |  | badb | B3/D09_A1 | [8 empty] | 斗工DS.220_CB | 220(11KV #2SC) CB | SC | [5 empty] | 113 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | XU26 | 工六線(XU26) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/XU26/T1 |  |  | 0149 |  | 0027 | 1-12-05 |  | 1-1B | F6 | ON/OFF | F6 CB 工六線 XU26 |  | baeb | B2/D09_D1 | [8 empty] | 斗工DS.XU26_CB | XU26(11KV工六線) CB | FEEDER | [5 empty] | 114 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | XU27 | 工七線(XU27) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/XU27/T1 |  |  | 0152 |  | 0028 | 1-13-00 |  | 1-1C | F7 | ON/OFF | F7 CB 工七線 XU27 |  | bafb | B2/D09_D1 | [8 empty] | 斗工DS.XU27_CB | XU27(11KV工七線) CB | FEEDER | [5 empty] | 115 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | XU28 | 工八線(XU28) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/XU28/T1 |  |  | 0155 |  | 0029 | 1-13-03 |  | 1-1D | F8 | ON/OFF | F8 CB 工八線 XU28 |  | bagb | B2/D09_D1 | [8 empty] | 斗工DS.XU28_CB | XU28(11KV工八線) CB | FEEDER | [5 empty] | 116 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | XU29 | 工九線(XU29) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/XU29/T1 |  |  | 0158 |  | 0030 | 1-13-06 |  | 1-1E | F9 | ON/OFF | F9 CB 工九線 XU29 |  | bahb | B2/D09_D1 | [8 empty] | 斗工DS.XU29_CB | XU29(11KV工九線) CB | FEEDER | [5 empty] | 117 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | XU30 | 工十線(XU30) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/XU30/T1 |  |  | 0161 |  | 0031 | 1-14-01 |  | 1-1F | F10 | ON/OFF | F10 CB 工十線 XU30 |  | baib | B2/D09_D1 | [8 empty] | 斗工DS.XU30_CB | XU30(11KV工十線) CB | FEEDER | [5 empty] | 118 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | 200 | TIE(200) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/1BBus | B/2B1Bus |  |  | 0167 |  | 0032 | 1-14-07 |  | 1-20 | 200 | ON/OFF | #1TIE 1B 200 CB |  | bajb | B3/D09_A1 | [8 empty] | 斗工DS.200_CB | 200(TIE) CB | TIE | [5 empty] | 119 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 22 | 22kV | XU61 | 工六一線(XU61) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2A1Bus | L/XU61/T1 |  |  | 0173 |  | 0033 | 1-15-05 |  | 1-21 | F11 | ON/OFF | F11 CB 工六一線 XU61 |  | abab | B2/D09_D1 | [8 empty] | 斗工DS.XU61_CB | XU61(23KV工六一線) CB | FEEDER | [5 empty] | 120 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | XU62 | 工六二線(XU62) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2A1Bus | L/XU62/T1 |  |  | 0176 |  | 0034 | 1-16-00 |  | 1-22 | F12 | ON/OFF | F12 CB 工六二線 XU62 |  | abbb | B2/D09_D1 | [8 empty] | 斗工DS.XU62_CB | XU62(23KV工六二線) CB | FEEDER | [5 empty] | 121 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | XU63 | 工六三線(XU63) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2A1Bus | L/XU63/T1 |  |  | 0179 |  | 0035 | 1-16-03 |  | 1-23 | F13 | ON/OFF | F13 CB 工六三線 XU63 |  | abcb | B2/D09_D1 | [8 empty] | 斗工DS.XU63_CB | XU63(23KV工六三線) CB | FEEDER | [5 empty] | 122 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | 230 | #3SC(230) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2A1Bus | C/3SC |  |  | 0191 |  | 0036 | 1-17-07 |  | 1-24 | 230 #3SC | ON/OFF | #2ASC 230 #3SC CB |  | abdb | B3/D09_A1 | [8 empty] | 斗工DS.230_CB | 230(23KV #3SC) CB | SC | [5 empty] | 123 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | 330A1 | #2DTR(A)(330A1) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2A1Bus | A/330A2^T/2DTR(A) |  |  | 0073 |  | 0037 | 1-09-01 |  | 1-25 | 330A1 | ON/OFF | #2DTR 1A 330A1 CB |  | abea | ELEM/D09_A1 | [8 empty] | 斗工DS.330A1_CB | 330A1(#2DTR) CB | MTR | [5 empty] | 124 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | 330A1 | #2DTR(A)(330A1) |  | DS1 |  | ADD | Status | DS | Close/Open | Y | 1 | DI-SP | [6 empty] | 0073 |  | 0037 | 1-09-01 |  | 1-25 | 330A1 | ON/OFF | #2DTR 1A 330A1 CB |  | abea | ELEM/D09_A1 | [8 empty] | 斗工DS.330A1_CB | 330A1(#2DTR) CB | MTR | [5 empty] | 124 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | 330A1 | #2DTR(A)(330A1) |  | E1 |  | ADD | Status | E1 | Close/Open | Y | 1 | DI-SP | [6 empty] | 0073 |  | 0037 | 1-09-01 |  | 1-25 | 330A1 | ON/OFF | #2DTR 1A 330A1 CB |  | abea | ELEM/D09_A1 | [8 empty] | 斗工DS.330A1_CB | 330A1(#2DTR) CB | MTR | [5 empty] | 124 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | 330A2 | #2DTR(A)(330A2) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2A2Bus | A/330A1^T/2DTR(A) |  |  | 0075 |  | 0038 | 1-09-03 |  | 1-26 | 330A2 | ON/OFF | #2DTR 330A2 CB |  | acba | ELEM/D09_A1 | [8 empty] | 斗工DS.330A2_CB | 330A2(#2DTR) CB | MTR | [5 empty] | 125 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | 330A2 | #2DTR(A)(330A2) |  | DS1 |  | ADD | Status | DS | Close/Open | Y | 1 | DI-SP | [6 empty] | 0075 |  | 0038 | 1-09-03 |  | 1-26 | 330A2 | ON/OFF | #2DTR 330A2 CB |  | acba | ELEM/D09_A1 | [8 empty] | 斗工DS.330A2_CB | 330A2(#2DTR) CB | MTR | [5 empty] | 125 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | 330A2 | #2DTR(A)(330A2) |  | E1 |  | ADD | Status | E1 | Close/Open | Y | 1 | DI-SP | [6 empty] | 0075 |  | 0038 | 1-09-03 |  | 1-26 | 330A2 | ON/OFF | #2DTR 330A2 CB |  | acba | ELEM/D09_A1 | [8 empty] | 斗工DS.330A2_CB | 330A2(#2DTR) CB | MTR | [5 empty] | 125 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | 490 | #2SSTR(490) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2A2Bus | T/1SSTR |  |  | 0194 |  | 0039 | 1-18-02 |  | 1-27 | 490 | ON/OFF | #2SSTR CB |  | accb | B3/D09_A1 | [8 empty] | 斗工DS.490_CB | 490(#2SSTR) CB | OTHER | [5 empty] | 126 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | XU64 | 工六四線(XU64) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2A2Bus | L/XU64/T1 |  |  | 0182 |  | 0040 | 1-16-06 |  | 1-28 | F14 | ON/OFF | F14 CB 工六四線 XU64 |  | acdb | B2/D09_D1 | [8 empty] | 斗工DS.XU64_CB | XU64(23KV工六四線) CB | FEEDER | [5 empty] | 127 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | XU65 | 工六五線(XU65) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2A2Bus | L/XU65/T1 |  |  | 0185 |  | 0041 | 1-17-01 |  | 1-29 | F15 | ON/OFF | F15 CB 工六五線 XU65 |  | aceb | B2/D09_D1 | [8 empty] | 斗工DS.XU65_CB | XU65(23KV工六五線) CB | FEEDER | [5 empty] | 128 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | 300 | TIE(300) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2A2Bus | A/100/N1 |  |  | 0188 |  | 0042 | 1-17-04 |  | 1-2A | 300 | ON/OFF | #2TIE 2A 300 CB |  | acfb | B3/D09_A1 | [8 empty] | 斗工DS.300_CB | 300(TIE) CB | TIE | [5 empty] | 129 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D09 | 斗工DS | 11 | 11kV | XU36 | 工十六線(XU36) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2B1Bus | L/XU36/T1 |  |  | 0197 |  | 0043 | 1-18-05 |  | 1-2B | F16 | ON/OFF | F16 CB 工十六線 XU36 |  | bbab | B2/D09_D1 | [8 empty] | 斗工DS.XU36_CB | XU36(11KV工十六線) CB | FEEDER | [5 empty] | 130 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | XU37 | 工十七線(XU37) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2B1Bus | L/XU37/T1 |  |  | 0200 |  | 0044 | 1-19-00 |  | 1-2C | F17 | ON/OFF | F17 CB 工十七線 XU37 |  | bbbb | B2/D09_D1 | [8 empty] | 斗工DS.XU37_CB | XU37(11KV工十七線) CB | FEEDER | [5 empty] | 131 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | 340B1 | #2DTR(B)(340B1) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2B1Bus | A/340B2^T/2DTR(B) |  |  | 0079 |  | 0045 | 1-09-07 |  | 1-2D | 340B1 | ON/OFF | #2DTR 1B 340B1 CB |  | bbca | ELEM/D09_A1 | [8 empty] | 斗工DS.340B1_CB | 340B1(#2DTR) CB | MTR | [5 empty] | 132 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | 340B1 | #2DTR(B)(340B1) |  | DS1 |  | ADD | Status | DS | Close/Open | Y | 1 | DI-SP | [6 empty] | 0079 |  | 0045 | 1-09-07 |  | 1-2D | 340B1 | ON/OFF | #2DTR 1B 340B1 CB |  | bbca | ELEM/D09_A1 | [8 empty] | 斗工DS.340B1_CB | 340B1(#2DTR) CB | MTR | [5 empty] | 132 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | 340B1 | #2DTR(B)(340B1) |  | E1 |  | ADD | Status | E1 | Close/Open | Y | 1 | DI-SP | [6 empty] | 0079 |  | 0045 | 1-09-07 |  | 1-2D | 340B1 | ON/OFF | #2DTR 1B 340B1 CB |  | bbca | ELEM/D09_A1 | [8 empty] | 斗工DS.340B1_CB | 340B1(#2DTR) CB | MTR | [5 empty] | 132 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | 340B2 | #2DTR(B)(340B2) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2B2Bus | A/340B1^T/2DTR(B) |  |  | 0077 |  | 0046 | 1-09-05 |  | 1-2E | 340B2 | ON/OFF | #2DTR 2B 340B2 CB |  | bcba | ELEM/D09_A1 | [8 empty] | 斗工DS.340B2_CB | 340B2(#2DTR) CB | MTR | [5 empty] | 133 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | 340B2 | #2DTR(B)(340B2) |  | DS1 |  | ADD | Status | DS | Close/Open | Y | 1 | DI-SP | [6 empty] | 0077 |  | 0046 | 1-09-05 |  | 1-2E | 340B2 | ON/OFF | #2DTR 2B 340B2 CB |  | bcba | ELEM/D09_A1 | [8 empty] | 斗工DS.340B2_CB | 340B2(#2DTR) CB | MTR | [5 empty] | 133 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | 340B2 | #2DTR(B)(340B2) |  | E1 |  | ADD | Status | E1 | Close/Open | Y | 1 | DI-SP | [6 empty] | 0077 |  | 0046 | 1-09-05 |  | 1-2E | 340B2 | ON/OFF | #2DTR 2B 340B2 CB |  | bcba | ELEM/D09_A1 | [8 empty] | 斗工DS.340B2_CB | 340B2(#2DTR) CB | MTR | [5 empty] | 133 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | 240 | #4SC(240) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2B2Bus | A/LBS240^C/4SC(A) |  |  | 0212 |  | 0047 | 1-1A-04 |  | 1-2F | 240 #4SC | ON/OFF | #2BSC 240 #4SC CB |  | bccb | B3/D09_A1 | [8 empty] | 斗工DS.240_CB | 240(11KV #4SC) CB | SC | [5 empty] | 134 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | XU38 | 工十八線(XU38) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2B2Bus | L/XU38/T1 |  |  | 0203 |  | 0048 | 1-19-03 |  | 1-30 | F18 | ON/OFF | F18 CB 工十八線 XU38 |  | bcdb | B2/D09_D1 | [8 empty] | 斗工DS.XU38_CB | XU38(11KV工十八線) CB | FEEDER | [5 empty] | 135 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | XU39 | 工十九線(XU39) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2B2Bus | L/XU39/T1 |  |  | 0206 |  | 0049 | 1-19-06 |  | 1-31 | F19 | ON/OFF | F19 CB 工十九線 XU39 |  | bceb | B2/D09_D1 | [8 empty] | 斗工DS.XU39_CB | XU39(11KV工十九線) CB | FEEDER | [5 empty] | 136 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | XU40 | 工二十線(XU40) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2B2Bus | L/XU40/T1 |  |  | 0209 |  | 0050 | 1-1A-01 |  | 1-32 | F20 | ON/OFF | F20 CB 工二十線 XU40 |  | bcfb | B2/D09_D1 | [8 empty] | 斗工DS.XU40_CB | XU40(11KV工二十線) CB | FEEDER | [5 empty] | 137 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | 400 | TIE(400) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2B2Bus | A/200/N1 |  |  | 0215 |  | 0051 | 1-1A-07 |  | 1-33 | 400 | ON/OFF | #2TIE 2B 400 CB |  | bcgb | B3/D09_A1 | [8 empty] | 斗工DS.400_CB | 400(TIE) CB | TIE | [5 empty] | 138 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D09 | 斗工DS |  |  | 1DTR | #1DTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0928 |  | 0052 | 2-3A-08 |  | 1-34 | #1DTR | U/L | #1DTR #1 87RY U/L |  |  | B1/D09_A1 | [8 empty] | 斗工DS.#1DTR_87UL1 | #1DTR #1 87RY U/L | OTHER | [5 empty] | 139 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS |  |  | 1DTR | #1DTR |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0929 |  | 0053 | 2-3A-09 |  | 1-35 | #1DTR | U/L | #1DTR #2 87RY U/L |  |  | B1/D09_A1 | [8 empty] | 斗工DS.#1DTR_87UL2 | #1DTR #2 87RY U/L | OTHER | [5 empty] | 140 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS |  |  | 1DTR | #1DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0930 |  | 0054 | 2-3A-10 |  | 1-36 | #1DTR | U/L | #1DTR 51Z RY U/L |  |  | B1/D09_A1 | [8 empty] | 斗工DS.#1DTR_51ZUL | #1DTR 51ZRY U/L | OTHER | [5 empty] | 141 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS |  |  | 2DTR | #2DTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0932 |  | 0055 | 2-3A-12 |  | 1-37 | #2DTR | U/L | #2DTR #1 87RY U/L |  |  | B1/D09_A1 | [8 empty] | 斗工DS.#2DTR_87UL1 | #2DTR #1 87RY U/L | OTHER | [5 empty] | 142 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS |  |  | 2DTR | #2DTR |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0933 |  | 0056 | 2-3A-13 |  | 1-38 | #2DTR | U/L | #2DTR #2 87RY U/L |  |  | B1/D09_A1 | [8 empty] | 斗工DS.#2DTR_87UL2 | #2DTR #2 87RY U/L | OTHER | [5 empty] | 143 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS |  |  | 2DTR | #2DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0934 |  | 0057 | 2-3A-14 |  | 1-39 | #2DTR | U/L | #2DTR 51Z RY U/L |  |  | B1/D09_A1 | [8 empty] | 斗工DS.#2DTR_51ZUL | #2DTR 51ZRY U/L | OTHER | [5 empty] | 144 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 11 | 11kV | LBS220 | #2SC(220) |  | LBS |  | Element | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/220 | C/2SC(B) |  |  | 0255 |  | 0067 | 1-1F-07 |  | 1-43 | 220 #2SC | LBS | #2SC 220 LBS |  |  | B3/D09_A1 | [8 empty] | 斗工DS.220_LBS | 220(11KV #2SC) LBS | SC | [5 empty] | 145 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | LBS240 | #4SC(240) |  | LBS |  | Element | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/240 | C/4SC(B) |  |  | 0385 |  | 0069 | 2-10-01 |  | 1-45 | 240 #4SC | LBS | #4SC 240 LBS |  |  | B3/D09_A1 | [8 empty] | 斗工DS.240_LBS | 240(11KV #4SC) LBS | SC | [5 empty] | 146 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工～斗工山線(1510) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0514 |  | 0072 | 1-30-02 |  | 1-48 | 1510 | USE/LOCK | 鉅工斗工山線 1510 87RY UL1 |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1510_87UL1 | 鉅工山線(1510) #1 87RY U/L | LINE161 | [5 empty] | 147 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工～斗工山線(1510) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0515 |  | 0073 | 1-30-03 |  | 1-49 | 1510 | USE/LOCK | 鉅工斗工山線 1510 79RY U/L |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1510_79UL | 鉅工山線(1510) 79RY U/L | LINE161 | [5 empty] | 148 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工～斗工海線(1520) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0516 |  | 0074 | 1-30-04 |  | 1-4A | 1520 | USE/LOCK | 鉅工斗工海線 1520 87RY UL1 |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1520_87UL1 | 鉅工海線(1520) #1 87RY U/L | LINE161 | [5 empty] | 149 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工～斗工海線(1520) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0517 |  | 0075 | 1-30-05 |  | 1-4B | 1520 | USE/LOCK | 鉅工斗工海線 1520 79RY U/L |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1520_79UL | 鉅工海線(1520) 79RY U/L | LINE161 | [5 empty] | 150 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 161 | 161kV | 1540 | 雲林~斗工線(1540) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0518 |  | 0076 | 1-30-06 |  | 1-4C | 1540 | USE/LOCK | 雲林斗工線 1540 87RY U/L |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1540_87UL | 雲林斗工線(1540) 87RY U/L | LINE161 | [5 empty] | 151 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 161 | 161kV | 1540 | 雲林~斗工線(1540) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0519 |  | 0077 | 1-30-07 |  | 1-4D | 1540 | USE/LOCK | 雲林斗工線 1540 79RY U/L |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1540_79UL | 雲林斗工線(1540) 79RY U/L | LINE161 | [5 empty] | 152 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 161 | 161kV | 1530 | 嘉民～斗工紅線(1530) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0520 |  | 0078 | 1-30-08 |  | 1-4E | 1530 | USE/LOCK | 嘉民斗工紅線 1530 87RY U/L |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1530_87UL | 嘉民斗工紅線(1530) 87RY U/L | LINE161 | [5 empty] | 153 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 161 | 161kV | 1530 | 嘉民～斗工紅線(1530) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0521 |  | 0079 | 1-30-09 |  | 1-4F | 1530 | USE/LOCK | 嘉民斗工紅線 1530 79RY U/L |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1530_79UL | 嘉民斗工紅線(1530) 79RY U/L | LINE161 | [5 empty] | 154 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 161 | 161kV | 1550 | 斗工～富喬線(1550) |  | 85UL | 87UL | Element | Status | 85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0522 |  | 0080 | 1-30-10 |  | 1-50 | 1550 | USE/LOCK | 斗工富喬線 1550 85 RY U/L |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1550_85UL | 富喬線(1550) 85RY U/L | LINE161 | [5 empty] | 155 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 161 | 161kV | 1550 | 斗工～富喬線(1550) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0523 |  | 0081 | 1-30-11 |  | 1-51 | 1550 | USE/LOCK | 斗工富喬線 1550 79 RY U/L |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1550_79UL | 富喬線(1550) 79RY U/L | LINE161 | [5 empty] | 156 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 161 | 161kV | 1610 | 榴中～斗工一路(1610) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0528 |  | 0086 | 1-31-00 |  | 1-56 | 1610 | USE/LOCK | 榴中斗工一路 1610 87RY U/L |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1610_87UL | 榴中斗工一路(1610) 87RY U/L | LINE161 | [5 empty] | 157 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 161 | 161kV | 1610 | 榴中～斗工一路(1610) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0529 |  | 0087 | 1-31-01 |  | 1-57 | 1610 | USE/LOCK | 榴中斗工一路 1610 79RY U/L |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1610_79UL | 榴中斗工一路(1610) 79RY U/L | LINE161 | [5 empty] | 158 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 161 | 161kV | 1620 | 榴中～斗工二路(1620) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0530 |  | 0088 | 1-31-02 |  | 1-58 | 1620 | USE/LOCK | 榴中斗工二路 1620 87RY U/L |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1620_87UL | 榴中斗工二路(1620) 87RY U/L | LINE161 | [5 empty] | 159 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 161 | 161kV | 1620 | 榴中～斗工二路(1620) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0531 |  | 0089 | 1-31-03 |  | 1-59 | 1620 | USE/LOCK | 榴中斗工二路 1620 79RY U/L |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1620_79UL | 榴中斗工二路(1620) 79RY U/L | LINE161 | [5 empty] | 160 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS |  |  | 1DTR(A) | #1DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0538 |  | 0092 | 1-31-10 |  | 1-5C | #1ATR | OLTC A/M | #1ATR OLTC A/M |  |  | B1/D09_A1 | [8 empty] | 斗工DS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | [5 empty] | 161 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D09 | 斗工DS |  |  | 1DTR(A) | #1DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0030 |  | 0093 | 1-9E |  | 1-5D | #1ATR | 升/降 | #1ATR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D09_A1 | [8 empty] | 斗工DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | [5 empty] | 162 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D09 | 斗工DS |  |  | 1DTR(B) | #1DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0542 |  | 0094 | 1-31-14 |  | 1-5E | #1BTR | OLTC A/M | #1BTR OLTC A/M |  |  | B1/D09_A1 | [8 empty] | 斗工DS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | [5 empty] | 163 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D09 | 斗工DS |  |  | 1DTR(B) | #1DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0031 |  | 0095 | 1-9F |  | 1-5F | #1BTR | 升/降 | #1BTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D09_A1 | [8 empty] | 斗工DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | [5 empty] | 164 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D09 | 斗工DS |  |  | 2DTR(A) | #2DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0545 |  | 0096 | 1-32-01 |  | 1-60 | #2ATR | OLTC A/M | #2ATR OLTC A/M |  |  | B1/D09_A1 | [8 empty] | 斗工DS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | [5 empty] | 165 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D09 | 斗工DS |  |  | 2DTR(A) | #2DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0035 |  | 0097 | 1-A3 |  | 1-61 | #2ATR | 升/降 | #2ATR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D09_A1 | [8 empty] | 斗工DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | [5 empty] | 166 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D09 | 斗工DS |  |  | 2DTR(B) | #2DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0549 |  | 0098 | 1-32-05 |  | 1-62 | #2BTR | OLTC A/M | #2BTR OLTC A/M |  |  | B1/D09_A1 | [8 empty] | 斗工DS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | [5 empty] | 167 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D09 | 斗工DS |  |  | 2DTR(B) | #2DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0036 |  | 0099 | 1-A4 |  | 1-63 | #2BTR | 升/降 | #2BTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D09_A1 | [8 empty] | 斗工DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | [5 empty] | 168 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D09 | 斗工DS |  |  | 3DTR | #3DTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0039 |  | 0101 | 1-A7 |  | 1-65 | #3DTR | 升/降 | #3DTR TAP位置 |  |  | B1/D09_A1 | [16 empty] | 169 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D09 | 斗工DS | 161 | 161kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0534 |  | 0102 | 1-31-06 |  | 1-66 | #1 BUS | ON/OFF | 161KV #1 BUS╴87UL |  |  | B2/D09_A1 | [8 empty] | 斗工DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | [5 empty] | 170 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 161 | 161kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0535 |  | 0103 | 1-31-07 |  | 1-67 | #2 BUS | ON/OFF | 161KV #2 BUS╴87UL |  |  | B2/D09_A1 | [8 empty] | 斗工DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | [5 empty] | 171 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工～斗工山線(1510) |  | DS1 | 1511 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0576 | 577 | 0104 | 1-34-00 | 1-34-01 | 1-68 | 1511 | ON | 鉅工斗工山線 1511 ABS |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1511_DS | 1511(鉅工山線) DS | LINE161 | [5 empty] | 172 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工～斗工山線(1510) |  | DS2 | 1512 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0578 | 579 | 0105 | 1-34-02 | 1-34-03 | 1-69 | 1512 | ON | 鉅工斗工山線 1512 ABS |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1512_DS | 1512(鉅工山線) DS | LINE161 | [5 empty] | 173 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工～斗工山線(1510) |  | DS3 | 1513 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0580 | 581 | 0106 | 1-34-04 | 1-34-05 | 1-6A | 1513 | ON | 鉅工斗工山線 1513 ABS |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1513_DS | 1513(鉅工山線) DS | LINE161 | [5 empty] | 174 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工～斗工山線(1510) |  | ES3 | 1513E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0582 | 583 | 0107 | 1-34-06 | 1-34-07 | 1-6B | 1513E | ON | 鉅工斗工山線 1513E ABS |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1513E_ES | 1513E(鉅工山線) ES | LINE161 | [5 empty] | 175 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工～斗工海線(1520) |  | DS1 | 1521 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0584 | 585 | 0108 | 1-34-08 | 1-34-09 | 1-6C | 1521 | ON | 鉅工斗工海線 1521 ABS |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1521_DS | 1521(鉅工海線) DS | LINE161 | [5 empty] | 176 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工～斗工海線(1520) |  | DS2 | 1522 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0586 | 587 | 0109 | 1-34-10 | 1-34-11 | 1-6D | 1522 | ON | 鉅工斗工海線 1522 ABS |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1522_DS | 1522(鉅工海線) DS | LINE161 | [5 empty] | 177 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工～斗工海線(1520) |  | DS3 | 1523 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0588 | 589 | 0110 | 1-34-12 | 1-34-13 | 1-6E | 1523 | ON | 鉅工斗工海線 1523 ABS |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1523_DS | 1523(鉅工海線) DS | LINE161 | [5 empty] | 178 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工～斗工海線(1520) |  | ES3 | 1523E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0590 | 591 | 0111 | 1-34-14 | 1-34-15 | 1-6F | 1523E | ON | 鉅工斗工海線 1523E ABS |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1523E_ES | 1523E(鉅工海線) ES | LINE161 | [5 empty] | 179 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 161 | 161kV | 1540 | 雲林~斗工線(1540) |  | DS1 | 1541 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0592 | 593 | 0112 | 1-35-00 | 1-35-01 | 1-70 | 1541 | ON | 雲林斗工線 1541 ABS |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1541_DS | 1541(雲林斗工線) DS | LINE161 | [5 empty] | 180 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 161 | 161kV | 1540 | 雲林~斗工線(1540) |  | DS2 | 1542 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0594 | 595 | 0113 | 1-35-02 | 1-35-03 | 1-71 | 1542 | ON | 雲林斗工線 1542 ABS |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1542_DS | 1542(雲林斗工線) DS | LINE161 | [5 empty] | 181 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1540 | 雲林~斗工線(1540) |  | DS3 | 1543 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0596 | 597 | 0114 | 1-35-04 | 1-35-05 | 1-72 | 1543 | ON | 雲林斗工線 1543 ABS |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1543_DS | 1543(雲林斗工線) DS | LINE161 | [5 empty] | 182 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1540 | 雲林~斗工線(1540) |  | ES3 | 1543E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0598 | 599 | 0115 | 1-35-06 | 1-35-07 | 1-73 | 1543E | ON | 雲林斗工線 1543E ABS |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1543E_ES | 1543E(雲林斗工線) ES | LINE161 | [5 empty] | 183 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 161 | 161kV | 1530 | 嘉民～斗工紅線(1530) |  | DS1 | 1531 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0600 | 601 | 0116 | 1-35-08 | 1-35-09 | 1-74 | 1531 | ON | 嘉民斗工紅線 1531 ABS |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1531_DS | 1531(嘉民斗工紅線) DS | LINE161 | [5 empty] | 184 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1530 | 嘉民～斗工紅線(1530) |  | DS2 | 1532 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0602 | 603 | 0117 | 1-35-10 | 1-35-11 | 1-75 | 1532 | ON | 嘉民斗工紅線 1532 ABS |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1532_DS | 1532(嘉民斗工紅線) DS | LINE161 | [5 empty] | 185 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 161 | 161kV | 1530 | 嘉民～斗工紅線(1530) |  | DS3 | 1533 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0604 | 605 | 0118 | 1-35-12 | 1-35-13 | 1-76 | 1533 | ON | 嘉民斗工紅線 1533 ABS |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1533_DS | 1533(嘉民斗工紅線) DS | LINE161 | [5 empty] | 186 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1530 | 嘉民～斗工紅線(1530) |  | ES3 | 1533E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0606 | 607 | 0119 | 1-35-14 | 1-35-15 | 1-77 | 1533E | ON | 嘉民斗工紅線 1533E ABS |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1533E_ES | 1533E(嘉民斗工紅線) ES | LINE161 | [5 empty] | 187 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 161 | 161kV | 1550 | 斗工～富喬線(1550) |  | DS1 | 1551 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0864 | 865 | 0120 | 2-36-00 | 2-36-01 | 1-78 | 1551 | ON | 斗工富喬線 1551ABS |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1551_DS | 1551(富喬線) DS | LINE161 | [5 empty] | 188 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1550 | 斗工～富喬線(1550) |  | DS2 | 1552 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0866 | 867 | 0121 | 2-36-02 | 2-36-03 | 1-79 | 1552 | ON | 斗工富喬線 1552ABS |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1552_DS | 1552(富喬線) DS | LINE161 | [5 empty] | 189 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 161 | 161kV | 1550 | 斗工～富喬線(1550) |  | DS3 | 1553 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0868 | 869 | 0122 | 2-36-04 | 2-36-05 | 1-7A | 1553 | ON | 斗工富喬線 1553ABS |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1553_DS | 1553(富喬線) DS | LINE161 | [5 empty] | 190 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1550 | 斗工～富喬線(1550) |  | ES3 | 1553E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0870 | 871 | 0123 | 2-36-06 | 2-36-07 | 1-7B | 1553E | ON | 斗工富喬線 1553EABS |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1553E_ES | 1553E(富喬線) ES | LINE161 | [5 empty] | 191 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 161 | 161kV | 1610 | 榴中～斗工一路(1610) |  | DS1 | 1611 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0888 | 889 | 0132 | 2-37-08 | 2-37-09 | 2-04 | 1611 | ON | 榴中斗工一路 1611 ABS |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1611_DS | 1611(榴中斗工一路) DS | LINE161 | [5 empty] | 192 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1610 | 榴中～斗工一路(1610) |  | DS2 | 1612 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0890 | 891 | 0133 | 2-37-10 | 2-37-11 | 2-05 | 1612 | ON | 榴中斗工一路 1612 ABS |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1612_DS | 1612(榴中斗工一路) DS | LINE161 | [5 empty] | 193 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 161 | 161kV | 1610 | 榴中～斗工一路(1610) |  | DS3 | 1613 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0892 | 893 | 0134 | 2-37-12 | 2-37-13 | 2-06 | 1613 | ON | 榴中斗工一路 1613 ABS |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1613_DS | 1613(榴中斗工一路) DS | LINE161 | [5 empty] | 194 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1610 | 榴中～斗工一路(1610) |  | ES3 | 1613E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0894 | 895 | 0135 | 2-37-14 | 2-37-15 | 2-07 | 1613E | ON | 榴中斗工一路 1613E ABS |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1613E_ES | 1613E(榴中斗工一路) ES | LINE161 | [5 empty] | 195 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 161 | 161kV | 1620 | 榴中～斗工二路(1620) |  | DS1 | 1621 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0896 | 897 | 0136 | 2-38-00 | 2-38-01 | 2-08 | 1621 | ON | 榴中斗工二路 1621 ABS |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1621_DS | 1621(榴中斗工二路) DS | LINE161 | [5 empty] | 196 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 161 | 161kV | 1620 | 榴中～斗工二路(1620) |  | DS2 | 1622 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0898 | 899 | 0137 | 2-38-02 | 2-38-03 | 2-09 | 1622 | ON | 榴中斗工二路 1622 ABS |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1622_DS | 1622(榴中斗工二路) DS | LINE161 | [5 empty] | 197 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1620 | 榴中～斗工二路(1620) |  | DS3 | 1623 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0900 | 901 | 0138 | 2-38-04 | 2-38-05 | 2-0A | 1623 | ON | 榴中斗工二路 1623 ABS |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1623_DS | 1623(榴中斗工二路) DS | LINE161 | [5 empty] | 198 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1620 | 榴中～斗工二路(1620) |  | ES3 | 1623E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0902 | 903 | 0139 | 2-38-06 | 2-38-07 | 2-0B | 1623E | ON | 榴中斗工二路 1623E ABS |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1623E_ES | 1623E(榴中斗工二路) ES | LINE161 | [5 empty] | 199 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0912 | 913 | 0144 | 2-39-00 | 2-39-01 | 2-10 | 1501 | ON | 161KV 1501 ABS |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1501_DS | 1501(TIE) DS | TIE | [5 empty] | 200 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0914 | 915 | 0145 | 2-39-02 | 2-39-03 | 2-11 | 1502 | ON | 161KV 1502 ABS |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1502_DS | 1502(TIE) DS | TIE | [5 empty] | 201 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0916 | 917 | 0146 | 2-39-04 | 2-39-05 | 2-12 | 1751 | ON | #1DTR 1751 ABS |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1751_DS | 1751(#1DTR) DS | MTR | [5 empty] | 202 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0918 | 919 | 0147 | 2-39-06 | 2-39-07 | 2-13 | 1752 | ON | #1DTR 1752 ABS |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1752_DS | 1752(#1DTR) DS | MTR | [5 empty] | 203 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0920 | 921 | 0148 | 2-39-08 | 2-39-09 | 2-14 | 1761 | ON | #2DTR 1761 ABS |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1761_DS | 1761(#2DTR) DS | MTR | [5 empty] | 204 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0922 | 923 | 0149 | 2-39-10 | 2-39-11 | 2-15 | 1762 | ON | #2DTR 1762 ABS |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1762_DS | 1762(#2DTR) DS | MTR | [5 empty] | 205 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工～斗工山線(1510) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0855 |  | 0152 | 2-35-07 |  | 2-18 | 1510 | USE/LOCK | 鉅工斗工山線 1510 87RY UL2 |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1510_87UL2 | 鉅工山線(1510) #2 87RY U/L | LINE161 | [5 empty] | 206 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工～斗工海線(1520) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0856 |  | 0153 | 2-35-08 |  | 2-19 | 1520 | USE/LOCK | 鉅工斗工海線 1520 87RY UL2 |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1520_87UL2 | 鉅工海線(1520) #2 87RY U/L | LINE161 | [5 empty] | 207 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 0 |  | ComPoint |  |  | 81AS1 | 工十六線 工十七線 工十八線、工八線、工九線、工十線 |  | Status | 81RY A/S(1) | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0388 |  | 0154 | 2-10-04 |  | 2-1A | F16,F17,F18F8,F9,F10 | 81A | 工十六線 工十七線 工十八線、工八線、工九線、工十線81 RY 動作 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.81RY_A/S(2) | XU(36_37_38_28_29_30)81RY動作 | OTHER | [5 empty] | 208 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
D09 | 斗工DS | 0 |  | ComPoint |  |  | 81AS2 | F7 工七線、F6 工六線 |  | Status | 81RY A/S(2) | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0389 |  | 0155 | 2-10-05 |  | 2-1B | F6，F7 | 81A | F7 工七線、F6 工六線 低頻電驛動作 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.81RY_A/S(1) | XU26 XU27低頻電驛動作/復歸 | OTHER | [5 empty] | 209 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
D09 | 斗工DS | 0 |  | ComPoint |  |  | 81AS3 | 330A1,330A2 |  | Status | 81RY A/S(3) | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0390 |  | 0156 | 2-10-06 |  | 2-1C | 330A1,330A2 | 81A | 330A1,330A2 低頻電驛動作 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.81RY_A/S(3) | 330A1 330A2低頻電驛動作/復歸 | OTHER | [5 empty] | 210 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
D09 | 斗工DS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0823 |  | 0157 | 2-33-07 |  | 2-1D | ACB2 | ON/OFF | 所內電源 ACB2 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | [5 empty] | 211 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D09 | 斗工DS | 0 |  | StaDev | 所內設施 |  | Lights1 |  |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0819 |  | 0158 | 2-33-03 |  | 2-1E | Locate Empty | ON/OFF | 開關場照明(A) |  |  | B3/D09_A1 | [8 empty] | 斗工DS.開關場照明(A) | 開關場照明(A) | OTHER | [5 empty] | 212 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
D09 | 斗工DS | 0 |  | StaDev | 所內設施 |  | Lights2 |  |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0820 |  | 0159 | 2-33-04 |  | 2-1F | Locate Empty | ON/OFF | 開關場照明(B) |  |  | B3/D09_A1 | [8 empty] | 斗工DS.開關場照明(B) | 開關場照明(B) | OTHER | [5 empty] | 213 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
D09 | 斗工DS | 22 | 22kV | XU51 | 工五一線(XU51) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0768 |  | 0160 | 2-30-00 |  | 2-20 | F1 | USE/LOCK | F1 工五一線 XU51 79RY U/L |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU51_79UL | 23KV工五一線(XU51) 79RY U/L | FEEDER | [5 empty] | 214 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 22 | 22kV | XU52 | 工五二線(XU52) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0769 |  | 0161 | 2-30-01 |  | 2-21 | F2 | USE/LOCK | F2 工五二線 XU52 79RY U/L |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU52_79UL | 23KV工五二線(XU52) 79RY U/L | FEEDER | [5 empty] | 215 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 22 | 22kV | XU53 | 工五三線(XU53) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0770 |  | 0162 | 2-30-02 |  | 2-22 | F3 | USE/LOCK | F3 工五三線 XU53 79RY U/L |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU53_79UL | 23KV工五三線(XU53) 79RY U/L | FEEDER | [5 empty] | 216 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 22 | 22kV | XU54 | 工五四線(XU54) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0771 |  | 0163 | 2-30-03 |  | 2-23 | F4 | USE/LOCK | F4 工五四線 XU54 79RY U/L |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU54_79UL | 23KV工五四線(XU54) 79RY U/L | FEEDER | [5 empty] | 217 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 22 | 22kV | XU55 | 工五五線(XU55) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0772 |  | 0164 | 2-30-04 |  | 2-24 | F5 | USE/LOCK | F5 工五五線 XU55 79 RY U/L |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU55_79UL | 23KV工五五線(XU55) 79RY U/L | FEEDER | [5 empty] | 218 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 22 | 22kV | 210 | #1SC(210) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0773 |  | 0165 | 2-30-05 |  | 2-25 | 210 #1SC | ON/OFF | #1A 210 #1SC Q-CTL A/M |  |  | B3/D09_A1 | [8 empty] | 斗工DS.210_A/M | 23KV #1SC 乏控器 A/M | SC | [5 empty] | 219 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D09 | 斗工DS | 11 | 11kV | XU26 | 工六線(XU26) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0775 |  | 0167 | 2-30-07 |  | 2-27 | F6 | USE/LOCK | F6 工六線 XU61 79RY U/L |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU26_79UL | 11KV工六線(XU26) 79RY U/L | FEEDER | [5 empty] | 220 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 11 | 11kV | XU27 | 工七線(XU27) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0776 |  | 0168 | 2-30-08 |  | 2-28 | F7 | USE/LOCK | F7 工七線 XU27 79RY U/L |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU27_79UL | 11KV工七線(XU27) 79RY U/L | FEEDER | [5 empty] | 221 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 11 | 11kV | XU28 | 工八線(XU28) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0777 |  | 0169 | 2-30-09 |  | 2-29 | F8 | USE/LOCK | F8 工八線 XU28 79RY U/L |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU28_79UL | 11KV工八線(XU28) 79RY U/L | FEEDER | [5 empty] | 222 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 11 | 11kV | XU29 | 工九線(XU29) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0778 |  | 0170 | 2-30-10 |  | 2-2A | F9 | USE/LOCK | F9 工九線 XU29 79RY U/L |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU29_79UL | 11KV工九線(XU29) 79RY U/L | FEEDER | [5 empty] | 223 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 11 | 11kV | XU30 | 工十線(XU30) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0779 |  | 0171 | 2-30-11 |  | 2-2B | F10 | USE/LOCK | F10 工十線 XU30 79RY U/L |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU30_79UL | 11KV工十線(XU30) 79RY U/L | FEEDER | [5 empty] | 224 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0780 |  | 0172 | 2-30-12 |  | 2-2C | 220 #2SC | ON/OFF | #1B 220 #2SC Q-CTL A/M |  |  | B3/D09_A1 | [8 empty] | 斗工DS.220_A/M | 11KV #2SC 乏控器 A/M | SC | [5 empty] | 225 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D09 | 斗工DS | 11 | 11kV | 220 | #2SC(220) |  | 1A5A_M | 乏控器 A/M2(請TPC確認) | INSERT | Status | A_M動作1 | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0781 |  | 0173 | 2-30-13 |  | 2-2D | 220 #2SC | ON/OFF | #1B 220 #2SC Q-CTL A/M-1 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.220_LBS_A/M | 11KV #2SC LBS 乏控器 A/M | SC | [5 empty] | 226 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D09 | 斗工DS | 22 | 22kV | XU61 | 工六一線(XU61) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0782 |  | 0174 | 2-30-14 |  | 2-2E | F11 | USE/LOCK | F11 工六一線 XU61 79RY U/L |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU61_79UL | 23KV工六一線(XU61) 79RY U/L | FEEDER | [5 empty] | 227 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 22 | 22kV | XU62 | 工六二線(XU62) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0783 |  | 0175 | 2-30-15 |  | 2-2F | F12 | USE/LOCK | F12 工六二線 XU62 79RY U/L |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU62_79UL | 23KV工六二線(XU62) 79RY U/L | FEEDER | [5 empty] | 228 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 22 | 22kV | XU63 | 工六三線(XU63) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0784 |  | 0176 | 2-31-00 |  | 2-30 | F13 | USE/LOCK | F13 工六三線 XU63 79RY U/L |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU63_79UL | 23KV工六三線(XU63) 79RY U/L | FEEDER | [5 empty] | 229 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 22 | 22kV | XU64 | 工六四線(XU64) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0785 |  | 0177 | 2-31-01 |  | 2-31 | F14 | USE/LOCK | F14 工六四線 XU64 79RY U/L |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU64_79UL | 23KV工六四線(XU64) 79RY U/L | FEEDER | [5 empty] | 230 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 22 | 22kV | XU65 | 工六五線(XU65) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0786 |  | 0178 | 2-31-02 |  | 2-32 | F15 | USE/LOCK | F15 工六五線 XU65 79RY U/L |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU65_79UL | 23KV工六五線(XU65) 79RY U/L | FEEDER | [5 empty] | 231 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 22 | 22kV | 230 | #3SC(230) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0787 |  | 0179 | 2-31-03 |  | 2-33 | 230 #3SC | ON/OFF | #2A1 230 #3SC Q-CTL A/M |  |  | B3/D09_A1 | [8 empty] | 斗工DS.230_A/M | 23KV #3SC 乏控器 A/M | SC | [5 empty] | 232 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D09 | 斗工DS | 22 | 22kV | 230 | #3SC(230) |  | 1A5A_M | 乏控器 A/M2(請TPC確認) | INSERT | Status | A_M動作1 | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0788 |  | 0180 | 2-31-11 |  | 2-3B | 230 #3SC | ON/OFF | #2B2 230 #3SC Q-CTL A/M-1 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.240_LBS_A/M | 11KV #4SC LBS 乏控器 A/M | SC | [5 empty] | 233 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D09 | 斗工DS | 11 | 11kV | XU36 | 工十六線(XU36) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0789 |  | 0181 | 2-31-05 |  | 2-35 | F16 | USE/LOCK | F16 工十六線 XU36 79RY U/L |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU36_79UL | 11KV工十六線(XU36) 79RY U/L | FEEDER | [5 empty] | 234 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 11 | 11kV | XU37 | 工十七線(XU37) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0790 |  | 0182 | 2-31-06 |  | 2-36 | F17 | USE/LOCK | F17 工十七線 XU37 79RY U/L |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU37_79UL | 11KV工十七線(XU37) 79RY U/L | FEEDER | [5 empty] | 235 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 11 | 11kV | XU38 | 工十八線(XU38) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0791 |  | 0183 | 2-31-07 |  | 2-37 | F18 | USE/LOCK | F18 工十八線 XU38 79RY U/L |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU38_79UL | 11KV工十八線(XU38) 79RY U/L | FEEDER | [5 empty] | 236 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 11 | 11kV | XU39 | 工十九線(XU39) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0792 |  | 0184 | 2-31-08 |  | 2-38 | F19 | USE/LOCK | F19 工十九線 XU39 79RY U/L |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU39_79UL | 11KV工十九線(XU39) 79RY U/L | FEEDER | [5 empty] | 237 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 11 | 11kV | XU40 | 工二十線(XU40) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0793 |  | 0185 | 2-31-09 |  | 2-39 | F20 | USE/LOCK | F20 工二十線 XU40 79RY U/L |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU40_79UL | 11KV工二十線(XU40) 79RY U/L | FEEDER | [5 empty] | 238 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D09 | 斗工DS | 11 | 11kV | 240 | #4SC(240) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0794 |  | 0186 | 2-31-10 |  | 2-3A | 240 #4SC | ON/OFF | #2B2 240 #4SC Q-CTL A/M |  |  | B3/D09_A1 | [8 empty] | 斗工DS.240_A/M | 11KV #4SC 乏控器 A/M | SC | [5 empty] | 239 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D09 | 斗工DS | 22 | 22kV | XU51 | 工五一線(XU51) |  | 50N_51N |  |  | Status | 50N/51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0796 |  | 0188 | 2-31-12 |  | 2-3C | F1 | ON/OFF | F1 工五一線 XU51 51NS |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU51_LCO_TAP | 23KV工五一線(XU51) LCO TAP | FEEDER | [5 empty] | 240 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D09 | 斗工DS | 22 | 22kV | XU52 | 工五二線(XU52) |  | 50N_51N |  |  | Status | 50N/51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0797 |  | 0189 | 2-31-13 |  | 2-3D | F2 | ON/OFF | F2 工五二線 XU52 51NS |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU52_LCO_TAP | 23KV工五二線(XU52) LCO TAP | FEEDER | [5 empty] | 241 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D09 | 斗工DS | 22 | 22kV | XU53 | 工五三線(XU53) |  | 50N_51N |  |  | Status | 50N/51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0798 |  | 0190 | 2-31-14 |  | 2-3E | F3 | ON/OFF | F3 工五三線 XU53 51NS |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU53_LCO_TAP | 23KV工五三線(XU53) LCO TAP | FEEDER | [5 empty] | 242 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D09 | 斗工DS | 22 | 22kV | XU54 | 工五四線(XU54) |  | 50N_51N |  |  | Status | 50N/51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0799 |  | 0191 | 2-31-15 |  | 2-3F | F4 | ON/OFF | F4 工五四線 XU54 51NS |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU54_LCO_TAP | 23KV工五四線(XU54) LCO TAP | FEEDER | [5 empty] | 243 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D09 | 斗工DS | 22 | 22kV | XU55 | 工五五線(XU55) |  | 50N_51N |  |  | Status | 50N/51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0800 |  | 0192 | 2-32-00 |  | 2-40 | F5 | ON/OFF | F5 工五五線 XU55 51NS |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU55_LCO_TAP | 23KV工五五線(XU55) LCO TAP | FEEDER | [5 empty] | 244 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D09 | 斗工DS | 11 | 11kV | XU26 | 工六線(XU26) |  | 50N_51N |  |  | Status | 50N/51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0801 |  | 0193 | 2-32-01 |  | 2-41 | F6 | ON/OFF | F6 工六線 XU61 51NS |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU26_LCO_TAP | 11KV工六線(XU26) LCO TAP | FEEDER | [5 empty] | 245 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D09 | 斗工DS | 11 | 11kV | XU27 | 工七線(XU27) |  | 50N_51N |  |  | Status | 50N/51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0802 |  | 0194 | 2-32-02 |  | 2-42 | F7 | ON/OFF | F7 工七線 XU27 51NS |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU27_LCO_TAP | 11KV工七線(XU27) LCO TAP | FEEDER | [5 empty] | 246 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D09 | 斗工DS | 11 | 11kV | XU28 | 工八線(XU28) |  | 50N_51N |  |  | Status | 50N/51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0803 |  | 0195 | 2-32-03 |  | 2-43 | F8 | ON/OFF | F8 工八線 XU28 51NS |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU28_LCO_TAP | 11KV工八線(XU28) LCO TAP | FEEDER | [5 empty] | 247 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D09 | 斗工DS | 11 | 11kV | XU29 | 工九線(XU29) |  | 50N_51N |  |  | Status | 50N/51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0804 |  | 0196 | 2-32-04 |  | 2-44 | F9 | ON/OFF | F9 工九線 XU29 51NS |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU29_LCO_TAP | 11KV工九線(XU29) LCO TAP | FEEDER | [5 empty] | 248 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D09 | 斗工DS | 11 | 11kV | XU30 | 工十線(XU30) |  | 50N_51N |  |  | Status | 50N/51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0805 |  | 0197 | 2-32-05 |  | 2-45 | F10 | ON/OFF | F10 工十線 XU30 51NS |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU30_LCO_TAP | 11KV工十線(XU30) LCO TAP | FEEDER | [5 empty] | 249 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D09 | 斗工DS | 22 | 22kV | XU61 | 工六一線(XU61) |  | 50N_51N |  |  | Status | 50N/51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0806 |  | 0198 | 2-32-06 |  | 2-46 | F11 | ON/OFF | F11 工六一線 XU61 51NS |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU61_LCO_TAP | 23KV工六一線(XU61) LCO TAP | FEEDER | [5 empty] | 250 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D09 | 斗工DS | 22 | 22kV | XU62 | 工六二線(XU62) |  | 50N_51N |  |  | Status | 50N/51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0807 |  | 0199 | 2-32-07 |  | 2-47 | F12 | ON/OFF | F12 工六二線 XU62 51NS |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU62_LCO_TAP | 23KV工六二線(XU62) LCO TAP | FEEDER | [5 empty] | 251 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D09 | 斗工DS | 22 | 22kV | XU63 | 工六三線(XU63) |  | 50N_51N |  |  | Status | 50N/51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0808 |  | 0200 | 2-32-08 |  | 2-48 | F13 | ON/OFF | F13 工六三線 XU63 51NS |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU63_LCO_TAP | 23KV工六三線(XU63) LCO TAP | FEEDER | [5 empty] | 252 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D09 | 斗工DS | 22 | 22kV | XU64 | 工六四線(XU64) |  | 50N_51N |  |  | Status | 50N/51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0809 |  | 0201 | 2-32-09 |  | 2-49 | F14 | ON/OFF | F14 工六四線 XU64 51NS |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU64_LCO_TAP | 23KV工六四線(XU64) LCO TAP | FEEDER | [5 empty] | 253 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D09 | 斗工DS | 22 | 22kV | XU65 | 工六五線(XU65) |  | 50N_51N |  |  | Status | 50N/51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0858 |  | 0202 | 2-35-10 |  | 2-4A | F15 | ON/OFF | F15 工六五線 XU65 51NS |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU65_LCO_TAP | 23KV工六五線(XU65) LCO TAP | FEEDER | [5 empty] | 254 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D09 | 斗工DS | 11 | 11kV | XU36 | 工十六線(XU36) |  | 50N_51N |  |  | Status | 50N/51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0859 |  | 0203 | 2-35-11 |  | 2-4B | F16 | ON/OFF | F16 工十六線 XU36 51NS |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU36_LCO_TAP | 11KV工十六線(XU36) LCO TAP | FEEDER | [5 empty] | 255 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D09 | 斗工DS | 11 | 11kV | XU37 | 工十七線(XU37) |  | 50N_51N |  |  | Status | 50N/51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0860 |  | 0204 | 2-35-12 |  | 2-4C | F17 | ON/OFF | F17 工十七線 XU37 51NS |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU37_LCO_TAP | 11KV工十七線(XU37) LCO TAP | FEEDER | [5 empty] | 256 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D09 | 斗工DS | 11 | 11kV | XU38 | 工十八線(XU38) |  | 50N_51N |  |  | Status | 50N/51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0861 |  | 0205 | 2-35-13 |  | 2-4D | F18 | ON/OFF | F18 工十八線 XU38 51NS |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU38_LCO_TAP | 11KV工十八線(XU38) LCO TAP | FEEDER | [5 empty] | 257 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D09 | 斗工DS | 11 | 11kV | XU39 | 工十九線(XU39) |  | 50N_51N |  |  | Status | 50N/51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0862 |  | 0206 | 2-35-14 |  | 2-4E | F19 | ON/OFF | F19 工十九線 XU39 51NS |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU39_LCO_TAP | 11KV工十九線(XU39) LCO TAP | FEEDER | [5 empty] | 258 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D09 | 斗工DS | 11 | 11kV | XU40 | 工二十線(XU40) |  | 50N_51N |  |  | Status | 50N/51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0863 |  | 0207 | 2-35-15 |  | 2-4F | F20 | ON/OFF | F20 工二十線 XU40 51NS |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU40_LCO_TAP | 11KV工二十線(XU40) LCO TAP | FEEDER | [5 empty] | 259 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D09 | 斗工DS | 0 |  | RTU | RTU |  | ADCL1 |  |  | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | [5 empty] | 260 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 0 |  | RTU | RTU |  | ADCH1 |  |  | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.1 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | [5 empty] | 261 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 161KV | KV | 161KV #1BUS 電壓 | kV_-210_210(-2000_2000) | aaa | B2/D09_A1 | [8 empty] | 斗工DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | [5 empty] | 262 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D09 | 斗工DS | 161 | 161kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0003 |  |  | 1-83 |  |  | 161KV | KV | 161KV #2BUS 電壓 | kV_-210_210(-2000_2000) | aab | B2/D09_A1 | [8 empty] | 斗工DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | [5 empty] | 263 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工～斗工山線(1510) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 1510 | MW | 鉅工斗工山線 1510 瓦 | MW_-560_560(-2000_2000) |  | B2/D09_A1 | [8 empty] | 斗工DS.1510_MW | 鉅工山線 MW | LINE161 | [5 empty] | 264 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工～斗工山線(1510) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 1510 | NVAR | 鉅工斗工山線 1510 乏 | MVAR_-560_560(-2000_2000) |  | B2/D09_A1 | [8 empty] | 斗工DS.1510_MVAR | 鉅工山線 MVAR | LINE161 | [5 empty] | 265 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工～斗工海線(1520) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 1520 | MW | 鉅工斗工海線 1520 瓦 | MW_-560_560(-2000_2000) |  | B2/D09_A1 | [8 empty] | 斗工DS.1520_MW | 鉅工海線 MW | LINE161 | [5 empty] | 266 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工～斗工海線(1520) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 1520 | NVAR | 鉅工斗工海線 1520 乏 | MVAR_-560_560(-2000_2000) |  | B2/D09_A1 | [8 empty] | 斗工DS.1520_MVAR | 鉅工海線 MVAR | LINE161 | [5 empty] | 267 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1540 | 雲林~斗工線(1540) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | 1540 | MW | 雲林斗工線 1540 瓦 | MW_-560_560(-2000_2000) |  | B2/D09_A1 | [8 empty] | 斗工DS.1540_MW | 雲林斗工線 MW | LINE161 | [5 empty] | 268 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1540 | 雲林~斗工線(1540) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 1540 | NVAR | 雲林斗工線 1540 乏 | MVAR_-560_560(-2000_2000) |  | B2/D09_A1 | [8 empty] | 斗工DS.1540_MVAR | 雲林斗工線 MVAR | LINE161 | [5 empty] | 269 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1530 | 嘉民～斗工紅線(1530) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | 1530 | MW | 嘉民斗工紅線 1530 瓦 | MW_-560_560(-2000_2000) |  | B2/D09_A1 | [8 empty] | 斗工DS.1530_MW | 嘉民斗工紅線 MW | LINE161 | [5 empty] | 270 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1530 | 嘉民～斗工紅線(1530) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | 1530 | NVAR | 嘉民斗工紅線 1530 乏 | MVAR_-560_560(-2000_2000) |  | B2/D09_A1 | [8 empty] | 斗工DS.1530_MVAR | 嘉民斗工紅線 MVAR | LINE161 | [5 empty] | 271 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1550 | 斗工～富喬線(1550) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0012 |  |  | 1-8C |  |  | 1550 | MW | 斗工富喬線 1550 瓦 | MW_-560_560(-2000_2000) |  | B2/D09_A1 | [8 empty] | 斗工DS.1550_MW | 富喬線 MW | LINE161 | [5 empty] | 272 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1550 | 斗工～富喬線(1550) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0013 |  |  | 1-8D |  |  | 1550 | NVAR | 斗工富喬線 1550 瓦 | MVAR_-560_560(-2000_2000) |  | B2/D09_A1 | [8 empty] | 斗工DS.1550_MVAR | 富喬線 MVAR | LINE161 | [5 empty] | 273 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1610 | 榴中～斗工一路(1610) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | 1610 | MW | 榴中斗工一路 1610 瓦 | MW_-560_560(-2000_2000) |  | B2/D09_A1 | [8 empty] | 斗工DS.1610_MW | 榴中斗工一路 MW | LINE161 | [5 empty] | 274 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1610 | 榴中～斗工一路(1610) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | 1610 | NVAR | 榴中斗工一路 1610 乏 | MVAR_-560_560(-2000_2000) |  | B2/D09_A1 | [8 empty] | 斗工DS.1610_MVAR | 榴中斗工一路 MVAR | LINE161 | [5 empty] | 275 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1620 | 榴中～斗工二路(1620) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | 1620 | MW | 榴中斗工二路 1620 瓦 | MW_-560_560(-2000_2000) |  | B2/D09_A1 | [8 empty] | 斗工DS.1620_MW | 榴中斗工二路 MW | LINE161 | [5 empty] | 276 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1620 | 榴中～斗工二路(1620) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | 1620 | NVAR | 榴中斗工二路 1620 乏 | MVAR_-560_560(-2000_2000) |  | B2/D09_A1 | [8 empty] | 斗工DS.1620_MVAR | 榴中斗工二路 MVAR | LINE161 | [5 empty] | 277 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D09 | 斗工DS | 0 |  | StaDev | 所內設施 |  | DCV_P |  |  | MvMoment | 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0024 |  |  | 1-98 |  |  | DCV | 65 | DC-P電壓 | kV_-150_150(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.直流P電源電壓 | 直流P電源電壓 | OTHER | [5 empty] | 278 |  |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 | 0.01 | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D09 | 斗工DS | 0 |  | StaDev | 所內設施 |  | DCV_N |  |  | MvMoment | 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | DCV | -65 | DC-N電壓 | kV_-150_150(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.直流N電源電壓 | 直流N電源電壓 | OTHER | [5 empty] | 279 |  |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 | 0.01 | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1500 | TIE(1500) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | 1500 | A | 161KV TIE R相電流 | A_-2000_2000(-2000_2000) |  | B2/D09_A1 | [8 empty] | 斗工DS.1500TIE_AMP | 1500TIE AMP | TIE | [5 empty] | 280 |  |  |  |  | AI | [5 empty] | C20R1600 | 1520 | 1600 | 1760 | 1968 | 2.27 | -1520 | -1600 | -1760 | -1968 | 1 | 0.01 | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS |  |  | 1DTR | #1DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0027 |  |  | 1-9B |  |  | #1DTR | ℃ | #1DTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/D09_A1 | [8 empty] | 斗工DS.#1DTR_OIL | #1DTR 油溫 | MTR | [5 empty] | 281 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D09 | 斗工DS |  |  | 1DTR(A) | #1DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | #1ATR | ℃ | #1ATR 線溫 | COIL_-120_120(-2000_2000) |  | B1/D09_A1 | [8 empty] | 斗工DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | [5 empty] | 282 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D09 | 斗工DS |  |  | 1DTR(B) | #1DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | #1BTR | ℃ | #1BTR 線溫 | COIL_-120_120(-2000_2000) |  | B1/D09_A1 | [8 empty] | 斗工DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | [5 empty] | 283 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D09 | 斗工DS |  |  | 2DTR | #2DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | #2DTR | ℃ | #2DTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/D09_A1 | [8 empty] | 斗工DS.#2DTR_OIL | #2DTR 油溫 | MTR | [5 empty] | 284 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D09 | 斗工DS |  |  | 2DTR(A) | #2DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | #2ATR | ℃ | #2ATR 線溫 | COIL_-120_120(-2000_2000) |  | B1/D09_A1 | [8 empty] | 斗工DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | [5 empty] | 285 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D09 | 斗工DS |  |  | 2DTR(B) | #2DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | #2BTR | ℃ | #2BTR 線溫 | COIL_-120_120(-2000_2000) |  | B1/D09_A1 | [8 empty] | 斗工DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | [5 empty] | 286 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D09 | 斗工DS |  |  | 3DTR | #3DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | #3DTR | ℃ | #3DTR 油溫 |  |  | B1/D09_A1 | [16 empty] | 287 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D09 | 斗工DS |  |  | 3DTR | #3DTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | #3DTR | ℃ | #3DTR 線溫 |  |  | B1/D09_A1 | [16 empty] | 288 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D09 | 斗工DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | 310 | MW | #1DTR 1A 310 瓦 | MW_-108_108(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | [5 empty] | 289 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.216 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | 310 | MVAR | #1DTR 1A 310 乏 | MVAR_-72_72(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | [5 empty] | 290 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | 310 | A | #1DTR 1A 310 R相電流 | A_-3000_3000(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | [5 empty] | 291 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | 310 | A | #1DTR 1A 310 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | [5 empty] | 292 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | 310 | A | #1DTR 1A 310 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | [5 empty] | 293 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU51 | 工五一線(XU51) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | F1 | MVAR | F1 工五一線 XU51 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工五一線KVAR | 23KV工五一線 KVAR | FEEDER | [5 empty] | 294 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU51 | 工五一線(XU51) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | F1 | A | F1 工五一線 XU51 R相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工五一線A1 | 23KV工五一線 R相AMP | FEEDER | [5 empty] | 295 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU51 | 工五一線(XU51) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | F1 | A | F1 工五一線 XU51 S相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工五一線A2 | 23KV工五一線 S相AMP | FEEDER | [5 empty] | 296 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU51 | 工五一線(XU51) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | F1 | A | F1 工五一線 XU51 T相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工五一線A3 | 23KV工五一線 T相AMP | FEEDER | [5 empty] | 297 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU51 | 工五一線(XU51) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | F1 | A | F1 工五一線 XU51 N相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工五一線A0 | 23KV工五一線 N相AMP | FEEDER | [5 empty] | 298 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU52 | 工五二線(XU52) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | F2 | MVAR | F2 工五二線 XU52 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工五二線KVAR | 23KV工五二線 KVAR | FEEDER | [5 empty] | 299 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU52 | 工五二線(XU52) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | F2 | A | F2 工五二線 XU52 R相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工五二線A1 | 23KV工五二線 R相AMP | FEEDER | [5 empty] | 300 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU52 | 工五二線(XU52) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | F2 | A | F2 工五二線 XU52 S相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工五二線A2 | 23KV工五二線 S相AMP | FEEDER | [5 empty] | 301 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU52 | 工五二線(XU52) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | F2 | A | F2 工五二線 XU52 T相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工五二線A3 | 23KV工五二線 T相AMP | FEEDER | [5 empty] | 302 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU52 | 工五二線(XU52) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | F2 | A | F2 工五二線 XU52 N相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工五二線A0 | 23KV工五二線 N相AMP | FEEDER | [5 empty] | 303 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU53 | 工五三線(XU53) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | F3 | MVAR | F3 工五三線 XU53 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工五三線KVAR | 23KV工五三線 KVAR | FEEDER | [5 empty] | 304 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU53 | 工五三線(XU53) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | F3 | A | F3 工五三線 XU53 R相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工五三線A1 | 23KV工五三線 R相AMP | FEEDER | [5 empty] | 305 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU53 | 工五三線(XU53) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | F3 | A | F3 工五三線 XU53 S相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工五三線A2 | 23KV工五三線 S相AMP | FEEDER | [5 empty] | 306 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU53 | 工五三線(XU53) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | F3 | A | F3 工五三線 XU53 T相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工五三線A3 | 23KV工五三線 T相AMP | FEEDER | [5 empty] | 307 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU53 | 工五三線(XU53) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | F3 | A | F3 工五三線 XU53 N相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工五三線A0 | 23KV工五三線 N相AMP | FEEDER | [5 empty] | 308 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU54 | 工五四線(XU54) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0060 |  |  | 1-BC |  |  | F4 | MVAR | F4 工五四線 XU54 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工五四線KVAR | 23KV工五四線 KVAR | FEEDER | [5 empty] | 309 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU54 | 工五四線(XU54) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | F4 | A | F4 工五四線 XU54 R相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工五四線A1 | 23KV工五四線 R相AMP | FEEDER | [5 empty] | 310 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU54 | 工五四線(XU54) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | F4 | A | F4 工五四線 XU54 S相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工五四線A2 | 23KV工五四線 S相AMP | FEEDER | [5 empty] | 311 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU54 | 工五四線(XU54) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0063 |  |  | 1-BF |  |  | F4 | A | F4 工五四線 XU54 T相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工五四線A3 | 23KV工五四線 T相AMP | FEEDER | [5 empty] | 312 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 0 |  | RTU | RTU |  | ADCL2 |  |  | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | [5 empty] | 313 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 0 |  | RTU | RTU |  | ADCH2 |  |  | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.2 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | [5 empty] | 314 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU54 | 工五四線(XU54) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | F4 | A | F5 工五四線 XU54 N相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工五四線A0 | 23KV工五四線 N相AMP | FEEDER | [5 empty] | 315 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU55 | 工五五線(XU55) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | F5 | MVAR | F5 工五五線 XU55 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工五五線KVAR | 23KV工五五線 KVAR | FEEDER | [5 empty] | 316 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU55 | 工五五線(XU55) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | F5 | A | F5 工五五線 XU55 R相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工五五線A1 | 23KV工五五線 R相AMP | FEEDER | [5 empty] | 317 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU55 | 工五五線(XU55) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | F5 | A | F5 工五五線 XU55 S相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工五五線A2 | 23KV工五五線 S相AMP | FEEDER | [5 empty] | 318 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU55 | 工五五線(XU55) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | F5 | A | F5 工五五線 XU55 T相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工五五線A3 | 23KV工五五線 T相AMP | FEEDER | [5 empty] | 319 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU55 | 工五五線(XU55) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | F5 | A | F5 工五五線 XU55 N相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工五五線A0 | 23KV工五五線 N相AMP | FEEDER | [5 empty] | 320 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 1ABUS | #1ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0072 |  |  | 1-C8 |  |  | #1A PT | KV | #1DTR 1A 310 #1ABUS PT電壓 | kV_-18_18(-2000_2000) | aaa | B3/D09_A1 | [8 empty] | 斗工DS.23KV#1ABUS_KV | 23KV #1ABUS KV | BUS | [5 empty] | 321 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D09 | 斗工DS | 22 | 22kV | 100 | TIE(100) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | 100 | A | TIE 1A 100 R相電流 | A_-2000_2000(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.23KV_100_A1 | 23KV 100 R相AMP | TIE | [5 empty] | 322 |  |  |  |  | AI | [5 empty] | C20R0750 | 712.5 | 750 | 825 | 922.5 | 0.45 | -712.5 | -750 | -825 | -922.5 | 1 | 0.01 | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 100 | TIE(100) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | 100 | A | TIE 1A 100 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.23KV_100_A2 | 23KV 100 S相AMP | TIE | [5 empty] | 323 |  |  |  |  | AI | [5 empty] | C20R0750 | 712.5 | 750 | 825 | 922.5 | 0.45 | -712.5 | -750 | -825 | -922.5 | 1 | 0.01 | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 100 | TIE(100) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | 100 | A | TIE 1A 100 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.23KV_100_A3 | 23KV 100 T相AMP | TIE | [5 empty] | 324 |  |  |  |  | AI | [5 empty] | C20R0750 | 712.5 | 750 | 825 | 922.5 | 0.45 | -712.5 | -750 | -825 | -922.5 | 1 | 0.01 | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | 320 | MW | #1DTR 1B 320 瓦 | MW_-54_54(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | [5 empty] | 325 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | 320 | MVAR | #1DTR 1B 320 乏 | MVAR_-36_36(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | [5 empty] | 326 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | 320 | A | #1DTR 1B 320 R相電流 | A_-3000_3000(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | [5 empty] | 327 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | 320 | A | #1DTR 1B 320 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | [5 empty] | 328 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | 320 | A | #1DTR 1B 320 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | [5 empty] | 329 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU26 | 工六線(XU26) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | F6 | MVAR | F6 工六線 XU26 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工六線KVAR | 11KV工六線 KVAR | FEEDER | [5 empty] | 330 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU26 | 工六線(XU26) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | F6 | A | F6 工六線 XU26 R相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工六線A1 | 11KV工六線 R相AMP | FEEDER | [5 empty] | 331 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU26 | 工六線(XU26) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | F6 | A | F6 工六線 XU26 S相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工六線A2 | 11KV工六線 S相AMP | FEEDER | [5 empty] | 332 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU26 | 工六線(XU26) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | F6 | A | F6 工六線 XU26 T相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工六線A3 | 11KV工六線 T相AMP | FEEDER | [5 empty] | 333 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU26 | 工六線(XU26) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | F6 | A | F6 工六線 XU26 N相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工六線A0 | 11KV工六線 N相AMP | FEEDER | [5 empty] | 334 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU27 | 工七線(XU27) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | F7 | MVAR | F7 工七線 XU27 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工七線KVAR | 11KV工七線 KVAR | FEEDER | [5 empty] | 335 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU27 | 工七線(XU27) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | F6 | A | F7 工七線 XU27 R相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工七線A1 | 11KV工七線 R相AMP | FEEDER | [5 empty] | 336 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU27 | 工七線(XU27) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | F7 | A | F7 工七線 XU27 S相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工七線A2 | 11KV工七線 S相AMP | FEEDER | [5 empty] | 337 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU27 | 工七線(XU27) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | F7 | A | F7 工七線 XU27 T相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工七線A3 | 11KV工七線 T相AMP | FEEDER | [5 empty] | 338 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU27 | 工七線(XU27) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | F7 | A | F7 工七線 XU27 N相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工七線A0 | 11KV工七線 N相AMP | FEEDER | [5 empty] | 339 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU28 | 工八線(XU28) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | F8 | MVAR | F8 工八線 XU28 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工八線KVAR | 11KV工八線 KVAR | FEEDER | [5 empty] | 340 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU28 | 工八線(XU28) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | F8 | A | F8 工八線 XU28 R相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工八線A1 | 11KV工八線 R相AMP | FEEDER | [5 empty] | 341 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU28 | 工八線(XU28) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | F8 | A | F8 工八線 XU28 S相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工八線A2 | 11KV工八線 S相AMP | FEEDER | [5 empty] | 342 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU28 | 工八線(XU28) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | F8 | A | F8 工八線 XU28 T相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工八線A3 | 11KV工八線 T相AMP | FEEDER | [5 empty] | 343 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU28 | 工八線(XU28) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | F8 | A | F8 工八線 XU28 N相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工八線A0 | 11KV工八線 N相AMP | FEEDER | [5 empty] | 344 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU29 | 工九線(XU29) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | F9 | MVAR | F9 工九線 XU29 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工九線KVAR | 11KV工九線 KVAR | FEEDER | [5 empty] | 345 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU29 | 工九線(XU29) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | F9 | A | F9 工九線 XU29 R相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工九線A1 | 11KV工九線 R相AMP | FEEDER | [5 empty] | 346 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU29 | 工九線(XU29) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0098 |  |  | 1-E2 |  |  | F9 | A | F9 工九線 XU29 S相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工九線A2 | 11KV工九線 S相AMP | FEEDER | [5 empty] | 347 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU29 | 工九線(XU29) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | F9 | A | F9 工九線 XU29 T相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工九線A3 | 11KV工九線 T相AMP | FEEDER | [5 empty] | 348 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU29 | 工九線(XU29) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | F9 | A | F9 工九線 XU29 N相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工九線A0 | 11KV工九線 N相AMP | FEEDER | [5 empty] | 349 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU30 | 工十線(XU30) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0101 |  |  | 1-E5 |  |  | F10 | MVAR | F10 工十線 XU30 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工十線KVAR | 11KV工十線 KVAR | FEEDER | [5 empty] | 350 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU30 | 工十線(XU30) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | F10 | A | F10 工十線 XU30 R相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工十線A1 | 11KV工十線 R相AMP | FEEDER | [5 empty] | 351 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU30 | 工十線(XU30) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | F10 | A | F10 工十線 XU30 S相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工十線A2 | 11KV工十線 S相AMP | FEEDER | [5 empty] | 352 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU30 | 工十線(XU30) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | F10 | A | F10 工十線 XU30 T相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工十線A3 | 11KV工十線 T相AMP | FEEDER | [5 empty] | 353 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU30 | 工十線(XU30) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | F10 | A | F10 工十線 XU30 N相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工十線A0 | 11KV工十線 N相AMP | FEEDER | [5 empty] | 354 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 1BBUS | #1BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0106 |  |  | 1-EA |  |  | #1B PT | KV | #1DTR 1B 320 #1BUS PT電壓 | kV_-9_9(-2000_2000) | baa | B3/D09_A1 | [8 empty] | 斗工DS.11KV#1BBUS_KV | 11KV #1BBUS KV | BUS | [5 empty] | 355 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D09 | 斗工DS | 11 | 11kV | 200 | TIE(200) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | 200 | A | TIE 1B 200 R相電流 | A_-2000_2000(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.11KV_200_A1 | 11KV 200 R相AMP | TIE | [5 empty] | 356 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 200 | TIE(200) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | 200 | A | TIE 1B 200 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.11KV_200_A2 | 11KV 200 S相AMP | TIE | [5 empty] | 357 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 200 | TIE(200) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | 200 | A | TIE 1B 200 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.11KV_200_A3 | 11KV 200 T相AMP | TIE | [5 empty] | 358 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS |  |  | 2DTR(A) | #2DTR(A) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | 330 | MW | #2DTR 2A 330 瓦 | MW_-108_108(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | [5 empty] | 359 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.216 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D09 | 斗工DS |  |  | 2DTR(A) | #2DTR(A) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | 330 | MVAR | #2DTR 2A 330 乏 | MVAR_-72_72(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | [5 empty] | 360 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D09 | 斗工DS |  |  | 2DTR(A) | #2DTR(A) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | 330 | A | #2DTR 2A 330 R相電流 | A_-3000_3000(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | [5 empty] | 361 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D09 | 斗工DS |  |  | 2DTR(A) | #2DTR(A) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | 330 | A | #2DTR 2A 330 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | [5 empty] | 362 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D09 | 斗工DS |  |  | 2DTR(A) | #2DTR(A) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | 330 | A | #2DTR 2A 330 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | [5 empty] | 363 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU61 | 工六一線(XU61) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | F11 | MVAR | F11 工六一線 XU61 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工六一線KVAR | 23KV工六一線 KVAR | FEEDER | [5 empty] | 364 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU61 | 工六一線(XU61) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | F11 | A | F11 工六一線 XU61 R相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工六一線A1 | 23KV工六一線 R相AMP | FEEDER | [5 empty] | 365 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU61 | 工六一線(XU61) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | F11 | A | F11 工六一線 XU61 S相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工六一線A2 | 23KV工六一線 S相AMP | FEEDER | [5 empty] | 366 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU61 | 工六一線(XU61) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | F11 | A | F11 工六一線 XU61 T相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工六一線A3 | 23KV工六一線 T相AMP | FEEDER | [5 empty] | 367 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU61 | 工六一線(XU61) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | F11 | A | F11 工六一線 XU61 N相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工六一線A0 | 23KV工六一線 N相AMP | FEEDER | [5 empty] | 368 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU62 | 工六二線(XU62) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | F12 | MVAR | F12 工六二線 XU62 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工六二線KVAR | 23KV工六二線 KVAR | FEEDER | [5 empty] | 369 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU62 | 工六二線(XU62) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | F12 | A | F12 工六二線 XU62 R相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工六二線A1 | 23KV工六二線 R相AMP | FEEDER | [5 empty] | 370 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU62 | 工六二線(XU62) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | F12 | A | F12 工六二線 XU62 S相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工六二線A2 | 23KV工六二線 S相AMP | FEEDER | [5 empty] | 371 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU62 | 工六二線(XU62) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | F12 | A | F12 工六二線 XU62 T相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工六二線A3 | 23KV工六二線 T相AMP | FEEDER | [5 empty] | 372 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU62 | 工六二線(XU62) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | F12 | A | F12 工六二線 XU62 N相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工六二線A0 | 23KV工六二線 N相AMP | FEEDER | [5 empty] | 373 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU63 | 工六三線(XU63) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | F13 | MVAR | F13 工六三線 XU63 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工六三線KVAR | 23KV工六三線 KVAR | FEEDER | [5 empty] | 374 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU63 | 工六三線(XU63) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | F13 | A | F13 工六三線 XU63 R相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工六三線A1 | 23KV工六三線 R相AMP | FEEDER | [5 empty] | 375 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU63 | 工六三線(XU63) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | F13 | A | F13 工六三線 XU63 S相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工六三線A2 | 23KV工六三線 S相AMP | FEEDER | [5 empty] | 376 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 0 |  | RTU | RTU |  | ADCL3 |  |  | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.3 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | [5 empty] | 377 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 0 |  | RTU | RTU |  | ADCH3 |  |  | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.3 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | [5 empty] | 378 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU63 | 工六三線(XU63) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | F13 | A | F13 工六三線 XU63 T相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工六三線A3 | 23KV工六三線 T相AMP | FEEDER | [5 empty] | 379 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU63 | 工六三線(XU63) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | F13 | A | F13 工六三線 XU63 N相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工六三線A0 | 23KV工六三線 N相AMP | FEEDER | [5 empty] | 380 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU64 | 工六四線(XU64) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | F14 | MVAR | F14 工六四線 XU64 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工六四線KVAR | 23KV工六四線 KVAR | FEEDER | [5 empty] | 381 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU64 | 工六四線(XU64) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0133 |  |  | 2-85 |  |  | F14 | A | F14 工六四線 XU64 R相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工六四線A1 | 23KV工六四線 R相AMP | FEEDER | [5 empty] | 382 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU64 | 工六四線(XU64) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | F14 | A | F14 工六四線 XU64 S相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工六四線A2 | 23KV工六四線 S相AMP | FEEDER | [5 empty] | 383 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU64 | 工六四線(XU64) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0135 |  |  | 2-87 |  |  | F14 | A | F14 工六四線 XU64 T相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工六四線A3 | 23KV工六四線 T相AMP | FEEDER | [5 empty] | 384 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU64 | 工六四線(XU64) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0136 |  |  | 2-88 |  |  | F14 | A | F14 工六四線 XU64 N相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工六四線A0 | 23KV工六四線 N相AMP | FEEDER | [5 empty] | 385 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU65 | 工六五線(XU65) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0137 |  |  | 2-89 |  |  | F15 | MVAR | F15 工六五線 XU65 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工六五線KVAR | 23KV工六五線 KVAR | FEEDER | [5 empty] | 386 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU65 | 工六五線(XU65) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0138 |  |  | 2-8A |  |  | F15 | A | F15 工六五線 XU65 R相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工六五線A1 | 23KV工六五線 R相AMP | FEEDER | [5 empty] | 387 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU65 | 工六五線(XU65) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0139 |  |  | 2-8B |  |  | F15 | A | F15 工六五線 XU65 S相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工六五線A2 | 23KV工六五線 S相AMP | FEEDER | [5 empty] | 388 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU65 | 工六五線(XU65) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0140 |  |  | 2-8C |  |  | F15 | A | F15 工六五線 XU65 T相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工六五線A3 | 23KV工六五線 T相AMP | FEEDER | [5 empty] | 389 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | XU65 | 工六五線(XU65) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0141 |  |  | 2-8D |  |  | F15 | A | F15 工六五線 XU65 N相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工六五線A0 | 23KV工六五線 N相AMP | FEEDER | [5 empty] | 390 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 2A1BUS | #2A1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0142 |  |  | 2-8E |  |  | #2A1 PT | KV | #2DTR 330A1 #2A1BUS PT電壓 | kV_-18_18(-2000_2000) | aba | B3/D09_A1 | [8 empty] | 斗工DS.23KV#2A1BUS_KV | 23KV #2A1BUS KV | BUS | [5 empty] | 391 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D09 | 斗工DS | 22 | 22kV | 2A2BUS | #2A2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0143 |  |  | 2-8F |  |  | #2A2 PT | KV | #2DTR 330A2 #2A2BUS PT電壓 | kV_-18_18(-2000_2000) | aca | B3/D09_A1 | [8 empty] | 斗工DS.23KV#2A2BUS_KV | 23KV #2A2BUS KV | BUS | [5 empty] | 392 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D09 | 斗工DS | 22 | 22kV | 300 | TIE(300) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0144 |  |  | 2-90 |  |  | 300 | A | TIE 2A 300 TIE R相電流 | A_-2000_2000(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.23KV_300_A1 | 23KV 300 R相AMP | TIE | [5 empty] | 393 |  |  |  |  | AI | [5 empty] | C20R0750 | 712.5 | 750 | 825 | 922.5 | 0.45 | -712.5 | -750 | -825 | -922.5 | 1 | 0.01 | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 300 | TIE(300) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0145 |  |  | 2-91 |  |  | 300 | A | TIE 2A 300 TIE S相電流 | A_-2000_2000(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.23KV_300_A2 | 23KV 300 S相AMP | TIE | [5 empty] | 394 |  |  |  |  | AI | [5 empty] | C20R0750 | 712.5 | 750 | 825 | 922.5 | 0.45 | -712.5 | -750 | -825 | -922.5 | 1 | 0.01 | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 300 | TIE(300) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0146 |  |  | 2-92 |  |  | 300 | A | TIE 2A 300 TIE T相電流 | A_-2000_2000(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.23KV_300_A3 | 23KV 300 T相AMP | TIE | [5 empty] | 395 |  |  |  |  | AI | [5 empty] | C20R0750 | 712.5 | 750 | 825 | 922.5 | 0.45 | -712.5 | -750 | -825 | -922.5 | 1 | 0.01 | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS |  |  | 2DTR(B) | #2DTR(B) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0147 |  |  | 2-93 |  |  | 340 | MW | #2DTR 2B 340 瓦 | MW_-36_36(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | [5 empty] | 396 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D09 | 斗工DS |  |  | 2DTR(B) | #2DTR(B) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0148 |  |  | 2-94 |  |  | 340 | MVAR | #2DTR 2B 340 乏 | MVAR_-36_36(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | [5 empty] | 397 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D09 | 斗工DS |  |  | 2DTR(B) | #2DTR(B) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0149 |  |  | 2-95 |  |  | 340 | A | #2DTR 2B 340 R相電流 | A_-3000_3000(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | [5 empty] | 398 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D09 | 斗工DS |  |  | 2DTR(B) | #2DTR(B) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0150 |  |  | 2-96 |  |  | 340 | A | #2DTR 2B 340 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | [5 empty] | 399 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D09 | 斗工DS |  |  | 2DTR(B) | #2DTR(B) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0151 |  |  | 2-97 |  |  | 340 | A | #2DTR 2B 340 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | [5 empty] | 400 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU36 | 工十六線(XU36) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0152 |  |  | 2-98 |  |  | F16 | MVAR | F16 工十六線 XU36 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工十六線KVAR | 11KV工十六線 KVAR | FEEDER | [5 empty] | 401 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU36 | 工十六線(XU36) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0153 |  |  | 2-99 |  |  | F16 | A | F16 工十六線 XU36 R相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工十六線A1 | 11KV工十六線 R相AMP | FEEDER | [5 empty] | 402 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU36 | 工十六線(XU36) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0154 |  |  | 2-9A |  |  | F16 | A | F16 工十六線 XU36 S相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工十六線A2 | 11KV工十六線 S相AMP | FEEDER | [5 empty] | 403 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU36 | 工十六線(XU36) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0155 |  |  | 2-9B |  |  | F16 | A | F16 工十六線 XU36 T相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工十六線A3 | 11KV工十六線 T相AMP | FEEDER | [5 empty] | 404 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU36 | 工十六線(XU36) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0156 |  |  | 2-9C |  |  | F16 | A | F16 工十六線 XU36 N相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工十六線A0 | 11KV工十六線 N相AMP | FEEDER | [5 empty] | 405 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU37 | 工十七線(XU37) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0157 |  |  | 2-9D |  |  | F17 | MVAR | F17 工十七線 XU37 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工十七線KVAR | 11KV工十七線 KVAR | FEEDER | [5 empty] | 406 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU37 | 工十七線(XU37) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0158 |  |  | 2-9E |  |  | F17 | A | F17 工十七線 XU37 R相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工十七線A1 | 11KV工十七線 R相AMP | FEEDER | [5 empty] | 407 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU37 | 工十七線(XU37) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0159 |  |  | 2-9F |  |  | F17 | A | F17 工十七線 XU37 S相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工十七線A2 | 11KV工十七線 S相AMP | FEEDER | [5 empty] | 408 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU37 | 工十七線(XU37) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0160 |  |  | 2-A0 |  |  | F17 | A | F17 工十七線 XU37 T相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工十七線A3 | 11KV工十七線 T相AMP | FEEDER | [5 empty] | 409 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU37 | 工十七線(XU37) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0161 |  |  | 2-A1 |  |  | F17 | A | F17 工十七線 XU37 N相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工十七線A0 | 11KV工十七線 N相AMP | FEEDER | [5 empty] | 410 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU38 | 工十八線(XU38) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0162 |  |  | 2-A2 |  |  | F18 | MVAR | F18 工十八線 XU38 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工十八線KVAR | 11KV工十八線 KVAR | FEEDER | [5 empty] | 411 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU38 | 工十八線(XU38) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0163 |  |  | 2-A3 |  |  | F18 | A | F18 工十八線 XU38 R相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工十八線A1 | 11KV工十八線 R相AMP | FEEDER | [5 empty] | 412 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU38 | 工十八線(XU38) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0164 |  |  | 2-A4 |  |  | F18 | A | F18 工十八線 XU38 S相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工十八線A2 | 11KV工十八線 S相AMP | FEEDER | [5 empty] | 413 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU38 | 工十八線(XU38) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0165 |  |  | 2-A5 |  |  | F18 | A | F18 工十八線 XU38 T相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工十八線A3 | 11KV工十八線 T相AMP | FEEDER | [5 empty] | 414 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU38 | 工十八線(XU38) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0166 |  |  | 2-A6 |  |  | F18 | A | F18 工十八線 XU38 N相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工十八線A0 | 11KV工十八線 N相AMP | FEEDER | [5 empty] | 415 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU39 | 工十九線(XU39) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0167 |  |  | 2-A7 |  |  | F19 | MVAR | F19 工十九線 XU39 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工十九線KVAR | 11KV工十九線 KVAR | FEEDER | [5 empty] | 416 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU39 | 工十九線(XU39) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0168 |  |  | 2-A8 |  |  | F19 | A | F19 工十九線 XU39 R相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工十九線A1 | 11KV工十九線 R相AMP | FEEDER | [5 empty] | 417 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU39 | 工十九線(XU39) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0169 |  |  | 2-A9 |  |  | F19 | A | F19 工十九線 XU39 S相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工十九線A2 | 11KV工十九線 S相AMP | FEEDER | [5 empty] | 418 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU39 | 工十九線(XU39) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0170 |  |  | 2-AA |  |  | F19 | A | F19 工十九線 XU39 T相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工十九線A3 | 11KV工十九線 T相AMP | FEEDER | [5 empty] | 419 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU39 | 工十九線(XU39) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0171 |  |  | 2-AB |  |  | F19 | A | F19 工十九線 XU39 N相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工十九線A0 | 11KV工十九線 N相AMP | FEEDER | [5 empty] | 420 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU40 | 工二十線(XU40) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0172 |  |  | 2-AC |  |  | F20 | MVAR | F20 工二十線 XU40 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工二十線KVAR | 11KV工二十線 KVAR | FEEDER | [5 empty] | 421 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU40 | 工二十線(XU40) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0173 |  |  | 2-AD |  |  | F20 | A | F20 工二十線 XU40 R相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工二十線A1 | 11KV工二十線 R相AMP | FEEDER | [5 empty] | 422 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU40 | 工二十線(XU40) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0174 |  |  | 2-AE |  |  | F20 | A | F20 工二十線 XU40 S相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工二十線A2 | 11KV工二十線 S相AMP | FEEDER | [5 empty] | 423 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU40 | 工二十線(XU40) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0175 |  |  | 2-AF |  |  | F20 | A | F20 工二十線 XU40 T相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工二十線A3 | 11KV工二十線 T相AMP | FEEDER | [5 empty] | 424 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | XU40 | 工二十線(XU40) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0176 |  |  | 2-B0 |  |  | F20 | A | F20 工二十線 XU40 N相電流 | A_-600_600(-2000_2000) |  | B2/D09_D1 | [8 empty] | 斗工DS.工二十線A0 | 11KV工二十線 N相AMP | FEEDER | [5 empty] | 425 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 2B1BUS | #2B1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0177 |  |  | 2-B1 |  |  | #2B1 PT | KV | #2DTR 340B1 #2B1 BUS PT電壓 | kV_-9_9(-2000_2000) | bba | B3/D09_A1 | [8 empty] | 斗工DS.11KV#2B1BUS_KV | 11KV #2B1BUS KV | BUS | [5 empty] | 426 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D09 | 斗工DS | 11 | 11kV | 2B2BUS | #2B2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0178 |  |  | 2-B2 |  |  | #2B2 PT | KV | #2DTR 340B2 #2B2 BUS PT電壓 | kV_-9_9(-2000_2000) | bca | B3/D09_A1 | [8 empty] | 斗工DS.11KV#2B2BUS_KV | 11KV #2B2BUS KV | BUS | [5 empty] | 427 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D09 | 斗工DS | 11 | 11kV | 400 | TIE(400) |  | I_R |  | B2 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0179 |  |  | 2-B3 |  |  | 400 | A | TIE 2B 400 R相電流 | A_-2000_2000(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.11KV_400_A1 | 11KV 400 R相AMP | TIE | [5 empty] | 428 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 400 | TIE(400) |  | I_S |  | B2 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0180 |  |  | 2-B4 |  |  | 400 | A | TIE 2B 400 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.11KV_400_A2 | 11KV 400 S相AMP | TIE | [5 empty] | 429 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 400 | TIE(400) |  | I_T |  | B2 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0181 |  |  | 2-B5 |  |  | 400 | A | TIE 2B 400 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.11KV_400_A3 | 11KV 400 T相AMP | TIE | [5 empty] | 430 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工～斗工山線(1510) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0246 |  |  | 2-F6 |  |  | 1510CB | KV | 鉅工斗工山線 LPT | kV_-210_210(-2000_2000) |  | B2/D09_A1 | [8 empty] | 斗工DS.1510LPD_KV | 鉅工山線(1510) LPD KV | LINE161 | [5 empty] | 431 |  |  |  |  | AI | [5 empty] | LG_16LPD | 169 | 170 | 172 | 210 | 0.5 | 153 | 152 | 151 | 0 | 5 | 10 | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工～斗工海線(1520) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0247 |  |  | 2-F7 |  |  | 1520CB | KV | 鉅工斗工海線 LPT | kV_-210_210(-2000_2000) |  | B2/D09_A1 | [8 empty] | 斗工DS.1520LPD_KV | 鉅工海線(1520) LPD KV | LINE161 | [5 empty] | 432 |  |  |  |  | AI | [5 empty] | LG_16LPD | 169 | 170 | 172 | 210 | 0.5 | 153 | 152 | 151 | 0 | 5 | 10 | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
D09 | 斗工DS | 161 | 161kV | 1530 | 嘉民～斗工紅線(1530) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0248 |  |  | 2-F8 |  |  | 1530CB | KV | 嘉民斗工紅線 LPT | kV_-210_210(-2000_2000) |  | B2/D09_A1 | [8 empty] | 斗工DS.1530LPD_KV | 嘉民斗工紅線(1530) LPD KV | LINE161 | [5 empty] | 433 |  |  |  |  | AI | [5 empty] | LG_16LPD | 169 | 170 | 172 | 210 | 0.5 | 153 | 152 | 151 | 0 | 5 | 10 | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
D09 | 斗工DS | 161 | 161kV | 1540 | 雲林~斗工線(1540) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0249 |  |  | 2-F9 |  |  | 1540CB | KV | 雲林斗工線 LPT | kV_-210_210(-2000_2000) |  | B2/D09_A1 | [8 empty] | 斗工DS.1540LPD_KV | 雲林斗工線(1540) LPD KV | LINE161 | [5 empty] | 434 |  |  |  |  | AI | [5 empty] | LG_16LPD | 169 | 170 | 172 | 210 | 0.5 | 153 | 152 | 151 | 0 | 5 | 10 | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工～斗工山線(1510) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0001 |  |  | 1-00-01 |  |  | 1510 | 87A1 | 鉅工斗工山線 1510 CB |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1510_87A1 | 鉅工山線(1510) #1 87RY | LINE161 | [5 empty] | 435 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工～斗工山線(1510) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0002 |  |  | 1-00-02 |  |  | 1510 | 87A2 | 鉅工斗工山線 1510 CB |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1510_87A2 | 鉅工山線(1510) #2 87RY | LINE161 | [5 empty] | 436 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工～斗工山線(1510) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | 1510 | PHA | 鉅工斗工山線 1510 CB |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1510_PHA | 鉅工山線(1510) 相間RY | LINE161 | [5 empty] | 437 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工～斗工山線(1510) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0004 |  |  | 1-00-04 |  |  | 1510 | GDA | 鉅工斗工山線 1510 CB |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1510_GDA | 鉅工山線(1510) 接地RY | LINE161 | [5 empty] | 438 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工～斗工海線(1520) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | 1520 | 87A1 | 鉅工斗工海線 1520 CB |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1520_87A1 | 鉅工海線(1520) #1 87RY | LINE161 | [5 empty] | 439 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工～斗工海線(1520) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-07 |  |  | 1520 | 87A2 | 鉅工斗工海線 1520 CB |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1520_87A2 | 鉅工海線(1520) #2 87RY | LINE161 | [5 empty] | 440 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工～斗工海線(1520) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-01-00 |  |  | 1520 | PHA | 鉅工斗工海線 1520 CB |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1520_PHA | 鉅工海線(1520) 相間RY | LINE161 | [5 empty] | 441 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工～斗工海線(1520) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | 1520 | GDA | 鉅工斗工海線 1520 CB |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1520_GDA | 鉅工海線(1520) 接地RY | LINE161 | [5 empty] | 442 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1540 | 雲林~斗工線(1540) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-03 |  |  | 1540 | 87A | 雲林斗工線 1540 CB |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1540_87A | 雲林斗工線(1540) 87RY | LINE161 | [5 empty] | 443 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1540 | 雲林~斗工線(1540) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0013 |  |  | 1-01-05 |  |  | 1540 | PHA | 雲林斗工線 1540 CB |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1540_PHA | 雲林斗工線(1540) 相間RY | LINE161 | [5 empty] | 444 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1540 | 雲林~斗工線(1540) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-06 |  |  | 1540 | GDA | 雲林斗工線 1540 CB |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1540_GDA | 雲林斗工線(1540) 接地RY | LINE161 | [5 empty] | 445 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1530 | 嘉民～斗工紅線(1530) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-02-00 |  |  | 1530 | 87A | 嘉民斗工紅線 1530 CB |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1530_87A | 嘉民斗工紅線(1530) 87RY | LINE161 | [5 empty] | 446 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1530 | 嘉民～斗工紅線(1530) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 |  |  | 1-02-02 |  |  | 1530 | PHA | 嘉民斗工紅線 1530 CB |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1530_PHA | 嘉民斗工紅線(1530) 相間RY | LINE161 | [5 empty] | 447 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1530 | 嘉民～斗工紅線(1530) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0019 |  |  | 1-02-03 |  |  | 1530 | GDA | 嘉民斗工紅線 1530 CB |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1530_GDA | 嘉民斗工紅線(1530) 接地RY | LINE161 | [5 empty] | 448 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1550 | 斗工～富喬線(1550) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-05 |  |  | 1550 | 85A | 斗工富喬線 1550 CB |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1550_85A | 富喬線(1550) 85RY | LINE161 | [5 empty] | 449 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1550 | 斗工～富喬線(1550) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0023 |  |  | 1-02-07 |  |  | 1550 | PHA | 斗工富喬線 1550 CB |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1550_PHA | 富喬線(1550) 相間RY | LINE161 | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1550 | 斗工～富喬線(1550) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0024 |  |  | 1-03-00 |  |  | 1550 | GDA | 斗工富喬線 1550 CB |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1550_GDA | 富喬線(1550) 接地RY | LINE161 | [5 empty] | 451 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1610 | 榴中～斗工一路(1610) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0036 |  |  | 1-04-04 |  |  | 1610 | 87A | 榴中斗工一路 1610 87A |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1610_87A | 榴中斗工一路(1610) 87RY | LINE161 | [5 empty] | 452 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1610 | 榴中～斗工一路(1610) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0038 |  |  | 1-04-06 |  |  | 1610 | PHA | 榴中斗工一路 1610 PHA |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1610_PHA | 榴中斗工一路(1610) 相間RY | LINE161 | [5 empty] | 453 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1610 | 榴中～斗工一路(1610) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0039 |  |  | 1-04-07 |  |  | 1610 | GDA | 榴中斗工一路 1610 GDA |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1610_GDA | 榴中斗工一路(1610) 接地RY | LINE161 | [5 empty] | 454 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1620 | 榴中～斗工二路(1620) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0041 |  |  | 1-05-01 |  |  | 1620 | 87A | 榴中斗工二路 1620 87A |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1620_87A | 榴中斗工二路(1620) 87RY | LINE161 | [5 empty] | 455 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1620 | 榴中～斗工二路(1620) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0043 |  |  | 1-05-03 |  |  | 1620 | PHA | 榴中斗工二路 1620 PHA |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1620_PHA | 榴中斗工二路(1620) 相間RY | LINE161 | [5 empty] | 456 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1620 | 榴中～斗工二路(1620) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0044 |  |  | 1-05-04 |  |  | 1620 | GDA | 榴中斗工二路 1620 GDA |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1620_GDA | 榴中斗工二路(1620) 接地RY | LINE161 | [5 empty] | 457 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | 1500 | 50A | 161KV TIE 1500 50A |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1500_50A | 161KV TIE(1500) 50RY | TIE | [5 empty] | 458 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0053 |  |  | 1-06-05 |  |  | 161KV BUS | 87B1A | 161KV #1BUS 87A |  |  | B2/D09_A1 | [8 empty] | 斗工DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | [5 empty] | 459 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0054 |  |  | 1-06-06 |  |  | 161KV BUS | 87B2A | 161KV #2BUS 87A |  |  | B2/D09_A1 | [8 empty] | 斗工DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | [5 empty] | 460 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0055 |  |  | 1-06-07 |  |  | 161KV RCA | ON/OFF | 復閉電驛警報 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | [5 empty] | 461 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0056 |  |  | 1-07-00 |  |  | OSCA | A/N | 161KV示波器啟動警報OSCA |  |  | B3/D09_A1 | [8 empty] | 斗工DS.161KV_OSCA | 161KV示波器啟動警報 | OTHER | [5 empty] | 462 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D09 | 斗工DS |  |  | 1DTR | #1DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0058 |  |  | 1-07-02 |  |  | #1DTR | 87A | #1DTR 87A |  |  | B1/D09_A1 | [8 empty] | 斗工DS.#1DTR_87A | #1DTR 87RY | MTR | [5 empty] | 463 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS |  |  | 1DTR | #1DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0059 |  |  | 1-07-03 |  |  | #1DTR | 96PA | #1DTR 機械保護動作(96PA) |  |  | B1/D09_A1 | [8 empty] | 斗工DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | [5 empty] | 464 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS |  |  | 1DTR | #1DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0060 |  |  | 1-07-04 |  |  | #1DTR | 51ZA | #1DTR 51ZA |  |  | B1/D09_A1 | [8 empty] | 斗工DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | [5 empty] | 465 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1750 | #1DTR(1750) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0061 |  |  | 1-07-05 |  |  | 1750 | PHA(51A) | #1DTR 1750 PHA |  |  | B2/D09_A1 | [8 empty] | 斗工DS.#1DTR_51A | #1DTR 51RY | MTR | [5 empty] | 466 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1750 | #1DTR(1750) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0062 |  |  | 1-07-06 |  |  | 1750 | GDA(51NA) | #1DTR 1750 GDA |  |  | B2/D09_A1 | [8 empty] | 斗工DS.#1DTR_51NA | #1DTR 51N RY | MTR | [5 empty] | 467 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0064 |  |  | 1-08-00 |  |  | 310 | PHA | #1DTR 1A 310 PHA |  |  | B3/D09_A1 | [8 empty] | 斗工DS.310_PHA2 | 310開關箱IED RY PHA | OTHER | [5 empty] | 468 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | PHA |  | B2 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0066 |  |  | 1-08-02 |  |  | 320 | PHA | #1DTR 1B 320 PHA |  |  | B3/D09_A1 | [8 empty] | 斗工DS.320_PHA2 | 320開關箱IED RY PHA | OTHER | [5 empty] | 469 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS |  |  | 2DTR | #2DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 |  |  | 1-08-04 |  |  | #2DTR | 87A | #2DTR 87A |  |  | B1/D09_A1 | [8 empty] | 斗工DS.#2DTR_87A | #2DTR 87RY | MTR | [5 empty] | 470 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS |  |  | 2DTR | #2DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 |  |  | 1-08-05 |  |  | #2DTR | 96PA | #2DTR 機械保護動作(96PA) |  |  | B1/D09_A1 | [8 empty] | 斗工DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | [5 empty] | 471 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS |  |  | 2DTR | #2DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0070 |  |  | 1-08-06 |  |  | #2DTR | 51ZA | #2DTR 51ZA |  |  | B1/D09_A1 | [8 empty] | 斗工DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | [5 empty] | 472 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1760 | #2DTR(1760) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0071 |  |  | 1-08-07 |  |  | 1760 | PHA | #2DTR 1760 PHA |  |  | B2/D09_A1 | [8 empty] | 斗工DS.#2DTR_51A | #2DTR 51RY | MTR | [5 empty] | 473 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1760 | #2DTR(1760) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0072 |  |  | 1-09-00 |  |  | 1760 | GDA | #2DTR 1760 GDA |  |  | B2/D09_A1 | [8 empty] | 斗工DS.#2DTR_51NA | #2DTR 51N RY | MTR | [5 empty] | 474 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | 330A1 | #2DTR(A)(330A1) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-09-02 |  |  | 330A1 | PHA | #2DTR 1A 330A1 PHA |  |  | B3/D09_A1 | [8 empty] | 斗工DS.330A1_PHA2 | 330A1開關箱IED RY PHA | OTHER | [5 empty] | 475 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | 330A2 | #2DTR(A)(330A2) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0076 |  |  | 1-09-04 |  |  | 330A2 | PHA | #2DTR 330A2 PHA |  |  | B3/D09_A1 | [8 empty] | 斗工DS.330A2_PHA2 | 330A2開關箱IED RY PHA | OTHER | [5 empty] | 476 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | 340B2 | #2DTR(B)(340B2) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0078 |  |  | 1-09-06 |  |  | 340B2 | PHA | #2DTR 2B 340B2 PHA |  |  | B3/D09_A1 | [8 empty] | 斗工DS.340B2_PHA2 | 340B2開關箱IED RY PHA | OTHER | [5 empty] | 477 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | 340B1 | #2DTR(B)(340B1) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0080 |  |  | 1-0A-00 |  |  | 340B1 | PHA | #2DTR 1B 340B1 PHA |  |  | B3/D09_A1 | [8 empty] | 斗工DS.340B1_PHA2 | 340B1開關箱IED RY PHA | OTHER | [5 empty] | 478 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0091 |  |  | 1-0B-03 |  |  | 310 | PHA(3相) | #1DTR D1A 51RY PHA |  |  | B3/D09_A1 | [8 empty] | 斗工DS.310_51A | #1DTR二次側(310) 51RY | MTR | [5 empty] | 479 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | 51A |  | B2 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0092 |  |  | 1-0B-04 |  |  | 320 | PHA(3相) | #1DTR D1B 51RY PHA |  |  | B3/D09_A1 | [8 empty] | 斗工DS.320_51A | #1DTR二次側(320) 51RY | MTR | [5 empty] | 480 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | 330A1 | #2DTR(A)(330A1) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0093 |  |  | 1-0B-05 |  |  | 330A1 | PHA(3相) | #2DTR D2A151RY PHA |  |  | B3/D09_A1 | [8 empty] | 斗工DS.330A1_51A | #2DTR二次側(330A1) 51RY | MTR | [5 empty] | 481 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | 330A2 | #2DTR(A)(330A2) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0094 |  |  | 1-0B-06 |  |  | 330A2 | PHA(3相) | #2DTR D2A2 51RY PHA |  |  | B3/D09_A1 | [8 empty] | 斗工DS.330A2_51A | #2DTR二次側(330A2) 51RY | MTR | [5 empty] | 482 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | 340B1 | #2DTR(B)(340B1) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0095 |  |  | 1-0B-07 |  |  | 340B1 | PHA(3相) | #2DTR D2B1 51RY PHA |  |  | B3/D09_A1 | [8 empty] | 斗工DS.340B1_51A | #2DTR二次側(340B1) 51RY | MTR | [5 empty] | 483 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | 340B2 | #2DTR(B)(340B2) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0096 |  |  | 1-0C-00 |  |  | 340B2 | PHA(3相) | #2DTR D2B2 51RY PHA |  |  | B3/D09_A1 | [8 empty] | 斗工DS.340B2_51A | #2DTR二次側(340B2) 51RY | MTR | [5 empty] | 484 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS |  |  | 1DTR | #1DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0099 |  |  | 1-0C-03 |  |  | #1DTR | ON/OFF | #1DTR 96P |  |  | B1/D09_A1 | [8 empty] | 斗工DS.#1DTR_96P | #1DTR 96P RY | MTR | [5 empty] | 485 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D09 | 斗工DS |  |  | 1DTR | #1DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0100 |  |  | 1-0C-04 |  |  | #1DTR | ON/OFF | #1DTR 96D |  |  | B1/D09_A1 | [8 empty] | 斗工DS.#1DTR_96D | #1DTR 96D RY | MTR | [5 empty] | 486 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D09 | 斗工DS |  |  | 1DTR | #1DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0101 |  |  | 1-0C-05 |  |  | #1DTR | ON/OFF | #1DTR 96B1 |  |  | B1/D09_A1 | [8 empty] | 斗工DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | [5 empty] | 487 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D09 | 斗工DS |  |  | 1DTR | #1DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0102 |  |  | 1-0C-06 |  |  | #1DTR | ON/OFF | #1DTR 96B2 |  |  | B1/D09_A1 | [8 empty] | 斗工DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | [5 empty] | 488 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D09 | 斗工DS |  |  | 1DTR | #1DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0103 |  |  | 1-0C-07 |  |  | #1DTR | ON/OFF | #1DTR 63Q |  |  | B1/D09_A1 | [8 empty] | 斗工DS.#1DTR_63Q | #1DTR 63Q RY | MTR | [5 empty] | 489 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D09 | 斗工DS |  |  | 2DTR | #2DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0104 |  |  | 1-0D-00 |  |  | #2DTR | ON/OFF | #2DTR 96P |  |  | B1/D09_A1 | [8 empty] | 斗工DS.#2DTR_96P | #2DTR 96P RY | MTR | [5 empty] | 490 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D09 | 斗工DS |  |  | 2DTR | #2DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0105 |  |  | 1-0D-01 |  |  | #2DTR | ON/OFF | #2DTR 96D |  |  | B1/D09_A1 | [8 empty] | 斗工DS.#2DTR_96D | #2DTR 96D RY | MTR | [5 empty] | 491 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D09 | 斗工DS |  |  | 2DTR | #2DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0106 |  |  | 1-0D-02 |  |  | #2DTR | ON/OFF | #2DTR 96B1 |  |  | B1/D09_A1 | [8 empty] | 斗工DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | [5 empty] | 492 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D09 | 斗工DS |  |  | 2DTR | #2DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0107 |  |  | 1-0D-03 |  |  | #2DTR | ON/OFF | #2DTR 96B2 |  |  | B1/D09_A1 | [8 empty] | 斗工DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | [5 empty] | 493 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D09 | 斗工DS |  |  | 2DTR | #2DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0108 |  |  | 1-0D-04 |  |  | #2DTR | ON/OFF | #2DTR 63Q |  |  | B1/D09_A1 | [8 empty] | 斗工DS.#2DTR_63Q | #2DTR 63Q RY | MTR | [5 empty] | 494 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0109 |  |  | 1-0D-05 |  |  | 310 | GDA | #1DTR 1A 310 GDA |  |  | B3/D09_A1 | [8 empty] | 斗工DS.310_GDA | #1DTR 1A 310 GDA | OTHER | [5 empty] | 495 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0110 |  |  | 1-0D-06 |  |  | 320 | GDA | #1DTR 1B 320 GDA |  |  | B3/D09_A1 | [8 empty] | 斗工DS.320_GDA | #1DTR 1B 320 GDA | OTHER | [5 empty] | 496 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | 330A1 | #2DTR(A)(330A1) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0111 |  |  | 1-0D-07 |  |  | 330A1 | GDA | #2DTR 2A 330A1 GDA |  |  | B3/D09_A1 | [8 empty] | 斗工DS.330A1_GDA | #2DTR 2A 330A1 GDA | OTHER | [5 empty] | 497 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | 330A2 | #2DTR(A)(330A2) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0112 |  |  | 1-0E-00 |  |  | 330A2 | GDA | #2DTR 2A 330A2 GDA |  |  | B3/D09_A1 | [8 empty] | 斗工DS.330A2_GDA | #2DTR 2A 330A2 GDA | OTHER | [5 empty] | 498 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | 340B1 | #2DTR(B)(340B1) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0113 |  |  | 1-0E-01 |  |  | 340B1 | GDA | #2DTR 2B 340B1 GDA |  |  | B3/D09_A1 | [8 empty] | 斗工DS.340B1_GDA | #2DTR 2B 340B1 GDA | OTHER | [5 empty] | 499 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | 340B2 | #2DTR(B)(340B2) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0114 |  |  | 1-0E-02 |  |  | 340B2 | GDA | #2DTR 2B 340B2 GDA |  |  | B3/D09_A1 | [8 empty] | 斗工DS.340B2_GDA | #2DTR 2B 340B2 GDA | OTHER | [5 empty] | 500 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | RTU | RTU |  | RTU_MCT |  |  | Status | RTU Master Ry | Open/Close | Y | E | DI-SP | [6 empty] | 0115 |  |  | 1-0E-03 |  |  | 161RTU | MCT_ SOE | RTU MASTER RY SOE |  |  | B3/D09_A1 | [16 empty] | 501 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D09 | 斗工DS |  |  | 1DTR | #1DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0116 |  |  | 1-0E-04 |  |  | 86A |  | #1 DTR. 86A |  |  | B1/D09_A1 | [8 empty] | 斗工DS.#1DTR_86A | #1DTR 86A | OTHER | [5 empty] | 502 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS |  |  | 2DTR | #2DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0117 |  |  | 1-0E-05 |  |  | 86A |  | #2 DTR. 86A |  |  | B1/D09_A1 | [8 empty] | 斗工DS.#2DTR_86A | #2DTR 86A | OTHER | [5 empty] | 503 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU51 | 工五一線(XU51) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0129 |  |  | 1-10-01 |  |  | F1 | 51A | F1 PHA 工五一線 XU51 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU51_PHA | 23KV工五一線(XU51) 相間RY | FEEDER | [5 empty] | 504 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU51 | 工五一線(XU51) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-10-02 |  |  | F1 | 51NA | F1 GDA 工五一線 XU51 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU51_GDA | 23KV工五一線(XU51) 接地RY | FEEDER | [5 empty] | 505 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU52 | 工五二線(XU52) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0132 |  |  | 1-10-04 |  |  | F2 | 51A | F2 PHA 工五二線 XU52 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU52_PHA | 23KV工五二線(XU52) 相間RY | FEEDER | [5 empty] | 506 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU52 | 工五二線(XU52) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0133 |  |  | 1-10-05 |  |  | F2 | 51NA | F2 GDA 工五二線 XU52 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU52_GDA | 23KV工五二線(XU52) 接地RY | FEEDER | [5 empty] | 507 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU53 | 工五三線(XU53) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0135 |  |  | 1-10-07 |  |  | F3 | 51A | F3 PHA 工五三線 XU53 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU53_PHA | 23KV工五三線(XU53) 相間RY | FEEDER | [5 empty] | 508 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU53 | 工五三線(XU53) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0136 |  |  | 1-11-00 |  |  | F3 | 51NA | F3 GDA 工五三線 XU53 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU53_GDA | 23KV工五三線(XU53) 接地RY | FEEDER | [5 empty] | 509 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU54 | 工五四線(XU54) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0138 |  |  | 1-11-02 |  |  | F4 | 51A | F4 PHA 工五四線 XU54 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU54_PHA | 23KV工五四線(XU54) 相間RY | FEEDER | [5 empty] | 510 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU54 | 工五四線(XU54) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0139 |  |  | 1-11-03 |  |  | F4 | 51NA | F4 GDA 工五四線 XU54 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU54_GDA | 23KV工五四線(XU54) 接地RY | FEEDER | [5 empty] | 511 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU55 | 工五五線(XU55) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0141 |  |  | 1-11-05 |  |  | F5 | 51A | F5 PHA 工五五線 XU55 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU55_PHA | 23KV工五五線(XU55) 相間RY | FEEDER | [5 empty] | 512 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU55 | 工五五線(XU55) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0142 |  |  | 1-11-06 |  |  | F5 | 51NA | F5 GDA 工五五線 XU55 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU55_GDA | 23KV工五五線(XU55) 接地RY | FEEDER | [5 empty] | 513 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | 210 | #1SC(210) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0144 |  |  | 1-12-00 |  |  | 210 #1SC | 51/51A | #1SC 210 #1SC SCA 51+51N |  |  | B3/D09_A1 | [8 empty] | 斗工DS.210_SCA | 23KV #1SC 51,51N RY | SC | [5 empty] | 514 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | 210 | #1SC(210) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0145 |  |  | 1-12-01 |  |  | 210 #1SC | 27/59A | #1SC 210 #1SC UVA 27+59 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.210_UVA | 23KV #1SC 27RY(欠壓) | SC | [5 empty] | 515 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | 100 | TIE(100) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0147 |  |  | 1-12-03 |  |  | 100 | PHA | #1TIE 1A 100 PHA |  |  | B3/D09_A1 | [8 empty] | 斗工DS.100_51A | 23KV TIE(100) 51RY | TIE | [5 empty] | 516 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | 100 | TIE(100) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0148 |  |  | 1-12-04 |  |  | 100 | GDA | #1TIE 1A 100 GDA |  |  | B3/D09_A1 | [8 empty] | 斗工DS.100_51NA | 23KV TIE(100) 51N RY | TIE | [5 empty] | 517 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU26 | 工六線(XU26) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0150 |  |  | 1-12-06 |  |  | F6 | 51A | F6 PHA 工六線 XU26 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU26_PHA | 11KV工六線(XU26) 相間RY | FEEDER | [5 empty] | 518 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU26 | 工六線(XU26) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0151 |  |  | 1-12-07 |  |  | F6 | 51NA | F6 GDA 工六線 XU26 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU26_GDA | 11KV工六線(XU26) 接地RY | FEEDER | [5 empty] | 519 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU27 | 工七線(XU27) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0153 |  |  | 1-13-01 |  |  | F7 | 51A | F7 PHA 工七線 XU27 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU27_PHA | 11KV工七線(XU27) 相間RY | FEEDER | [5 empty] | 520 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU27 | 工七線(XU27) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0154 |  |  | 1-13-02 |  |  | F7 | 51NA | F7 GDA 工七線 XU27 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU27_GDA | 11KV工七線(XU27) 接地RY | FEEDER | [5 empty] | 521 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU28 | 工八線(XU28) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0156 |  |  | 1-13-04 |  |  | F8 | 51A | F8 PHA 工八線 XU28 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU28_PHA | 11KV工八線(XU28) 相間RY | FEEDER | [5 empty] | 522 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU28 | 工八線(XU28) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0157 |  |  | 1-13-05 |  |  | F8 | 51NA | F8 GDA 工八線 XU28 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU28_GDA | 11KV工八線(XU28) 接地RY | FEEDER | [5 empty] | 523 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU29 | 工九線(XU29) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0159 |  |  | 1-13-07 |  |  | F9 | 51A | F9 PHA 工九線 XU29 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU29_PHA | 11KV工九線(XU29) 相間RY | FEEDER | [5 empty] | 524 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU29 | 工九線(XU29) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0160 |  |  | 1-14-00 |  |  | F9 | 51NA | F9 GDA 工九線 XU29 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU29_GDA | 11KV工九線(XU29) 接地RY | FEEDER | [5 empty] | 525 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU30 | 工十線(XU30) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0162 |  |  | 1-14-02 |  |  | F10 | 51A | F10 PHA 工十線 XU30 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU30_PHA | 11KV工十線(XU30) 相間RY | FEEDER | [5 empty] | 526 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU30 | 工十線(XU30) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0163 |  |  | 1-14-03 |  |  | F10 | 51NA | F10 GDA 工十線 XU30 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU30_GDA | 11KV工十線(XU30) 接地RY | FEEDER | [5 empty] | 527 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0165 |  |  | 1-14-05 |  |  | 220 #2SC | 51/51A | #2SC 220 #2SC SCA 51+51N |  |  | B3/D09_A1 | [8 empty] | 斗工DS.220_SCA | 11KV #2SC 51,51N RY | SC | [5 empty] | 528 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0166 |  |  | 1-14-06 |  |  | 220 #2SC | 27/59A | #2SC 220 #2SC UVA 27+59 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | [5 empty] | 529 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | 200 | TIE(200) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0168 |  |  | 1-15-00 |  |  | 200 | 51/51A | #1TIE 1B 200 PHA |  |  | B3/D09_A1 | [8 empty] | 斗工DS.200_51A | 11KV TIE(200) 51RY | TIE | [5 empty] | 530 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | 200 | TIE(200) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0169 |  |  | 1-15-01 |  |  | 200 | 27/59 A | #1TIE 1B 200 GDA |  |  | B3/D09_A1 | [8 empty] | 斗工DS.200_51NA | 11KV TIE(200) 51N RY | TIE | [5 empty] | 531 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | 390 | #1SSTR(390) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0171 |  |  | 1-15-03 |  |  | 390 | PHA | #1SSTR HPA |  |  | B3/D09_A1 | [8 empty] | 斗工DS.#1SSTR_51A | #1SSTR 51RY | OTHER | [5 empty] | 532 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | 390 | #1SSTR(390) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0172 |  |  | 1-15-04 |  |  | 390 | GDA | #1SSTR GDA |  |  | B3/D09_A1 | [8 empty] | 斗工DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | [5 empty] | 533 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU61 | 工六一線(XU61) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0174 |  |  | 1-15-06 |  |  | F11 | 51A | F11 PHA 工六一線 XU61 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU61_PHA | 23KV工六一線(XU61) 相間RY | FEEDER | [5 empty] | 534 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU61 | 工六一線(XU61) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0175 |  |  | 1-15-07 |  |  | F11 | 51NA | F11 GDA 工六一線 XU61 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU61_GDA | 23KV工六一線(XU61) 接地RY | FEEDER | [5 empty] | 535 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU62 | 工六二線(XU62) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0177 |  |  | 1-16-01 |  |  | F12 | 51A | F12 PHA 工六二線 XU62 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU62_PHA | 23KV工六二線(XU62) 相間RY | FEEDER | [5 empty] | 536 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU62 | 工六二線(XU62) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0178 |  |  | 1-16-02 |  |  | F12 | 51NA | F12 GDA 工六二線 XU62 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU62_GDA | 23KV工六二線(XU62) 接地RY | FEEDER | [5 empty] | 537 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU63 | 工六三線(XU63) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0180 |  |  | 1-16-04 |  |  | F13 | 51A | F13 PHA 工六三線 XU63 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU63_PHA | 23KV工六三線(XU63) 相間RY | FEEDER | [5 empty] | 538 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU63 | 工六三線(XU63) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0181 |  |  | 1-16-05 |  |  | F13 | 51NA | F13 GDA 工六三線 XU63 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU63_GDA | 23KV工六三線(XU63) 接地RY | FEEDER | [5 empty] | 539 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU64 | 工六四線(XU64) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0183 |  |  | 1-16-07 |  |  | F14 | 51/51A | F14 PHA 工六四線 XU64 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU64_PHA | 23KV工六四線(XU64) 相間RY | FEEDER | [5 empty] | 540 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU64 | 工六四線(XU64) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0184 |  |  | 1-17-00 |  |  | F14 | 27/59 A | F14 GDA 工六四線 XU64 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU64_GDA | 23KV工六四線(XU64) 接地RY | FEEDER | [5 empty] | 541 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU65 | 工六五線(XU65) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0186 |  |  | 1-17-02 |  |  | F15 | 51A | F15 PHA 工六五線 XU65 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU65_PHA | 23KV工六五線(XU65) 相間RY | FEEDER | [5 empty] | 542 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU65 | 工六五線(XU65) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0187 |  |  | 1-17-03 |  |  | F15 | 51NA | F15 GDA 工六五線 XU65 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU65_GDA | 23KV工六五線(XU65) 接地RY | FEEDER | [5 empty] | 543 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | 300 | TIE(300) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0189 |  |  | 1-17-05 |  |  | 300 | 51A | #2TIE 2A 300 PHA |  |  | B3/D09_A1 | [8 empty] | 斗工DS.300_51A | 23KV TIE(300) 51RY | TIE | [5 empty] | 544 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | 300 | TIE(300) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0190 |  |  | 1-17-06 |  |  | 300 | 51NA | #2TIE 2A 300 GDA |  |  | B3/D09_A1 | [8 empty] | 斗工DS.300_51NA | 23KV TIE(300) 51N RY | TIE | [5 empty] | 545 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | 230 | #3SC(230) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0192 |  |  | 1-18-00 |  |  | 230 #3SC | 51A | #2ASC 230 #3SC SCA 51+51N |  |  | B3/D09_A1 | [8 empty] | 斗工DS.230_SCA | 23KV #3SC 51,51N RY | SC | [5 empty] | 546 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | 230 | #3SC(230) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0193 |  |  | 1-18-01 |  |  | 230 #3SC | 51NA | #2ASC 230 #3SC UVA 27+59 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.230_UVA | 23KV #3SC 27RY(欠壓) | SC | [5 empty] | 547 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | 490 | #1SSTR(490) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0195 |  |  | 1-18-03 |  |  | 490 | 51A | #2SSTR PHA |  |  | B3/D09_A1 | [8 empty] | 斗工DS.#2SSTR_51A | #2SSTR 51RY | OTHER | [5 empty] | 548 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | 490 | #1SSTR(490) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0196 |  |  | 1-18-04 |  |  | 490 | 51NA | #2SSTR GDA |  |  | B3/D09_A1 | [8 empty] | 斗工DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | [5 empty] | 549 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU36 | 工十六線(XU36) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0198 |  |  | 1-18-06 |  |  | F16 | 51A | F16 PHA 工十六線 XU36 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU36_PHA | 11KV工十六線(XU36) 相間RY | FEEDER | [5 empty] | 550 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU36 | 工十六線(XU36) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0199 |  |  | 1-18-07 |  |  | F16 | 51NA | F16 GDA 工十六線 XU36 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU36_GDA | 11KV工十六線(XU36) 接地RY | FEEDER | [5 empty] | 551 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU37 | 工十七線(XU37) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0201 |  |  | 1-19-01 |  |  | F17 | 51A | F17 PHA 工十七線 XU37 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU37_PHA | 11KV工十七線(XU37) 相間RY | FEEDER | [5 empty] | 552 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU37 | 工十七線(XU37) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0202 |  |  | 1-19-02 |  |  | F17 | 51NA | F17 GDA 工十七線 XU37 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU37_GDA | 11KV工十七線(XU37) 接地RY | FEEDER | [5 empty] | 553 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU38 | 工十八線(XU38) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0204 |  |  | 1-19-04 |  |  | F18 | 51A | F18 PHA 工十八線 XU38 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU38_PHA | 11KV工十八線(XU38) 相間RY | FEEDER | [5 empty] | 554 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU38 | 工十八線(XU38) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0205 |  |  | 1-19-05 |  |  | F18 | 51NA | F18 GDA 工十八線 XU38 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU38_GDA | 11KV工十八線(XU38) 接地RY | FEEDER | [5 empty] | 555 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU39 | 工十九線(XU39) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0207 |  |  | 1-19-07 |  |  | F19 | 51A | F19 PHA 工十九線 XU39 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU39_PHA | 11KV工十九線(XU39) 相間RY | FEEDER | [5 empty] | 556 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU39 | 工十九線(XU39) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0208 |  |  | 1-1A-00 |  |  | F19 | 51NA | F19 GDA 工十九線 XU39 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU39_GDA | 11KV工十九線(XU39) 接地RY | FEEDER | [5 empty] | 557 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU40 | 工二十線(XU40) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0210 |  |  | 1-1A-02 |  |  | F20 | 51A | F20 PHA 工二十線 XU40 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU40_PHA | 11KV工二十線(XU40) 相間RY | FEEDER | [5 empty] | 558 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU40 | 工二十線(XU40) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0211 |  |  | 1-1A-03 |  |  | F20 | 51NA | F20 GDA 工二十線 XU40 |  |  | B2/D09_D1 | [8 empty] | 斗工DS.XU40_GDA | 11KV工二十線(XU40) 接地RY | FEEDER | [5 empty] | 559 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | 240 | #4SC(240) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0213 |  |  | 1-1A-05 |  |  | 240 #4SC | 51A | #2BSC 240 #4SC SCA 51+51N |  |  | B3/D09_A1 | [8 empty] | 斗工DS.240_SCA | 11KV #4SC 51,51N RY | SC | [5 empty] | 560 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | 240 | #4SC(240) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0214 |  |  | 1-1A-06 |  |  | 240 #4SC | 51NA | #2BSC 240 #4SC UVA 27+59 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.240_UVA | 11KV #4SC 27RY(欠壓) | SC | [5 empty] | 561 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | 400 | TIE(400) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0216 |  |  | 1-1B-00 |  |  | 400 | 51A | #2TIE 2B 400 PHA |  |  | B3/D09_A1 | [8 empty] | 斗工DS.400_51A | 11KV TIE(400) 51RY | TIE | [5 empty] | 562 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | 400 | TIE(400) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0217 |  |  | 1-1B-01 |  |  | 400 | 51NA | #2TIE 2B 400 GDA |  |  | B3/D09_A1 | [8 empty] | 斗工DS.400_51NA | 11KV TIE(400) 51N RY | TIE | [5 empty] | 563 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | RTU | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0513 |  |  | 1-30-01 |  |  | RTU | L/R | L/R STATUS |  |  | ELEM/D09_A1 | [8 empty] | 斗工DS.RTU_S/L | RTU SUPY/LOCAL | OTHER | [5 empty] | 564 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
D09 | 斗工DS |  |  | 1DTR(A) | #1DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0537 |  |  | 1-31-09 |  |  | #1ATR | 遙控/現場 | #1ATR OLTC S/L |  | c | B1/D09_A1 | [8 empty] | 斗工DS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | [5 empty] | 565 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D09 | 斗工DS |  |  | 1DTR(A) | #1DTR(A) |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0539 |  |  | 1-31-11 |  |  | #1DTR | TRA | #1DTR 重故障 |  | a | B1/D09_A1 | [8 empty] | 斗工DS.#1DTR_TRA | #1DTR 重故障 | MTR | [5 empty] | 566 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS |  |  | 1DTR(A) | #1DTR(A) |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0540 |  |  | 1-31-12 |  |  | #1DTR | TRF | #1DTR 輕故障 |  |  | B1/D09_A1 | [8 empty] | 斗工DS.#1DTR_TRF | #1DTR 輕故障 | MTR | [5 empty] | 567 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS |  |  | 1DTR(B) | #1DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0541 |  |  | 1-31-13 |  |  | #1BTR | 遙控/現場 | #1BTR OLTC S/L |  | b | B1/D09_A1 | [8 empty] | 斗工DS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | [5 empty] | 568 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D09 | 斗工DS |  |  | 2DTR | #2DTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0544 |  |  | 1-32-00 |  |  | #2ATR | 遙控/現場 | #2ATR OLTC S/L |  | c | B1/D09_A1 | [8 empty] | 斗工DS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | [5 empty] | 569 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D09 | 斗工DS |  |  | 2DTR | #2DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0546 |  |  | 1-32-02 |  |  | #2DTR | TRA | #2DTR 重故障 |  | a | B1/D09_A1 | [8 empty] | 斗工DS.#2DTR_TRA | #2DTR 重故障 | MTR | [5 empty] | 570 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS |  |  | 2DTR | #2DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0547 |  |  | 1-32-03 |  |  | #2DTR | TRF | #2DTR 輕故障 |  |  | B1/D09_A1 | [8 empty] | 斗工DS.#2DTR_TRF | #2DTR 輕故障 | MTR | [5 empty] | 571 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS |  |  | 2DTR | #2DTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0548 |  |  | 1-32-04 |  |  | #2BTR | 遙控/現場 | #2BTR OLTC S/L |  | a | B1/D09_A1 | [8 empty] | 斗工DS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | [5 empty] | 572 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D09 | 斗工DS | 0 |  | ComPoint |  |  | OLTC_A |  |  | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0555 |  |  | 1-32-11 |  |  | OLTC | OLTCA | OLTC 15分鐘內連動3次警報 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | [5 empty] | 573 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工～斗工山線(1510) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0556 |  |  | 1-32-12 |  |  | 1510 | RYFA | 鉅工斗工山線 1510 電驛故障 |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1510_RYFA | 鉅工斗工山線(1510)數位電驛故障 | OTHER | [5 empty] | 574 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工～斗工山線(1510) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0557 |  |  | 1-32-13 |  |  | 1510 | 87CFA | 鉅工斗工山線 1510 電驛通訊故障 |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1510_87CFA | 鉅工斗工山線(1510)87RY通訊故障 | OTHER | [5 empty] | 575 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工～斗工海線(1520) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0558 |  |  | 1-32-14 |  |  | 1520 | RYFA | 鉅工斗工海線 1520 電驛故障 |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1520_RYFA | 鉅工斗工海線(1520)數位電驛故障 | OTHER | [5 empty] | 576 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工～斗工海線(1520) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0559 |  |  | 1-32-15 |  |  | 1520 | 87CFA | 鉅工斗工海線 1520 電驛通訊故障 |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1520_87CFA | 鉅工斗工海線(1520)87RY通訊故障 | OTHER | [5 empty] | 577 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1540 | 雲林~斗工線(1540) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0560 |  |  | 1-33-00 |  |  | 1540 | RYFA | 雲林斗工線 1540 電驛故障 |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1540_RYFA | 雲林斗工線(1540)數位電驛故障 | OTHER | [5 empty] | 578 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1540 | 雲林~斗工線(1540) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0561 |  |  | 1-33-01 |  |  | 1540 | 87CFA | 雲林斗工線 1540 電驛通訊故障 |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1540_87CFA | 雲林斗工線(1540)87RY通訊故障 | OTHER | [5 empty] | 579 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1530 | 嘉民～斗工紅線(1530) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0562 |  |  | 1-33-02 |  |  | 1530 | RYFA | 嘉民斗工紅線 1530 電驛故障 |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1530_RYFA | 嘉民斗工紅線(1530)數位電驛故障 | OTHER | [5 empty] | 580 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1530 | 嘉民～斗工紅線(1530) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0563 |  |  | 1-33-03 |  |  | 1530 | 87CFA | 嘉民斗工紅線 1530 電驛通訊故障 |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1530_87CFA | 嘉民斗工紅線(1530)87RY通訊故障 | OTHER | [5 empty] | 581 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1550 | 斗工～富喬線(1550) |  | 1A5Other | 待新增!!__MDAR | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0564 |  |  | 1-33-04 |  |  | 1550 | ON/OFF | 斗工富喬線 1550 MADR |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1550_MDARF | 1550MDAR RY故障 | OTHER | [5 empty] | 582 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1550 | 斗工～富喬線(1550) |  | 85CFA |  |  | Status | 85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0565 |  |  | 1-33-05 |  |  | 1550 | ON/OFF | 斗工富喬線 1550 TONE |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1550_TONEF | 1550TONE訊號不良 | OTHER | [5 empty] | 583 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1610 | 榴中～斗工一路(1610) |  | 87C_LA |  |  | Status | Cable 87RY 閉鎖RC | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0570 |  |  | 1-33-10 |  |  | 1610 | A/N | 榴中斗工一路 1610 87LA |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1610_87LA | 1610 數位電驛故障 | OTHER | [5 empty] | 584 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1610 | 榴中～斗工一路(1610) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0571 |  |  | 1-33-11 |  |  | 1610 | A/N | 榴中斗工一路 1610 87LCFA(87L通訊故障) |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1610_87LCFA | 1610 87L通訊故障 | OTHER | [5 empty] | 585 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1620 | 榴中～斗工二路(1620) |  | 87C_LA |  |  | Status | Cable 87RY 閉鎖RC | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0572 |  |  | 1-33-12 |  |  | 1620 | A/N | 榴中斗工二路 1620 87LA |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1620_87LA | 1620 數位電驛故障 | OTHER | [5 empty] | 586 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1620 | 榴中～斗工二路(1620) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0573 |  |  | 1-33-13 |  |  | 1620 | A/N | 榴中斗工二路 1620 87LCFA(87L通訊故障) |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1620_87LCFA | 1620 87L通訊故障 | OTHER | [5 empty] | 587 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | StaDev | 所內設施 |  | GEN | 緊急發電機運轉 | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0574 |  |  | 1-33-14 |  |  | Locate Empty | ON/OFF | 緊急發電機運轉 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.GEN | 緊急發電機運轉 | OTHER | [5 empty] | 588 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ON/OFF | OFF
D09 | 斗工DS | 0 |  | StaDev | 所內設施 |  | Fire1 | 受信總機 |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0810 |  |  | 2-32-10 |  |  | 火災警報(1) | ON/OFF | 火災警報(1)受信總機 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | [5 empty] | 589 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | ComPoint | BUS |  | BUS_RYFA |  |  | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0811 |  |  | 2-32-11 |  |  | BUS | A/N | 161KV BUS數位電驛故障 |  |  | B2/D09_A1 | [8 empty] | 斗工DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | [5 empty] | 590 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | ComPoint |  |  | 87CTFA |  | Element | Status | 87RY CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0812 |  |  | 2-32-12 |  |  | BUS | A/N | 161KV BUS 87RY CT 迴路故障 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.161KV_BUS_CTFA | 161KV BUS 87RY CT回路故障 | OTHER | [5 empty] | 591 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | StaDev | 所內設施 |  | Burglar1 | 保全 |  | Status | 無人化防盜1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0813 |  |  | 2-32-13 |  |  | Locate Empty | ON/OFF | 無人化防盜(1) 保全 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | [5 empty] | 592 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工～斗工山線(1510) |  | DTTA |  |  | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0814 |  |  | 2-32-14 |  |  | Locate Empty | ON/OFF | 無人化防盜(2) |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1510_DTTA | 鉅工斗工山線(1510)遠方遙跳 | OTHER | [5 empty] | 593 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工～斗工海線(1520) |  | DTTA |  |  | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0815 |  |  | 2-32-15 |  |  | Locate Empty | ON/OFF | 無人化防盜(3) |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1520_DTTA | 鉅工斗工海線(1520)遠方遙跳 | OTHER | [5 empty] | 594 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | StaDev | 所內設施 |  | Door1 |  |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0816 |  |  | 2-33-00 |  |  | Locate Empty | ON/OFF | 無人化門禁(1) 大門 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.無人化門禁(1) | 無人化門禁(1)建築物大門 | OTHER | [5 empty] | 595 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | StaDev | 所內設施 |  | Door2 |  |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0817 |  |  | 2-33-01 |  |  | Locate Empty | ON/OFF | 無人化門禁(2)控制室 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.無人化門禁(2) | 無人化門禁(2)控制室大門 | OTHER | [5 empty] | 596 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | StaDev | 所內設施 |  | Door3 |  |  | Status | 無人化門禁3 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0818 |  |  | 2-33-02 |  |  | Locate Empty | ON/OFF | 無人化門禁(3) |  |  | B3/D09_A1 | [8 empty] | 斗工DS.無人化門禁(3) | 無人化門禁(3) | OTHER | [5 empty] | 597 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | StaDev | 所內設施 |  | AIRCON |  |  | Status | 冷氣跳脫 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0821 |  |  | 2-33-05 |  |  | Locate Empty | ON/OFF | 空調機警報 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.空調機故障 | 空調機故障或電源跳脫 | OTHER | [5 empty] | 598 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | NORMAL/FAULT | NORMAL
D09 | 斗工DS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0822 |  |  | 2-33-06 |  |  | ACB1 | ON/OFF | 所內電源 ACB1 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | [5 empty] | 599 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D09 | 斗工DS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0824 |  |  | 2-33-08 |  |  | STUV | ON/OFF | 所內欠壓警報 |  |  | ELEM/D09_A1 | [8 empty] | 斗工DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | [5 empty] | 600 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0825 |  |  | 2-33-09 |  |  | VUA | ON/OFF | VUA1 |  |  | B2/D09_A1 | [8 empty] | 斗工DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | [5 empty] | 601 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0826 |  |  | 2-33-10 |  |  | VUA | ON/OFF | VUA2 |  |  | B2/D09_A1 | [8 empty] | 斗工DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | [5 empty] | 602 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0827 |  |  | 2-33-11 |  |  | DCA | ON/OFF | DCA 直流電源故障 |  |  | ELEM/D09_A1 | [8 empty] | 斗工DS.直流電源DCA | 直流電源故障警報 | OTHER | [5 empty] | 603 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0828 |  |  | 2-33-12 |  |  | CHG1 | ON/OFF | CHG1充電機故障 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | [5 empty] | 604 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0829 |  |  | 2-33-13 |  |  | CHG2 | ON/OFF | 通訊充電機故障 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | [5 empty] | 605 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0830 |  |  | 2-33-14 |  |  | DCE | ON/OFF | DCE 直流接地 |  |  | ELEM/D09_A1 | [8 empty] | 斗工DS.直流電源DCE | 直流電源接地故障警報 | OTHER | [5 empty] | 606 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | ComPoint |  |  | COMT |  |  | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0831 |  |  | 2-33-15 |  |  | 空壓機 | ON/OFF | 161KV COMT 空壓機超時 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.161空壓機COMT | 161KV空壓機運轉超時警報 | OTHER | [5 empty] | 607 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0832 |  |  | 2-34-00 |  |  | 161KV | ON/OFF | 161KV CB重故障 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.161KV_CBA | 161KV斷路器重故障 | OTHER | [5 empty] | 608 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0833 |  |  | 2-34-01 |  |  | 161KV | ON/OFF | 161KV CB輕故障 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | [5 empty] | 609 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | ComPoint |  |  | FDR_CBA |  |  | Status | 11/22kV斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0834 |  |  | 2-34-02 |  |  | 22KV 11KV | ON/OFF | 22KV 11KV CB重故障 |  |  | ELEM/D09_D1 | [8 empty] | 斗工DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | [5 empty] | 610 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | ComPoint |  |  | FDR_CBF |  |  | Status | 11/22kV斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0835 |  |  | 2-34-03 |  |  | 22KV 11KV | ON/OFF | 22KV 11KV CB輕故障 |  |  | ELEM/D09_D1 | [8 empty] | 斗工DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | [5 empty] | 611 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | StaDev | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0836 |  |  | 2-34-04 |  |  | PSF | ON/OFF | 其他重故障 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.其他重故障 | 變電所內其他重故障 | OTHER | [5 empty] | 612 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | StaDev | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0837 |  |  | 2-34-05 |  |  | PSA | ON/OFF | 其他輕故障 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.其他輕故障 | 變電所內其他輕故障 | OTHER | [5 empty] | 613 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | ComPoint |  |  | FDR_60A |  |  | Status | 11/22kV電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0838 |  |  | 2-34-06 |  |  | SC 60RY | ON/OFF | 60A |  |  | B3/D09_A1 | [8 empty] | 斗工DS.23KV_SC_60A | 23/11KV SC 60A | OTHER | [5 empty] | 614 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0839 |  |  | 2-34-07 |  |  | ACFA | ON/OFF | 通訊設備 AC故障 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | [5 empty] | 615 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | StaDev | 所內設施 |  | R_Temp | 通信室 |  | Status | 溫度警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0842 |  |  | 2-34-10 |  |  | PCMA | ON/OFF | 通信室溫控警報 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.通信機房溫度 | 通信機房溫度警報 | OTHER | [5 empty] | 616 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | StaDev | 所內設施 |  | OilLeak1 |  |  | Status | 洩油池水位警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0843 |  |  | 2-34-11 |  |  | OW1 | ON/OFF | 水位警報 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.洩油池水位警報 | 洩油池水位警報 | OTHER | [5 empty] | 617 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0845 |  |  | 2-34-13 |  |  | ACBA | ON/OFF | ACB警報 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.所內電源ACBA | 所內電源故障警報 | OTHER | [5 empty] | 618 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | ComPoint |  |  | 25TA |  |  | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0846 |  |  | 2-34-14 |  |  | 25TA | ON/OFF | 同步校核裝置超時警報 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | [5 empty] | 619 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | ComPoint |  |  | 25PFA |  |  | Status | 同步校核電驛電源 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0847 |  |  | 2-34-15 |  |  | 25PFA | ON/OFF | 同步校核裝置電源故障 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER | [5 empty] | 620 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | ComPoint |  |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0848 |  |  | 2-35-00 |  |  | LOA | ON/OFF | 11KV 22KV 饋線 79RY 復閉失敗 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.饋線復閉LOA | 11KV 22KV饋線79RY復閉失敗 | OTHER | [5 empty] | 621 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | ComPoint |  |  | OPA |  |  | Status | 充油電纜低壓警報 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0849 |  |  | 2-35-01 |  |  | OPA | ON/OFF | 161KV 油壓電纜警報 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | [5 empty] | 622 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | StaDev | 所內設施 |  | Water1 | 0.5M |  | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0850 |  |  | 2-35-02 |  |  | 地下室 | A/N | 地下室 0.5M 水位警報 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.水位警報(1) | 地下室水位警報(1) | OTHER | [5 empty] | 623 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | StaDev | 所內設施 |  | Water2 | 1M |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0851 |  |  | 2-35-03 |  |  | 地下室 | A/N | 地下室 1M 水位警報 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.水位警報(2) | 地下室水位警報(2) | OTHER | [5 empty] | 624 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | ComPoint |  |  | 81A_RYFA | 81RY RYFA | Element | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0852 |  |  | 2-35-04 |  |  | RYFA | A/N | 饋線低頻電驛故障 |  |  | B3/D09_A1 | [8 empty] | 斗工DS.81RYFA | 低頻電驛故障 | OTHER | [5 empty] | 625 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0853 |  |  | 2-35-05 |  |  | 161KV TIE | 測試/正常 | 161KV TIE (1500)50RY 測試/正常 |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | [5 empty] | 626 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Test | Test | 1 |  |  | TEST/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0854 |  |  | 2-35-06 |  |  | OSCF | A/N | 161KV示波器缺紙或故障警報OSCF |  |  | B3/D09_A1 | [8 empty] | 斗工DS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | [5 empty] | 627 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1530 | 嘉民～斗工紅線(1530) |  | DTTA |  |  | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0857 |  |  | 2-35-09 |  |  | 1530 | DTTA | 嘉民斗工紅線 1530 遠方遙跳DTTA |  |  | B2/D09_A1 | [8 empty] | 斗工DS.1530_DTTA | 嘉民斗工紅線(1530)遠方遙跳 | OTHER | [5 empty] | 628 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D09 | 斗工DS |  |  | 1DTR | #1DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0931 |  |  | 2-3A-11 |  |  | #1DTR | RYFA | #1DTR. 數位電驛故障 |  |  | B1/D09_A1 | [8 empty] | 斗工DS.#1DTR_RYFA | #1DTR數位電驛故障 | OTHER | [5 empty] | 629 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS |  |  | 2DTR | #2DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0935 |  |  | 2-3A-15 |  |  | #2DTR | RYFA | #2DTR. 數位電驛故障 |  |  | B1/D09_A1 | [8 empty] | 斗工DS.#2DTR_RYFA | #2DTR數位電驛故障 | OTHER | [5 empty] | 630 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | RTU | RTU |  | ADCH4 | 請TPC確認 | INSERT | MvMoment | No4 AI參考點 90% |  | Y |  | AI | [6 empty] | 0193 |  |  | 2-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.4 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | [5 empty] | 631 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 0 |  | RTU | RTU |  | ADCL4 | 請TPC確認 | INSERT | MvMoment | No4 AI參考點 10% |  | Y |  | AI | [6 empty] | 0192 |  |  | 2-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.4 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D09_A1 | [8 empty] | 斗工DS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | [5 empty] | 632 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
D09 | 斗工DS | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/D09_A1 | [12 empty] | 斗工DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: D09/161/1BUS/V; OPRD2: D09/161/2BUS/V
D09 | 斗工DS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/D09_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: D09/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
D09 | 斗工DS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/D09_A1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_7 | OPRD1: D09/161/1510/MW; OPRD2: D09/161/1520/MW; OPRD3: D09/161/1530/MW; OPRD4: D09/161/1540/MW; OPRD5: D09/161/1550/MW; OPRD6: D09/161/1610/MW; OPRD7: D09/161/1620/MW
D09 | 斗工DS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/D09_A1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: D09/0/CalcPoint/OPRN2_MW
D09 | 斗工DS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/D09_A1 | [17 empty] | none
D09 | 斗工DS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/D09_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: D09/0/CalcPoint/OPRN1; OPRD2: D09/0/CalcPoint/OPRN2; OPRD3: D09/0/CalcPoint/PRFL_UL
D09 | 斗工DS |  |  | 1DTR | 1DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D09_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D09/22/310/I_R; OPRD2: D09/11/320/I_R
D09 | 斗工DS |  |  | 1DTR | 1DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D09_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D09/22/310/I_S; OPRD2: D09/11/320/I_S
D09 | 斗工DS |  |  | 1DTR | 1DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D09_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D09/22/310/I_T; OPRD2: D09/11/320/I_T
D09 | 斗工DS |  |  | 2DTR | 2DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D09_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D09/22/330/I_R; OPRD2: D09/11/340/I_R
D09 | 斗工DS |  |  | 2DTR | 2DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D09_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D09/22/330/I_S; OPRD2: D09/11/340/I_S
D09 | 斗工DS |  |  | 2DTR | 2DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D09_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D09/22/330/I_T; OPRD2: D09/11/340/I_T
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工～斗工山線(1510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D09_A1 | [12 empty] | 斗工DS.1510_AMP | 鉅工山線 AMP | LINE161 | AMP_CAL | C20R1576 | amp_cal | OPRD1: D09/161/1510/MW; OPRD2: D09/161/1510/MVAR; OPRD3: D09/0/CalcPoint/Vbs4
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工～斗工海線(1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D09_A1 | [12 empty] | 斗工DS.1520_AMP | 鉅工海線 AMP | LINE161 | AMP_CAL | C20R1576 | amp_cal | OPRD1: D09/161/1520/MW; OPRD2: D09/161/1520/MVAR; OPRD3: D09/0/CalcPoint/Vbs4
D09 | 斗工DS | 161 | 161kV | 1530 | 嘉民～斗工紅線(1530) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D09_A1 | [12 empty] | 斗工DS.1530_AMP | 嘉民斗工紅線 AMP | LINE161 | AMP_CAL | C20R1576 | amp_cal | OPRD1: D09/161/1530/MW; OPRD2: D09/161/1530/MVAR; OPRD3: D09/0/CalcPoint/Vbs4
D09 | 斗工DS | 161 | 161kV | 1540 | 雲林~斗工線(1540) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D09_A1 | [12 empty] | 斗工DS.1540_AMP | 雲林斗工線 AMP | LINE161 | AMP_CAL | C20R1576 | amp_cal | OPRD1: D09/161/1540/MW; OPRD2: D09/161/1540/MVAR; OPRD3: D09/0/CalcPoint/Vbs4
D09 | 斗工DS | 161 | 161kV | 1550 | 斗工～富喬線(1550) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D09_A1 | [12 empty] | 斗工DS.1550_AMP | 富喬線 AMP | LINE161 | AMP_CAL | C20R1394 | amp_cal | OPRD1: D09/161/1550/MW; OPRD2: D09/161/1550/MVAR; OPRD3: D09/0/CalcPoint/Vbs4
D09 | 斗工DS | 161 | 161kV | 1610 | 榴中～斗工一路(1610) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D09_A1 | [12 empty] | 斗工DS.1610_AMP | 榴中斗工一路 AMP | LINE161 | AMP_CAL | C20R1576 | amp_cal | OPRD1: D09/161/1610/MW; OPRD2: D09/161/1610/MVAR; OPRD3: D09/0/CalcPoint/Vbs4
D09 | 斗工DS | 161 | 161kV | 1620 | 榴中～斗工二路(1620) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D09_A1 | [12 empty] | 斗工DS.1620_AMP | 榴中斗工二路 AMP | LINE161 | AMP_CAL | C20R1576 | amp_cal | OPRD1: D09/161/1620/MW; OPRD2: D09/161/1620/MVAR; OPRD3: D09/0/CalcPoint/Vbs4
D09 | 斗工DS | 11 | 11kV | 1BBUS | #1BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D09_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D09/11/1BBUS/V
D09 | 斗工DS | 11 | 11kV | 2B1BUS | #2B1BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D09_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D09/11/2B1BUS/V
D09 | 斗工DS | 11 | 11kV | 2B2BUS | #2B2BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D09_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D09/11/2B2BUS/V
D09 | 斗工DS | 22 | 22kV | 1ABUS | #1ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D09_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D09/22/1ABUS/V
D09 | 斗工DS | 22 | 22kV | 2A1BUS | #2A1BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D09_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D09/22/2A1BUS/V
D09 | 斗工DS | 22 | 22kV | 2A2BUS | #2A2BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D09_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D09/22/2A2BUS/V
D09 | 斗工DS |  |  | 1DTR(A) | #1DTR(A) |  | TR_PERM | [9 empty] | B1/D09_A1 | [12 empty] | 斗工DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D09//1DTR(A)/SupLocal; OPRD2: D09//1DTR(A)/Tap Chan
D09 | 斗工DS |  |  | 1DTR(B) | #1DTR(B) |  | TR_PERM | [9 empty] | B1/D09_A1 | [12 empty] | 斗工DS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D09//1DTR(B)/SupLocal; OPRD2: D09//1DTR(B)/Tap Chan
D09 | 斗工DS |  |  | 2DTR(A) | #2DTR(A) |  | TR_PERM | [9 empty] | B1/D09_A1 | [12 empty] | 斗工DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D09//2DTR(A)/SupLocal; OPRD2: D09//2DTR(A)/Tap Chan
D09 | 斗工DS |  |  | 2DTR(B) | #2DTR(B) |  | TR_PERM | [9 empty] | B1/D09_A1 | [12 empty] | 斗工DS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D09//2DTR(B)/SupLocal; OPRD2: D09//2DTR(B)/Tap Chan
D09 | 斗工DS | 11 | 11kV | XU26 | 工六線(XU26) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D09/11/1BBUS/V; OPRD2: D09/11/XU26/I_R; OPRD3: D09/11/XU26/I_S; OPRD4: D09/11/XU26/I_T
D09 | 斗工DS | 11 | 11kV | XU27 | 工七線(XU27) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D09/11/1BBUS/V; OPRD2: D09/11/XU27/I_R; OPRD3: D09/11/XU27/I_S; OPRD4: D09/11/XU27/I_T
D09 | 斗工DS | 11 | 11kV | XU28 | 工八線(XU28) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D09/11/1BBUS/V; OPRD2: D09/11/XU28/I_R; OPRD3: D09/11/XU28/I_S; OPRD4: D09/11/XU28/I_T
D09 | 斗工DS | 11 | 11kV | XU29 | 工九線(XU29) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D09/11/1BBUS/V; OPRD2: D09/11/XU29/I_R; OPRD3: D09/11/XU29/I_S; OPRD4: D09/11/XU29/I_T
D09 | 斗工DS | 11 | 11kV | XU30 | 工十線(XU30) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D09/11/1BBUS/V; OPRD2: D09/11/XU30/I_R; OPRD3: D09/11/XU30/I_S; OPRD4: D09/11/XU30/I_T
D09 | 斗工DS | 11 | 11kV | XU36 | 工十六線(XU36) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D09/11/2B1BUS/V; OPRD2: D09/11/XU36/I_R; OPRD3: D09/11/XU36/I_S; OPRD4: D09/11/XU36/I_T
D09 | 斗工DS | 11 | 11kV | XU37 | 工十七線(XU37) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D09/11/2B1BUS/V; OPRD2: D09/11/XU37/I_R; OPRD3: D09/11/XU37/I_S; OPRD4: D09/11/XU37/I_T
D09 | 斗工DS | 11 | 11kV | XU38 | 工十八線(XU38) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D09/11/2B2BUS/V; OPRD2: D09/11/XU38/I_R; OPRD3: D09/11/XU38/I_S; OPRD4: D09/11/XU38/I_T
D09 | 斗工DS | 11 | 11kV | XU39 | 工十九線(XU39) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D09/11/2B2BUS/V; OPRD2: D09/11/XU39/I_R; OPRD3: D09/11/XU39/I_S; OPRD4: D09/11/XU39/I_T
D09 | 斗工DS | 11 | 11kV | XU40 | 工二十線(XU40) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D09/11/2B2BUS/V; OPRD2: D09/11/XU40/I_R; OPRD3: D09/11/XU40/I_S; OPRD4: D09/11/XU40/I_T
D09 | 斗工DS | 22 | 22kV | XU51 | 工五一線(XU51) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D09/22/1ABUS/V; OPRD2: D09/22/XU51/I_R; OPRD3: D09/22/XU51/I_S; OPRD4: D09/22/XU51/I_T
D09 | 斗工DS | 22 | 22kV | XU52 | 工五二線(XU52) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D09/22/1ABUS/V; OPRD2: D09/22/XU52/I_R; OPRD3: D09/22/XU52/I_S; OPRD4: D09/22/XU52/I_T
D09 | 斗工DS | 22 | 22kV | XU53 | 工五三線(XU53) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D09/22/1ABUS/V; OPRD2: D09/22/XU53/I_R; OPRD3: D09/22/XU53/I_S; OPRD4: D09/22/XU53/I_T
D09 | 斗工DS | 22 | 22kV | XU54 | 工五四線(XU54) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D09/22/1ABUS/V; OPRD2: D09/22/XU54/I_R; OPRD3: D09/22/XU54/I_S; OPRD4: D09/22/XU54/I_T
D09 | 斗工DS | 22 | 22kV | XU55 | 工五五線(XU55) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D09/22/1ABUS/V; OPRD2: D09/22/XU55/I_R; OPRD3: D09/22/XU55/I_S; OPRD4: D09/22/XU55/I_T
D09 | 斗工DS | 22 | 22kV | XU61 | 工六一線(XU61) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D09/22/2A1BUS/V; OPRD2: D09/22/XU61/I_R; OPRD3: D09/22/XU61/I_S; OPRD4: D09/22/XU61/I_T
D09 | 斗工DS | 22 | 22kV | XU62 | 工六二線(XU62) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D09/22/2A1BUS/V; OPRD2: D09/22/XU62/I_R; OPRD3: D09/22/XU62/I_S; OPRD4: D09/22/XU62/I_T
D09 | 斗工DS | 22 | 22kV | XU63 | 工六三線(XU63) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D09/22/2A1BUS/V; OPRD2: D09/22/XU63/I_R; OPRD3: D09/22/XU63/I_S; OPRD4: D09/22/XU63/I_T
D09 | 斗工DS | 22 | 22kV | XU64 | 工六四線(XU64) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D09/22/2A2BUS/V; OPRD2: D09/22/XU64/I_R; OPRD3: D09/22/XU64/I_S; OPRD4: D09/22/XU64/I_T
D09 | 斗工DS | 22 | 22kV | XU65 | 工六五線(XU65) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D09/22/2A2BUS/V; OPRD2: D09/22/XU65/I_R; OPRD3: D09/22/XU65/I_S; OPRD4: D09/22/XU65/I_T
D09 | 斗工DS | 11 | 11kV | XU26 | 工六線(XU26) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D09/11/XU26/kVA; OPRD2: D09/11/XU26/KVAR
D09 | 斗工DS | 11 | 11kV | XU27 | 工七線(XU27) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D09/11/XU27/kVA; OPRD2: D09/11/XU27/KVAR
D09 | 斗工DS | 11 | 11kV | XU28 | 工八線(XU28) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D09/11/XU28/kVA; OPRD2: D09/11/XU28/KVAR
D09 | 斗工DS | 11 | 11kV | XU29 | 工九線(XU29) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D09/11/XU29/kVA; OPRD2: D09/11/XU29/KVAR
D09 | 斗工DS | 11 | 11kV | XU30 | 工十線(XU30) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D09/11/XU30/kVA; OPRD2: D09/11/XU30/KVAR
D09 | 斗工DS | 11 | 11kV | XU36 | 工十六線(XU36) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D09/11/XU36/kVA; OPRD2: D09/11/XU36/KVAR
D09 | 斗工DS | 11 | 11kV | XU37 | 工十七線(XU37) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D09/11/XU37/kVA; OPRD2: D09/11/XU37/KVAR
D09 | 斗工DS | 11 | 11kV | XU38 | 工十八線(XU38) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D09/11/XU38/kVA; OPRD2: D09/11/XU38/KVAR
D09 | 斗工DS | 11 | 11kV | XU39 | 工十九線(XU39) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D09/11/XU39/kVA; OPRD2: D09/11/XU39/KVAR
D09 | 斗工DS | 11 | 11kV | XU40 | 工二十線(XU40) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D09/11/XU40/kVA; OPRD2: D09/11/XU40/KVAR
D09 | 斗工DS | 22 | 22kV | XU51 | 工五一線(XU51) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D09/22/XU51/kVA; OPRD2: D09/22/XU51/KVAR
D09 | 斗工DS | 22 | 22kV | XU52 | 工五二線(XU52) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D09/22/XU52/kVA; OPRD2: D09/22/XU52/KVAR
D09 | 斗工DS | 22 | 22kV | XU53 | 工五三線(XU53) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D09/22/XU53/kVA; OPRD2: D09/22/XU53/KVAR
D09 | 斗工DS | 22 | 22kV | XU54 | 工五四線(XU54) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D09/22/XU54/kVA; OPRD2: D09/22/XU54/KVAR
D09 | 斗工DS | 22 | 22kV | XU55 | 工五五線(XU55) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D09/22/XU55/kVA; OPRD2: D09/22/XU55/KVAR
D09 | 斗工DS | 22 | 22kV | XU61 | 工六一線(XU61) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D09/22/XU61/kVA; OPRD2: D09/22/XU61/KVAR
D09 | 斗工DS | 22 | 22kV | XU62 | 工六二線(XU62) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D09/22/XU62/kVA; OPRD2: D09/22/XU62/KVAR
D09 | 斗工DS | 22 | 22kV | XU63 | 工六三線(XU63) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D09/22/XU63/kVA; OPRD2: D09/22/XU63/KVAR
D09 | 斗工DS | 22 | 22kV | XU64 | 工六四線(XU64) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D09/22/XU64/kVA; OPRD2: D09/22/XU64/KVAR
D09 | 斗工DS | 22 | 22kV | XU65 | 工六五線(XU65) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D09_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D09/22/XU65/kVA; OPRD2: D09/22/XU65/KVAR
D09 | 斗工DS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D09_A1 | [12 empty] | 斗工DS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D09/11/220/CB; OPRD2: 6.9; OPRD3: 0
D09 | 斗工DS | 11 | 11kV | 240 | #4SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D09_A1 | [12 empty] | 斗工DS.240_SC_MVAR | 11KV#4SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D09/11/240/CB; OPRD2: 6.9; OPRD3: 0
D09 | 斗工DS | 22 | 22kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D09_A1 | [12 empty] | 斗工DS.210_SC_MVAR | 23KV#1SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D09/22/210/CB; OPRD2: 13.8; OPRD3: 0
D09 | 斗工DS | 22 | 22kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D09_A1 | [12 empty] | 斗工DS.230_SC_MVAR | 23KV#3SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D09/22/230/CB; OPRD2: 13.8; OPRD3: 0
D09 | 斗工DS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/D09_A1 | [12 empty] | 斗工DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_20 |  | com_alarm_34 | D09//1DTR/96B1 | D09//1DTR/51ZA | D09//1DTR/63Q | D09//1DTR/96B2 | D09//1DTR/96D | D09//1DTR/87A | D09//1DTR/96PA | D09//1DTR(A)/TRA | D09//2DTR/96PA | D09//2DTR/51ZA | D09//2DTR/96B2 | D09//2DTR/63Q | D09//2DTR/96B1 | D09//2DTR/87A | D09//2DTR/96D | D09//2DTR(A)/TRA | D09/11/320/GDA | D09/11/320/PHA | D09/11/340B1/GDA | D09/11/340B2/GDA | D09/161/1750/GDA | D09/161/1750/PHA | D09/161/1760/GDA | D09/161/1760/PHA | D09/161/1BUS/87A | D09/161/2BUS/87A | D09/22/310/PHA | D09/22/310/GDA | D09/22/330A1/GDA | D09/22/330A1/PHA | D09/22/330A2/PHA | D09/22/330A2/GDA | D09/22/340B1/PHA | D09/22/340B2/PHA
D09 | 斗工DS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/D09_A1 | [12 empty] | 斗工DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | STATION_FAULT_2 |  | com_alarm_2 | OPRD1: D09//1DTR(A)/TRF; OPRD2: D09//2DTR(A)/TRF
D09 | 斗工DS | 161 | 161kV | 1750_D1 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D09_D1 | [17 empty] | lamp2CC | OPRD1: D09/161/1750/CB
D09 | 斗工DS | 161 | 161kV | 1760_D1 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D09_D1 | [17 empty] | lamp2CC | OPRD1: D09/161/1760/CB
D09 | 斗工DS | 22 | 22kV | 310_D1 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D09_D1 | [17 empty] | lamp2CC | OPRD1: D09/22/310/CB
D09 | 斗工DS | 11 | 11kV | 320_D1 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D09_D1 | [17 empty] | lamp2CC | OPRD1: D09/11/320/CB
D09 | 斗工DS | 22 | 22kV | 330A1_D1 | #2DTR(A)(330A1) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D09_D1 | [17 empty] | lamp2CC | OPRD1: D09/22/330A1/CB
D09 | 斗工DS | 22 | 22kV | 330A2_D1 | #2DTR(A)(330A2) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D09_D1 | [17 empty] | lamp2CC | OPRD1: D09/22/330A2/CB
D09 | 斗工DS | 11 | 11kV | 340B1_D1 | #2DTR(B)(340B1) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D09_D1 | [17 empty] | lamp2CC | OPRD1: D09/11/340B1/CB
D09 | 斗工DS | 11 | 11kV | 340B2_D1 | #2DTR(B)(340B2) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D09_D1 | [17 empty] | lamp2CC | OPRD1: D09/11/340B2/CB
D09 | 斗工DS | 0 |  | RTU_D1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/D09_D1 | [17 empty] | lamp2CC | OPRD1: D09/0/RTU/RTU_R_L
D09 | 斗工DS | 0 |  | StaDev_D1 | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/D09_D1 | [17 empty] | lamp2CC | OPRD1: D09/0/StaDev/STUV
D09 | 斗工DS | 0 |  | StaDev_D1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D09_D1 | [17 empty] | lamp2CC | OPRD1: D09/0/StaDev/DCA
D09 | 斗工DS | 0 |  | StaDev_D1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D09_D1 | [17 empty] | lamp2CC | OPRD1: D09/0/StaDev/DCE

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D09 | 斗工DS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 斗工DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | D09/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工山線(1510) |  | I | [25 empty] | ADCS_N | [8 empty] | 斗工DS.1510_AMP | 鉅工山線 AMP | LINE161 | D09/161/1510/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C20R1576 | 1418.000000 | 1418.000000 | 1576.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工海線(1520) |  | I | [25 empty] | ADCS_N | [8 empty] | 斗工DS.1520_AMP | 鉅工海線 AMP | LINE161 | D09/161/1520/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C20R1576 | 1418.000000 | 1418.000000 | 1576.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D09 | 斗工DS | 161 | 161kV | 1530 | 嘉民斗工紅線(1530) |  | I | [25 empty] | ADCS_N | [8 empty] | 斗工DS.1530_AMP | 嘉民斗工紅線 AMP | LINE161 | D09/161/1530/I |  | AMP_CAL |  |  | 5 | CalcAIPoint | [21 empty] | C20R1576 | 1418.000000 | 1418.000000 | 1576.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D09 | 斗工DS | 161 | 161kV | 1540 | 雲林斗工線(1540) |  | I | [25 empty] | ADCS_N | [8 empty] | 斗工DS.1540_AMP | 雲林斗工線 AMP | LINE161 | D09/161/1540/I |  | AMP_CAL |  |  | 6 | CalcAIPoint | [21 empty] | C20R1576 | 1418.000000 | 1418.000000 | 1576.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D09 | 斗工DS | 161 | 161kV | 1550 | 富喬線(1550) |  | I | [25 empty] | ADCS_N | [8 empty] | 斗工DS.1550_AMP | 富喬線 AMP | LINE161 | D09/161/1550/I |  | AMP_CAL |  |  | 7 | CalcAIPoint | [21 empty] | C20R1394 | 1254.599976 | 1254.599976 | 1394.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D09 | 斗工DS | 0 |  |  |  |  | 工七線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工七線KVA | 11KV工七線KVA | FEEDER |  |  | KVA_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工七線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工七線KW | 11KV工七線KW | FEEDER |  |  | KW_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工九線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工九線KVA | 11KV工九線KVA | FEEDER |  |  | KVA_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工九線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工九線KW | 11KV工九線KW | FEEDER |  |  | KW_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工二十線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工二十線KVA | 11KV工二十線KVA | FEEDER |  |  | KVA_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工二十線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工二十線KW | 11KV工二十線KW | FEEDER |  |  | KW_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工八線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工八線KVA | 11KV工八線KVA | FEEDER |  |  | KVA_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工八線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工八線KW | 11KV工八線KW | FEEDER |  |  | KW_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工十七線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工十七線KVA | 11KV工十七線KVA | FEEDER |  |  | KVA_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工十七線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工十七線KW | 11KV工十七線KW | FEEDER |  |  | KW_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工十九線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工十九線KVA | 11KV工十九線KVA | FEEDER |  |  | KVA_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工十九線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工十九線KW | 11KV工十九線KW | FEEDER |  |  | KW_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工十八線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工十八線KVA | 11KV工十八線KVA | FEEDER |  |  | KVA_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工十八線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工十八線KW | 11KV工十八線KW | FEEDER |  |  | KW_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工十六線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工十六線KVA | 11KV工十六線KVA | FEEDER |  |  | KVA_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工十六線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工十六線KW | 11KV工十六線KW | FEEDER |  |  | KW_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工十線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工十線KVA | 11KV工十線KVA | FEEDER |  |  | KVA_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工十線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工十線KW | 11KV工十線KW | FEEDER |  |  | KW_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工六線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工六線KVA | 11KV工六線KVA | FEEDER |  |  | KVA_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工六線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工六線KW | 11KV工六線KW | FEEDER |  |  | KW_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工五一線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工五一線KVA | 23KV工五一線KVA | FEEDER |  |  | KVA_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工五一線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工五一線KW | 23KV工五一線KW | FEEDER |  |  | KW_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工五二線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工五二線KVA | 23KV工五二線KVA | FEEDER |  |  | KVA_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工五二線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工五二線KW | 23KV工五二線KW | FEEDER |  |  | KW_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工五三線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工五三線KVA | 23KV工五三線KVA | FEEDER |  |  | KVA_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工五三線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工五三線KW | 23KV工五三線KW | FEEDER |  |  | KW_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工五五線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工五五線KVA | 23KV工五五線KVA | FEEDER |  |  | KVA_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工五五線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工五五線KW | 23KV工五五線KW | FEEDER |  |  | KW_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工五四線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工五四線KVA | 23KV工五四線KVA | FEEDER |  |  | KVA_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工五四線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工五四線KW | 23KV工五四線KW | FEEDER |  |  | KW_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工六一線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工六一線KVA | 23KV工六一線KVA | FEEDER |  |  | KVA_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工六一線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工六一線KW | 23KV工六一線KW | FEEDER |  |  | KW_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工六二線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工六二線KVA | 23KV工六二線KVA | FEEDER |  |  | KVA_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工六二線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工六二線KW | 23KV工六二線KW | FEEDER |  |  | KW_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工六三線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工六三線KVA | 23KV工六三線KVA | FEEDER |  |  | KVA_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工六三線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工六三線KW | 23KV工六三線KW | FEEDER |  |  | KW_CAL |  |  | 43 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工六五線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工六五線KVA | 23KV工六五線KVA | FEEDER |  |  | KVA_CAL |  |  | 44 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工六五線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工六五線KW | 23KV工六五線KW | FEEDER |  |  | KW_CAL |  |  | 45 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工六四線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工六四線KVA | 23KV工六四線KVA | FEEDER |  |  | KVA_CAL |  |  | 46 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  |  |  |  | 工六四線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.工六四線KW | 23KV工六四線KW | FEEDER |  |  | KW_CAL |  |  | 47 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  | TRTOT | 斗工主變瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 斗工DS.TRTOT_MW | 斗工主變瞬時供電量 MW |  |  |  | MTR_PQ_CAL |  |  | 48 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  | TRTOT | 斗工主變瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 斗工DS.TRTOT_MVAR | 斗工主變瞬時供電量 MVAR |  |  |  | MTR_PQ_CAL |  |  | 49 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 斗工DS.#1DTR(A)_MVA | #1DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 50 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D09 | 斗工DS | 0 |  | 1DTR(A) | #1DTR(A) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 斗工DS.#1DTR(A)_LOAD | #1DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 51 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D09 | 斗工DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PF | [25 empty] | ADCS_N | [8 empty] | 斗工DS.#1DTR(A)_PF | #1DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 52 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D09 | 斗工DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 斗工DS.#1DTR(B)_MVA | #1DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 53 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D09 | 斗工DS | 0 |  | 1DTR(B) | #1DTR(B) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 斗工DS.#1DTR(B)_LOAD | #1DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 54 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D09 | 斗工DS | 0 |  | 1DTR(B) | #1DTR(B) |  | PF | [25 empty] | ADCS_N | [8 empty] | 斗工DS.#1DTR(B)_PF | #1DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 55 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D09 | 斗工DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 斗工DS.#2DTR(A)_MVA | #2DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 56 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D09 | 斗工DS | 0 |  | 2DTR(A) | #2DTR(A) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 斗工DS.#2DTR(A)_LOAD | #2DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 57 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D09 | 斗工DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PF | [25 empty] | ADCS_N | [8 empty] | 斗工DS.#2DTR(A)_PF | #2DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 58 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D09 | 斗工DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 斗工DS.#2DTR(B)_MVA | #2DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 59 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D09 | 斗工DS | 0 |  | 2DTR(B) | #2DTR(B) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 斗工DS.#2DTR(B)_LOAD | #2DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 60 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D09 | 斗工DS | 0 |  | 2DTR(B) | #2DTR(B) |  | PF | [25 empty] | ADCS_N | [8 empty] | 斗工DS.#2DTR(B)_PF | #2DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 61 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D09 | 斗工DS | 0 |  | 1DTR | #1DTR |  | MW | [25 empty] | ADCS_N | [8 empty] | 斗工DS.#1DTR_MW | #1DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 62 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  | 1DTR | #1DTR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 斗工DS.#1DTR_MVAR | #1DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 63 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  | 1DTR | #1DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 斗工DS.#1DTR_MVA | #1DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 64 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D09 | 斗工DS | 0 |  | 1DTR | #1DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 斗工DS.#1DTR_LOAD | #1DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 65 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D09 | 斗工DS | 0 |  | 2DTR | #2DTR |  | MW | [25 empty] | ADCS_N | [8 empty] | 斗工DS.#2DTR_MW | #2DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 66 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  | 2DTR | #2DTR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 斗工DS.#2DTR_MVAR | #2DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 67 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 0 |  | 2DTR | #2DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 斗工DS.#2DTR_MVA | #2DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 68 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D09 | 斗工DS | 0 |  | 2DTR | #2DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 斗工DS.#2DTR_LOAD | #2DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 69 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D09 | 斗工DS | 11 | 11kV | 220_SC | #2SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 斗工DS.220_SC_MVAR | 11KV#2SC MVAR | SC | D09/11/220/MVAR |  | SC_LBS_11 |  |  | 70 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 22 | 22kV | 210_SC | #1SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 斗工DS.210_SC_MVAR | 23KV#1SC MVAR | SC | D09/22/210/MVAR |  | SC_CAL_23 |  |  | 71 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 11 | 11kV | 240_SC | #4SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 斗工DS.240_SC_MVAR | 11KV#4SC MVAR | SC | D09/11/240/MVAR |  | SC_LBS_11 |  |  | 72 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 22 | 22kV | 230_SC | #3SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 斗工DS.230_SC_MVAR | 23KV#3SC MVAR | SC | D09/22/230/MVAR |  | SC_CAL_23 |  |  | 73 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 161 | 161kV | 1570 | 備用線(1570) |  | I | [25 empty] | ADCS_N | [8 empty] | 斗工DS.1570_AMP | 備用線 AMP | LINE161 |  |  | AMP_CAL |  |  | 74 | CalcAIPoint | [21 empty] | C20R1576 | 1418.000000 | 1418.000000 | 1576.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D09 | 斗工DS | 161 | 161kV | 1580 | 斗六斗工線(1580) |  | I | [25 empty] | ADCS_N | [8 empty] | 斗工DS.1580_AMP | 斗六斗工線 AMP | LINE161 |  |  | AMP_CAL |  |  | 75 | CalcAIPoint | [21 empty] | C20R1576 | 1418.000000 | 1418.000000 | 1576.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D09 | 斗工DS | 161 | 161kV | 1610 | 榴中斗工一路(1610) |  | I | [25 empty] | ADCS_N | [8 empty] | 斗工DS.1610_AMP | 榴中斗工一路 AMP | LINE161 | D09/161/1610/I |  | AMP_CAL |  |  | 76 | CalcAIPoint | [21 empty] | C20R1576 | 1418.000000 | 1418.000000 | 1576.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D09 | 斗工DS | 161 | 161kV | 1620 | 榴中斗工二路(1620) |  | I | [25 empty] | ADCS_N | [8 empty] | 斗工DS.1620_AMP | 榴中斗工二路 AMP | LINE161 | D09/161/1620/I |  | AMP_CAL |  |  | 77 | CalcAIPoint | [21 empty] | C20R1576 | 1418.000000 | 1418.000000 | 1576.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D09 | 斗工DS | 22 | 22kV | 2ABUS | #2ABUS |  | V | [25 empty] | ADCS_N | [8 empty] | 斗工DS.23KV#2ABUS_KV | 23KV #2ABUS BEST SOURCE | BUS |  |  | BEST_1W2CB |  |  | 78 | CalcAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D09 | 斗工DS | 11 | 11kV | 2BBUS | #2BBUS |  | V | [25 empty] | ADCS_N | [8 empty] | 斗工DS.11KV#2BBUS_KV | 11KV #2BBUS BEST SOURCE | BUS |  |  | BEST_1W2CB |  |  | 79 | CalcAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D09 | 斗工DS | 0 |  | 100_CB | 100(100_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.100_CB_1 | 100 CB (D1) | TIE |  |  | AD_LAMP_DD_1 |  |  | 80 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 200_CB | 200(200_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.200_CB_1 | 200 CB (D1) | TIE |  |  | AD_LAMP_DD_1 |  |  | 81 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 300_CB | 300(300_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.300_CB_1 | 300 CB (D1) | TIE |  |  | AD_LAMP_DD_1 |  |  | 82 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 400_CB | 400(400_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.400_CB_1 | 400 CB (D1) | TIE |  |  | AD_LAMP_DD_1 |  |  | 83 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 1750_CB | #1DTR(1750_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.1750_CB_1 | 1750(#1DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 84 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 310_CB | #1DTR(310_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.310_CB_1 | 310(#1DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 85 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 320_CB | #1DTR(320_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.320_CB_1 | 320(#1DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 86 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 1760_CB | #2DTR(1760_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.1760_CB_1 | 1760(#2DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 87 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | 11__CBA | 11/斷路器重故障點燈(11__CBA) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.11/23KV_CBA_1 | 11/23KV斷路器重故障點燈 (D1) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 88 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | 11__CBF | 11/斷路器輕故障(11__CBF) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.11/23KV_CBF_1 | 11/23KV斷路器輕故障 (D1) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 89 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | RTU_S_L | RTU |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.RTU_S/L_1 | RTU SUPY/LOCAL (D1) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 90 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D09 | 斗工DS | 0 |  | TEST_CB | TEST(TEST_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.TEST_CB_1 | TEST CB (D1) | OTHER |  |  | AD_LAMP_DD_1 |  |  | 91 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_N | [8 empty] | 斗工DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | D09/0/CalcPoint/SUBA |  | STATION_FAULT_20 |  |  | 92 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 變電所輕故障點燈 | 變電所輕故障點燈 |  | SUBF | [25 empty] | ADCS_N | [8 empty] | 斗工DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | D09/0/CalcPoint/SUBF |  | STATION_FAULT_2 |  |  | 93 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.變電所重故障_1 | 變電所重故障點燈 (D1) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 94 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.變電所輕故障_1 | 變電所輕故障點燈 (D1) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 95 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1510_AMP | 鉅工山線 | [27 empty] | ADCS_N | [8 empty] | 斗工DS.1510_AMP_A | 鉅工山線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 96 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D09 | 斗工DS | 161 | 161kV | 1520_AMP | 鉅工海線 | [27 empty] | ADCS_N | [8 empty] | 斗工DS.1520_AMP_A | 鉅工海線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 97 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D09 | 斗工DS | 161 | 161kV | 1530_AMP | 嘉民紅線 | [27 empty] | ADCS_N | [8 empty] | 斗工DS.1530_AMP_A | 嘉民紅線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 98 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D09 | 斗工DS | 161 | 161kV | 1540_AMP | 雲林斗工線 | [27 empty] | ADCS_N | [8 empty] | 斗工DS.1540_AMP_A | 雲林斗工線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 99 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D09 | 斗工DS | 161 | 161kV | 1550_AMP | 富喬線 | [27 empty] | ADCS_N | [8 empty] | 斗工DS.1550_AMP_A | 富喬線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 100 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D09 | 斗工DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PERM | [25 empty] | ADCS_N | [8 empty] | 斗工DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | D09//1DTR(A)/TR_PERM |  | DTR_PERM |  |  | 101 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D09 | 斗工DS | 0 |  | 1DTR(B) | #1DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 斗工DS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | D09//1DTR(B)/TR_PERM |  | DTR_PERM |  |  | 102 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D09 | 斗工DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PERM | [25 empty] | ADCS_N | [8 empty] | 斗工DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | D09//2DTR(A)/TR_PERM |  | DTR_PERM |  |  | 103 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D09 | 斗工DS | 0 |  | 2DTR(B) | #2DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 斗工DS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | D09//2DTR(B)/TR_PERM |  | DTR_PERM |  |  | 104 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D09 | 斗工DS | 0 |  | 1DTR_MVA | #1DTR | [27 empty] | ADCS_N | [8 empty] | 斗工DS.#1DTR_MVA_A | #1DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 105 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D09 | 斗工DS | 0 |  | 1DTR_MVA | #1DTR(A) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.#1DTR_MVA_1 | #1DTR(A) MVA 點燈 (D1) | MTR |  |  | MAP_SET |  |  | 106 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D09 | 斗工DS | 0 |  | 1DTR_MVA | #1DTR(B) | [27 empty] | DDCS1_1 | [8 empty] | 斗工DS.#1DTR_MVA_2 | #1DTR(B) MVA 點燈 (D1) | MTR |  |  | MAP_SET |  |  | 107 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
D09 | 斗工DS | 0 |  | 2DTR_MVA | #2DTR | [27 empty] | ADCS_N | [8 empty] | 斗工DS.#2DTR_MVA_A | #2DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 108 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D09 | 斗工DS | 0 |  | 2DTR_MVA | #2DTR(A) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.#2DTR_MVA_1 | #2DTR(A) MVA 點燈 (D1) | MTR |  |  | MAP_SET |  |  | 109 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D09 | 斗工DS | 0 |  | 2DTR_MVA | #2DTR(B) | [27 empty] | DDCS1_1 | [8 empty] | 斗工DS.#2DTR_MVA_2 | #2DTR(B) MVA 點燈 (D1) | MTR |  |  | MAP_SET |  |  | 110 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
D09 | 斗工DS | 11 | 11kV | 220_CB | #2SC(220_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.220_CB_1 | 220(11KV #2SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 111 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | 210_CB | #1SC(210_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.210_CB_1 | 210(23KV #1SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 112 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 330A2_CB | #2DTR(330A2_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.330A2_CB_1 | 330A2(#2DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 113 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 330A1_CB | #2DTR(330A1_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.330A1_CB_1 | 330A1(#2DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 114 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 340B1_CB | #2DTR(340B1_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.340B1_CB_1 | 340B1(#2DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 115 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 340B2_CB | #2DTR(340B2_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.340B2_CB_1 | 340B2(#2DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 116 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | 240_CB | #4SC(240_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.240_CB_1 | 240(11KV #4SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 117 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | 230_CB | #3SC(230_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗工DS.230_CB_1 | 230(23KV #3SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 118 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_N | [8 empty] | 斗工DS.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_DS |  |  | 119 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1570_AMP | 備用線 | [27 empty] | ADCS_N | [8 empty] | 斗工DS.1570_AMP_A | 備用線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 120 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D09 | 斗工DS | 161 | 161kV | 1580_AMP | 斗六斗工線 | [27 empty] | ADCS_N | [8 empty] | 斗工DS.1580_AMP_A | 斗六斗工線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 121 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D09 | 斗工DS | 161 | 161kV | 1610_AMP | 榴中斗工一路 | [27 empty] | ADCS_N | [8 empty] | 斗工DS.1610_AMP_A | 榴中斗工一路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 122 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D09 | 斗工DS | 161 | 161kV | 1620_AMP | 榴中斗工二路 | [27 empty] | ADCS_N | [8 empty] | 斗工DS.1620_AMP_A | 榴中斗工二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 123 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D09 | 斗工DS | 0 |  | 1ABUS | #1ABUS |  | 23KV#1ABUSC | [25 empty] | CDCS | [8 empty] | 斗工DS.23KV#1ABUSC | #1ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 124 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D09 | 斗工DS | 0 |  | 1BBUS | #1BBUS |  | 11KV#1BBUSC | [25 empty] | CDCS | [8 empty] | 斗工DS.11KV#1BBUSC | #1BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 125 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D09 | 斗工DS | 0 |  | 2A1BUS | #2A1BUS |  | 23KV#2A1BUSC | [25 empty] | CDCS | [8 empty] | 斗工DS.23KV#2A1BUSC | #2A1BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 126 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D09 | 斗工DS | 0 |  | 2A2BUS | #2A2BUS |  | 23KV#2A2BUSC | [25 empty] | CDCS | [8 empty] | 斗工DS.23KV#2A2BUSC | #2A2BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 127 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D09 | 斗工DS | 0 |  | 2B1BUS | #2B1BUS |  | 11KV#2B1BUSC | [25 empty] | CDCS | [8 empty] | 斗工DS.11KV#2B1BUSC | #2B1BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 128 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D09 | 斗工DS | 0 |  | 2B2BUS | #2B2BUS |  | 11KV#2B2BUSC | [25 empty] | CDCS | [8 empty] | 斗工DS.11KV#2B2BUSC | #2B2BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 129 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D09 | 斗工DS | 0 |  | TAP_OVER | TAP |  | SET | [25 empty] | ADCS_N | [8 empty] | 斗工DS.TAP_OVER_SET | TAP OVER HI/LO ALARM | MTR |  |  | 5000_CB_T4 |  |  | 130 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D09 | 斗工DS | 0 |  | BUS_OVER | BUS |  | SET | [25 empty] | ADCS_N | [8 empty] | 斗工DS.BUS_OVER_SET | BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B6 |  |  | 131 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D09 | 斗工DS | 0 |  | 5000 | 虛擬5000 |  | CB動作 | [25 empty] | ADCS_N | [8 empty] | 斗工DS.5000_CB動作 | 虛擬5000 CB動作,請查明原因處理 | MTR |  |  | 5000_CB_M |  |  | 132 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 注意OLTC | 注意OLTC |  | BUS電壓異常 | [25 empty] | ADCS_N | [8 empty] | 斗工DS.BUS電壓異常 | 注意OLTC Tap位置,並將RPDC閉鎖 | OTHER |  |  | STATION_FAULT_1 |  |  | 133 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | D09/0/RTU/ADCH1 |  |  |  | CDC | 134 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | D09/0/RTU/ADCH2 |  |  |  | CDC | 135 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | D09/0/RTU/ADCH3 |  |  |  | CDC | 136 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 0 |  | AI | AI |  | ADCH4 | [17 empty] | 2-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | D09/0/RTU/ADCH4 |  |  |  | CDC | 137 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | D09/0/RTU/ADCL1 |  |  |  | CDC | 138 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | D09/0/RTU/ADCL2 |  |  |  | CDC | 139 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | D09/0/RTU/ADCL3 |  |  |  | CDC | 140 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 0 |  | AI | AI |  | ADCL4 | [17 empty] | 2-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | D09/0/RTU/ADCL4 |  |  |  | CDC | 141 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | D09/161/1BUS/V |  |  |  | CDC | 142 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D09 | 斗工DS | 161 | 161kV | 2BUS | #2BUS |  | V | [17 empty] | 1-83 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | D09/161/2BUS/V |  |  |  | CDC | 143 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工山線(1510) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.1510_MW | 鉅工山線 MW | LINE161 | D09/161/1510/MW |  |  |  | CDC | 144 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工山線(1510) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.1510_MVAR | 鉅工山線 MVAR | LINE161 | D09/161/1510/MVAR |  |  |  | CDC | 145 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1510LPD | 鉅工山線(1510) |  | V | [17 empty] | 2-F6 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.1510LPD_KV | 鉅工山線(1510) LPD KV | LINE161 | D09/161/1510/V |  |  |  | CDC | 146 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工海線(1520) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.1520_MW | 鉅工海線 MW | LINE161 | D09/161/1520/MW |  |  |  | CDC | 147 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工海線(1520) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.1520_MVAR | 鉅工海線 MVAR | LINE161 | D09/161/1520/MVAR |  |  |  | CDC | 148 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1520LPD | 鉅工海線(1520) |  | V | [17 empty] | 2-F7 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.1520LPD_KV | 鉅工海線(1520) LPD KV | LINE161 | D09/161/1520/V |  |  |  | CDC | 149 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
D09 | 斗工DS | 161 | 161kV | 1530 | 嘉民斗工紅線(1530) |  | MW | [17 empty] | 1-8A | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.1530_MW | 嘉民斗工紅線 MW | LINE161 | D09/161/1530/MW |  |  |  | CDC | 150 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1530 | 嘉民斗工紅線(1530) |  | MVAR | [17 empty] | 1-8B | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.1530_MVAR | 嘉民斗工紅線 MVAR | LINE161 | D09/161/1530/MVAR |  |  |  | CDC | 151 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1530LPD | 嘉民斗工紅線(1530) |  | V | [17 empty] | 2-F8 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.1530LPD_KV | 嘉民斗工紅線(1530) LPD KV | LINE161 | D09/161/1530/V |  |  |  | CDC | 152 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
D09 | 斗工DS | 161 | 161kV | 1540 | 雲林斗工線(1540) |  | MW | [17 empty] | 1-88 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.1540_MW | 雲林斗工線 MW | LINE161 | D09/161/1540/MW |  |  |  | CDC | 153 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1540 | 雲林斗工線(1540) |  | MVAR | [17 empty] | 1-89 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.1540_MVAR | 雲林斗工線 MVAR | LINE161 | D09/161/1540/MVAR |  |  |  | CDC | 154 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1540LPD | 雲林斗工線(1540) |  | V | [17 empty] | 2-F9 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.1540LPD_KV | 雲林斗工線(1540) LPD KV | LINE161 | D09/161/1540/V |  |  |  | CDC | 155 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
D09 | 斗工DS | 161 | 161kV | 1550 | 富喬線(1550) |  | MW | [17 empty] | 1-8C | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.1550_MW | 富喬線 MW | LINE161 | D09/161/1550/MW |  |  |  | CDC | 156 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1550 | 富喬線(1550) |  | MVAR | [17 empty] | 1-8D | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.1550_MVAR | 富喬線 MVAR | LINE161 | D09/161/1550/MVAR |  |  |  | CDC | 157 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工七線 | 工七線 |  | 工七線KVAR | [17 empty] | 1-D6 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工七線KVAR | 11KV工七線 KVAR | FEEDER | D09/11/XU27/KVAR |  |  |  | CDC | 158 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工七線 | 工七線 |  | 工七線A1 | [17 empty] | 1-D7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工七線A1 | 11KV工七線 R相AMP | FEEDER | D09/11/XU27/I_R |  |  |  | CDC | 159 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工七線 | 工七線 |  | 工七線A2 | [17 empty] | 1-D8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工七線A2 | 11KV工七線 S相AMP | FEEDER | D09/11/XU27/I_S |  |  |  | CDC | 160 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工七線 | 工七線 |  | 工七線A3 | [17 empty] | 1-D9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工七線A3 | 11KV工七線 T相AMP | FEEDER | D09/11/XU27/I_T |  |  |  | CDC | 161 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工七線 | 工七線 |  | 工七線A0 | [17 empty] | 1-DA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工七線A0 | 11KV工七線 N相AMP | FEEDER | D09/11/XU27/I_N |  |  |  | CDC | 162 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工九線 | 工九線 |  | 工九線KVAR | [17 empty] | 1-E0 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工九線KVAR | 11KV工九線 KVAR | FEEDER | D09/11/XU29/KVAR |  |  |  | CDC | 163 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工九線 | 工九線 |  | 工九線A1 | [17 empty] | 1-E1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工九線A1 | 11KV工九線 R相AMP | FEEDER | D09/11/XU29/I_R |  |  |  | CDC | 164 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工九線 | 工九線 |  | 工九線A2 | [17 empty] | 1-E2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工九線A2 | 11KV工九線 S相AMP | FEEDER | D09/11/XU29/I_S |  |  |  | CDC | 165 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工九線 | 工九線 |  | 工九線A3 | [17 empty] | 1-E3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工九線A3 | 11KV工九線 T相AMP | FEEDER | D09/11/XU29/I_T |  |  |  | CDC | 166 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工九線 | 工九線 |  | 工九線A0 | [17 empty] | 1-E4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工九線A0 | 11KV工九線 N相AMP | FEEDER | D09/11/XU29/I_N |  |  |  | CDC | 167 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工二十線 | 工二十線 |  | 工二十線KVAR | [17 empty] | 2-AC | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工二十線KVAR | 11KV工二十線 KVAR | FEEDER | D09/11/XU40/KVAR |  |  |  | CDC | 168 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工二十線 | 工二十線 |  | 工二十線A1 | [17 empty] | 2-AD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工二十線A1 | 11KV工二十線 R相AMP | FEEDER | D09/11/XU40/I_R |  |  |  | CDC | 169 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工二十線 | 工二十線 |  | 工二十線A2 | [17 empty] | 2-AE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工二十線A2 | 11KV工二十線 S相AMP | FEEDER | D09/11/XU40/I_S |  |  |  | CDC | 170 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工二十線 | 工二十線 |  | 工二十線A3 | [17 empty] | 2-AF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工二十線A3 | 11KV工二十線 T相AMP | FEEDER | D09/11/XU40/I_T |  |  |  | CDC | 171 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工二十線 | 工二十線 |  | 工二十線A0 | [17 empty] | 2-B0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工二十線A0 | 11KV工二十線 N相AMP | FEEDER | D09/11/XU40/I_N |  |  |  | CDC | 172 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工八線 | 工八線 |  | 工八線KVAR | [17 empty] | 1-DB | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工八線KVAR | 11KV工八線 KVAR | FEEDER | D09/11/XU28/KVAR |  |  |  | CDC | 173 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工八線 | 工八線 |  | 工八線A1 | [17 empty] | 1-DC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工八線A1 | 11KV工八線 R相AMP | FEEDER | D09/11/XU28/I_R |  |  |  | CDC | 174 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工八線 | 工八線 |  | 工八線A2 | [17 empty] | 1-DD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工八線A2 | 11KV工八線 S相AMP | FEEDER | D09/11/XU28/I_S |  |  |  | CDC | 175 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工八線 | 工八線 |  | 工八線A3 | [17 empty] | 1-DE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工八線A3 | 11KV工八線 T相AMP | FEEDER | D09/11/XU28/I_T |  |  |  | CDC | 176 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工八線 | 工八線 |  | 工八線A0 | [17 empty] | 1-DF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工八線A0 | 11KV工八線 N相AMP | FEEDER | D09/11/XU28/I_N |  |  |  | CDC | 177 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工十七線 | 工十七線 |  | 工十七線KVAR | [17 empty] | 2-9D | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工十七線KVAR | 11KV工十七線 KVAR | FEEDER | D09/11/XU37/KVAR |  |  |  | CDC | 178 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工十七線 | 工十七線 |  | 工十七線A1 | [17 empty] | 2-9E | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工十七線A1 | 11KV工十七線 R相AMP | FEEDER | D09/11/XU37/I_R |  |  |  | CDC | 179 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工十七線 | 工十七線 |  | 工十七線A2 | [17 empty] | 2-9F | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工十七線A2 | 11KV工十七線 S相AMP | FEEDER | D09/11/XU37/I_S |  |  |  | CDC | 180 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工十七線 | 工十七線 |  | 工十七線A3 | [17 empty] | 2-A0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工十七線A3 | 11KV工十七線 T相AMP | FEEDER | D09/11/XU37/I_T |  |  |  | CDC | 181 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工十七線 | 工十七線 |  | 工十七線A0 | [17 empty] | 2-A1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工十七線A0 | 11KV工十七線 N相AMP | FEEDER | D09/11/XU37/I_N |  |  |  | CDC | 182 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工十九線 | 工十九線 |  | 工十九線KVAR | [17 empty] | 2-A7 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工十九線KVAR | 11KV工十九線 KVAR | FEEDER | D09/11/XU39/KVAR |  |  |  | CDC | 183 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工十九線 | 工十九線 |  | 工十九線A1 | [17 empty] | 2-A8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工十九線A1 | 11KV工十九線 R相AMP | FEEDER | D09/11/XU39/I_R |  |  |  | CDC | 184 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工十九線 | 工十九線 |  | 工十九線A2 | [17 empty] | 2-A9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工十九線A2 | 11KV工十九線 S相AMP | FEEDER | D09/11/XU39/I_S |  |  |  | CDC | 185 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工十九線 | 工十九線 |  | 工十九線A3 | [17 empty] | 2-AA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工十九線A3 | 11KV工十九線 T相AMP | FEEDER | D09/11/XU39/I_T |  |  |  | CDC | 186 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工十九線 | 工十九線 |  | 工十九線A0 | [17 empty] | 2-AB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工十九線A0 | 11KV工十九線 N相AMP | FEEDER | D09/11/XU39/I_N |  |  |  | CDC | 187 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工十八線 | 工十八線 |  | 工十八線KVAR | [17 empty] | 2-A2 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工十八線KVAR | 11KV工十八線 KVAR | FEEDER | D09/11/XU38/KVAR |  |  |  | CDC | 188 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工十八線 | 工十八線 |  | 工十八線A1 | [17 empty] | 2-A3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工十八線A1 | 11KV工十八線 R相AMP | FEEDER | D09/11/XU38/I_R |  |  |  | CDC | 189 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工十八線 | 工十八線 |  | 工十八線A2 | [17 empty] | 2-A4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工十八線A2 | 11KV工十八線 S相AMP | FEEDER | D09/11/XU38/I_S |  |  |  | CDC | 190 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工十八線 | 工十八線 |  | 工十八線A3 | [17 empty] | 2-A5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工十八線A3 | 11KV工十八線 T相AMP | FEEDER | D09/11/XU38/I_T |  |  |  | CDC | 191 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工十八線 | 工十八線 |  | 工十八線A0 | [17 empty] | 2-A6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工十八線A0 | 11KV工十八線 N相AMP | FEEDER | D09/11/XU38/I_N |  |  |  | CDC | 192 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工十六線 | 工十六線 |  | 工十六線KVAR | [17 empty] | 2-98 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工十六線KVAR | 11KV工十六線 KVAR | FEEDER | D09/11/XU36/KVAR |  |  |  | CDC | 193 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工十六線 | 工十六線 |  | 工十六線A1 | [17 empty] | 2-99 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工十六線A1 | 11KV工十六線 R相AMP | FEEDER | D09/11/XU36/I_R |  |  |  | CDC | 194 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工十六線 | 工十六線 |  | 工十六線A2 | [17 empty] | 2-9A | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工十六線A2 | 11KV工十六線 S相AMP | FEEDER | D09/11/XU36/I_S |  |  |  | CDC | 195 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工十六線 | 工十六線 |  | 工十六線A3 | [17 empty] | 2-9B | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工十六線A3 | 11KV工十六線 T相AMP | FEEDER | D09/11/XU36/I_T |  |  |  | CDC | 196 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工十六線 | 工十六線 |  | 工十六線A0 | [17 empty] | 2-9C | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工十六線A0 | 11KV工十六線 N相AMP | FEEDER | D09/11/XU36/I_N |  |  |  | CDC | 197 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工十線 | 工十線 |  | 工十線KVAR | [17 empty] | 1-E5 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工十線KVAR | 11KV工十線 KVAR | FEEDER | D09/11/XU30/KVAR |  |  |  | CDC | 198 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工十線 | 工十線 |  | 工十線A1 | [17 empty] | 1-E6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工十線A1 | 11KV工十線 R相AMP | FEEDER | D09/11/XU30/I_R |  |  |  | CDC | 199 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工十線 | 工十線 |  | 工十線A2 | [17 empty] | 1-E7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工十線A2 | 11KV工十線 S相AMP | FEEDER | D09/11/XU30/I_S |  |  |  | CDC | 200 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工十線 | 工十線 |  | 工十線A3 | [17 empty] | 1-E8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工十線A3 | 11KV工十線 T相AMP | FEEDER | D09/11/XU30/I_T |  |  |  | CDC | 201 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工十線 | 工十線 |  | 工十線A0 | [17 empty] | 1-E9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工十線A0 | 11KV工十線 N相AMP | FEEDER | D09/11/XU30/I_N |  |  |  | CDC | 202 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工六線 | 工六線 |  | 工六線KVAR | [17 empty] | 1-D1 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工六線KVAR | 11KV工六線 KVAR | FEEDER | D09/11/XU26/KVAR |  |  |  | CDC | 203 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工六線 | 工六線 |  | 工六線A1 | [17 empty] | 1-D2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工六線A1 | 11KV工六線 R相AMP | FEEDER | D09/11/XU26/I_R |  |  |  | CDC | 204 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工六線 | 工六線 |  | 工六線A2 | [17 empty] | 1-D3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工六線A2 | 11KV工六線 S相AMP | FEEDER | D09/11/XU26/I_S |  |  |  | CDC | 205 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工六線 | 工六線 |  | 工六線A3 | [17 empty] | 1-D4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工六線A3 | 11KV工六線 T相AMP | FEEDER | D09/11/XU26/I_T |  |  |  | CDC | 206 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 工六線 | 工六線 |  | 工六線A0 | [17 empty] | 1-D5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工六線A0 | 11KV工六線 N相AMP | FEEDER | D09/11/XU26/I_N |  |  |  | CDC | 207 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工五一線 | 工五一線 |  | 工五一線KVAR | [17 empty] | 1-AD | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工五一線KVAR | 23KV工五一線 KVAR | FEEDER | D09/22/XU51/KVAR |  |  |  | CDC | 208 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工五一線 | 工五一線 |  | 工五一線A1 | [17 empty] | 1-AE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工五一線A1 | 23KV工五一線 R相AMP | FEEDER | D09/22/XU51/I_R |  |  |  | CDC | 209 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工五一線 | 工五一線 |  | 工五一線A2 | [17 empty] | 1-AF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工五一線A2 | 23KV工五一線 S相AMP | FEEDER | D09/22/XU51/I_S |  |  |  | CDC | 210 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工五一線 | 工五一線 |  | 工五一線A3 | [17 empty] | 1-B0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工五一線A3 | 23KV工五一線 T相AMP | FEEDER | D09/22/XU51/I_T |  |  |  | CDC | 211 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工五一線 | 工五一線 |  | 工五一線A0 | [17 empty] | 1-B1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工五一線A0 | 23KV工五一線 N相AMP | FEEDER | D09/22/XU51/I_N |  |  |  | CDC | 212 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工五二線 | 工五二線 |  | 工五二線KVAR | [17 empty] | 1-B2 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工五二線KVAR | 23KV工五二線 KVAR | FEEDER | D09/22/XU52/KVAR |  |  |  | CDC | 213 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工五二線 | 工五二線 |  | 工五二線A1 | [17 empty] | 1-B3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工五二線A1 | 23KV工五二線 R相AMP | FEEDER | D09/22/XU52/I_R |  |  |  | CDC | 214 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工五二線 | 工五二線 |  | 工五二線A2 | [17 empty] | 1-B4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工五二線A2 | 23KV工五二線 S相AMP | FEEDER | D09/22/XU52/I_S |  |  |  | CDC | 215 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工五二線 | 工五二線 |  | 工五二線A3 | [17 empty] | 1-B5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工五二線A3 | 23KV工五二線 T相AMP | FEEDER | D09/22/XU52/I_T |  |  |  | CDC | 216 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工五二線 | 工五二線 |  | 工五二線A0 | [17 empty] | 1-B6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工五二線A0 | 23KV工五二線 N相AMP | FEEDER | D09/22/XU52/I_N |  |  |  | CDC | 217 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工五三線 | 工五三線 |  | 工五三線KVAR | [17 empty] | 1-B7 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工五三線KVAR | 23KV工五三線 KVAR | FEEDER | D09/22/XU53/KVAR |  |  |  | CDC | 218 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工五三線 | 工五三線 |  | 工五三線A1 | [17 empty] | 1-B8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工五三線A1 | 23KV工五三線 R相AMP | FEEDER | D09/22/XU53/I_R |  |  |  | CDC | 219 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工五三線 | 工五三線 |  | 工五三線A2 | [17 empty] | 1-B9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工五三線A2 | 23KV工五三線 S相AMP | FEEDER | D09/22/XU53/I_S |  |  |  | CDC | 220 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工五三線 | 工五三線 |  | 工五三線A3 | [17 empty] | 1-BA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工五三線A3 | 23KV工五三線 T相AMP | FEEDER | D09/22/XU53/I_T |  |  |  | CDC | 221 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工五三線 | 工五三線 |  | 工五三線A0 | [17 empty] | 1-BB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工五三線A0 | 23KV工五三線 N相AMP | FEEDER | D09/22/XU53/I_N |  |  |  | CDC | 222 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工五五線 | 工五五線 |  | 工五五線KVAR | [17 empty] | 1-C3 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工五五線KVAR | 23KV工五五線 KVAR | FEEDER | D09/22/XU55/KVAR |  |  |  | CDC | 223 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工五五線 | 工五五線 |  | 工五五線A1 | [17 empty] | 1-C4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工五五線A1 | 23KV工五五線 R相AMP | FEEDER | D09/22/XU55/I_R |  |  |  | CDC | 224 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工五五線 | 工五五線 |  | 工五五線A2 | [17 empty] | 1-C5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工五五線A2 | 23KV工五五線 S相AMP | FEEDER | D09/22/XU55/I_S |  |  |  | CDC | 225 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工五五線 | 工五五線 |  | 工五五線A3 | [17 empty] | 1-C6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工五五線A3 | 23KV工五五線 T相AMP | FEEDER | D09/22/XU55/I_T |  |  |  | CDC | 226 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工五五線 | 工五五線 |  | 工五五線A0 | [17 empty] | 1-C7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工五五線A0 | 23KV工五五線 N相AMP | FEEDER | D09/22/XU55/I_N |  |  |  | CDC | 227 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工五四線 | 工五四線 |  | 工五四線KVAR | [17 empty] | 1-BC | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工五四線KVAR | 23KV工五四線 KVAR | FEEDER | D09/22/XU54/KVAR |  |  |  | CDC | 228 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工五四線 | 工五四線 |  | 工五四線A1 | [17 empty] | 1-BD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工五四線A1 | 23KV工五四線 R相AMP | FEEDER | D09/22/XU54/I_R |  |  |  | CDC | 229 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工五四線 | 工五四線 |  | 工五四線A2 | [17 empty] | 1-BE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工五四線A2 | 23KV工五四線 S相AMP | FEEDER | D09/22/XU54/I_S |  |  |  | CDC | 230 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工五四線 | 工五四線 |  | 工五四線A3 | [17 empty] | 1-BF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工五四線A3 | 23KV工五四線 T相AMP | FEEDER | D09/22/XU54/I_T |  |  |  | CDC | 231 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工五四線 | 工五四線 |  | 工五四線A0 | [17 empty] | 1-C2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工五四線A0 | 23KV工五四線 N相AMP | FEEDER | D09/22/XU54/I_N |  |  |  | CDC | 232 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工六一線 | 工六一線 |  | 工六一線KVAR | [17 empty] | 1-F3 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工六一線KVAR | 23KV工六一線 KVAR | FEEDER | D09/22/XU61/KVAR |  |  |  | CDC | 233 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工六一線 | 工六一線 |  | 工六一線A1 | [17 empty] | 1-F4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工六一線A1 | 23KV工六一線 R相AMP | FEEDER | D09/22/XU61/I_R |  |  |  | CDC | 234 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工六一線 | 工六一線 |  | 工六一線A2 | [17 empty] | 1-F5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工六一線A2 | 23KV工六一線 S相AMP | FEEDER | D09/22/XU61/I_S |  |  |  | CDC | 235 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工六一線 | 工六一線 |  | 工六一線A3 | [17 empty] | 1-F6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工六一線A3 | 23KV工六一線 T相AMP | FEEDER | D09/22/XU61/I_T |  |  |  | CDC | 236 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工六一線 | 工六一線 |  | 工六一線A0 | [17 empty] | 1-F7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工六一線A0 | 23KV工六一線 N相AMP | FEEDER | D09/22/XU61/I_N |  |  |  | CDC | 237 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工六二線 | 工六二線 |  | 工六二線KVAR | [17 empty] | 1-F8 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工六二線KVAR | 23KV工六二線 KVAR | FEEDER | D09/22/XU62/KVAR |  |  |  | CDC | 238 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工六二線 | 工六二線 |  | 工六二線A1 | [17 empty] | 1-F9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工六二線A1 | 23KV工六二線 R相AMP | FEEDER | D09/22/XU62/I_R |  |  |  | CDC | 239 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工六二線 | 工六二線 |  | 工六二線A2 | [17 empty] | 1-FA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工六二線A2 | 23KV工六二線 S相AMP | FEEDER | D09/22/XU62/I_S |  |  |  | CDC | 240 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工六二線 | 工六二線 |  | 工六二線A3 | [17 empty] | 1-FB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工六二線A3 | 23KV工六二線 T相AMP | FEEDER | D09/22/XU62/I_T |  |  |  | CDC | 241 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工六二線 | 工六二線 |  | 工六二線A0 | [17 empty] | 1-FC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工六二線A0 | 23KV工六二線 N相AMP | FEEDER | D09/22/XU62/I_N |  |  |  | CDC | 242 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工六三線 | 工六三線 |  | 工六三線KVAR | [17 empty] | 1-FD | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工六三線KVAR | 23KV工六三線 KVAR | FEEDER | D09/22/XU63/KVAR |  |  |  | CDC | 243 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工六三線 | 工六三線 |  | 工六三線A1 | [17 empty] | 1-FE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工六三線A1 | 23KV工六三線 R相AMP | FEEDER | D09/22/XU63/I_R |  |  |  | CDC | 244 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工六三線 | 工六三線 |  | 工六三線A2 | [17 empty] | 1-FF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工六三線A2 | 23KV工六三線 S相AMP | FEEDER | D09/22/XU63/I_S |  |  |  | CDC | 245 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工六三線 | 工六三線 |  | 工六三線A3 | [17 empty] | 2-82 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工六三線A3 | 23KV工六三線 T相AMP | FEEDER | D09/22/XU63/I_T |  |  |  | CDC | 246 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工六三線 | 工六三線 |  | 工六三線A0 | [17 empty] | 2-83 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工六三線A0 | 23KV工六三線 N相AMP | FEEDER | D09/22/XU63/I_N |  |  |  | CDC | 247 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工六五線 | 工六五線 |  | 工六五線KVAR | [17 empty] | 2-89 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工六五線KVAR | 23KV工六五線 KVAR | FEEDER | D09/22/XU65/KVAR |  |  |  | CDC | 248 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工六五線 | 工六五線 |  | 工六五線A1 | [17 empty] | 2-8A | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工六五線A1 | 23KV工六五線 R相AMP | FEEDER | D09/22/XU65/I_R |  |  |  | CDC | 249 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工六五線 | 工六五線 |  | 工六五線A2 | [17 empty] | 2-8B | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工六五線A2 | 23KV工六五線 S相AMP | FEEDER | D09/22/XU65/I_S |  |  |  | CDC | 250 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工六五線 | 工六五線 |  | 工六五線A3 | [17 empty] | 2-8C | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工六五線A3 | 23KV工六五線 T相AMP | FEEDER | D09/22/XU65/I_T |  |  |  | CDC | 251 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工六五線 | 工六五線 |  | 工六五線A0 | [17 empty] | 2-8D | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工六五線A0 | 23KV工六五線 N相AMP | FEEDER | D09/22/XU65/I_N |  |  |  | CDC | 252 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工六四線 | 工六四線 |  | 工六四線KVAR | [17 empty] | 2-84 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工六四線KVAR | 23KV工六四線 KVAR | FEEDER | D09/22/XU64/KVAR |  |  |  | CDC | 253 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工六四線 | 工六四線 |  | 工六四線A1 | [17 empty] | 2-85 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工六四線A1 | 23KV工六四線 R相AMP | FEEDER | D09/22/XU64/I_R |  |  |  | CDC | 254 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工六四線 | 工六四線 |  | 工六四線A2 | [17 empty] | 2-86 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工六四線A2 | 23KV工六四線 S相AMP | FEEDER | D09/22/XU64/I_S |  |  |  | CDC | 255 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工六四線 | 工六四線 |  | 工六四線A3 | [17 empty] | 2-87 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工六四線A3 | 23KV工六四線 T相AMP | FEEDER | D09/22/XU64/I_T |  |  |  | CDC | 256 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | 工六四線 | 工六四線 |  | 工六四線A0 | [17 empty] | 2-88 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗工DS.工六四線A0 | 23KV工六四線 N相AMP | FEEDER | D09/22/XU64/I_N |  |  |  | CDC | 257 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 0 |  | 1500TIE | 1500TIE |  | I | [17 empty] | 1-9A | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.1500TIE_AMP | 1500TIE AMP | TIE | D09/161/1500/I_R |  |  |  | CDC | 258 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | _400 | 400 |  | I_R | [17 empty] | 2-B3 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.11KV_400_A1 | 11KV 400 R相AMP | TIE | D09/11/400/I_R |  |  |  | CDC | 259 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | _400 | 400 |  | I_S | [17 empty] | 2-B4 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.11KV_400_A2 | 11KV 400 S相AMP | TIE | D09/11/400/I_S |  |  |  | CDC | 260 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | _400 | 400 |  | I_T | [17 empty] | 2-B5 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.11KV_400_A3 | 11KV 400 T相AMP | TIE | D09/11/400/I_T |  |  |  | CDC | 261 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | _100 | 100 |  | I_R | [17 empty] | 1-C9 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.23KV_100_A1 | 23KV 100 R相AMP | TIE | D09/22/100/I_R |  |  |  | CDC | 262 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | _100 | 100 |  | I_S | [17 empty] | 1-CA | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.23KV_100_A2 | 23KV 100 S相AMP | TIE | D09/22/100/I_S |  |  |  | CDC | 263 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | _100 | 100 |  | I_T | [17 empty] | 1-CB | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.23KV_100_A3 | 23KV 100 T相AMP | TIE | D09/22/100/I_T |  |  |  | CDC | 264 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 0 |  |  |  |  | DCV_N | [17 empty] | 1-99 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.直流N電源電壓 | 直流N電源電壓 | OTHER | D09/0/StaDev/DCV_N |  |  |  | CDC | 265 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D09 | 斗工DS | 0 |  |  |  |  | DCV_P | [17 empty] | 1-98 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.直流P電源電壓 | 直流P電源電壓 | OTHER | D09/0/StaDev/DCV_P |  |  |  | CDC | 266 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D09 | 斗工DS | 11 | 11kV | 1BBUS | #1BBUS |  | V | [17 empty] | 1-EA | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.11KV#1BBUS_KV | 11KV #1BBUS KV | BUS | D09/11/1BBUS/V |  |  |  | CDC | 267 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D09 | 斗工DS | 11 | 11kV | 2B1BUS | #2B1BUS |  | V | [17 empty] | 2-B1 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.11KV#2B1BUS_KV | 11KV #2B1BUS KV | BUS | D09/11/2B1BUS/V |  |  |  | CDC | 268 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D09 | 斗工DS | 11 | 11kV | 2B2BUS | #2B2BUS |  | V | [17 empty] | 2-B2 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.11KV#2B2BUS_KV | 11KV #2B2BUS KV | BUS | D09/11/2B2BUS/V |  |  |  | CDC | 269 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D09 | 斗工DS | 22 | 22kV | 1ABUS | #1ABUS |  | V | [17 empty] | 1-C8 | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.23KV#1ABUS_KV | 23KV #1ABUS KV | BUS | D09/22/1ABUS/V |  |  |  | CDC | 270 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D09 | 斗工DS | 22 | 22kV | 2A1BUS | #2A1BUS |  | V | [17 empty] | 2-8E | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.23KV#2A1BUS_KV | 23KV #2A1BUS KV | BUS | D09/22/2A1BUS/V |  |  |  | CDC | 271 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D09 | 斗工DS | 22 | 22kV | 2A2BUS | #2A2BUS |  | V | [17 empty] | 2-8F | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.23KV#2A2BUS_KV | 23KV #2A2BUS KV | BUS | D09/22/2A2BUS/V |  |  |  | CDC | 272 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D09 | 斗工DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MW | [17 empty] | 1-A8 | [5 empty] | MW_-108_108(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | D09/22/310/KW |  |  |  | CDC | 273 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D09 | 斗工DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVAR | [17 empty] | 1-A9 | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | D09/22/310/KVAR |  |  |  | CDC | 274 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D09 | 斗工DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_R | [17 empty] | 1-AA | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | D09/22/310/I_R |  |  |  | CDC | 275 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_S | [17 empty] | 1-AB | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | D09/22/310/I_S |  |  |  | CDC | 276 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_T | [17 empty] | 1-AC | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | D09/22/310/I_T |  |  |  | CDC | 277 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 0 |  | 1DTR | #1DTR |  | OilTemp | [17 empty] | 1-9B | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.#1DTR_OIL | #1DTR 油溫 | MTR | D09//1DTR/OilTemp |  |  |  | CDC | 278 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D09 | 斗工DS | 0 |  | 1DTR(A) | #1DTR(A) |  | CoilTemp | [17 empty] | 1-9C | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | D09//1DTR(A)/CoilTemp |  |  |  | CDC | 279 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D09 | 斗工DS | 0 |  | 1DTR(A) | #1DTR(A) |  | TapPosMv | [17 empty] | 1-9E |  | 1-5D |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 斗工DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | D09//1DTR(A)/TapPosMv |  |  |  | CDC | 280 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D09 | 斗工DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MW | [17 empty] | 1-CC | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | D09/11/320/KW |  |  |  | CDC | 281 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D09 | 斗工DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVAR | [17 empty] | 1-CD | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | D09/11/320/KVAR |  |  |  | CDC | 282 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D09 | 斗工DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_R | [17 empty] | 1-CE | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | D09/11/320/I_R |  |  |  | CDC | 283 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_S | [17 empty] | 1-CF | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | D09/11/320/I_S |  |  |  | CDC | 284 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_T | [17 empty] | 1-D0 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | D09/11/320/I_T |  |  |  | CDC | 285 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 0 |  | 1DTR(B) | #1DTR(B) |  | CoilTemp | [17 empty] | 1-9D | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | D09//1DTR(B)/CoilTemp |  |  |  | CDC | 286 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D09 | 斗工DS | 0 |  | 1DTR(B) | #1DTR(B) |  | TapPosMv | [17 empty] | 1-9F |  | 1-5F |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 斗工DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | D09//1DTR(B)/TapPosMv |  |  |  | CDC | 287 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D09 | 斗工DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MW | [17 empty] | 1-EE | [5 empty] | MW_-108_108(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | D09/22/330/KW |  |  |  | CDC | 288 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D09 | 斗工DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVAR | [17 empty] | 1-EF | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | D09/22/330/KVAR |  |  |  | CDC | 289 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D09 | 斗工DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_R | [17 empty] | 1-F0 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | D09/22/330/I_R |  |  |  | CDC | 290 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_S | [17 empty] | 1-F1 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | D09/22/330/I_S |  |  |  | CDC | 291 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_T | [17 empty] | 1-F2 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | D09/22/330/I_T |  |  |  | CDC | 292 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 0 |  | 2DTR | #2DTR |  | OilTemp | [17 empty] | 1-A0 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.#2DTR_OIL | #2DTR 油溫 | MTR | D09//2DTR/OilTemp |  |  |  | CDC | 293 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D09 | 斗工DS | 0 |  | 2DTR(A) | #2DTR(A) |  | CoilTemp | [17 empty] | 1-A1 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | D09//2DTR(A)/CoilTemp |  |  |  | CDC | 294 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D09 | 斗工DS | 0 |  | 2DTR(A) | #2DTR(A) |  | TapPosMv | [17 empty] | 1-A3 |  | 1-61 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 斗工DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | D09//2DTR(A)/TapPosMv |  |  |  | CDC | 295 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D09 | 斗工DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MW | [17 empty] | 2-93 | [5 empty] | MW_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | D09/11/340/KW |  |  |  | CDC | 296 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D09 | 斗工DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVAR | [17 empty] | 2-94 | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | D09/11/340/KVAR |  |  |  | CDC | 297 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D09 | 斗工DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_R | [17 empty] | 2-95 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | D09/11/340/I_R |  |  |  | CDC | 298 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_S | [17 empty] | 2-96 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | D09/11/340/I_S |  |  |  | CDC | 299 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_T | [17 empty] | 2-97 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | D09/11/340/I_T |  |  |  | CDC | 300 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 0 |  | 2DTR(B) | #2DTR(B) |  | CoilTemp | [17 empty] | 1-A2 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | D09//2DTR(B)/CoilTemp |  |  |  | CDC | 301 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D09 | 斗工DS | 0 |  | 2DTR(B) | #2DTR(B) |  | TapPosMv | [17 empty] | 1-A4 |  | 1-63 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 斗工DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | D09//2DTR(B)/TapPosMv |  |  |  | CDC | 302 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D09 | 斗工DS | 11 | 11kV | _200 | 200 |  | I_R | [17 empty] | 1-EB | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.11KV_200_A1 | 11KV 200 R相AMP | TIE | D09/11/200/I_R |  |  |  | CDC | 303 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | _200 | 200 |  | I_S | [17 empty] | 1-EC | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.11KV_200_A2 | 11KV 200 S相AMP | TIE | D09/11/200/I_S |  |  |  | CDC | 304 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 11 | 11kV | _200 | 200 |  | I_T | [17 empty] | 1-ED | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.11KV_200_A3 | 11KV 200 T相AMP | TIE | D09/11/200/I_T |  |  |  | CDC | 305 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | _300 | 300 |  | I_R | [17 empty] | 2-90 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.23KV_300_A1 | 23KV 300 R相AMP | TIE | D09/22/300/I_R |  |  |  | CDC | 306 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | _300 | 300 |  | I_S | [17 empty] | 2-91 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.23KV_300_A2 | 23KV 300 S相AMP | TIE | D09/22/300/I_S |  |  |  | CDC | 307 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 22 | 22kV | _300 | 300 |  | I_T | [17 empty] | 2-92 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.23KV_300_A3 | 23KV 300 T相AMP | TIE | D09/22/300/I_T |  |  |  | CDC | 308 | GENERICAIPoint | DS036_L2 | CDC2_AI |  | AI | [17 empty] | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1570 | 備用線(1570) |  | MW | [17 empty] | 1-8E | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.1570_MW | 備用線 MW | LINE161 |  |  |  |  | CDC | 309 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1570 | 備用線(1570) |  | MVAR | [17 empty] | 1-8F | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.1570_MVAR | 備用線 MVAR | LINE161 |  |  |  |  | CDC | 310 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1580 | 斗六斗工線(1580) |  | MW | [17 empty] | 1-90 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.1580_MW | 斗六斗工線 MW | LINE161 |  |  |  |  | CDC | 311 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1580 | 斗六斗工線(1580) |  | MVAR | [17 empty] | 1-91 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.1580_MVAR | 斗六斗工線 MVAR | LINE161 |  |  |  |  | CDC | 312 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1610 | 榴中斗工一路(1610) |  | MW | [17 empty] | 1-92 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.1610_MW | 榴中斗工一路 MW | LINE161 | D09/161/1610/MW |  |  |  | CDC | 313 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1610 | 榴中斗工一路(1610) |  | MVAR | [17 empty] | 1-93 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.1610_MVAR | 榴中斗工一路 MVAR | LINE161 | D09/161/1610/MVAR |  |  |  | CDC | 314 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1620 | 榴中斗工二路(1620) |  | MW | [17 empty] | 1-94 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.1620_MW | 榴中斗工二路 MW | LINE161 | D09/161/1620/MW |  |  |  | CDC | 315 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1620 | 榴中斗工二路(1620) |  | MVAR | [17 empty] | 1-95 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 斗工DS.1620_MVAR | 榴中斗工二路 MVAR | LINE161 | D09/161/1620/MVAR |  |  |  | CDC | 316 | GENERICAIPoint | DS036_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工山線(1510) |  | PHA | [17 empty] | 1-00-03 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.1510_PHA | 鉅工山線(1510) 相間RY | LINE161 | D09/161/1510/PHA |  |  |  | CDC | 317 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工山線(1510) |  | GDA | [17 empty] | 1-00-04 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.1510_GDA | 鉅工山線(1510) 接地RY | LINE161 | D09/161/1510/GDA |  |  |  | CDC | 318 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工山線(1510) |  | CB | [17 empty] | 1-00-00 |  | 1-01 | [5 empty] | 161KV_N | [8 empty] | 斗工DS.1510_CB | 1510(鉅工山線) CB | LINE161 | D09/161/1510/CB |  |  |  | CDC | 319 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工山線(1510) |  | 79UL | [17 empty] | 1-30-03 |  | 1-49 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1510_79UL | 鉅工山線(1510) 79RY U/L | LINE161 | D09/161/1510/79UL |  |  |  | CDC | 320 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工山線(1510) |  | DS1 | 1511 | [16 empty] | 1-34-00 | 1-34-01 | 1-68 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1511_DS | 1511(鉅工山線) DS | LINE161 | D09/161/1510/DS1 |  |  |  | CDC | 321 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工山線(1510) |  | DS2 | 1512 | [16 empty] | 1-34-02 | 1-34-03 | 1-69 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1512_DS | 1512(鉅工山線) DS | LINE161 | D09/161/1510/DS2 |  |  |  | CDC | 322 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工山線(1510) |  | DS3 | 1513 | [16 empty] | 1-34-04 | 1-34-05 | 1-6A | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1513_DS | 1513(鉅工山線) DS | LINE161 | D09/161/1510/DS3 |  |  |  | CDC | 323 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工山線(1510) |  | E3 | 1513E | [16 empty] | 1-34-06 | 1-34-07 | 1-6B | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1513E_ES | 1513E(鉅工山線) ES | LINE161 | D09/161/1510/ES3 |  |  |  | CDC | 324 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工海線(1520) |  | PHA | [17 empty] | 1-01-00 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.1520_PHA | 鉅工海線(1520) 相間RY | LINE161 | D09/161/1520/PHA |  |  |  | CDC | 325 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工海線(1520) |  | GDA | [17 empty] | 1-01-01 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.1520_GDA | 鉅工海線(1520) 接地RY | LINE161 | D09/161/1520/GDA |  |  |  | CDC | 326 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工海線(1520) |  | CB | [17 empty] | 1-00-05 |  | 1-02 | [5 empty] | 161KV_N | [8 empty] | 斗工DS.1520_CB | 1520(鉅工海線) CB | LINE161 | D09/161/1520/CB |  |  |  | CDC | 327 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工海線(1520) |  | 79UL | [17 empty] | 1-30-05 |  | 1-4B | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1520_79UL | 鉅工海線(1520) 79RY U/L | LINE161 | D09/161/1520/79UL |  |  |  | CDC | 328 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工海線(1520) |  | DS1 | 1521 | [16 empty] | 1-34-08 | 1-34-09 | 1-6C | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1521_DS | 1521(鉅工海線) DS | LINE161 | D09/161/1520/DS1 |  |  |  | CDC | 329 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工海線(1520) |  | DS2 | 1522 | [16 empty] | 1-34-10 | 1-34-11 | 1-6D | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1522_DS | 1522(鉅工海線) DS | LINE161 | D09/161/1520/DS2 |  |  |  | CDC | 330 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工海線(1520) |  | DS3 | 1523 | [16 empty] | 1-34-12 | 1-34-13 | 1-6E | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1523_DS | 1523(鉅工海線) DS | LINE161 | D09/161/1520/DS3 |  |  |  | CDC | 331 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工海線(1520) |  | E3 | 1523E | [16 empty] | 1-34-14 | 1-34-15 | 1-6F | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1523E_ES | 1523E(鉅工海線) ES | LINE161 | D09/161/1520/ES3 |  |  |  | CDC | 332 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 161 | 161kV | 1530 | 嘉民斗工紅線(1530) |  | PHA | [17 empty] | 1-02-02 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.1530_PHA | 嘉民斗工紅線(1530) 相間RY | LINE161 | D09/161/1530/PHA |  |  |  | CDC | 333 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1530 | 嘉民斗工紅線(1530) |  | GDA | [17 empty] | 1-02-03 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.1530_GDA | 嘉民斗工紅線(1530) 接地RY | LINE161 | D09/161/1530/GDA |  |  |  | CDC | 334 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1530 | 嘉民斗工紅線(1530) |  | CB | [17 empty] | 1-01-07 |  | 1-04 | [5 empty] | 161KV_N | [8 empty] | 斗工DS.1530_CB | 1530(嘉民斗工紅線) CB | LINE161 | D09/161/1530/CB |  |  |  | CDC | 335 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 161 | 161kV | 1530 | 嘉民斗工紅線(1530) |  | 79UL | [17 empty] | 1-30-09 |  | 1-4F | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1530_79UL | 嘉民斗工紅線(1530) 79RY U/L | LINE161 | D09/161/1530/79UL |  |  |  | CDC | 336 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 161 | 161kV | 1530 | 嘉民斗工紅線(1530) |  | DS1 | 1531 | [16 empty] | 1-35-08 | 1-35-09 | 1-74 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1531_DS | 1531(嘉民斗工紅線) DS | LINE161 | D09/161/1530/DS1 |  |  |  | CDC | 337 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1530 | 嘉民斗工紅線(1530) |  | DS2 | 1532 | [16 empty] | 1-35-10 | 1-35-11 | 1-75 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1532_DS | 1532(嘉民斗工紅線) DS | LINE161 | D09/161/1530/DS2 |  |  |  | CDC | 338 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 161 | 161kV | 1530 | 嘉民斗工紅線(1530) |  | DS3 | 1533 | [16 empty] | 1-35-12 | 1-35-13 | 1-76 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1533_DS | 1533(嘉民斗工紅線) DS | LINE161 | D09/161/1530/DS3 |  |  |  | CDC | 339 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1530 | 嘉民斗工紅線(1530) |  | E3 | 1533E | [16 empty] | 1-35-14 | 1-35-15 | 1-77 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1533E_ES | 1533E(嘉民斗工紅線) ES | LINE161 | D09/161/1530/ES3 |  |  |  | CDC | 340 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 161 | 161kV | 1540 | 雲林斗工線(1540) |  | PHA | [17 empty] | 1-01-05 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.1540_PHA | 雲林斗工線(1540) 相間RY | LINE161 | D09/161/1540/PHA |  |  |  | CDC | 341 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1540 | 雲林斗工線(1540) |  | GDA | [17 empty] | 1-01-06 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.1540_GDA | 雲林斗工線(1540) 接地RY | LINE161 | D09/161/1540/GDA |  |  |  | CDC | 342 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1540 | 雲林斗工線(1540) |  | CB | [17 empty] | 1-01-02 |  | 1-03 | [5 empty] | 161KV_N | [8 empty] | 斗工DS.1540_CB | 1540(雲林斗工線) CB | LINE161 | D09/161/1540/CB |  |  |  | CDC | 343 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 161 | 161kV | 1540 | 雲林斗工線(1540) |  | 79UL | [17 empty] | 1-30-07 |  | 1-4D | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1540_79UL | 雲林斗工線(1540) 79RY U/L | LINE161 | D09/161/1540/79UL |  |  |  | CDC | 344 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 161 | 161kV | 1540 | 雲林斗工線(1540) |  | DS1 | 1541 | [16 empty] | 1-35-00 | 1-35-01 | 1-70 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1541_DS | 1541(雲林斗工線) DS | LINE161 | D09/161/1540/DS1 |  |  |  | CDC | 345 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 161 | 161kV | 1540 | 雲林斗工線(1540) |  | DS2 | 1542 | [16 empty] | 1-35-02 | 1-35-03 | 1-71 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1542_DS | 1542(雲林斗工線) DS | LINE161 | D09/161/1540/DS2 |  |  |  | CDC | 346 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1540 | 雲林斗工線(1540) |  | DS3 | 1543 | [16 empty] | 1-35-04 | 1-35-05 | 1-72 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1543_DS | 1543(雲林斗工線) DS | LINE161 | D09/161/1540/DS3 |  |  |  | CDC | 347 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1540 | 雲林斗工線(1540) |  | E3 | 1543E | [16 empty] | 1-35-06 | 1-35-07 | 1-73 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1543E_ES | 1543E(雲林斗工線) ES | LINE161 | D09/161/1540/ES3 |  |  |  | CDC | 348 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 161 | 161kV | 1550 | 富喬線(1550) |  | PHA | [17 empty] | 1-02-07 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.1550_PHA | 富喬線(1550) 相間RY | LINE161 | D09/161/1550/PHA |  |  |  | CDC | 349 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1550 | 富喬線(1550) |  | GDA | [17 empty] | 1-03-00 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.1550_GDA | 富喬線(1550) 接地RY | LINE161 | D09/161/1550/GDA |  |  |  | CDC | 350 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1550 | 富喬線(1550) |  | 85A | [17 empty] | 1-02-05 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.1550_85A | 富喬線(1550) 85RY | LINE161 | D09/161/1550/85A |  |  |  | CDC | 351 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1550 | 富喬線(1550) |  | 85UL | [17 empty] | 1-30-10 |  | 1-50 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1550_85UL | 富喬線(1550) 85RY U/L | LINE161 | D09/161/1550/85UL |  |  |  | CDC | 352 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 161 | 161kV | 1550 | 富喬線(1550) |  | CB | [17 empty] | 1-02-04 |  | 1-05 | [5 empty] | 161KV_N | [8 empty] | 斗工DS.1550_CB | 1550(富喬線) CB | LINE161 | D09/161/1550/CB |  |  |  | CDC | 353 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 161 | 161kV | 1550 | 富喬線(1550) |  | 79UL | [17 empty] | 1-30-11 |  | 1-51 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1550_79UL | 富喬線(1550) 79RY U/L | LINE161 | D09/161/1550/79UL |  |  |  | CDC | 354 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 161 | 161kV | 1550 | 富喬線(1550) |  | DS1 | 1551 | [16 empty] | 2-36-00 | 2-36-01 | 1-78 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1551_DS | 1551(富喬線) DS | LINE161 | D09/161/1550/DS1 |  |  |  | CDC | 355 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1550 | 富喬線(1550) |  | DS2 | 1552 | [16 empty] | 2-36-02 | 2-36-03 | 1-79 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1552_DS | 1552(富喬線) DS | LINE161 | D09/161/1550/DS2 |  |  |  | CDC | 356 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 161 | 161kV | 1550 | 富喬線(1550) |  | DS3 | 1553 | [16 empty] | 2-36-04 | 2-36-05 | 1-7A | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1553_DS | 1553(富喬線) DS | LINE161 | D09/161/1550/DS3 |  |  |  | CDC | 357 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1550 | 富喬線(1550) |  | E3 | 1553E | [16 empty] | 2-36-06 | 2-36-07 | 1-7B | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1553E_ES | 1553E(富喬線) ES | LINE161 | D09/161/1550/ES3 |  |  |  | CDC | 358 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 11 | 11kV | XU26 | 工六線(XU26) |  | PHA | [17 empty] | 1-12-06 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU26_PHA | 11KV工六線(XU26) 相間RY | FEEDER | D09/11/XU26/PHA |  |  |  | CDC | 359 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU26 | 工六線(XU26) |  | GDA | [17 empty] | 1-12-07 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU26_GDA | 11KV工六線(XU26) 接地RY | FEEDER | D09/11/XU26/GDA |  |  |  | CDC | 360 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU26 | 工六線(XU26) 79RY |  | 79UL | [17 empty] | 2-30-07 |  | 2-27 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU26_79UL | 11KV工六線(XU26) 79RY U/L | FEEDER | D09/11/XU26/79UL |  |  |  | CDC | 361 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 11 | 11kV | XU26_LCO | 工六線(XU26) LCO |  | TapPosMv | [17 empty] | 2-32-01 |  | 2-41 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU26_LCO_TAP | 11KV工六線(XU26) LCO TAP | FEEDER | D09/11/XU26/50N_51N |  |  |  | CDC | 362 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D09 | 斗工DS | 11 | 11kV | XU26 | XU26(11KV工六線) |  | CB | [17 empty] | 1-12-05 |  | 1-1B | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU26_CB | XU26(11KV工六線) CB | FEEDER | D09/11/XU26/CB |  |  |  | CDC | 363 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | XU27 | 工七線(XU27) |  | PHA | [17 empty] | 1-13-01 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU27_PHA | 11KV工七線(XU27) 相間RY | FEEDER | D09/11/XU27/PHA |  |  |  | CDC | 364 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU27 | 工七線(XU27) |  | GDA | [17 empty] | 1-13-02 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU27_GDA | 11KV工七線(XU27) 接地RY | FEEDER | D09/11/XU27/GDA |  |  |  | CDC | 365 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU27 | 工七線(XU27) 79RY |  | 79UL | [17 empty] | 2-30-08 |  | 2-28 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU27_79UL | 11KV工七線(XU27) 79RY U/L | FEEDER | D09/11/XU27/79UL |  |  |  | CDC | 366 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 11 | 11kV | XU27_LCO | 工七線(XU27) LCO |  | TapPosMv | [17 empty] | 2-32-02 |  | 2-42 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU27_LCO_TAP | 11KV工七線(XU27) LCO TAP | FEEDER | D09/11/XU27/50N_51N |  |  |  | CDC | 367 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D09 | 斗工DS | 11 | 11kV | XU27 | XU27(11KV工七線) |  | CB | [17 empty] | 1-13-00 |  | 1-1C | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU27_CB | XU27(11KV工七線) CB | FEEDER | D09/11/XU27/CB |  |  |  | CDC | 368 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | XU28 | 工八線(XU28) |  | PHA | [17 empty] | 1-13-04 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU28_PHA | 11KV工八線(XU28) 相間RY | FEEDER | D09/11/XU28/PHA |  |  |  | CDC | 369 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU28 | 工八線(XU28) |  | GDA | [17 empty] | 1-13-05 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU28_GDA | 11KV工八線(XU28) 接地RY | FEEDER | D09/11/XU28/GDA |  |  |  | CDC | 370 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU28 | 工八線(XU28) 79RY |  | 79UL | [17 empty] | 2-30-09 |  | 2-29 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU28_79UL | 11KV工八線(XU28) 79RY U/L | FEEDER | D09/11/XU28/79UL |  |  |  | CDC | 371 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 11 | 11kV | XU28_LCO | 工八線(XU28) LCO |  | TapPosMv | [17 empty] | 2-32-03 |  | 2-43 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU28_LCO_TAP | 11KV工八線(XU28) LCO TAP | FEEDER | D09/11/XU28/50N_51N |  |  |  | CDC | 372 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D09 | 斗工DS | 11 | 11kV | XU28 | XU28(11KV工八線) |  | CB | [17 empty] | 1-13-03 |  | 1-1D | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU28_CB | XU28(11KV工八線) CB | FEEDER | D09/11/XU28/CB |  |  |  | CDC | 373 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | XU29 | 工九線(XU29) |  | PHA | [17 empty] | 1-13-07 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU29_PHA | 11KV工九線(XU29) 相間RY | FEEDER | D09/11/XU29/PHA |  |  |  | CDC | 374 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU29 | 工九線(XU29) |  | GDA | [17 empty] | 1-14-00 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU29_GDA | 11KV工九線(XU29) 接地RY | FEEDER | D09/11/XU29/GDA |  |  |  | CDC | 375 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU29 | 工九線(XU29) 79RY |  | 79UL | [17 empty] | 2-30-10 |  | 2-2A | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU29_79UL | 11KV工九線(XU29) 79RY U/L | FEEDER | D09/11/XU29/79UL |  |  |  | CDC | 376 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 11 | 11kV | XU29_LCO | 工九線(XU29) LCO |  | TapPosMv | [17 empty] | 2-32-04 |  | 2-44 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU29_LCO_TAP | 11KV工九線(XU29) LCO TAP | FEEDER | D09/11/XU29/50N_51N |  |  |  | CDC | 377 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D09 | 斗工DS | 11 | 11kV | XU29 | XU29(11KV工九線) |  | CB | [17 empty] | 1-13-06 |  | 1-1E | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU29_CB | XU29(11KV工九線) CB | FEEDER | D09/11/XU29/CB |  |  |  | CDC | 378 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | XU30 | 工十線(XU30) |  | PHA | [17 empty] | 1-14-02 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU30_PHA | 11KV工十線(XU30) 相間RY | FEEDER | D09/11/XU30/PHA |  |  |  | CDC | 379 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU30 | 工十線(XU30) |  | GDA | [17 empty] | 1-14-03 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU30_GDA | 11KV工十線(XU30) 接地RY | FEEDER | D09/11/XU30/GDA |  |  |  | CDC | 380 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU30 | 工十線(XU30) 79RY |  | 79UL | [17 empty] | 2-30-11 |  | 2-2B | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU30_79UL | 11KV工十線(XU30) 79RY U/L | FEEDER | D09/11/XU30/79UL |  |  |  | CDC | 381 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 11 | 11kV | XU30_LCO | 工十線(XU30) LCO |  | TapPosMv | [17 empty] | 2-32-05 |  | 2-45 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU30_LCO_TAP | 11KV工十線(XU30) LCO TAP | FEEDER | D09/11/XU30/50N_51N |  |  |  | CDC | 382 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D09 | 斗工DS | 11 | 11kV | XU30 | XU30(11KV工十線) |  | CB | [17 empty] | 1-14-01 |  | 1-1F | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU30_CB | XU30(11KV工十線) CB | FEEDER | D09/11/XU30/CB |  |  |  | CDC | 383 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | XU36 | 工十六線(XU36) |  | PHA | [17 empty] | 1-18-06 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU36_PHA | 11KV工十六線(XU36) 相間RY | FEEDER | D09/11/XU36/PHA |  |  |  | CDC | 384 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU36 | 工十六線(XU36) |  | GDA | [17 empty] | 1-18-07 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU36_GDA | 11KV工十六線(XU36) 接地RY | FEEDER | D09/11/XU36/GDA |  |  |  | CDC | 385 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU36 | 工十六線(XU36) 79RY |  | 79UL | [17 empty] | 2-31-05 |  | 2-35 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU36_79UL | 11KV工十六線(XU36) 79RY U/L | FEEDER | D09/11/XU36/79UL |  |  |  | CDC | 386 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 11 | 11kV | XU36_LCO | 工十六線(XU36) LCO |  | TapPosMv | [17 empty] | 2-35-11 |  | 2-4B | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU36_LCO_TAP | 11KV工十六線(XU36) LCO TAP | FEEDER | D09/11/XU36/50N_51N |  |  |  | CDC | 387 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D09 | 斗工DS | 11 | 11kV | XU36 | XU36(11KV工十六線) |  | CB | [17 empty] | 1-18-05 |  | 1-2B | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU36_CB | XU36(11KV工十六線) CB | FEEDER | D09/11/XU36/CB |  |  |  | CDC | 388 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | XU37 | 工十七線(XU37) |  | PHA | [17 empty] | 1-19-01 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU37_PHA | 11KV工十七線(XU37) 相間RY | FEEDER | D09/11/XU37/PHA |  |  |  | CDC | 389 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU37 | 工十七線(XU37) |  | GDA | [17 empty] | 1-19-02 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU37_GDA | 11KV工十七線(XU37) 接地RY | FEEDER | D09/11/XU37/GDA |  |  |  | CDC | 390 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU37 | 工十七線(XU37) 79RY |  | 79UL | [17 empty] | 2-31-06 |  | 2-36 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU37_79UL | 11KV工十七線(XU37) 79RY U/L | FEEDER | D09/11/XU37/79UL |  |  |  | CDC | 391 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 11 | 11kV | XU37_LCO | 工十七線(XU37) LCO |  | TapPosMv | [17 empty] | 2-35-12 |  | 2-4C | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU37_LCO_TAP | 11KV工十七線(XU37) LCO TAP | FEEDER | D09/11/XU37/50N_51N |  |  |  | CDC | 392 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D09 | 斗工DS | 11 | 11kV | XU37 | XU37(11KV工十七線) |  | CB | [17 empty] | 1-19-00 |  | 1-2C | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU37_CB | XU37(11KV工十七線) CB | FEEDER | D09/11/XU37/CB |  |  |  | CDC | 393 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | XU38 | 工十八線(XU38) |  | PHA | [17 empty] | 1-19-04 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU38_PHA | 11KV工十八線(XU38) 相間RY | FEEDER | D09/11/XU38/PHA |  |  |  | CDC | 394 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU38 | 工十八線(XU38) |  | GDA | [17 empty] | 1-19-05 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU38_GDA | 11KV工十八線(XU38) 接地RY | FEEDER | D09/11/XU38/GDA |  |  |  | CDC | 395 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU38 | 工十八線(XU38) 79RY |  | 79UL | [17 empty] | 2-31-07 |  | 2-37 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU38_79UL | 11KV工十八線(XU38) 79RY U/L | FEEDER | D09/11/XU38/79UL |  |  |  | CDC | 396 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 11 | 11kV | XU38_LCO | 工十八線(XU38) LCO |  | TapPosMv | [17 empty] | 2-35-13 |  | 2-4D | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU38_LCO_TAP | 11KV工十八線(XU38) LCO TAP | FEEDER | D09/11/XU38/50N_51N |  |  |  | CDC | 397 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D09 | 斗工DS | 11 | 11kV | XU38 | XU38(11KV工十八線) |  | CB | [17 empty] | 1-19-03 |  | 1-30 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU38_CB | XU38(11KV工十八線) CB | FEEDER | D09/11/XU38/CB |  |  |  | CDC | 398 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | XU39 | 工十九線(XU39) |  | PHA | [17 empty] | 1-19-07 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU39_PHA | 11KV工十九線(XU39) 相間RY | FEEDER | D09/11/XU39/PHA |  |  |  | CDC | 399 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU39 | 工十九線(XU39) |  | GDA | [17 empty] | 1-1A-00 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU39_GDA | 11KV工十九線(XU39) 接地RY | FEEDER | D09/11/XU39/GDA |  |  |  | CDC | 400 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU39 | 工十九線(XU39) 79RY |  | 79UL | [17 empty] | 2-31-08 |  | 2-38 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU39_79UL | 11KV工十九線(XU39) 79RY U/L | FEEDER | D09/11/XU39/79UL |  |  |  | CDC | 401 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 11 | 11kV | XU39_LCO | 工十九線(XU39) LCO |  | TapPosMv | [17 empty] | 2-35-14 |  | 2-4E | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU39_LCO_TAP | 11KV工十九線(XU39) LCO TAP | FEEDER | D09/11/XU39/50N_51N |  |  |  | CDC | 402 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D09 | 斗工DS | 11 | 11kV | XU39 | XU39(11KV工十九線) |  | CB | [17 empty] | 1-19-06 |  | 1-31 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU39_CB | XU39(11KV工十九線) CB | FEEDER | D09/11/XU39/CB |  |  |  | CDC | 403 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | XU40 | 工二十線(XU40) |  | PHA | [17 empty] | 1-1A-02 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU40_PHA | 11KV工二十線(XU40) 相間RY | FEEDER | D09/11/XU40/PHA |  |  |  | CDC | 404 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU40 | 工二十線(XU40) |  | GDA | [17 empty] | 1-1A-03 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU40_GDA | 11KV工二十線(XU40) 接地RY | FEEDER | D09/11/XU40/GDA |  |  |  | CDC | 405 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | XU40 | 工二十線(XU40) 79RY |  | 79UL | [17 empty] | 2-31-09 |  | 2-39 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU40_79UL | 11KV工二十線(XU40) 79RY U/L | FEEDER | D09/11/XU40/79UL |  |  |  | CDC | 406 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 11 | 11kV | XU40_LCO | 工二十線(XU40) LCO |  | TapPosMv | [17 empty] | 2-35-15 |  | 2-4F | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU40_LCO_TAP | 11KV工二十線(XU40) LCO TAP | FEEDER | D09/11/XU40/50N_51N |  |  |  | CDC | 407 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D09 | 斗工DS | 11 | 11kV | XU40 | XU40(11KV工二十線) |  | CB | [17 empty] | 1-1A-01 |  | 1-32 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU40_CB | XU40(11KV工二十線) CB | FEEDER | D09/11/XU40/CB |  |  |  | CDC | 408 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | XU51 | 工五一線(XU51) |  | PHA | [17 empty] | 1-10-01 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU51_PHA | 23KV工五一線(XU51) 相間RY | FEEDER | D09/22/XU51/PHA |  |  |  | CDC | 409 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU51 | 工五一線(XU51) |  | GDA | [17 empty] | 1-10-02 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU51_GDA | 23KV工五一線(XU51) 接地RY | FEEDER | D09/22/XU51/GDA |  |  |  | CDC | 410 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU51 | 工五一線(XU51) 79RY |  | 79UL | [17 empty] | 2-30-00 |  | 2-20 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU51_79UL | 23KV工五一線(XU51) 79RY U/L | FEEDER | D09/22/XU51/79UL |  |  |  | CDC | 411 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 22 | 22kV | XU51_LCO | 工五一線(XU51) LCO |  | TapPosMv | [17 empty] | 2-31-12 |  | 2-3C | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU51_LCO_TAP | 23KV工五一線(XU51) LCO TAP | FEEDER | D09/22/XU51/50N_51N |  |  |  | CDC | 412 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D09 | 斗工DS | 22 | 22kV | XU51 | XU51(23KV工五一線) |  | CB | [17 empty] | 1-10-00 |  | 1-12 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU51_CB | XU51(23KV工五一線) CB | FEEDER | D09/22/XU51/CB |  |  |  | CDC | 413 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | XU52 | 工五二線(XU52) |  | PHA | [17 empty] | 1-10-04 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU52_PHA | 23KV工五二線(XU52) 相間RY | FEEDER | D09/22/XU52/PHA |  |  |  | CDC | 414 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU52 | 工五二線(XU52) |  | GDA | [17 empty] | 1-10-05 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU52_GDA | 23KV工五二線(XU52) 接地RY | FEEDER | D09/22/XU52/GDA |  |  |  | CDC | 415 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU52 | 工五二線(XU52) 79RY |  | 79UL | [17 empty] | 2-30-01 |  | 2-21 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU52_79UL | 23KV工五二線(XU52) 79RY U/L | FEEDER | D09/22/XU52/79UL |  |  |  | CDC | 416 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 22 | 22kV | XU52_LCO | 工五二線(XU52) LCO |  | TapPosMv | [17 empty] | 2-31-13 |  | 2-3D | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU52_LCO_TAP | 23KV工五二線(XU52) LCO TAP | FEEDER | D09/22/XU52/50N_51N |  |  |  | CDC | 417 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D09 | 斗工DS | 22 | 22kV | XU52 | XU52(23KV工五二線) |  | CB | [17 empty] | 1-10-03 |  | 1-13 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU52_CB | XU52(23KV工五二線) CB | FEEDER | D09/22/XU52/CB |  |  |  | CDC | 418 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | XU53 | 工五三線(XU53) |  | PHA | [17 empty] | 1-10-07 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU53_PHA | 23KV工五三線(XU53) 相間RY | FEEDER | D09/22/XU53/PHA |  |  |  | CDC | 419 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU53 | 工五三線(XU53) |  | GDA | [17 empty] | 1-11-00 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU53_GDA | 23KV工五三線(XU53) 接地RY | FEEDER | D09/22/XU53/GDA |  |  |  | CDC | 420 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU53 | 工五三線(XU53) 79RY |  | 79UL | [17 empty] | 2-30-02 |  | 2-22 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU53_79UL | 23KV工五三線(XU53) 79RY U/L | FEEDER | D09/22/XU53/79UL |  |  |  | CDC | 421 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 22 | 22kV | XU53_LCO | 工五三線(XU53) LCO |  | TapPosMv | [17 empty] | 2-31-14 |  | 2-3E | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU53_LCO_TAP | 23KV工五三線(XU53) LCO TAP | FEEDER | D09/22/XU53/50N_51N |  |  |  | CDC | 422 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D09 | 斗工DS | 22 | 22kV | XU53 | XU53(23KV工五三線) |  | CB | [17 empty] | 1-10-06 |  | 1-14 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU53_CB | XU53(23KV工五三線) CB | FEEDER | D09/22/XU53/CB |  |  |  | CDC | 423 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | XU54 | 工五四線(XU54) |  | PHA | [17 empty] | 1-11-02 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU54_PHA | 23KV工五四線(XU54) 相間RY | FEEDER | D09/22/XU54/PHA |  |  |  | CDC | 424 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU54 | 工五四線(XU54) |  | GDA | [17 empty] | 1-11-03 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU54_GDA | 23KV工五四線(XU54) 接地RY | FEEDER | D09/22/XU54/GDA |  |  |  | CDC | 425 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU54 | 工五四線(XU54) 79RY |  | 79UL | [17 empty] | 2-30-03 |  | 2-23 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU54_79UL | 23KV工五四線(XU54) 79RY U/L | FEEDER | D09/22/XU54/79UL |  |  |  | CDC | 426 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 22 | 22kV | XU54_LCO | 工五四線(XU54) LCO |  | TapPosMv | [17 empty] | 2-31-15 |  | 2-3F | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU54_LCO_TAP | 23KV工五四線(XU54) LCO TAP | FEEDER | D09/22/XU54/50N_51N |  |  |  | CDC | 427 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D09 | 斗工DS | 22 | 22kV | XU54 | XU54(23KV工五四線) |  | CB | [17 empty] | 1-11-01 |  | 1-15 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU54_CB | XU54(23KV工五四線) CB | FEEDER | D09/22/XU54/CB |  |  |  | CDC | 428 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | XU55 | 工五五線(XU55) |  | PHA | [17 empty] | 1-11-05 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU55_PHA | 23KV工五五線(XU55) 相間RY | FEEDER | D09/22/XU55/PHA |  |  |  | CDC | 429 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU55 | 工五五線(XU55) |  | GDA | [17 empty] | 1-11-06 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU55_GDA | 23KV工五五線(XU55) 接地RY | FEEDER | D09/22/XU55/GDA |  |  |  | CDC | 430 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU55 | 工五五線(XU55) 79RY |  | 79UL | [17 empty] | 2-30-04 |  | 2-24 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU55_79UL | 23KV工五五線(XU55) 79RY U/L | FEEDER | D09/22/XU55/79UL |  |  |  | CDC | 431 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 22 | 22kV | XU55_LCO | 工五五線(XU55) LCO |  | TapPosMv | [17 empty] | 2-32-00 |  | 2-40 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU55_LCO_TAP | 23KV工五五線(XU55) LCO TAP | FEEDER | D09/22/XU55/50N_51N |  |  |  | CDC | 432 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D09 | 斗工DS | 22 | 22kV | XU55 | XU55(23KV工五五線) |  | CB | [17 empty] | 1-11-04 |  | 1-16 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU55_CB | XU55(23KV工五五線) CB | FEEDER | D09/22/XU55/CB |  |  |  | CDC | 433 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | XU61 | 工六一線(XU61) |  | PHA | [17 empty] | 1-15-06 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU61_PHA | 23KV工六一線(XU61) 相間RY | FEEDER | D09/22/XU61/PHA |  |  |  | CDC | 434 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU61 | 工六一線(XU61) |  | GDA | [17 empty] | 1-15-07 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU61_GDA | 23KV工六一線(XU61) 接地RY | FEEDER | D09/22/XU61/GDA |  |  |  | CDC | 435 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU61 | 工六一線(XU61) 79RY |  | 79UL | [17 empty] | 2-30-14 |  | 2-2E | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU61_79UL | 23KV工六一線(XU61) 79RY U/L | FEEDER | D09/22/XU61/79UL |  |  |  | CDC | 436 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 22 | 22kV | XU61_LCO | 工六一線(XU61) LCO |  | TapPosMv | [17 empty] | 2-32-06 |  | 2-46 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU61_LCO_TAP | 23KV工六一線(XU61) LCO TAP | FEEDER | D09/22/XU61/50N_51N |  |  |  | CDC | 437 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D09 | 斗工DS | 22 | 22kV | XU61 | XU61(23KV工六一線) |  | CB | [17 empty] | 1-15-05 |  | 1-21 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU61_CB | XU61(23KV工六一線) CB | FEEDER | D09/22/XU61/CB |  |  |  | CDC | 438 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | XU62 | 工六二線(XU62) |  | PHA | [17 empty] | 1-16-01 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU62_PHA | 23KV工六二線(XU62) 相間RY | FEEDER | D09/22/XU62/PHA |  |  |  | CDC | 439 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU62 | 工六二線(XU62) |  | GDA | [17 empty] | 1-16-02 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU62_GDA | 23KV工六二線(XU62) 接地RY | FEEDER | D09/22/XU62/GDA |  |  |  | CDC | 440 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU62 | 工六二線(XU62) 79RY |  | 79UL | [17 empty] | 2-30-15 |  | 2-2F | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU62_79UL | 23KV工六二線(XU62) 79RY U/L | FEEDER | D09/22/XU62/79UL |  |  |  | CDC | 441 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 22 | 22kV | XU62_LCO | 工六二線(XU62) LCO |  | TapPosMv | [17 empty] | 2-32-07 |  | 2-47 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU62_LCO_TAP | 23KV工六二線(XU62) LCO TAP | FEEDER | D09/22/XU62/50N_51N |  |  |  | CDC | 442 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D09 | 斗工DS | 22 | 22kV | XU62 | XU62(23KV工六二線) |  | CB | [17 empty] | 1-16-00 |  | 1-22 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU62_CB | XU62(23KV工六二線) CB | FEEDER | D09/22/XU62/CB |  |  |  | CDC | 443 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | XU63 | 工六三線(XU63) |  | PHA | [17 empty] | 1-16-04 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU63_PHA | 23KV工六三線(XU63) 相間RY | FEEDER | D09/22/XU63/PHA |  |  |  | CDC | 444 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU63 | 工六三線(XU63) |  | GDA | [17 empty] | 1-16-05 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU63_GDA | 23KV工六三線(XU63) 接地RY | FEEDER | D09/22/XU63/GDA |  |  |  | CDC | 445 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU63 | 工六三線(XU63) 79RY |  | 79UL | [17 empty] | 2-31-00 |  | 2-30 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU63_79UL | 23KV工六三線(XU63) 79RY U/L | FEEDER | D09/22/XU63/79UL |  |  |  | CDC | 446 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 22 | 22kV | XU63_LCO | 工六三線(XU63) LCO |  | TapPosMv | [17 empty] | 2-32-08 |  | 2-48 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU63_LCO_TAP | 23KV工六三線(XU63) LCO TAP | FEEDER | D09/22/XU63/50N_51N |  |  |  | CDC | 447 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D09 | 斗工DS | 22 | 22kV | XU63 | XU63(23KV工六三線) |  | CB | [17 empty] | 1-16-03 |  | 1-23 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU63_CB | XU63(23KV工六三線) CB | FEEDER | D09/22/XU63/CB |  |  |  | CDC | 448 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | XU64 | 工六四線(XU64) |  | PHA | [17 empty] | 1-16-07 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU64_PHA | 23KV工六四線(XU64) 相間RY | FEEDER | D09/22/XU64/PHA |  |  |  | CDC | 449 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU64 | 工六四線(XU64) |  | GDA | [17 empty] | 1-17-00 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU64_GDA | 23KV工六四線(XU64) 接地RY | FEEDER | D09/22/XU64/GDA |  |  |  | CDC | 450 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU64 | 工六四線(XU64) 79RY |  | 79UL | [17 empty] | 2-31-01 |  | 2-31 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU64_79UL | 23KV工六四線(XU64) 79RY U/L | FEEDER | D09/22/XU64/79UL |  |  |  | CDC | 451 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 22 | 22kV | XU64_LCO | 工六四線(XU64) LCO |  | TapPosMv | [17 empty] | 2-32-09 |  | 2-49 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU64_LCO_TAP | 23KV工六四線(XU64) LCO TAP | FEEDER | D09/22/XU64/50N_51N |  |  |  | CDC | 452 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D09 | 斗工DS | 22 | 22kV | XU64 | XU64(23KV工六四線) |  | CB | [17 empty] | 1-16-06 |  | 1-28 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU64_CB | XU64(23KV工六四線) CB | FEEDER | D09/22/XU64/CB |  |  |  | CDC | 453 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | XU65 | 工六五線(XU65) |  | PHA | [17 empty] | 1-17-02 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU65_PHA | 23KV工六五線(XU65) 相間RY | FEEDER | D09/22/XU65/PHA |  |  |  | CDC | 454 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU65 | 工六五線(XU65) |  | GDA | [17 empty] | 1-17-03 | [7 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU65_GDA | 23KV工六五線(XU65) 接地RY | FEEDER | D09/22/XU65/GDA |  |  |  | CDC | 455 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | XU65 | 工六五線(XU65) 79RY |  | 79UL | [17 empty] | 2-31-02 |  | 2-32 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU65_79UL | 23KV工六五線(XU65) 79RY U/L | FEEDER | D09/22/XU65/79UL |  |  |  | CDC | 456 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 22 | 22kV | XU65_LCO | 工六五線(XU65) LCO |  | TapPosMv | [17 empty] | 2-35-10 |  | 2-4A | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU65_LCO_TAP | 23KV工六五線(XU65) LCO TAP | FEEDER | D09/22/XU65/50N_51N |  |  |  | CDC | 457 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D09 | 斗工DS | 22 | 22kV | XU65 | XU65(23KV工六五線) |  | CB | [17 empty] | 1-17-01 |  | 1-29 | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU65_CB | XU65(23KV工六五線) CB | FEEDER | D09/22/XU65/CB |  |  |  | CDC | 458 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 100 | TIE(100) |  | CB | [17 empty] | 1-12-02 |  | 1-17 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.100_CB | 100(TIE) CB | TIE | D09/22/100/CB |  |  |  | CDC | 459 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 100 | TIE(100) |  | 51A | [17 empty] | 1-12-03 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.100_51A | 23KV TIE(100) 51RY | TIE | D09/22/100/PHA |  |  |  | CDC | 460 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 100 | TIE(100) |  | 51NA | [17 empty] | 1-12-04 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.100_51NA | 23KV TIE(100) 51N RY | TIE | D09/22/100/GDA |  |  |  | CDC | 461 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [17 empty] | 1-06-03 |  | 1-0B | [5 empty] | 161KV_N | [8 empty] | 斗工DS.1500_CB | 1500(TIE) CB | TIE | D09/161/1500/CB |  |  |  | CDC | 462 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 1500 | TIE(1500) |  | 50A | [17 empty] | 1-06-04 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.1500_50A | 161KV TIE(1500) 50RY | TIE | D09/161/1500/50A |  |  |  | CDC | 463 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [16 empty] | 2-39-00 | 2-39-01 | 2-10 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1501_DS | 1501(TIE) DS | TIE | D09/161/1500/DS1 |  |  |  | CDC | 464 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [16 empty] | 2-39-02 | 2-39-03 | 2-11 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1502_DS | 1502(TIE) DS | TIE | D09/161/1500/DS2 |  |  |  | CDC | 465 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 0 |  | 200 | TIE(200) |  | CB | [17 empty] | 1-14-07 |  | 1-20 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.200_CB | 200(TIE) CB | TIE | D09/11/200/CB |  |  |  | CDC | 466 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 200 | TIE(200) |  | 51A | [17 empty] | 1-15-00 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.200_51A | 11KV TIE(200) 51RY | TIE | D09/11/200/PHA |  |  |  | CDC | 467 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 200 | TIE(200) |  | 51NA | [17 empty] | 1-15-01 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.200_51NA | 11KV TIE(200) 51N RY | TIE | D09/11/200/GDA |  |  |  | CDC | 468 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 300 | TIE(300) |  | CB | [17 empty] | 1-17-04 |  | 1-2A | [5 empty] | ADCS_N | [8 empty] | 斗工DS.300_CB | 300(TIE) CB | TIE | D09/22/300/CB |  |  |  | CDC | 469 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 300 | TIE(300) |  | 51A | [17 empty] | 1-17-05 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.300_51A | 23KV TIE(300) 51RY | TIE | D09/22/300/PHA |  |  |  | CDC | 470 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 300 | TIE(300) |  | 51NA | [17 empty] | 1-17-06 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.300_51NA | 23KV TIE(300) 51N RY | TIE | D09/22/300/GDA |  |  |  | CDC | 471 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 400 | TIE(400) |  | CB | [17 empty] | 1-1A-07 |  | 1-33 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.400_CB | 400(TIE) CB | TIE | D09/11/400/CB |  |  |  | CDC | 472 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 400 | TIE(400) |  | 51A | [17 empty] | 1-1B-00 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.400_51A | 11KV TIE(400) 51RY | TIE | D09/11/400/PHA |  |  |  | CDC | 473 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 400 | TIE(400) |  | 51NA | [17 empty] | 1-1B-01 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.400_51NA | 11KV TIE(400) 51N RY | TIE | D09/11/400/GDA |  |  |  | CDC | 474 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 390 | #1SSTR(390) |  | CB | [17 empty] | 1-15-02 |  | 1-18 | [5 empty] | 161KV_N | [8 empty] | 斗工DS.390_CB | 390(#1SSTR) CB | OTHER | D09/11/390/CB |  |  |  | CDC | 475 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 1SSTR | #1SSTR |  | 51A | [17 empty] | 1-15-03 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.#1SSTR_51A | #1SSTR 51RY | OTHER | D09/11/390/PHA |  |  |  | CDC | 476 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 1SSTR | #1SSTR |  | 51NA | [17 empty] | 1-15-04 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | D09/11/390/GDA |  |  |  | CDC | 477 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 490 | #2SSTR(490) |  | CB | [17 empty] | 1-18-02 |  | 1-27 | [5 empty] | 161KV_N | [8 empty] | 斗工DS.490_CB | 490(#2SSTR) CB | OTHER | D09/22/490/CB |  |  |  | CDC | 478 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 2SSTR | #2SSTR |  | 51A | [17 empty] | 1-18-03 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.#2SSTR_51A | #2SSTR 51RY | OTHER | D09/22/490/PHA |  |  |  | CDC | 479 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 2SSTR | #2SSTR |  | 51NA | [17 empty] | 1-18-04 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | D09/22/490/GDA |  |  |  | CDC | 480 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB | [17 empty] | 1-07-01 |  | 1-0C | [5 empty] | 161KV_N | [8 empty] | 斗工DS.1750_CB | 1750(#1DTR) CB | MTR | D09/161/1750/CB |  |  |  | CDC | 481 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 310 | #1DTR(310) |  | CB | [17 empty] | 1-07-07 |  | 1-10 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.310_CB | 310(#1DTR) CB | MTR | D09/22/310/CB |  |  |  | CDC | 482 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 320 | #1DTR(320) |  | CB | [17 empty] | 1-08-01 |  | 1-19 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.320_CB | 320(#1DTR) CB | MTR | D09/11/320/CB |  |  |  | CDC | 483 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 310 | #1DTR(310) |  | 51A | [17 empty] | 1-0B-03 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.310_51A | #1DTR二次側(310) 51RY | MTR | D09/22/310/51A |  |  |  | CDC | 484 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 320 | #1DTR(320) |  | 51A | [17 empty] | 1-0B-04 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.320_51A | #1DTR二次側(320) 51RY | MTR | D09/11/320/51A |  |  |  | CDC | 485 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 | [16 empty] | 2-39-04 | 2-39-05 | 2-12 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1751_DS | 1751(#1DTR) DS | MTR | D09/161/1750/DS1 |  |  |  | CDC | 486 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 | [16 empty] | 2-39-06 | 2-39-07 | 2-13 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1752_DS | 1752(#1DTR) DS | MTR | D09/161/1750/DS2 |  |  |  | CDC | 487 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB | [17 empty] | 1-08-03 |  | 1-0D | [5 empty] | 161KV_N | [8 empty] | 斗工DS.1760_CB | 1760(#2DTR) CB | MTR | D09/161/1760/CB |  |  |  | CDC | 488 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 | [16 empty] | 2-39-08 | 2-39-09 | 2-14 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1761_DS | 1761(#2DTR) DS | MTR | D09/161/1760/DS1 |  |  |  | CDC | 489 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 | [16 empty] | 2-39-10 | 2-39-11 | 2-15 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1762_DS | 1762(#2DTR) DS | MTR | D09/161/1760/DS2 |  |  |  | CDC | 490 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1611BUS | #1BUS |  | VUA | [17 empty] | 2-33-09 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | D09/161/1BUS/BUS_VUA |  |  |  | CDC | 491 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1611BUS | #1BUS |  | 87A | [17 empty] | 1-06-05 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | D09/161/1BUS/87A |  |  |  | CDC | 492 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1611BUS | #1BUS |  | 87UL | [17 empty] | 1-31-06 |  | 1-66 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | D09/161/1BUS/87UL |  |  |  | CDC | 493 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 161 | 161kV | 1612BUS | #2BUS |  | VUA | [17 empty] | 2-33-10 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | D09/161/2BUS/BUS_VUA |  |  |  | CDC | 494 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1612BUS | #2BUS |  | 87A | [17 empty] | 1-06-06 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | D09/161/2BUS/87A |  |  |  | CDC | 495 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1612BUS | #2BUS |  | 87UL | [17 empty] | 1-31-07 |  | 1-67 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | D09/161/2BUS/87UL |  |  |  | CDC | 496 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 22 | 22kV | 11_ | 11/ |  | CBA | [17 empty] | 2-34-02 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | D09/0/ComPoint/FDR_CBA |  |  |  | CDC | 497 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | 11_ | 11/ |  | CBF | [17 empty] | 2-34-03 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | D09/0/ComPoint/FDR_CBF |  |  |  | CDC | 498 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV |  |  |  | CBA | [17 empty] | 2-34-00 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.161KV_CBA | 161KV斷路器重故障 | OTHER | D09/161/ComPoint/CBA |  |  |  | CDC | 499 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV |  |  |  | CBF | [17 empty] | 2-34-01 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | D09/161/ComPoint/CBF |  |  |  | CDC | 500 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV |  |  |  | OSCA | [17 empty] | 1-07-00 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.161KV_OSCA | 161KV示波器啟動警報 | OTHER | D09/161/ComPoint/OSCA |  |  |  | CDC | 501 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | LINE | LINE |  | RCA | [17 empty] | 1-06-07 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | D09/161/ComPoint/RCA |  |  |  | CDC | 502 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV |  |  |  | COMT | [17 empty] | 2-33-15 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.161空壓機COMT | 161KV空壓機運轉超時警報 | OTHER | D09/161/ComPoint/COMT |  |  |  | CDC | 503 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | _SC | 23/ SC |  | 60A | [17 empty] | 2-34-06 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.23KV_SC_60A | 23/11KV SC 60A | OTHER | D09/0/ComPoint/FDR_60A |  |  |  | CDC | 504 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.RTU_S/L | RTU SUPY/LOCAL | OTHER | D09/0/RTU/RTU_R_L |  |  |  | CDC | 505 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D09 | 斗工DS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.TEST_CB | TEST CB | OTHER | D09/0/RTU/Test_CB |  |  |  | CDC | 506 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  |  |  |  | Fire1 | [17 empty] | 2-32-10 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | D09/0/StaDev/Fire1 |  |  |  | CDC | 507 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  |  |  |  | OPA | [17 empty] | 2-35-01 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | D09/161/ComPoint/OPA |  |  |  | CDC | 508 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  |  |  |  | 25PFA | [17 empty] | 2-34-15 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER | D09/0/ComPoint/25PFA |  |  |  | CDC | 509 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  |  |  |  | 25TA | [17 empty] | 2-34-14 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | D09/0/ComPoint/25TA |  |  |  | CDC | 510 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  |  |  |  | SUBA | [17 empty] | 2-34-04 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.其他重故障 | 變電所內其他重故障 | OTHER | D09/0/StaDev/PSA |  |  |  | CDC | 511 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  |  |  |  | SUBF | [17 empty] | 2-34-05 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.其他輕故障 | 變電所內其他輕故障 | OTHER | D09/0/StaDev/PSF |  |  |  | CDC | 512 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  |  |  |  | ACB1 | [17 empty] | 2-33-06 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | D09/0/StaDev/ACB1 |  |  |  | CDC | 513 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
D09 | 斗工DS | 0 |  |  |  |  | ACB2 | [17 empty] | 2-33-07 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | D09/0/StaDev/ACB2 |  |  |  | CDC | 514 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
D09 | 斗工DS | 0 |  |  |  |  | ACBA | [17 empty] | 2-34-13 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.所內電源ACBA | 所內電源故障警報 | OTHER | D09/0/StaDev/ACBA |  |  |  | CDC | 515 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  |  |  |  | STUV | [17 empty] | 2-33-08 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | D09/0/StaDev/STUV |  |  |  | CDC | 516 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  |  |  |  | CHG1 | [17 empty] | 2-33-12 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | D09/0/StaDev/CHG1 |  |  |  | CDC | 517 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  |  |  |  | DCA | [17 empty] | 2-33-11 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.直流電源DCA | 直流電源故障警報 | OTHER | D09/0/StaDev/DCA |  |  |  | CDC | 518 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  |  |  |  | DCE | [17 empty] | 2-33-14 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.直流電源DCE | 直流電源接地故障警報 | OTHER | D09/0/StaDev/DCE |  |  |  | CDC | 519 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  |  |  |  | OilLeak | [17 empty] | 2-34-11 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.洩油池水位警報 | 洩油池水位警報 | OTHER | D09/0/StaDev/OilLeak1 |  |  |  | CDC | 520 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  |  |  |  | CHG2 | [17 empty] | 2-33-13 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | D09/0/StaDev/CHG2 |  |  |  | CDC | 521 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  |  |  |  | CommACF | [17 empty] | 2-34-07 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | D09/0/StaDev/CommACF |  |  |  | CDC | 522 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  |  |  |  | Burglar1 | [17 empty] | 2-32-13 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | D09/0/StaDev/Burglar1 |  |  |  | CDC | 523 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  |  |  |  | Door1 | [17 empty] | 2-33-00 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.無人化門禁(1) | 無人化門禁(1)建築物大門 | OTHER | D09/0/StaDev/Door1 |  |  |  | CDC | 524 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  |  |  |  | Door2 | [17 empty] | 2-33-01 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.無人化門禁(2) | 無人化門禁(2)控制室大門 | OTHER | D09/0/StaDev/Door2 |  |  |  | CDC | 525 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  |  |  |  | Door3 | [17 empty] | 2-33-02 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.無人化門禁(3) | 無人化門禁(3) | OTHER | D09/0/StaDev/Door3 |  |  |  | CDC | 526 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  |  |  |  | Lights1 | [17 empty] | 2-33-03 |  | 2-1E | [5 empty] | ADCS_N | [8 empty] | 斗工DS.開關場照明(A) | 開關場照明(A) | OTHER | D09/0/StaDev/Lights1 |  |  |  | CDC | 527 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D09 | 斗工DS | 0 |  |  |  |  | Lights2 | [17 empty] | 2-33-04 |  | 2-1F | [5 empty] | ADCS_N | [8 empty] | 斗工DS.開關場照明(B) | 開關場照明(B) | OTHER | D09/0/StaDev/Lights2 |  |  |  | CDC | 528 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D09 | 斗工DS | 0 |  | 1550 | 富喬線(1550) |  | MDARF | [17 empty] | 1-33-04 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.1550_MDARF | 1550MDAR RY故障 | OTHER | D09/161/1550/1A5Other |  |  |  | CDC | 529 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 1550 | 富喬線(1550) |  | TONEF | [17 empty] | 1-33-05 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.1550_TONEF | 1550TONE訊號不良 | OTHER | D09/161/1550/85CFA |  |  |  | CDC | 530 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 310 | #1DTR(310) |  | PHA2 | [17 empty] | 1-08-00 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.310_PHA2 | 310開關箱IED RY PHA | OTHER | D09/22/310/PHA |  |  |  | CDC | 531 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 320 | #1DTR(320) |  | PHA2 | [17 empty] | 1-08-02 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.320_PHA2 | 320開關箱IED RY PHA | OTHER | D09/11/320/PHA |  |  |  | CDC | 532 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  |  |  |  | 空調機故障 | [17 empty] | 2-33-05 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.空調機故障 | 空調機故障或電源跳脫 | OTHER | D09/0/StaDev/AIRCON |  |  |  | CDC | 533 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | NORMAL/FAULT | NORMAL
D09 | 斗工DS | 0 |  |  |  |  | 水位警報(1) | [17 empty] | 2-35-02 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.水位警報(1) | 地下室水位警報(1) | OTHER | D09/0/StaDev/Water1 |  |  |  | CDC | 534 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  |  |  |  | 水位警報(2) | [17 empty] | 2-35-03 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.水位警報(2) | 地下室水位警報(2) | OTHER | D09/0/StaDev/Water2 |  |  |  | CDC | 535 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 81RY | XU26 |  | A/S(1) | [17 empty] | 2-10-05 |  | 2-1B | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.81RY_A/S(1) | XU26 XU27低頻電驛動作/復歸 | OTHER | D09/0/ComPoint/81AS2 |  |  |  | CDC | 536 | GENERICDIPoint | DS036_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
D09 | 斗工DS | 0 |  | 1500TIE | 1500 |  | 50SA | [17 empty] | 2-35-05 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | D09/161/1500/50SA |  |  |  | CDC | 537 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | TEST/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 1DTR | #1DTR |  | 51A | [17 empty] | 1-07-05 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.#1DTR_51A | #1DTR 51RY | MTR | D09/161/1750/PHA |  |  |  | CDC | 538 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 1DTR | #1DTR |  | 51NA | [17 empty] | 1-07-06 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.#1DTR_51NA | #1DTR 51N RY | MTR | D09/161/1750/GDA |  |  |  | CDC | 539 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 1DTR | #1DTR |  | 51ZA | [17 empty] | 1-07-04 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | D09//1DTR/51ZA |  |  |  | CDC | 540 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 1DTR | #1DTR |  | 87A | [17 empty] | 1-07-02 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.#1DTR_87A | #1DTR 87RY | MTR | D09//1DTR/87A |  |  |  | CDC | 541 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 1DTR | #1DTR |  | 96PA | [17 empty] | 1-07-03 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | D09//1DTR/96PA |  |  |  | CDC | 542 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 1DTR | #1DTR |  | 96D | [17 empty] | 1-0C-04 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.#1DTR_96D | #1DTR 96D RY | MTR | D09//1DTR/96D |  |  |  | CDC | 543 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 1DTR | #1DTR |  | 96P | [17 empty] | 1-0C-03 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.#1DTR_96P | #1DTR 96P RY | MTR | D09//1DTR/96P |  |  |  | CDC | 544 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 1DTR | #1DTR |  | 63Q | [17 empty] | 1-0C-07 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.#1DTR_63Q | #1DTR 63Q RY | MTR | D09//1DTR/63Q |  |  |  | CDC | 545 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 1DTR | #1DTR |  | 96B1 | [17 empty] | 1-0C-05 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | D09//1DTR/96B1 |  |  |  | CDC | 546 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 1DTR | #1DTR |  | 96B2 | [17 empty] | 1-0C-06 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | D09//1DTR/96B2 |  |  |  | CDC | 547 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 1DTR | #1DTR |  | TRA | [17 empty] | 1-31-11 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.#1DTR_TRA | #1DTR 重故障 | MTR | D09//1DTR(A)/TRA |  |  |  | CDC | 548 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 1DTR | #1DTR |  | TRF | [17 empty] | 1-31-12 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.#1DTR_TRF | #1DTR 輕故障 | MTR | D09//1DTR(A)/TRF |  |  |  | CDC | 549 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 1DTR(A) | #1DTR(A) |  | SupLocal | [17 empty] | 1-31-09 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | D09//1DTR(A)/SupLocal |  |  |  | CDC | 550 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D09 | 斗工DS | 0 |  | 1DTR(A) | #1DTR(A) |  | A_M | [17 empty] | 1-31-10 |  | 1-5C | [5 empty] | ADCS_N | [8 empty] | 斗工DS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | D09//1DTR(A)/Tap Chan |  |  |  | CDC | 551 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D09 | 斗工DS | 0 |  | 1DTR(B) | #1DTR(B) |  | SupLocal | [17 empty] | 1-31-13 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | D09//1DTR(B)/SupLocal |  |  |  | CDC | 552 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D09 | 斗工DS | 0 |  | 1DTR(B) | #1DTR(B) |  | A_M | [17 empty] | 1-31-14 |  | 1-5E | [5 empty] | ADCS_N | [8 empty] | 斗工DS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | D09//1DTR(B)/Tap Chan |  |  |  | CDC | 553 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D09 | 斗工DS | 0 |  | 2DTR | #2DTR |  | 51A | [17 empty] | 1-08-07 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.#2DTR_51A | #2DTR 51RY | MTR | D09/161/1760/PHA |  |  |  | CDC | 554 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 2DTR | #2DTR |  | 51NA | [17 empty] | 1-09-00 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.#2DTR_51NA | #2DTR 51N RY | MTR | D09/161/1760/GDA |  |  |  | CDC | 555 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 2DTR | #2DTR |  | 51ZA | [17 empty] | 1-08-06 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | D09//2DTR/51ZA |  |  |  | CDC | 556 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 2DTR | #2DTR |  | 87A | [17 empty] | 1-08-04 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.#2DTR_87A | #2DTR 87RY | MTR | D09//2DTR/87A |  |  |  | CDC | 557 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 2DTR | #2DTR |  | 96PA | [17 empty] | 1-08-05 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | D09//2DTR/96PA |  |  |  | CDC | 558 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 2DTR | #2DTR |  | 96D | [17 empty] | 1-0D-01 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.#2DTR_96D | #2DTR 96D RY | MTR | D09//2DTR/96D |  |  |  | CDC | 559 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 2DTR | #2DTR |  | 96P | [17 empty] | 1-0D-00 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.#2DTR_96P | #2DTR 96P RY | MTR | D09//2DTR/96P |  |  |  | CDC | 560 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 2DTR | #2DTR |  | 63Q | [17 empty] | 1-0D-04 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.#2DTR_63Q | #2DTR 63Q RY | MTR | D09//2DTR/63Q |  |  |  | CDC | 561 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 2DTR | #2DTR |  | 96B1 | [17 empty] | 1-0D-02 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | D09//2DTR/96B1 |  |  |  | CDC | 562 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 2DTR | #2DTR |  | 96B2 | [17 empty] | 1-0D-03 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | D09//2DTR/96B2 |  |  |  | CDC | 563 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 2DTR | #2DTR |  | TRA | [17 empty] | 1-32-02 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.#2DTR_TRA | #2DTR 重故障 | MTR | D09//2DTR(A)/TRA |  |  |  | CDC | 564 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 2DTR | #2DTR |  | TRF | [17 empty] | 1-32-03 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.#2DTR_TRF | #2DTR 輕故障 | MTR | D09//2DTR(A)/TRF |  |  |  | CDC | 565 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 2DTR(A) | #2DTR(A) |  | SupLocal | [17 empty] | 1-32-00 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | D09//2DTR(A)/SupLocal |  |  |  | CDC | 566 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D09 | 斗工DS | 0 |  | 2DTR(A) | #2DTR(A) |  | A_M | [17 empty] | 1-32-01 |  | 1-60 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | D09//2DTR(A)/Tap Chan |  |  |  | CDC | 567 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D09 | 斗工DS | 0 |  | 2DTR(B) | #2DTR(B) |  | SupLocal | [17 empty] | 1-32-04 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | D09//2DTR(B)/SupLocal |  |  |  | CDC | 568 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D09 | 斗工DS | 0 |  | 2DTR(B) | #2DTR(B) |  | A_M | [17 empty] | 1-32-05 |  | 1-62 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | D09//2DTR(B)/Tap Chan |  |  |  | CDC | 569 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D09 | 斗工DS | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 1-14-04 |  | 1-1A | [5 empty] | ADCS_N | [8 empty] | 斗工DS.220_CB | 220(11KV #2SC) CB | SC | D09/11/220/CB |  |  |  | CDC | 570 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M | [17 empty] | 2-30-12 |  | 2-2C | [5 empty] | ADCS_N | [8 empty] | 斗工DS.220_A/M | 11KV #2SC 乏控器 A/M | SC | D09/11/220/SC_A_M |  |  |  | CDC | 571 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D09 | 斗工DS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 1-14-05 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.220_SCA | 11KV #2SC 51,51N RY | SC | D09/11/220/SCA |  |  |  | CDC | 572 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 1-14-06 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | D09/11/220/UVA |  |  |  | CDC | 573 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | 220 | #2SC(220) |  | LBS | [17 empty] | 1-1F-07 |  | 1-43 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.220_LBS | 220(11KV #2SC) LBS | SC | D09/11/220/LBS |  |  |  | CDC | 574 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | 220_LBS | #2SC |  | SC_A_M | [17 empty] | 2-30-13 |  | 2-2D | [5 empty] | ADCS_N | [8 empty] | 斗工DS.220_LBS_A/M | 11KV #2SC LBS 乏控器 A/M | SC | D09/11/220/1A5A_M |  |  |  | CDC | 575 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D09 | 斗工DS | 22 | 22kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-11-07 |  | 1-11 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.210_CB | 210(23KV #1SC) CB | SC | D09/22/210/CB |  |  |  | CDC | 576 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | 210 | #1SC(210) |  | SC_A_M | [17 empty] | 2-30-05 |  | 2-25 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.210_A/M | 23KV #1SC 乏控器 A/M | SC | D09/22/210/SC_A_M |  |  |  | CDC | 577 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D09 | 斗工DS | 22 | 22kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-12-00 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.210_SCA | 23KV #1SC 51,51N RY | SC | D09/22/210/SCA |  |  |  | CDC | 578 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-12-01 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.210_UVA | 23KV #1SC 27RY(欠壓) | SC | D09/22/210/UVA |  |  |  | CDC | 579 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 330A2 | #2DTR |  | CB | [17 empty] | 1-09-03 |  | 1-26 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.330A2_CB | 330A2(#2DTR) CB | MTR | D09/22/330A2/CB |  |  |  | CDC | 580 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 330A1 | #2DTR |  | CB | [17 empty] | 1-09-01 |  | 1-25 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.330A1_CB | 330A1(#2DTR) CB | MTR | D09/22/330A1/CB |  |  |  | CDC | 581 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 340B1 | #2DTR |  | CB | [17 empty] | 1-09-07 |  | 1-2D | [5 empty] | ADCS_N | [8 empty] | 斗工DS.340B1_CB | 340B1(#2DTR) CB | MTR | D09/11/340B1/CB |  |  |  | CDC | 582 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 340B2 | #2DTR |  | CB | [17 empty] | 1-09-05 |  | 1-2E | [5 empty] | ADCS_N | [8 empty] | 斗工DS.340B2_CB | 340B2(#2DTR) CB | MTR | D09/11/340B2/CB |  |  |  | CDC | 583 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 330A2 | #2DTR二次側(330A2) |  | 51A | [17 empty] | 1-0B-06 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.330A2_51A | #2DTR二次側(330A2) 51RY | MTR | D09/22/330A2/51A |  |  |  | CDC | 584 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 330A1 | #2DTR二次側(330A1) |  | 51A | [17 empty] | 1-0B-05 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.330A1_51A | #2DTR二次側(330A1) 51RY | MTR | D09/22/330A1/51A |  |  |  | CDC | 585 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 340B1 | #2DTR二次側(340B1) |  | 51A | [17 empty] | 1-0B-07 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.340B1_51A | #2DTR二次側(340B1) 51RY | MTR | D09/22/340B1/51A |  |  |  | CDC | 586 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 340B2 | #2DTR二次側(340B2) |  | 51A | [17 empty] | 1-0C-00 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.340B2_51A | #2DTR二次側(340B2) 51RY | MTR | D09/22/340B2/51A |  |  |  | CDC | 587 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | 240 | #4SC(240) |  | CB | [17 empty] | 1-1A-04 |  | 1-2F | [5 empty] | ADCS_N | [8 empty] | 斗工DS.240_CB | 240(11KV #4SC) CB | SC | D09/11/240/CB |  |  |  | CDC | 588 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | 240 | #4SC(240) |  | SC_A_M | [17 empty] | 2-31-10 |  | 2-3A | [5 empty] | ADCS_N | [8 empty] | 斗工DS.240_A/M | 11KV #4SC 乏控器 A/M | SC | D09/11/240/SC_A_M |  |  |  | CDC | 589 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D09 | 斗工DS | 11 | 11kV | 240 | #4SC(240) |  | SCA | [17 empty] | 1-1A-05 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.240_SCA | 11KV #4SC 51,51N RY | SC | D09/11/240/SCA |  |  |  | CDC | 590 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | 240 | #4SC(240) |  | UVA | [17 empty] | 1-1A-06 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.240_UVA | 11KV #4SC 27RY(欠壓) | SC | D09/11/240/UVA |  |  |  | CDC | 591 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV | 240 | #4SC(240) |  | LBS | [17 empty] | 2-10-01 |  | 1-45 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.240_LBS | 240(11KV #4SC) LBS | SC | D09/11/240/LBS |  |  |  | CDC | 592 | GENERICDIPoint | DS036_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 11 | 11kV | 240_LBS | #4SC |  | SC_A_M | [17 empty] | 2-31-11 |  | 2-3B | [5 empty] | ADCS_N | [8 empty] | 斗工DS.240_LBS_A/M | 11KV #4SC LBS 乏控器 A/M | SC | D09/11/230/1A5A_M |  |  |  | CDC | 593 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D09 | 斗工DS | 22 | 22kV | 230 | #3SC(230) |  | CB | [17 empty] | 1-17-07 |  | 1-24 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.230_CB | 230(23KV #3SC) CB | SC | D09/22/230/CB |  |  |  | CDC | 594 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 22 | 22kV | 230 | #3SC(230) |  | SC_A_M | [17 empty] | 2-31-03 |  | 2-33 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.230_A/M | 23KV #3SC 乏控器 A/M | SC | D09/22/230/SC_A_M |  |  |  | CDC | 595 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D09 | 斗工DS | 22 | 22kV | 230 | #3SC(230) |  | SCA | [17 empty] | 1-18-00 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.230_SCA | 23KV #3SC 51,51N RY | SC | D09/22/230/SCA |  |  |  | CDC | 596 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 22 | 22kV | 230 | #3SC(230) |  | UVA | [17 empty] | 1-18-01 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.230_UVA | 23KV #3SC 27RY(欠壓) | SC | D09/22/230/UVA |  |  |  | CDC | 597 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 330A1 | 330A1開關箱IED |  | PHA2 | [17 empty] | 1-09-02 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.330A1_PHA2 | 330A1開關箱IED RY PHA | OTHER | D09/22/330A1/PHA |  |  |  | CDC | 598 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 330A2 | 330A2開關箱IED |  | PHA2 | [17 empty] | 1-09-04 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.330A2_PHA2 | 330A2開關箱IED RY PHA | OTHER | D09/22/330A2/PHA |  |  |  | CDC | 599 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 340B1 | 340B1開關箱IED |  | PHA2 | [17 empty] | 1-0A-00 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.340B1_PHA2 | 340B1開關箱IED RY PHA | OTHER | D09/22/340B1/PHA |  |  |  | CDC | 600 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 340B2 | 340B2開關箱IED |  | PHA2 | [17 empty] | 1-09-06 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.340B2_PHA2 | 340B2開關箱IED RY PHA | OTHER | D09/22/340B2/PHA |  |  |  | CDC | 601 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  |  |  |  | 通信機房溫度 | [17 empty] | 2-34-10 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.通信機房溫度 | 通信機房溫度警報 | OTHER | D09/0/StaDev/R_Temp |  |  |  | CDC | 602 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1570 | 備用線(1570) |  | PHA | [17 empty] | 1-03-04 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.1570_PHA | 備用線(1570) 相間RY | LINE161 |  |  |  |  | CDC | 603 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1570 | 備用線(1570) |  | GDA | [17 empty] | 1-03-05 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.1570_GDA | 備用線(1570) 接地RY | LINE161 |  |  |  |  | CDC | 604 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1570 | 備用線(1570) |  | 87A | [17 empty] | 1-03-02 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.1570_87A | 備用線(1570) 87RY | LINE161 |  |  |  |  | CDC | 605 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1570 | 備用線(1570) |  | 87UL | [17 empty] | 1-30-12 |  | 1-52 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1570_87UL | 備用線(1570) 87RY U/L | LINE161 |  |  |  |  | CDC | 606 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 161 | 161kV | 1570 | 備用線(1570) |  | CB | [17 empty] | 1-03-01 |  | 1-06 | [5 empty] | 161KV_N | [8 empty] | 斗工DS.1570_CB | 1570(備用線) CB | LINE161 |  |  |  |  | CDC | 607 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 161 | 161kV | 1570 | 備用線(1570) |  | 79UL | [17 empty] | 1-30-13 |  | 1-53 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1570_79UL | 備用線(1570) 79RY U/L | LINE161 |  |  |  |  | CDC | 608 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 161 | 161kV | 1570 | 備用線(1570) |  | DS1 | 1571 | [16 empty] | 2-36-08 | 2-36-09 | 1-7C | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1571_DS | 1571(備用線) DS | LINE161 |  |  |  |  | CDC | 609 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1570 | 備用線(1570) |  | DS2 | 1572 | [16 empty] | 2-36-10 | 2-36-11 | 1-7D | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1572_DS | 1572(備用線) DS | LINE161 |  |  |  |  | CDC | 610 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 161 | 161kV | 1570 | 備用線(1570) |  | DS3 | 1573 | [16 empty] | 2-36-12 | 2-36-13 | 1-7E | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1573_DS | 1573(備用線) DS | LINE161 |  |  |  |  | CDC | 611 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1570 | 備用線(1570) |  | E3 | 1573E | [16 empty] | 2-36-14 | 2-36-15 | 1-7F | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1573E_ES | 1573E(備用線) ES | LINE161 |  |  |  |  | CDC | 612 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 161 | 161kV | 1580 | 斗六斗工線(1580) |  | PHA | [17 empty] | 1-04-01 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.1580_PHA | 斗六斗工線(1580) 相間RY | LINE161 |  |  |  |  | CDC | 613 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1580 | 斗六斗工線(1580) |  | GDA | [17 empty] | 1-04-02 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.1580_GDA | 斗六斗工線(1580) 接地RY | LINE161 |  |  |  |  | CDC | 614 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1580 | 斗六斗工線(1580) |  | 87A | [17 empty] | 1-03-07 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.1580_87A | 斗六斗工線(1580) 87RY | LINE161 |  |  |  |  | CDC | 615 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1580 | 斗六斗工線(1580) |  | 87UL | [17 empty] | 1-30-14 |  | 1-54 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1580_87UL | 斗六斗工線(1580) 87RY U/L | LINE161 |  |  |  |  | CDC | 616 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 161 | 161kV | 1580 | 斗六斗工線(1580) |  | CB | [17 empty] | 1-03-06 |  | 1-07 | [5 empty] | 161KV_N | [8 empty] | 斗工DS.1580_CB | 1580(斗六斗工線) CB | LINE161 |  |  |  |  | CDC | 617 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 161 | 161kV | 1580 | 斗六斗工線(1580) |  | 79UL | [17 empty] | 1-30-15 |  | 1-55 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1580_79UL | 斗六斗工線(1580) 79RY U/L | LINE161 |  |  |  |  | CDC | 618 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 161 | 161kV | 1580 | 斗六斗工線(1580) |  | DS1 | 1581 | [16 empty] | 2-37-00 | 2-37-01 | 2-00 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1581_DS | 1581(斗六斗工線) DS | LINE161 |  |  |  |  | CDC | 619 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 161 | 161kV | 1580 | 斗六斗工線(1580) |  | DS2 | 1582 | [16 empty] | 2-37-02 | 2-37-03 | 2-01 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1582_DS | 1582(斗六斗工線) DS | LINE161 |  |  |  |  | CDC | 620 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1580 | 斗六斗工線(1580) |  | DS3 | 1583 | [16 empty] | 2-37-04 | 2-37-05 | 2-02 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1583_DS | 1583(斗六斗工線) DS | LINE161 |  |  |  |  | CDC | 621 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1580 | 斗六斗工線(1580) |  | E3 | 1583E | [16 empty] | 2-37-06 | 2-37-07 | 2-03 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1583E_ES | 1583E(斗六斗工線) ES | LINE161 |  |  |  |  | CDC | 622 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 161 | 161kV | 1610 | 榴中斗工一路(1610) |  | PHA | [17 empty] | 1-04-06 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.1610_PHA | 榴中斗工一路(1610) 相間RY | LINE161 | D09/161/1610/PHA |  |  |  | CDC | 623 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1610 | 榴中斗工一路(1610) |  | GDA | [17 empty] | 1-04-07 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.1610_GDA | 榴中斗工一路(1610) 接地RY | LINE161 | D09/161/1610/GDA |  |  |  | CDC | 624 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1610 | 榴中斗工一路(1610) |  | 87A | [17 empty] | 1-04-04 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.1610_87A | 榴中斗工一路(1610) 87RY | LINE161 | D09/161/1610/87A |  |  |  | CDC | 625 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1610 | 榴中斗工一路(1610) |  | 87UL | [17 empty] | 1-31-00 |  | 1-56 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1610_87UL | 榴中斗工一路(1610) 87RY U/L | LINE161 | D09/161/1610/87UL |  |  |  | CDC | 626 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 161 | 161kV | 1610 | 榴中斗工一路(1610) |  | CB | [17 empty] | 1-04-03 |  | 1-08 | [5 empty] | 161KV_N | [8 empty] | 斗工DS.1610_CB | 1610(榴中斗工一路) CB | LINE161 | D09/161/1610/CB |  |  |  | CDC | 627 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 161 | 161kV | 1610 | 榴中斗工一路(1610) |  | 79UL | [17 empty] | 1-31-01 |  | 1-57 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1610_79UL | 榴中斗工一路(1610) 79RY U/L | LINE161 | D09/161/1610/79UL |  |  |  | CDC | 628 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 161 | 161kV | 1610 | 榴中斗工一路(1610) |  | DS1 | 1611 | [16 empty] | 2-37-08 | 2-37-09 | 2-04 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1611_DS | 1611(榴中斗工一路) DS | LINE161 | D09/161/1610/DS1 |  |  |  | CDC | 629 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1610 | 榴中斗工一路(1610) |  | DS2 | 1612 | [16 empty] | 2-37-10 | 2-37-11 | 2-05 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1612_DS | 1612(榴中斗工一路) DS | LINE161 | D09/161/1610/DS2 |  |  |  | CDC | 630 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 161 | 161kV | 1610 | 榴中斗工一路(1610) |  | DS3 | 1613 | [16 empty] | 2-37-12 | 2-37-13 | 2-06 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1613_DS | 1613(榴中斗工一路) DS | LINE161 | D09/161/1610/DS3 |  |  |  | CDC | 631 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1610 | 榴中斗工一路(1610) |  | E3 | 1613E | [16 empty] | 2-37-14 | 2-37-15 | 2-07 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1613E_ES | 1613E(榴中斗工一路) ES | LINE161 | D09/161/1610/ES3 |  |  |  | CDC | 632 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 161 | 161kV | 1620 | 榴中斗工二路(1620) |  | PHA | [17 empty] | 1-05-03 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.1620_PHA | 榴中斗工二路(1620) 相間RY | LINE161 | D09/161/1620/PHA |  |  |  | CDC | 633 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1620 | 榴中斗工二路(1620) |  | GDA | [17 empty] | 1-05-04 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.1620_GDA | 榴中斗工二路(1620) 接地RY | LINE161 | D09/161/1620/GDA |  |  |  | CDC | 634 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1620 | 榴中斗工二路(1620) |  | 87A | [17 empty] | 1-05-01 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.1620_87A | 榴中斗工二路(1620) 87RY | LINE161 | D09/161/1620/87A |  |  |  | CDC | 635 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1620 | 榴中斗工二路(1620) |  | 87UL | [17 empty] | 1-31-02 |  | 1-58 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1620_87UL | 榴中斗工二路(1620) 87RY U/L | LINE161 | D09/161/1620/87UL |  |  |  | CDC | 636 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 161 | 161kV | 1620 | 榴中斗工二路(1620) |  | CB | [17 empty] | 1-05-00 |  | 1-09 | [5 empty] | 161KV_N | [8 empty] | 斗工DS.1620_CB | 1620(榴中斗工二路) CB | LINE161 | D09/161/1620/CB |  |  |  | CDC | 637 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 161 | 161kV | 1620 | 榴中斗工二路(1620) |  | 79UL | [17 empty] | 1-31-03 |  | 1-59 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1620_79UL | 榴中斗工二路(1620) 79RY U/L | LINE161 | D09/161/1620/79UL |  |  |  | CDC | 638 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 161 | 161kV | 1620 | 榴中斗工二路(1620) |  | DS1 | 1621 | [16 empty] | 2-38-00 | 2-38-01 | 2-08 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1621_DS | 1621(榴中斗工二路) DS | LINE161 | D09/161/1620/DS1 |  |  |  | CDC | 639 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 161 | 161kV | 1620 | 榴中斗工二路(1620) |  | DS2 | 1622 | [16 empty] | 2-38-02 | 2-38-03 | 2-09 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1622_DS | 1622(榴中斗工二路) DS | LINE161 | D09/161/1620/DS2 |  |  |  | CDC | 640 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1620 | 榴中斗工二路(1620) |  | DS3 | 1623 | [16 empty] | 2-38-04 | 2-38-05 | 2-0A | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1623_DS | 1623(榴中斗工二路) DS | LINE161 | D09/161/1620/DS3 |  |  |  | CDC | 641 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D09 | 斗工DS | 161 | 161kV | 1620 | 榴中斗工二路(1620) |  | E3 | 1623E | [16 empty] | 2-38-06 | 2-38-07 | 2-0B | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1623E_ES | 1623E(榴中斗工二路) ES | LINE161 | D09/161/1620/ES3 |  |  |  | CDC | 642 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D09 | 斗工DS | 0 |  | 1570 | 備用線(1570) |  | 87LA | [17 empty] | 1-33-06 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.1570_87LA | 備用線(1570) 數位電驛故障 | OTHER |  |  |  |  | CDC | 643 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 1570 | 備用線(1570) |  | 87LCFA | [17 empty] | 1-33-07 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.1570_87LCFA | 備用線(1570) 87L通訊故障 | OTHER |  |  |  |  | CDC | 644 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 1580 | 斗六斗工線(1580) |  | 87LA | [17 empty] | 1-33-08 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.1580_87LA | 1580 數位電驛故障 | OTHER |  |  |  |  | CDC | 645 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 1580 | 斗六斗工線(1580) |  | 87LCFA | [17 empty] | 1-33-09 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.1580_87LCFA | 1580 87L通訊故障 | OTHER |  |  |  |  | CDC | 646 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 1610 | 榴中斗工一路(1610) |  | 87LA | [17 empty] | 1-33-10 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.1610_87LA | 1610 數位電驛故障 | OTHER | D09/161/1610/87C_LA |  |  |  | CDC | 647 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 1610 | 榴中斗工一路(1610) |  | 87LCFA | [17 empty] | 1-33-11 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.1610_87LCFA | 1610 87L通訊故障 | OTHER | D09/161/1610/87CFA |  |  |  | CDC | 648 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 1620 | 榴中斗工二路(1620) |  | 87LA | [17 empty] | 1-33-12 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.1620_87LA | 1620 數位電驛故障 | OTHER | D09/161/1620/87C_LA |  |  |  | CDC | 649 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 1620 | 榴中斗工二路(1620) |  | 87LCFA | [17 empty] | 1-33-13 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.1620_87LCFA | 1620 87L通訊故障 | OTHER | D09/161/1620/87CFA |  |  |  | CDC | 650 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV |  |  |  | OSCF | [17 empty] | 2-35-06 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | D09/161/ComPoint/OSCF |  |  |  | CDC | 651 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 81RY | 81RY |  | A/S(2) | [17 empty] | 2-10-04 |  | 2-1A | [5 empty] | DDCS1_1 | [8 empty] | 斗工DS.81RY_A/S(2) | XU(36_37_38_28_29_30)81RY動作 | OTHER | D09/0/ComPoint/81AS1 |  |  |  | CDC | 652 | GENERICDIPoint | DS036_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
D09 | 斗工DS | 161 | 161kV | 1530 | 嘉民斗工紅線(1530) |  | 87A | [17 empty] | 1-02-00 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.1530_87A | 嘉民斗工紅線(1530) 87RY | LINE161 | D09/161/1530/87A |  |  |  | CDC | 653 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1530 | 嘉民斗工紅線(1530) |  | 87UL | [17 empty] | 1-30-08 |  | 1-4E | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1530_87UL | 嘉民斗工紅線(1530) 87RY U/L | LINE161 | D09/161/1530/87UL |  |  |  | CDC | 654 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 0 |  | 1530 | 嘉民斗工紅線(1530) |  | 87CFA | [17 empty] | 1-33-03 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.1530_87CFA | 嘉民斗工紅線(1530)87RY通訊故障 | OTHER | D09/161/1530/87CFA |  |  |  | CDC | 655 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 1530 | 嘉民斗工紅線(1530) |  | DTTA | [17 empty] | 2-35-09 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.1530_DTTA | 嘉民斗工紅線(1530)遠方遙跳 | OTHER | D09/161/1530/DTTA |  |  |  | CDC | 656 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 1530 | 嘉民斗工紅線(1530) |  | RYFA | [17 empty] | 1-33-02 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.1530_RYFA | 嘉民斗工紅線(1530)數位電驛故障 | OTHER | D09/161/1530/RYFA |  |  |  | CDC | 657 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1540 | 雲林斗工線(1540) |  | 87A | [17 empty] | 1-01-03 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.1540_87A | 雲林斗工線(1540) 87RY | LINE161 | D09/161/1540/87A |  |  |  | CDC | 658 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1540 | 雲林斗工線(1540) |  | 87UL | [17 empty] | 1-30-06 |  | 1-4C | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1540_87UL | 雲林斗工線(1540) 87RY U/L | LINE161 | D09/161/1540/87UL |  |  |  | CDC | 659 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 0 |  | 1540 | 雲林斗工線(1540) |  | 87CFA | [17 empty] | 1-33-01 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.1540_87CFA | 雲林斗工線(1540)87RY通訊故障 | OTHER | D09/161/1540/87CFA |  |  |  | CDC | 660 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 1540 | 雲林斗工線(1540) |  | RYFA | [17 empty] | 1-33-00 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.1540_RYFA | 雲林斗工線(1540)數位電驛故障 | OTHER | D09/161/1540/RYFA |  |  |  | CDC | 661 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 81RY | 330A1 |  | A/S(3) | [17 empty] | 2-10-06 |  | 2-1C | [5 empty] | ADCS_N | [8 empty] | 斗工DS.81RY_A/S(3) | 330A1 330A2低頻電驛動作/復歸 | OTHER | D09/0/ComPoint/81AS3 |  |  |  | CDC | 662 | GENERICDIPoint | DS036_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
D09 | 斗工DS | 0 |  |  |  |  | 81RYFA | [17 empty] | 2-35-04 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.81RYFA | 低頻電驛故障 | OTHER | D09/0/ComPoint/3A5Other |  |  |  | CDC | 663 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工山線(1510) |  | 87A1 | [17 empty] | 1-00-01 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.1510_87A1 | 鉅工山線(1510) #1 87RY | LINE161 | D09/161/1510/87A1 |  |  |  | CDC | 664 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工山線(1510) |  | 87A2 | [17 empty] | 1-00-02 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.1510_87A2 | 鉅工山線(1510) #2 87RY | LINE161 | D09/161/1510/87A2 |  |  |  | CDC | 665 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工山線(1510) |  | 1_87UL1 | [17 empty] | 1-30-02 |  | 1-48 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1510_87UL1 | 鉅工山線(1510) #1 87RY U/L | LINE161 | D09/161/1510/87UL |  |  |  | CDC | 666 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工山線(1510) |  | 1_87UL2 | [17 empty] | 2-35-07 |  | 2-18 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1510_87UL2 | 鉅工山線(1510) #2 87RY U/L | LINE161 | D09/161/1510/1_87UL2 |  |  |  | CDC | 667 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 0 |  | 1510 | 鉅工山線(1510) |  | 87CFA | [17 empty] | 1-32-13 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.1510_87CFA | 鉅工斗工山線(1510)87RY通訊故障 | OTHER | D09/161/1510/87CFA |  |  |  | CDC | 668 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 1510 | 鉅工山線(1510) |  | RYFA | [17 empty] | 1-32-12 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.1510_RYFA | 鉅工斗工山線(1510)數位電驛故障 | OTHER | D09/161/1510/RYFA |  |  |  | CDC | 669 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工海線(1520) |  | 87A1 | [17 empty] | 1-00-06 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.1520_87A1 | 鉅工海線(1520) #1 87RY | LINE161 | D09/161/1520/87A1 |  |  |  | CDC | 670 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工海線(1520) |  | 87A2 | [17 empty] | 1-00-07 | [7 empty] | 161KV_N | [8 empty] | 斗工DS.1520_87A2 | 鉅工海線(1520) #2 87RY | LINE161 | D09/161/1520/87A2 |  |  |  | CDC | 671 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工海線(1520) |  | 1_87UL1 | [17 empty] | 1-30-04 |  | 1-4A | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1520_87UL1 | 鉅工海線(1520) #1 87RY U/L | LINE161 | D09/161/1520/87UL |  |  |  | CDC | 672 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工海線(1520) |  | 1_87UL2 | [17 empty] | 2-35-08 |  | 2-19 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.1520_87UL2 | 鉅工海線(1520) #2 87RY U/L | LINE161 | D09/161/1520/1_87UL2 |  |  |  | CDC | 673 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 0 |  | 1520 | 鉅工海線(1520) |  | 87CFA | [17 empty] | 1-32-15 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.1520_87CFA | 鉅工斗工海線(1520)87RY通訊故障 | OTHER | D09/161/1520/87CFA |  |  |  | CDC | 674 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 1520 | 鉅工海線(1520) |  | RYFA | [17 empty] | 1-32-14 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.1520_RYFA | 鉅工斗工海線(1520)數位電驛故障 | OTHER | D09/161/1520/RYFA |  |  |  | CDC | 675 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  |  |  |  | GEN | [17 empty] | 1-33-14 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.GEN | 緊急發電機運轉 | OTHER | D09/0/StaDev/2A5Other |  |  |  | CDC | 676 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D09 | 斗工DS | 0 |  | 310 | #1DTR(310) |  | GDA | [17 empty] | 1-0D-05 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.310_GDA | #1DTR 1A 310 GDA | OTHER | D09/22/310/GDA |  |  |  | CDC | 677 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 320 | #1DTR(320) |  | GDA | [17 empty] | 1-0D-06 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.320_GDA | #1DTR 1B 320 GDA | OTHER | D09/11/320/GDA |  |  |  | CDC | 678 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 330A1 | #2DTR |  | GDA | [17 empty] | 1-0D-07 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.330A1_GDA | #2DTR 2A 330A1 GDA | OTHER | D09/22/330A1/GDA |  |  |  | CDC | 679 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 330A2 | #2DTR |  | GDA | [17 empty] | 1-0E-00 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.330A2_GDA | #2DTR 2A 330A2 GDA | OTHER | D09/22/330A2/GDA |  |  |  | CDC | 680 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 340B1 | #2DTR |  | GDA | [17 empty] | 1-0E-01 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.340B1_GDA | #2DTR 2B 340B1 GDA | OTHER | D09/11/340B1/GDA |  |  |  | CDC | 681 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 340B2 | #2DTR |  | GDA | [17 empty] | 1-0E-02 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.340B2_GDA | #2DTR 2B 340B2 GDA | OTHER | D09/11/340B2/GDA |  |  |  | CDC | 682 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 11 | 11kV |  |  |  | 饋線復閉LOA | [17 empty] | 2-35-00 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.饋線復閉LOA | 11KV 22KV饋線79RY復閉失敗 | OTHER | D09/0/ComPoint/LOA |  |  |  | CDC | 683 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | _BUS | BUS |  | 87CTFA | [17 empty] | 2-32-12 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.161KV_BUS_CTFA | 161KV BUS 87RY CT回路故障 | OTHER | D09/161/ComPoint/87CTFA |  |  |  | CDC | 684 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 161 | 161kV | _BUS | BUS |  | RYFA | [17 empty] | 2-32-11 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | D09/161/BUS/BUS_RYFA |  |  |  | CDC | 685 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 1DTR | #1DTR |  | 51Z_UL | [17 empty] | 2-3A-10 |  | 1-36 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.#1DTR_51ZUL | #1DTR 51ZRY U/L | OTHER | D09//1DTR/51Z_UL |  |  |  | CDC | 686 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 0 |  | 1DTR | #1DTR |  | DTR_86A | [17 empty] | 1-0E-04 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.#1DTR_86A | #1DTR 86A | OTHER | D09//1DTR/DTR_86A |  |  |  | CDC | 687 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 1DTR | #1DTR |  | 1_87UL1 | [17 empty] | 2-3A-08 |  | 1-34 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.#1DTR_87UL1 | #1DTR #1 87RY U/L | OTHER | D09//1DTR/1_87UL1 |  |  |  | CDC | 688 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 0 |  | 1DTR | #1DTR |  | 1_87UL2 | [17 empty] | 2-3A-09 |  | 1-35 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.#1DTR_87UL2 | #1DTR #2 87RY U/L | OTHER | D09//1DTR/1_87UL2 |  |  |  | CDC | 689 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 0 |  | 1DTR | #1DTR |  | RYFA | [17 empty] | 2-3A-11 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.#1DTR_RYFA | #1DTR數位電驛故障 | OTHER | D09//1DTR/RYFA |  |  |  | CDC | 690 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 2DTR | #2DTR |  | 51Z_UL | [17 empty] | 2-3A-14 |  | 1-39 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.#2DTR_51ZUL | #2DTR 51ZRY U/L | OTHER | D09//2DTR/51Z_UL |  |  |  | CDC | 691 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 0 |  | 2DTR | #2DTR |  | DTR_86A | [17 empty] | 1-0E-05 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.#2DTR_86A | #2DTR 86A | OTHER | D09//2DTR/DTR_86A |  |  |  | CDC | 692 | GENERICDIPoint | DS036_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 2DTR | #2DTR |  | 1_87UL1 | [17 empty] | 2-3A-12 |  | 1-37 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.#2DTR_87UL1 | #2DTR #1 87RY U/L | OTHER | D09//2DTR/1_87UL1 |  |  |  | CDC | 693 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 0 |  | 2DTR | #2DTR |  | 1_87UL2 | [17 empty] | 2-3A-13 |  | 1-38 | [5 empty] | ADCS_N | [8 empty] | 斗工DS.#2DTR_87UL2 | #2DTR #2 87RY U/L | OTHER | D09//2DTR/1_87UL2 |  |  |  | CDC | 694 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D09 | 斗工DS | 0 |  | 2DTR | #2DTR |  | RYFA | [17 empty] | 2-3A-15 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.#2DTR_RYFA | #2DTR數位電驛故障 | OTHER | D09//2DTR/RYFA |  |  |  | CDC | 695 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | OLTC | OLTC |  | OLTCA | [17 empty] | 1-32-11 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | D09/0/ComPoint/OLTC_A |  |  |  | CDC | 696 | GENERICDIPoint | DS036_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 1510 | 鉅工山線(1510) |  | DTTA | [17 empty] | 2-32-14 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.1510_DTTA | 鉅工斗工山線(1510)遠方遙跳 | OTHER | D09/161/1510/DTTA |  |  |  | CDC | 697 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | 1520 | 鉅工海線(1520) |  | DTTA | [17 empty] | 2-32-15 | [7 empty] | ADCS_N | [8 empty] | 斗工DS.1520_DTTA | 鉅工斗工海線(1520)遠方遙跳 | OTHER | D09/161/1520/DTTA |  |  |  | CDC | 698 | GENERICDIPoint | DS036_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D09 | 斗工DS | 0 |  | TRD | 斗工DS |  | 109 | [25 empty] | TRAIN_AD | [8 empty] | 斗工DS.TRD_109 | 斗工DS NT #1ADTR 23KV_Hi_Limit | [6 empty] | 699 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D09 | 斗工DS | 0 |  | TRD | 斗工DS |  | 110 | [25 empty] | TRAIN_AD | [8 empty] | 斗工DS.TRD_110 | 斗工DS NT #1ADTR 23KV_Lo_Limit | [6 empty] | 700 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D09 | 斗工DS | 0 |  | TRD | 斗工DS |  | 111 | [25 empty] | TRAIN_AD | [8 empty] | 斗工DS.TRD_111 | 斗工DS NT #1BDTR 11KV_Hi_Limit | [6 empty] | 701 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D09 | 斗工DS | 0 |  | TRD | 斗工DS |  | 112 | [25 empty] | TRAIN_AD | [8 empty] | 斗工DS.TRD_112 | 斗工DS NT #1BDTR 11KV_Lo_Limit | [6 empty] | 702 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D09 | 斗工DS | 0 |  | TRD | 斗工DS |  | 113 | [25 empty] | TRAIN_AD | [8 empty] | 斗工DS.TRD_113 | 斗工DS NT #2ADTR 23KV_Hi_Limit | [6 empty] | 703 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D09 | 斗工DS | 0 |  | TRD | 斗工DS |  | 114 | [25 empty] | TRAIN_AD | [8 empty] | 斗工DS.TRD_114 | 斗工DS NT #2ADTR 23KV_Lo_Limit | [6 empty] | 704 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D09 | 斗工DS | 0 |  | TRD | 斗工DS |  | 115 | [25 empty] | TRAIN_AD | [8 empty] | 斗工DS.TRD_115 | 斗工DS NT #2BDTR 11KV_Hi_Limit | [6 empty] | 705 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D09 | 斗工DS | 0 |  | TRD | 斗工DS |  | 116 | [25 empty] | TRAIN_AD | [8 empty] | 斗工DS.TRD_116 | 斗工DS NT #2BDTR 11KV_Lo_Limit | [6 empty] | 706 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D09 | 斗工DS | 11 | 11kV | 220_SC | #2SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 斗工DS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 707 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 22 | 22kV | 210_SC | #1SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 斗工DS.210_SC_CAP | 23KV#1SC 容量 | SC | [5 empty] | 708 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 11 | 11kV | 240_SC | #4SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 斗工DS.240_SC_CAP | 11KV#4SC 容量 | SC | [5 empty] | 709 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 22 | 22kV | 230_SC | #3SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 斗工DS.230_SC_CAP | 23KV#3SC 容量 | SC | [5 empty] | 710 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工山線(1510) |  | LE0 | 1510LE | [24 empty] | ADCS_N | [8 empty] | 斗工DS.1510LE | 1510LE (非取樣點) | LINE161 | D09/161/1510/LE0 |  |  |  |  | 711 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1510 | 鉅工山線(1510) |  | BE0 | 1510BE | [24 empty] | ADCS_N | [8 empty] | 斗工DS.1510BE | 1510BE (非取樣點) | LINE161 | D09/161/1510/BE0 |  |  |  |  | 712 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工海線(1520) |  | LE0 | 1520LE | [24 empty] | ADCS_N | [8 empty] | 斗工DS.1520LE | 1520LE (非取樣點) | LINE161 | D09/161/1520/LE0 |  |  |  |  | 713 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1520 | 鉅工海線(1520) |  | BE0 | 1520BE | [24 empty] | ADCS_N | [8 empty] | 斗工DS.1520BE | 1520BE (非取樣點) | LINE161 | D09/161/1520/BE0 |  |  |  |  | 714 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1530 | 嘉民斗工紅線(1530) |  | LE0 | 1530LE | [24 empty] | ADCS_N | [8 empty] | 斗工DS.1530LE | 1530LE (非取樣點) | LINE161 | D09/161/1530/LE0 |  |  |  |  | 715 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1530 | 嘉民斗工紅線(1530) |  | BE0 | 1530BE | [24 empty] | ADCS_N | [8 empty] | 斗工DS.1530BE | 1530BE (非取樣點) | LINE161 | D09/161/1530/BE0 |  |  |  |  | 716 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1540 | 雲林斗工線(1540) |  | LE0 | 1540LE | [24 empty] | ADCS_N | [8 empty] | 斗工DS.1540LE | 1540LE (非取樣點) | LINE161 | D09/161/1540/LE0 |  |  |  |  | 717 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1540 | 雲林斗工線(1540) |  | BE0 | 1540BE | [24 empty] | ADCS_N | [8 empty] | 斗工DS.1540BE | 1540BE (非取樣點) | LINE161 | D09/161/1540/BE0 |  |  |  |  | 718 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1550 | 富喬線(1550) |  | LE0 | 1550LE | [24 empty] | ADCS_N | [8 empty] | 斗工DS.1550LE | 1550LE (非取樣點) | LINE161 | D09/161/1550/LE0 |  |  |  |  | 719 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1550 | 富喬線(1550) |  | BE0 | 1550BE | [24 empty] | ADCS_N | [8 empty] | 斗工DS.1550BE | 1550BE (非取樣點) | LINE161 | D09/161/1550/BE0 |  |  |  |  | 720 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | XU26 | XU26_DS |  | DS1 | XU26_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU26_DS | XU26_DS (非取樣點) | FEEDER | D09/11/XU26/DS |  |  |  |  | 721 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | XU26 | XU26_ES |  | LE0 | XU26_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU26_ES | XU26_ES (非取樣點) | FEEDER | D09/11/XU26/ES |  |  |  |  | 722 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | XU27 | XU27_DS |  | DS1 | XU27_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU27_DS | XU27_DS (非取樣點) | FEEDER | D09/11/XU27/DS |  |  |  |  | 723 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | XU27 | XU27_ES |  | LE0 | XU27_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU27_ES | XU27_ES (非取樣點) | FEEDER | D09/11/XU27/ES |  |  |  |  | 724 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | XU28 | XU28_DS |  | DS1 | XU28_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU28_DS | XU28_DS (非取樣點) | FEEDER | D09/11/XU28/DS |  |  |  |  | 725 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | XU28 | XU28_ES |  | LE0 | XU28_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU28_ES | XU28_ES (非取樣點) | FEEDER | D09/11/XU28/ES |  |  |  |  | 726 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | XU29 | XU29_DS |  | DS1 | XU29_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU29_DS | XU29_DS (非取樣點) | FEEDER | D09/11/XU29/DS |  |  |  |  | 727 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | XU29 | XU29_ES |  | LE0 | XU29_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU29_ES | XU29_ES (非取樣點) | FEEDER | D09/11/XU29/ES |  |  |  |  | 728 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | XU30 | XU30_DS |  | DS1 | XU30_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU30_DS | XU30_DS (非取樣點) | FEEDER | D09/11/XU30/DS |  |  |  |  | 729 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | XU30 | XU30_ES |  | LE0 | XU30_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU30_ES | XU30_ES (非取樣點) | FEEDER | D09/11/XU30/ES |  |  |  |  | 730 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | XU36 | XU36_DS |  | DS1 | XU36_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU36_DS | XU36_DS (非取樣點) | FEEDER | D09/11/XU36/DS |  |  |  |  | 731 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | XU36 | XU36_ES |  | LE0 | XU36_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU36_ES | XU36_ES (非取樣點) | FEEDER | D09/11/XU36/ES |  |  |  |  | 732 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | XU37 | XU37_DS |  | DS1 | XU37_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU37_DS | XU37_DS (非取樣點) | FEEDER | D09/11/XU37/DS |  |  |  |  | 733 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | XU37 | XU37_ES |  | LE0 | XU37_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU37_ES | XU37_ES (非取樣點) | FEEDER | D09/11/XU37/ES |  |  |  |  | 734 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | XU38 | XU38_DS |  | DS1 | XU38_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU38_DS | XU38_DS (非取樣點) | FEEDER | D09/11/XU38/DS |  |  |  |  | 735 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | XU38 | XU38_ES |  | LE0 | XU38_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU38_ES | XU38_ES (非取樣點) | FEEDER | D09/11/XU38/ES |  |  |  |  | 736 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | XU39 | XU39_DS |  | DS1 | XU39_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU39_DS | XU39_DS (非取樣點) | FEEDER | D09/11/XU39/DS |  |  |  |  | 737 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | XU39 | XU39_ES |  | LE0 | XU39_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU39_ES | XU39_ES (非取樣點) | FEEDER | D09/11/XU39/ES |  |  |  |  | 738 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | XU40 | XU40_DS |  | DS1 | XU40_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU40_DS | XU40_DS (非取樣點) | FEEDER | D09/11/XU40/DS |  |  |  |  | 739 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | XU40 | XU40_ES |  | LE0 | XU40_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU40_ES | XU40_ES (非取樣點) | FEEDER | D09/11/XU40/ES |  |  |  |  | 740 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | XU51 | XU51_DS |  | DS1 | XU51_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU51_DS | XU51_DS (非取樣點) | FEEDER | D09/22/XU51/DS |  |  |  |  | 741 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | XU51 | XU51_ES |  | LE0 | XU51_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU51_ES | XU51_ES (非取樣點) | FEEDER | D09/22/XU51/ES |  |  |  |  | 742 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | XU52 | XU52_DS |  | DS1 | XU52_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU52_DS | XU52_DS (非取樣點) | FEEDER | D09/22/XU52/DS |  |  |  |  | 743 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | XU52 | XU52_ES |  | LE0 | XU52_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU52_ES | XU52_ES (非取樣點) | FEEDER | D09/22/XU52/ES |  |  |  |  | 744 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | XU53 | XU53_DS |  | DS1 | XU53_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU53_DS | XU53_DS (非取樣點) | FEEDER | D09/22/XU53/DS |  |  |  |  | 745 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | XU53 | XU53_ES |  | LE0 | XU53_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU53_ES | XU53_ES (非取樣點) | FEEDER | D09/22/XU53/ES |  |  |  |  | 746 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | XU54 | XU54_DS |  | DS1 | XU54_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU54_DS | XU54_DS (非取樣點) | FEEDER | D09/22/XU54/DS |  |  |  |  | 747 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | XU54 | XU54_ES |  | LE0 | XU54_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU54_ES | XU54_ES (非取樣點) | FEEDER | D09/22/XU54/ES |  |  |  |  | 748 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | XU55 | XU55_DS |  | DS1 | XU55_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU55_DS | XU55_DS (非取樣點) | FEEDER | D09/22/XU55/DS |  |  |  |  | 749 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | XU55 | XU55_ES |  | LE0 | XU55_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU55_ES | XU55_ES (非取樣點) | FEEDER | D09/22/XU55/ES |  |  |  |  | 750 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | XU61 | XU61_DS |  | DS1 | XU61_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU61_DS | XU61_DS (非取樣點) | FEEDER | D09/22/XU61/DS |  |  |  |  | 751 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | XU61 | XU61_ES |  | LE0 | XU61_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU61_ES | XU61_ES (非取樣點) | FEEDER | D09/22/XU61/ES |  |  |  |  | 752 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | XU62 | XU62_DS |  | DS1 | XU62_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU62_DS | XU62_DS (非取樣點) | FEEDER | D09/22/XU62/DS |  |  |  |  | 753 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | XU62 | XU62_ES |  | LE0 | XU62_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU62_ES | XU62_ES (非取樣點) | FEEDER | D09/22/XU62/ES |  |  |  |  | 754 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | XU63 | XU63_DS |  | DS1 | XU63_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU63_DS | XU63_DS (非取樣點) | FEEDER | D09/22/XU63/DS |  |  |  |  | 755 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | XU63 | XU63_ES |  | LE0 | XU63_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU63_ES | XU63_ES (非取樣點) | FEEDER | D09/22/XU63/ES |  |  |  |  | 756 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | XU64 | XU64_DS |  | DS1 | XU64_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU64_DS | XU64_DS (非取樣點) | FEEDER | D09/22/XU64/DS |  |  |  |  | 757 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | XU64 | XU64_ES |  | LE0 | XU64_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU64_ES | XU64_ES (非取樣點) | FEEDER | D09/22/XU64/ES |  |  |  |  | 758 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | XU65 | XU65_DS |  | DS1 | XU65_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU65_DS | XU65_DS (非取樣點) | FEEDER | D09/22/XU65/DS |  |  |  |  | 759 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | XU65 | XU65_ES |  | LE0 | XU65_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗工DS.XU65_ES | XU65_ES (非取樣點) | FEEDER | D09/22/XU65/ES |  |  |  |  | 760 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 101 | 101 |  | 101 | 101 | [24 empty] | ADCS_N | [8 empty] | 斗工DS.101 | 101 (非取樣點) | TIE | D09/22/100/D1 |  |  |  |  | 761 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 102 | 102 |  | 102 | 102 | [24 empty] | ADCS_N | [8 empty] | 斗工DS.102 | 102 (非取樣點) | TIE | D09/22/100/D2 |  |  |  |  | 762 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [24 empty] | ADCS_N | [8 empty] | 斗工DS.1501E | 1501E (非取樣點) | TIE | D09/161/1500/E1 |  |  |  |  | 763 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [24 empty] | ADCS_N | [8 empty] | 斗工DS.1502E | 1502E (非取樣點) | TIE | D09/161/1500/E2 |  |  |  |  | 764 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 201 | 201 |  | 201 | 201 | [24 empty] | ADCS_N | [8 empty] | 斗工DS.201 | 201 (非取樣點) | TIE | D09/11/200/D1 |  |  |  |  | 765 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 301 | 301 |  | 301 | 301 | [24 empty] | ADCS_N | [8 empty] | 斗工DS.301 | 301 (非取樣點) | TIE | D09/22/300/D1 |  |  |  |  | 766 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 401 | 401 |  | 401 | 401 | [24 empty] | ADCS_N | [8 empty] | 斗工DS.401 | 401 (非取樣點) | TIE | D09/11/400/D1 |  |  |  |  | 767 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 391 | 391 |  | 391 | 391 | [24 empty] | ADCS_N | [8 empty] | 斗工DS.391 | 391 (非取樣點) | OTHER | D09/11/390/D1 |  |  |  |  | 768 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 491 | 491 |  | 491 | 491 | [24 empty] | ADCS_N | [8 empty] | 斗工DS.491 | 491 (非取樣點) | OTHER | D09/22/490/D1 |  |  |  |  | 769 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | 1750TE | [24 empty] | ADCS_N | [8 empty] | 斗工DS.1750TE | 1750TE (非取樣點) | MTR | D09/161/1750/TE0 |  |  |  |  | 770 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | 1750BE | [24 empty] | ADCS_N | [8 empty] | 斗工DS.1750BE | 1750BE (非取樣點) | MTR | D09/161/1750/BE0 |  |  |  |  | 771 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 311 | 311 |  | 311 | 311 | [24 empty] | ADCS_N | [8 empty] | 斗工DS.311 | 311 (非取樣點) | MTR | D09/22/310/D1 |  |  |  |  | 772 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 310 | #1DTR(310) |  | E1 | 311E | [24 empty] | ADCS_N | [8 empty] | 斗工DS.311E | 311E (非取樣點) | MTR | D09/22/310/E1 |  |  |  |  | 773 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 321 | 321 |  | 321 | 321 | [24 empty] | ADCS_N | [8 empty] | 斗工DS.321 | 321 (非取樣點) | MTR | D09/11/320/D1 |  |  |  |  | 774 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 320 | #1DTR(320) |  | E1 | 321E | [24 empty] | ADCS_N | [8 empty] | 斗工DS.321E | 321E (非取樣點) | MTR | D09/11/320/E1 |  |  |  |  | 775 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | 1760TE | [24 empty] | ADCS_N | [8 empty] | 斗工DS.1760TE | 1760TE (非取樣點) | MTR | D09/161/1760/TE0 |  |  |  |  | 776 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | 1760BE | [24 empty] | ADCS_N | [8 empty] | 斗工DS.1760BE | 1760BE (非取樣點) | MTR | D09/161/1760/BE0 |  |  |  |  | 777 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 15B1E | 15B1E |  | BE1 | 15B1E | [24 empty] | ADCS_N | [8 empty] | 斗工DS.15B1E | 15B1E (非取樣點) | BUS | D09/161/161B1E/BE1 |  |  |  |  | 778 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 15B2E | 15B2E |  | BE2 | 15B2E | [24 empty] | ADCS_N | [8 empty] | 斗工DS.15B2E | 15B2E (非取樣點) | BUS | D09/161/161B2E/BE2 |  |  |  |  | 779 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | ADCS_N | [8 empty] | 斗工DS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 780 | NotelDIPoint | [38 empty] | START/STOP | STOP
D09 | 斗工DS | 0 |  |  |  |  | 101E | 101E | [24 empty] | ADCS_N | [8 empty] | 斗工DS.101E | 101E(非取樣點) | OTHER | D09/22/100/E1 |  |  |  |  | 781 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  |  |  |  | 102E | 102E | [24 empty] | ADCS_N | [8 empty] | 斗工DS.102E | 102E(非取樣點) | OTHER | D09/22/100/E2 |  |  |  |  | 782 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  |  |  |  | 201E | 201E | [24 empty] | ADCS_N | [8 empty] | 斗工DS.201E | 201E(非取樣點) | OTHER | D09/11/200/E1 |  |  |  |  | 783 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  |  |  |  | 301E | 301E | [24 empty] | ADCS_N | [8 empty] | 斗工DS.301E | 301E(非取樣點) | OTHER | D09/22/300/E1 |  |  |  |  | 784 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  |  |  |  | 391E | 391E | [24 empty] | ADCS_N | [8 empty] | 斗工DS.391E | 391E(非取樣點)(非取樣點) | OTHER | D09/11/390/E1 |  |  |  |  | 785 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  |  |  |  | 401E | 401E | [24 empty] | ADCS_N | [8 empty] | 斗工DS.401E | 401E(非取樣點) | OTHER | D09/11/400/E1 |  |  |  |  | 786 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  |  |  |  | 491E | 491E | [24 empty] | ADCS_N | [8 empty] | 斗工DS.491E | 491E(非取樣點)(非取樣點) | OTHER | D09/22/490/E1 |  |  |  |  | 787 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 202 | 202 |  | 202 | 202 | [24 empty] | ADCS_N | [8 empty] | 斗工DS.202 | 202 (非取樣點) | TIE | D09/11/200/D2 |  |  |  |  | 788 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 221E | 221E |  | 221E | 221E | [24 empty] | ADCS_N | [8 empty] | 斗工DS.221E | 221E (非取樣點) | SC | D09/11/220/E1 |  |  |  |  | 789 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 220 | #2SC(220) |  | SC10 | 220SC1 | [24 empty] | ADCS_N | [8 empty] | 斗工DS.220SC1_ES | 220SC1_ES (非取樣點) | SC | [5 empty] | 790 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 221 | 221 |  | 221 | 221 | [24 empty] | ADCS_N | [8 empty] | 斗工DS.221 | 221 (非取樣點) | SC | D09/11/220/D1 |  |  |  |  | 791 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 220 | #2SC(220) |  | SC20 | 220SC2 | [24 empty] | ADCS_N | [8 empty] | 斗工DS.220SC2_ES | 220SC2_ES (非取樣點) | SC | [5 empty] | 792 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 211E | 211E |  | 211E | 211E | [24 empty] | ADCS_N | [8 empty] | 斗工DS.211E | 211E (非取樣點) | SC | D09/22/210/E1 |  |  |  |  | 793 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 210 | #1SC(210) |  | SC10 | 210SC1 | [24 empty] | ADCS_N | [8 empty] | 斗工DS.210SC1_ES | 210SC1_ES (非取樣點) | SC | [5 empty] | 794 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 211 | 211 |  | 211 | 211 | [24 empty] | ADCS_N | [8 empty] | 斗工DS.211 | 211 (非取樣點) | SC | D09/22/210/D1 |  |  |  |  | 795 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  |  |  |  | 202E | 202E | [24 empty] | ADCS_N | [8 empty] | 斗工DS.202E | 202E(非取樣點) | OTHER | D09/11/200/E2 |  |  |  |  | 796 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 330 | 330 |  | A21 | 331A2 | [24 empty] | ADCS_N | [8 empty] | 斗工DS.331A2 | 331A2 (非取樣點) | MTR | [5 empty] | 797 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 330 | 330 |  | A2E1 | 331A2E | [24 empty] | ADCS_N | [8 empty] | 斗工DS.331A2E | 331A2E (非取樣點) | MTR | [5 empty] | 798 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 330 | 330 |  | A11 | 331A1 | [24 empty] | ADCS_N | [8 empty] | 斗工DS.331A1 | 331A1 (非取樣點) | MTR | [5 empty] | 799 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 330 | 330 |  | A1E1 | 331A1E | [24 empty] | ADCS_N | [8 empty] | 斗工DS.331A1E | 331A1E (非取樣點) | MTR | [5 empty] | 800 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 340 | 340 |  | B11 | 341B1 | [24 empty] | ADCS_N | [8 empty] | 斗工DS.341B1 | 341B1 (非取樣點) | MTR | [5 empty] | 801 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 340 | 340 |  | BE1 | 341B1E | [24 empty] | ADCS_N | [8 empty] | 斗工DS.341B1E | 341B1E (非取樣點) | MTR | [5 empty] | 802 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 340 | 340 |  | B21 | 341B2 | [24 empty] | ADCS_N | [8 empty] | 斗工DS.341B2 | 341B2 (非取樣點) | MTR | [5 empty] | 803 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 340 | 340 |  | BE2 | 341B2E | [24 empty] | ADCS_N | [8 empty] | 斗工DS.341B2E | 341B2E (非取樣點) | MTR | [5 empty] | 804 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 241E | 241E |  | 241E | 241E | [24 empty] | ADCS_N | [8 empty] | 斗工DS.241E | 241E (非取樣點) | SC | D09/11/240/E1 |  |  |  |  | 805 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 240 | #4SC(240) |  | SC10 | 240SC1 | [24 empty] | ADCS_N | [8 empty] | 斗工DS.240SC1_ES | 240SC1_ES (非取樣點) | SC | [5 empty] | 806 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 241 | 241 |  | 241 | 241 | [24 empty] | ADCS_N | [8 empty] | 斗工DS.241 | 241 (非取樣點) | SC | D09/11/240/D1 |  |  |  |  | 807 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 0 |  | 240 | #4SC(240) |  | SC20 | 240SC2 | [24 empty] | ADCS_N | [8 empty] | 斗工DS.240SC2_ES | 240SC2_ES (非取樣點) | SC | [5 empty] | 808 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 231E | 231E |  | 231E | 231E | [24 empty] | ADCS_N | [8 empty] | 斗工DS.231E | 231E (非取樣點) | SC | D09/22/230/E1 |  |  |  |  | 809 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 230 | #3SC(230) |  | SC10 | 230SC1 | [24 empty] | ADCS_N | [8 empty] | 斗工DS.230SC1_ES | 230SC1_ES (非取樣點) | SC | [5 empty] | 810 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 231 | 231 |  | 231 | 231 | [24 empty] | ADCS_N | [8 empty] | 斗工DS.231 | 231 (非取樣點) | SC | D09/22/230/D1 |  |  |  |  | 811 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D09 | 斗工DS | 161 | 161kV | 1570 | 備用線(1570) |  | LE0 | 1570LE | [24 empty] | ADCS_N | [8 empty] | 斗工DS.1570LE | 1570LE (非取樣點) | LINE161 | [5 empty] | 812 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1570 | 備用線(1570) |  | BE0 | 1570BE | [24 empty] | ADCS_N | [8 empty] | 斗工DS.1570BE | 1570BE (非取樣點) | LINE161 | [5 empty] | 813 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1580 | 斗六斗工線(1580) |  | LE0 | 1580LE | [24 empty] | ADCS_N | [8 empty] | 斗工DS.1580LE | 1580LE (非取樣點) | LINE161 | [5 empty] | 814 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1580 | 斗六斗工線(1580) |  | BE0 | 1580BE | [24 empty] | ADCS_N | [8 empty] | 斗工DS.1580BE | 1580BE (非取樣點) | LINE161 | [5 empty] | 815 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1610 | 榴中斗工一路(1610) |  | LE0 | 1610LE | [24 empty] | ADCS_N | [8 empty] | 斗工DS.1610LE | 1610LE (非取樣點) | LINE161 | D09/161/1610/LE0 |  |  |  |  | 816 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1610 | 榴中斗工一路(1610) |  | BE0 | 1610BE | [24 empty] | ADCS_N | [8 empty] | 斗工DS.1610BE | 1610BE (非取樣點) | LINE161 | D09/161/1610/BE0 |  |  |  |  | 817 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1620 | 榴中斗工二路(1620) |  | LE0 | 1620LE | [24 empty] | ADCS_N | [8 empty] | 斗工DS.1620LE | 1620LE (非取樣點) | LINE161 | D09/161/1620/LE0 |  |  |  |  | 818 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 161 | 161kV | 1620 | 榴中斗工二路(1620) |  | BE0 | 1620BE | [24 empty] | ADCS_N | [8 empty] | 斗工DS.1620BE | 1620BE (非取樣點) | LINE161 | D09/161/1620/BE0 |  |  |  |  | 819 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 1A | #1A |  | BE | #1A_BE | [24 empty] | ADCS_N | [8 empty] | 斗工DS.#1A_BE | #1A BE(非取樣點) | OTHER | [5 empty] | 820 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 1B | #1B |  | BE | #1B_BE | [24 empty] | ADCS_N | [8 empty] | 斗工DS.#1B_BE | #1B BE(非取樣點) | OTHER | [5 empty] | 821 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 2A1 | #2A1 |  | BE | #2A1_BE | [24 empty] | ADCS_N | [8 empty] | 斗工DS.#2A1_BE | #2A1 BE(非取樣點) | OTHER | [5 empty] | 822 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 2A2 | #2A2 |  | BE | #2A2_BE | [24 empty] | ADCS_N | [8 empty] | 斗工DS.#2A2_BE | #2A2 BE(非取樣點) | OTHER | [5 empty] | 823 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 2B1 | #2B1 |  | BE | #2B1_BE | [24 empty] | ADCS_N | [8 empty] | 斗工DS.#2B1_BE | #2B1 BE(非取樣點) | OTHER | [5 empty] | 824 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D09 | 斗工DS | 0 |  | 2B2 | #2B2 |  | BE | #2B2_BE | [24 empty] | ADCS_N | [8 empty] | 斗工DS.#2B2_BE | #2B2 BE(非取樣點) | OTHER | [5 empty] | 825 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo