## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D10 | 北勢DS | 161 | 161kV | 1510 | 雲林～北勢線(1510) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_A1 | [8 empty] | 北勢DS.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 2 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 161 | 161kV | 1510 | 雲林～北勢線(1510) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_A1 | [8 empty] | 北勢DS.1510BE | 1510BE (非取樣點) | LINE161 | [5 empty] | 3 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 161 | 161kV | 1520 | 斗南～北勢線(1520) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_A1 | [8 empty] | 北勢DS.1520LE | 1520LE (非取樣點) | LINE161 | [5 empty] | 4 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 161 | 161kV | 1520 | 斗南～北勢線(1520) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_A1 | [8 empty] | 北勢DS.1520BE | 1520BE (非取樣點) | LINE161 | [5 empty] | 5 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 161 | 161kV | 1530 | 北勢～旭硝子、旭硝二紅線(1530) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_A1 | [8 empty] | 北勢DS.1530LE | 1530LE (非取樣點) | LINE161 | [5 empty] | 6 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 161 | 161kV | 1530 | 北勢～旭硝子、旭硝二紅線(1530) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_A1 | [8 empty] | 北勢DS.1530BE | 1530BE (非取樣點) | LINE161 | [5 empty] | 7 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 161 | 161kV | 1540 | 北勢～旭硝子、旭硝二白線(1540) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_A1 | [8 empty] | 北勢DS.1540LE | 1540LE (非取樣點) | LINE161 | [5 empty] | 8 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 161 | 161kV | 1540 | 北勢～旭硝子、旭硝二白線(1540) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_A1 | [8 empty] | 北勢DS.1540BE | 1540BE (非取樣點) | LINE161 | [5 empty] | 9 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_A1 | [8 empty] | 北勢DS.1501E | 1501E (非取樣點) | TIE | [5 empty] | 10 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_A1 | [8 empty] | 北勢DS.1502E | 1502E (非取樣點) | TIE | [5 empty] | 11 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_A1 | [8 empty] | 北勢DS.1750TE | 1750TE (非取樣點) | MTR | [5 empty] | 12 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_A1 | [8 empty] | 北勢DS.1750BE | 1750BE (非取樣點) | MTR | [5 empty] | 13 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | D1 | 311(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D10_A1 | [8 empty] | 北勢DS.311 | 311 (非取樣點) | MTR | [5 empty] | 14 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | E1 | 311E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D10_A1 | [8 empty] | 北勢DS.311E | 311E (非取樣點) | MTR | [5 empty] | 15 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | D1 | 321(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D10_A1 | [8 empty] | 北勢DS.321 | 321 (非取樣點) | MTR | [5 empty] | 16 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | E1 | 321E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D10_A1 | [8 empty] | 北勢DS.321E | 321E (非取樣點) | MTR | [5 empty] | 17 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 161 | 161kV | 1760 | #1DTR(1760) |  | TE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_A1 | [8 empty] | 北勢DS.1760TE | 1760TE (非取樣點) | MTR | [5 empty] | 12 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 161 | 161kV | 1760 | #1DTR(1760) |  | BE0 | (非取樣點) | ADD | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_A1 | [8 empty] | 北勢DS.1760BE | 1760BE (非取樣點) | MTR | [5 empty] | 13 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_A1 | [8 empty] | 北勢DS.1770TE | 1770TE (非取樣點) | MTR | [5 empty] | 18 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_A1 | [8 empty] | 北勢DS.1770BE | 1770BE (非取樣點) | MTR | [5 empty] | 19 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 22 | 22kV | 350 | #3DTR(350) |  | D1 | 351(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D10_A1 | [8 empty] | 北勢DS.351 | 351 (非取樣點) | MTR | [5 empty] | 20 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | 350 | #3DTR(350) |  | E1 | 351E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D10_A1 | [8 empty] | 北勢DS.351E | 351E (非取樣點) | MTR | [5 empty] | 21 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 161 | 161kV | 1780 | #4DTR(1780) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_A1 | [8 empty] | 北勢DS.1780TE | 1780TE (非取樣點) | MTR | [5 empty] | 22 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 161 | 161kV | 1780 | #4DTR(1780) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_A1 | [8 empty] | 北勢DS.1780BE | 1780BE (非取樣點) | MTR | [5 empty] | 23 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 22 | 22kV | 370 | #4DTR(370) |  | D1 | 371(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D10_A1 | [8 empty] | 北勢DS.371 | 371 (非取樣點) | MTR | [5 empty] | 24 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | 370 | #4DTR(370) |  | E1 | 371E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D10_A1 | [8 empty] | 北勢DS.371E | 371E (非取樣點) | MTR | [5 empty] | 25 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 11 | 11kV | 210 | #1SC(210) |  | E1 | 211E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D10_A1 | [8 empty] | 北勢DS.211E | 211E (非取樣點) | SC | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 11 | 11kV | 210 | #1SC(210) |  | DS1 | 211(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D10_A1 | [8 empty] | 北勢DS.211 | 211 (非取樣點) | SC | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | XL21 | 北一線(XL21) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL21_DS | XL21_DS (非取樣點) | FEEDER | [5 empty] | 28 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | XL21 | 北一線(XL21) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL21_ES | XL21_ES (非取樣點) | FEEDER | [5 empty] | 29 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 11 | 11kV | XL22 | 北二線(XL22) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL22_DS | XL22_DS (非取樣點) | FEEDER | [5 empty] | 30 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | XL22 | 北二線(XL22) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL22_ES | XL22_ES (非取樣點) | FEEDER | [5 empty] | 31 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 11 | 11kV | XL23 | 北三線(XL23) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL23_DS | XL23_DS (非取樣點) | FEEDER | [5 empty] | 32 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | XL23 | 北三線(XL23) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL23_ES | XL23_ES (非取樣點) | FEEDER | [5 empty] | 33 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 11 | 11kV | XL24 | 北四線(XL24) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL24_DS | XL24_DS (非取樣點) | FEEDER | [5 empty] | 34 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | XL24 | 北四線(XL24) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL24_ES | XL24_ES (非取樣點) | FEEDER | [5 empty] | 35 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 11 | 11kV | XL25 | 北五線(XL25) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL25_DS | XL25_DS (非取樣點) | FEEDER | [5 empty] | 36 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | XL25 | 北五線(XL25) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL25_ES | XL25_ES (非取樣點) | FEEDER | [5 empty] | 37 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 11 | 11kV | 100 | TIE(100) |  | D1 | 101(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D10_A1 | [8 empty] | 北勢DS.101 | 101 (非取樣點) | TIE | [5 empty] | 38 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | 100 | TIE(100) |  | E1 | 101E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D10_A1 | [8 empty] | 北勢DS.101E | 101E(非取樣點) | OTHER | [5 empty] | 39 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 11 | 11kV | 390 | #1SSTR(390) |  | D1 | 391(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D10_A1 | [8 empty] | 北勢DS.391 | 391 (非取樣點) | OTHER | [5 empty] | 40 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 11 | 11kV | 390 | #1SSTR(390) |  | E1 | 391E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D10_A1 | [8 empty] | 北勢DS.391E | 391E (非取樣點) | OTHER | [5 empty] | 41 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 11 | 11kV | 220 | #2SC(220) |  | E1 | 221E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D10_A1 | [8 empty] | 北勢DS.221E | 221E (非取樣點) | SC | [5 empty] | 42 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 11 | 11kV | 220 | #2SC(220) |  | DS1 | 221(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D10_A1 | [8 empty] | 北勢DS.221 | 221 (非取樣點) | SC | [5 empty] | 43 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | XL26 | 北六線(XL26) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL26_DS | XL26_DS (非取樣點) | FEEDER | [5 empty] | 44 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | XL26 | 北六線(XL26) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL26_ES | XL26_ES (非取樣點) | FEEDER | [5 empty] | 45 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 11 | 11kV | XL27 | 北七線(XL27) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL27_DS | XL27_DS (非取樣點) | FEEDER | [5 empty] | 46 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | XL27 | 北七線(XL27) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL27_ES | XL27_ES (非取樣點) | FEEDER | [5 empty] | 47 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 11 | 11kV | XL28 | 北八線(XL28) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL28_DS | XL28_DS (非取樣點) | FEEDER | [5 empty] | 48 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | XL28 | 北八線(XL28) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL28_ES | XL28_ES (非取樣點) | FEEDER | [5 empty] | 49 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 11 | 11kV | XL29 | 北九線(XL29) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL29_DS | XL29_DS (非取樣點) | FEEDER | [5 empty] | 50 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | XL29 | 北九線(XL29) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL29_ES | XL29_ES (非取樣點) | FEEDER | [5 empty] | 51 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 11 | 11kV | XL30 | 北十線(XL30) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL30_DS | XL30_DS (非取樣點) | FEEDER | [5 empty] | 52 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | XL30 | 北十線(XL30) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL30_ES | XL30_ES (非取樣點) | FEEDER | [5 empty] | 53 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 22 | 22kV | 250 | #5SC(250) |  | E1 | 251E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D10_A1 | [8 empty] | 北勢DS.251E | 251E (非取樣點) | SC | [5 empty] | 54 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 22 | 22kV | 250 | #5SC(250) |  | D1 | 251(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D10_A1 | [8 empty] | 北勢DS.251 | 251 (非取樣點) | SC | [5 empty] | 55 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL61 | 北六一線(XL61) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL61_DS | XL61_DS (非取樣點) | FEEDER | [5 empty] | 56 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL61 | 北六一線(XL61) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL61_ES | XL61_ES (非取樣點) | FEEDER | [5 empty] | 57 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 22 | 22kV | XL62 | 北六二線(XL62) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL62_DS | XL62_DS (非取樣點) | FEEDER | [5 empty] | 58 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL62 | 北六二線(XL62) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL62_ES | XL62_ES (非取樣點) | FEEDER | [5 empty] | 59 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 22 | 22kV | XL63 | 北六三線(XL63) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL63_DS | XL63_DS (非取樣點) | FEEDER | [5 empty] | 60 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL63 | 北六三線(XL63) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL63_ES | XL63_ES (非取樣點) | FEEDER | [5 empty] | 61 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 22 | 22kV | XL64 | 北六四線(XL64) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL64_DS | XL64_DS (非取樣點) | FEEDER | [5 empty] | 62 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL64 | 北六四線(XL64) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL64_ES | XL64_ES (非取樣點) | FEEDER | [5 empty] | 63 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 22 | 22kV | XL65 | 北六五線(XL65) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL65_DS | XL65_DS (非取樣點) | FEEDER | [5 empty] | 64 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL65 | 北六五線(XL65) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL65_ES | XL65_ES (非取樣點) | FEEDER | [5 empty] | 65 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 22 | 22kV | XL66 | 北六六線(XL66) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL66_DS | XL66_DS (非取樣點) | FEEDER | [5 empty] | 66 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL66 | 北六六線(XL66) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL66_ES | XL66_ES (非取樣點) | FEEDER | [5 empty] | 67 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 22 | 22kV | XL67 | 北六七線(XL67) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL67_DS | XL67_DS (非取樣點) | FEEDER | [5 empty] | 68 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL67 | 北六七線(XL67) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL67_ES | XL67_ES (非取樣點) | FEEDER | [5 empty] | 69 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 22 | 22kV | XL68 | 北六八線(XL68) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL68_DS | XL68_DS (非取樣點) | FEEDER | [5 empty] | 70 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL68 | 北六八線(XL68) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL68_ES | XL68_ES (非取樣點) | FEEDER | [5 empty] | 71 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 22 | 22kV | 260 | #6SC(260) |  | E1 | 261E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D10_A1 | [8 empty] | 北勢DS.261E | 261E (非取樣點) | SC | [5 empty] | 72 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 22 | 22kV | 260 | #6SC(260) |  | D1 | 261(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D10_A1 | [8 empty] | 北勢DS.261 | 261 (非取樣點) | SC | [5 empty] | 73 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | 300 | TIE(300) |  | D1 | 301(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D10_A1 | [8 empty] | 北勢DS.301 | 301 (非取樣點) | TIE | [5 empty] | 74 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | 300 | TIE(300) |  | D2 | 302(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D10_A1 | [8 empty] | 北勢DS.302 | 302 (非取樣點) | TIE | [5 empty] | 75 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | 300 | TIE(300) |  | E1 | 301E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D10_A1 | [8 empty] | 北勢DS.301E | 301E(非取樣點) | OTHER | [5 empty] | 76 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 22 | 22kV | 300 | TIE(300) |  | E2 | 302E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D10_A1 | [8 empty] | 北勢DS.302E | 302E(非取樣點) | OTHER | [5 empty] | 77 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 22 | 22kV | 270 | #7SC(270) |  | E1 | 271E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D10_A1 | [8 empty] | 北勢DS.271E | 271E (非取樣點) | SC | [5 empty] | 78 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 22 | 22kV | 270 | #7SC(270) |  | D1 | 271(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D10_A1 | [8 empty] | 北勢DS.271 | 271 (非取樣點) | SC | [5 empty] | 79 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL71 | 北七一線(XL71) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL71_DS | XL71_DS (非取樣點) | FEEDER | [5 empty] | 80 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL71 | 北七一線(XL71) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL71_ES | XL71_ES (非取樣點) | FEEDER | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 22 | 22kV | XL72 | 北七二線(XL72) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL72_DS | XL72_DS (非取樣點) | FEEDER | [5 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL72 | 北七二線(XL72) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL72_ES | XL72_ES (非取樣點) | FEEDER | [5 empty] | 83 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 22 | 22kV | XL73 | 北七三線(XL73) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL73_DS | XL73_DS (非取樣點) | FEEDER | [5 empty] | 84 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL73 | 北七三線(XL73) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL73_ES | XL73_ES (非取樣點) | FEEDER | [5 empty] | 85 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 22 | 22kV | XL74 | 北七四線(XL74) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL74_DS | XL74_DS (非取樣點) | FEEDER | [5 empty] | 86 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL74 | 北七四線(XL74) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL74_ES | XL74_ES (非取樣點) | FEEDER | [5 empty] | 87 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 22 | 22kV | XL75 | 北七五線(XL75) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL75_DS | XL75_DS (非取樣點) | FEEDER | [5 empty] | 88 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL75 | 北七五線(XL75) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL75_ES | XL75_ES (非取樣點) | FEEDER | [5 empty] | 89 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 22 | 22kV | XL76 | 北七六線(XL76) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL76_DS | XL76_DS (非取樣點) | FEEDER | [5 empty] | 90 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL76 | 北七六線(XL76) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL76_ES | XL76_ES (非取樣點) | FEEDER | [5 empty] | 91 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 22 | 22kV | XL77 | 北七七線(XL77) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL77_DS | XL77_DS (非取樣點) | FEEDER | [5 empty] | 92 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL77 | 北七七線(XL77) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL77_ES | XL77_ES (非取樣點) | FEEDER | [5 empty] | 93 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 22 | 22kV | XL78 | 北七八線(XL78) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL78_DS | XL78_DS (非取樣點) | FEEDER | [5 empty] | 94 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL78 | 北七八線(XL78) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D10_D1 | [8 empty] | 北勢DS.XL78_ES | XL78_ES (非取樣點) | FEEDER | [5 empty] | 95 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 22 | 22kV | 280 | #8SC(280) |  | E1 | 281E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D10_A1 | [8 empty] | 北勢DS.281E | 281E (非取樣點) | SC | [5 empty] | 96 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 22 | 22kV | 280 | #8SC(280) |  | D1 | 281(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D10_A1 | [8 empty] | 北勢DS.281 | 281 (非取樣點) | SC | [5 empty] | 97 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | 490 | #2SSTR(490) |  | D1 | 491(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D10_A1 | [8 empty] | 北勢DS.491 | 491 (非取樣點) | OTHER | [5 empty] | 98 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 22 | 22kV | 490 | #2SSTR(490) |  | E1 | 491E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D10_A1 | [8 empty] | 北勢DS.491E | 491E (非取樣點) | OTHER | [5 empty] | 99 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | 15B1E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aaaz | B2/D10_A1 | [8 empty] | 北勢DS.15B1E | 15B1E (非取樣點) | BUS | [5 empty] | 100 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | 15B2E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/2Bus | [13 empty] | aaaz | B2/D10_A1 | [8 empty] | 北勢DS.15B2E | 15B2E (非取樣點) | BUS | [5 empty] | 101 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | RTU | RTU |  | ADCL1 |  |  | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | [5 empty] | 102 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 0 |  | RTU | RTU |  | ADCH1 |  |  | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.1 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | [5 empty] | 103 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 161 | 161kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 161KV | KV | 161KV #1BUS 電壓 | kV_-210_210(-2000_2000) | aaa | B2/D10_A1 | [8 empty] | 北勢DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | [5 empty] | 104 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D10 | 北勢DS | 161 | 161kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0003 |  |  | 1-83 |  |  | 161KV | KV | 161KV #2BUS 電壓 | kV_-210_210(-2000_2000) | aab | B2/D10_A1 | [8 empty] | 北勢DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | [5 empty] | 105 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D10 | 北勢DS | 161 | 161kV | 1510 | 雲林～北勢線(1510) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 1510 | MW | 雲林北勢線 1510 瓦 | MW_-560_560(-2000_2000) |  | B2/D10_A1 | [8 empty] | 北勢DS.1510_MW | 雲林北勢線 MW | LINE161 | [5 empty] | 106 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D10 | 北勢DS | 161 | 161kV | 1510 | 雲林～北勢線(1510) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 1510 | MVAR | 雲林北勢線 1510 乏 | MVAR_-560_560(-2000_2000) |  | B2/D10_A1 | [8 empty] | 北勢DS.1510_MVAR | 雲林北勢線 MVAR | LINE161 | [5 empty] | 107 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D10 | 北勢DS | 161 | 161kV | 1520 | 斗南～北勢線(1520) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 1520 | MW | 斗南北勢線 1520 瓦 | MW_-560_560(-2000_2000) |  | B2/D10_A1 | [8 empty] | 北勢DS.1520_MW | 斗南北勢線 MW | LINE161 | [5 empty] | 108 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D10 | 北勢DS | 161 | 161kV | 1520 | 斗南～北勢線(1520) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 1520 | MVAR | 斗南北勢線 1520 乏 | MVAR_-560_560(-2000_2000) |  | B2/D10_A1 | [8 empty] | 北勢DS.1520_MVAR | 斗南北勢線 MVAR | LINE161 | [5 empty] | 109 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D10 | 北勢DS | 161 | 161kV | 1530 | 北勢～旭硝子、旭硝二紅線(1530) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | 1530 | MW | 北勢旭硝子旭硝二紅線 1530 瓦 | MW_-560_560(-2000_2000) |  | B2/D10_A1 | [8 empty] | 北勢DS.1530_MW | 旭硝子旭硝二紅 MW | LINE161 | [5 empty] | 110 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D10 | 北勢DS | 161 | 161kV | 1530 | 北勢～旭硝子、旭硝二紅線(1530) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 1530 | MVAR | 北勢旭硝子旭硝二紅線 1530 乏 | MVAR_-560_560(-2000_2000) |  | B2/D10_A1 | [8 empty] | 北勢DS.1530_MVAR | 旭硝子旭硝二紅 MVAR | LINE161 | [5 empty] | 111 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D10 | 北勢DS | 161 | 161kV | 1540 | 北勢～旭硝子、旭硝二白線(1540) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | 1540 | MW | 北勢旭硝子旭硝二白線 1540 瓦 | MW_-560_560(-2000_2000) |  | B2/D10_A1 | [8 empty] | 北勢DS.1540_MW | 旭硝子旭硝二白 MW | LINE161 | [5 empty] | 112 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D10 | 北勢DS | 161 | 161kV | 1540 | 北勢～旭硝子、旭硝二白線(1540) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | 1540 | MVAR | 北勢旭硝子旭硝二白線 1540 乏 | MVAR_-560_560(-2000_2000) |  | B2/D10_A1 | [8 empty] | 北勢DS.1540_MVAR | 旭硝子旭硝二白 MVAR | LINE161 | [5 empty] | 113 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D10 | 北勢DS | 161 | 161kV | 1500 | TIE(1500) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0024 |  |  | 1-98 |  |  | 1500 | A | 161KV TIE 1500 A | A_-2000_2000(-2000_2000) |  | B2/D10_A1 | [8 empty] | 北勢DS.1500TIE_AMP | 1500TIE AMP | TIE | [5 empty] | 114 |  |  |  |  | AI | [5 empty] | C20R1600 | 1520 | 1600 | 1760 | 1968 | 2.27 | -1520 | -1600 | -1760 | -1968 | 1 | 0.01 | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS |  |  | 1DTR | #1DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | #1DTR | ℃ | #1DTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/D10_A1 | [8 empty] | 北勢DS.#1DTR_OIL | #1DTR 油溫 | MTR | [5 empty] | 115 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D10 | 北勢DS |  |  | 1DTR(A) | #1DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | #1ATR | ℃ | #1ATR 線溫 | COIL_-120_120(-2000_2000) |  | B1/D10_A1 | [8 empty] | 北勢DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | [5 empty] | 116 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D10 | 北勢DS |  |  | 1DTR(B) | #1DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0027 |  |  | 1-9B |  |  | #1BTR | ℃ | #1BTR 線溫 | COIL_-120_120(-2000_2000) |  | B1/D10_A1 | [8 empty] | 北勢DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | [5 empty] | 117 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D10 | 北勢DS |  |  | 1DTR(A) | #1DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0028 |  | 0057 | 1-9C |  | 1-39 | #1ATR | 升/降 | #1ATR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D10_A1 | [8 empty] | 北勢DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | [5 empty] | 118 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D10 | 北勢DS |  |  | 1DTR(B) | #1DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0029 |  | 0059 | 1-9D |  | 1-3B | #1BTR | 升/降 | #1BTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D10_A1 | [8 empty] | 北勢DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | [5 empty] | 119 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D10 | 北勢DS |  |  | 3DTR | #3DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | #3DTR | ℃ | #3DTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/D10_A1 | [8 empty] | 北勢DS.#3DTR_OIL | #3DTR 油溫 | MTR | [5 empty] | 120 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D10 | 北勢DS |  |  | 3DTR | #3DTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | #3DTR | ℃ | #3DTR 線溫 | COIL_-120_120(-2000_2000) |  | B1/D10_A1 | [8 empty] | 北勢DS.#3DTR_COIL | #3DTR 線溫 | MTR | [5 empty] | 121 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D10 | 北勢DS |  |  | 3DTR | #3DTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0037 |  | 0065 | 1-A5 |  | 1-41 | #3DTR | 升/降 | #3DTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D10_A1 | [8 empty] | 北勢DS.#3DTR_TAP | #3DTR OLTC TAP | MTR | [5 empty] | 122 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D10 | 北勢DS |  |  | 4DTR | #4DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | #4DTR | ℃ | #4DTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/D10_A1 | [8 empty] | 北勢DS.#4DTR_OIL | #4DTR 油溫 | MTR | [5 empty] | 123 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D10 | 北勢DS |  |  | 4DTR | #4DTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | #4DTR | ℃ | #4DTR 線溫 | COIL_-120_120(-2000_2000) |  | B1/D10_A1 | [8 empty] | 北勢DS.#4DTR_COIL | #4DTR 線溫 | MTR | [5 empty] | 124 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D10 | 北勢DS |  |  | 4DTR | #4DTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0040 |  | 0067 | 1-A8 |  | 1-43 | #4DTR | 升/降 | #4DTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D10_A1 | [8 empty] | 北勢DS.#4DTR_TAP | #4DTR OLTC TAP | MTR | [5 empty] | 125 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D10 | 北勢DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | 310 | MW | 310 瓦 | MW_-54_54(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | [5 empty] | 126 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | 310 | MVAR | 310 乏 | MVAR_-36_36(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | [5 empty] | 127 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | 310 | A | 310 R相電流 | A_-3000_3000(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | [5 empty] | 128 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | 310 | A | 310 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | [5 empty] | 129 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | 310 | A | 310 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | [5 empty] | 130 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL21 | 北一線(XL21) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | XL21 | KVAR | 北一線 XL21 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北一線KVAR | 11KV北一線 KVAR | FEEDER | [5 empty] | 131 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL21 | 北一線(XL21) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | XL21 | A | 北一線 XL21 R相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北一線A1 | 11KV北一線 R相AMP | FEEDER | [5 empty] | 132 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL21 | 北一線(XL21) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | XL21 | A | 北一線 XL21 S相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北一線A2 | 11KV北一線 S相AMP | FEEDER | [5 empty] | 133 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL21 | 北一線(XL21) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | XL21 | A | 北一線 XL21 T相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北一線A3 | 11KV北一線 T相AMP | FEEDER | [5 empty] | 134 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL21 | 北一線(XL21) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | XL21 | A | 北一線 XL21 N相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北一線A0 | 11KV北一線 N相AMP | FEEDER | [5 empty] | 135 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL22 | 北二線(XL22) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | XL22 | KVAR | 北二線 XL22 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北二線KVAR | 11KV北二線 KVAR | FEEDER | [5 empty] | 136 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL22 | 北二線(XL22) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | XL22 | A | 北二線 XL22 R相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北二線A1 | 11KV北二線 R相AMP | FEEDER | [5 empty] | 137 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL22 | 北二線(XL22) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | XL22 | A | 北二線 XL22 S相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北二線A2 | 11KV北二線 S相AMP | FEEDER | [5 empty] | 138 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL22 | 北二線(XL22) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | XL22 | A | 北二線 XL22 T相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北二線A3 | 11KV北二線 T相AMP | FEEDER | [5 empty] | 139 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL22 | 北二線(XL22) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | XL22 | A | 北二線 XL22 N相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北二線A0 | 11KV北二線 N相AMP | FEEDER | [5 empty] | 140 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL23 | 北三線(XL23) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | XL23 | KVAR | 北三線 XL23 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北三線KVAR | 11KV北三線 KVAR | FEEDER | [5 empty] | 141 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL23 | 北三線(XL23) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | XL23 | A | 北三線 XL23 R相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北三線A1 | 11KV北三線 R相AMP | FEEDER | [5 empty] | 142 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL23 | 北三線(XL23) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | XL23 | A | 北三線 XL23 S相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北三線A2 | 11KV北三線 S相AMP | FEEDER | [5 empty] | 143 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL23 | 北三線(XL23) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | XL23 | A | 北三線 XL23 T相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北三線A3 | 11KV北三線 T相AMP | FEEDER | [5 empty] | 144 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL23 | 北三線(XL23) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0060 |  |  | 1-BC |  |  | XL23 | A | 北三線 XL23 N相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北三線A0 | 11KV北三線 N相AMP | FEEDER | [5 empty] | 145 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL24 | 北四線(XL24) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | XL24 | KVAR | 北四線 XL24 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北四線KVAR | 11KV北四線 KVAR | FEEDER | [5 empty] | 146 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL24 | 北四線(XL24) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | XL24 | A | 北四線 XL24 R相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北四線A1 | 11KV北四線 R相AMP | FEEDER | [5 empty] | 147 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL24 | 北四線(XL24) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0063 |  |  | 1-BF |  |  | XL24 | A | 北四線 XL24 S相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北四線A2 | 11KV北四線 S相AMP | FEEDER | [5 empty] | 148 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 0 |  | RTU | RTU |  | ADCL2 |  |  | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | [5 empty] | 149 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 0 |  | RTU | RTU |  | ADCH2 |  |  | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.2 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | [5 empty] | 150 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL24 | 北四線(XL24) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | XL24 | A | 北四線 XL24 T相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北四線A3 | 11KV北四線 T相AMP | FEEDER | [5 empty] | 151 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL24 | 北四線(XL24) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | XL24 | A | 北四線 XL24 N相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北四線A0 | 11KV北四線 N相AMP | FEEDER | [5 empty] | 152 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL25 | 北五線(XL25) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | XL25 | KVAR | 北五線 XL25 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北五線KVAR | 11KV北五線 KVAR | FEEDER | [5 empty] | 153 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL25 | 北五線(XL25) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | XL25 | A | 北五線 XL25 R相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北五線A1 | 11KV北五線 R相AMP | FEEDER | [5 empty] | 154 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL25 | 北五線(XL25) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | XL25 | A | 北五線 XL25 S相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北五線A2 | 11KV北五線 S相AMP | FEEDER | [5 empty] | 155 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL25 | 北五線(XL25) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | XL25 | A | 北五線 XL25 T相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北五線A3 | 11KV北五線 T相AMP | FEEDER | [5 empty] | 156 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL25 | 北五線(XL25) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | XL25 | A | 北五線 XL25 N相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北五線A0 | 11KV北五線 N相AMP | FEEDER | [5 empty] | 157 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 1ABUS | #1ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0073 |  |  | 1-C9 |  |  | #1A PT | KV | 11KV #1A 電壓 | kV_-9_9(-2000_2000) | aaa | B3/D10_A1 | [8 empty] | 北勢DS.11KV#1ABUS_KV | 11KV #1ABUS KV | BUS | [5 empty] | 158 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D10 | 北勢DS | 11 | 11kV | 100 | TIE(100) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | 100 | A | 100 TIE R相電流 | A_-2000_2000(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.11KV_100_A1 | 11KV 100 R相AMP | TIE | [5 empty] | 159 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 100 | TIE(100) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | 100 | A | 100 TIE S相電流 | A_-2000_2000(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.11KV_100_A2 | 11KV 100 S相AMP | TIE | [5 empty] | 160 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 100 | TIE(100) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | 100 | A | 100 TIE T相電流 | A_-2000_2000(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.11KV_100_A3 | 11KV 100 T相AMP | TIE | [5 empty] | 161 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 1BBUS | #1BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0077 |  |  | 1-CD |  |  | #1B PT | KV | 11KV #1B 電壓 | kV_-9_9(-2000_2000) | aba | B3/D10_A1 | [8 empty] | 北勢DS.11KV#1BBUS_KV | 11KV #1BBUS KV | BUS | [5 empty] | 162 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D10 | 北勢DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | 320 | MW | 320 瓦 | MW_-54_54(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | [5 empty] | 163 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | 320 | MVAR | 320 乏 | MVAR_-36_36(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | [5 empty] | 164 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | 320 | A | 320 R相電流 | A_-3000_3000(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | [5 empty] | 165 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | 320 | A | 320 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | [5 empty] | 166 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | 320 | A | 320 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | [5 empty] | 167 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL26 | 北六線(XL26) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | XL26 | KVAR | 北六線 XL26 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六線KVAR | 11KV北六線 KVAR | FEEDER | [5 empty] | 168 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL26 | 北六線(XL26) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | XL26 | A | 北六線 XL26 R相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六線A1 | 11KV北六線 R相AMP | FEEDER | [5 empty] | 169 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL26 | 北六線(XL26) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | XL26 | A | 北六線 XL26 S相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六線A2 | 11KV北六線 S相AMP | FEEDER | [5 empty] | 170 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL26 | 北六線(XL26) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | XL26 | A | 北六線 XL26 T相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六線A3 | 11KV北六線 T相AMP | FEEDER | [5 empty] | 171 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL26 | 北六線(XL26) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | XL26 | A | 北六線 XL26 N相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六線A0 | 11KV北六線 N相AMP | FEEDER | [5 empty] | 172 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL27 | 北七線(XL27) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | XL27 | KVAR | 北七線 XL27 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七線KVAR | 11KV北七線 KVAR | FEEDER | [5 empty] | 173 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL27 | 北七線(XL27) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | XL27 | A | 北七線 XL27 R相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七線A1 | 11KV北七線 R相AMP | FEEDER | [5 empty] | 174 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL27 | 北七線(XL27) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | XL27 | A | 北七線 XL27 S相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七線A2 | 11KV北七線 S相AMP | FEEDER | [5 empty] | 175 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL27 | 北七線(XL27) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | XL27 | A | 北七線 XL27 T相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七線A3 | 11KV北七線 T相AMP | FEEDER | [5 empty] | 176 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL27 | 北七線(XL27) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | XL27 | A | 北七線 XL27 N相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七線A0 | 11KV北七線 N相AMP | FEEDER | [5 empty] | 177 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL28 | 北八線(XL28) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | XL28 | KVAR | 北八線 XL28 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北八線KVAR | 11KV北八線 KVAR | FEEDER | [5 empty] | 178 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL28 | 北八線(XL28) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | XL28 | A | 北八線 XL28 R相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北八線A1 | 11KV北八線 R相AMP | FEEDER | [5 empty] | 179 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL28 | 北八線(XL28) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | XL28 | A | 北八線 XL28 S相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北八線A2 | 11KV北八線 S相AMP | FEEDER | [5 empty] | 180 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL28 | 北八線(XL28) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | XL28 | A | 北八線 XL28 T相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北八線A3 | 11KV北八線 T相AMP | FEEDER | [5 empty] | 181 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL28 | 北八線(XL28) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | XL28 | A | 北八線 XL28 N相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北八線A0 | 11KV北八線 N相AMP | FEEDER | [5 empty] | 182 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL29 | 北九線(XL29) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0098 |  |  | 1-E2 |  |  | XL29 | KVAR | 北九線 XL29 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北九線KVAR | 11KV北九線 KVAR | FEEDER | [5 empty] | 183 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL29 | 北九線(XL29) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | XL29 | A | 北九線 XL29 R相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北九線A1 | 11KV北九線 R相AMP | FEEDER | [5 empty] | 184 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL29 | 北九線(XL29) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | XL29 | A | 北九線 XL29 S相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北九線A2 | 11KV北九線 S相AMP | FEEDER | [5 empty] | 185 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL29 | 北九線(XL29) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0101 |  |  | 1-E5 |  |  | XL29 | A | 北九線 XL29 T相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北九線A3 | 11KV北九線 T相AMP | FEEDER | [5 empty] | 186 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL29 | 北九線(XL29) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | XL29 | A | 北九線 XL29 N相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北九線A0 | 11KV北九線 N相AMP | FEEDER | [5 empty] | 187 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL30 | 北十線(XL30) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | XL30 | KVAR | 北十線 XL30 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北十線KVAR | 11KV北十線 KVAR | FEEDER | [5 empty] | 188 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL30 | 北十線(XL30) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | XL30 | A | 北十線 XL30 R相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北十線A1 | 11KV北十線 R相AMP | FEEDER | [5 empty] | 189 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL30 | 北十線(XL30) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | XL30 | A | 北十線 XL30 S相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北十線A2 | 11KV北十線 S相AMP | FEEDER | [5 empty] | 190 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL30 | 北十線(XL30) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | XL30 | A | 北十線 XL30 T相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北十線A3 | 11KV北十線 T相AMP | FEEDER | [5 empty] | 191 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | XL30 | 北十線(XL30) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | XL30 | A | 北十線 XL30 N相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北十線A0 | 11KV北十線 N相AMP | FEEDER | [5 empty] | 192 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 350 | #3DTR(350) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | 350 | MW | 350 瓦 | MW_-108_108(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.#3DTR_MW | #3DTR二次側 MW | MTR | [5 empty] | 193 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.216 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 350 | #3DTR(350) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | 350 | MVAR | 350 乏 | MVAR_-72_72(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.#3DTR_MVAR | #3DTR二次側 MVAR | MTR | [5 empty] | 194 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 350 | #3DTR(350) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | 350 | A | 350 R相電流 | A_-3000_3000(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.#3DTR_A1 | #3DTR二次側 R相AMP | MTR | [5 empty] | 195 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 350 | #3DTR(350) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | 350 | A | 350 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.#3DTR_A2 | #3DTR二次側 S相AMP | MTR | [5 empty] | 196 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 350 | #3DTR(350) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | 350 | A | 350 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.#3DTR_A3 | #3DTR二次側 T相AMP | MTR | [5 empty] | 197 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 370 | #4DTR(370) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | 360 | MW | 370 瓦 | MW_-108_108(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.#4DTR_MW | #4DTR二次側 MW | MTR | [5 empty] | 198 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.216 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 370 | #4DTR(370) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | 360 | MVAR | 370 乏 | MVAR_-72_72(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.#4DTR_MVAR | #4DTR二次側 MVAR | MTR | [5 empty] | 199 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 370 | #4DTR(370) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | 370 | A | 370 R相電流 | A_-3000_3000(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.#4DTR_A1 | #4DTR二次側 R相AMP | MTR | [5 empty] | 200 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 370 | #4DTR(370) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | 370 | A | 370 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.#4DTR_A2 | #4DTR二次側 S相AMP | MTR | [5 empty] | 201 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 370 | #4DTR(370) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | 370 | A | 370 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.#4DTR_A3 | #4DTR二次側 T相AMP | MTR | [5 empty] | 202 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 0 |  | RTU | RTU |  | ADCL3 |  |  | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.3 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | [5 empty] | 203 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 0 |  | RTU | RTU |  | ADCH3 |  |  | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.3 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | [5 empty] | 204 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL61 | 北六一線(XL61) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0185 |  |  | 2-B9 |  |  | XL61 | KVAR | 北六一線 XL61 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六一線KVAR | 23KV北六一線 KVAR | FEEDER | [5 empty] | 205 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL61 | 北六一線(XL61) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0186 |  |  | 2-BA |  |  | XL61 | A | 北六一線 XL61 R相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六一線A1 | 23KV北六一線 R相AMP | FEEDER | [5 empty] | 206 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL61 | 北六一線(XL61) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0187 |  |  | 2-BB |  |  | XL61 | A | 北六一線 XL61 S相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六一線A2 | 23KV北六一線 S相AMP | FEEDER | [5 empty] | 207 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL61 | 北六一線(XL61) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0188 |  |  | 2-BC |  |  | XL61 | A | 北六一線 XL61 T相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六一線A3 | 23KV北六一線 T相AMP | FEEDER | [5 empty] | 208 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL61 | 北六一線(XL61) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0189 |  |  | 2-BD |  |  | XL61 | A | 北六一線 XL61 N相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六一線A0 | 23KV北六一線 N相AMP | FEEDER | [5 empty] | 209 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL62 | 北六二線(XL62) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0190 |  |  | 2-BE |  |  | XL62 | KVAR | 北六二線 XL62 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六二線KVAR | 23KV北六二線 KVAR | FEEDER | [5 empty] | 210 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL62 | 北六二線(XL62) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0191 |  |  | 2-BF |  |  | XL62 | A | 北六二線 XL62 R相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六二線A1 | 23KV北六二線 R相AMP | FEEDER | [5 empty] | 211 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 0 |  | RTU | RTU |  | ADCL4 |  |  | MvMoment | No4 AI參考點 10% |  | Y |  | AI | [6 empty] | 0192 |  |  | 2-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.4 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | [5 empty] | 212 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 0 |  | RTU | RTU |  | ADCH4 |  |  | MvMoment | No4 AI參考點 90% |  | Y |  | AI | [6 empty] | 0193 |  |  | 2-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.4 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | [5 empty] | 213 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL62 | 北六二線(XL62) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0194 |  |  | 2-C2 |  |  | XL62 | A | 北六二線 XL62 S相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六二線A2 | 23KV北六二線 S相AMP | FEEDER | [5 empty] | 214 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL62 | 北六二線(XL62) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0195 |  |  | 2-C3 |  |  | XL62 | A | 北六二線 XL62 T相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六二線A3 | 23KV北六二線 T相AMP | FEEDER | [5 empty] | 215 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL62 | 北六二線(XL62) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0196 |  |  | 2-C4 |  |  | XL62 | A | 北六二線 XL62 N相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六二線A0 | 23KV北六二線 N相AMP | FEEDER | [5 empty] | 216 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL63 | 北六三線(XL63) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0197 |  |  | 2-C5 |  |  | XL63 | KVAR | 北六三線 XL63 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六三線KVAR | 23KV北六三線 KVAR | FEEDER | [5 empty] | 217 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL63 | 北六三線(XL63) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0198 |  |  | 2-C6 |  |  | XL63 | A | 北六三線 XL63 R相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六三線A1 | 23KV北六三線 R相AMP | FEEDER | [5 empty] | 218 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL63 | 北六三線(XL63) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0199 |  |  | 2-C7 |  |  | XL63 | A | 北六三線 XL63 S相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六三線A2 | 23KV北六三線 S相AMP | FEEDER | [5 empty] | 219 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL63 | 北六三線(XL63) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0200 |  |  | 2-C8 |  |  | XL63 | A | 北六三線 XL63 T相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六三線A3 | 23KV北六三線 T相AMP | FEEDER | [5 empty] | 220 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL63 | 北六三線(XL63) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0201 |  |  | 2-C9 |  |  | XL63 | A | 北六三線 XL63 N相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六三線A0 | 23KV北六三線 N相AMP | FEEDER | [5 empty] | 221 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL64 | 北六四線(XL64) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0202 |  |  | 2-CA |  |  | XL64 | KVAR | 北六四線 XL64 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六四線KVAR | 23KV北六四線 KVAR | FEEDER | [5 empty] | 222 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL64 | 北六四線(XL64) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0203 |  |  | 2-CB |  |  | XL64 | A | 北六四線 XL64 R相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六四線A1 | 23KV北六四線 R相AMP | FEEDER | [5 empty] | 223 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL64 | 北六四線(XL64) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0204 |  |  | 2-CC |  |  | XL64 | A | 北六四線 XL64 S相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六四線A2 | 23KV北六四線 S相AMP | FEEDER | [5 empty] | 224 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL64 | 北六四線(XL64) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0205 |  |  | 2-CD |  |  | XL64 | A | 北六四線 XL64 T相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六四線A3 | 23KV北六四線 T相AMP | FEEDER | [5 empty] | 225 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL64 | 北六四線(XL64) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0206 |  |  | 2-CE |  |  | XL64 | A | 北六四線 XL64 N相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六四線A0 | 23KV北六四線 N相AMP | FEEDER | [5 empty] | 226 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL65 | 北六五線(XL65) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0207 |  |  | 2-CF |  |  | XL65 | KVAR | 北六五線 XL65 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六五線KVAR | 23KV北六五線 KVAR | FEEDER | [5 empty] | 227 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL65 | 北六五線(XL65) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0208 |  |  | 2-D0 |  |  | XL65 | A | 北六五線 XL65 R相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六五線A1 | 23KV北六五線 R相AMP | FEEDER | [5 empty] | 228 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL65 | 北六五線(XL65) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0209 |  |  | 2-D1 |  |  | XL65 | A | 北六五線 XL65 S相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六五線A2 | 23KV北六五線 S相AMP | FEEDER | [5 empty] | 229 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL65 | 北六五線(XL65) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0210 |  |  | 2-D2 |  |  | XL65 | A | 北六五線 XL65 T相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六五線A3 | 23KV北六五線 T相AMP | FEEDER | [5 empty] | 230 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL65 | 北六五線(XL65) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0211 |  |  | 2-D3 |  |  | XL65 | A | 北六五線 XL65 N相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六五線A0 | 23KV北六五線 N相AMP | FEEDER | [5 empty] | 231 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL66 | 北六六線(XL66) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0212 |  |  | 2-D4 |  |  | XL66 | KVAR | 北六六線 XL66 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六六線KVAR | 23KV北六六線 KVAR | FEEDER | [5 empty] | 232 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL66 | 北六六線(XL66) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0213 |  |  | 2-D5 |  |  | XL66 | A | 北六六線 XL66 R相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六六線A1 | 23KV北六六線 R相AMP | FEEDER | [5 empty] | 233 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL66 | 北六六線(XL66) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0214 |  |  | 2-D6 |  |  | XL66 | A | 北六六線 XL66 S相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六六線A2 | 23KV北六六線 S相AMP | FEEDER | [5 empty] | 234 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL66 | 北六六線(XL66) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0215 |  |  | 2-D7 |  |  | XL66 | A | 北六六線 XL66 T相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六六線A3 | 23KV北六六線 T相AMP | FEEDER | [5 empty] | 235 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL66 | 北六六線(XL66) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0216 |  |  | 2-D8 |  |  | XL66 | A | 北六六線 XL66 N相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六六線A0 | 23KV北六六線 N相AMP | FEEDER | [5 empty] | 236 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL67 | 北六七線(XL67) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0217 |  |  | 2-D9 |  |  | XL67 | KVAR | 北六七線 XL67 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六七線KVAR | 23KV北六七線 KVAR | FEEDER | [5 empty] | 237 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL67 | 北六七線(XL67) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0218 |  |  | 2-DA |  |  | XL67 | A | 北六七線 XL67 R相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六七線A1 | 23KV北六七線 R相AMP | FEEDER | [5 empty] | 238 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL67 | 北六七線(XL67) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0219 |  |  | 2-DB |  |  | XL67 | A | 北六七線 XL67 S相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六七線A2 | 23KV北六七線 S相AMP | FEEDER | [5 empty] | 239 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL67 | 北六七線(XL67) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0220 |  |  | 2-DC |  |  | XL67 | A | 北六七線 XL67 T相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六七線A3 | 23KV北六七線 T相AMP | FEEDER | [5 empty] | 240 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL67 | 北六七線(XL67) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0221 |  |  | 2-DD |  |  | XL67 | A | 北六七線 XL67 N相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六七線A0 | 23KV北六七線 N相AMP | FEEDER | [5 empty] | 241 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL68 | 北六八線(XL68) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0222 |  |  | 2-DE |  |  | XL68 | KVAR | 北六八線 XL68 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六八線KVAR | 23KV北六八線 KVAR | FEEDER | [5 empty] | 242 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL68 | 北六八線(XL68) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0223 |  |  | 2-DF |  |  | XL68 | A | 北六八線 XL68 R相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六八線A1 | 23KV北六八線 R相AMP | FEEDER | [5 empty] | 243 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL68 | 北六八線(XL68) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0224 |  |  | 2-E0 |  |  | XL68 | A | 北六八線 XL68 S相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六八線A2 | 23KV北六八線 S相AMP | FEEDER | [5 empty] | 244 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL68 | 北六八線(XL68) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0225 |  |  | 2-E1 |  |  | XL68 | A | 北六八線 XL68 T相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六八線A3 | 23KV北六八線 T相AMP | FEEDER | [5 empty] | 245 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL68 | 北六八線(XL68) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0226 |  |  | 2-E2 |  |  | XL68 | A | 北六八線 XL68 N相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北六八線A0 | 23KV北六八線 N相AMP | FEEDER | [5 empty] | 246 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 3BUS | #3BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0227 |  |  | 2-E3 |  |  | #3 PT | KV | 22KV #3PT 電壓 | kV_-18_18(-2000_2000) | baa | B3/D10_A1 | [8 empty] | 北勢DS.23KV#3BUS_KV | 23KV #3BUS KV | BUS | [5 empty] | 247 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D10 | 北勢DS | 22 | 22kV | 300 | TIE(300) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0228 |  |  | 2-E4 |  |  | 300 | A | 300 TIE R相電流 | A_-2000_2000(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.23KV_300_A1 | 23KV 300 R相AMP | TIE | [5 empty] | 248 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 300 | TIE(300) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0229 |  |  | 2-E5 |  |  | 300 | A | 300 TIE S相電流 | A_-2000_2000(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.23KV_300_A2 | 23KV 300 S相AMP | TIE | [5 empty] | 249 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 300 | TIE(300) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0230 |  |  | 2-E6 |  |  | 300 | A | 300 TIE T相電流 | A_-2000_2000(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.23KV_300_A3 | 23KV 300 T相AMP | TIE | [5 empty] | 250 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 4BUS | #4BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0231 |  |  | 2-E7 |  |  | #4 PT | KV | 22KV #4PT 電壓 | kV_-18_18(-2000_2000) | bba | B3/D10_A1 | [8 empty] | 北勢DS.23KV#4BUS_KV | 23KV #4BUS KV | BUS | [5 empty] | 251 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D10 | 北勢DS | 22 | 22kV | XL71 | 北七一線(XL71) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0232 |  |  | 2-E8 |  |  | XL71 | KVAR | 北七一線 XL71 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七一線KVAR | 23KV北七一線 KVAR | FEEDER | [5 empty] | 252 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL71 | 北七一線(XL71) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0233 |  |  | 2-E9 |  |  | XL71 | A | 北七一線 XL71 R相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七一線A1 | 23KV北七一線 R相AMP | FEEDER | [5 empty] | 253 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL71 | 北七一線(XL71) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0234 |  |  | 2-EA |  |  | XL71 | A | 北七一線 XL71 S相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七一線A2 | 23KV北七一線 S相AMP | FEEDER | [5 empty] | 254 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL71 | 北七一線(XL71) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0235 |  |  | 2-EB |  |  | XL71 | A | 北七一線 XL71 T相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七一線A3 | 23KV北七一線 T相AMP | FEEDER | [5 empty] | 255 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL71 | 北七一線(XL71) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0236 |  |  | 2-EC |  |  | XL71 | A | 北七一線 XL71 N相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七一線A0 | 23KV北七一線 N相AMP | FEEDER | [5 empty] | 256 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL72 | 北七二線(XL72) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0237 |  |  | 2-ED |  |  | XL72 | KVAR | 北七二線 XL72 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七二線KVAR | 23KV北七二線 KVAR | FEEDER | [5 empty] | 257 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL72 | 北七二線(XL72) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0238 |  |  | 2-EE |  |  | XL72 | A | 北七二線 XL72 R相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七二線A1 | 23KV北七二線 R相AMP | FEEDER | [5 empty] | 258 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL72 | 北七二線(XL72) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0239 |  |  | 2-EF |  |  | XL72 | A | 北七二線 XL72 S相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七二線A2 | 23KV北七二線 S相AMP | FEEDER | [5 empty] | 259 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL72 | 北七二線(XL72) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0240 |  |  | 2-F0 |  |  | XL72 | A | 北七二線 XL72 T相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七二線A3 | 23KV北七二線 T相AMP | FEEDER | [5 empty] | 260 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL72 | 北七二線(XL72) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0241 |  |  | 2-F1 |  |  | XL72 | A | 北七二線 XL72 N相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七二線A0 | 23KV北七二線 N相AMP | FEEDER | [5 empty] | 261 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL73 | 北七三線(XL73) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0242 |  |  | 2-F2 |  |  | XL73 | KVAR | 北七三線 XL73 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七三線KVAR | 23KV北七三線 KVAR | FEEDER | [5 empty] | 262 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL73 | 北七三線(XL73) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0243 |  |  | 2-F3 |  |  | XL73 | A | 北七三線 XL73 R相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七三線A1 | 23KV北七三線 R相AMP | FEEDER | [5 empty] | 263 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL73 | 北七三線(XL73) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0244 |  |  | 2-F4 |  |  | XL73 | A | 北七三線 XL73 S相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七三線A2 | 23KV北七三線 S相AMP | FEEDER | [5 empty] | 264 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL73 | 北七三線(XL73) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0245 |  |  | 2-F5 |  |  | XL73 | A | 北七三線 XL73 T相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七三線A3 | 23KV北七三線 T相AMP | FEEDER | [5 empty] | 265 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL73 | 北七三線(XL73) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0246 |  |  | 2-F6 |  |  | XL73 | A | 北七三線 XL73 N相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七三線A0 | 23KV北七三線 N相AMP | FEEDER | [5 empty] | 266 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL74 | 北七四線(XL74) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0247 |  |  | 2-F7 |  |  | XL74 | KVAR | 北七四線 XL74 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七四線KVAR | 23KV北七四線 KVAR | FEEDER | [5 empty] | 267 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL74 | 北七四線(XL74) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0248 |  |  | 2-F8 |  |  | XL74 | A | 北七四線 XL74 R相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七四線A1 | 23KV北七四線 R相AMP | FEEDER | [5 empty] | 268 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL74 | 北七四線(XL74) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0249 |  |  | 2-F9 |  |  | XL74 | A | 北七四線 XL74 S相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七四線A2 | 23KV北七四線 S相AMP | FEEDER | [5 empty] | 269 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL74 | 北七四線(XL74) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0250 |  |  | 2-FA |  |  | XL74 | A | 北七四線 XL74 T相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七四線A3 | 23KV北七四線 T相AMP | FEEDER | [5 empty] | 270 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL74 | 北七四線(XL74) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0251 |  |  | 2-FB |  |  | XL74 | A | 北七四線 XL74 N相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七四線A0 | 23KV北七四線 N相AMP | FEEDER | [5 empty] | 271 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 0 |  | StaDev | 所內設施 |  | DCV_P |  |  | MvMoment | 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0252 |  |  | 2-FC |  |  | DC |  | DC-P 電壓 | kV_-150_150(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.直流P電源電壓 | 直流P電源電壓 | OTHER | [5 empty] | 272 |  |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 | 0.01 | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D10 | 北勢DS | 0 |  | StaDev | 所內設施 |  | DCV_N |  |  | MvMoment | 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0253 |  |  | 2-FD |  |  | DC |  | DC-N 電壓 | kV_-150_150(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.直流N電源電壓 | 直流N電源電壓 | OTHER | [5 empty] | 273 |  |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 | 0.01 | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D10 | 北勢DS | 0 |  | RTU | RTU |  | ADCL5 |  |  | MvMoment | No5 AI參考點 10% |  | Y |  | AI | [6 empty] | 0256 |  |  | 3-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.5 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.AI_ADCL5 | AI 10%參考點 ADCL5 | OTHER | [5 empty] | 274 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 0 |  | RTU | RTU |  | ADCH5 |  |  | MvMoment | No5 AI參考點 90% |  | Y |  | AI | [6 empty] | 0257 |  |  | 3-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.5 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D10_A1 | [8 empty] | 北勢DS.AI_ADCH5 | AI 90%參考點 ADCH5 | OTHER | [5 empty] | 275 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL75 | 北七五線(XL75) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0258 |  |  | 3-82 |  |  | XL75 | KVAR | 北七五線 XL75 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七五線KVAR | 23KV北七五線 KVAR | FEEDER | [5 empty] | 276 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL75 | 北七五線(XL75) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0259 |  |  | 3-83 |  |  | XL75 | A | 北七五線 XL75 R相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七五線A1 | 23KV北七五線 R相AMP | FEEDER | [5 empty] | 277 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL75 | 北七五線(XL75) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0260 |  |  | 3-84 |  |  | XL75 | A | 北七五線 XL75 S相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七五線A2 | 23KV北七五線 S相AMP | FEEDER | [5 empty] | 278 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL75 | 北七五線(XL75) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0261 |  |  | 3-85 |  |  | XL75 | A | 北七五線 XL75 T相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七五線A3 | 23KV北七五線 T相AMP | FEEDER | [5 empty] | 279 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL75 | 北七五線(XL75) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0262 |  |  | 3-86 |  |  | XL75 | A | 北七五線 XL75 N相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七五線A0 | 23KV北七五線 N相AMP | FEEDER | [5 empty] | 280 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL76 | 北七六線(XL76) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0263 |  |  | 3-87 |  |  | XL76 | KVAR | 北七六線 XL76 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七六線KVAR | 23KV北七六線 KVAR | FEEDER | [5 empty] | 281 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL76 | 北七六線(XL76) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0264 |  |  | 3-88 |  |  | XL76 | A | 北七六線 XL76 R相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七六線A1 | 23KV北七六線 R相AMP | FEEDER | [5 empty] | 282 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL76 | 北七六線(XL76) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0265 |  |  | 3-89 |  |  | XL76 | A | 北七六線 XL76 S相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七六線A2 | 23KV北七六線 S相AMP | FEEDER | [5 empty] | 283 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL76 | 北七六線(XL76) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0266 |  |  | 3-8A |  |  | XL76 | A | 北七六線 XL76 T相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七六線A3 | 23KV北七六線 T相AMP | FEEDER | [5 empty] | 284 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL76 | 北七六線(XL76) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0267 |  |  | 3-8B |  |  | XL76 | A | 北七六線 XL76 N相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七六線A0 | 23KV北七六線 N相AMP | FEEDER | [5 empty] | 285 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL77 | 北七七線(XL77) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0268 |  |  | 3-8C |  |  | XL77 | KVAR | 北七七線 XL77 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七七線KVAR | 23KV北七七線 KVAR | FEEDER | [5 empty] | 286 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL77 | 北七七線(XL77) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0269 |  |  | 3-8D |  |  | XL77 | A | 北七七線 XL77 R相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七七線A1 | 23KV北七七線 R相AMP | FEEDER | [5 empty] | 287 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL77 | 北七七線(XL77) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0270 |  |  | 3-8E |  |  | XL77 | A | 北七七線 XL77 S相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七七線A2 | 23KV北七七線 S相AMP | FEEDER | [5 empty] | 288 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL77 | 北七七線(XL77) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0271 |  |  | 3-8F |  |  | XL77 | A | 北七七線 XL77 T相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七七線A3 | 23KV北七七線 T相AMP | FEEDER | [5 empty] | 289 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL77 | 北七七線(XL77) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0272 |  |  | 3-90 |  |  | XL77 | A | 北七七線 XL77 N相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七七線A0 | 23KV北七七線 N相AMP | FEEDER | [5 empty] | 290 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL78 | 北七八線(XL78) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0273 |  |  | 3-91 |  |  | XL78 | KVAR | 北七八線 XL78 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七八線KVAR | 23KV北七八線 KVAR | FEEDER | [5 empty] | 291 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL78 | 北七八線(XL78) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0274 |  |  | 3-92 |  |  | XL78 | A | 北七八線 XL78 R相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七八線A1 | 23KV北七八線 R相AMP | FEEDER | [5 empty] | 292 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL78 | 北七八線(XL78) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0275 |  |  | 3-93 |  |  | XL78 | A | 北七八線 XL78 S相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七八線A2 | 23KV北七八線 S相AMP | FEEDER | [5 empty] | 293 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL78 | 北七八線(XL78) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0276 |  |  | 3-94 |  |  | XL78 | A | 北七八線 XL78 T相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七八線A3 | 23KV北七八線 T相AMP | FEEDER | [5 empty] | 294 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | XL78 | 北七八線(XL78) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0277 |  |  | 3-95 |  |  | XL78 | A | 北七八線 XL78 N相電流 | A_-600_600(-2000_2000) |  | B2/D10_D1 | [8 empty] | 北勢DS.北七八線A0 | 23KV北七八線 N相AMP | FEEDER | [5 empty] | 295 |  |  |  |  | AI | [5 empty] | LGA0_80 | 64 | 72 | 76 | 600 | 0.4 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 161 | 161kV | 1510 | 雲林～北勢線(1510) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P03D10/T2 |  | 0000 |  | 0001 | 1-00-00 |  | 1-01 | 1510 | ON/OFF | 雲林北勢線 1510 CB |  | aaca | B2/D10_A1 | [8 empty] | 北勢DS.1510_CB | 1510(雲林北勢線) CB | LINE161 | [5 empty] | 296 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 161 | 161kV | 1510 | 雲林～北勢線(1510) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0001 |  |  | 1-00-01 |  |  | 1510 | 87A | 雲林北勢線 1510 87A |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1510_87A | 雲林北勢線(1510) 87RY | LINE161 | [5 empty] | 297 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1510 | 雲林～北勢線(1510) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | 1510 | PHA | 雲林北勢線 1510 PHA |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1510_PHA | 雲林北勢線(1510) 相間RY | LINE161 | [5 empty] | 298 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1510 | 雲林～北勢線(1510) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0004 |  |  | 1-00-04 |  |  | 1510 | GDA | 雲林北勢線 1510 GDA |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1510_GDA | 雲林北勢線(1510) 接地RY | LINE161 | [5 empty] | 299 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1520 | 斗南～北勢線(1520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D08D10/T2 |  | 0005 |  | 0002 | 1-00-05 |  | 1-02 | 1520 | ON/OFF | 斗南北勢線 1520 CB |  | aaea | B2/D10_A1 | [8 empty] | 北勢DS.1520_CB | 1520(斗南北勢線) CB | LINE161 | [5 empty] | 300 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 161 | 161kV | 1520 | 斗南～北勢線(1520) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | 1520 | 87A1 | 斗南北勢線 1520 87A1 |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1520_87A1 | 斗南北勢線(1520)第一套87RY | OTHER | [5 empty] | 301 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1520 | 斗南～北勢線(1520) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-07 |  |  | 1520 | 87A2 | 斗南北勢線 1520 87A2 |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1520_87A2 | 斗南北勢線(1520)第二套87RY | OTHER | [5 empty] | 302 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1520 | 斗南～北勢線(1520) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-01-00 |  |  | 1520 | PHA | 斗南北勢線 1520 PHA |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1520_PHA | 斗南北勢線(1520) 相間RY | LINE161 | [5 empty] | 303 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1520 | 斗南～北勢線(1520) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | 1520 | GDA | 斗南北勢線 1520GDA |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1520_GDA | 斗南北勢線(1520) 接地RY | LINE161 | [5 empty] | 304 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1530 | 北勢～旭硝子、旭硝二紅線(1530) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D10TN07R/T2 |  | 0010 |  | 0003 | 1-01-02 |  | 1-03 | 1530 | ON/OFF | 北勢旭硝子旭硝二紅線 1530 CB |  | aaia | B2/D10_A1 | [8 empty] | 北勢DS.1530_CB | 1530(旭硝子旭硝二紅) CB | LINE161 | [5 empty] | 305 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 161 | 161kV | 1530 | 北勢～旭硝子、旭硝二紅線(1530) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-03 |  |  | 1530 | 87A | 北勢旭硝子旭硝二紅線 1530 187A |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1530_87A1 | 旭硝子旭硝二紅(1530) 87A1 | OTHER | [5 empty] | 306 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1530 | 北勢～旭硝子、旭硝二紅線(1530) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0012 |  |  | 1-01-04 |  |  | 1530 | 87A | 北勢旭硝子旭硝二紅線 1530 287A |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1530_87A2 | 旭硝子旭硝二紅(1530) 87A2 | OTHER | [5 empty] | 307 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1530 | 北勢～旭硝子、旭硝二紅線(1530) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0013 |  |  | 1-01-05 |  |  | 1530 | PHA | 北勢旭硝子旭硝二紅線 1530 PHA |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1530_PHA | 旭硝子旭硝二紅(1530) 相間RY | LINE161 | [5 empty] | 308 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1530 | 北勢～旭硝子、旭硝二紅線(1530) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-06 |  |  | 1530 | GDA | 北勢旭硝子旭硝二紅線 1530 GDA |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1530_GDA | 旭硝子旭硝二紅(1530) 接地RY | LINE161 | [5 empty] | 309 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1540 | 北勢～旭硝子、旭硝二白線(1540) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D10TN08W/T2 |  | 0015 |  | 0004 | 1-01-07 |  | 1-04 | 1540 | ON/OFF | 北勢旭硝子旭硝二白線 1540 CB |  | aaja | B2/D10_A1 | [8 empty] | 北勢DS.1540_CB | 1540(旭硝子旭硝二白) CB | LINE161 | [5 empty] | 310 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 161 | 161kV | 1540 | 北勢～旭硝子、旭硝二白線(1540) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-02-00 |  |  | 1540 | 87A | 北勢旭硝子旭硝二白線 1540 187A |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1540_87A1 | 旭硝子旭硝二白(1540) #1 87RY | LINE161 | [5 empty] | 311 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1540 | 北勢～旭硝子、旭硝二白線(1540) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0017 |  |  | 1-02-01 |  |  | 1540 | 87A | 北勢旭硝子旭硝二白線 1540 287A |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1540_87A2 | 旭硝子旭硝二白(1540) #2 87RY | LINE161 | [5 empty] | 312 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1540 | 北勢～旭硝子、旭硝二白線(1540) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 |  |  | 1-02-02 |  |  | 1540 | PHA | 北勢旭硝子旭硝二白線 1540 PHA |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1540_PHA | 旭硝子旭硝二白(1540) 相間RY | LINE161 | [5 empty] | 313 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1540 | 北勢～旭硝子、旭硝二白線(1540) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0019 |  |  | 1-02-03 |  |  | 1540 | GDA | 北勢旭硝子旭硝二白線 1540 GDA |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1540_GDA | 旭硝子旭硝二白(1540) 接地RY | LINE161 | [5 empty] | 314 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0050 |  | 0011 | 1-06-02 |  | 1-0B | 1500 | ON/OFF | 161KV TIE 1500 CB |  | aafz | B2/D10_A1 | [8 empty] | 北勢DS.1500_CB | 1500(TIE) CB | TIE | [5 empty] | 315 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0051 |  |  | 1-06-03 |  |  | 1500 | 50A | 161KV TIE 1500 50 A |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1500_50A | 161KV TIE(1500) 50RY | TIE | [5 empty] | 316 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | 161KV BUS | 87B1A | 161KV #1BUS 87A |  |  | B2/D10_A1 | [8 empty] | 北勢DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | [5 empty] | 317 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0053 |  |  | 1-06-05 |  |  | 161KV BUS | 87B2A | 161KV #2BUS 87A |  |  | B2/D10_A1 | [8 empty] | 北勢DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | [5 empty] | 318 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0054 |  |  | 1-06-06 |  |  | RCA | ON/OFF | RCA 復閉電驛警報 |  |  | B3/D10_A1 | [8 empty] | 北勢DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | [5 empty] | 319 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0055 |  |  | 1-06-07 |  |  | OSCA | A/N | 161KV示波器啟動警報OSCA |  |  | B3/D10_A1 | [8 empty] | 北勢DS.161KV_OSCA | 161KV示波器啟動警報 | OTHER | [5 empty] | 320 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/1DTR |  | 0056 |  | 0012 | 1-07-00 |  | 1-0C | 1750 | ON/OFF | #1DTR 1750 CB |  | aabb | ELEM/D10_A1 | [8 empty] | 北勢DS.1750_CB | 1750(#1DTR) CB | MTR | [5 empty] | 321 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS |  |  | 1DTR | #1DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0057 |  |  | 1-07-01 |  |  | #1DTR | 87A | #1DTR 87A |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#1DTR_87A | #1DTR 87RY | MTR | [5 empty] | 322 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS |  |  | 1DTR | #1DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0058 |  |  | 1-07-02 |  |  | #1DTR | 96PA | #1DTR 機械保護動作(96PA) |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | [5 empty] | 323 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS |  |  | 1DTR | #1DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0059 |  |  | 1-07-03 |  |  | #1DTR | 51ZA | #1DTR 51ZA |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | [5 empty] | 324 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1750 | #1DTR(1750) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0060 |  |  | 1-07-04 |  |  | 1750 | PHA | #1DTR 1750 PHA |  |  | B2/D10_A1 | [8 empty] | 北勢DS.#1DTR_51A | #1DTR 51RY | MTR | [5 empty] | 325 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1750 | #1DTR(1750) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0061 |  |  | 1-07-05 |  |  | 1750 | GDA | #1DTR 1750 GDA |  |  | B2/D10_A1 | [8 empty] | 北勢DS.#1DTR_51NA | #1DTR 51N RY | MTR | [5 empty] | 326 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | T/1DTR(A) |  |  | 0062 |  | 0016 | 1-07-06 |  | 1-10 | 310 | ON/OFF | 310 CB |  | aaba | ELEM/D10_A1 | [8 empty] | 北勢DS.310_CB | 310(#1DTR) CB | MTR | [5 empty] | 327 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0064 |  |  | 1-08-00 |  |  | 310 | PHA | 310 PHA |  |  | B3/D10_A1 | [8 empty] | 北勢DS.310_PHA2 | 310開關箱IED RY PHA | OTHER | [5 empty] | 328 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0065 |  |  | 1-08-01 |  |  | 310 | GDA | 310 GDA |  |  | B3/D10_A1 | [8 empty] | 北勢DS.310_GDA | 310開關箱IED RY GDA | OTHER | [5 empty] | 329 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | T/1DTR(B) |  |  | 0066 |  | 0025 | 1-08-02 |  | 1-19 | 320 | ON/OFF | 320 CB |  | abca | ELEM/D10_A1 | [8 empty] | 北勢DS.320_CB | 320(#1DTR) CB | MTR | [5 empty] | 330 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 |  |  | 1-08-04 |  |  | 320 | PHA | 320 PHA |  |  | B3/D10_A1 | [8 empty] | 北勢DS.320_PHA2 | 320開關箱IED RY PHA | OTHER | [5 empty] | 331 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 |  |  | 1-08-05 |  |  | 320 | GDA | 320 GDA |  |  | B3/D10_A1 | [8 empty] | 北勢DS.320_GDA | 320開關箱IED RY GDA | OTHER | [5 empty] | 332 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | S |  | 0070 |  | 0013 | 1-08-06 |  | 1-0D | 1760 | ON/OFF | #2DTR 1760 CB |  | aadb | ELEM/D10_A1 | [16 empty] | 333 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D10 | 北勢DS | 161 | 161kV | 1760 | #2DTR(1760) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-09-02 |  |  | 1760 | PHA | #2DTR 1760 PHA |  |  | B2/D10_A1 | [16 empty] | 334 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D10 | 北勢DS | 161 | 161kV | 1760 | #2DTR(1760) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0075 |  |  | 1-09-03 |  |  | 1760 | GDA | #2DTR 1760 GDA |  |  | B2/D10_A1 | [16 empty] | 335 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D10 | 北勢DS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/3DTR |  | 0084 |  | 0014 | 1-0A-04 |  | 1-0E | 1770 | ON/OFF | #3DTR 1770 CB |  | aagb | ELEM/D10_A1 | [8 empty] | 北勢DS.1770_CB | 1770(#3DTR) CB | MTR | [5 empty] | 336 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS |  |  | 3DTR | #3DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0085 |  |  | 1-0A-05 |  |  | #3DTR | 87A | #3DTR 87A |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#3DTR_87A | #3DTR 87RY | MTR | [5 empty] | 337 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS |  |  | 3DTR | #3DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0086 |  |  | 1-0A-06 |  |  | #3DTR | 96PA | #3DTR 機械保護動作(96PA) |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#3DTR_96PA | #3DTR 機械保護動作 | MTR | [5 empty] | 338 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS |  |  | 3DTR | #3DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0087 |  |  | 1-0A-07 |  |  | #3DTR | 51ZA | #3DTR 51ZA |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#3DTR_51ZA | #3DTR 51Z RY | MTR | [5 empty] | 339 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS |  |  | 3DTR | #3DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0088 |  |  | 1-0B-00 |  |  | 1770 | PHA | #3DTR 1770 PHA |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#3DTR_51A | #3DTR 51RY | MTR | [5 empty] | 340 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS |  |  | 3DTR | #3DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0089 |  |  | 1-0B-01 |  |  | 1770 | GDA | #3DTR 1770 GDA |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#3DTR_51NA | #3DTR 51N RY | MTR | [5 empty] | 341 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | 350 | #3DTR(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3Bus | T/3DTR |  |  | 0090 |  | 0034 | 1-0B-02 |  | 1-22 | 350 | ON/OFF | 350 CB |  | baaa | ELEM/D10_A1 | [8 empty] | 北勢DS.350_CB | 350(#3DTR) CB | MTR | [5 empty] | 342 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | 350 | #3DTR(350) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0092 |  |  | 1-0B-04 |  |  | 350 | PHA | 350 PHA |  |  | B3/D10_A1 | [8 empty] | 北勢DS.350_PHA2 | 350開關箱IED RY PHA | OTHER | [5 empty] | 343 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | 350 | #3DTR(350) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0093 |  |  | 1-0B-05 |  |  | 350 | GDA | 350 GDA |  |  | B3/D10_A1 | [8 empty] | 北勢DS.350_GDA | 350開關箱IED RY GDA | OTHER | [5 empty] | 344 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1780 | #4DTR(1780) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/4DTR |  | 0094 |  | 0015 | 1-0B-06 |  | 1-0F | 1780 | ON/OFF | #4DTR 1780 CB |  | aahb | ELEM/D10_A1 | [8 empty] | 北勢DS.1780_CB | 1780(#4DTR) CB | MTR | [5 empty] | 345 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS |  |  | 4DTR | #4DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0095 |  |  | 1-0B-07 |  |  | #4DTR | 87A | #4DTR 87A |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#4DTR_87A | #4DTR 87RY | MTR | [5 empty] | 346 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS |  |  | 4DTR | #4DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0096 |  |  | 1-0C-00 |  |  | #4DTR | 96PA | #4DTR 機械保護動作(96PA) |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#4DTR_96PA | #4DTR 機械保護動作 | MTR | [5 empty] | 347 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS |  |  | 4DTR | #4DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0097 |  |  | 1-0C-01 |  |  | #4DTR | 51ZA | #4DTR 51ZA |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#4DTR_51ZA | #4DTR 51Z RY | MTR | [5 empty] | 348 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS |  |  | 4DTR | #4DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0098 |  |  | 1-0C-02 |  |  | 1780 | PHA | #4DTR 1780 PHA |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#4DTR_51A | #4DTR 51RY | MTR | [5 empty] | 349 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS |  |  | 4DTR | #4DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0099 |  |  | 1-0C-03 |  |  | 1780 | GDA | #4DTR 1780 GDA |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#4DTR_51NA | #4DTR 51N RY | MTR | [5 empty] | 350 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | 370 | #4DTR(370) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4Bus | T/4DTR |  |  | 0100 |  | 0035 | 1-0C-04 |  | 1-23 | 370 | ON/OFF | 370 CB |  | bbba | ELEM/D10_A1 | [8 empty] | 北勢DS.370_CB | 370(#4DTR) CB | MTR | [5 empty] | 351 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | 370 | #4DTR(370) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0102 |  |  | 1-0C-06 |  |  | 370 | PHA | 370 PHA |  |  | B3/D10_A1 | [8 empty] | 北勢DS.370_PHA2 | 370開關箱IED RY PHA | OTHER | [5 empty] | 352 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | 370 | #4DTR(370) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0103 |  |  | 1-0C-07 |  |  | 370 | GDA | 370 GDA |  |  | B3/D10_A1 | [8 empty] | 北勢DS.370_GDA | 370開關箱IED RY GDA | OTHER | [5 empty] | 353 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | RTU | RTU |  | RTU_MCT |  |  | Status | RTU Master Ry | Open/Close | Y | E | DI-SP | [6 empty] | 0105 |  |  | 1-0D-01 |  |  | 161RTU | MCT_ SOE | RTU MASTER RY SOE |  |  | B3/D10_A1 | [16 empty] | 354 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D10 | 北勢DS |  |  | 1DTR | #1DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0106 |  |  | 1-0D-02 |  |  | #1DTR | 86A | #1DTR_86A |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#1DTR_86A | #1DTR 86(50/50N/51Z/87/96)RY | OTHER | [5 empty] | 355 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS |  |  | 3DTR | #3DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0107 |  |  | 1-0D-03 |  |  | #3DTR | 86A | #3DTR_86A |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#3DTR_86A | #3DTR 86(50/50N/51Z/87/96)RY | OTHER | [5 empty] | 356 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS |  |  | 4DTR | #4DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0108 |  |  | 1-0D-04 |  |  | #4DTR | 86A | #4DTR_86A |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#4DTR_86A | #4DTR 86(50/50N/51Z/87/96)RY | OTHER | [5 empty] | 357 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | 210 | #1SC(210) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | A/LBS210^C/1SC(A) |  |  | 0160 |  | 0017 | 1-14-00 |  | 1-11 | 210 | ON/OFF | #1SC 210 CB |  | aacb | B3/D10_A1 | [8 empty] | 北勢DS.210_CB | 210(11KV #1SC) CB | SC | [5 empty] | 358 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0161 |  |  | 1-14-01 |  |  | 210 | 51A | #1SC 210 SCA |  |  | B3/D10_A1 | [8 empty] | 北勢DS.210_SCA | 11KV #1SC 51,51N RY | SC | [5 empty] | 359 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0162 |  |  | 1-14-02 |  |  | 210 | 51NA | #1SC 210 UVA |  |  | B3/D10_A1 | [8 empty] | 北勢DS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | [5 empty] | 360 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL21 | 北一線(XL21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/XL21/T1 |  |  | 0163 |  | 0018 | 1-14-03 |  | 1-12 | XL21 | ON/OFF | 北一線 XL21 CB |  | aadb | B2/D10_D1 | [8 empty] | 北勢DS.XL21_CB | XL21(11KV北一線) CB | FEEDER | [5 empty] | 361 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | XL21 | 北一線(XL21) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0164 |  |  | 1-14-04 |  |  | XL21 | 51A | 北一線 XL21 PHA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL21_PHA | 11KV北一線(XL21) 相間RY | FEEDER | [5 empty] | 362 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL21 | 北一線(XL21) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0165 |  |  | 1-14-05 |  |  | XL21 | 51NA | 北一線 XL21 GDA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL21_GDA | 11KV北一線(XL21) 接地RY | FEEDER | [5 empty] | 363 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL22 | 北二線(XL22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/XL22/T1 |  |  | 0166 |  | 0019 | 1-14-06 |  | 1-13 | XL22 | ON/OFF | 北二線 XL22 CB |  | aaeb | B2/D10_D1 | [8 empty] | 北勢DS.XL22_CB | XL22(11KV北二線) CB | FEEDER | [5 empty] | 364 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | XL22 | 北二線(XL22) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0167 |  |  | 1-14-07 |  |  | XL22 | 51A | 北二線 XL22 PHA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL22_PHA | 11KV北二線(XL22) 相間RY | FEEDER | [5 empty] | 365 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL22 | 北二線(XL22) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0168 |  |  | 1-15-00 |  |  | XL22 | 51NA | 北二線 XL22 GDA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL22_GDA | 11KV北二線(XL22) 接地RY | FEEDER | [5 empty] | 366 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL23 | 北三線(XL23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/XL23/T1 |  |  | 0169 |  | 0020 | 1-15-01 |  | 1-14 | XL23 | ON/OFF | 北三線 XL23 CB |  | aafb | B2/D10_D1 | [8 empty] | 北勢DS.XL23_CB | XL23(11KV北三線) CB | FEEDER | [5 empty] | 367 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | XL23 | 北三線(XL23) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0170 |  |  | 1-15-02 |  |  | XL23 | 51A | 北三線 XL23 PHA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL23_PHA | 11KV北三線(XL23) 相間RY | FEEDER | [5 empty] | 368 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL23 | 北三線(XL23) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0171 |  |  | 1-15-03 |  |  | XL23 | 51NA | 北三線 XL23 GDA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL23_GDA | 11KV北三線(XL23) 接地RY | FEEDER | [5 empty] | 369 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL24 | 北四線(XL24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/XL24/T1 |  |  | 0172 |  | 0021 | 1-15-04 |  | 1-15 | XL24 | ON/OFF | 北四線 XL24 CB |  | aagb | B2/D10_D1 | [8 empty] | 北勢DS.XL24_CB | XL24(11KV北四線) CB | FEEDER | [5 empty] | 370 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | XL24 | 北四線(XL24) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0173 |  |  | 1-15-05 |  |  | XL24 | 51A | 北四線 XL24 PHA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL24_PHA | 11KV北四線(XL24) 相間RY | FEEDER | [5 empty] | 371 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL24 | 北四線(XL24) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0174 |  |  | 1-15-06 |  |  | XL24 | 51NA | 北四線 XL24 GDA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL24_GDA | 11KV北四線(XL24) 接地RY | FEEDER | [5 empty] | 372 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL25 | 北五線(XL25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/XL25/T1 |  |  | 0175 |  | 0022 | 1-15-07 |  | 1-16 | XL25 | ON/OFF | 北五線 XL25 CB |  | aahb | B2/D10_D1 | [8 empty] | 北勢DS.XL25_CB | XL25(11KV北五線) CB | FEEDER | [5 empty] | 373 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | XL25 | 北五線(XL25) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0176 |  |  | 1-16-00 |  |  | XL25 | 51/51A | 北五線 XL25 PHA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL25_PHA | 11KV北五線(XL25) 相間RY | FEEDER | [5 empty] | 374 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL25 | 北五線(XL25) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0177 |  |  | 1-16-01 |  |  | XL25 | 27/59A | 北五線 XL25 GDA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL25_GDA | 11KV北五線(XL25) 接地RY | FEEDER | [5 empty] | 375 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | 100 | TIE(100) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | L/TIE-1A |  |  | 0178 |  | 0023 | 1-16-02 |  | 1-17 | 100 | ON/OFF | 100 TIE CB |  | aaib | B3/D10_A1 | [8 empty] | 北勢DS.100_CB | 100(TIE) CB | TIE | [5 empty] | 376 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 11 | 11kV | 100 | TIE(100) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0179 |  |  | 1-16-03 |  |  | 100 | PHA | 100 TIE PHA |  |  | B3/D10_A1 | [8 empty] | 北勢DS.100_51A | 11KV TIE(100) 51RY | TIE | [5 empty] | 377 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | 100 | TIE(100) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0180 |  |  | 1-16-04 |  |  | 100 | GDA | 100 TIE GDA |  |  | B3/D10_A1 | [8 empty] | 北勢DS.100_51NA | 11KV TIE(100) 51N RY | TIE | [5 empty] | 378 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | 390 | #1SSTR(390) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | T/1SSTR |  |  | 0181 |  | 0024 | 1-16-05 |  | 1-18 | 390 | ON/OFF | #1SSTR 390 CB |  | abbb | B3/D10_A1 | [8 empty] | 北勢DS.390_CB | 390(#1SSTR) CB | OTHER | [5 empty] | 379 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | 390 | #1SSTR(390) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0182 |  |  | 1-16-06 |  |  | 390 | 51A | #1SSTR 390 PHA |  |  | B3/D10_A1 | [8 empty] | 北勢DS.#1SSTR_51A | #1SSTR 51RY | OTHER | [5 empty] | 380 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | 390 | #1SSTR(390) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0183 |  |  | 1-16-07 |  |  | 390 | 51NA | #1SSTR 390 GDA |  |  | B3/D10_A1 | [8 empty] | 北勢DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | [5 empty] | 381 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | 220 | #2SC(220) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | A/LBS220^C/2SC(A) |  |  | 0184 |  | 0026 | 1-17-00 |  | 1-1A | 220 | ON/OFF | #2SC 220 CB |  | abdb | B3/D10_A1 | [8 empty] | 北勢DS.220_CB | 220(11KV #2SC) CB | SC | [5 empty] | 382 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0185 |  |  | 1-17-01 |  |  | 220 | 51A | #2SC 220 SCA |  |  | B3/D10_A1 | [8 empty] | 北勢DS.220_SCA | 11KV #2SC 51,51N RY | SC | [5 empty] | 383 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0186 |  |  | 1-17-02 |  |  | 220 | 51NA | #2SC 220 UVA |  |  | B3/D10_A1 | [8 empty] | 北勢DS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | [5 empty] | 384 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL26 | 北六線(XL26) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/XL26/T1 |  |  | 0187 |  | 0027 | 1-17-03 |  | 1-1B | XL26 | ON/OFF | 北六線 XL26 CB |  | abeb | B2/D10_D1 | [8 empty] | 北勢DS.XL26_CB | XL26(11KV北六線) CB | FEEDER | [5 empty] | 385 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | XL26 | 北六線(XL26) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0188 |  |  | 1-17-04 |  |  | XL26 | 51A | 北六線 XL26 PHA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL26_PHA | 11KV北六線(XL26) 相間RY | FEEDER | [5 empty] | 386 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL26 | 北六線(XL26) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0189 |  |  | 1-17-05 |  |  | XL26 | 51NA | 北六線 XL26 GDA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL26_GDA | 11KV北六線(XL26) 接地RY | FEEDER | [5 empty] | 387 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL27 | 北七線(XL27) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/XL27/T1 |  |  | 0190 |  | 0028 | 1-17-06 |  | 1-1C | XL27 | ON/OFF | 北七線 XL27 CB |  | abfb | B2/D10_D1 | [8 empty] | 北勢DS.XL27_CB | XL27(11KV北七線) CB | FEEDER | [5 empty] | 388 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | XL27 | 北七線(XL27) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0191 |  |  | 1-17-07 |  |  | XL27 | 51A | 北七線 XL27 PHA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL27_PHA | 11KV北七線(XL27) 相間RY | FEEDER | [5 empty] | 389 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL27 | 北七線(XL27) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0192 |  |  | 1-18-00 |  |  | XL27 | 51NA | 北七線 XL27 GDA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL27_GDA | 11KV北七線(XL27) 接地RY | FEEDER | [5 empty] | 390 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL28 | 北八線(XL28) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/XL28/T1 |  |  | 0193 |  | 0029 | 1-18-01 |  | 1-1D | XL28 | ON/OFF | 北八線 XL28 CB |  | abgb | B2/D10_D1 | [8 empty] | 北勢DS.XL28_CB | XL28(11KV北八線) CB | FEEDER | [5 empty] | 391 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | XL28 | 北八線(XL28) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0194 |  |  | 1-18-02 |  |  | XL28 | 51A | 北八線 XL28 PHA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL28_PHA | 11KV北八線(XL28) 相間RY | FEEDER | [5 empty] | 392 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL28 | 北八線(XL28) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0195 |  |  | 1-18-03 |  |  | XL28 | 51NA | 北八線 XL28 GDA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL28_GDA | 11KV北八線(XL28) 接地RY | FEEDER | [5 empty] | 393 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL29 | 北九線(XL29) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/XL29/T1 |  |  | 0196 |  | 0030 | 1-18-04 |  | 1-1E | XL29 | ON/OFF | 北九線 XL29 CB |  | abhb | B2/D10_D1 | [8 empty] | 北勢DS.XL29_CB | XL29(11KV北九線) CB | FEEDER | [5 empty] | 394 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | XL29 | 北九線(XL29) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0197 |  |  | 1-18-05 |  |  | XL29 | 51/51A | 北九線 XL29 PHA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL29_PHA | 11KV北九線(XL29) 相間RY | FEEDER | [5 empty] | 395 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL29 | 北九線(XL29) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0198 |  |  | 1-18-06 |  |  | XL29 | 27/59A | 北九線 XL29 GDA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL29_GDA | 11KV北九線(XL29) 接地RY | FEEDER | [5 empty] | 396 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL30 | 北十線(XL30) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/XL30/T1 |  |  | 0199 |  | 0031 | 1-18-07 |  | 1-1F | XL30 | ON/OFF | 北十線 XL30 CB |  | abib | B2/D10_D1 | [8 empty] | 北勢DS.XL30_CB | XL30(11KV北十線) CB | FEEDER | [5 empty] | 397 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | XL30 | 北十線(XL30) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0200 |  |  | 1-19-00 |  |  | XL30 | 51/51A | 北十線 XL30 PHA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL30_PHA | 11KV北十線(XL30) 相間RY | FEEDER | [5 empty] | 398 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL30 | 北十線(XL30) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0201 |  |  | 1-19-01 |  |  | XL30 | 27/59 A | 北十線 XL30 GDA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL30_GDA | 11KV北十線(XL30) 接地RY | FEEDER | [5 empty] | 399 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | 250 | #5SC(250) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3Bus | C/5SC |  |  | 0295 |  | 0141 | 2-04-07 |  | 2-0D | 250 | ON/OFF | #5SC 250 CB |  | babb | B3/D10_A1 | [8 empty] | 北勢DS.250_CB | 250(23KV #5SC) CB | SC | [5 empty] | 400 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | 250 | #5SC(250) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0296 |  |  | 2-05-00 |  |  | 250 | 51A | #5SC 250 SCA |  |  | B3/D10_A1 | [8 empty] | 北勢DS.250_SCA | 23KV #5SC 51,51N RY | SC | [5 empty] | 401 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | 250 | #5SC(250) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0297 |  |  | 2-05-01 |  |  | 250 | 51NA | #5SC 250 UVA |  |  | B3/D10_A1 | [8 empty] | 北勢DS.250_UVA | 23KV #5SC 27RY(欠壓) | SC | [5 empty] | 402 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL61 | 北六一線(XL61) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/XL61/T1 |  |  | 0298 |  | 0142 | 2-05-02 |  | 2-0E | XL61 | ON/OFF | 北六一線 XL61 CB |  | bacb | B2/D10_D1 | [8 empty] | 北勢DS.XL61_CB | XL61(23KV北六一線) CB | FEEDER | [5 empty] | 403 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL61 | 北六一線(XL61) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0299 |  |  | 2-05-03 |  |  | XL61 | 51A | 北六一線 XL61 PHA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL61_PHA | 23KV北六一線(XL61) 相間RY | FEEDER | [5 empty] | 404 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL61 | 北六一線(XL61) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0300 |  |  | 2-05-04 |  |  | XL61 | 51NA | 北六一線 XL61 GDA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL61_GDA | 23KV北六一線(XL61) 接地RY | FEEDER | [5 empty] | 405 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL62 | 北六二線(XL62) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/XL62/T1 |  |  | 0301 |  | 0143 | 2-05-05 |  | 2-0F | XL62 | ON/OFF | 北六二線 XL62 CB |  | badb | B2/D10_D1 | [8 empty] | 北勢DS.XL62_CB | XL62(23KV北六二線) CB | FEEDER | [5 empty] | 406 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL62 | 北六二線(XL62) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0302 |  |  | 2-05-06 |  |  | XL62 | 51A | 北六二線 XL62 PHA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL62_PHA | 23KV北六二線(XL62) 相間RY | FEEDER | [5 empty] | 407 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL62 | 北六二線(XL62) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0303 |  |  | 2-05-07 |  |  | XL62 | 51NA | 北六二線 XL62 GDA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL62_GDA | 23KV北六二線(XL62) 接地RY | FEEDER | [5 empty] | 408 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL63 | 北六三線(XL63) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/XL63/T1 |  |  | 0304 |  | 0144 | 2-06-00 |  | 2-10 | XL63 | ON/OFF | 北六三線 XL63 CB |  | baeb | B2/D10_D1 | [8 empty] | 北勢DS.XL63_CB | XL63(23KV北六三線) CB | FEEDER | [5 empty] | 409 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL63 | 北六三線(XL63) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0305 |  |  | 2-06-01 |  |  | XL63 | 51A | 北六三線 XL63 PHA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL63_PHA | 23KV北六三線(XL63) 相間RY | FEEDER | [5 empty] | 410 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL63 | 北六三線(XL63) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0306 |  |  | 2-06-02 |  |  | XL63 | 51NA | 北六三線 XL63 GDA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL63_GDA | 23KV北六三線(XL63) 接地RY | FEEDER | [5 empty] | 411 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL64 | 北六四線(XL64) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/XL64/T1 |  |  | 0307 |  | 0145 | 2-06-03 |  | 2-11 | XL64 | ON/OFF | 北六四線 XL64 CB |  | bagb | B2/D10_D1 | [8 empty] | 北勢DS.XL64_CB | XL64(23KV北六四線) CB | FEEDER | [5 empty] | 412 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL64 | 北六四線(XL64) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0308 |  |  | 2-06-04 |  |  | XL64 | 51A | 北六四線 XL64 PHA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL64_PHA | 23KV北六四線(XL64) 相間RY | FEEDER | [5 empty] | 413 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL64 | 北六四線(XL64) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0309 |  |  | 2-06-05 |  |  | XL64 | 51NA | 北六四線 XL64 GDA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL64_GDA | 23KV北六四線(XL64) 接地RY | FEEDER | [5 empty] | 414 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL65 | 北六五線(XL65) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/XL65/T1 |  |  | 0310 |  | 0146 | 2-06-06 |  | 2-12 | XL65 | ON/OFF | 北六五線 XL65 CB |  | bahb | B2/D10_D1 | [8 empty] | 北勢DS.XL65_CB | XL65(23KV北六五線) CB | FEEDER | [5 empty] | 415 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL65 | 北六五線(XL65) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0311 |  |  | 2-06-07 |  |  | XL65 | 51A | 北六五線 XL65 PHA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL65_PHA | 23KV北六五線(XL65) 相間RY | FEEDER | [5 empty] | 416 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL65 | 北六五線(XL65) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0312 |  |  | 2-07-00 |  |  | XL65 | 51NA | 北六五線 XL65 GDA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL65_GDA | 23KV北六五線(XL65) 接地RY | FEEDER | [5 empty] | 417 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL66 | 北六六線(XL66) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/XL66/T1 |  |  | 0313 |  | 0147 | 2-07-01 |  | 2-13 | XL66 | ON/OFF | 北六六線 XL66 CB |  | baib | B2/D10_D1 | [8 empty] | 北勢DS.XL66_CB | XL66(23KV北六六線) CB | FEEDER | [5 empty] | 418 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL66 | 北六六線(XL66) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0314 |  |  | 2-07-02 |  |  | XL66 | 51A | 北六六線 XL66 PHA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL66_PHA | 23KV北六六線(XL66) 相間RY | FEEDER | [5 empty] | 419 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL66 | 北六六線(XL66) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0315 |  |  | 2-07-03 |  |  | XL66 | 51NA | 北六六線 XL66 GDA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL66_GDA | 23KV北六六線(XL66) 接地RY | FEEDER | [5 empty] | 420 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL67 | 北六七線(XL67) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/XL67/T1 |  |  | 0316 |  | 0148 | 2-07-04 |  | 2-14 | XL67 | ON/OFF | 北六七線 XL67 CB |  | bajb | B2/D10_D1 | [8 empty] | 北勢DS.XL67_CB | XL67(23KV北六七線) CB | FEEDER | [5 empty] | 421 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL67 | 北六七線(XL67) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0317 |  |  | 2-07-05 |  |  | XL67 | 51A | 北六七線 XL67 PHA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL67_PHA | 23KV北六七線(XL67) 相間RY | FEEDER | [5 empty] | 422 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL67 | 北六七線(XL67) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0318 |  |  | 2-07-06 |  |  | XL67 | 51NA | 北六七線 XL67 GDA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL67_GDA | 23KV北六七線(XL67) 接地RY | FEEDER | [5 empty] | 423 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL68 | 北六八線(XL68) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/XL68/T1 |  |  | 0319 |  | 0149 | 2-07-07 |  | 2-15 | XL68 | ON/OFF | 北六八線 XL68 CB |  | bakb | B2/D10_D1 | [8 empty] | 北勢DS.XL68_CB | XL68(23KV北六八線) CB | FEEDER | [5 empty] | 424 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL68 | 北六八線(XL68) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0320 |  |  | 2-08-00 |  |  | XL68 | 51A | 北六八線 XL68 PHA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL68_PHA | 23KV北六八線(XL68) 相間RY | FEEDER | [5 empty] | 425 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL68 | 北六八線(XL68) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0321 |  |  | 2-08-01 |  |  | XL68 | 51NA | 北六八線 XL68 GDA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL68_GDA | 23KV北六八線(XL68) 接地RY | FEEDER | [5 empty] | 426 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | 260 | #6SC(260) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3Bus | C/6SC |  |  | 0322 |  | 0150 | 2-08-02 |  | 2-16 | 260 | ON/OFF | #6SC 260 CB |  | balb | B3/D10_A1 | [8 empty] | 北勢DS.260_CB | 260(23KV #6SC) CB | SC | [5 empty] | 427 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | 260 | #6SC(260) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0323 |  |  | 2-08-03 |  |  | 260 | 51A | #6SC 260 SCA |  |  | B3/D10_A1 | [8 empty] | 北勢DS.260_SCA | 23KV #6SC 51,51N RY | SC | [5 empty] | 428 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | 260 | #6SC(260) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0324 |  |  | 2-08-04 |  |  | 260 | 51NA | #6SC 260 UVA |  |  | B3/D10_A1 | [8 empty] | 北勢DS.260_UVA | 23KV #6SC 27RY(欠壓) | SC | [5 empty] | 429 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | 300 | TIE(300) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/4Bus | B/3Bus |  |  | 0325 |  | 0151 | 2-08-05 |  | 2-17 | 300 | ON/OFF | 300 TIE CB |  | bbab | B3/D10_A1 | [8 empty] | 北勢DS.300_CB | 300(TIE) CB | TIE | [5 empty] | 430 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D10 | 北勢DS | 22 | 22kV | 300 | TIE(300) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0326 |  |  | 2-08-06 |  |  | 300 | 51A | 300 TIE PHA |  |  | B3/D10_A1 | [8 empty] | 北勢DS.300_51A | 23KV TIE(300) 51RY | TIE | [5 empty] | 431 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | 300 | TIE(300) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0327 |  |  | 2-08-07 |  |  | 300 | 51NA | 300 TIE GDA |  |  | B3/D10_A1 | [8 empty] | 北勢DS.300_51NA | 23KV TIE(300) 51N RY | TIE | [5 empty] | 432 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | 270 | #7SC(270) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4Bus | C/7SC |  |  | 0328 |  | 0152 | 2-09-00 |  | 2-18 | 270 | ON/OFF | #7SC 270 CB |  | bbcb | B3/D10_A1 | [8 empty] | 北勢DS.270_CB | 270(23KV #7SC) CB | SC | [5 empty] | 433 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | 270 | #7SC(270) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0329 |  |  | 2-09-01 |  |  | 270 | 51A | #7SC 270 SCA |  |  | B3/D10_A1 | [8 empty] | 北勢DS.270_SCA | 23KV #7SC 51,51N RY | SC | [5 empty] | 434 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | 270 | #7SC(270) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0330 |  |  | 2-09-02 |  |  | 270 | 51NA | #7SC 270 UVA |  |  | B3/D10_A1 | [8 empty] | 北勢DS.270_UVA | 23KV #7SC 27RY(欠壓) | SC | [5 empty] | 435 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL71 | 北七一線(XL71) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4Bus | L/XL71/T1 |  |  | 0331 |  | 0153 | 2-09-03 |  | 2-19 | XL71 | ON/OFF | 北七一線 XL71 CB |  | bbdb | B2/D10_D1 | [8 empty] | 北勢DS.XL71_CB | XL71(23KV北七一線) CB | FEEDER | [5 empty] | 436 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL71 | 北七一線(XL71) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0332 |  |  | 2-09-04 |  |  | XL71 | 51A | 北七一線 XL71 PHA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL71_PHA | 23KV北七一線(XL71) 相間RY | FEEDER | [5 empty] | 437 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL71 | 北七一線(XL71) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0333 |  |  | 2-09-05 |  |  | XL71 | 51NA | 北七一線 XL71 GDA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL71_GDA | 23KV北七一線(XL71) 接地RY | FEEDER | [5 empty] | 438 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL72 | 北七二線(XL72) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4Bus | L/XL72/T1 |  |  | 0334 |  | 0154 | 2-09-06 |  | 2-1A | XL72 | ON/OFF | 北七二線 XL72 CB |  | bbeb | B2/D10_D1 | [8 empty] | 北勢DS.XL72_CB | XL72(23KV北七二線) CB | FEEDER | [5 empty] | 439 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL72 | 北七二線(XL72) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0335 |  |  | 2-09-07 |  |  | XL72 | 51A | 北七二線 XL72 PHA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL72_PHA | 23KV北七二線(XL72) 相間RY | FEEDER | [5 empty] | 440 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL72 | 北七二線(XL72) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0336 |  |  | 2-0A-00 |  |  | XL72 | 51NA | 北七二線 XL72 GDA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL72_GDA | 23KV北七二線(XL72) 接地RY | FEEDER | [5 empty] | 441 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL73 | 北七三線(XL73) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4Bus | L/XL73/T1 |  |  | 0337 |  | 0155 | 2-0A-01 |  | 2-1B | XL73 | ON/OFF | 北七三線 XL73 CB |  | bbfb | B2/D10_D1 | [8 empty] | 北勢DS.XL73_CB | XL73(23KV北七三線) CB | FEEDER | [5 empty] | 442 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL73 | 北七三線(XL73) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0338 |  |  | 2-0A-02 |  |  | XL73 | 51A | 北七三線 XL73 PHA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL73_PHA | 23KV北七三線(XL73) 相間RY | FEEDER | [5 empty] | 443 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL73 | 北七三線(XL73) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0339 |  |  | 2-0A-03 |  |  | XL73 | 51NA | 北七三線 XL73 GDA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL73_GDA | 23KV北七三線(XL73) 接地RY | FEEDER | [5 empty] | 444 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL74 | 北七四線(XL74) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4Bus | L/XL74/T1 |  |  | 0340 |  | 0156 | 2-0A-04 |  | 2-1C | XL74 | ON/OFF | 北七四線 XL74 CB |  | bbhb | B2/D10_D1 | [8 empty] | 北勢DS.XL74_CB | XL74(23KV北七四線) CB | FEEDER | [5 empty] | 445 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL74 | 北七四線(XL74) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0341 |  |  | 2-0A-05 |  |  | XL74 | 51A | 北七四線 XL74 PHA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL74_PHA | 23KV北七四線(XL74) 相間RY | FEEDER | [5 empty] | 446 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL74 | 北七四線(XL74) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0342 |  |  | 2-0A-06 |  |  | XL74 | 51NA | 北七四線 XL74 GDA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL74_GDA | 23KV北七四線(XL74) 接地RY | FEEDER | [5 empty] | 447 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL75 | 北七五線(XL75) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4Bus | L/XL75/T1 |  |  | 0343 |  | 0157 | 2-0A-07 |  | 2-1D | XL75 | ON/OFF | 北七五線 XL75 CB |  | bbib | B2/D10_D1 | [8 empty] | 北勢DS.XL75_CB | XL75(23KV北七五線) CB | FEEDER | [5 empty] | 448 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL75 | 北七五線(XL75) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0344 |  |  | 2-0B-00 |  |  | XL75 | 51A | 北七五線 XL75 PHA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL75_PHA | 23KV北七五線(XL75) 相間RY | FEEDER | [5 empty] | 449 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL75 | 北七五線(XL75) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0345 |  |  | 2-0B-01 |  |  | XL75 | 51NA | 北七五線 XL75 GDA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL75_GDA | 23KV北七五線(XL75) 接地RY | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL76 | 北七六線(XL76) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4Bus | L/XL76/T1 |  |  | 0346 |  | 0158 | 2-0B-02 |  | 2-1E | XL76 | ON/OFF | 北七六線 XL76 CB |  | bbjb | B2/D10_D1 | [8 empty] | 北勢DS.XL76_CB | XL76(23KV北七六線) CB | FEEDER | [5 empty] | 451 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL76 | 北七六線(XL76) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0347 |  |  | 2-0B-03 |  |  | XL76 | 51A | 北七六線 XL76 PHA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL76_PHA | 23KV北七六線(XL76) 相間RY | FEEDER | [5 empty] | 452 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL76 | 北七六線(XL76) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0348 |  |  | 2-0B-04 |  |  | XL76 | 51NA | 北七六線 XL76 GDA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL76_GDA | 23KV北七六線(XL76) 接地RY | FEEDER | [5 empty] | 453 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL77 | 北七七線(XL77) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4Bus | L/XL77/T1 |  |  | 0349 |  | 0159 | 2-0B-05 |  | 2-1F | XL77 | ON/OFF | 北七七線 XL77 CB |  | bbkb | B2/D10_D1 | [8 empty] | 北勢DS.XL77_CB | XL77(23KV北七七線) CB | FEEDER | [5 empty] | 454 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL77 | 北七七線(XL77) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0350 |  |  | 2-0B-06 |  |  | XL77 | 51A | 北七七線 XL77 PHA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL77_PHA | 23KV北七七線(XL77) 相間RY | FEEDER | [5 empty] | 455 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL77 | 北七七線(XL77) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0351 |  |  | 2-0B-07 |  |  | XL77 | 51NA | 北七七線 XL77 GDA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL77_GDA | 23KV北七七線(XL77) 接地RY | FEEDER | [5 empty] | 456 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL78 | 北七八線(XL78) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4Bus | L/XL78/T1 |  |  | 0352 |  | 0160 | 2-0C-00 |  | 2-20 | XL78 | ON/OFF | 北七八線 XL78 CB |  | bblb | B2/D10_D1 | [8 empty] | 北勢DS.XL78_CB | XL78(23KV北七八線) CB | FEEDER | [5 empty] | 457 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL78 | 北七八線(XL78) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0353 |  |  | 2-0C-01 |  |  | XL78 | 51A | 北七八線 XL78 PHA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL78_PHA | 23KV北七八線(XL78) 相間RY | FEEDER | [5 empty] | 458 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL78 | 北七八線(XL78) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0354 |  |  | 2-0C-02 |  |  | XL78 | 51NA | 北七八線 XL78 GDA |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL78_GDA | 23KV北七八線(XL78) 接地RY | FEEDER | [5 empty] | 459 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | 280 | #8SC(280) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4Bus | C/8SC |  |  | 0355 |  | 0161 | 2-0C-03 |  | 2-21 | 280 | ON/OFF | #8SC 280 CB |  | bbmb | B3/D10_A1 | [8 empty] | 北勢DS.280_CB | 280(23KV #8SC) CB | SC | [5 empty] | 460 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | 280 | #8SC(280) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0356 |  |  | 2-0C-04 |  |  | 280 | 51A | #8SC 280 SCA |  |  | B3/D10_A1 | [8 empty] | 北勢DS.280_SCA | 23KV #8SC 51,51N RY | SC | [5 empty] | 461 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | 280 | #8SC(280) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0357 |  |  | 2-0C-05 |  |  | 280 | 51NA | #8SC 280 UVA |  |  | B3/D10_A1 | [8 empty] | 北勢DS.280_UVA | 23KV #8SC 27RY(欠壓) | SC | [5 empty] | 462 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | 490 | #2SSTR(490) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4Bus | T/2SSTR |  |  | 0358 |  | 0162 | 2-0C-06 |  | 2-22 | 490 | ON/OFF | #2SSTR 490 CB |  | bbnb | B3/D10_A1 | [8 empty] | 北勢DS.490_CB | 490(#2SSTR) CB | OTHER | [5 empty] | 463 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | 490 | #2SSTR(490) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0359 |  |  | 2-0C-07 |  |  | 490 | 51A | #2SSTR 490 PHA |  |  | B3/D10_A1 | [8 empty] | 北勢DS.#2SSTR_51A | #2SSTR 51RY | OTHER | [5 empty] | 464 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | 490 | #2SSTR(490) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0360 |  |  | 2-0D-00 |  |  | 490 | 51NA | #2SSTR 490 GDA |  |  | B3/D10_A1 | [8 empty] | 北勢DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | [5 empty] | 465 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL25 | 北五線(XL25) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0361 |  |  | 2-0D-01 |  |  | XL25 | 81A | 北五線 XL25 低頻電驛動作 |  |  | B2/D10_D1 | [8 empty] | 北勢DS.81RY_A/S(1) | XL25低頻電驛動作/復歸 | OTHER | [5 empty] | 466 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
D10 | 北勢DS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0768 |  | 0000 | 1-30-00 |  | 1-00 | TEST CB | ON/OFF | TEST CB |  |  | ELEM/ALL | [8 empty] | 北勢DS.TEST_CB | TEST CB | OTHER | [5 empty] | 467 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | RTU | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0769 |  |  | 1-30-01 |  |  | RTU | L/R | L/R STATUS |  |  | ELEM/D10_A1 | [8 empty] | 北勢DS.RTU_S/L | RTU SUPY/LOCAL | OTHER | [5 empty] | 468 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
D10 | 北勢DS | 161 | 161kV | 1510 | 雲林～北勢線(1510) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0770 |  | 0036 | 1-30-02 |  | 1-24 | 1510 | USE/LOCK | 雲林北勢線 1510 87RY U/L |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1510_87UL | 雲林北勢線(1510) 87RY U/L | LINE161 | [5 empty] | 469 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 161 | 161kV | 1510 | 雲林～北勢線(1510) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0771 |  | 0037 | 1-30-03 |  | 1-25 | 1510 | USE/LOCK | 雲林北勢線 1510 79RY U/L |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1510_79UL | 雲林北勢線(1510) 79RY U/L | LINE161 | [5 empty] | 470 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 161 | 161kV | 1520 | 斗南～北勢線(1520) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0772 |  | 0038 | 1-30-04 |  | 1-26 | 1520 | USE/LOCK | 斗南北勢線 1520 187RY U/L |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1520_87UL1 | 斗南北勢線(1520)#1 87RY U/L | OTHER | [5 empty] | 471 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 161 | 161kV | 1520 | 斗南～北勢線(1520) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0773 |  | 0039 | 1-30-05 |  | 1-27 | 1520 | USE/LOCK | 斗南北勢線 1520 79RY U/L |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1520_79UL | 斗南北勢線(1520) 79RY U/L | LINE161 | [5 empty] | 472 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 161 | 161kV | 1530 | 北勢～旭硝子、旭硝二紅線(1530) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0774 |  | 0040 | 1-30-06 |  | 1-28 | 1530 | USE/LOCK | 北勢旭硝子旭硝二紅線 1530 187RY U/L |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1530_87UL1 | 旭硝子旭硝二紅(1530) 87RY1 U/L | OTHER | [5 empty] | 473 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 161 | 161kV | 1530 | 北勢～旭硝子、旭硝二紅線(1530) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0775 |  | 0041 | 1-30-07 |  | 1-29 | 1530 | USE/LOCK | 北勢旭硝子旭硝二紅線 1530 79RY U/L |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1530_79UL | 旭硝子旭硝二紅(1530) 79RY U/L | LINE161 | [5 empty] | 474 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 161 | 161kV | 1540 | 北勢～旭硝子、旭硝二白線(1540) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0776 |  | 0042 | 1-30-08 |  | 1-2A | 1540 | USE/LOCK | 北勢旭硝子旭硝二白線 1540 187RY U/L |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1540_87UL1 | 旭硝子旭硝二白(1540)#187RY U/L | LINE161 | [5 empty] | 475 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 161 | 161kV | 1540 | 北勢～旭硝子、旭硝二白線(1540) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0777 |  | 0043 | 1-30-09 |  | 1-2B | 1540 | USE/LOCK | 北勢旭硝子旭硝二白線 1540 79RY U/L |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1540_79UL | 旭硝子旭硝二白(1540) 79RY U/L | LINE161 | [5 empty] | 476 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 161 | 161kV | 1520 | 斗南～北勢線(1520) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0778 |  | 0044 | 1-30-10 |  | 1-2C | 1520 | USE/LOCK | 斗南北勢線 1520 287RY U/L |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1520_87UL2 | 斗南北勢線(1520)#2 87RY U/L | OTHER | [5 empty] | 477 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 161 | 161kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0790 |  | 0126 | 1-31-06 |  | 1-7E | #1 BUS | ON/OFF | 161KV #1 BUS╴87UL |  |  | B2/D10_A1 | [8 empty] | 北勢DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | [5 empty] | 478 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 161 | 161kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0791 |  | 0127 | 1-31-07 |  | 1-7F | #2 BUS | ON/OFF | 161KV #2 BUS╴87UL |  |  | B2/D10_A1 | [8 empty] | 北勢DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | [5 empty] | 479 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS |  |  | 1DTR(A) | #1DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0793 |  |  | 1-31-09 |  |  | #1ATR | 遙控/現場 | #1ATR OLTC R/L |  | c | B1/D10_A1 | [8 empty] | 北勢DS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | [5 empty] | 480 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D10 | 北勢DS |  |  | 1DTR(A) | #1DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0794 |  | 0056 | 1-31-10 |  | 1-38 | #1ATR | OLTC A/M | #1ATR OLTC A/M |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | [5 empty] | 481 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D10 | 北勢DS |  |  | 1DTR(A) | #1DTR(A) |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0795 |  |  | 1-31-11 |  |  | #1DTR | ON/OFF | #1DTR 重故障 |  | a | B1/D10_A1 | [8 empty] | 北勢DS.#1DTR_TRA | #1DTR 重故障 | MTR | [5 empty] | 482 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS |  |  | 1DTR(A) | #1DTR(A) |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0796 |  |  | 1-31-12 |  |  | #1DTR | ON/OFF | #1DTR 輕故障 |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#1DTR_TRF | #1DTR 輕故障 | MTR | [5 empty] | 483 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS |  |  | 1DTR(B) | #1DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0797 |  |  | 1-31-13 |  |  | #1BTR | 遙控/現場 | #1BTR OLTC R/L |  | b | B1/D10_A1 | [8 empty] | 北勢DS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | [5 empty] | 484 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D10 | 北勢DS |  |  | 1DTR(B) | #1DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0798 |  | 0058 | 1-31-14 |  | 1-3A | #1BTR | OLTC A/M | #1BTR OLTC A/M |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | [5 empty] | 485 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D10 | 北勢DS |  |  | 3DTR | #3DTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0807 |  |  | 1-32-07 |  |  | #3DTR | 遙控/現場 | #3DTR OLTC R/L |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#3DTR_S/L | #3DTR OLTC S/L | MTR | [5 empty] | 486 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D10 | 北勢DS |  |  | 3DTR | #3DTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0808 |  | 0064 | 1-32-08 |  | 1-40 | #3DTR | OLTC A/M | #3DTR OLTC A/M |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#3DTR_A/M | #3DTR OLTC A/M | MTR | [5 empty] | 487 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D10 | 北勢DS |  |  | 3DTR | #3DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR |  |  |  |  | 0809 |  |  | 1-32-09 |  |  | #3DTR | ON/OFF | #3DTR 重故障 |  | a | B1/D10_A1 | [8 empty] | 北勢DS.#3DTR_TRA | #3DTR 重故障 | MTR | [5 empty] | 488 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS |  |  | 3DTR | #3DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0810 |  |  | 1-32-10 |  |  | #3DTR | ON/OFF | #3DTR 輕故障 |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#3DTR_TRF | #3DTR 輕故障 | MTR | [5 empty] | 489 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS |  |  | 4DTR | #4DTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0812 |  |  | 1-32-12 |  |  | #4DTR | 遙控/現場 | #4DTR OLTC R/L |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#4DTR_S/L | #4DTR OLTC S/L | MTR | [5 empty] | 490 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D10 | 北勢DS |  |  | 4DTR | #4DTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0813 |  | 0066 | 1-32-13 |  | 1-42 | #4DTR | OLTC A/M | #4DTR OLTC A/M |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#4DTR_A/M | #4DTR OLTC A/M | MTR | [5 empty] | 491 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D10 | 北勢DS |  |  | 4DTR | #4DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR |  |  |  |  | 0814 |  |  | 1-32-14 |  |  | #4DTR | ON/OFF | #4DTR 重故障 |  | a | B1/D10_A1 | [8 empty] | 北勢DS.#4DTR_TRA | #4DTR 重故障 | MTR | [5 empty] | 492 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS |  |  | 4DTR | #4DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0815 |  |  | 1-32-15 |  |  | #4DTR | ON/OFF | #4DTR 輕故障 |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#4DTR_TRF | #4DTR 輕故障 | MTR | [5 empty] | 493 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1510 | 雲林～北勢線(1510) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0816 |  |  | 1-33-00 |  |  | 1510 | RYFA | 雲林北勢線 1510 數位電驛故障 |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1510_RYFA | 雲林北勢線(1510) 數位電驛故障 | OTHER | [5 empty] | 494 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1510 | 雲林～北勢線(1510) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0817 |  |  | 1-33-01 |  |  | 1510 | 87CFA | 雲林北勢線 1510 87RY通訊故障 |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1510_87CFA | 雲林北勢線(1510) 87RY通訊故障 | OTHER | [5 empty] | 495 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1520 | 斗南～北勢線(1520) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0818 |  |  | 1-33-02 |  |  | 1520 | RYFA | 斗南北勢線 1520 數位電驛故障 |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1520_RYFA | 斗南北勢線(1520)數位電驛故障 | OTHER | [5 empty] | 496 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1520 | 斗南～北勢線(1520) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0819 |  |  | 1-33-03 |  |  | 1520 | 87CFA | 斗南北勢線 1520 87RY通訊故障 |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1520_87CFA | 斗南北勢線(1520))87RY通訊故障 | OTHER | [5 empty] | 497 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1530 | 北勢～旭硝子、旭硝二紅線(1530) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0820 |  |  | 1-33-04 |  |  | 1530 | RYFA | 北勢旭硝子旭硝二紅線1530 數位電驛故障 |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1530_RYFA | 旭硝子旭硝二紅(1530)數位RY故障 | OTHER | [5 empty] | 498 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1530 | 北勢～旭硝子、旭硝二紅線(1530) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0821 |  |  | 1-33-05 |  |  | 1530 | 87CFA | 北勢旭硝子旭硝二紅線1530 87RY通訊故障 |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1530_87CFA | 旭硝子旭硝二紅(1530)87通訊故障 | OTHER | [5 empty] | 499 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1540 | 北勢～旭硝子、旭硝二白線(1540) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0822 |  |  | 1-33-06 |  |  | 1540 | RYFA | 北勢旭硝子旭硝二白線 1540 數位電驛故障 |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1540_RYFA | 旭硝子旭硝二白(1540)數位RY故障 | OTHER | [5 empty] | 500 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1540 | 北勢～旭硝子、旭硝二白線(1540) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0823 |  |  | 1-33-07 |  |  | 1540 | 87CFA | 北勢旭硝子旭硝二白線 1540 87RY通訊故障 |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1540_87CFA | 旭硝子旭硝二白(1540)87通訊故障 | OTHER | [5 empty] | 501 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | StaDev | 所內設施 |  | Fire1 |  |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0836 |  |  | 1-34-04 |  |  | 火災警報(1) | ON/OFF | 火災警報(1)受信總機 |  |  | B3/D10_A1 | [8 empty] | 北勢DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | [5 empty] | 502 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | StaDev | 所內設施 |  | Fire2 |  |  | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0837 |  |  | 1-34-05 |  |  | 火災警報(2) | ON/OFF | 火災警報(2) |  |  | B3/D10_A1 | [8 empty] | 北勢DS.火災警報(2) | 火災警報(2) | OTHER | [5 empty] | 503 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | ComPoint |  |  | BUS_RYFA |  |  | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0838 |  |  | 1-34-06 |  |  | BUS | A/N | 161KV BUS數位電驛故障 |  |  | B3/D10_A1 | [8 empty] | 北勢DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | [5 empty] | 504 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | ComPoint |  |  | 12B_CTFA |  | Element | Status | #1#2 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0839 |  |  | 1-34-07 |  |  | BUS | A/N | 161KV BUS 87RY CT 迴路故障 |  |  | B3/D10_A1 | [8 empty] | 北勢DS.161KV_BUS_CTFA | 161KV BUS 87RY CT回路故障 | OTHER | [5 empty] | 505 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | StaDev | 所內設施 |  | Fire3 |  |  | Status | 火災警報3 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0840 |  |  | 1-34-08 |  |  | 火災警報(5) | ON/OFF | 火災警報(5) |  |  | B3/D10_A1 | [8 empty] | 北勢DS.火災警報(5) | 火災警報(5) | OTHER | [5 empty] | 506 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | StaDev | 所內設施 |  | Door1 | 建物大門 |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0841 |  |  | 1-34-09 |  |  | Locate Empty | ON/OFF | 建物大門 無人化門禁(1) |  |  | B3/D10_A1 | [8 empty] | 北勢DS.無人化門禁(1) | 無人化門禁(1)建築物大門 | OTHER | [5 empty] | 507 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | StaDev | 所內設施 |  | Door2 | 控制室 |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0842 |  |  | 1-34-10 |  |  | Locate Empty | ON/OFF | 控制室 無人化門禁(2) |  |  | B3/D10_A1 | [8 empty] | 北勢DS.無人化門禁(2) | 無人化門禁(2)控制室大門 | OTHER | [5 empty] | 508 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | StaDev | 所內設施 |  | Door3 |  |  | Status | 無人化門禁3 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0843 |  |  | 1-34-11 |  |  | Locate Empty | ON/OFF | 無人化門禁(3) |  |  | B3/D10_A1 | [8 empty] | 北勢DS.無人化門禁(3) | 無人化門禁(3) | OTHER | [5 empty] | 509 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | StaDev | 所內設施 |  | Burglar1 | 保全系統 |  | Status | 無人化防盜1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0844 |  |  | 1-34-12 |  |  | Locate Empty | ON/OFF | 保全系統 無人化防盜(1) |  |  | B3/D10_A1 | [8 empty] | 北勢DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | [5 empty] | 510 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | StaDev | 所內設施 |  | Burglar2 |  |  | Status | 無人化防盜2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0845 |  |  | 1-34-13 |  |  | Locate Empty | ON/OFF | 無人化防盜(2) |  |  | B3/D10_A1 | [8 empty] | 北勢DS.無人化防盜(2) | 無人化防盜(2) | OTHER | [5 empty] | 511 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | StaDev | 所內設施 |  | Lights1 | 開關場1 |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0846 |  | 0122 | 1-34-14 |  | 1-7A | Locate Empty | ON/OFF | 開關場照明(A) |  |  | B3/D10_A1 | [8 empty] | 北勢DS.開關場照明(A) | 開關場照明(A) | OTHER | [5 empty] | 512 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
D10 | 北勢DS | 0 |  | StaDev | 所內設施 |  | Lights2 | 開關場 |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0847 |  | 0123 | 1-34-15 |  | 1-7B | Locate Empty | ON/OFF | 開關場照明(B) |  |  | B3/D10_A1 | [8 empty] | 北勢DS.開關場照明(B) | 開關場照明(B) | OTHER | [5 empty] | 513 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
D10 | 北勢DS | 0 |  | StaDev | 所內設施 |  | AIRCON |  |  | Status | 冷氣跳脫 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0848 |  |  | 1-35-00 |  |  | Locate Empty | ON/OFF | 空調機警報 |  |  | B3/D10_A1 | [8 empty] | 北勢DS.空調機故障 | 空調機故障或電源跳脫 | OTHER | [5 empty] | 514 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | NORMAL/FAULT | NORMAL
D10 | 北勢DS | 0 |  | ComPoint |  |  | OPA |  |  | Status | 充油電纜低壓警報 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0850 |  |  | 1-35-02 |  |  | OPA | ON/OFF | OPA 充油電纜警報 |  |  | B3/D10_A1 | [8 empty] | 北勢DS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | [5 empty] | 515 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0851 |  |  | 1-35-03 |  |  | ACB1 | ON/OFF | 所內電源 ACB1 |  |  | B3/D10_A1 | [8 empty] | 北勢DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | [5 empty] | 516 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D10 | 北勢DS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0852 |  |  | 1-35-04 |  |  | ACB2 | ON/OFF | 所內電源 ACB2 |  |  | B3/D10_A1 | [8 empty] | 北勢DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | [5 empty] | 517 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D10 | 北勢DS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0853 |  |  | 1-35-05 |  |  | Locate Empty | ON/OFF | STUV 所內欠壓 |  |  | ELEM/D10_A1 | [8 empty] | 北勢DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | [5 empty] | 518 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0854 |  |  | 1-35-06 |  |  | CBA | ON/OFF | 161KV CB 重故障 |  |  | B3/D10_A1 | [8 empty] | 北勢DS.161KV_CBA | 161KV斷路器重故障 | OTHER | [5 empty] | 519 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0855 |  |  | 1-35-07 |  |  | CBF | ON/OFF | 161KV CB 輕故障 |  |  | B3/D10_A1 | [8 empty] | 北勢DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | [5 empty] | 520 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0856 |  |  | 1-35-08 |  |  | DCA | ON/OFF | DCA DC 警報 |  |  | ELEM/D10_A1 | [8 empty] | 北勢DS.直流電源DCA | 直流電源故障警報 | OTHER | [5 empty] | 521 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0857 |  |  | 1-35-09 |  |  | ACBA | ON/OFF | ACBA ACB 警報 |  |  | B3/D10_A1 | [8 empty] | 北勢DS.所內電源ACBA | 所內電源故障警報 | OTHER | [5 empty] | 522 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0858 |  |  | 1-35-10 |  |  | Locate Empty | ON/OFF | VUA1 |  |  | B2/D10_A1 | [8 empty] | 北勢DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | [5 empty] | 523 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0859 |  |  | 1-35-11 |  |  | Locate Empty | ON/OFF | VUA2 |  |  | B2/D10_A1 | [8 empty] | 北勢DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | [5 empty] | 524 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0860 |  |  | 1-35-12 |  |  | CHG1 | ON/OFF | CHG1 直流電源故障 |  |  | B3/D10_A1 | [8 empty] | 北勢DS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | [5 empty] | 525 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0861 |  |  | 1-35-13 |  |  | DCE | ON/OFF | DCE DC 接地 |  |  | ELEM/D10_A1 | [8 empty] | 北勢DS.直流電源DCE | 直流電源接地故障警報 | OTHER | [5 empty] | 526 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | ComPoint |  |  | COMT |  |  | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0862 |  |  | 1-35-14 |  |  | COMT | ON/OFF | COMT 空壓機超時 |  |  | B3/D10_A1 | [8 empty] | 北勢DS.161空壓機COMT | 161KV空壓機運轉超時警報 | OTHER | [5 empty] | 527 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | ComPoint |  |  | FDR_60A |  |  | Status | 11/22kV電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0863 |  |  | 1-35-15 |  |  | 60A | ON/OFF | 60A |  |  | B3/D10_A1 | [8 empty] | 北勢DS.23KV_SC_60A | 23/11KV SC 60A | OTHER | [5 empty] | 528 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | StaDev | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0864 |  |  | 1-36-00 |  |  | PSF | ON/OFF | PSF 其他輕故障 |  |  | B3/D10_A1 | [8 empty] | 北勢DS.其他輕故障 | 變電所內其他輕故障 | OTHER | [5 empty] | 529 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | StaDev | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0865 |  |  | 1-36-01 |  |  | PSA | ON/OFF | PSA 其他重故障 |  |  | B3/D10_A1 | [8 empty] | 北勢DS.其他重故障 | 變電所內其他重故障 | OTHER | [5 empty] | 530 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | ComPoint |  |  | FDR_CBA |  |  | Status | 11/22kV斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0866 |  |  | 1-36-02 |  |  | CBA | ON/OFF | 22KV/11KV CB 重故障 |  |  | ELEM/D10_D1 | [8 empty] | 北勢DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | [5 empty] | 531 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | ComPoint |  |  | FDR_CBF |  |  | Status | 11/22kV斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0867 |  |  | 1-36-03 |  |  | CBF | ON/OFF | 22KV/11KV CB 輕故障 |  |  | ELEM/D10_D1 | [8 empty] | 北勢DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | [5 empty] | 532 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | ComPoint |  |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0868 |  |  | 1-36-04 |  |  | LOA | ON/OFF | 22KV/11KV LOA 復閉失敗 |  |  | B3/D10_A1 | [8 empty] | 北勢DS.FEEDER_RCA | 饋線復閉電驛動作 | FEEDER | [5 empty] | 533 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | StaDev | 所內設施 |  | OilLeak1 |  |  | Status | 洩油池水位警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0869 |  |  | 1-36-05 |  |  | OW1 | ON/OFF | OW1 水位警報 |  |  | B3/D10_A1 | [8 empty] | 北勢DS.洩油池水位警報 | 洩油池水位警報 | OTHER | [5 empty] | 534 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | StaDev | 所內設施 |  | OilLeak2 |  |  | Status | 洩油池水位警報2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0870 |  |  | 1-36-06 |  |  | OW2 | ON/OFF | OW2 水位警報 |  |  | B3/D10_A1 | [8 empty] | 北勢DS.洩油池警報(2) | 洩油池水位警報(2) | OTHER | [5 empty] | 535 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0871 |  |  | 1-36-07 |  |  | CHG2 | ON/OFF | 通訊充電機故障 |  |  | B3/D10_A1 | [8 empty] | 北勢DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | [5 empty] | 536 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0872 |  |  | 1-36-08 |  |  | Locate Empty | ON/OFF | 通訊設備 AC故障 |  |  | B3/D10_A1 | [8 empty] | 北勢DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | [5 empty] | 537 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | StaDev | 所內設施 |  | R_Temp | 通信室 |  | Status | 溫度警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0875 |  |  | 1-36-11 |  |  | Locate Empty | ON/OFF | 通信室溫控警報 |  |  | B3/D10_A1 | [8 empty] | 北勢DS.通信機房溫度 | 通信機房溫度警報 | OTHER | [5 empty] | 538 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS |  |  | 1DTR | #1DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0876 |  |  | 1-36-12 |  |  | #1DTR | ON/OFF | #1DTR 96D |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#1DTR_96D | #1DTR 96D RY | MTR | [5 empty] | 539 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS |  |  | 1DTR | #1DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0877 |  |  | 1-36-13 |  |  | #1DTR | ON/OFF | #1DTR 96P |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#1DTR_96P | #1DTR 96P RY | MTR | [5 empty] | 540 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS |  |  | 1DTR | #1DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0878 |  |  | 1-36-14 |  |  | #1DTR | ON/OFF | #1DTR 63Q |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#1DTR_63Q | #1DTR 63Q RY | MTR | [5 empty] | 541 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS |  |  | 1DTR | #1DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0879 |  |  | 1-36-15 |  |  | #1DTR | ON/OFF | #1DTR 96B1 |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | [5 empty] | 542 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS |  |  | 1DTR | #1DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0880 |  |  | 1-37-00 |  |  | #1DTR | ON/OFF | #1DTR 96B2 |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | [5 empty] | 543 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS |  |  | 3DTR | #3DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0886 |  |  | 1-37-06 |  |  | #3DTR | ON/OFF | #3DTR 96D |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#3DTR_96D | #3DTR 96D RY | MTR | [5 empty] | 544 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS |  |  | 3DTR | #3DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0887 |  |  | 1-37-07 |  |  | #3DTR | ON/OFF | #3DTR 96P |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#3DTR_96P | #3DTR 96P RY | MTR | [5 empty] | 545 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS |  |  | 3DTR | #3DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0888 |  |  | 1-37-08 |  |  | #3DTR | ON/OFF | #3DTR 63Q |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#3DTR_63Q | #3DTR 63Q RY | MTR | [5 empty] | 546 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS |  |  | 3DTR | #3DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0889 |  |  | 1-37-09 |  |  | #3DTR | ON/OFF | #3DTR 96B1 |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#3DTR_96B1 | #3DTR 96B1 RY | MTR | [5 empty] | 547 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS |  |  | 3DTR | #3DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0890 |  |  | 1-37-10 |  |  | #3DTR | ON/OFF | #3DTR 96B2 |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#3DTR_96B2 | #3DTR 96B2 RY | MTR | [5 empty] | 548 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS |  |  | 4DTR | #4DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0891 |  |  | 1-37-11 |  |  | #4DTR | ON/OFF | #4DTR 96D |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#4DTR_96D | #4DTR 96D RY | MTR | [5 empty] | 549 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS |  |  | 4DTR | #4DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0892 |  |  | 1-37-12 |  |  | #4DTR | ON/OFF | #4DTR 96P |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#4DTR_96P | #4DTR 96P RY | MTR | [5 empty] | 550 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS |  |  | 4DTR | #4DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0893 |  |  | 1-37-13 |  |  | #4DTR | ON/OFF | #4DTR 63Q |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#4DTR_63Q | #4DTR 63Q RY | MTR | [5 empty] | 551 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS |  |  | 4DTR | #4DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0894 |  |  | 1-37-14 |  |  | #4DTR | ON/OFF | #4DTR 96B1 |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#4DTR_96B1 | #4DTR 96B1 RY | MTR | [5 empty] | 552 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS |  |  | 4DTR | #4DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0895 |  |  | 1-37-15 |  |  | #4DTR | ON/OFF | #4DTR 96B2 |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#4DTR_96B2 | #4DTR 96B2 RY | MTR | [5 empty] | 553 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 1024 |  | 0163 | 2-30-00 |  | 2-23 | 210 | A/M | #1SC 210 Q-CTL A/M |  |  | B3/D10_A1 | [8 empty] | 北勢DS.210_A/M | 11KV #1SC 乏控器 A/M | SC | [5 empty] | 554 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D10 | 北勢DS | 11 | 11kV | 210 | #1SC(210) |  | 1A5A_M | SC_A_M #2 | Element | Status | A_M動作1 | Auto/Man | Y | 5 | DI-SP | [6 empty] | 1025 |  | 0164 | 2-30-01 |  | 2-24 | 210 | AM-1 | #1SC 210 Q-CTL A/M-1 |  |  | B3/D10_A1 | [8 empty] | 北勢DS.210_LBS_A/M | 11KV #1SC LBS 乏控器 A/M | SC | [5 empty] | 555 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D10 | 北勢DS | 11 | 11kV | XL21 | 北一線(XL21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1026 |  | 0165 | 2-30-02 |  | 2-25 | XL21 | USE/LOCK | 北一線 XL21 79RY U/L |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL21_79UL | 11KV北一線(XL21) 79RY U/L | FEEDER | [5 empty] | 556 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 11 | 11kV | XL21 | 北一線(XL21) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1027 |  | 0166 | 2-30-03 |  | 2-26 | XL21 | USE/LOCK | 北一線 XL21 LCO 分流器 |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL21_LCO_TAP | 11KV北一線(XL21) LCO TAP | FEEDER | [5 empty] | 557 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D10 | 北勢DS | 11 | 11kV | XL22 | 北二線(XL22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1028 |  | 0167 | 2-30-04 |  | 2-27 | XL22 | USE/LOCK | 北二線 XL22 79RY U/L |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL22_79UL | 11KV北二線(XL22) 79RY U/L | FEEDER | [5 empty] | 558 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 11 | 11kV | XL22 | 北二線(XL22) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1029 |  | 0168 | 2-30-05 |  | 2-28 | XL22 | USE/LOCK | 北二線 XL22 LCO 分流器 |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL22_LCO_TAP | 11KV北二線(XL22) LCO TAP | FEEDER | [5 empty] | 559 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D10 | 北勢DS | 11 | 11kV | XL23 | 北三線(XL23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1030 |  | 0169 | 2-30-06 |  | 2-29 | XL23 | USE/LOCK | 北三線 XL23 79RY U/L |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL23_79UL | 11KV北三線(XL23) 79RY U/L | FEEDER | [5 empty] | 560 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 11 | 11kV | XL23 | 北三線(XL23) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1031 |  | 0170 | 2-30-07 |  | 2-2A | XL23 | USE/LOCK | 北三線 XL23 LCO 分流器 |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL23_LCO_TAP | 11KV北三線(XL23) LCO TAP | FEEDER | [5 empty] | 561 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D10 | 北勢DS | 11 | 11kV | XL24 | 北四線(XL24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1032 |  | 0171 | 2-30-08 |  | 2-2B | XL24 | USE/LOCK | 北四線 XL24 79RY U/L |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL24_79UL | 11KV北四線(XL24) 79RY U/L | FEEDER | [5 empty] | 562 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 11 | 11kV | XL24 | 北四線(XL24) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1033 |  | 0172 | 2-30-09 |  | 2-2C | XL24 | USE/LOCK | 北四線 XL24 LCO 分流器 |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL24_LCO_TAP | 11KV北四線(XL24) LCO TAP | FEEDER | [5 empty] | 563 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D10 | 北勢DS | 11 | 11kV | XL25 | 北五線(XL25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1034 |  | 0173 | 2-30-10 |  | 2-2D | XL25 | USE/LOCK | 北五線 XL25 79RY U/L |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL25_79UL | 11KV北五線(XL25) 79RY U/L | FEEDER | [5 empty] | 564 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 11 | 11kV | XL25 | 北五線(XL25) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1035 |  | 0174 | 2-30-11 |  | 2-2E | XL25 | USE/LOCK | 北五線 XL25 LCO 分流器 |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL25_LCO_TAP | 11KV北五線(XL25) LCO TAP | FEEDER | [5 empty] | 565 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D10 | 北勢DS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 1036 |  | 0175 | 2-30-12 |  | 2-2F | 220 | A/M | #2SC 220 Q-CTL A/M |  |  | B3/D10_A1 | [8 empty] | 北勢DS.220_A/M | 11KV #2SC 乏控器 A/M | SC | [5 empty] | 566 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D10 | 北勢DS | 11 | 11kV | 220 | #2SC(220) |  | 1A5A_M | SC_A_M #2 | Element | Status | A_M動作1 | Auto/Man | Y | 5 | DI-SP | [6 empty] | 1037 |  | 0176 | 2-30-13 |  | 2-30 | 220 | AM-1 | #2SC 220 Q-CTL A/M-1 |  |  | B3/D10_A1 | [8 empty] | 北勢DS.220_LBS_A/M | 11KV #2SC LBS 乏控器 A/M | SC | [5 empty] | 567 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D10 | 北勢DS | 11 | 11kV | XL26 | 北六線(XL26) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1038 |  | 0177 | 2-30-14 |  | 2-31 | XL26 | USE/LOCK | 北六線 XL26 79RY U/L |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL26_79UL | 11KV北六線(XL26) 79RY U/L | FEEDER | [5 empty] | 568 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 11 | 11kV | XL26 | 北六線(XL26) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1039 |  | 0178 | 2-30-15 |  | 2-32 | XL26 | USE/LOCK | 北六線 XL26 LCO 分流器 |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL26_LCO_TAP | 11KV北六線(XL26) LCO TAP | FEEDER | [5 empty] | 569 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D10 | 北勢DS | 11 | 11kV | XL27 | 北七線(XL27) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1040 |  | 0179 | 2-31-00 |  | 2-33 | XL27 | USE/LOCK | 北七線 XL27 79RY U/L |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL27_79UL | 11KV北七線(XL27) 79RY U/L | FEEDER | [5 empty] | 570 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 11 | 11kV | XL27 | 北七線(XL27) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1041 |  | 0180 | 2-31-01 |  | 2-34 | XL27 | USE/LOCK | 北七線 XL27 LCO 分流器 |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL27_LCO_TAP | 11KV北七線(XL27) LCO TAP | FEEDER | [5 empty] | 571 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D10 | 北勢DS | 11 | 11kV | XL28 | 北八線(XL28) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1042 |  | 0181 | 2-31-02 |  | 2-35 | XL28 | USE/LOCK | 北八線 XL28 79RY U/L |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL28_79UL | 11KV北八線(XL28) 79RY U/L | FEEDER | [5 empty] | 572 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 11 | 11kV | XL28 | 北八線(XL28) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1043 |  | 0182 | 2-31-03 |  | 2-36 | XL28 | USE/LOCK | 北八線 XL28 LCO 分流器 |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL28_LCO_TAP | 11KV北八線(XL28) LCO TAP | FEEDER | [5 empty] | 573 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D10 | 北勢DS | 11 | 11kV | XL29 | 北九線(XL29) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1044 |  | 0183 | 2-31-04 |  | 2-37 | XL29 | USE/LOCK | 北九線 XL29 79RY U/L |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL29_79UL | 11KV北九線(XL29) 79RY U/L | FEEDER | [5 empty] | 574 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 11 | 11kV | XL29 | 北九線(XL29) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1045 |  | 0184 | 2-31-05 |  | 2-38 | XL29 | USE/LOCK | 北九線 XL29 LCO 分流器 |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL29_LCO_TAP | 11KV北九線(XL29) LCO TAP | FEEDER | [5 empty] | 575 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D10 | 北勢DS | 11 | 11kV | XL30 | 北十線(XL30) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1046 |  | 0185 | 2-31-06 |  | 2-39 | XL30 | USE/LOCK | 北十線 XL30 79RY U/L |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL30_79UL | 11KV北十線(XL30) 79RY U/L | FEEDER | [5 empty] | 576 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 11 | 11kV | XL30 | 北十線(XL30) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1047 |  | 0186 | 2-31-07 |  | 2-3A | XL30 | USE/LOCK | 北十線 XL30 LCO 分流器 |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL30_LCO_TAP | 11KV北十線(XL30) LCO TAP | FEEDER | [5 empty] | 577 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D10 | 北勢DS | 22 | 22kV | 250 | #5SC(250) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 1072 |  | 0211 | 2-33-00 |  | 2-53 | 250 | A/M | #5SC 250 Q-CTL A/M |  |  | B3/D10_A1 | [8 empty] | 北勢DS.250_A/M | 23KV #5SC 乏控器 A/M | SC | [5 empty] | 578 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D10 | 北勢DS | 22 | 22kV | XL61 | 北六一線(XL61) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1073 |  | 0212 | 2-33-01 |  | 2-54 | XL61 | USE/LOCK | 北六一線 XL61 79RY U/L |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL61_79UL | 23KV北六一線(XL61) 79RY U/L | FEEDER | [5 empty] | 579 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 22 | 22kV | XL61 | 北六一線(XL61) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1074 |  | 0213 | 2-33-02 |  | 2-55 | XL61 | USE/LOCK | 北六一線 XL61 LCO 分流器 |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL61_LCO_TAP | 23KV北六一線(XL61) LCO TAP | FEEDER | [5 empty] | 580 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D10 | 北勢DS | 22 | 22kV | XL62 | 北六二線(XL62) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1075 |  | 0214 | 2-33-03 |  | 2-56 | XL62 | USE/LOCK | 北六二線 XL62 79RY U/L |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL62_79UL | 23KV北六二線(XL62) 79RY U/L | FEEDER | [5 empty] | 581 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 22 | 22kV | XL62 | 北六二線(XL62) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1076 |  | 0215 | 2-33-04 |  | 2-57 | XL62 | USE/LOCK | 北六二線 XL62 LCO 分流器 |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL62_LCO_TAP | 23KV北六二線(XL62) LCO TAP | FEEDER | [5 empty] | 582 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D10 | 北勢DS | 22 | 22kV | XL63 | 北六三線(XL63) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1077 |  | 0216 | 2-33-05 |  | 2-58 | XL63 | USE/LOCK | 北六三線 XL63 79RY U/L |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL63_79UL | 23KV北六三線(XL63) 79RY U/L | FEEDER | [5 empty] | 583 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 22 | 22kV | XL63 | 北六三線(XL63) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1078 |  | 0217 | 2-33-06 |  | 2-59 | XL63 | USE/LOCK | 北六三線 XL63 LCO 分流器 |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL63_LCO_TAP | 23KV北六三線(XL63) LCO TAP | FEEDER | [5 empty] | 584 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D10 | 北勢DS | 22 | 22kV | XL64 | 北六四線(XL64) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1079 |  | 0218 | 2-33-07 |  | 2-5A | XL64 | USE/LOCK | 北六四線 XL64 79RY U/L |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL64_79UL | 23KV北六四線(XL64) 79RY U/L | FEEDER | [5 empty] | 585 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 22 | 22kV | XL64 | 北六四線(XL64) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1080 |  | 0219 | 2-33-08 |  | 2-5B | XL64 | USE/LOCK | 北六四線 XL64 LCO 分流器 |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL64_LCO_TAP | 23KV北六四線(XL64) LCO TAP | FEEDER | [5 empty] | 586 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D10 | 北勢DS | 22 | 22kV | XL65 | 北六五線(XL65) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1081 |  | 0220 | 2-33-09 |  | 2-5C | XL65 | USE/LOCK | 北六五線 XL65 79RY U/L |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL65_79UL | 23KV北六五線(XL65) 79RY U/L | FEEDER | [5 empty] | 587 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 22 | 22kV | XL65 | 北六五線(XL65) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1082 |  | 0221 | 2-33-10 |  | 2-5D | XL65 | USE/LOCK | 北六五線 XL65 LCO 分流器 |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL65_LCO_TAP | 23KV北六五線(XL65) LCO TAP | FEEDER | [5 empty] | 588 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D10 | 北勢DS | 22 | 22kV | XL66 | 北六六線(XL66) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1083 |  | 0222 | 2-33-11 |  | 2-5E | XL66 | USE/LOCK | 北六六線 XL66 79RY U/L |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL66_79UL | 23KV北六六線(XL66) 79RY U/L | FEEDER | [5 empty] | 589 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 22 | 22kV | XL66 | 北六六線(XL66) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1084 |  | 0223 | 2-33-12 |  | 2-5F | XL66 | USE/LOCK | 北六六線 XL66 LCO 分流器 |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL66_LCO_TAP | 23KV北六六線(XL66) LCO TAP | FEEDER | [5 empty] | 590 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D10 | 北勢DS | 22 | 22kV | XL67 | 北六七線(XL67) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1085 |  | 0224 | 2-33-13 |  | 2-60 | XL67 | USE/LOCK | 北六七線 XL67 79RY U/L |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL67_79UL | 23KV北六七線(XL67) 79RY U/L | FEEDER | [5 empty] | 591 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 22 | 22kV | XL67 | 北六七線(XL67) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1086 |  | 0225 | 2-33-14 |  | 2-61 | XL67 | USE/LOCK | 北六七線 XL67 LCO 分流器 |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL67_LCO_TAP | 23KV北六七線(XL67) LCO TAP | FEEDER | [5 empty] | 592 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D10 | 北勢DS | 22 | 22kV | XL68 | 北六八線(XL68) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1087 |  | 0226 | 2-33-15 |  | 2-62 | XL68 | USE/LOCK | 北六八線 XL68 79RY U/L |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL68_79UL | 23KV北六八線(XL68) 79RY U/L | FEEDER | [5 empty] | 593 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 22 | 22kV | XL68 | 北六八線(XL68) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1088 |  | 0227 | 2-34-00 |  | 2-63 | XL68 | USE/LOCK | 北六八線 XL68 LCO 分流器 |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL68_LCO_TAP | 23KV北六八線(XL68) LCO TAP | FEEDER | [5 empty] | 594 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D10 | 北勢DS | 22 | 22kV | 260 | #6SC(260) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 1089 |  | 0228 | 2-34-01 |  | 2-64 | 260 | A/M | #6SC 260 Q-CTL A/M |  |  | B3/D10_A1 | [8 empty] | 北勢DS.260_A/M | 23KV #6SC 乏控器 A/M | SC | [5 empty] | 595 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D10 | 北勢DS | 22 | 22kV | 270 | #7SC(270) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 1090 |  | 0229 | 2-34-02 |  | 2-65 | 270 | A/M | #7SC 270 Q-CTL A/M |  |  | B3/D10_A1 | [8 empty] | 北勢DS.270_A/M | 23KV #7SC 乏控器 A/M | SC | [5 empty] | 596 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D10 | 北勢DS | 22 | 22kV | XL71 | 北七一線(XL71) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1091 |  | 0230 | 2-34-03 |  | 2-66 | XL71 | USE/LOCK | 北七一線 XL71 79RY U/L |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL71_79UL | 23KV北七一線(XL71) 79RY U/L | FEEDER | [5 empty] | 597 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 22 | 22kV | XL71 | 北七一線(XL71) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1092 |  | 0231 | 2-34-04 |  | 2-67 | XL71 | USE/LOCK | 北七一線 XL71 LCO 分流器 |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL71_LCO_TAP | 23KV北七一線(XL71) LCO TAP | FEEDER | [5 empty] | 598 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D10 | 北勢DS | 22 | 22kV | XL72 | 北七二線(XL72) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1093 |  | 0232 | 2-34-05 |  | 2-68 | XL72 | USE/LOCK | 北七二線 XL72 79RY U/L |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL72_79UL | 23KV北七二線(XL72) 79RY U/L | FEEDER | [5 empty] | 599 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 22 | 22kV | XL72 | 北七二線(XL72) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1094 |  | 0233 | 2-34-06 |  | 2-69 | XL72 | USE/LOCK | 北七二線 XL72 LCO 分流器 |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL72_LCO_TAP | 23KV北七二線(XL72) LCO TAP | FEEDER | [5 empty] | 600 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D10 | 北勢DS | 22 | 22kV | XL73 | 北七三線(XL73) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1095 |  | 0234 | 2-34-07 |  | 2-6A | XL73 | USE/LOCK | 北七三線 XL73 79RY U/L |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL73_79UL | 23KV北七三線(XL73) 79RY U/L | FEEDER | [5 empty] | 601 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 22 | 22kV | XL73 | 北七三線(XL73) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1096 |  | 0235 | 2-34-08 |  | 2-6B | XL73 | USE/LOCK | 北七三線 XL73 LCO 分流器 |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL73_LCO_TAP | 23KV北七三線(XL73) LCO TAP | FEEDER | [5 empty] | 602 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D10 | 北勢DS | 22 | 22kV | XL74 | 北七四線(XL74) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1097 |  | 0236 | 2-34-09 |  | 2-6C | XL74 | USE/LOCK | 北七四線 XL74 79RY U/L |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL74_79UL | 23KV北七四線(XL74) 79RY U/L | FEEDER | [5 empty] | 603 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 22 | 22kV | XL74 | 北七四線(XL74) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1098 |  | 0237 | 2-34-10 |  | 2-6D | XL74 | USE/LOCK | 北七四線 XL74 LCO 分流器 |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL74_LCO_TAP | 23KV北七四線(XL74) LCO TAP | FEEDER | [5 empty] | 604 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D10 | 北勢DS | 22 | 22kV | XL75 | 北七五線(XL75) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1099 |  | 0238 | 2-34-11 |  | 2-6E | XL76 | USE/LOCK | 北七五線 XL75 79RY U/L |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL75_79UL | 23KV北七五線(XL75) 79RY U/L | FEEDER | [5 empty] | 605 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 22 | 22kV | XL75 | 北七五線(XL75) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1100 |  | 0239 | 2-34-12 |  | 2-6F | XL75 | USE/LOCK | 北七五線 XL75 LCO 分流器 |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL75_LCO_TAP | 23KV北七五線(XL75) LCO TAP | FEEDER | [5 empty] | 606 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D10 | 北勢DS | 22 | 22kV | XL76 | 北七六線(XL76) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1101 |  | 0240 | 2-34-13 |  | 2-70 | XL76 | USE/LOCK | 北七六線 XL76 79RY U/L |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL76_79UL | 23KV北七六線(XL76) 79RY U/L | FEEDER | [5 empty] | 607 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 22 | 22kV | XL76 | 北七六線(XL76) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1102 |  | 0241 | 2-34-14 |  | 2-71 | XL76 | USE/LOCK | 北七六線 XL76 LCO 分流器 |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL76_LCO_TAP | 23KV北七六線(XL76) LCO TAP | FEEDER | [5 empty] | 608 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D10 | 北勢DS | 22 | 22kV | XL77 | 北七七線(XL77) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1103 |  | 0242 | 2-34-15 |  | 2-72 | XL77 | USE/LOCK | 北七七線 XL77 79RY U/L |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL77_79UL | 23KV北七七線(XL77) 79RY U/L | FEEDER | [5 empty] | 609 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 22 | 22kV | XL77 | 北七七線(XL77) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1104 |  | 0243 | 2-35-00 |  | 2-73 | XL77 | USE/LOCK | 北七七線 XL77 LCO 分流器 |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL77_LCO_TAP | 23KV北七七線(XL77) LCO TAP | FEEDER | [5 empty] | 610 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D10 | 北勢DS | 22 | 22kV | XL78 | 北七八線(XL78) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1105 |  | 0244 | 2-35-01 |  | 2-74 | XL78 | USE/LOCK | 北七八線 XL78 79RY U/L |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL78_79UL | 23KV北七八線(XL78) 79RY U/L | FEEDER | [5 empty] | 611 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 22 | 22kV | XL78 | 北七八線(XL78) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1106 |  | 0245 | 2-35-02 |  | 2-75 | XL78 | USE/LOCK | 北七八線 XL78 LCO 分流器 |  |  | B2/D10_D1 | [8 empty] | 北勢DS.XL78_LCO_TAP | 23KV北七八線(XL78) LCO TAP | FEEDER | [5 empty] | 612 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D10 | 北勢DS | 22 | 22kV | 280 | #8SC(280) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 1107 |  | 0246 | 2-35-03 |  | 2-76 | 280 | A/M | #8SC 280 Q-CTL A/M |  |  | B3/D10_A1 | [8 empty] | 北勢DS.280_A/M | 23KV #8SC 乏控器 A/M | SC | [5 empty] | 613 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D10 | 北勢DS | 0 |  | StaDev | 所內設施 |  | Water1 | 0.5M |  | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1108 |  |  | 2-35-04 |  |  | 地下室 | A/N | 地下室 0.5M 水位警報 |  |  | B3/D10_A1 | [8 empty] | 北勢DS.水位警報(1) | 地下室水位警報(1) | OTHER | [5 empty] | 614 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | StaDev | 所內設施 |  | Water2 | 1M |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1109 |  |  | 2-35-05 |  |  | 地下室 | A/N | 地下室 1M 水位警報 |  |  | B3/D10_A1 | [8 empty] | 北勢DS.水位警報(2) | 地下室水位警報(2) | OTHER | [5 empty] | 615 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 1110 |  |  | 2-35-06 |  |  | 161KV TIE | 測試/正常 | 161KV TIE (1500)50RY 測試/正常 |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | [5 empty] | 616 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Test | Test | 1 |  |  | TEST/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1111 |  |  | 2-35-07 |  |  | OSCF | A/N | 161KV示波器缺紙或故障警報OSCF |  |  | B3/D10_A1 | [8 empty] | 北勢DS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | [5 empty] | 617 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | StaDev | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1112 |  |  | 2-35-08 |  |  | Power Meter | A/N | Power Meter 故障警報 PMA |  |  | ELEM/D10_A1 | [8 empty] | 北勢DS.PMA | 電力量測表計故障 | OTHER | [5 empty] | 618 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL25 | 北五線 |  | RYFA | 低頻電驛 |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1113 |  |  | 2-35-09 |  |  | XL25 | 81RF | 北五線 XL25 低頻電驛故障 |  |  | B2/D10_D1 | [8 empty] | 北勢DS.81RF(1) | XL25低頻電驛故障 | OTHER | [5 empty] | 619 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | ComPoint |  |  | GRZ100 |  |  | Status | 電驛GRZ100閉鎖 | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1114 |  |  | 2-35-10 |  |  | BVS盤 | LOCK/USE | 本所各GRZ100 Ry U/L |  |  | B3/D10_A1 | [8 empty] | 北勢DS.BVS_RY | BVS GRZ100 RY U/L | OTHER | [5 empty] | 620 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | LOCK/USE | USE
D10 | 北勢DS | 161 | 161kV | 1530 | 北勢～旭硝子、旭硝二紅線(1530) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1115 |  | 0124 | 2-35-11 |  | 1-7C | 1530 | USE/LOCK | 北勢旭硝子旭硝二紅線 1530 287RY U/L |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1530_87UL2 | 旭硝子旭硝二紅(1530) 87RY2 U/L | OTHER | [5 empty] | 621 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 161 | 161kV | 1540 | 北勢～旭硝子、旭硝二白線(1540) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1116 |  | 0125 | 2-35-12 |  | 1-7D | 1540 | USE/LOCK | 北勢旭硝子旭硝二白線 1540 287RY U/L |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1540_87UL2 | 旭硝子旭硝二白(1540)#287RY U/L | LINE161 | [5 empty] | 622 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS | 0 |  | StaDev | 所內設施 |  | GEN | 緊急發電機運轉 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1117 |  |  | 2-35-13 |  |  | Locate Empty | ON/OFF | 緊急發電機運轉 |  |  | B3/D10_A1 | [8 empty] | 北勢DS.GEN | 緊急發電機運轉 | OTHER | [5 empty] | 623 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ON/OFF | OFF
D10 | 北勢DS |  |  | 1DTR | #1DTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1118 |  | 0248 | 2-35-14 |  | 2-7A | #1DTR | USE/LOCK | 1DTR #1 87RY U/L |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#1DTR_87UL1 | #1DTR #1 87RY U/L | OTHER |  | CDC_Mon1_DPC,DNP_DI_Mon1_DPC |  |  |  | 624 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS |  |  | 1DTR | #1DTR |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1119 |  | 0249 | 2-35-15 |  | 2-79 | #1DTR | USE/LOCK | 1DTR #2 87RY U/L |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#1DTR_87UL2 | #1DTR #2 87RY U/L | OTHER | [5 empty] | 625 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS |  |  | 1DTR | #1DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1120 |  | 0250 | 2-35-14 |  | 2-7A | #1DTR | USE/LOCK | 1DTR #1 87RY U/L |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#1DTR_87UL1 | #1DTR #1 87RY U/L | OTHER |  | CDC_Mon1_DPC,DNP_DI_Mon1_DPC |  |  |  | 626 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS |  |  | 1DTR | #1DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1121 |  |  | 2-36-01 |  |  | #1DTR | RYFA | 1DTR 數位電驛故障 |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#1DTR_RYFA | #1DTR數位電驛故障 | OTHER | [5 empty] | 627 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS |  |  | 3DTR | #3DTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1122 |  | 0251 | 2-36-02 |  | 2-7B | #3DTR | USE/LOCK | 3DTR #1 87RY U/L |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#3DTR_87UL1 | #3DTR #1 87RY U/L | OTHER | [5 empty] | 628 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS |  |  | 3DTR | #3DTR |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1123 |  | 0252 | 2-36-03 |  | 2-7C | #3DTR | USE/LOCK | 3DTR #2 87RY U/L |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#3DTR_87UL2 | #3DTR #2 87RY U/L | OTHER | [5 empty] | 629 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS |  |  | 3DTR | #3DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1124 |  | 0253 | 2-36-04 |  | 2-7D | #3DTR | USE/LOCK | 3DTR 51Z RY U/L |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#3DTR_51ZUL | #3DTR 51ZRY U/L | OTHER | [5 empty] | 630 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS |  |  | 3DTR | #3DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1125 |  |  | 2-36-05 |  |  | #3DTR | RYFA | 3DTR 數位電驛故障 |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#3DTR_RYFA | #3DTR數位電驛故障 | OTHER | [5 empty] | 631 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS |  |  | 4DTR | #4DTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1126 |  | 0256 | 2-36-06 |  | 3-00 | #4DTR | USE/LOCK | 4DTR #1 87RY U/L |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#4DTR_87UL1 | #4DTR #1 87RY U/L | OTHER | [5 empty] | 632 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS |  |  | 4DTR | #4DTR |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1127 |  | 0257 | 2-36-07 |  | 3-01 | #4DTR | USE/LOCK | 4DTR #2 87RY U/L |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#4DTR_87UL2 | #4DTR #2 87RY U/L | OTHER | [5 empty] | 633 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS |  |  | 4DTR | #4DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1128 |  | 0258 | 2-36-08 |  | 3-02 | #4DTR | USE/LOCK | 4DTR 51Z RY U/L |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#4DTR_51ZUL | #4DTR 51ZRY U/L | OTHER | [5 empty] | 634 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D10 | 北勢DS |  |  | 4DTR | #4DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1129 |  |  | 2-36-09 |  |  | #4DTR | RYFA | 4DTR 數位電驛故障 |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#4DTR_RYFA | #4DTR數位電驛故障 | OTHER | [5 empty] | 635 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | ComPoint |  |  | OLTC_A |  |  | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1130 |  |  | 2-36-10 |  |  | OLTC | OLTCA | OLTC 15分鐘內連動3次警報 |  |  | B3/D10_A1 | [8 empty] | 北勢DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | [5 empty] | 636 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1510 | 雲林～北勢線(1510) |  | DS1 | 1511 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0896 | 897 | 0068 | 1-38-00 | 1-38-01 | 1-44 | 1511 | ON | 雲林北勢線 1511 ABS |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1511_DS | 1511(雲林北勢線) DS | LINE161 | [5 empty] | 637 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D10 | 北勢DS | 161 | 161kV | 1510 | 雲林～北勢線(1510) |  | DS2 | 1512 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0898 | 899 | 0069 | 1-38-02 | 1-38-03 | 1-45 | 1512 | ON | 雲林北勢線 1512 ABS |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1512_DS | 1512(雲林北勢線) DS | LINE161 | [5 empty] | 638 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D10 | 北勢DS | 161 | 161kV | 1510 | 雲林～北勢線(1510) |  | DS3 | 1513 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0900 | 901 | 0070 | 1-38-04 | 1-38-05 | 1-46 | 1513 | ON | 雲林北勢線 1513 ABS |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1513_DS | 1513(雲林北勢線) DS | LINE161 | [5 empty] | 639 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D10 | 北勢DS | 161 | 161kV | 1510 | 雲林～北勢線(1510) |  | ES3 | 1513E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0902 | 903 | 0071 | 1-38-06 | 1-38-07 | 1-47 | 1513E | ON | 雲林北勢線 1513E ABS |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1513E_ES | 1513E(雲林北勢線) ES | LINE161 | [5 empty] | 640 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D10 | 北勢DS | 161 | 161kV | 1520 | 斗南～北勢線(1520) |  | DS1 | 1521 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0904 | 905 | 0072 | 1-38-08 | 1-38-09 | 1-48 | 1521 | ON | 斗南北勢線 1521 ABS |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1521_DS | 1521(斗南北勢線) DS | LINE161 | [5 empty] | 641 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D10 | 北勢DS | 161 | 161kV | 1520 | 斗南～北勢線(1520) |  | DS2 | 1522 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0906 | 907 | 0073 | 1-38-10 | 1-38-11 | 1-49 | 1522 | ON | 斗南北勢線 1522 ABS |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1522_DS | 1522(斗南北勢線) DS | LINE161 | [5 empty] | 642 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D10 | 北勢DS | 161 | 161kV | 1520 | 斗南～北勢線(1520) |  | DS3 | 1523 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0908 | 909 | 0074 | 1-38-12 | 1-38-13 | 1-4A | 1523 | ON | 斗南北勢線 1523 ABS |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1523_DS | 1523(斗南北勢線) DS | LINE161 | [5 empty] | 643 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D10 | 北勢DS | 161 | 161kV | 1520 | 斗南～北勢線(1520) |  | ES3 | 1523E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0910 | 911 | 0075 | 1-38-14 | 1-38-15 | 1-4B | 1523E | ON | 斗南北勢線 1523E ABS |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1523E_ES | 1523E(斗南北勢線) ES | LINE161 | [5 empty] | 644 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D10 | 北勢DS | 161 | 161kV | 1530 | 北勢～旭硝子、旭硝二紅線(1530) |  | DS1 | 1531 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0912 | 913 | 0076 | 1-39-00 | 1-39-01 | 1-4C | 1531 | ON | 北勢旭硝子旭硝二紅線 1531 DS |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1531_DS | 1531(旭硝子旭硝二紅) DS | LINE161 | [5 empty] | 645 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D10 | 北勢DS | 161 | 161kV | 1530 | 北勢～旭硝子、旭硝二紅線(1530) |  | DS2 | 1532 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0914 | 915 | 0077 | 1-39-02 | 1-39-03 | 1-4D | 1532 | ON | 北勢旭硝子旭硝二紅線 1532 DS |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1532_DS | 1532(旭硝子旭硝二紅) DS | LINE161 | [5 empty] | 646 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D10 | 北勢DS | 161 | 161kV | 1530 | 北勢～旭硝子、旭硝二紅線(1530) |  | DS3 | 1533 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0916 | 917 | 0078 | 1-39-04 | 1-39-05 | 1-4E | 1533 | ON | 北勢旭硝子旭硝二紅線 1533 DS |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1533_DS | 1533(旭硝子旭硝二紅) DS | LINE161 | [5 empty] | 647 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D10 | 北勢DS | 161 | 161kV | 1530 | 北勢～旭硝子、旭硝二紅線(1530) |  | ES3 | 1533E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0918 | 919 | 0079 | 1-39-06 | 1-39-07 | 1-4F | 1533E | ON | 北勢旭硝子旭硝二紅線 1533E DS |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1533E_ES | 1533E(旭硝子旭硝二紅) ES | LINE161 | [5 empty] | 648 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D10 | 北勢DS | 161 | 161kV | 1540 | 北勢～旭硝子、旭硝二白線(1540) |  | DS1 | 1541 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0920 | 921 | 0080 | 1-39-08 | 1-39-09 | 1-50 | 1541 | ON | 北勢旭硝子旭硝二白線 1541 DS |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1541_DS | 1541(旭硝子旭硝二白) DS | LINE161 | [5 empty] | 649 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D10 | 北勢DS | 161 | 161kV | 1540 | 北勢～旭硝子、旭硝二白線(1540) |  | DS2 | 1542 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0922 | 923 | 0081 | 1-39-10 | 1-39-11 | 1-51 | 1542 | ON | 北勢旭硝子旭硝二白線 1542 DS |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1542_DS | 1542(旭硝子旭硝二白) DS | LINE161 | [5 empty] | 650 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D10 | 北勢DS | 161 | 161kV | 1540 | 北勢～旭硝子、旭硝二白線(1540) |  | DS3 | 1543 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0924 | 925 | 0082 | 1-39-12 | 1-39-13 | 1-52 | 1543 | ON | 北勢旭硝子旭硝二白線 1543 DS |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1543_DS | 1543(旭硝子旭硝二白) DS | LINE161 | [5 empty] | 651 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D10 | 北勢DS | 161 | 161kV | 1540 | 北勢～旭硝子、旭硝二白線(1540) |  | ES3 | 1543E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0926 | 927 | 0083 | 1-39-14 | 1-39-15 | 1-53 | 1543E | ON | 北勢旭硝子旭硝二白線 1543E DS |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1543E_ES | 1543E(旭硝子旭硝二白) ES | LINE161 | [5 empty] | 652 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D10 | 北勢DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0976 | 977 | 0108 | 1-3D-00 | 1-3D-01 | 1-6C | 1501 | ON | 161KV TIE 1501 ABS |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1501_DS | 1501(TIE) DS | TIE | [5 empty] | 653 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D10 | 北勢DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0978 | 979 | 0109 | 1-3D-02 | 1-3D-03 | 1-6D | 1502 | ON | 161KV TIE 1502 ABS |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1502_DS | 1502(TIE) DS | TIE | [5 empty] | 654 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D10 | 北勢DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0980 | 981 | 0110 | 1-3D-04 | 1-3D-05 | 1-6E | 1751 | ON | #1DTR 1751 ABS |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1751_DS | 1751(#1DTR) DS | MTR | [5 empty] | 655 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D10 | 北勢DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0982 | 983 | 0111 | 1-3D-06 | 1-3D-07 | 1-6F | 1752 | ON | #1DTR 1752 ABS |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1752_DS | 1752(#1DTR) DS | MTR | [5 empty] | 656 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D10 | 北勢DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0984 | 985 | 0112 | 1-3D-08 | 1-3D-09 | 1-70 | 1761 | ON | #2DTR 1761 ABS |  |  | B2/D10_A1 | [16 empty] | 657 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D10 | 北勢DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0986 | 987 | 0113 | 1-3D-10 | 1-3D-11 | 1-71 | 1762 | ON | #2DTR 1762 ABS |  |  | B2/D10_A1 | [16 empty] | 658 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D10 | 北勢DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0988 | 989 | 0114 | 1-3D-12 | 1-3D-13 | 1-72 | 1771 | ON | #3DTR 1771 ABS |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1771_DS | 1771(#3DTR) DS | MTR | [5 empty] | 659 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D10 | 北勢DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0990 | 991 | 0115 | 1-3D-14 | 1-3D-15 | 1-73 | 1772 | ON | #3DTR 1772 ABS |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1772_DS | 1772(#3DTR) DS | MTR | [5 empty] | 660 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D10 | 北勢DS | 161 | 161kV | 1780 | #4DTR(1780) |  | DS1 | 1781 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0992 | 993 | 0116 | 1-3E-00 | 1-3E-01 | 1-74 | 1781 | ON | #4DTR 1781 ABS |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1781_DS | 1781(#4DTR) DS | MTR | [5 empty] | 661 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D10 | 北勢DS | 161 | 161kV | 1780 | #4DTR(1780) |  | DS2 | 1782 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0994 | 995 | 0117 | 1-3E-02 | 1-3E-03 | 1-75 | 1782 | ON | #4DTR 1782 ABS |  |  | B2/D10_A1 | [8 empty] | 北勢DS.1782_DS | 1782(#4DTR) DS | MTR | [5 empty] | 662 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D10 | 北勢DS | 11 | 11kV | LBS210 | #1SC(210) |  | LBS |  | Element | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/210 | C/1SC(B) |  |  | 0996 | 997 | 0118 | 1-3E-04 | 1-3E-05 | 1-76 | 210 | ON | #1SC 210 LBS |  |  | B3/D10_A1 | [8 empty] | 北勢DS.210_LBS | 210(11KV #1SC) LBS | SC | [5 empty] | 663 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D10 | 北勢DS | 11 | 11kV | LBS220 | #2SC(220) |  | LBS |  | Element | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/220 | C/2SC(B) |  |  | 0998 | 999 | 0119 | 1-3E-06 | 1-3E-07 | 1-77 | 210 | ON | #2SC 220 LBS |  |  | B3/D10_A1 | [8 empty] | 北勢DS.220_LBS | 220(11KV #2SC) LBS | SC | [5 empty] | 664 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D10 | 北勢DS |  |  | 3DTR | #3DTR |  | OLTC_A | TAP連動 | INSERT | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0207 |  |  | 1-19-07 |  |  | #3 DTR | ON/OFF | #3 DTR OLTC TAP連動 |  |  | B1/D10_A1 | [8 empty] | 北勢DS.#3OLTC_TAP連動 | #3DTR OLTC TAP連動,請確認處理 | OTHER | [5 empty] | 665 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
D10 | 北勢DS | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/D10_A1 | [12 empty] | 北勢DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: D10/161/1BUS/V; OPRD2: D10/161/2BUS/V
D10 | 北勢DS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/D10_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: D10/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
D10 | 北勢DS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/D10_A1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_4 | OPRD1: D10/161/1510/MW; OPRD2: D10/161/1520/MW; OPRD3: D10/161/1530/MW; OPRD4: D10/161/1540/MW
D10 | 北勢DS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/D10_A1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: D10/0/CalcPoint/OPRN2_MW
D10 | 北勢DS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/D10_A1 | [17 empty] | none
D10 | 北勢DS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/D10_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: D10/0/CalcPoint/OPRN1; OPRD2: D10/0/CalcPoint/OPRN2; OPRD3: D10/0/CalcPoint/PRFL_UL
D10 | 北勢DS |  |  | 1DTR | 1DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D10_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D10/11/310/I_R; OPRD2: D10/11/320/I_R
D10 | 北勢DS |  |  | 1DTR | 1DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D10_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D10/11/310/I_S; OPRD2: D10/11/320/I_S
D10 | 北勢DS |  |  | 1DTR | 1DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D10_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D10/11/310/I_T; OPRD2: D10/11/320/I_T
D10 | 北勢DS | 161 | 161kV | 1510 | 雲林～北勢線(1510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D10_A1 | [12 empty] | 北勢DS.1510_AMP | 雲林北勢線 AMP | LINE161 | AMP_CAL | C20R2000 | amp_cal | OPRD1: D10/161/1510/MW; OPRD2: D10/161/1510/MVAR; OPRD3: D10/0/CalcPoint/Vbs4
D10 | 北勢DS | 161 | 161kV | 1520 | 斗南～北勢線(1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D10_A1 | [12 empty] | 北勢DS.1520_AMP | 斗南北勢線 AMP | LINE161 | AMP_CAL | C20R2000 | amp_cal | OPRD1: D10/161/1520/MW; OPRD2: D10/161/1520/MVAR; OPRD3: D10/0/CalcPoint/Vbs4
D10 | 北勢DS | 161 | 161kV | 1530 | 北勢～旭硝子、旭硝二紅線(1530) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D10_A1 | [12 empty] | 北勢DS.1530_AMP | 旭硝子旭硝二紅 AMP | LINE161 | AMP_CAL | C20R1394 | amp_cal | OPRD1: D10/161/1530/MW; OPRD2: D10/161/1530/MVAR; OPRD3: D10/0/CalcPoint/Vbs4
D10 | 北勢DS | 161 | 161kV | 1540 | 北勢～旭硝子、旭硝二白線(1540) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D10_A1 | [12 empty] | 北勢DS.1540_AMP | 旭硝子旭硝二白 AMP | LINE161 | AMP_CAL | C20R1394 | amp_cal | OPRD1: D10/161/1540/MW; OPRD2: D10/161/1540/MVAR; OPRD3: D10/0/CalcPoint/Vbs4
D10 | 北勢DS | 11 | 11kV | 1ABUS | #1ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D10_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D10/11/1ABUS/V
D10 | 北勢DS | 11 | 11kV | 1BBUS | #1BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D10_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D10/11/1BBUS/V
D10 | 北勢DS | 22 | 22kV | 3BUS | #3BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D10_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D10/22/3BUS/V
D10 | 北勢DS | 22 | 22kV | 4BUS | #4BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D10_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D10/22/4BUS/V
D10 | 北勢DS |  |  | 1DTR(A) | #1DTR(A) |  | TR_PERM | [9 empty] | B1/D10_A1 | [12 empty] | 北勢DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D10//1DTR(A)/SupLocal; OPRD2: D10//1DTR(A)/Tap Chan
D10 | 北勢DS |  |  | 1DTR(B) | #1DTR(B) |  | TR_PERM | [9 empty] | B1/D10_A1 | [12 empty] | 北勢DS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D10//1DTR(B)/SupLocal; OPRD2: D10//1DTR(B)/Tap Chan
D10 | 北勢DS |  |  | 3DTR | #3DTR |  | TR_PERM | [9 empty] | B1/D10_A1 | [12 empty] | 北勢DS.#3DTR_PERM | #3DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D10//3DTR/SupLocal; OPRD2: D10//3DTR/Tap Chan
D10 | 北勢DS |  |  | 4DTR | #4DTR |  | TR_PERM | [9 empty] | B1/D10_A1 | [12 empty] | 北勢DS.#4DTR_PERM | #4DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D10//4DTR/SupLocal; OPRD2: D10//4DTR/Tap Chan
D10 | 北勢DS | 11 | 11kV | XL21 | 北一線(XL21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D10/11/1ABUS/V; OPRD2: D10/11/XL21/I_R; OPRD3: D10/11/XL21/I_S; OPRD4: D10/11/XL21/I_T
D10 | 北勢DS | 11 | 11kV | XL22 | 北二線(XL22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D10/11/1ABUS/V; OPRD2: D10/11/XL22/I_R; OPRD3: D10/11/XL22/I_S; OPRD4: D10/11/XL22/I_T
D10 | 北勢DS | 11 | 11kV | XL23 | 北三線(XL23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D10/11/1ABUS/V; OPRD2: D10/11/XL23/I_R; OPRD3: D10/11/XL23/I_S; OPRD4: D10/11/XL23/I_T
D10 | 北勢DS | 11 | 11kV | XL24 | 北四線(XL24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D10/11/1ABUS/V; OPRD2: D10/11/XL24/I_R; OPRD3: D10/11/XL24/I_S; OPRD4: D10/11/XL24/I_T
D10 | 北勢DS | 11 | 11kV | XL25 | 北五線(XL25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D10/11/1ABUS/V; OPRD2: D10/11/XL25/I_R; OPRD3: D10/11/XL25/I_S; OPRD4: D10/11/XL25/I_T
D10 | 北勢DS | 11 | 11kV | XL26 | 北六線(XL26) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D10/11/1BBUS/V; OPRD2: D10/11/XL26/I_R; OPRD3: D10/11/XL26/I_S; OPRD4: D10/11/XL26/I_T
D10 | 北勢DS | 11 | 11kV | XL27 | 北七線(XL27) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D10/11/1BBUS/V; OPRD2: D10/11/XL27/I_R; OPRD3: D10/11/XL27/I_S; OPRD4: D10/11/XL27/I_T
D10 | 北勢DS | 11 | 11kV | XL28 | 北八線(XL28) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D10/11/1BBUS/V; OPRD2: D10/11/XL28/I_R; OPRD3: D10/11/XL28/I_S; OPRD4: D10/11/XL28/I_T
D10 | 北勢DS | 11 | 11kV | XL29 | 北九線(XL29) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D10/11/1BBUS/V; OPRD2: D10/11/XL29/I_R; OPRD3: D10/11/XL29/I_S; OPRD4: D10/11/XL29/I_T
D10 | 北勢DS | 11 | 11kV | XL30 | 北十線(XL30) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D10/11/1BBUS/V; OPRD2: D10/11/XL30/I_R; OPRD3: D10/11/XL30/I_S; OPRD4: D10/11/XL30/I_T
D10 | 北勢DS | 22 | 22kV | XL61 | 北六一線(XL61) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D10/22/3BUS/V; OPRD2: D10/22/XL61/I_R; OPRD3: D10/22/XL61/I_S; OPRD4: D10/22/XL61/I_T
D10 | 北勢DS | 22 | 22kV | XL62 | 北六二線(XL62) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D10/22/3BUS/V; OPRD2: D10/22/XL62/I_R; OPRD3: D10/22/XL62/I_S; OPRD4: D10/22/XL62/I_T
D10 | 北勢DS | 22 | 22kV | XL63 | 北六三線(XL63) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D10/22/3BUS/V; OPRD2: D10/22/XL63/I_R; OPRD3: D10/22/XL63/I_S; OPRD4: D10/22/XL63/I_T
D10 | 北勢DS | 22 | 22kV | XL64 | 北六四線(XL64) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D10/22/3BUS/V; OPRD2: D10/22/XL64/I_R; OPRD3: D10/22/XL64/I_S; OPRD4: D10/22/XL64/I_T
D10 | 北勢DS | 22 | 22kV | XL65 | 北六五線(XL65) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D10/22/3BUS/V; OPRD2: D10/22/XL65/I_R; OPRD3: D10/22/XL65/I_S; OPRD4: D10/22/XL65/I_T
D10 | 北勢DS | 22 | 22kV | XL66 | 北六六線(XL66) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D10/22/3BUS/V; OPRD2: D10/22/XL66/I_R; OPRD3: D10/22/XL66/I_S; OPRD4: D10/22/XL66/I_T
D10 | 北勢DS | 22 | 22kV | XL67 | 北六七線(XL67) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D10/22/3BUS/V; OPRD2: D10/22/XL67/I_R; OPRD3: D10/22/XL67/I_S; OPRD4: D10/22/XL67/I_T
D10 | 北勢DS | 22 | 22kV | XL68 | 北六八線(XL68) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D10/22/3BUS/V; OPRD2: D10/22/XL68/I_R; OPRD3: D10/22/XL68/I_S; OPRD4: D10/22/XL68/I_T
D10 | 北勢DS | 22 | 22kV | XL71 | 北七一線(XL71) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D10/22/4BUS/V; OPRD2: D10/22/XL71/I_R; OPRD3: D10/22/XL71/I_S; OPRD4: D10/22/XL71/I_T
D10 | 北勢DS | 22 | 22kV | XL72 | 北七二線(XL72) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D10/22/4BUS/V; OPRD2: D10/22/XL72/I_R; OPRD3: D10/22/XL72/I_S; OPRD4: D10/22/XL72/I_T
D10 | 北勢DS | 22 | 22kV | XL73 | 北七三線(XL73) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D10/22/4BUS/V; OPRD2: D10/22/XL73/I_R; OPRD3: D10/22/XL73/I_S; OPRD4: D10/22/XL73/I_T
D10 | 北勢DS | 22 | 22kV | XL74 | 北七四線(XL74) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D10/22/4BUS/V; OPRD2: D10/22/XL74/I_R; OPRD3: D10/22/XL74/I_S; OPRD4: D10/22/XL74/I_T
D10 | 北勢DS | 22 | 22kV | XL75 | 北七五線(XL75) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D10/22/4BUS/V; OPRD2: D10/22/XL75/I_R; OPRD3: D10/22/XL75/I_S; OPRD4: D10/22/XL75/I_T
D10 | 北勢DS | 22 | 22kV | XL76 | 北七六線(XL76) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D10/22/4BUS/V; OPRD2: D10/22/XL76/I_R; OPRD3: D10/22/XL76/I_S; OPRD4: D10/22/XL76/I_T
D10 | 北勢DS | 22 | 22kV | XL77 | 北七七線(XL77) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D10/22/4BUS/V; OPRD2: D10/22/XL77/I_R; OPRD3: D10/22/XL77/I_S; OPRD4: D10/22/XL77/I_T
D10 | 北勢DS | 22 | 22kV | XL78 | 北七八線(XL78) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D10/22/4BUS/V; OPRD2: D10/22/XL78/I_R; OPRD3: D10/22/XL78/I_S; OPRD4: D10/22/XL78/I_T
D10 | 北勢DS | 11 | 11kV | XL21 | 北一線(XL21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D10/11/XL21/kVA; OPRD2: D10/11/XL21/KVAR
D10 | 北勢DS | 11 | 11kV | XL22 | 北二線(XL22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D10/11/XL22/kVA; OPRD2: D10/11/XL22/KVAR
D10 | 北勢DS | 11 | 11kV | XL23 | 北三線(XL23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D10/11/XL23/kVA; OPRD2: D10/11/XL23/KVAR
D10 | 北勢DS | 11 | 11kV | XL24 | 北四線(XL24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D10/11/XL24/kVA; OPRD2: D10/11/XL24/KVAR
D10 | 北勢DS | 11 | 11kV | XL25 | 北五線(XL25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D10/11/XL25/kVA; OPRD2: D10/11/XL25/KVAR
D10 | 北勢DS | 11 | 11kV | XL26 | 北六線(XL26) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D10/11/XL26/kVA; OPRD2: D10/11/XL26/KVAR
D10 | 北勢DS | 11 | 11kV | XL27 | 北七線(XL27) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D10/11/XL27/kVA; OPRD2: D10/11/XL27/KVAR
D10 | 北勢DS | 11 | 11kV | XL28 | 北八線(XL28) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D10/11/XL28/kVA; OPRD2: D10/11/XL28/KVAR
D10 | 北勢DS | 11 | 11kV | XL29 | 北九線(XL29) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D10/11/XL29/kVA; OPRD2: D10/11/XL29/KVAR
D10 | 北勢DS | 11 | 11kV | XL30 | 北十線(XL30) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D10/11/XL30/kVA; OPRD2: D10/11/XL30/KVAR
D10 | 北勢DS | 22 | 22kV | XL61 | 北六一線(XL61) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D10/22/XL61/kVA; OPRD2: D10/22/XL61/KVAR
D10 | 北勢DS | 22 | 22kV | XL62 | 北六二線(XL62) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D10/22/XL62/kVA; OPRD2: D10/22/XL62/KVAR
D10 | 北勢DS | 22 | 22kV | XL63 | 北六三線(XL63) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D10/22/XL63/kVA; OPRD2: D10/22/XL63/KVAR
D10 | 北勢DS | 22 | 22kV | XL64 | 北六四線(XL64) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D10/22/XL64/kVA; OPRD2: D10/22/XL64/KVAR
D10 | 北勢DS | 22 | 22kV | XL65 | 北六五線(XL65) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D10/22/XL65/kVA; OPRD2: D10/22/XL65/KVAR
D10 | 北勢DS | 22 | 22kV | XL66 | 北六六線(XL66) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D10/22/XL66/kVA; OPRD2: D10/22/XL66/KVAR
D10 | 北勢DS | 22 | 22kV | XL67 | 北六七線(XL67) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D10/22/XL67/kVA; OPRD2: D10/22/XL67/KVAR
D10 | 北勢DS | 22 | 22kV | XL68 | 北六八線(XL68) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D10/22/XL68/kVA; OPRD2: D10/22/XL68/KVAR
D10 | 北勢DS | 22 | 22kV | XL71 | 北七一線(XL71) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D10/22/XL71/kVA; OPRD2: D10/22/XL71/KVAR
D10 | 北勢DS | 22 | 22kV | XL72 | 北七二線(XL72) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D10/22/XL72/kVA; OPRD2: D10/22/XL72/KVAR
D10 | 北勢DS | 22 | 22kV | XL73 | 北七三線(XL73) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D10/22/XL73/kVA; OPRD2: D10/22/XL73/KVAR
D10 | 北勢DS | 22 | 22kV | XL74 | 北七四線(XL74) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D10/22/XL74/kVA; OPRD2: D10/22/XL74/KVAR
D10 | 北勢DS | 22 | 22kV | XL75 | 北七五線(XL75) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D10/22/XL75/kVA; OPRD2: D10/22/XL75/KVAR
D10 | 北勢DS | 22 | 22kV | XL76 | 北七六線(XL76) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D10/22/XL76/kVA; OPRD2: D10/22/XL76/KVAR
D10 | 北勢DS | 22 | 22kV | XL77 | 北七七線(XL77) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D10/22/XL77/kVA; OPRD2: D10/22/XL77/KVAR
D10 | 北勢DS | 22 | 22kV | XL78 | 北七八線(XL78) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D10_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D10/22/XL78/kVA; OPRD2: D10/22/XL78/KVAR
D10 | 北勢DS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D10_A1 | [12 empty] | 北勢DS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D10/11/210/CB; OPRD2: 6.9; OPRD3: 0
D10 | 北勢DS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D10_A1 | [12 empty] | 北勢DS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D10/11/220/CB; OPRD2: 6.9; OPRD3: 0
D10 | 北勢DS | 22 | 22kV | 250 | #5SC(250) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D10_A1 | [12 empty] | 北勢DS.250_SC_MVAR | 23KV#5SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D10/22/250/CB; OPRD2: 13.8; OPRD3: 0
D10 | 北勢DS | 22 | 22kV | 260 | #6SC(260) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D10_A1 | [12 empty] | 北勢DS.260_SC_MVAR | 23KV#6SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D10/22/260/CB; OPRD2: 13.8; OPRD3: 0
D10 | 北勢DS | 22 | 22kV | 270 | #7SC(270) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D10_A1 | [12 empty] | 北勢DS.270_SC_MVAR | 23KV#7SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D10/22/270/CB; OPRD2: 13.8; OPRD3: 0
D10 | 北勢DS | 22 | 22kV | 280 | #8SC(280) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D10_A1 | [12 empty] | 北勢DS.280_SC_MVAR | 23KV#8SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D10/22/280/CB; OPRD2: 13.8; OPRD3: 0
D10 | 北勢DS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/D10_A1 | [12 empty] | 北勢DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_14 |  | com_alarm_42 | D10//1DTR/96B1 | D10//1DTR/96B2 | D10//1DTR/96D | D10//1DTR/63Q | D10//1DTR/51ZA | D10//1DTR/96PA | D10//1DTR/87A | D10//1DTR(A)/TRA | D10//3DTR/96PA | D10//3DTR/51ZA | D10//3DTR/TRA | D10//3DTR/GDA | D10//3DTR/PHA | D10//3DTR/87A | D10//3DTR/96B1 | D10//3DTR/96B2 | D10//3DTR/96D | D10//3DTR/63Q | D10//4DTR/96D | D10//4DTR/63Q | D10//4DTR/GDA | D10//4DTR/96B1 | D10//4DTR/96B2 | D10//4DTR/TRA | D10//4DTR/51ZA | D10//4DTR/96PA | D10//4DTR/87A | D10//4DTR/PHA | D10/11/310/PHA | D10/11/310/GDA | D10/11/320/PHA | D10/11/320/GDA | D10/161/1750/PHA | D10/161/1750/GDA | D10/161/1760/GDA | D10/161/1760/PHA | D10/161/1BUS/87A | D10/161/2BUS/87A | D10/22/350/GDA | D10/22/350/PHA | D10/22/370/GDA | D10/22/370/PHA
D10 | 北勢DS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/D10_A1 | [12 empty] | 北勢DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | STATION_FAULT_3 |  | com_alarm_3 | OPRD1: D10//1DTR(A)/TRF; OPRD2: D10//3DTR/TRF; OPRD3: D10//4DTR/TRF
D10 | 北勢DS | 161 | 161kV | 1750_D1 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D10_D1 | [17 empty] | lamp2CC | OPRD1: D10/161/1750/CB
D10 | 北勢DS | 11 | 11kV | 310_D1 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D10_D1 | [17 empty] | lamp2CC | OPRD1: D10/11/310/CB
D10 | 北勢DS | 11 | 11kV | 320_D1 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D10_D1 | [17 empty] | lamp2CC | OPRD1: D10/11/320/CB
D10 | 北勢DS | 161 | 161kV | 1760_D1 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D10_D1 | [17 empty] | lamp2CC | OPRD1: D10/161/1760/CB
D10 | 北勢DS | 161 | 161kV | 1770_D1 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D10_D1 | [17 empty] | lamp2CC | OPRD1: D10/161/1770/CB
D10 | 北勢DS | 22 | 22kV | 350_D1 | #3DTR(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D10_D1 | [17 empty] | lamp2CC | OPRD1: D10/22/350/CB
D10 | 北勢DS | 161 | 161kV | 1780_D1 | #4DTR(1780) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D10_D1 | [17 empty] | lamp2CC | OPRD1: D10/161/1780/CB
D10 | 北勢DS | 22 | 22kV | 370_D1 | #4DTR(370) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D10_D1 | [17 empty] | lamp2CC | OPRD1: D10/22/370/CB
D10 | 北勢DS | 0 |  | RTU_D1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/D10_D1 | [17 empty] | lamp2CC | OPRD1: D10/0/RTU/RTU_R_L
D10 | 北勢DS | 0 |  | StaDev_D1 | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/D10_D1 | [17 empty] | lamp2CC | OPRD1: D10/0/StaDev/STUV
D10 | 北勢DS | 0 |  | StaDev_D1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D10_D1 | [17 empty] | lamp2CC | OPRD1: D10/0/StaDev/DCA
D10 | 北勢DS | 0 |  | StaDev_D1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D10_D1 | [17 empty] | lamp2CC | OPRD1: D10/0/StaDev/DCE
D10 | 北勢DS | 0 |  | StaDev_D1 | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D10_D1 | [17 empty] | lamp2CC | OPRD1: D10/0/StaDev/PMA

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D10 | 北勢DS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 北勢DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | D10/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
D10 | 北勢DS | 161 | 161kV | 1510 | 雲林北勢線(1510) |  | I | [25 empty] | ADCS_N | [8 empty] | 北勢DS.1510_AMP | 雲林北勢線 AMP | LINE161 | D10/161/1510/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000
D10 | 北勢DS | 161 | 161kV | 1520 | 斗南北勢線(1520) |  | I | [25 empty] | ADCS_N | [8 empty] | 北勢DS.1520_AMP | 斗南北勢線 AMP | LINE161 | D10/161/1520/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北一線KVA | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北一線KVA | 11KV北一線KVA | FEEDER |  |  | KVA_CAL |  |  | 5 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北一線KW | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北一線KW | 11KV北一線KW | FEEDER |  |  | KW_CAL |  |  | 6 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北七線KVA | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北七線KVA | 11KV北七線KVA | FEEDER |  |  | KVA_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北七線KW | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北七線KW | 11KV北七線KW | FEEDER |  |  | KW_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北九線KVA | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北九線KVA | 11KV北九線KVA | FEEDER |  |  | KVA_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北九線KW | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北九線KW | 11KV北九線KW | FEEDER |  |  | KW_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北二線KVA | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北二線KVA | 11KV北二線KVA | FEEDER |  |  | KVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北二線KW | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北二線KW | 11KV北二線KW | FEEDER |  |  | KW_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北八線KVA | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北八線KVA | 11KV北八線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北八線KW | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北八線KW | 11KV北八線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北十線KVA | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北十線KVA | 11KV北十線KVA | FEEDER |  |  | KVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北十線KW | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北十線KW | 11KV北十線KW | FEEDER |  |  | KW_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北三線KVA | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北三線KVA | 11KV北三線KVA | FEEDER |  |  | KVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北三線KW | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北三線KW | 11KV北三線KW | FEEDER |  |  | KW_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北五線KVA | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北五線KVA | 11KV北五線KVA | FEEDER |  |  | KVA_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北五線KW | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北五線KW | 11KV北五線KW | FEEDER |  |  | KW_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北六線KVA | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北六線KVA | 11KV北六線KVA | FEEDER |  |  | KVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北六線KW | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北六線KW | 11KV北六線KW | FEEDER |  |  | KW_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北四線KVA | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北四線KVA | 11KV北四線KVA | FEEDER |  |  | KVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北四線KW | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北四線KW | 11KV北四線KW | FEEDER |  |  | KW_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北七一線KVA | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北七一線KVA | 23KV北七一線KVA | FEEDER |  |  | KVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北七一線KW | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北七一線KW | 23KV北七一線KW | FEEDER |  |  | KW_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北七七線KVA | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北七七線KVA | 23KV北七七線KVA | FEEDER |  |  | KVA_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北七七線KW | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北七七線KW | 23KV北七七線KW | FEEDER |  |  | KW_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北七二線KVA | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北七二線KVA | 23KV北七二線KVA | FEEDER |  |  | KVA_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北七二線KW | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北七二線KW | 23KV北七二線KW | FEEDER |  |  | KW_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北七八線KVA | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北七八線KVA | 23KV北七八線KVA | FEEDER |  |  | KVA_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北七八線KW | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北七八線KW | 23KV北七八線KW | FEEDER |  |  | KW_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北七三線KVA | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北七三線KVA | 23KV北七三線KVA | FEEDER |  |  | KVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北七三線KW | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北七三線KW | 23KV北七三線KW | FEEDER |  |  | KW_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北七五線KVA | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北七五線KVA | 23KV北七五線KVA | FEEDER |  |  | KVA_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北七五線KW | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北七五線KW | 23KV北七五線KW | FEEDER |  |  | KW_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北七六線KVA | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北七六線KVA | 23KV北七六線KVA | FEEDER |  |  | KVA_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北七六線KW | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北七六線KW | 23KV北七六線KW | FEEDER |  |  | KW_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北七四線KVA | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北七四線KVA | 23KV北七四線KVA | FEEDER |  |  | KVA_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北七四線KW | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北七四線KW | 23KV北七四線KW | FEEDER |  |  | KW_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北六一線KVA | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北六一線KVA | 23KV北六一線KVA | FEEDER |  |  | KVA_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北六一線KW | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北六一線KW | 23KV北六一線KW | FEEDER |  |  | KW_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北六七線KVA | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北六七線KVA | 23KV北六七線KVA | FEEDER |  |  | KVA_CAL |  |  | 43 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北六七線KW | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北六七線KW | 23KV北六七線KW | FEEDER |  |  | KW_CAL |  |  | 44 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北六二線KVA | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北六二線KVA | 23KV北六二線KVA | FEEDER |  |  | KVA_CAL |  |  | 45 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北六二線KW | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北六二線KW | 23KV北六二線KW | FEEDER |  |  | KW_CAL |  |  | 46 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北六八線KVA | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北六八線KVA | 23KV北六八線KVA | FEEDER |  |  | KVA_CAL |  |  | 47 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北六八線KW | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北六八線KW | 23KV北六八線KW | FEEDER |  |  | KW_CAL |  |  | 48 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北六三線KVA | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北六三線KVA | 23KV北六三線KVA | FEEDER |  |  | KVA_CAL |  |  | 49 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北六三線KW | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北六三線KW | 23KV北六三線KW | FEEDER |  |  | KW_CAL |  |  | 50 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北六五線KVA | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北六五線KVA | 23KV北六五線KVA | FEEDER |  |  | KVA_CAL |  |  | 51 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北六五線KW | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北六五線KW | 23KV北六五線KW | FEEDER |  |  | KW_CAL |  |  | 52 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北六六線KVA | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北六六線KVA | 23KV北六六線KVA | FEEDER |  |  | KVA_CAL |  |  | 53 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北六六線KW | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北六六線KW | 23KV北六六線KW | FEEDER |  |  | KW_CAL |  |  | 54 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北六四線KVA | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北六四線KVA | 23KV北六四線KVA | FEEDER |  |  | KVA_CAL |  |  | 55 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  |  |  |  | 北六四線KW | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.北六四線KW | 23KV北六四線KW | FEEDER |  |  | KW_CAL |  |  | 56 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 北勢DS.210_SC_MVAR | 11KV#1SC MVAR | SC | D10/11/210/MVAR |  | SC_LBS_11 |  |  | 57 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 11 | 11kV | 220_SC | #2SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 北勢DS.220_SC_MVAR | 11KV#2SC MVAR | SC | D10/11/220/MVAR |  | SC_LBS_11 |  |  | 58 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 22 | 22kV | 250_SC | #5SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 北勢DS.250_SC_MVAR | 23KV#5SC MVAR | SC | D10/22/250/MVAR |  | SC_CAL_23 |  |  | 59 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 22 | 22kV | 260_SC | #6SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 北勢DS.260_SC_MVAR | 23KV#6SC MVAR | SC | D10/22/260/MVAR |  | SC_CAL_23 |  |  | 60 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 22 | 22kV | 270_SC | #7SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 北勢DS.270_SC_MVAR | 23KV#7SC MVAR | SC | D10/22/270/MVAR |  | SC_CAL_23 |  |  | 61 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 22 | 22kV | 280_SC | #8SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 北勢DS.280_SC_MVAR | 23KV#8SC MVAR | SC | D10/22/280/MVAR |  | SC_CAL_23 |  |  | 62 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 161 | 161kV | 1530 | 旭硝子旭硝二紅(1530) |  | I | [25 empty] | ADCS_N | [8 empty] | 北勢DS.1530_AMP | 旭硝子旭硝二紅 AMP | LINE161 | D10/161/1530/I |  | AMP_CAL |  |  | 63 | CalcAIPoint | [21 empty] | C20R1394 | 1254.599976 | 1254.599976 | 1394.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D10 | 北勢DS | 0 |  | TRTOT | 北勢主變瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 北勢DS.TRTOT_MW | 北勢主變瞬時供電量 MW |  |  |  | TOTAL_PQ_CAL_3 |  |  | 64 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  | TRTOT | 北勢主變瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 北勢DS.TRTOT_MVAR | 北勢主變瞬時供電量 MVAR |  |  |  | TOTAL_PQ_CAL_3 |  |  | 65 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 北勢DS.#1DTR(A)_MVA | #1DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 66 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D10 | 北勢DS | 0 |  | 1DTR(A) | #1DTR(A) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 北勢DS.#1DTR(A)_LOAD | #1DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 67 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D10 | 北勢DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PF | [25 empty] | ADCS_N | [8 empty] | 北勢DS.#1DTR(A)_PF | #1DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 68 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D10 | 北勢DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 北勢DS.#1DTR(B)_MVA | #1DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 69 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D10 | 北勢DS | 0 |  | 1DTR(B) | #1DTR(B) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 北勢DS.#1DTR(B)_LOAD | #1DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 70 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D10 | 北勢DS | 0 |  | 1DTR(B) | #1DTR(B) |  | PF | [25 empty] | ADCS_N | [8 empty] | 北勢DS.#1DTR(B)_PF | #1DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 71 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D10 | 北勢DS | 0 |  | 3DTR | #3DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 北勢DS.#3DTR_MVA | #3DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 72 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D10 | 北勢DS | 0 |  | 3DTR | #3DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 北勢DS.#3DTR_LOAD | #3DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 73 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D10 | 北勢DS | 0 |  | 3DTR | #3DTR |  | PF | [25 empty] | ADCS_N | [8 empty] | 北勢DS.#3DTR_PF | #3DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 74 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D10 | 北勢DS | 0 |  | 4DTR | #4DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 北勢DS.#4DTR_MVA | #4DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 75 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D10 | 北勢DS | 0 |  | 4DTR | #4DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 北勢DS.#4DTR_LOAD | #4DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 76 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D10 | 北勢DS | 0 |  | 4DTR | #4DTR |  | PF | [25 empty] | ADCS_N | [8 empty] | 北勢DS.#4DTR_PF | #4DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 77 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D10 | 北勢DS | 0 |  | 1DTR | #1DTR |  | MW | [25 empty] | ADCS_N | [8 empty] | 北勢DS.#1DTR_MW | #1DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 78 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  | 1DTR | #1DTR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 北勢DS.#1DTR_MVAR | #1DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 79 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  | 1DTR | #1DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 北勢DS.#1DTR_MVA | #1DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 80 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D10 | 北勢DS | 0 |  | 1DTR | #1DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 北勢DS.#1DTR_LOAD | #1DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 81 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D10 | 北勢DS | 161 | 161kV | 1540 | 旭硝子旭硝二白(1540) |  | I | [25 empty] | ADCS_N | [8 empty] | 北勢DS.1540_AMP | 旭硝子旭硝二白 AMP | LINE161 | D10/161/1540/I |  | AMP_CAL |  |  | 82 | CalcAIPoint | [21 empty] | C20R1394 | 1254.599976 | 1254.599976 | 1394.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D10 | 北勢DS | 0 |  | 100_CB | 100(100_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.100_CB_1 | 100 CB (D1) | TIE |  |  | AD_LAMP_DD_1 |  |  | 83 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 300_CB | 300(300_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.300_CB_1 | 300 CB (D1) | TIE |  |  | AD_LAMP_DD_1 |  |  | 84 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 1750_CB | #1DTR(1750_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.1750_CB_1 | 1750(#1DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 85 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | 310_CB | #1DTR(310_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.310_CB_1 | 310(#1DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 86 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | 320_CB | #1DTR(320_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.320_CB_1 | 320(#1DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 87 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | 1770_CB | #3DTR(1770_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.1770_CB_1 | 1770(#3DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 88 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | 350_CB | #3DTR(350_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.350_CB_1 | 350(#3DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 89 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | 1780_CB | #4DTR(1780_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.1780_CB_1 | 1780(#4DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 90 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | 210_CB | #1SC(210_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.210_CB_1 | 210(11KV #1SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 91 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | 220_CB | #2SC(220_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.220_CB_1 | 220(11KV #2SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 92 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | 250_CB | #5SC(250_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.250_CB_1 | 250(23KV #5SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 93 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | 260_CB | #6SC(260_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.260_CB_1 | 260(23KV #6SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 94 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | 270_CB | #7SC(270_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.270_CB_1 | 270(23KV #7SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 95 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | 280_CB | #8SC(280_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.280_CB_1 | 280(23KV #8SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 96 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | 11__CBA | 11/斷路器重故障點燈(11__CBA) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.11/23KV_CBA_1 | 11/23KV斷路器重故障點燈 (D1) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 97 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | 11__CBF | 11/斷路器輕故障(11__CBF) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.11/23KV_CBF_1 | 11/23KV斷路器輕故障 (D1) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 98 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | RTU_S_L | RTU |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.RTU_S/L_1 | RTU SUPY/LOCAL (D1) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 99 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D10 | 北勢DS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_N | [8 empty] | 北勢DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | D10/0/CalcPoint/SUBA |  | STATION_FAULT_14 |  |  | 100 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 變電所輕故障點燈 | 變電所輕故障點燈 |  | SUBF | [25 empty] | ADCS_N | [8 empty] | 北勢DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | D10/0/CalcPoint/SUBF |  | STATION_FAULT_3 |  |  | 101 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.變電所重故障_1 | 變電所重故障點燈 (D1) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 102 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.變電所輕故障_1 | 變電所輕故障點燈 (D1) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 103 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1510_AMP | 雲林北勢線 | [27 empty] | ADCS_N | [8 empty] | 北勢DS.1510_AMP_A | 雲林北勢線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 104 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D10 | 北勢DS | 161 | 161kV | 1520_AMP | 斗南北勢線 | [27 empty] | ADCS_N | [8 empty] | 北勢DS.1520_AMP_A | 斗南北勢線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 105 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D10 | 北勢DS | 161 | 161kV | 1530_AMP | 旭硝子旭硝二紅 | [27 empty] | ADCS_N | [8 empty] | 北勢DS.1530_AMP_A | 旭硝子旭硝二紅 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 106 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D10 | 北勢DS | 0 |  | 370_CB | #4DTR(370_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.370_CB_1 | 370(#4DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 107 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PERM | [25 empty] | ADCS_N | [8 empty] | 北勢DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | D10//1DTR(A)/TR_PERM |  | DTR_PERM |  |  | 108 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D10 | 北勢DS | 0 |  | 1DTR(B) | #1DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 北勢DS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | D10//1DTR(B)/TR_PERM |  | DTR_PERM |  |  | 109 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D10 | 北勢DS | 0 |  | 3DTR | #3DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 北勢DS.#3DTR_PERM | #3DTR TAP PERMISSION POINT | MTR | D10//3DTR/TR_PERM |  | DTR_PERM |  |  | 110 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D10 | 北勢DS | 0 |  | 4DTR | #4DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 北勢DS.#4DTR_PERM | #4DTR TAP PERMISSION POINT | MTR | D10//4DTR/TR_PERM |  | DTR_PERM |  |  | 111 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D10 | 北勢DS | 0 |  | 1DTR_MVA | #1DTR | [27 empty] | ADCS_N | [8 empty] | 北勢DS.#1DTR_MVA_A | #1DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 112 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D10 | 北勢DS | 0 |  | 1DTR_MVA | #1DTR(A) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.#1DTR_MVA_1 | #1DTR(A) MVA 點燈 (D1) | MTR |  |  | MAP_SET |  |  | 113 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D10 | 北勢DS | 0 |  | 1DTR_MVA | #1DTR(B) | [27 empty] | DDCS1_1 | [8 empty] | 北勢DS.#1DTR_MVA_2 | #1DTR(B) MVA 點燈 (D1) | MTR |  |  | MAP_SET |  |  | 114 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
D10 | 北勢DS | 0 |  | 3DTR_MVA | #3DTR | [27 empty] | ADCS_N | [8 empty] | 北勢DS.#3DTR_MVA_A | #3DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 115 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D10 | 北勢DS | 0 |  | 3DTR_MVA | #3DTR |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.#3DTR_MVA_1 | #3DTR MVA 點燈 (D1) | MTR |  |  | AD_LAMP_DD_2 |  |  | 116 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D10 | 北勢DS | 0 |  | 4DTR_MVA | #4DTR | [27 empty] | ADCS_N | [8 empty] | 北勢DS.#4DTR_MVA_A | #4DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 117 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D10 | 北勢DS | 0 |  | 4DTR_MVA | #4DTR |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 北勢DS.#4DTR_MVA_1 | #4DTR MVA 點燈 (D1) | MTR |  |  | AD_LAMP_DD_2 |  |  | 118 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D10 | 北勢DS | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_N | [8 empty] | 北勢DS.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_DS |  |  | 119 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 1ABUS | #1ABUS |  | 11KV#1ABUSC | [25 empty] | CDCS | [8 empty] | 北勢DS.11KV#1ABUSC | #1ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 120 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D10 | 北勢DS | 0 |  | 1BBUS | #1BBUS |  | 11KV#1BBUSC | [25 empty] | CDCS | [8 empty] | 北勢DS.11KV#1BBUSC | #1BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 121 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D10 | 北勢DS | 0 |  | 3BUS | #3BUS |  | 23KV#3BUSC | [25 empty] | CDCS | [8 empty] | 北勢DS.23KV#3BUSC | #3BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 122 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D10 | 北勢DS | 0 |  | 4BUS | #4BUS |  | 23KV#4BUSC | [25 empty] | CDCS | [8 empty] | 北勢DS.23KV#4BUSC | #4BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 123 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D10 | 北勢DS | 0 |  | TAP_OVER | TAP |  | SET | [25 empty] | ADCS_N | [8 empty] | 北勢DS.TAP_OVER_SET | TAP OVER HI/LO ALARM | MTR |  |  | 5000_CB_T4 |  |  | 124 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D10 | 北勢DS | 0 |  | BUS_OVER | BUS |  | SET | [25 empty] | ADCS_N | [8 empty] | 北勢DS.BUS_OVER_SET | BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B4 |  |  | 125 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D10 | 北勢DS | 0 |  | 5000 | 虛擬5000 |  | CB動作 | [25 empty] | ADCS_N | [8 empty] | 北勢DS.5000_CB動作 | 虛擬5000 CB動作,請查明原因處理 | MTR |  |  | 5000_CB_M |  |  | 126 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 161 | 161kV | 1540_AMP | 旭硝子旭硝二白 | [27 empty] | ADCS_N | [8 empty] | 北勢DS.1540_AMP_A | 旭硝子旭硝二白 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 127 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D10 | 北勢DS | 0 |  | 注意OLTC | 注意OLTC |  | BUS電壓異常 | [25 empty] | ADCS_N | [8 empty] | 北勢DS.BUS電壓異常 | 注意OLTC Tap位置,並將RPDC閉鎖 | OTHER |  |  | STATION_FAULT_2 |  |  | 128 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | D10/0/RTU/ADCH1 |  |  |  | CDC | 129 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | D10/0/RTU/ADCH2 |  |  |  | CDC | 130 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | D10/0/RTU/ADCH3 |  |  |  | CDC | 131 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 0 |  | AI | AI |  | ADCH4 | [17 empty] | 2-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | D10/0/RTU/ADCH4 |  |  |  | CDC | 132 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 0 |  | AI | AI |  | ADCH5 | [17 empty] | 3-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.AI_ADCH5 | AI 90%參考點 ADCH5 | OTHER | D10/0/RTU/ADCH5 |  |  |  | CDC | 133 | GENERICAIPoint | DS038_L3 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | D10/0/RTU/ADCL1 |  |  |  | CDC | 134 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | D10/0/RTU/ADCL2 |  |  |  | CDC | 135 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | D10/0/RTU/ADCL3 |  |  |  | CDC | 136 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 0 |  | AI | AI |  | ADCL4 | [17 empty] | 2-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | D10/0/RTU/ADCL4 |  |  |  | CDC | 137 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 0 |  | AI | AI |  | ADCL5 | [17 empty] | 3-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.AI_ADCL5 | AI 10%參考點 ADCL5 | OTHER | D10/0/RTU/ADCL5 |  |  |  | CDC | 138 | GENERICAIPoint | DS038_L3 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 161 | 161kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | D10/161/1BUS/V |  |  |  | CDC | 139 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D10 | 北勢DS | 161 | 161kV | 2BUS | #2BUS |  | V | [17 empty] | 1-83 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | D10/161/2BUS/V |  |  |  | CDC | 140 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D10 | 北勢DS | 11 | 11kV | 1ABUS | #1ABUS |  | V | [17 empty] | 1-C9 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.11KV#1ABUS_KV | 11KV #1ABUS KV | BUS | D10/11/1ABUS/V |  |  |  | CDC | 141 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D10 | 北勢DS | 11 | 11kV | 1BBUS | #1BBUS |  | V | [17 empty] | 1-CD | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.11KV#1BBUS_KV | 11KV #1BBUS KV | BUS | D10/11/1BBUS/V |  |  |  | CDC | 142 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D10 | 北勢DS | 22 | 22kV | 3BUS | #3BUS |  | V | [17 empty] | 2-E3 | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.23KV#3BUS_KV | 23KV #3BUS KV | BUS | D10/22/3BUS/V |  |  |  | CDC | 143 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D10 | 北勢DS | 22 | 22kV | 4BUS | #4BUS |  | V | [17 empty] | 2-E7 | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.23KV#4BUS_KV | 23KV #4BUS KV | BUS | D10/22/4BUS/V |  |  |  | CDC | 144 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D10 | 北勢DS | 161 | 161kV | 1510 | 雲林北勢線(1510) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.1510_MW | 雲林北勢線 MW | LINE161 | D10/161/1510/MW |  |  |  | CDC | 145 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D10 | 北勢DS | 161 | 161kV | 1510 | 雲林北勢線(1510) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.1510_MVAR | 雲林北勢線 MVAR | LINE161 | D10/161/1510/MVAR |  |  |  | CDC | 146 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D10 | 北勢DS | 161 | 161kV | 1520 | 斗南北勢線(1520) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.1520_MW | 斗南北勢線 MW | LINE161 | D10/161/1520/MW |  |  |  | CDC | 147 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D10 | 北勢DS | 161 | 161kV | 1520 | 斗南北勢線(1520) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.1520_MVAR | 斗南北勢線 MVAR | LINE161 | D10/161/1520/MVAR |  |  |  | CDC | 148 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北一線 | 北一線 |  | 北一線KVAR | [17 empty] | 1-AE | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北一線KVAR | 11KV北一線 KVAR | FEEDER | D10/11/XL21/KVAR |  |  |  | CDC | 149 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北一線 | 北一線 |  | 北一線A1 | [17 empty] | 1-AF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北一線A1 | 11KV北一線 R相AMP | FEEDER | D10/11/XL21/I_R |  |  |  | CDC | 150 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北一線 | 北一線 |  | 北一線A2 | [17 empty] | 1-B0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北一線A2 | 11KV北一線 S相AMP | FEEDER | D10/11/XL21/I_S |  |  |  | CDC | 151 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北一線 | 北一線 |  | 北一線A3 | [17 empty] | 1-B1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北一線A3 | 11KV北一線 T相AMP | FEEDER | D10/11/XL21/I_T |  |  |  | CDC | 152 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北一線 | 北一線 |  | 北一線A0 | [17 empty] | 1-B2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北一線A0 | 11KV北一線 N相AMP | FEEDER | D10/11/XL21/I_N |  |  |  | CDC | 153 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北七線 | 北七線 |  | 北七線KVAR | [17 empty] | 1-D8 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七線KVAR | 11KV北七線 KVAR | FEEDER | D10/11/XL27/KVAR |  |  |  | CDC | 154 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北七線 | 北七線 |  | 北七線A1 | [17 empty] | 1-D9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七線A1 | 11KV北七線 R相AMP | FEEDER | D10/11/XL27/I_R |  |  |  | CDC | 155 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北七線 | 北七線 |  | 北七線A2 | [17 empty] | 1-DA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七線A2 | 11KV北七線 S相AMP | FEEDER | D10/11/XL27/I_S |  |  |  | CDC | 156 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北七線 | 北七線 |  | 北七線A3 | [17 empty] | 1-DB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七線A3 | 11KV北七線 T相AMP | FEEDER | D10/11/XL27/I_T |  |  |  | CDC | 157 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北七線 | 北七線 |  | 北七線A0 | [17 empty] | 1-DC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七線A0 | 11KV北七線 N相AMP | FEEDER | D10/11/XL27/I_N |  |  |  | CDC | 158 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北九線 | 北九線 |  | 北九線KVAR | [17 empty] | 1-E2 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北九線KVAR | 11KV北九線 KVAR | FEEDER | D10/11/XL29/KVAR |  |  |  | CDC | 159 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北九線 | 北九線 |  | 北九線A1 | [17 empty] | 1-E3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北九線A1 | 11KV北九線 R相AMP | FEEDER | D10/11/XL29/I_R |  |  |  | CDC | 160 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北九線 | 北九線 |  | 北九線A2 | [17 empty] | 1-E4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北九線A2 | 11KV北九線 S相AMP | FEEDER | D10/11/XL29/I_S |  |  |  | CDC | 161 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北九線 | 北九線 |  | 北九線A3 | [17 empty] | 1-E5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北九線A3 | 11KV北九線 T相AMP | FEEDER | D10/11/XL29/I_T |  |  |  | CDC | 162 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北九線 | 北九線 |  | 北九線A0 | [17 empty] | 1-E6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北九線A0 | 11KV北九線 N相AMP | FEEDER | D10/11/XL29/I_N |  |  |  | CDC | 163 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北二線 | 北二線 |  | 北二線KVAR | [17 empty] | 1-B3 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北二線KVAR | 11KV北二線 KVAR | FEEDER | D10/11/XL22/KVAR |  |  |  | CDC | 164 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北二線 | 北二線 |  | 北二線A1 | [17 empty] | 1-B4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北二線A1 | 11KV北二線 R相AMP | FEEDER | D10/11/XL22/I_R |  |  |  | CDC | 165 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北二線 | 北二線 |  | 北二線A2 | [17 empty] | 1-B5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北二線A2 | 11KV北二線 S相AMP | FEEDER | D10/11/XL22/I_S |  |  |  | CDC | 166 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北二線 | 北二線 |  | 北二線A3 | [17 empty] | 1-B6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北二線A3 | 11KV北二線 T相AMP | FEEDER | D10/11/XL22/I_T |  |  |  | CDC | 167 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北二線 | 北二線 |  | 北二線A0 | [17 empty] | 1-B7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北二線A0 | 11KV北二線 N相AMP | FEEDER | D10/11/XL22/I_N |  |  |  | CDC | 168 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北八線 | 北八線 |  | 北八線KVAR | [17 empty] | 1-DD | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北八線KVAR | 11KV北八線 KVAR | FEEDER | D10/11/XL28/KVAR |  |  |  | CDC | 169 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北八線 | 北八線 |  | 北八線A1 | [17 empty] | 1-DE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北八線A1 | 11KV北八線 R相AMP | FEEDER | D10/11/XL28/I_R |  |  |  | CDC | 170 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北八線 | 北八線 |  | 北八線A2 | [17 empty] | 1-DF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北八線A2 | 11KV北八線 S相AMP | FEEDER | D10/11/XL28/I_S |  |  |  | CDC | 171 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北八線 | 北八線 |  | 北八線A3 | [17 empty] | 1-E0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北八線A3 | 11KV北八線 T相AMP | FEEDER | D10/11/XL28/I_T |  |  |  | CDC | 172 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北八線 | 北八線 |  | 北八線A0 | [17 empty] | 1-E1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北八線A0 | 11KV北八線 N相AMP | FEEDER | D10/11/XL28/I_N |  |  |  | CDC | 173 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北十線 | 北十線 |  | 北十線KVAR | [17 empty] | 1-E7 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北十線KVAR | 11KV北十線 KVAR | FEEDER | D10/11/XL30/KVAR |  |  |  | CDC | 174 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北十線 | 北十線 |  | 北十線A1 | [17 empty] | 1-E8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北十線A1 | 11KV北十線 R相AMP | FEEDER | D10/11/XL30/I_R |  |  |  | CDC | 175 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北十線 | 北十線 |  | 北十線A2 | [17 empty] | 1-E9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北十線A2 | 11KV北十線 S相AMP | FEEDER | D10/11/XL30/I_S |  |  |  | CDC | 176 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北十線 | 北十線 |  | 北十線A3 | [17 empty] | 1-EA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北十線A3 | 11KV北十線 T相AMP | FEEDER | D10/11/XL30/I_T |  |  |  | CDC | 177 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北十線 | 北十線 |  | 北十線A0 | [17 empty] | 1-EB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北十線A0 | 11KV北十線 N相AMP | FEEDER | D10/11/XL30/I_N |  |  |  | CDC | 178 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北三線 | 北三線 |  | 北三線KVAR | [17 empty] | 1-B8 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北三線KVAR | 11KV北三線 KVAR | FEEDER | D10/11/XL23/KVAR |  |  |  | CDC | 179 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北三線 | 北三線 |  | 北三線A1 | [17 empty] | 1-B9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北三線A1 | 11KV北三線 R相AMP | FEEDER | D10/11/XL23/I_R |  |  |  | CDC | 180 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北三線 | 北三線 |  | 北三線A2 | [17 empty] | 1-BA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北三線A2 | 11KV北三線 S相AMP | FEEDER | D10/11/XL23/I_S |  |  |  | CDC | 181 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北三線 | 北三線 |  | 北三線A3 | [17 empty] | 1-BB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北三線A3 | 11KV北三線 T相AMP | FEEDER | D10/11/XL23/I_T |  |  |  | CDC | 182 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北三線 | 北三線 |  | 北三線A0 | [17 empty] | 1-BC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北三線A0 | 11KV北三線 N相AMP | FEEDER | D10/11/XL23/I_N |  |  |  | CDC | 183 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北五線 | 北五線 |  | 北五線KVAR | [17 empty] | 1-C4 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北五線KVAR | 11KV北五線 KVAR | FEEDER | D10/11/XL25/KVAR |  |  |  | CDC | 184 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北五線 | 北五線 |  | 北五線A1 | [17 empty] | 1-C5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北五線A1 | 11KV北五線 R相AMP | FEEDER | D10/11/XL25/I_R |  |  |  | CDC | 185 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北五線 | 北五線 |  | 北五線A2 | [17 empty] | 1-C6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北五線A2 | 11KV北五線 S相AMP | FEEDER | D10/11/XL25/I_S |  |  |  | CDC | 186 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北五線 | 北五線 |  | 北五線A3 | [17 empty] | 1-C7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北五線A3 | 11KV北五線 T相AMP | FEEDER | D10/11/XL25/I_T |  |  |  | CDC | 187 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北五線 | 北五線 |  | 北五線A0 | [17 empty] | 1-C8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北五線A0 | 11KV北五線 N相AMP | FEEDER | D10/11/XL25/I_N |  |  |  | CDC | 188 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北六線 | 北六線 |  | 北六線KVAR | [17 empty] | 1-D3 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六線KVAR | 11KV北六線 KVAR | FEEDER | D10/11/XL26/KVAR |  |  |  | CDC | 189 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北六線 | 北六線 |  | 北六線A1 | [17 empty] | 1-D4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六線A1 | 11KV北六線 R相AMP | FEEDER | D10/11/XL26/I_R |  |  |  | CDC | 190 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北六線 | 北六線 |  | 北六線A2 | [17 empty] | 1-D5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六線A2 | 11KV北六線 S相AMP | FEEDER | D10/11/XL26/I_S |  |  |  | CDC | 191 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北六線 | 北六線 |  | 北六線A3 | [17 empty] | 1-D6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六線A3 | 11KV北六線 T相AMP | FEEDER | D10/11/XL26/I_T |  |  |  | CDC | 192 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北六線 | 北六線 |  | 北六線A0 | [17 empty] | 1-D7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六線A0 | 11KV北六線 N相AMP | FEEDER | D10/11/XL26/I_N |  |  |  | CDC | 193 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北四線 | 北四線 |  | 北四線KVAR | [17 empty] | 1-BD | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北四線KVAR | 11KV北四線 KVAR | FEEDER | D10/11/XL24/KVAR |  |  |  | CDC | 194 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北四線 | 北四線 |  | 北四線A1 | [17 empty] | 1-BE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北四線A1 | 11KV北四線 R相AMP | FEEDER | D10/11/XL24/I_R |  |  |  | CDC | 195 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北四線 | 北四線 |  | 北四線A2 | [17 empty] | 1-BF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北四線A2 | 11KV北四線 S相AMP | FEEDER | D10/11/XL24/I_S |  |  |  | CDC | 196 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北四線 | 北四線 |  | 北四線A3 | [17 empty] | 1-C2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北四線A3 | 11KV北四線 T相AMP | FEEDER | D10/11/XL24/I_T |  |  |  | CDC | 197 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | 北四線 | 北四線 |  | 北四線A0 | [17 empty] | 1-C3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北四線A0 | 11KV北四線 N相AMP | FEEDER | D10/11/XL24/I_N |  |  |  | CDC | 198 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七一線 | 北七一線 |  | 北七一線KVAR | [17 empty] | 2-E8 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七一線KVAR | 23KV北七一線 KVAR | FEEDER | D10/22/XL71/KVAR |  |  |  | CDC | 199 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七一線 | 北七一線 |  | 北七一線A1 | [17 empty] | 2-E9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七一線A1 | 23KV北七一線 R相AMP | FEEDER | D10/22/XL71/I_R |  |  |  | CDC | 200 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七一線 | 北七一線 |  | 北七一線A2 | [17 empty] | 2-EA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七一線A2 | 23KV北七一線 S相AMP | FEEDER | D10/22/XL71/I_S |  |  |  | CDC | 201 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七一線 | 北七一線 |  | 北七一線A3 | [17 empty] | 2-EB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七一線A3 | 23KV北七一線 T相AMP | FEEDER | D10/22/XL71/I_T |  |  |  | CDC | 202 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七一線 | 北七一線 |  | 北七一線A0 | [17 empty] | 2-EC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七一線A0 | 23KV北七一線 N相AMP | FEEDER | D10/22/XL71/I_N |  |  |  | CDC | 203 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七七線 | 北七七線 |  | 北七七線KVAR | [17 empty] | 3-8C | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七七線KVAR | 23KV北七七線 KVAR | FEEDER | D10/22/XL77/KVAR |  |  |  | CDC | 204 | GENERICAIPoint | DS038_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七七線 | 北七七線 |  | 北七七線A1 | [17 empty] | 3-8D | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七七線A1 | 23KV北七七線 R相AMP | FEEDER | D10/22/XL77/I_R |  |  |  | CDC | 205 | GENERICAIPoint | DS038_L3 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七七線 | 北七七線 |  | 北七七線A2 | [17 empty] | 3-8E | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七七線A2 | 23KV北七七線 S相AMP | FEEDER | D10/22/XL77/I_S |  |  |  | CDC | 206 | GENERICAIPoint | DS038_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七七線 | 北七七線 |  | 北七七線A3 | [17 empty] | 3-8F | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七七線A3 | 23KV北七七線 T相AMP | FEEDER | D10/22/XL77/I_T |  |  |  | CDC | 207 | GENERICAIPoint | DS038_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七七線 | 北七七線 |  | 北七七線A0 | [17 empty] | 3-90 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七七線A0 | 23KV北七七線 N相AMP | FEEDER | D10/22/XL77/I_N |  |  |  | CDC | 208 | GENERICAIPoint | DS038_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七二線 | 北七二線 |  | 北七二線KVAR | [17 empty] | 2-ED | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七二線KVAR | 23KV北七二線 KVAR | FEEDER | D10/22/XL72/KVAR |  |  |  | CDC | 209 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七二線 | 北七二線 |  | 北七二線A1 | [17 empty] | 2-EE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七二線A1 | 23KV北七二線 R相AMP | FEEDER | D10/22/XL72/I_R |  |  |  | CDC | 210 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七二線 | 北七二線 |  | 北七二線A2 | [17 empty] | 2-EF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七二線A2 | 23KV北七二線 S相AMP | FEEDER | D10/22/XL72/I_S |  |  |  | CDC | 211 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七二線 | 北七二線 |  | 北七二線A3 | [17 empty] | 2-F0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七二線A3 | 23KV北七二線 T相AMP | FEEDER | D10/22/XL72/I_T |  |  |  | CDC | 212 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七二線 | 北七二線 |  | 北七二線A0 | [17 empty] | 2-F1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七二線A0 | 23KV北七二線 N相AMP | FEEDER | D10/22/XL72/I_N |  |  |  | CDC | 213 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七八線 | 北七八線 |  | 北七八線KVAR | [17 empty] | 3-91 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七八線KVAR | 23KV北七八線 KVAR | FEEDER | D10/22/XL78/KVAR |  |  |  | CDC | 214 | GENERICAIPoint | DS038_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七八線 | 北七八線 |  | 北七八線A1 | [17 empty] | 3-92 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七八線A1 | 23KV北七八線 R相AMP | FEEDER | D10/22/XL78/I_R |  |  |  | CDC | 215 | GENERICAIPoint | DS038_L3 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七八線 | 北七八線 |  | 北七八線A2 | [17 empty] | 3-93 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七八線A2 | 23KV北七八線 S相AMP | FEEDER | D10/22/XL78/I_S |  |  |  | CDC | 216 | GENERICAIPoint | DS038_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七八線 | 北七八線 |  | 北七八線A3 | [17 empty] | 3-94 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七八線A3 | 23KV北七八線 T相AMP | FEEDER | D10/22/XL78/I_T |  |  |  | CDC | 217 | GENERICAIPoint | DS038_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七八線 | 北七八線 |  | 北七八線A0 | [17 empty] | 3-95 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七八線A0 | 23KV北七八線 N相AMP | FEEDER | D10/22/XL78/I_N |  |  |  | CDC | 218 | GENERICAIPoint | DS038_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七三線 | 北七三線 |  | 北七三線KVAR | [17 empty] | 2-F2 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七三線KVAR | 23KV北七三線 KVAR | FEEDER | D10/22/XL73/KVAR |  |  |  | CDC | 219 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七三線 | 北七三線 |  | 北七三線A1 | [17 empty] | 2-F3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七三線A1 | 23KV北七三線 R相AMP | FEEDER | D10/22/XL73/I_R |  |  |  | CDC | 220 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七三線 | 北七三線 |  | 北七三線A2 | [17 empty] | 2-F4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七三線A2 | 23KV北七三線 S相AMP | FEEDER | D10/22/XL73/I_S |  |  |  | CDC | 221 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七三線 | 北七三線 |  | 北七三線A3 | [17 empty] | 2-F5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七三線A3 | 23KV北七三線 T相AMP | FEEDER | D10/22/XL73/I_T |  |  |  | CDC | 222 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七三線 | 北七三線 |  | 北七三線A0 | [17 empty] | 2-F6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七三線A0 | 23KV北七三線 N相AMP | FEEDER | D10/22/XL73/I_N |  |  |  | CDC | 223 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七五線 | 北七五線 |  | 北七五線KVAR | [17 empty] | 3-82 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七五線KVAR | 23KV北七五線 KVAR | FEEDER | D10/22/XL75/KVAR |  |  |  | CDC | 224 | GENERICAIPoint | DS038_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七五線 | 北七五線 |  | 北七五線A1 | [17 empty] | 3-83 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七五線A1 | 23KV北七五線 R相AMP | FEEDER | D10/22/XL75/I_R |  |  |  | CDC | 225 | GENERICAIPoint | DS038_L3 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七五線 | 北七五線 |  | 北七五線A2 | [17 empty] | 3-84 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七五線A2 | 23KV北七五線 S相AMP | FEEDER | D10/22/XL75/I_S |  |  |  | CDC | 226 | GENERICAIPoint | DS038_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七五線 | 北七五線 |  | 北七五線A3 | [17 empty] | 3-85 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七五線A3 | 23KV北七五線 T相AMP | FEEDER | D10/22/XL75/I_T |  |  |  | CDC | 227 | GENERICAIPoint | DS038_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七五線 | 北七五線 |  | 北七五線A0 | [17 empty] | 3-86 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七五線A0 | 23KV北七五線 N相AMP | FEEDER | D10/22/XL75/I_N |  |  |  | CDC | 228 | GENERICAIPoint | DS038_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七六線 | 北七六線 |  | 北七六線KVAR | [17 empty] | 3-87 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七六線KVAR | 23KV北七六線 KVAR | FEEDER | D10/22/XL76/KVAR |  |  |  | CDC | 229 | GENERICAIPoint | DS038_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七六線 | 北七六線 |  | 北七六線A1 | [17 empty] | 3-88 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七六線A1 | 23KV北七六線 R相AMP | FEEDER | D10/22/XL76/I_R |  |  |  | CDC | 230 | GENERICAIPoint | DS038_L3 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七六線 | 北七六線 |  | 北七六線A2 | [17 empty] | 3-89 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七六線A2 | 23KV北七六線 S相AMP | FEEDER | D10/22/XL76/I_S |  |  |  | CDC | 231 | GENERICAIPoint | DS038_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七六線 | 北七六線 |  | 北七六線A3 | [17 empty] | 3-8A | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七六線A3 | 23KV北七六線 T相AMP | FEEDER | D10/22/XL76/I_T |  |  |  | CDC | 232 | GENERICAIPoint | DS038_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七六線 | 北七六線 |  | 北七六線A0 | [17 empty] | 3-8B | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七六線A0 | 23KV北七六線 N相AMP | FEEDER | D10/22/XL76/I_N |  |  |  | CDC | 233 | GENERICAIPoint | DS038_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七四線 | 北七四線 |  | 北七四線KVAR | [17 empty] | 2-F7 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七四線KVAR | 23KV北七四線 KVAR | FEEDER | D10/22/XL74/KVAR |  |  |  | CDC | 234 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七四線 | 北七四線 |  | 北七四線A1 | [17 empty] | 2-F8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七四線A1 | 23KV北七四線 R相AMP | FEEDER | D10/22/XL74/I_R |  |  |  | CDC | 235 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七四線 | 北七四線 |  | 北七四線A2 | [17 empty] | 2-F9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七四線A2 | 23KV北七四線 S相AMP | FEEDER | D10/22/XL74/I_S |  |  |  | CDC | 236 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七四線 | 北七四線 |  | 北七四線A3 | [17 empty] | 2-FA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七四線A3 | 23KV北七四線 T相AMP | FEEDER | D10/22/XL74/I_T |  |  |  | CDC | 237 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北七四線 | 北七四線 |  | 北七四線A0 | [17 empty] | 2-FB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北七四線A0 | 23KV北七四線 N相AMP | FEEDER | D10/22/XL74/I_N |  |  |  | CDC | 238 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六一線 | 北六一線 |  | 北六一線KVAR | [17 empty] | 2-B9 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六一線KVAR | 23KV北六一線 KVAR | FEEDER | D10/22/XL61/KVAR |  |  |  | CDC | 239 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六一線 | 北六一線 |  | 北六一線A1 | [17 empty] | 2-BA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六一線A1 | 23KV北六一線 R相AMP | FEEDER | D10/22/XL61/I_R |  |  |  | CDC | 240 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六一線 | 北六一線 |  | 北六一線A2 | [17 empty] | 2-BB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六一線A2 | 23KV北六一線 S相AMP | FEEDER | D10/22/XL61/I_S |  |  |  | CDC | 241 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六一線 | 北六一線 |  | 北六一線A3 | [17 empty] | 2-BC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六一線A3 | 23KV北六一線 T相AMP | FEEDER | D10/22/XL61/I_T |  |  |  | CDC | 242 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六一線 | 北六一線 |  | 北六一線A0 | [17 empty] | 2-BD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六一線A0 | 23KV北六一線 N相AMP | FEEDER | D10/22/XL61/I_N |  |  |  | CDC | 243 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六七線 | 北六七線 |  | 北六七線KVAR | [17 empty] | 2-D9 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六七線KVAR | 23KV北六七線 KVAR | FEEDER | D10/22/XL67/KVAR |  |  |  | CDC | 244 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六七線 | 北六七線 |  | 北六七線A1 | [17 empty] | 2-DA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六七線A1 | 23KV北六七線 R相AMP | FEEDER | D10/22/XL67/I_R |  |  |  | CDC | 245 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六七線 | 北六七線 |  | 北六七線A2 | [17 empty] | 2-DB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六七線A2 | 23KV北六七線 S相AMP | FEEDER | D10/22/XL67/I_S |  |  |  | CDC | 246 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六七線 | 北六七線 |  | 北六七線A3 | [17 empty] | 2-DC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六七線A3 | 23KV北六七線 T相AMP | FEEDER | D10/22/XL67/I_T |  |  |  | CDC | 247 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六七線 | 北六七線 |  | 北六七線A0 | [17 empty] | 2-DD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六七線A0 | 23KV北六七線 N相AMP | FEEDER | D10/22/XL67/I_N |  |  |  | CDC | 248 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六二線 | 北六二線 |  | 北六二線KVAR | [17 empty] | 2-BE | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六二線KVAR | 23KV北六二線 KVAR | FEEDER | D10/22/XL62/KVAR |  |  |  | CDC | 249 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六二線 | 北六二線 |  | 北六二線A1 | [17 empty] | 2-BF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六二線A1 | 23KV北六二線 R相AMP | FEEDER | D10/22/XL62/I_R |  |  |  | CDC | 250 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六二線 | 北六二線 |  | 北六二線A2 | [17 empty] | 2-C2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六二線A2 | 23KV北六二線 S相AMP | FEEDER | D10/22/XL62/I_S |  |  |  | CDC | 251 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六二線 | 北六二線 |  | 北六二線A3 | [17 empty] | 2-C3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六二線A3 | 23KV北六二線 T相AMP | FEEDER | D10/22/XL62/I_T |  |  |  | CDC | 252 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六二線 | 北六二線 |  | 北六二線A0 | [17 empty] | 2-C4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六二線A0 | 23KV北六二線 N相AMP | FEEDER | D10/22/XL62/I_N |  |  |  | CDC | 253 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六八線 | 北六八線 |  | 北六八線KVAR | [17 empty] | 2-DE | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六八線KVAR | 23KV北六八線 KVAR | FEEDER | D10/22/XL68/KVAR |  |  |  | CDC | 254 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六八線 | 北六八線 |  | 北六八線A1 | [17 empty] | 2-DF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六八線A1 | 23KV北六八線 R相AMP | FEEDER | D10/22/XL68/I_R |  |  |  | CDC | 255 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六八線 | 北六八線 |  | 北六八線A2 | [17 empty] | 2-E0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六八線A2 | 23KV北六八線 S相AMP | FEEDER | D10/22/XL68/I_S |  |  |  | CDC | 256 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六八線 | 北六八線 |  | 北六八線A3 | [17 empty] | 2-E1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六八線A3 | 23KV北六八線 T相AMP | FEEDER | D10/22/XL68/I_T |  |  |  | CDC | 257 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六八線 | 北六八線 |  | 北六八線A0 | [17 empty] | 2-E2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六八線A0 | 23KV北六八線 N相AMP | FEEDER | D10/22/XL68/I_N |  |  |  | CDC | 258 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六三線 | 北六三線 |  | 北六三線KVAR | [17 empty] | 2-C5 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六三線KVAR | 23KV北六三線 KVAR | FEEDER | D10/22/XL63/KVAR |  |  |  | CDC | 259 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六三線 | 北六三線 |  | 北六三線A1 | [17 empty] | 2-C6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六三線A1 | 23KV北六三線 R相AMP | FEEDER | D10/22/XL63/I_R |  |  |  | CDC | 260 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六三線 | 北六三線 |  | 北六三線A2 | [17 empty] | 2-C7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六三線A2 | 23KV北六三線 S相AMP | FEEDER | D10/22/XL63/I_S |  |  |  | CDC | 261 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六三線 | 北六三線 |  | 北六三線A3 | [17 empty] | 2-C8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六三線A3 | 23KV北六三線 T相AMP | FEEDER | D10/22/XL63/I_T |  |  |  | CDC | 262 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六三線 | 北六三線 |  | 北六三線A0 | [17 empty] | 2-C9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六三線A0 | 23KV北六三線 N相AMP | FEEDER | D10/22/XL63/I_N |  |  |  | CDC | 263 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六五線 | 北六五線 |  | 北六五線KVAR | [17 empty] | 2-CF | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六五線KVAR | 23KV北六五線 KVAR | FEEDER | D10/22/XL65/KVAR |  |  |  | CDC | 264 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六五線 | 北六五線 |  | 北六五線A1 | [17 empty] | 2-D0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六五線A1 | 23KV北六五線 R相AMP | FEEDER | D10/22/XL65/I_R |  |  |  | CDC | 265 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六五線 | 北六五線 |  | 北六五線A2 | [17 empty] | 2-D1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六五線A2 | 23KV北六五線 S相AMP | FEEDER | D10/22/XL65/I_S |  |  |  | CDC | 266 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六五線 | 北六五線 |  | 北六五線A3 | [17 empty] | 2-D2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六五線A3 | 23KV北六五線 T相AMP | FEEDER | D10/22/XL65/I_T |  |  |  | CDC | 267 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六五線 | 北六五線 |  | 北六五線A0 | [17 empty] | 2-D3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六五線A0 | 23KV北六五線 N相AMP | FEEDER | D10/22/XL65/I_N |  |  |  | CDC | 268 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六六線 | 北六六線 |  | 北六六線KVAR | [17 empty] | 2-D4 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六六線KVAR | 23KV北六六線 KVAR | FEEDER | D10/22/XL66/KVAR |  |  |  | CDC | 269 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六六線 | 北六六線 |  | 北六六線A1 | [17 empty] | 2-D5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六六線A1 | 23KV北六六線 R相AMP | FEEDER | D10/22/XL66/I_R |  |  |  | CDC | 270 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六六線 | 北六六線 |  | 北六六線A2 | [17 empty] | 2-D6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六六線A2 | 23KV北六六線 S相AMP | FEEDER | D10/22/XL66/I_S |  |  |  | CDC | 271 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六六線 | 北六六線 |  | 北六六線A3 | [17 empty] | 2-D7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六六線A3 | 23KV北六六線 T相AMP | FEEDER | D10/22/XL66/I_T |  |  |  | CDC | 272 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六六線 | 北六六線 |  | 北六六線A0 | [17 empty] | 2-D8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六六線A0 | 23KV北六六線 N相AMP | FEEDER | D10/22/XL66/I_N |  |  |  | CDC | 273 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六四線 | 北六四線 |  | 北六四線KVAR | [17 empty] | 2-CA | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六四線KVAR | 23KV北六四線 KVAR | FEEDER | D10/22/XL64/KVAR |  |  |  | CDC | 274 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六四線 | 北六四線 |  | 北六四線A1 | [17 empty] | 2-CB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六四線A1 | 23KV北六四線 R相AMP | FEEDER | D10/22/XL64/I_R |  |  |  | CDC | 275 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六四線 | 北六四線 |  | 北六四線A2 | [17 empty] | 2-CC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六四線A2 | 23KV北六四線 S相AMP | FEEDER | D10/22/XL64/I_S |  |  |  | CDC | 276 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六四線 | 北六四線 |  | 北六四線A3 | [17 empty] | 2-CD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六四線A3 | 23KV北六四線 T相AMP | FEEDER | D10/22/XL64/I_T |  |  |  | CDC | 277 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | 北六四線 | 北六四線 |  | 北六四線A0 | [17 empty] | 2-CE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 北勢DS.北六四線A0 | 23KV北六四線 N相AMP | FEEDER | D10/22/XL64/I_N |  |  |  | CDC | 278 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_80 | 64.000000 | 72.000000 | 76.000000 | 600.000000 | 0.400000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 0 |  | 1500TIE | 1500TIE |  | I | [17 empty] | 1-98 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.1500TIE_AMP | 1500TIE AMP | TIE | D10/161/1500/I_R |  |  |  | CDC | 279 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | _100 | 100 |  | I_R | [17 empty] | 1-CA | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.11KV_100_A1 | 11KV 100 R相AMP | TIE | D10/11/100/I_R |  |  |  | CDC | 280 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | _100 | 100 |  | I_S | [17 empty] | 1-CB | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.11KV_100_A2 | 11KV 100 S相AMP | TIE | D10/11/100/I_S |  |  |  | CDC | 281 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 11 | 11kV | _100 | 100 |  | I_T | [17 empty] | 1-CC | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.11KV_100_A3 | 11KV 100 T相AMP | TIE | D10/11/100/I_T |  |  |  | CDC | 282 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | _300 | 300 |  | I_R | [17 empty] | 2-E4 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.23KV_300_A1 | 23KV 300 R相AMP | TIE | D10/22/300/I_R |  |  |  | CDC | 283 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | _300 | 300 |  | I_S | [17 empty] | 2-E5 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.23KV_300_A2 | 23KV 300 S相AMP | TIE | D10/22/300/I_S |  |  |  | CDC | 284 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 22 | 22kV | _300 | 300 |  | I_T | [17 empty] | 2-E6 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.23KV_300_A3 | 23KV 300 T相AMP | TIE | D10/22/300/I_T |  |  |  | CDC | 285 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 0 |  |  |  |  | DCV_N | [17 empty] | 2-FD | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.直流N電源電壓 | 直流N電源電壓 | OTHER | D10/0/StaDev/DCV_N |  |  |  | CDC | 286 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D10 | 北勢DS | 0 |  |  |  |  | DCV_P | [17 empty] | 2-FC | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.直流P電源電壓 | 直流P電源電壓 | OTHER | D10/0/StaDev/DCV_P |  |  |  | CDC | 287 | GENERICAIPoint | DS038_L2 | CDC2_AI |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D10 | 北勢DS | 161 | 161kV | 1530 | 旭硝子旭硝二紅(1530) |  | MW | [17 empty] | 1-88 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.1530_MW | 旭硝子旭硝二紅 MW | LINE161 | D10/161/1530/MW |  |  |  | CDC | 288 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D10 | 北勢DS | 161 | 161kV | 1530 | 旭硝子旭硝二紅(1530) |  | MVAR | [17 empty] | 1-89 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.1530_MVAR | 旭硝子旭硝二紅 MVAR | LINE161 | D10/161/1530/MVAR |  |  |  | CDC | 289 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D10 | 北勢DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MW | [17 empty] | 1-A9 | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | D10/11/310/KW |  |  |  | CDC | 290 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D10 | 北勢DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVAR | [17 empty] | 1-AA | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | D10/11/310/KVAR |  |  |  | CDC | 291 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D10 | 北勢DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_R | [17 empty] | 1-AB | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | D10/11/310/I_R |  |  |  | CDC | 292 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_S | [17 empty] | 1-AC | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | D10/11/310/I_S |  |  |  | CDC | 293 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_T | [17 empty] | 1-AD | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | D10/11/310/I_T |  |  |  | CDC | 294 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 0 |  | 1DTR | #1DTR |  | OilTemp | [17 empty] | 1-99 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.#1DTR_OIL | #1DTR 油溫 | MTR | D10//1DTR/OilTemp |  |  |  | CDC | 295 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D10 | 北勢DS | 0 |  | 1DTR(A) | #1DTR(A) |  | CoilTemp | [17 empty] | 1-9A | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | D10//1DTR(A)/CoilTemp |  |  |  | CDC | 296 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D10 | 北勢DS | 0 |  | 1DTR(A) | #1DTR(A) |  | TapPosMv | [17 empty] | 1-9C |  | 1-39 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 北勢DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | D10//1DTR(A)/TapPosMv |  |  |  | CDC | 297 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D10 | 北勢DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MW | [17 empty] | 1-CE | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | D10/11/320/KW |  |  |  | CDC | 298 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D10 | 北勢DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVAR | [17 empty] | 1-CF | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | D10/11/320/KVAR |  |  |  | CDC | 299 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D10 | 北勢DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_R | [17 empty] | 1-D0 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | D10/11/320/I_R |  |  |  | CDC | 300 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_S | [17 empty] | 1-D1 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | D10/11/320/I_S |  |  |  | CDC | 301 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_T | [17 empty] | 1-D2 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | D10/11/320/I_T |  |  |  | CDC | 302 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 0 |  | 1DTR(B) | #1DTR(B) |  | CoilTemp | [17 empty] | 1-9B | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | D10//1DTR(B)/CoilTemp |  |  |  | CDC | 303 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D10 | 北勢DS | 0 |  | 1DTR(B) | #1DTR(B) |  | TapPosMv | [17 empty] | 1-9D |  | 1-3B |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 北勢DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | D10//1DTR(B)/TapPosMv |  |  |  | CDC | 304 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D10 | 北勢DS | 0 |  | 3DTR | #3DTR二次側 |  | MW | [17 empty] | 1-F6 | [5 empty] | MW_-108_108(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.#3DTR_MW | #3DTR二次側 MW | MTR | D10/22/350/KW |  |  |  | CDC | 305 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D10 | 北勢DS | 0 |  | 3DTR | #3DTR二次側 |  | MVAR | [17 empty] | 1-F7 | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.#3DTR_MVAR | #3DTR二次側 MVAR | MTR | D10/22/350/KVAR |  |  |  | CDC | 306 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D10 | 北勢DS | 0 |  | 3DTR | #3DTR二次側 |  | I_R | [17 empty] | 1-F8 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.#3DTR_A1 | #3DTR二次側 R相AMP | MTR | D10/22/350/I_R |  |  |  | CDC | 307 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 0 |  | 3DTR | #3DTR二次側 |  | I_S | [17 empty] | 1-F9 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.#3DTR_A2 | #3DTR二次側 S相AMP | MTR | D10/22/350/I_S |  |  |  | CDC | 308 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 0 |  | 3DTR | #3DTR二次側 |  | I_T | [17 empty] | 1-FA | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.#3DTR_A3 | #3DTR二次側 T相AMP | MTR | D10/22/350/I_T |  |  |  | CDC | 309 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 0 |  | 3DTR | #3DTR |  | OilTemp | [17 empty] | 1-A3 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.#3DTR_OIL | #3DTR 油溫 | MTR | D10//3DTR/OilTemp |  |  |  | CDC | 310 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D10 | 北勢DS | 0 |  | 3DTR | #3DTR |  | CoilTemp | [17 empty] | 1-A4 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.#3DTR_COIL | #3DTR 線溫 | MTR | D10//3DTR/CoilTemp |  |  |  | CDC | 311 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D10 | 北勢DS | 0 |  | 3DTR | #3DTR |  | TapPosMv | [17 empty] | 1-A5 |  | 1-41 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 北勢DS.#3DTR_TAP | #3DTR OLTC TAP | MTR | D10//3DTR/TapPosMv |  |  |  | CDC | 312 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D10 | 北勢DS | 0 |  | 4DTR | #4DTR二次側 |  | MW | [17 empty] | 1-FB | [5 empty] | MW_-108_108(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.#4DTR_MW | #4DTR二次側 MW | MTR | D10/22/370/KW |  |  |  | CDC | 313 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D10 | 北勢DS | 0 |  | 4DTR | #4DTR二次側 |  | MVAR | [17 empty] | 1-FC | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.#4DTR_MVAR | #4DTR二次側 MVAR | MTR | D10/22/370/KVAR |  |  |  | CDC | 314 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D10 | 北勢DS | 0 |  | 4DTR | #4DTR二次側 |  | I_R | [17 empty] | 1-FD | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.#4DTR_A1 | #4DTR二次側 R相AMP | MTR | D10/22/370/I_R |  |  |  | CDC | 315 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 0 |  | 4DTR | #4DTR二次側 |  | I_S | [17 empty] | 1-FE | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.#4DTR_A2 | #4DTR二次側 S相AMP | MTR | D10/22/370/I_S |  |  |  | CDC | 316 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 0 |  | 4DTR | #4DTR二次側 |  | I_T | [17 empty] | 1-FF | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.#4DTR_A3 | #4DTR二次側 T相AMP | MTR | D10/22/370/I_T |  |  |  | CDC | 317 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D10 | 北勢DS | 0 |  | 4DTR | #4DTR |  | OilTemp | [17 empty] | 1-A6 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.#4DTR_OIL | #4DTR 油溫 | MTR | D10//4DTR/OilTemp |  |  |  | CDC | 318 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D10 | 北勢DS | 0 |  | 4DTR | #4DTR |  | CoilTemp | [17 empty] | 1-A7 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.#4DTR_COIL | #4DTR 線溫 | MTR | D10//4DTR/CoilTemp |  |  |  | CDC | 319 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D10 | 北勢DS | 0 |  | 4DTR | #4DTR |  | TapPosMv | [17 empty] | 1-A8 |  | 1-43 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 北勢DS.#4DTR_TAP | #4DTR OLTC TAP | MTR | D10//4DTR/TapPosMv |  |  |  | CDC | 320 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D10 | 北勢DS | 161 | 161kV | 1540 | 旭硝子旭硝二白(1540) |  | MW | [17 empty] | 1-8A | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.1540_MW | 旭硝子旭硝二白 MW | LINE161 | D10/161/1540/MW |  |  |  | CDC | 321 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D10 | 北勢DS | 161 | 161kV | 1540 | 旭硝子旭硝二白(1540) |  | MVAR | [17 empty] | 1-8B | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 北勢DS.1540_MVAR | 旭硝子旭硝二白 MVAR | LINE161 | D10/161/1540/MVAR |  |  |  | CDC | 322 | GENERICAIPoint | DS038_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D10 | 北勢DS | 161 | 161kV | 1510 | 雲林北勢線(1510) |  | PHA | [17 empty] | 1-00-03 | [7 empty] | 161KV_N | [8 empty] | 北勢DS.1510_PHA | 雲林北勢線(1510) 相間RY | LINE161 | D10/161/1510/PHA |  |  |  | CDC | 323 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1510 | 雲林北勢線(1510) |  | GDA | [17 empty] | 1-00-04 | [7 empty] | 161KV_N | [8 empty] | 北勢DS.1510_GDA | 雲林北勢線(1510) 接地RY | LINE161 | D10/161/1510/GDA |  |  |  | CDC | 324 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1510 | 雲林北勢線(1510) |  | CB | [17 empty] | 1-00-00 |  | 1-01 | [5 empty] | 161KV_N | [8 empty] | 北勢DS.1510_CB | 1510(雲林北勢線) CB | LINE161 | D10/161/1510/CB |  |  |  | CDC | 325 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 161 | 161kV | 1510 | 雲林北勢線(1510) |  | 79UL | [17 empty] | 1-30-03 |  | 1-25 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1510_79UL | 雲林北勢線(1510) 79RY U/L | LINE161 | D10/161/1510/79UL |  |  |  | CDC | 326 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 161 | 161kV | 1510 | 雲林北勢線(1510) |  | DS1 | 1511 | [16 empty] | 1-38-00 | 1-38-01 | 1-44 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1511_DS | 1511(雲林北勢線) DS | LINE161 | D10/161/1510/DS1 |  |  |  | CDC | 327 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D10 | 北勢DS | 161 | 161kV | 1510 | 雲林北勢線(1510) |  | DS2 | 1512 | [16 empty] | 1-38-02 | 1-38-03 | 1-45 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1512_DS | 1512(雲林北勢線) DS | LINE161 | D10/161/1510/DS2 |  |  |  | CDC | 328 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D10 | 北勢DS | 161 | 161kV | 1510 | 雲林北勢線(1510) |  | DS3 | 1513 | [16 empty] | 1-38-04 | 1-38-05 | 1-46 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1513_DS | 1513(雲林北勢線) DS | LINE161 | D10/161/1510/DS3 |  |  |  | CDC | 329 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D10 | 北勢DS | 161 | 161kV | 1510 | 雲林北勢線(1510) |  | E3 | 1513E | [16 empty] | 1-38-06 | 1-38-07 | 1-47 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1513E_ES | 1513E(雲林北勢線) ES | LINE161 | D10/161/1510/ES3 |  |  |  | CDC | 330 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D10 | 北勢DS | 161 | 161kV | 1520 | 斗南北勢線(1520) |  | PHA | [17 empty] | 1-01-00 | [7 empty] | 161KV_N | [8 empty] | 北勢DS.1520_PHA | 斗南北勢線(1520) 相間RY | LINE161 | D10/161/1520/PHA |  |  |  | CDC | 331 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1520 | 斗南北勢線(1520) |  | GDA | [17 empty] | 1-01-01 | [7 empty] | 161KV_N | [8 empty] | 北勢DS.1520_GDA | 斗南北勢線(1520) 接地RY | LINE161 | D10/161/1520/GDA |  |  |  | CDC | 332 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1520 | 斗南北勢線(1520) |  | CB | [17 empty] | 1-00-05 |  | 1-02 | [5 empty] | 161KV_N | [8 empty] | 北勢DS.1520_CB | 1520(斗南北勢線) CB | LINE161 | D10/161/1520/CB |  |  |  | CDC | 333 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 161 | 161kV | 1520 | 斗南北勢線(1520) |  | 79UL | [17 empty] | 1-30-05 |  | 1-27 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1520_79UL | 斗南北勢線(1520) 79RY U/L | LINE161 | D10/161/1520/79UL |  |  |  | CDC | 334 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 161 | 161kV | 1520 | 斗南北勢線(1520) |  | DS1 | 1521 | [16 empty] | 1-38-08 | 1-38-09 | 1-48 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1521_DS | 1521(斗南北勢線) DS | LINE161 | D10/161/1520/DS1 |  |  |  | CDC | 335 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D10 | 北勢DS | 161 | 161kV | 1520 | 斗南北勢線(1520) |  | DS2 | 1522 | [16 empty] | 1-38-10 | 1-38-11 | 1-49 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1522_DS | 1522(斗南北勢線) DS | LINE161 | D10/161/1520/DS2 |  |  |  | CDC | 336 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D10 | 北勢DS | 161 | 161kV | 1520 | 斗南北勢線(1520) |  | DS3 | 1523 | [16 empty] | 1-38-12 | 1-38-13 | 1-4A | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1523_DS | 1523(斗南北勢線) DS | LINE161 | D10/161/1520/DS3 |  |  |  | CDC | 337 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D10 | 北勢DS | 161 | 161kV | 1520 | 斗南北勢線(1520) |  | E3 | 1523E | [16 empty] | 1-38-14 | 1-38-15 | 1-4B | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1523E_ES | 1523E(斗南北勢線) ES | LINE161 | D10/161/1520/ES3 |  |  |  | CDC | 338 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D10 | 北勢DS | 11 | 11kV | XL21 | 北一線(XL21) |  | PHA | [17 empty] | 1-14-04 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL21_PHA | 11KV北一線(XL21) 相間RY | FEEDER | D10/11/XL21/PHA |  |  |  | CDC | 339 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL21 | 北一線(XL21) |  | GDA | [17 empty] | 1-14-05 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL21_GDA | 11KV北一線(XL21) 接地RY | FEEDER | D10/11/XL21/GDA |  |  |  | CDC | 340 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL21 | 北一線(XL21) 79RY |  | 79UL | [17 empty] | 2-30-02 |  | 2-25 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL21_79UL | 11KV北一線(XL21) 79RY U/L | FEEDER | D10/11/XL21/79UL |  |  |  | CDC | 341 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 11 | 11kV | XL21_LCO | 北一線(XL21) LCO |  | TapPosMv | [17 empty] | 2-30-03 |  | 2-26 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL21_LCO_TAP | 11KV北一線(XL21) LCO TAP | FEEDER | D10/11/XL21/ADJ |  |  |  | CDC | 342 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D10 | 北勢DS | 11 | 11kV | XL21 | XL21(11KV北一線) |  | CB | [17 empty] | 1-14-03 |  | 1-12 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL21_CB | XL21(11KV北一線) CB | FEEDER | D10/11/XL21/CB |  |  |  | CDC | 343 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | XL22 | 北二線(XL22) |  | PHA | [17 empty] | 1-14-07 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL22_PHA | 11KV北二線(XL22) 相間RY | FEEDER | D10/11/XL22/PHA |  |  |  | CDC | 344 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL22 | 北二線(XL22) |  | GDA | [17 empty] | 1-15-00 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL22_GDA | 11KV北二線(XL22) 接地RY | FEEDER | D10/11/XL22/GDA |  |  |  | CDC | 345 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL22 | 北二線(XL22) 79RY |  | 79UL | [17 empty] | 2-30-04 |  | 2-27 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL22_79UL | 11KV北二線(XL22) 79RY U/L | FEEDER | D10/11/XL22/79UL |  |  |  | CDC | 346 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 11 | 11kV | XL22_LCO | 北二線(XL22) LCO |  | TapPosMv | [17 empty] | 2-30-05 |  | 2-28 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL22_LCO_TAP | 11KV北二線(XL22) LCO TAP | FEEDER | D10/11/XL22/ADJ |  |  |  | CDC | 347 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D10 | 北勢DS | 11 | 11kV | XL22 | XL22(11KV北二線) |  | CB | [17 empty] | 1-14-06 |  | 1-13 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL22_CB | XL22(11KV北二線) CB | FEEDER | D10/11/XL22/CB |  |  |  | CDC | 348 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | XL23 | 北三線(XL23) |  | PHA | [17 empty] | 1-15-02 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL23_PHA | 11KV北三線(XL23) 相間RY | FEEDER | D10/11/XL23/PHA |  |  |  | CDC | 349 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL23 | 北三線(XL23) |  | GDA | [17 empty] | 1-15-03 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL23_GDA | 11KV北三線(XL23) 接地RY | FEEDER | D10/11/XL23/GDA |  |  |  | CDC | 350 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL23 | 北三線(XL23) 79RY |  | 79UL | [17 empty] | 2-30-06 |  | 2-29 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL23_79UL | 11KV北三線(XL23) 79RY U/L | FEEDER | D10/11/XL23/79UL |  |  |  | CDC | 351 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 11 | 11kV | XL23_LCO | 北三線(XL23) LCO |  | TapPosMv | [17 empty] | 2-30-07 |  | 2-2A | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL23_LCO_TAP | 11KV北三線(XL23) LCO TAP | FEEDER | D10/11/XL23/ADJ |  |  |  | CDC | 352 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D10 | 北勢DS | 11 | 11kV | XL23 | XL23(11KV北三線) |  | CB | [17 empty] | 1-15-01 |  | 1-14 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL23_CB | XL23(11KV北三線) CB | FEEDER | D10/11/XL23/CB |  |  |  | CDC | 353 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | XL24 | 北四線(XL24) |  | PHA | [17 empty] | 1-15-05 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL24_PHA | 11KV北四線(XL24) 相間RY | FEEDER | D10/11/XL24/PHA |  |  |  | CDC | 354 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL24 | 北四線(XL24) |  | GDA | [17 empty] | 1-15-06 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL24_GDA | 11KV北四線(XL24) 接地RY | FEEDER | D10/11/XL24/GDA |  |  |  | CDC | 355 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL24 | 北四線(XL24) 79RY |  | 79UL | [17 empty] | 2-30-08 |  | 2-2B | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL24_79UL | 11KV北四線(XL24) 79RY U/L | FEEDER | D10/11/XL24/79UL |  |  |  | CDC | 356 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 11 | 11kV | XL24_LCO | 北四線(XL24) LCO |  | TapPosMv | [17 empty] | 2-30-09 |  | 2-2C | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL24_LCO_TAP | 11KV北四線(XL24) LCO TAP | FEEDER | D10/11/XL24/ADJ |  |  |  | CDC | 357 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D10 | 北勢DS | 11 | 11kV | XL24 | XL24(11KV北四線) |  | CB | [17 empty] | 1-15-04 |  | 1-15 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL24_CB | XL24(11KV北四線) CB | FEEDER | D10/11/XL24/CB |  |  |  | CDC | 358 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | XL25 | 北五線(XL25) |  | PHA | [17 empty] | 1-16-00 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL25_PHA | 11KV北五線(XL25) 相間RY | FEEDER | D10/11/XL25/PHA |  |  |  | CDC | 359 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL25 | 北五線(XL25) |  | GDA | [17 empty] | 1-16-01 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL25_GDA | 11KV北五線(XL25) 接地RY | FEEDER | D10/11/XL25/GDA |  |  |  | CDC | 360 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL25 | 北五線(XL25) 79RY |  | 79UL | [17 empty] | 2-30-10 |  | 2-2D | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL25_79UL | 11KV北五線(XL25) 79RY U/L | FEEDER | D10/11/XL25/79UL |  |  |  | CDC | 361 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 11 | 11kV | XL25_LCO | 北五線(XL25) LCO |  | TapPosMv | [17 empty] | 2-30-11 |  | 2-2E | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL25_LCO_TAP | 11KV北五線(XL25) LCO TAP | FEEDER | D10/11/XL25/ADJ |  |  |  | CDC | 362 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D10 | 北勢DS | 11 | 11kV | XL25 | XL25(11KV北五線) |  | CB | [17 empty] | 1-15-07 |  | 1-16 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL25_CB | XL25(11KV北五線) CB | FEEDER | D10/11/XL25/CB |  |  |  | CDC | 363 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | XL26 | 北六線(XL26) |  | PHA | [17 empty] | 1-17-04 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL26_PHA | 11KV北六線(XL26) 相間RY | FEEDER | D10/11/XL26/PHA |  |  |  | CDC | 364 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL26 | 北六線(XL26) |  | GDA | [17 empty] | 1-17-05 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL26_GDA | 11KV北六線(XL26) 接地RY | FEEDER | D10/11/XL26/GDA |  |  |  | CDC | 365 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL26 | 北六線(XL26) 79RY |  | 79UL | [17 empty] | 2-30-14 |  | 2-31 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL26_79UL | 11KV北六線(XL26) 79RY U/L | FEEDER | D10/11/XL26/79UL |  |  |  | CDC | 366 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 11 | 11kV | XL26_LCO | 北六線(XL26) LCO |  | TapPosMv | [17 empty] | 2-30-15 |  | 2-32 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL26_LCO_TAP | 11KV北六線(XL26) LCO TAP | FEEDER | D10/11/XL26/ADJ |  |  |  | CDC | 367 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D10 | 北勢DS | 11 | 11kV | XL26 | XL26(11KV北六線) |  | CB | [17 empty] | 1-17-03 |  | 1-1B | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL26_CB | XL26(11KV北六線) CB | FEEDER | D10/11/XL26/CB |  |  |  | CDC | 368 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | XL27 | 北七線(XL27) |  | PHA | [17 empty] | 1-17-07 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL27_PHA | 11KV北七線(XL27) 相間RY | FEEDER | D10/11/XL27/PHA |  |  |  | CDC | 369 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL27 | 北七線(XL27) |  | GDA | [17 empty] | 1-18-00 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL27_GDA | 11KV北七線(XL27) 接地RY | FEEDER | D10/11/XL27/GDA |  |  |  | CDC | 370 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL27 | 北七線(XL27) 79RY |  | 79UL | [17 empty] | 2-31-00 |  | 2-33 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL27_79UL | 11KV北七線(XL27) 79RY U/L | FEEDER | D10/11/XL27/79UL |  |  |  | CDC | 371 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 11 | 11kV | XL27_LCO | 北七線(XL27) LCO |  | TapPosMv | [17 empty] | 2-31-01 |  | 2-34 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL27_LCO_TAP | 11KV北七線(XL27) LCO TAP | FEEDER | D10/11/XL27/ADJ |  |  |  | CDC | 372 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D10 | 北勢DS | 11 | 11kV | XL27 | XL27(11KV北七線) |  | CB | [17 empty] | 1-17-06 |  | 1-1C | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL27_CB | XL27(11KV北七線) CB | FEEDER | D10/11/XL27/CB |  |  |  | CDC | 373 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | XL28 | 北八線(XL28) |  | PHA | [17 empty] | 1-18-02 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL28_PHA | 11KV北八線(XL28) 相間RY | FEEDER | D10/11/XL28/PHA |  |  |  | CDC | 374 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL28 | 北八線(XL28) |  | GDA | [17 empty] | 1-18-03 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL28_GDA | 11KV北八線(XL28) 接地RY | FEEDER | D10/11/XL28/GDA |  |  |  | CDC | 375 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL28 | 北八線(XL28) 79RY |  | 79UL | [17 empty] | 2-31-02 |  | 2-35 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL28_79UL | 11KV北八線(XL28) 79RY U/L | FEEDER | D10/11/XL28/79UL |  |  |  | CDC | 376 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 11 | 11kV | XL28_LCO | 北八線(XL28) LCO |  | TapPosMv | [17 empty] | 2-31-03 |  | 2-36 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL28_LCO_TAP | 11KV北八線(XL28) LCO TAP | FEEDER | D10/11/XL28/ADJ |  |  |  | CDC | 377 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D10 | 北勢DS | 11 | 11kV | XL28 | XL28(11KV北八線) |  | CB | [17 empty] | 1-18-01 |  | 1-1D | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL28_CB | XL28(11KV北八線) CB | FEEDER | D10/11/XL28/CB |  |  |  | CDC | 378 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | XL29 | 北九線(XL29) |  | PHA | [17 empty] | 1-18-05 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL29_PHA | 11KV北九線(XL29) 相間RY | FEEDER | D10/11/XL29/PHA |  |  |  | CDC | 379 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL29 | 北九線(XL29) |  | GDA | [17 empty] | 1-18-06 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL29_GDA | 11KV北九線(XL29) 接地RY | FEEDER | D10/11/XL29/GDA |  |  |  | CDC | 380 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL29 | 北九線(XL29) 79RY |  | 79UL | [17 empty] | 2-31-04 |  | 2-37 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL29_79UL | 11KV北九線(XL29) 79RY U/L | FEEDER | D10/11/XL29/79UL |  |  |  | CDC | 381 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 11 | 11kV | XL29_LCO | 北九線(XL29) LCO |  | TapPosMv | [17 empty] | 2-31-05 |  | 2-38 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL29_LCO_TAP | 11KV北九線(XL29) LCO TAP | FEEDER | D10/11/XL29/ADJ |  |  |  | CDC | 382 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D10 | 北勢DS | 11 | 11kV | XL29 | XL29(11KV北九線) |  | CB | [17 empty] | 1-18-04 |  | 1-1E | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL29_CB | XL29(11KV北九線) CB | FEEDER | D10/11/XL29/CB |  |  |  | CDC | 383 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | XL30 | 北十線(XL30) |  | PHA | [17 empty] | 1-19-00 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL30_PHA | 11KV北十線(XL30) 相間RY | FEEDER | D10/11/XL30/PHA |  |  |  | CDC | 384 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL30 | 北十線(XL30) |  | GDA | [17 empty] | 1-19-01 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL30_GDA | 11KV北十線(XL30) 接地RY | FEEDER | D10/11/XL30/GDA |  |  |  | CDC | 385 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | XL30 | 北十線(XL30) 79RY |  | 79UL | [17 empty] | 2-31-06 |  | 2-39 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL30_79UL | 11KV北十線(XL30) 79RY U/L | FEEDER | D10/11/XL30/79UL |  |  |  | CDC | 386 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 11 | 11kV | XL30_LCO | 北十線(XL30) LCO |  | TapPosMv | [17 empty] | 2-31-07 |  | 2-3A | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL30_LCO_TAP | 11KV北十線(XL30) LCO TAP | FEEDER | D10/11/XL30/ADJ |  |  |  | CDC | 387 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D10 | 北勢DS | 11 | 11kV | XL30 | XL30(11KV北十線) |  | CB | [17 empty] | 1-18-07 |  | 1-1F | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL30_CB | XL30(11KV北十線) CB | FEEDER | D10/11/XL30/CB |  |  |  | CDC | 388 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL61 | 北六一線(XL61) |  | PHA | [17 empty] | 2-05-03 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL61_PHA | 23KV北六一線(XL61) 相間RY | FEEDER | D10/22/XL61/PHA |  |  |  | CDC | 389 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL61 | 北六一線(XL61) |  | GDA | [17 empty] | 2-05-04 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL61_GDA | 23KV北六一線(XL61) 接地RY | FEEDER | D10/22/XL61/GDA |  |  |  | CDC | 390 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL61 | 北六一線(XL61) 79RY |  | 79UL | [17 empty] | 2-33-01 |  | 2-54 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL61_79UL | 23KV北六一線(XL61) 79RY U/L | FEEDER | D10/22/XL61/79UL |  |  |  | CDC | 391 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 22 | 22kV | XL61_LCO | 北六一線(XL61) LCO |  | TapPosMv | [17 empty] | 2-33-02 |  | 2-55 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL61_LCO_TAP | 23KV北六一線(XL61) LCO TAP | FEEDER | D10/22/XL61/ADJ |  |  |  | CDC | 392 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D10 | 北勢DS | 22 | 22kV | XL61 | XL61(23KV北六一線) |  | CB | [17 empty] | 2-05-02 |  | 2-0E | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL61_CB | XL61(23KV北六一線) CB | FEEDER | D10/22/XL61/CB |  |  |  | CDC | 393 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL62 | 北六二線(XL62) |  | PHA | [17 empty] | 2-05-06 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL62_PHA | 23KV北六二線(XL62) 相間RY | FEEDER | D10/22/XL62/PHA |  |  |  | CDC | 394 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL62 | 北六二線(XL62) |  | GDA | [17 empty] | 2-05-07 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL62_GDA | 23KV北六二線(XL62) 接地RY | FEEDER | D10/22/XL62/GDA |  |  |  | CDC | 395 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL62 | 北六二線(XL62) 79RY |  | 79UL | [17 empty] | 2-33-03 |  | 2-56 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL62_79UL | 23KV北六二線(XL62) 79RY U/L | FEEDER | D10/22/XL62/79UL |  |  |  | CDC | 396 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 22 | 22kV | XL62_LCO | 北六二線(XL62) LCO |  | TapPosMv | [17 empty] | 2-33-04 |  | 2-57 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL62_LCO_TAP | 23KV北六二線(XL62) LCO TAP | FEEDER | D10/22/XL62/ADJ |  |  |  | CDC | 397 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D10 | 北勢DS | 22 | 22kV | XL62 | XL62(23KV北六二線) |  | CB | [17 empty] | 2-05-05 |  | 2-0F | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL62_CB | XL62(23KV北六二線) CB | FEEDER | D10/22/XL62/CB |  |  |  | CDC | 398 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL63 | 北六三線(XL63) |  | PHA | [17 empty] | 2-06-01 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL63_PHA | 23KV北六三線(XL63) 相間RY | FEEDER | D10/22/XL63/PHA |  |  |  | CDC | 399 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL63 | 北六三線(XL63) |  | GDA | [17 empty] | 2-06-02 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL63_GDA | 23KV北六三線(XL63) 接地RY | FEEDER | D10/22/XL63/GDA |  |  |  | CDC | 400 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL63 | 北六三線(XL63) 79RY |  | 79UL | [17 empty] | 2-33-05 |  | 2-58 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL63_79UL | 23KV北六三線(XL63) 79RY U/L | FEEDER | D10/22/XL63/79UL |  |  |  | CDC | 401 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 22 | 22kV | XL63_LCO | 北六三線(XL63) LCO |  | TapPosMv | [17 empty] | 2-33-06 |  | 2-59 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL63_LCO_TAP | 23KV北六三線(XL63) LCO TAP | FEEDER | D10/22/XL63/ADJ |  |  |  | CDC | 402 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D10 | 北勢DS | 22 | 22kV | XL63 | XL63(23KV北六三線) |  | CB | [17 empty] | 2-06-00 |  | 2-10 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL63_CB | XL63(23KV北六三線) CB | FEEDER | D10/22/XL63/CB |  |  |  | CDC | 403 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL64 | 北六四線(XL64) |  | PHA | [17 empty] | 2-06-04 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL64_PHA | 23KV北六四線(XL64) 相間RY | FEEDER | D10/22/XL64/PHA |  |  |  | CDC | 404 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL64 | 北六四線(XL64) |  | GDA | [17 empty] | 2-06-05 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL64_GDA | 23KV北六四線(XL64) 接地RY | FEEDER | D10/22/XL64/GDA |  |  |  | CDC | 405 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL64 | 北六四線(XL64) 79RY |  | 79UL | [17 empty] | 2-33-07 |  | 2-5A | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL64_79UL | 23KV北六四線(XL64) 79RY U/L | FEEDER | D10/22/XL64/79UL |  |  |  | CDC | 406 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 22 | 22kV | XL64_LCO | 北六四線(XL64) LCO |  | TapPosMv | [17 empty] | 2-33-08 |  | 2-5B | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL64_LCO_TAP | 23KV北六四線(XL64) LCO TAP | FEEDER | D10/22/XL64/ADJ |  |  |  | CDC | 407 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D10 | 北勢DS | 22 | 22kV | XL64 | XL64(23KV北六四線) |  | CB | [17 empty] | 2-06-03 |  | 2-11 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL64_CB | XL64(23KV北六四線) CB | FEEDER | D10/22/XL64/CB |  |  |  | CDC | 408 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL65 | 北六五線(XL65) |  | PHA | [17 empty] | 2-06-07 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL65_PHA | 23KV北六五線(XL65) 相間RY | FEEDER | D10/22/XL65/PHA |  |  |  | CDC | 409 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL65 | 北六五線(XL65) |  | GDA | [17 empty] | 2-07-00 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL65_GDA | 23KV北六五線(XL65) 接地RY | FEEDER | D10/22/XL65/GDA |  |  |  | CDC | 410 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL65 | 北六五線(XL65) 79RY |  | 79UL | [17 empty] | 2-33-09 |  | 2-5C | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL65_79UL | 23KV北六五線(XL65) 79RY U/L | FEEDER | D10/22/XL65/79UL |  |  |  | CDC | 411 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 22 | 22kV | XL65_LCO | 北六五線(XL65) LCO |  | TapPosMv | [17 empty] | 2-33-10 |  | 2-5D | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL65_LCO_TAP | 23KV北六五線(XL65) LCO TAP | FEEDER | D10/22/XL65/ADJ |  |  |  | CDC | 412 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D10 | 北勢DS | 22 | 22kV | XL65 | XL65(23KV北六五線) |  | CB | [17 empty] | 2-06-06 |  | 2-12 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL65_CB | XL65(23KV北六五線) CB | FEEDER | D10/22/XL65/CB |  |  |  | CDC | 413 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL66 | 北六六線(XL66) |  | PHA | [17 empty] | 2-07-02 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL66_PHA | 23KV北六六線(XL66) 相間RY | FEEDER | D10/22/XL66/PHA |  |  |  | CDC | 414 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL66 | 北六六線(XL66) |  | GDA | [17 empty] | 2-07-03 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL66_GDA | 23KV北六六線(XL66) 接地RY | FEEDER | D10/22/XL66/GDA |  |  |  | CDC | 415 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL66 | 北六六線(XL66) 79RY |  | 79UL | [17 empty] | 2-33-11 |  | 2-5E | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL66_79UL | 23KV北六六線(XL66) 79RY U/L | FEEDER | D10/22/XL66/79UL |  |  |  | CDC | 416 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 22 | 22kV | XL66_LCO | 北六六線(XL66) LCO |  | TapPosMv | [17 empty] | 2-33-12 |  | 2-5F | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL66_LCO_TAP | 23KV北六六線(XL66) LCO TAP | FEEDER | D10/22/XL66/ADJ |  |  |  | CDC | 417 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D10 | 北勢DS | 22 | 22kV | XL66 | XL66(23KV北六六線) |  | CB | [17 empty] | 2-07-01 |  | 2-13 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL66_CB | XL66(23KV北六六線) CB | FEEDER | D10/22/XL66/CB |  |  |  | CDC | 418 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL67 | 北六七線(XL67) |  | PHA | [17 empty] | 2-07-05 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL67_PHA | 23KV北六七線(XL67) 相間RY | FEEDER | D10/22/XL67/PHA |  |  |  | CDC | 419 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL67 | 北六七線(XL67) |  | GDA | [17 empty] | 2-07-06 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL67_GDA | 23KV北六七線(XL67) 接地RY | FEEDER | D10/22/XL67/GDA |  |  |  | CDC | 420 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL67 | 北六七線(XL67) 79RY |  | 79UL | [17 empty] | 2-33-13 |  | 2-60 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL67_79UL | 23KV北六七線(XL67) 79RY U/L | FEEDER | D10/22/XL67/79UL |  |  |  | CDC | 421 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 22 | 22kV | XL67_LCO | 北六七線(XL67) LCO |  | TapPosMv | [17 empty] | 2-33-14 |  | 2-61 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL67_LCO_TAP | 23KV北六七線(XL67) LCO TAP | FEEDER | D10/22/XL67/ADJ |  |  |  | CDC | 422 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D10 | 北勢DS | 22 | 22kV | XL67 | XL67(23KV北六七線) |  | CB | [17 empty] | 2-07-04 |  | 2-14 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL67_CB | XL67(23KV北六七線) CB | FEEDER | D10/22/XL67/CB |  |  |  | CDC | 423 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL68 | 北六八線(XL68) |  | PHA | [17 empty] | 2-08-00 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL68_PHA | 23KV北六八線(XL68) 相間RY | FEEDER | D10/22/XL68/PHA |  |  |  | CDC | 424 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL68 | 北六八線(XL68) |  | GDA | [17 empty] | 2-08-01 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL68_GDA | 23KV北六八線(XL68) 接地RY | FEEDER | D10/22/XL68/GDA |  |  |  | CDC | 425 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL68 | 北六八線(XL68) 79RY |  | 79UL | [17 empty] | 2-33-15 |  | 2-62 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL68_79UL | 23KV北六八線(XL68) 79RY U/L | FEEDER | D10/22/XL68/79UL |  |  |  | CDC | 426 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 22 | 22kV | XL68_LCO | 北六八線(XL68) LCO |  | TapPosMv | [17 empty] | 2-34-00 |  | 2-63 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL68_LCO_TAP | 23KV北六八線(XL68) LCO TAP | FEEDER | D10/22/XL68/ADJ |  |  |  | CDC | 427 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D10 | 北勢DS | 22 | 22kV | XL68 | XL68(23KV北六八線) |  | CB | [17 empty] | 2-07-07 |  | 2-15 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL68_CB | XL68(23KV北六八線) CB | FEEDER | D10/22/XL68/CB |  |  |  | CDC | 428 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL71 | 北七一線(XL71) |  | PHA | [17 empty] | 2-09-04 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL71_PHA | 23KV北七一線(XL71) 相間RY | FEEDER | D10/22/XL71/PHA |  |  |  | CDC | 429 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL71 | 北七一線(XL71) |  | GDA | [17 empty] | 2-09-05 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL71_GDA | 23KV北七一線(XL71) 接地RY | FEEDER | D10/22/XL71/GDA |  |  |  | CDC | 430 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL71 | 北七一線(XL71) 79RY |  | 79UL | [17 empty] | 2-34-03 |  | 2-66 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL71_79UL | 23KV北七一線(XL71) 79RY U/L | FEEDER | D10/22/XL71/79UL |  |  |  | CDC | 431 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 22 | 22kV | XL71_LCO | 北七一線(XL71) LCO |  | TapPosMv | [17 empty] | 2-34-04 |  | 2-67 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL71_LCO_TAP | 23KV北七一線(XL71) LCO TAP | FEEDER | D10/22/XL71/ADJ |  |  |  | CDC | 432 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D10 | 北勢DS | 22 | 22kV | XL71 | XL71(23KV北七一線) |  | CB | [17 empty] | 2-09-03 |  | 2-19 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL71_CB | XL71(23KV北七一線) CB | FEEDER | D10/22/XL71/CB |  |  |  | CDC | 433 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL72 | 北七二線(XL72) |  | PHA | [17 empty] | 2-09-07 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL72_PHA | 23KV北七二線(XL72) 相間RY | FEEDER | D10/22/XL72/PHA |  |  |  | CDC | 434 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL72 | 北七二線(XL72) |  | GDA | [17 empty] | 2-0A-00 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL72_GDA | 23KV北七二線(XL72) 接地RY | FEEDER | D10/22/XL72/GDA |  |  |  | CDC | 435 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL72 | 北七二線(XL72) 79RY |  | 79UL | [17 empty] | 2-34-05 |  | 2-68 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL72_79UL | 23KV北七二線(XL72) 79RY U/L | FEEDER | D10/22/XL72/79UL |  |  |  | CDC | 436 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 22 | 22kV | XL72_LCO | 北七二線(XL72) LCO |  | TapPosMv | [17 empty] | 2-34-06 |  | 2-69 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL72_LCO_TAP | 23KV北七二線(XL72) LCO TAP | FEEDER | D10/22/XL72/ADJ |  |  |  | CDC | 437 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D10 | 北勢DS | 22 | 22kV | XL72 | XL72(23KV北七二線) |  | CB | [17 empty] | 2-09-06 |  | 2-1A | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL72_CB | XL72(23KV北七二線) CB | FEEDER | D10/22/XL72/CB |  |  |  | CDC | 438 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL73 | 北七三線(XL73) |  | PHA | [17 empty] | 2-0A-02 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL73_PHA | 23KV北七三線(XL73) 相間RY | FEEDER | D10/22/XL73/PHA |  |  |  | CDC | 439 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL73 | 北七三線(XL73) |  | GDA | [17 empty] | 2-0A-03 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL73_GDA | 23KV北七三線(XL73) 接地RY | FEEDER | D10/22/XL73/GDA |  |  |  | CDC | 440 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL73 | 北七三線(XL73) 79RY |  | 79UL | [17 empty] | 2-34-07 |  | 2-6A | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL73_79UL | 23KV北七三線(XL73) 79RY U/L | FEEDER | D10/22/XL73/79UL |  |  |  | CDC | 441 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 22 | 22kV | XL73_LCO | 北七三線(XL73) LCO |  | TapPosMv | [17 empty] | 2-34-08 |  | 2-6B | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL73_LCO_TAP | 23KV北七三線(XL73) LCO TAP | FEEDER | D10/22/XL73/ADJ |  |  |  | CDC | 442 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D10 | 北勢DS | 22 | 22kV | XL73 | XL73(23KV北七三線) |  | CB | [17 empty] | 2-0A-01 |  | 2-1B | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL73_CB | XL73(23KV北七三線) CB | FEEDER | D10/22/XL73/CB |  |  |  | CDC | 443 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL74 | 北七四線(XL74) |  | PHA | [17 empty] | 2-0A-05 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL74_PHA | 23KV北七四線(XL74) 相間RY | FEEDER | D10/22/XL74/PHA |  |  |  | CDC | 444 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL74 | 北七四線(XL74) |  | GDA | [17 empty] | 2-0A-06 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL74_GDA | 23KV北七四線(XL74) 接地RY | FEEDER | D10/22/XL74/GDA |  |  |  | CDC | 445 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL74 | 北七四線(XL74) 79RY |  | 79UL | [17 empty] | 2-34-09 |  | 2-6C | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL74_79UL | 23KV北七四線(XL74) 79RY U/L | FEEDER | D10/22/XL74/79UL |  |  |  | CDC | 446 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 22 | 22kV | XL74_LCO | 北七四線(XL74) LCO |  | TapPosMv | [17 empty] | 2-34-10 |  | 2-6D | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL74_LCO_TAP | 23KV北七四線(XL74) LCO TAP | FEEDER | D10/22/XL74/ADJ |  |  |  | CDC | 447 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D10 | 北勢DS | 22 | 22kV | XL74 | XL74(23KV北七四線) |  | CB | [17 empty] | 2-0A-04 |  | 2-1C | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL74_CB | XL74(23KV北七四線) CB | FEEDER | D10/22/XL74/CB |  |  |  | CDC | 448 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL75 | 北七五線(XL75) |  | PHA | [17 empty] | 2-0B-00 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL75_PHA | 23KV北七五線(XL75) 相間RY | FEEDER | D10/22/XL75/PHA |  |  |  | CDC | 449 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL75 | 北七五線(XL75) |  | GDA | [17 empty] | 2-0B-01 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL75_GDA | 23KV北七五線(XL75) 接地RY | FEEDER | D10/22/XL75/GDA |  |  |  | CDC | 450 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL75 | 北七五線(XL75) 79RY |  | 79UL | [17 empty] | 2-34-11 |  | 2-6E | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL75_79UL | 23KV北七五線(XL75) 79RY U/L | FEEDER | D10/22/XL75/79UL |  |  |  | CDC | 451 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 22 | 22kV | XL75_LCO | 北七五線(XL75) LCO |  | TapPosMv | [17 empty] | 2-34-12 |  | 2-6F | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL75_LCO_TAP | 23KV北七五線(XL75) LCO TAP | FEEDER | D10/22/XL75/ADJ |  |  |  | CDC | 452 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D10 | 北勢DS | 22 | 22kV | XL75 | XL75(23KV北七五線) |  | CB | [17 empty] | 2-0A-07 |  | 2-1D | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL75_CB | XL75(23KV北七五線) CB | FEEDER | D10/22/XL75/CB |  |  |  | CDC | 453 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL76 | 北七六線(XL76) |  | PHA | [17 empty] | 2-0B-03 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL76_PHA | 23KV北七六線(XL76) 相間RY | FEEDER | D10/22/XL76/PHA |  |  |  | CDC | 454 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL76 | 北七六線(XL76) |  | GDA | [17 empty] | 2-0B-04 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL76_GDA | 23KV北七六線(XL76) 接地RY | FEEDER | D10/22/XL76/GDA |  |  |  | CDC | 455 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL76 | 北七六線(XL76) 79RY |  | 79UL | [17 empty] | 2-34-13 |  | 2-70 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL76_79UL | 23KV北七六線(XL76) 79RY U/L | FEEDER | D10/22/XL76/79UL |  |  |  | CDC | 456 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 22 | 22kV | XL76_LCO | 北七六線(XL76) LCO |  | TapPosMv | [17 empty] | 2-34-14 |  | 2-71 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL76_LCO_TAP | 23KV北七六線(XL76) LCO TAP | FEEDER | D10/22/XL76/ADJ |  |  |  | CDC | 457 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D10 | 北勢DS | 22 | 22kV | XL76 | XL76(23KV北七六線) |  | CB | [17 empty] | 2-0B-02 |  | 2-1E | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL76_CB | XL76(23KV北七六線) CB | FEEDER | D10/22/XL76/CB |  |  |  | CDC | 458 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL77 | 北七七線(XL77) |  | PHA | [17 empty] | 2-0B-06 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL77_PHA | 23KV北七七線(XL77) 相間RY | FEEDER | D10/22/XL77/PHA |  |  |  | CDC | 459 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL77 | 北七七線(XL77) |  | GDA | [17 empty] | 2-0B-07 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL77_GDA | 23KV北七七線(XL77) 接地RY | FEEDER | D10/22/XL77/GDA |  |  |  | CDC | 460 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL77 | 北七七線(XL77) 79RY |  | 79UL | [17 empty] | 2-34-15 |  | 2-72 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL77_79UL | 23KV北七七線(XL77) 79RY U/L | FEEDER | D10/22/XL77/79UL |  |  |  | CDC | 461 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 22 | 22kV | XL77_LCO | 北七七線(XL77) LCO |  | TapPosMv | [17 empty] | 2-35-00 |  | 2-73 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL77_LCO_TAP | 23KV北七七線(XL77) LCO TAP | FEEDER | D10/22/XL77/ADJ |  |  |  | CDC | 462 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D10 | 北勢DS | 22 | 22kV | XL77 | XL77(23KV北七七線) |  | CB | [17 empty] | 2-0B-05 |  | 2-1F | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL77_CB | XL77(23KV北七七線) CB | FEEDER | D10/22/XL77/CB |  |  |  | CDC | 463 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | XL78 | 北七八線(XL78) |  | PHA | [17 empty] | 2-0C-01 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL78_PHA | 23KV北七八線(XL78) 相間RY | FEEDER | D10/22/XL78/PHA |  |  |  | CDC | 464 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL78 | 北七八線(XL78) |  | GDA | [17 empty] | 2-0C-02 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL78_GDA | 23KV北七八線(XL78) 接地RY | FEEDER | D10/22/XL78/GDA |  |  |  | CDC | 465 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | XL78 | 北七八線(XL78) 79RY |  | 79UL | [17 empty] | 2-35-01 |  | 2-74 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL78_79UL | 23KV北七八線(XL78) 79RY U/L | FEEDER | D10/22/XL78/79UL |  |  |  | CDC | 466 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 22 | 22kV | XL78_LCO | 北七八線(XL78) LCO |  | TapPosMv | [17 empty] | 2-35-02 |  | 2-75 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL78_LCO_TAP | 23KV北七八線(XL78) LCO TAP | FEEDER | D10/22/XL78/ADJ |  |  |  | CDC | 467 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D10 | 北勢DS | 22 | 22kV | XL78 | XL78(23KV北七八線) |  | CB | [17 empty] | 2-0C-00 |  | 2-20 | [5 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL78_CB | XL78(23KV北七八線) CB | FEEDER | D10/22/XL78/CB |  |  |  | CDC | 468 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | 100 | TIE(100) |  | CB | [17 empty] | 1-16-02 |  | 1-17 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.100_CB | 100(TIE) CB | TIE | D10/11/100/CB |  |  |  | CDC | 469 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 100 | TIE(100) |  | 51A | [17 empty] | 1-16-03 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.100_51A | 11KV TIE(100) 51RY | TIE | D10/11/100/PHA |  |  |  | CDC | 470 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 100 | TIE(100) |  | 51NA | [17 empty] | 1-16-04 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.100_51NA | 11KV TIE(100) 51N RY | TIE | D10/11/100/GDA |  |  |  | CDC | 471 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [17 empty] | 1-06-02 |  | 1-0B | [5 empty] | 161KV_N | [8 empty] | 北勢DS.1500_CB | 1500(TIE) CB | TIE | D10/161/1500/CB |  |  |  | CDC | 472 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | 1500 | TIE(1500) |  | 50A | [17 empty] | 1-06-03 | [7 empty] | 161KV_N | [8 empty] | 北勢DS.1500_50A | 161KV TIE(1500) 50RY | TIE | D10/161/1500/50A |  |  |  | CDC | 473 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [16 empty] | 1-3D-00 | 1-3D-01 | 1-6C | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1501_DS | 1501(TIE) DS | TIE | D10/161/1500/DS1 |  |  |  | CDC | 474 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D10 | 北勢DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [16 empty] | 1-3D-02 | 1-3D-03 | 1-6D | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1502_DS | 1502(TIE) DS | TIE | D10/161/1500/DS2 |  |  |  | CDC | 475 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D10 | 北勢DS | 0 |  | 300 | TIE(300) |  | CB | [17 empty] | 2-08-05 |  | 2-17 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.300_CB | 300(TIE) CB | TIE | D10/22/300/CB |  |  |  | CDC | 476 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 300 | TIE(300) |  | 51A | [17 empty] | 2-08-06 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.300_51A | 23KV TIE(300) 51RY | TIE | D10/22/300/PHA |  |  |  | CDC | 477 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 300 | TIE(300) |  | 51NA | [17 empty] | 2-08-07 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.300_51NA | 23KV TIE(300) 51N RY | TIE | D10/22/300/GDA |  |  |  | CDC | 478 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 390 | #1SSTR(390) |  | CB | [17 empty] | 1-16-05 |  | 1-18 | [5 empty] | 161KV_N | [8 empty] | 北勢DS.390_CB | 390(#1SSTR) CB | OTHER | D10/11/390/CB |  |  |  | CDC | 479 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | 1SSTR | #1SSTR |  | 51A | [17 empty] | 1-16-06 | [7 empty] | 161KV_N | [8 empty] | 北勢DS.#1SSTR_51A | #1SSTR 51RY | OTHER | D10/11/390/PHA |  |  |  | CDC | 480 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 1SSTR | #1SSTR |  | 51NA | [17 empty] | 1-16-07 | [7 empty] | 161KV_N | [8 empty] | 北勢DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | D10/11/390/GDA |  |  |  | CDC | 481 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 490 | #2SSTR(490) |  | CB | [17 empty] | 2-0C-06 |  | 2-22 | [5 empty] | 161KV_N | [8 empty] | 北勢DS.490_CB | 490(#2SSTR) CB | OTHER | D10/22/490/CB |  |  |  | CDC | 482 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | 2SSTR | #2SSTR |  | 51A | [17 empty] | 2-0C-07 | [7 empty] | 161KV_N | [8 empty] | 北勢DS.#2SSTR_51A | #2SSTR 51RY | OTHER | D10/22/490/PHA |  |  |  | CDC | 483 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 2SSTR | #2SSTR |  | 51NA | [17 empty] | 2-0D-00 | [7 empty] | 161KV_N | [8 empty] | 北勢DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | D10/22/490/GDA |  |  |  | CDC | 484 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB | [17 empty] | 1-07-00 |  | 1-0C | [5 empty] | 161KV_N | [8 empty] | 北勢DS.1750_CB | 1750(#1DTR) CB | MTR | D10/161/1750/CB |  |  |  | CDC | 485 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | 310 | #1DTR(310) |  | CB | [17 empty] | 1-07-06 |  | 1-10 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.310_CB | 310(#1DTR) CB | MTR | D10/11/310/CB |  |  |  | CDC | 486 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | 320 | #1DTR(320) |  | CB | [17 empty] | 1-08-02 |  | 1-19 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.320_CB | 320(#1DTR) CB | MTR | D10/11/320/CB |  |  |  | CDC | 487 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | 310 | #1DTR(310) |  | 51A | [17 empty] | 1-07-07 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.310_51A | #1DTR二次側(310) 51RY | MTR |  |  |  |  | CDC | 488 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 320 | #1DTR(320) |  | 51A | [17 empty] | 1-08-03 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.320_51A | #1DTR二次側(320) 51RY | MTR |  |  |  |  | CDC | 489 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 | [16 empty] | 1-3D-04 | 1-3D-05 | 1-6E | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1751_DS | 1751(#1DTR) DS | MTR | D10/161/1750/DS1 |  |  |  | CDC | 490 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D10 | 北勢DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 | [16 empty] | 1-3D-06 | 1-3D-07 | 1-6F | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1752_DS | 1752(#1DTR) DS | MTR | D10/161/1750/DS2 |  |  |  | CDC | 491 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D10 | 北勢DS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB | [17 empty] | 1-0A-04 |  | 1-0E | [5 empty] | 161KV_N | [8 empty] | 北勢DS.1770_CB | 1770(#3DTR) CB | MTR | D10/161/1770/CB |  |  |  | CDC | 492 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | 350 | #3DTR(350) |  | CB | [17 empty] | 1-0B-02 |  | 1-22 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.350_CB | 350(#3DTR) CB | MTR | D10/22/350/CB |  |  |  | CDC | 493 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | 350 | #3DTR(350) |  | 51A | [17 empty] | 1-0B-03 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.350_51A | #3DTR二次側(350) 51RY | MTR |  |  |  |  | CDC | 494 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 | [16 empty] | 1-3D-12 | 1-3D-13 | 1-72 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1771_DS | 1771(#3DTR) DS | MTR | D10/161/1770/DS1 |  |  |  | CDC | 495 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D10 | 北勢DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 | [16 empty] | 1-3D-14 | 1-3D-15 | 1-73 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1772_DS | 1772(#3DTR) DS | MTR | D10/161/1770/DS2 |  |  |  | CDC | 496 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D10 | 北勢DS | 161 | 161kV | 1780 | #4DTR(1780) |  | CB | [17 empty] | 1-0B-06 |  | 1-0F | [5 empty] | 161KV_N | [8 empty] | 北勢DS.1780_CB | 1780(#4DTR) CB | MTR | D10/161/1780/CB |  |  |  | CDC | 497 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 161 | 161kV | 1780 | #4DTR(1780) |  | DS1 | 1781 | [16 empty] | 1-3E-00 | 1-3E-01 | 1-74 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1781_DS | 1781(#4DTR) DS | MTR | D10/161/1780/DS1 |  |  |  | CDC | 498 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D10 | 北勢DS | 161 | 161kV | 1780 | #4DTR(1780) |  | DS2 | 1782 | [16 empty] | 1-3E-02 | 1-3E-03 | 1-75 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1782_DS | 1782(#4DTR) DS | MTR | D10/161/1780/DS2 |  |  |  | CDC | 499 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D10 | 北勢DS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-14-00 |  | 1-11 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.210_CB | 210(11KV #1SC) CB | SC | D10/11/210/CB |  |  |  | CDC | 500 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M | [17 empty] | 2-30-00 |  | 2-23 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.210_A/M | 11KV #1SC 乏控器 A/M | SC | D10/11/210/SC_A_M |  |  |  | CDC | 501 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D10 | 北勢DS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-14-01 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.210_SCA | 11KV #1SC 51,51N RY | SC | D10/11/210/SCA |  |  |  | CDC | 502 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-14-02 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | D10/11/210/UVA |  |  |  | CDC | 503 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | 210 | #1SC(210) |  | LBS | [17 empty] | 1-3E-04 | 1-3E-05 | 1-76 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.210_LBS | 210(11KV #1SC) LBS | SC | D10/11/210/LBS |  |  |  | CDC | 504 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D10 | 北勢DS | 11 | 11kV | 210_LBS | #1SC |  | SC_A_M | [17 empty] | 2-30-01 |  | 2-24 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.210_LBS_A/M | 11KV #1SC LBS 乏控器 A/M | SC | D10/11/210/1A5A_M |  |  |  | CDC | 505 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D10 | 北勢DS | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 1-17-00 |  | 1-1A | [5 empty] | ADCS_N | [8 empty] | 北勢DS.220_CB | 220(11KV #2SC) CB | SC | D10/11/220/CB |  |  |  | CDC | 506 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M | [17 empty] | 2-30-12 |  | 2-2F | [5 empty] | ADCS_N | [8 empty] | 北勢DS.220_A/M | 11KV #2SC 乏控器 A/M | SC | D10/11/220/SC_A_M |  |  |  | CDC | 507 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D10 | 北勢DS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 1-17-01 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.220_SCA | 11KV #2SC 51,51N RY | SC | D10/11/220/SCA |  |  |  | CDC | 508 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 1-17-02 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | D10/11/220/UVA |  |  |  | CDC | 509 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | 220 | #2SC(220) |  | LBS | [17 empty] | 1-3E-06 | 1-3E-07 | 1-77 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.220_LBS | 220(11KV #2SC) LBS | SC | D10/11/220/LBS |  |  |  | CDC | 510 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D10 | 北勢DS | 11 | 11kV | 220_LBS | #2SC |  | SC_A_M | [17 empty] | 2-30-13 |  | 2-30 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.220_LBS_A/M | 11KV #2SC LBS 乏控器 A/M | SC | D10/11/220/1A5A_M |  |  |  | CDC | 511 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D10 | 北勢DS | 22 | 22kV | 250 | #5SC(250) |  | CB | [17 empty] | 2-04-07 |  | 2-0D | [5 empty] | ADCS_N | [8 empty] | 北勢DS.250_CB | 250(23KV #5SC) CB | SC | D10/22/250/CB |  |  |  | CDC | 512 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | 250 | #5SC(250) |  | SC_A_M | [17 empty] | 2-33-00 |  | 2-53 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.250_A/M | 23KV #5SC 乏控器 A/M | SC | D10/22/250/SC_A_M |  |  |  | CDC | 513 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D10 | 北勢DS | 22 | 22kV | 250 | #5SC(250) |  | SCA | [17 empty] | 2-05-00 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.250_SCA | 23KV #5SC 51,51N RY | SC | D10/22/250/SCA |  |  |  | CDC | 514 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | 250 | #5SC(250) |  | UVA | [17 empty] | 2-05-01 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.250_UVA | 23KV #5SC 27RY(欠壓) | SC | D10/22/250/UVA |  |  |  | CDC | 515 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | 260 | #6SC(260) |  | CB | [17 empty] | 2-08-02 |  | 2-16 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.260_CB | 260(23KV #6SC) CB | SC | D10/22/260/CB |  |  |  | CDC | 516 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | 260 | #6SC(260) |  | SC_A_M | [17 empty] | 2-34-01 |  | 2-64 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.260_A/M | 23KV #6SC 乏控器 A/M | SC | D10/22/260/SC_A_M |  |  |  | CDC | 517 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D10 | 北勢DS | 22 | 22kV | 260 | #6SC(260) |  | SCA | [17 empty] | 2-08-03 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.260_SCA | 23KV #6SC 51,51N RY | SC | D10/22/260/SCA |  |  |  | CDC | 518 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | 260 | #6SC(260) |  | UVA | [17 empty] | 2-08-04 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.260_UVA | 23KV #6SC 27RY(欠壓) | SC | D10/22/260/UVA |  |  |  | CDC | 519 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | 270 | #7SC(270) |  | CB | [17 empty] | 2-09-00 |  | 2-18 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.270_CB | 270(23KV #7SC) CB | SC | D10/22/270/CB |  |  |  | CDC | 520 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | 270 | #7SC(270) |  | SC_A_M | [17 empty] | 2-34-02 |  | 2-65 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.270_A/M | 23KV #7SC 乏控器 A/M | SC | D10/22/270/SC_A_M |  |  |  | CDC | 521 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D10 | 北勢DS | 22 | 22kV | 270 | #7SC(270) |  | SCA | [17 empty] | 2-09-01 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.270_SCA | 23KV #7SC 51,51N RY | SC | D10/22/270/SCA |  |  |  | CDC | 522 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | 270 | #7SC(270) |  | UVA | [17 empty] | 2-09-02 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.270_UVA | 23KV #7SC 27RY(欠壓) | SC | D10/22/270/UVA |  |  |  | CDC | 523 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | 280 | #8SC(280) |  | CB | [17 empty] | 2-0C-03 |  | 2-21 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.280_CB | 280(23KV #8SC) CB | SC | D10/22/280/CB |  |  |  | CDC | 524 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 22 | 22kV | 280 | #8SC(280) |  | SC_A_M | [17 empty] | 2-35-03 |  | 2-76 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.280_A/M | 23KV #8SC 乏控器 A/M | SC | D10/22/280/SC_A_M |  |  |  | CDC | 525 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D10 | 北勢DS | 22 | 22kV | 280 | #8SC(280) |  | SCA | [17 empty] | 2-0C-04 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.280_SCA | 23KV #8SC 51,51N RY | SC | D10/22/280/SCA |  |  |  | CDC | 526 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | 280 | #8SC(280) |  | UVA | [17 empty] | 2-0C-05 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.280_UVA | 23KV #8SC 27RY(欠壓) | SC | D10/22/280/UVA |  |  |  | CDC | 527 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1611BUS | #1BUS |  | VUA | [17 empty] | 1-35-10 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | D10/161/1BUS/BUS_VUA |  |  |  | CDC | 528 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1611BUS | #1BUS |  | 87A | [17 empty] | 1-06-04 | [7 empty] | 161KV_N | [8 empty] | 北勢DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | D10/161/1BUS/87A |  |  |  | CDC | 529 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1611BUS | #1BUS |  | 87UL | [17 empty] | 1-31-06 |  | 1-7E | [5 empty] | ADCS_N | [8 empty] | 北勢DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | D10/161/1BUS/87UL |  |  |  | CDC | 530 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 161 | 161kV | 1612BUS | #2BUS |  | VUA | [17 empty] | 1-35-11 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | D10/161/2BUS/BUS_VUA |  |  |  | CDC | 531 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1612BUS | #2BUS |  | 87A | [17 empty] | 1-06-05 | [7 empty] | 161KV_N | [8 empty] | 北勢DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | D10/161/2BUS/87A |  |  |  | CDC | 532 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1612BUS | #2BUS |  | 87UL | [17 empty] | 1-31-07 |  | 1-7F | [5 empty] | ADCS_N | [8 empty] | 北勢DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | D10/161/2BUS/87UL |  |  |  | CDC | 533 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 22 | 22kV | 11_ | 11/ |  | CBA | [17 empty] | 1-36-02 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | D10/0/ComPoint/FDR_CBA |  |  |  | CDC | 534 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | 11_ | 11/ |  | CBF | [17 empty] | 1-36-03 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | D10/0/ComPoint/FDR_CBF |  |  |  | CDC | 535 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV |  |  |  | CBA | [17 empty] | 1-35-06 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.161KV_CBA | 161KV斷路器重故障 | OTHER | D10/161/ComPoint/CBA |  |  |  | CDC | 536 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV |  |  |  | CBF | [17 empty] | 1-35-07 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | D10/161/ComPoint/CBF |  |  |  | CDC | 537 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV |  |  |  | OSCA | [17 empty] | 1-06-07 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.161KV_OSCA | 161KV示波器啟動警報 | OTHER | D10/161/ComPoint/OSCA |  |  |  | CDC | 538 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | LINE | LINE |  | RCA | [17 empty] | 1-06-06 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | D10/161/ComPoint/RCA |  |  |  | CDC | 539 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV |  |  |  | COMT | [17 empty] | 1-35-14 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.161空壓機COMT | 161KV空壓機運轉超時警報 | OTHER | D10/0/ComPoint/COMT |  |  |  | CDC | 540 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 22 | 22kV | _SC | 23/ SC |  | 60A | [17 empty] | 1-35-15 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.23KV_SC_60A | 23/11KV SC 60A | OTHER | D10/0/ComPoint/FDR_60A |  |  |  | CDC | 541 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | FEEDER | FEEDER |  | RCA | [17 empty] | 1-36-04 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.FEEDER_RCA | 饋線復閉電驛動作 | FEEDER | D10/0/ComPoint/LOA |  |  |  | CDC | 542 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.RTU_S/L | RTU SUPY/LOCAL | OTHER | D10/0/RTU/RTU_R_L |  |  |  | CDC | 543 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D10 | 北勢DS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.TEST_CB | TEST CB | OTHER | D10/0/RTU/Test_CB |  |  |  | CDC | 544 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  |  |  |  | Fire1 | [17 empty] | 1-34-04 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | D10/0/StaDev/Fire1 |  |  |  | CDC | 545 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  |  |  |  | Fire2 | [17 empty] | 1-34-05 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.火災警報(2) | 火災警報(2) | OTHER | D10/0/StaDev/Fire2 |  |  |  | CDC | 546 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  |  |  |  | OPA | [17 empty] | 1-35-02 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | D10/0/ComPoint/OPA |  |  |  | CDC | 547 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  |  |  |  | SUBA | [17 empty] | 1-36-01 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.其他重故障 | 變電所內其他重故障 | OTHER | D10/0/StaDev/PSA |  |  |  | CDC | 548 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  |  |  |  | SUBF | [17 empty] | 1-36-00 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.其他輕故障 | 變電所內其他輕故障 | OTHER | D10/0/StaDev/PSF |  |  |  | CDC | 549 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  |  |  |  | ACB1 | [17 empty] | 1-35-03 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | D10/0/StaDev/ACB1 |  |  |  | CDC | 550 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
D10 | 北勢DS | 0 |  |  |  |  | ACB2 | [17 empty] | 1-35-04 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | D10/0/StaDev/ACB2 |  |  |  | CDC | 551 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
D10 | 北勢DS | 0 |  |  |  |  | ACBA | [17 empty] | 1-35-09 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.所內電源ACBA | 所內電源故障警報 | OTHER | D10/0/StaDev/ACBA |  |  |  | CDC | 552 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  |  |  |  | STUV | [17 empty] | 1-35-05 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | D10/0/StaDev/STUV |  |  |  | CDC | 553 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-35-12 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | D10/0/StaDev/CHG1 |  |  |  | CDC | 554 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  |  |  |  | DCA | [17 empty] | 1-35-08 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.直流電源DCA | 直流電源故障警報 | OTHER | D10/0/StaDev/DCA |  |  |  | CDC | 555 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  |  |  |  | DCE | [17 empty] | 1-35-13 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.直流電源DCE | 直流電源接地故障警報 | OTHER | D10/0/StaDev/DCE |  |  |  | CDC | 556 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  |  |  |  | OilLeak | [17 empty] | 1-36-05 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.洩油池水位警報 | 洩油池水位警報 | OTHER | D10/0/StaDev/OilLeak1 |  |  |  | CDC | 557 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-36-07 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | D10/0/StaDev/CHG2 |  |  |  | CDC | 558 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  |  |  |  | CommACF | [17 empty] | 1-36-08 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | D10/0/StaDev/CommACF |  |  |  | CDC | 559 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  |  |  |  | Burglar1 | [17 empty] | 1-34-12 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | D10/0/StaDev/Burglar1 |  |  |  | CDC | 560 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  |  |  |  | Burglar2 | [17 empty] | 1-34-13 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.無人化防盜(2) | 無人化防盜(2) | OTHER | D10/0/StaDev/Burglar2 |  |  |  | CDC | 561 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  |  |  |  | Door1 | [17 empty] | 1-34-09 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.無人化門禁(1) | 無人化門禁(1)建築物大門 | OTHER | D10/0/StaDev/Door1 |  |  |  | CDC | 562 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  |  |  |  | Door2 | [17 empty] | 1-34-10 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.無人化門禁(2) | 無人化門禁(2)控制室大門 | OTHER | D10/0/StaDev/Door2 |  |  |  | CDC | 563 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  |  |  |  | Door3 | [17 empty] | 1-34-11 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.無人化門禁(3) | 無人化門禁(3) | OTHER | D10/0/StaDev/Door3 |  |  |  | CDC | 564 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  |  |  |  | Lights1 | [17 empty] | 1-34-14 |  | 1-7A | [5 empty] | ADCS_N | [8 empty] | 北勢DS.開關場照明(A) | 開關場照明(A) | OTHER | D10/0/StaDev/Lights1 |  |  |  | CDC | 565 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D10 | 北勢DS | 0 |  |  |  |  | Lights2 | [17 empty] | 1-34-15 |  | 1-7B | [5 empty] | ADCS_N | [8 empty] | 北勢DS.開關場照明(B) | 開關場照明(B) | OTHER | D10/0/StaDev/Lights2 |  |  |  | CDC | 566 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D10 | 北勢DS | 0 |  | 310 | #1DTR(310) |  | GDA | [17 empty] | 1-08-01 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.310_GDA | 310開關箱IED RY GDA | OTHER | D10/11/310/GDA |  |  |  | CDC | 567 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 310 | #1DTR(310) |  | PHA2 | [17 empty] | 1-08-00 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.310_PHA2 | 310開關箱IED RY PHA | OTHER | D10/11/310/PHA |  |  |  | CDC | 568 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 320 | #1DTR(320) |  | GDA | [17 empty] | 1-08-05 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.320_GDA | 320開關箱IED RY GDA | OTHER | D10/11/320/GDA |  |  |  | CDC | 569 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 320 | #1DTR(320) |  | PHA2 | [17 empty] | 1-08-04 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.320_PHA2 | 320開關箱IED RY PHA | OTHER | D10/11/320/PHA |  |  |  | CDC | 570 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 350 | #3DTR(350) |  | GDA | [17 empty] | 1-0B-05 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.350_GDA | 350開關箱IED RY GDA | OTHER | D10/22/350/GDA |  |  |  | CDC | 571 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 350 | #3DTR(350) |  | PHA2 | [17 empty] | 1-0B-04 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.350_PHA2 | 350開關箱IED RY PHA | OTHER | D10/22/350/PHA |  |  |  | CDC | 572 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 0 |  |  |  |  | 空調機故障 | [17 empty] | 1-35-00 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.空調機故障 | 空調機故障或電源跳脫 | OTHER | D10/0/StaDev/AIRCON |  |  |  | CDC | 573 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | NORMAL/FAULT | NORMAL
D10 | 北勢DS | 0 |  |  |  |  | OilLeak2 | [17 empty] | 1-36-06 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.洩油池警報(2) | 洩油池水位警報(2) | OTHER | D10/0/StaDev/OilLeak2 |  |  |  | CDC | 574 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1530 | 旭硝子旭硝二紅(1530) |  | PHA | [17 empty] | 1-01-05 | [7 empty] | 161KV_N | [8 empty] | 北勢DS.1530_PHA | 旭硝子旭硝二紅(1530) 相間RY | LINE161 | D10/161/1530/PHA |  |  |  | CDC | 575 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1530 | 旭硝子旭硝二紅(1530) |  | GDA | [17 empty] | 1-01-06 | [7 empty] | 161KV_N | [8 empty] | 北勢DS.1530_GDA | 旭硝子旭硝二紅(1530) 接地RY | LINE161 | D10/161/1530/GDA |  |  |  | CDC | 576 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1530 | 旭硝子旭硝二紅(1530) |  | CB | [17 empty] | 1-01-02 |  | 1-03 | [5 empty] | 161KV_N | [8 empty] | 北勢DS.1530_CB | 1530(旭硝子旭硝二紅) CB | LINE161 | D10/161/1530/CB |  |  |  | CDC | 577 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 161 | 161kV | 1530 | 旭硝子旭硝二紅(1530) |  | 79UL | [17 empty] | 1-30-07 |  | 1-29 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1530_79UL | 旭硝子旭硝二紅(1530) 79RY U/L | LINE161 | D10/161/1530/79UL |  |  |  | CDC | 578 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 161 | 161kV | 1530 | 旭硝子旭硝二紅(1530) |  | DS1 | 1531 | [16 empty] | 1-39-00 | 1-39-01 | 1-4C | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1531_DS | 1531(旭硝子旭硝二紅) DS | LINE161 | D10/161/1530/DS1 |  |  |  | CDC | 579 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D10 | 北勢DS | 161 | 161kV | 1530 | 旭硝子旭硝二紅(1530) |  | DS2 | 1532 | [16 empty] | 1-39-02 | 1-39-03 | 1-4D | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1532_DS | 1532(旭硝子旭硝二紅) DS | LINE161 | D10/161/1530/DS2 |  |  |  | CDC | 580 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D10 | 北勢DS | 161 | 161kV | 1530 | 旭硝子旭硝二紅(1530) |  | DS3 | 1533 | [16 empty] | 1-39-04 | 1-39-05 | 1-4E | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1533_DS | 1533(旭硝子旭硝二紅) DS | LINE161 | D10/161/1530/DS3 |  |  |  | CDC | 581 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D10 | 北勢DS | 161 | 161kV | 1530 | 旭硝子旭硝二紅(1530) |  | E3 | 1533E | [16 empty] | 1-39-06 | 1-39-07 | 1-4F | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1533E_ES | 1533E(旭硝子旭硝二紅) ES | LINE161 | D10/161/1530/ES3 |  |  |  | CDC | 582 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D10 | 北勢DS | 0 |  |  |  |  | 水位警報(1) | [17 empty] | 2-35-04 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.水位警報(1) | 地下室水位警報(1) | OTHER | D10/0/StaDev/Water1 |  |  |  | CDC | 583 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  |  |  |  | 水位警報(2) | [17 empty] | 2-35-05 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.水位警報(2) | 地下室水位警報(2) | OTHER | D10/0/StaDev/Water2 |  |  |  | CDC | 584 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 1500TIE | 1500 |  | 50SA | [17 empty] | 2-35-06 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | D10/161/1500/50SA |  |  |  | CDC | 585 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | TEST/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 1DTR | #1DTR |  | 51A | [17 empty] | 1-07-04 | [7 empty] | 161KV_N | [8 empty] | 北勢DS.#1DTR_51A | #1DTR 51RY | MTR | D10/161/1750/PHA |  |  |  | CDC | 586 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 1DTR | #1DTR |  | 51NA | [17 empty] | 1-07-05 | [7 empty] | 161KV_N | [8 empty] | 北勢DS.#1DTR_51NA | #1DTR 51N RY | MTR | D10/161/1750/GDA |  |  |  | CDC | 587 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 1DTR | #1DTR |  | 51ZA | [17 empty] | 1-07-03 | [7 empty] | 161KV_N | [8 empty] | 北勢DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | D10//1DTR/51ZA |  |  |  | CDC | 588 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 1DTR | #1DTR |  | 87A | [17 empty] | 1-07-01 | [7 empty] | 161KV_N | [8 empty] | 北勢DS.#1DTR_87A | #1DTR 87RY | MTR | D10//1DTR/87A |  |  |  | CDC | 589 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 1DTR | #1DTR |  | 96PA | [17 empty] | 1-07-02 | [7 empty] | 161KV_N | [8 empty] | 北勢DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | D10//1DTR/96PA |  |  |  | CDC | 590 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 1DTR | #1DTR |  | 96D | [17 empty] | 1-36-12 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.#1DTR_96D | #1DTR 96D RY | MTR | D10//1DTR/96D |  |  |  | CDC | 591 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 1DTR | #1DTR |  | 96P | [17 empty] | 1-36-13 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.#1DTR_96P | #1DTR 96P RY | MTR | D10//1DTR/96P |  |  |  | CDC | 592 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 1DTR | #1DTR |  | 63Q | [17 empty] | 1-36-14 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.#1DTR_63Q | #1DTR 63Q RY | MTR | D10//1DTR/63Q |  |  |  | CDC | 593 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 1DTR | #1DTR |  | 96B1 | [17 empty] | 1-36-15 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | D10//1DTR/96B1 |  |  |  | CDC | 594 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 1DTR | #1DTR |  | 96B2 | [17 empty] | 1-37-00 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | D10//1DTR/96B2 |  |  |  | CDC | 595 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 1DTR | #1DTR |  | TRA | [17 empty] | 1-31-11 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.#1DTR_TRA | #1DTR 重故障 | MTR | D10//1DTR(A)/TRA |  |  |  | CDC | 596 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 1DTR | #1DTR |  | TRF | [17 empty] | 1-31-12 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.#1DTR_TRF | #1DTR 輕故障 | MTR | D10//1DTR(A)/TRF |  |  |  | CDC | 597 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 1DTR(A) | #1DTR(A) |  | SupLocal | [17 empty] | 1-31-09 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | D10//1DTR(A)/SupLocal |  |  |  | CDC | 598 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D10 | 北勢DS | 0 |  | 1DTR(A) | #1DTR(A) |  | A_M | [17 empty] | 1-31-10 |  | 1-38 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | D10//1DTR(A)/Tap Chan |  |  |  | CDC | 599 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D10 | 北勢DS | 0 |  | 1DTR(B) | #1DTR(B) |  | SupLocal | [17 empty] | 1-31-13 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | D10//1DTR(B)/SupLocal |  |  |  | CDC | 600 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D10 | 北勢DS | 0 |  | 1DTR(B) | #1DTR(B) |  | A_M | [17 empty] | 1-31-14 |  | 1-3A | [5 empty] | ADCS_N | [8 empty] | 北勢DS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | D10//1DTR(B)/Tap Chan |  |  |  | CDC | 601 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D10 | 北勢DS | 0 |  | 3DTR | #3DTR |  | 51A | [17 empty] | 1-0B-00 | [7 empty] | 161KV_N | [8 empty] | 北勢DS.#3DTR_51A | #3DTR 51RY | MTR | D10//3DTR/PHA |  |  |  | CDC | 602 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 3DTR | #3DTR |  | 51NA | [17 empty] | 1-0B-01 | [7 empty] | 161KV_N | [8 empty] | 北勢DS.#3DTR_51NA | #3DTR 51N RY | MTR | D10//3DTR/GDA |  |  |  | CDC | 603 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 3DTR | #3DTR |  | 51ZA | [17 empty] | 1-0A-07 | [7 empty] | 161KV_N | [8 empty] | 北勢DS.#3DTR_51ZA | #3DTR 51Z RY | MTR | D10//3DTR/51ZA |  |  |  | CDC | 604 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 3DTR | #3DTR |  | 87A | [17 empty] | 1-0A-05 | [7 empty] | 161KV_N | [8 empty] | 北勢DS.#3DTR_87A | #3DTR 87RY | MTR | D10//3DTR/87A |  |  |  | CDC | 605 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 3DTR | #3DTR |  | 96PA | [17 empty] | 1-0A-06 | [7 empty] | 161KV_N | [8 empty] | 北勢DS.#3DTR_96PA | #3DTR 機械保護動作 | MTR | D10//3DTR/96PA |  |  |  | CDC | 606 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 3DTR | #3DTR |  | 96D | [17 empty] | 1-37-06 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.#3DTR_96D | #3DTR 96D RY | MTR | D10//3DTR/96D |  |  |  | CDC | 607 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 3DTR | #3DTR |  | 96P | [17 empty] | 1-37-07 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.#3DTR_96P | #3DTR 96P RY | MTR | D10//3DTR/96P |  |  |  | CDC | 608 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 3DTR | #3DTR |  | 63Q | [17 empty] | 1-37-08 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.#3DTR_63Q | #3DTR 63Q RY | MTR | D10//3DTR/63Q |  |  |  | CDC | 609 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 3DTR | #3DTR |  | 96B1 | [17 empty] | 1-37-09 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.#3DTR_96B1 | #3DTR 96B1 RY | MTR | D10//3DTR/96B1 |  |  |  | CDC | 610 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 3DTR | #3DTR |  | 96B2 | [17 empty] | 1-37-10 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.#3DTR_96B2 | #3DTR 96B2 RY | MTR | D10//3DTR/96B2 |  |  |  | CDC | 611 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 3DTR | #3DTR |  | TRA | [17 empty] | 1-32-09 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.#3DTR_TRA | #3DTR 重故障 | MTR | D10//3DTR/TRA |  |  |  | CDC | 612 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 3DTR | #3DTR |  | TRF | [17 empty] | 1-32-10 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.#3DTR_TRF | #3DTR 輕故障 | MTR | D10//3DTR/TRF |  |  |  | CDC | 613 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 3DTR | #3DTR |  | SupLocal | [17 empty] | 1-32-07 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.#3DTR_S/L | #3DTR OLTC S/L | MTR | D10//3DTR/SupLocal |  |  |  | CDC | 614 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D10 | 北勢DS | 0 |  | 3DTR | #3DTR |  | A_M | [17 empty] | 1-32-08 |  | 1-40 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.#3DTR_A/M | #3DTR OLTC A/M | MTR | D10//3DTR/Tap Chan |  |  |  | CDC | 615 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D10 | 北勢DS | 0 |  | 370 | #4DTR(370) |  | CB | [17 empty] | 1-0C-04 |  | 1-23 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.370_CB | 370(#4DTR) CB | MTR | D10/22/370/CB |  |  |  | CDC | 616 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | 4DTR | #4DTR |  | 51A | [17 empty] | 1-0C-02 | [7 empty] | 161KV_N | [8 empty] | 北勢DS.#4DTR_51A | #4DTR 51RY | MTR | D10//4DTR/PHA |  |  |  | CDC | 617 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 4DTR | #4DTR |  | 51NA | [17 empty] | 1-0C-03 | [7 empty] | 161KV_N | [8 empty] | 北勢DS.#4DTR_51NA | #4DTR 51N RY | MTR | D10//4DTR/GDA |  |  |  | CDC | 618 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 4DTR | #4DTR |  | 51ZA | [17 empty] | 1-0C-01 | [7 empty] | 161KV_N | [8 empty] | 北勢DS.#4DTR_51ZA | #4DTR 51Z RY | MTR | D10//4DTR/51ZA |  |  |  | CDC | 619 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 4DTR | #4DTR |  | 87A | [17 empty] | 1-0B-07 | [7 empty] | 161KV_N | [8 empty] | 北勢DS.#4DTR_87A | #4DTR 87RY | MTR | D10//4DTR/87A |  |  |  | CDC | 620 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 370 | #4DTR(370) |  | 51A | [17 empty] | 1-0C-05 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.370_51A | #4DTR二次側(370) 51RY | MTR |  |  |  |  | CDC | 621 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 4DTR | #4DTR |  | 96PA | [17 empty] | 1-0C-00 | [7 empty] | 161KV_N | [8 empty] | 北勢DS.#4DTR_96PA | #4DTR 機械保護動作 | MTR | D10//4DTR/96PA |  |  |  | CDC | 622 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 4DTR | #4DTR |  | 96D | [17 empty] | 1-37-11 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.#4DTR_96D | #4DTR 96D RY | MTR | D10//4DTR/96D |  |  |  | CDC | 623 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 4DTR | #4DTR |  | 96P | [17 empty] | 1-37-12 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.#4DTR_96P | #4DTR 96P RY | MTR | D10//4DTR/96P |  |  |  | CDC | 624 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 4DTR | #4DTR |  | 63Q | [17 empty] | 1-37-13 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.#4DTR_63Q | #4DTR 63Q RY | MTR | D10//4DTR/63Q |  |  |  | CDC | 625 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 4DTR | #4DTR |  | 96B1 | [17 empty] | 1-37-14 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.#4DTR_96B1 | #4DTR 96B1 RY | MTR | D10//4DTR/96B1 |  |  |  | CDC | 626 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 4DTR | #4DTR |  | 96B2 | [17 empty] | 1-37-15 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.#4DTR_96B2 | #4DTR 96B2 RY | MTR | D10//4DTR/96B2 |  |  |  | CDC | 627 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 4DTR | #4DTR |  | TRA | [17 empty] | 1-32-14 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.#4DTR_TRA | #4DTR 重故障 | MTR | D10//4DTR/TRA |  |  |  | CDC | 628 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 4DTR | #4DTR |  | TRF | [17 empty] | 1-32-15 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.#4DTR_TRF | #4DTR 輕故障 | MTR | D10//4DTR/TRF |  |  |  | CDC | 629 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 4DTR | #4DTR |  | SupLocal | [17 empty] | 1-32-12 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.#4DTR_S/L | #4DTR OLTC S/L | MTR | D10//4DTR/SupLocal |  |  |  | CDC | 630 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D10 | 北勢DS | 0 |  | 4DTR | #4DTR |  | A_M | [17 empty] | 1-32-13 |  | 1-42 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.#4DTR_A/M | #4DTR OLTC A/M | MTR | D10//4DTR/Tap Chan |  |  |  | CDC | 631 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D10 | 北勢DS | 0 |  | 370 | #4DTR(370) |  | GDA | [17 empty] | 1-0C-07 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.370_GDA | 370開關箱IED RY GDA | OTHER | D10/22/370/GDA |  |  |  | CDC | 632 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 370 | #4DTR(370) |  | PHA2 | [17 empty] | 1-0C-06 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.370_PHA2 | 370開關箱IED RY PHA | OTHER | D10/22/370/PHA |  |  |  | CDC | 633 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 0 |  |  |  |  | 通信機房溫度 | [17 empty] | 1-36-11 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.通信機房溫度 | 通信機房溫度警報 | OTHER | D10/0/StaDev/R_Temp |  |  |  | CDC | 634 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV |  |  |  | OSCF | [17 empty] | 2-35-07 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | D10/161/ComPoint/OSCF |  |  |  | CDC | 635 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  |  |  |  | PMA | [17 empty] | 2-35-08 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.PMA | 電力量測表計故障 | OTHER | D10/0/StaDev/PMA |  |  |  | CDC | 636 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 1530 | 旭硝子旭硝二紅(1530) |  | RYFA | [17 empty] | 1-33-04 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.1530_RYFA | 旭硝子旭硝二紅(1530)數位RY故障 | OTHER | D10/161/1530/RYFA |  |  |  | CDC | 637 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 81RY | 81RY |  | A/S(1) | [17 empty] | 2-0D-01 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.81RY_A/S(1) | XL25低頻電驛動作/復歸 | OTHER | D10/11/XL25/81A |  |  |  | CDC | 638 | GENERICDIPoint | DS038_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
D10 | 北勢DS | 0 |  |  |  |  | 81RF(1) | [17 empty] | 2-35-09 | [7 empty] | DDCS1_1 | [8 empty] | 北勢DS.81RF(1) | XL25低頻電驛故障 | OTHER | D10/11/XL25/RYFA |  |  |  | CDC | 639 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1510 | 雲林北勢線(1510) |  | 87A | [17 empty] | 1-00-01 | [7 empty] | 161KV_N | [8 empty] | 北勢DS.1510_87A | 雲林北勢線(1510) 87RY | LINE161 | D10/161/1510/87A |  |  |  | CDC | 640 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1510 | 雲林北勢線(1510) |  | 87UL | [17 empty] | 1-30-02 |  | 1-24 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1510_87UL | 雲林北勢線(1510) 87RY U/L | LINE161 | D10/161/1510/87UL |  |  |  | CDC | 641 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 0 |  | 1510 | 雲林北勢線(1510) |  | 87CFA | [17 empty] | 1-33-01 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.1510_87CFA | 雲林北勢線(1510) 87RY通訊故障 | OTHER | D10/161/1510/87CFA |  |  |  | CDC | 642 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 1510 | 雲林北勢線(1510) |  | RYFA | [17 empty] | 1-33-00 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.1510_RYFA | 雲林北勢線(1510) 數位電驛故障 | OTHER | D10/161/1510/RYFA |  |  |  | CDC | 643 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | BVS | BVS |  | RY | [17 empty] | 2-35-10 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.BVS_RY | BVS GRZ100 RY U/L | OTHER | D10/0/ComPoint/GRZ100 |  |  |  | CDC | 644 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | LOCK/USE | USE
D10 | 北勢DS | 161 | 161kV | 1540 | 旭硝子旭硝二白(1540) |  | PHA | [17 empty] | 1-02-02 | [7 empty] | 161KV_N | [8 empty] | 北勢DS.1540_PHA | 旭硝子旭硝二白(1540) 相間RY | LINE161 | D10/161/1540/PHA |  |  |  | CDC | 645 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1540 | 旭硝子旭硝二白(1540) |  | GDA | [17 empty] | 1-02-03 | [7 empty] | 161KV_N | [8 empty] | 北勢DS.1540_GDA | 旭硝子旭硝二白(1540) 接地RY | LINE161 | D10/161/1540/GDA |  |  |  | CDC | 646 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1540 | 旭硝子旭硝二白(1540) |  | 87A1 | [17 empty] | 1-02-00 | [7 empty] | 161KV_N | [8 empty] | 北勢DS.1540_87A1 | 旭硝子旭硝二白(1540) #1 87RY | LINE161 | D10/161/1540/87A1 |  |  |  | CDC | 647 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1540 | 旭硝子旭硝二白(1540) |  | 87A2 | [17 empty] | 1-02-01 | [7 empty] | 161KV_N | [8 empty] | 北勢DS.1540_87A2 | 旭硝子旭硝二白(1540) #2 87RY | LINE161 | D10/161/1540/87A2 |  |  |  | CDC | 648 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | 1540 | 旭硝子旭硝二白(1540)#187RY |  | 1_87UL1 | [17 empty] | 1-30-08 |  | 1-2A | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1540_87UL1 | 旭硝子旭硝二白(1540)#187RY U/L | LINE161 | D10/161/1540/1_87UL1 |  |  |  | CDC | 649 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 161 | 161kV | 1540 | 旭硝子旭硝二白(1540)#287RY |  | 1_87UL2 | [17 empty] | 2-35-12 |  | 1-7D | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1540_87UL2 | 旭硝子旭硝二白(1540)#287RY U/L | LINE161 | D10/161/1540/1_87UL2 |  |  |  | CDC | 650 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 161 | 161kV | 1540 | 旭硝子旭硝二白(1540) |  | CB | [17 empty] | 1-01-07 |  | 1-04 | [5 empty] | 161KV_N | [8 empty] | 北勢DS.1540_CB | 1540(旭硝子旭硝二白) CB | LINE161 | D10/161/1540/CB |  |  |  | CDC | 651 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 161 | 161kV | 1540 | 旭硝子旭硝二白(1540) |  | 79UL | [17 empty] | 1-30-09 |  | 1-2B | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1540_79UL | 旭硝子旭硝二白(1540) 79RY U/L | LINE161 | D10/161/1540/79UL |  |  |  | CDC | 652 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 161 | 161kV | 1540 | 旭硝子旭硝二白(1540) |  | DS1 | 1541 | [16 empty] | 1-39-08 | 1-39-09 | 1-50 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1541_DS | 1541(旭硝子旭硝二白) DS | LINE161 | D10/161/1540/DS1 |  |  |  | CDC | 653 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D10 | 北勢DS | 161 | 161kV | 1540 | 旭硝子旭硝二白(1540) |  | DS2 | 1542 | [16 empty] | 1-39-10 | 1-39-11 | 1-51 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1542_DS | 1542(旭硝子旭硝二白) DS | LINE161 | D10/161/1540/DS2 |  |  |  | CDC | 654 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D10 | 北勢DS | 161 | 161kV | 1540 | 旭硝子旭硝二白(1540) |  | DS3 | 1543 | [16 empty] | 1-39-12 | 1-39-13 | 1-52 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1543_DS | 1543(旭硝子旭硝二白) DS | LINE161 | D10/161/1540/DS3 |  |  |  | CDC | 655 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D10 | 北勢DS | 161 | 161kV | 1540 | 旭硝子旭硝二白(1540) |  | E3 | 1543E | [16 empty] | 1-39-14 | 1-39-15 | 1-53 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1543E_ES | 1543E(旭硝子旭硝二白) ES | LINE161 | D10/161/1540/ES3 |  |  |  | CDC | 656 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D10 | 北勢DS | 0 |  | 1540 | 旭硝子旭硝二白(1540) |  | 87CFA | [17 empty] | 1-33-07 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.1540_87CFA | 旭硝子旭硝二白(1540)87通訊故障 | OTHER | D10/161/1540/87CFA |  |  |  | CDC | 657 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 1540 | 旭硝子旭硝二白(1540) |  | RYFA | [17 empty] | 1-33-06 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.1540_RYFA | 旭硝子旭硝二白(1540)數位RY故障 | OTHER | D10/161/1540/RYFA |  |  |  | CDC | 658 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 1530 | 旭硝子旭硝二紅(1530) |  | 87A1 | [17 empty] | 1-01-03 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.1530_87A1 | 旭硝子旭硝二紅(1530) 87A1 | OTHER | D10/161/1530/87A1 |  |  |  | CDC | 659 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 1530 | 旭硝子旭硝二紅(1530) |  | 87A2 | [17 empty] | 1-01-04 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.1530_87A2 | 旭硝子旭硝二紅(1530) 87A2 | OTHER | D10/161/1530/87A2 |  |  |  | CDC | 660 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 1530 | 旭硝子旭硝二紅(1530) |  | 87CFA | [17 empty] | 1-33-05 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.1530_87CFA | 旭硝子旭硝二紅(1530)87通訊故障 | OTHER | D10/161/1530/87CFA |  |  |  | CDC | 661 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 1530 | 旭硝子旭硝二紅(1530) |  | 1_87UL1 | [17 empty] | 1-30-06 |  | 1-28 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1530_87UL1 | 旭硝子旭硝二紅(1530) 87RY1 U/L | OTHER | D10/161/1530/1_87UL1 |  |  |  | CDC | 662 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 0 |  | 1530 | 旭硝子旭硝二紅(1530) |  | 1_87UL2 | [17 empty] | 2-35-11 |  | 1-7C | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1530_87UL2 | 旭硝子旭硝二紅(1530) 87RY2 U/L | OTHER | D10/161/1530/1_87UL2 |  |  |  | CDC | 663 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 0 |  |  |  |  | 火災警報(5) | [17 empty] | 1-34-08 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.火災警報(5) | 火災警報(5) | OTHER | D10/0/StaDev/Fire3 |  |  |  | CDC | 664 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  |  |  |  | GEN | [17 empty] | 2-35-13 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.GEN | 緊急發電機運轉 | OTHER | D10/0/ComPoint/1A5Other |  |  |  | CDC | 665 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D10 | 北勢DS | 0 |  | 1520 | 斗南北勢線(1520) |  | 87A1 | [17 empty] | 1-00-06 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.1520_87A1 | 斗南北勢線(1520)第一套87RY | OTHER | D10/161/1520/87A1 |  |  |  | CDC | 666 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 1520 | 斗南北勢線(1520) |  | 87A2 | [17 empty] | 1-00-07 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.1520_87A2 | 斗南北勢線(1520)第二套87RY | OTHER | D10/161/1520/87A2 |  |  |  | CDC | 667 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 1520 | 斗南北勢線(1520) |  | 87CFA | [17 empty] | 1-33-03 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.1520_87CFA | 斗南北勢線(1520))87RY通訊故障 | OTHER | D10/161/1520/87CFA |  |  |  | CDC | 668 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 1520 | 斗南北勢線(1520) |  | 1_87UL1 | [17 empty] | 1-30-04 |  | 1-26 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1520_87UL1 | 斗南北勢線(1520)#1 87RY U/L | OTHER | D10/161/1520/1_87UL1 |  |  |  | CDC | 669 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 0 |  | 1520 | 斗南北勢線(1520) |  | 1_87UL2 | [17 empty] | 1-30-10 |  | 1-2C | [5 empty] | ADCS_N | [8 empty] | 北勢DS.1520_87UL2 | 斗南北勢線(1520)#2 87RY U/L | OTHER | D10/161/1520/1_87UL2 |  |  |  | CDC | 670 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 0 |  | 1520 | 斗南北勢線(1520) |  | RYFA | [17 empty] | 1-33-02 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.1520_RYFA | 斗南北勢線(1520)數位電驛故障 | OTHER | D10/161/1520/RYFA |  |  |  | CDC | 671 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | _BUS | BUS |  | 87CTFA | [17 empty] | 1-34-07 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.161KV_BUS_CTFA | 161KV BUS 87RY CT回路故障 | OTHER | D10/161/ComPoint/12B_CTFA |  |  |  | CDC | 672 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 161 | 161kV | _BUS | BUS |  | RYFA | [17 empty] | 1-34-06 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | D10/161/ComPoint/BUS_RYFA |  |  |  | CDC | 673 | GENERICDIPoint | DS038_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 3OLTC | #3DTR |  | TAP連動 | [17 empty] | 1-19-07 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.#3OLTC_TAP連動 | #3DTR OLTC TAP連動,請確認處理 | OTHER | D10//3DTR/OLTC_A |  |  |  | CDC | 674 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 1DTR | #1DTR |  | 51Z_UL | [17 empty] | 2-36-00 |  | 2-7A | [5 empty] | ADCS_N | [8 empty] | 北勢DS.#1DTR_51ZUL | #1DTR 51ZRY U/L | OTHER |  |  |  |  | CDC | 675 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 0 |  | 1DTR | #1DTR |  | DTR_86A | [17 empty] | 1-0D-02 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.#1DTR_86A | #1DTR 86(50/50N/51Z/87/96)RY | OTHER | D10//1DTR/DTR_86A |  |  |  | CDC | 676 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 1DTR | #1DTR |  | 1_87UL1 | [17 empty] | 2-35-14 |  | 2-78 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.#1DTR_87UL1 | #1DTR #1 87RY U/L | OTHER | D10//1DTR/1_87UL1 |  |  |  | CDC | 677 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 0 |  | 1DTR | #1DTR |  | 1_87UL2 | [17 empty] | 2-35-15 |  | 2-79 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.#1DTR_87UL2 | #1DTR #2 87RY U/L | OTHER | D10//1DTR/1_87UL2 |  |  |  | CDC | 678 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 0 |  | 1DTR | #1DTR |  | RYFA | [17 empty] | 2-36-01 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.#1DTR_RYFA | #1DTR數位電驛故障 | OTHER | D10//1DTR/RYFA |  |  |  | CDC | 679 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 3DTR | #3DTR |  | 51Z_UL | [17 empty] | 2-36-04 |  | 2-7D | [5 empty] | ADCS_N | [8 empty] | 北勢DS.#3DTR_51ZUL | #3DTR 51ZRY U/L | OTHER | D10//3DTR/51Z_UL |  |  |  | CDC | 680 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 0 |  | 3DTR | #3DTR |  | 1_87UL1 | [17 empty] | 2-36-02 |  | 2-7B | [5 empty] | ADCS_N | [8 empty] | 北勢DS.#3DTR_87UL1 | #3DTR #1 87RY U/L | OTHER | D10//3DTR/1_87UL1 |  |  |  | CDC | 681 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 0 |  | 3DTR | #3DTR |  | 1_87UL2 | [17 empty] | 2-36-03 |  | 2-7C | [5 empty] | ADCS_N | [8 empty] | 北勢DS.#3DTR_87UL2 | #3DTR #2 87RY U/L | OTHER | D10//3DTR/1_87UL2 |  |  |  | CDC | 682 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 0 |  | 3DTR | #3DTR |  | RYFA | [17 empty] | 2-36-05 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.#3DTR_RYFA | #3DTR數位電驛故障 | OTHER | D10//3DTR/RYFA |  |  |  | CDC | 683 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 3DTR | #3DTR |  | DTR_86A | [17 empty] | 1-0D-03 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.#3DTR_86A | #3DTR 86(50/50N/51Z/87/96)RY | OTHER | D10//3DTR/DTR_86A |  |  |  | CDC | 684 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 4DTR | #4DTR |  | 51Z_UL | [17 empty] | 2-36-08 |  | 3-02 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.#4DTR_51ZUL | #4DTR 51ZRY U/L | OTHER | D10//4DTR/51Z_UL |  |  |  | CDC | 685 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 0 |  | 4DTR | #4DTR |  | DTR_86A | [17 empty] | 1-0D-04 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.#4DTR_86A | #4DTR 86(50/50N/51Z/87/96)RY | OTHER | D10//4DTR/DTR_86A |  |  |  | CDC | 686 | GENERICDIPoint | DS038_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | 4DTR | #4DTR |  | 1_87UL1 | [17 empty] | 2-36-06 |  | 3-00 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.#4DTR_87UL1 | #4DTR #1 87RY U/L | OTHER | D10//4DTR/1_87UL1 |  |  |  | CDC | 687 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 0 |  | 4DTR | #4DTR |  | 1_87UL2 | [17 empty] | 2-36-07 |  | 3-01 | [5 empty] | ADCS_N | [8 empty] | 北勢DS.#4DTR_87UL2 | #4DTR #2 87RY U/L | OTHER | D10//4DTR/1_87UL2 |  |  |  | CDC | 688 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D10 | 北勢DS | 0 |  | 4DTR | #4DTR |  | RYFA | [17 empty] | 2-36-09 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.#4DTR_RYFA | #4DTR數位電驛故障 | OTHER | D10//4DTR/RYFA |  |  |  | CDC | 689 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D10 | 北勢DS | 0 |  | OLTC | OLTC |  | OLTCA | [17 empty] | 2-36-10 | [7 empty] | ADCS_N | [8 empty] | 北勢DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | D10/0/ComPoint/OLTC_A |  |  |  | CDC | 690 | GENERICDIPoint | DS038_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D10 | 北勢DS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 北勢DS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 691 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 11 | 11kV | 220_SC | #2SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 北勢DS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 692 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 22 | 22kV | 250_SC | #5SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 北勢DS.250_SC_CAP | 23KV#5SC 容量 | SC | [5 empty] | 693 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 22 | 22kV | 260_SC | #6SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 北勢DS.260_SC_CAP | 23KV#6SC 容量 | SC | [5 empty] | 694 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 22 | 22kV | 270_SC | #7SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 北勢DS.270_SC_CAP | 23KV#7SC 容量 | SC | [5 empty] | 695 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 22 | 22kV | 280_SC | #8SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 北勢DS.280_SC_CAP | 23KV#8SC 容量 | SC | [5 empty] | 696 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D10 | 北勢DS | 0 |  | TRD | 北勢DS |  | 101 | [25 empty] | TRAIN_AD | [8 empty] | 北勢DS.TRD_101 | 北勢DS NT #1ADTR 11KV_Hi_Limit | [6 empty] | 697 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D10 | 北勢DS | 0 |  | TRD | 北勢DS |  | 102 | [25 empty] | TRAIN_AD | [8 empty] | 北勢DS.TRD_102 | 北勢DS NT #1ADTR 11KV_Lo_Limit | [6 empty] | 698 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D10 | 北勢DS | 0 |  | TRD | 北勢DS |  | 103 | [25 empty] | TRAIN_AD | [8 empty] | 北勢DS.TRD_103 | 北勢DS NT #1BDTR 11KV_Hi_Limit | [6 empty] | 699 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D10 | 北勢DS | 0 |  | TRD | 北勢DS |  | 104 | [25 empty] | TRAIN_AD | [8 empty] | 北勢DS.TRD_104 | 北勢DS NT #1BDTR 11KV_Lo_Limit | [6 empty] | 700 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D10 | 北勢DS | 0 |  | TRD | 北勢DS |  | 105 | [25 empty] | TRAIN_AD | [8 empty] | 北勢DS.TRD_105 | 北勢DS NT #3DTR 23KV_Hi_Limit | [6 empty] | 701 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D10 | 北勢DS | 0 |  | TRD | 北勢DS |  | 106 | [25 empty] | TRAIN_AD | [8 empty] | 北勢DS.TRD_106 | 北勢DS NT #3DTR 23KV_Lo_Limit | [6 empty] | 702 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D10 | 北勢DS | 0 |  | TRD | 北勢DS |  | 107 | [25 empty] | TRAIN_AD | [8 empty] | 北勢DS.TRD_107 | 北勢DS NT #4DTR 23KV_Hi_Limit | [6 empty] | 703 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D10 | 北勢DS | 0 |  | TRD | 北勢DS |  | 108 | [25 empty] | TRAIN_AD | [8 empty] | 北勢DS.TRD_108 | 北勢DS NT #4DTR 23KV_Lo_Limit | [6 empty] | 704 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D10 | 北勢DS | 161 | 161kV | 1510 | 雲林北勢線(1510) |  | LE0 | 1510LE | [24 empty] | ADCS_N | [8 empty] | 北勢DS.1510LE | 1510LE (非取樣點) | LINE161 | D10/161/1510/LE0 |  |  |  |  | 705 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 161 | 161kV | 1510 | 雲林北勢線(1510) |  | BE0 | 1510BE | [24 empty] | ADCS_N | [8 empty] | 北勢DS.1510BE | 1510BE (非取樣點) | LINE161 | D10/161/1510/BE0 |  |  |  |  | 706 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 161 | 161kV | 1520 | 斗南北勢線(1520) |  | LE0 | 1520LE | [24 empty] | ADCS_N | [8 empty] | 北勢DS.1520LE | 1520LE (非取樣點) | LINE161 | D10/161/1520/LE0 |  |  |  |  | 707 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 161 | 161kV | 1520 | 斗南北勢線(1520) |  | BE0 | 1520BE | [24 empty] | ADCS_N | [8 empty] | 北勢DS.1520BE | 1520BE (非取樣點) | LINE161 | D10/161/1520/BE0 |  |  |  |  | 708 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | XL21 | XL21_DS |  | DS1 | XL21_DS | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL21_DS | XL21_DS (非取樣點) | FEEDER | D10/11/XL21/DS |  |  |  |  | 709 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | XL21 | XL21_ES |  | LE0 | XL21_ES | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL21_ES | XL21_ES (非取樣點) | FEEDER | D10/11/XL21/ES |  |  |  |  | 710 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | XL22 | XL22_DS |  | DS1 | XL22_DS | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL22_DS | XL22_DS (非取樣點) | FEEDER | D10/11/XL22/DS |  |  |  |  | 711 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | XL22 | XL22_ES |  | LE0 | XL22_ES | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL22_ES | XL22_ES (非取樣點) | FEEDER | D10/11/XL22/ES |  |  |  |  | 712 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | XL23 | XL23_DS |  | DS1 | XL23_DS | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL23_DS | XL23_DS (非取樣點) | FEEDER | D10/11/XL23/DS |  |  |  |  | 713 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | XL23 | XL23_ES |  | LE0 | XL23_ES | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL23_ES | XL23_ES (非取樣點) | FEEDER | D10/11/XL23/ES |  |  |  |  | 714 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | XL24 | XL24_DS |  | DS1 | XL24_DS | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL24_DS | XL24_DS (非取樣點) | FEEDER | D10/11/XL24/DS |  |  |  |  | 715 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | XL24 | XL24_ES |  | LE0 | XL24_ES | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL24_ES | XL24_ES (非取樣點) | FEEDER | D10/11/XL24/ES |  |  |  |  | 716 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | XL25 | XL25_DS |  | DS1 | XL25_DS | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL25_DS | XL25_DS (非取樣點) | FEEDER | D10/11/XL25/DS |  |  |  |  | 717 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | XL25 | XL25_ES |  | LE0 | XL25_ES | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL25_ES | XL25_ES (非取樣點) | FEEDER | D10/11/XL25/ES |  |  |  |  | 718 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | XL26 | XL26_DS |  | DS1 | XL26_DS | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL26_DS | XL26_DS (非取樣點) | FEEDER | D10/11/XL26/DS |  |  |  |  | 719 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | XL26 | XL26_ES |  | LE0 | XL26_ES | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL26_ES | XL26_ES (非取樣點) | FEEDER | D10/11/XL26/ES |  |  |  |  | 720 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | XL27 | XL27_DS |  | DS1 | XL27_DS | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL27_DS | XL27_DS (非取樣點) | FEEDER | D10/11/XL27/DS |  |  |  |  | 721 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | XL27 | XL27_ES |  | LE0 | XL27_ES | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL27_ES | XL27_ES (非取樣點) | FEEDER | D10/11/XL27/ES |  |  |  |  | 722 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | XL28 | XL28_DS |  | DS1 | XL28_DS | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL28_DS | XL28_DS (非取樣點) | FEEDER | D10/11/XL28/DS |  |  |  |  | 723 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | XL28 | XL28_ES |  | LE0 | XL28_ES | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL28_ES | XL28_ES (非取樣點) | FEEDER | D10/11/XL28/ES |  |  |  |  | 724 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | XL29 | XL29_DS |  | DS1 | XL29_DS | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL29_DS | XL29_DS (非取樣點) | FEEDER | D10/11/XL29/DS |  |  |  |  | 725 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | XL29 | XL29_ES |  | LE0 | XL29_ES | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL29_ES | XL29_ES (非取樣點) | FEEDER | D10/11/XL29/ES |  |  |  |  | 726 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | XL30 | XL30_DS |  | DS1 | XL30_DS | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL30_DS | XL30_DS (非取樣點) | FEEDER | D10/11/XL30/DS |  |  |  |  | 727 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | XL30 | XL30_ES |  | LE0 | XL30_ES | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL30_ES | XL30_ES (非取樣點) | FEEDER | D10/11/XL30/ES |  |  |  |  | 728 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | XL61 | XL61_DS |  | DS1 | XL61_DS | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL61_DS | XL61_DS (非取樣點) | FEEDER | D10/22/XL61/DS |  |  |  |  | 729 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | XL61 | XL61_ES |  | LE0 | XL61_ES | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL61_ES | XL61_ES (非取樣點) | FEEDER | D10/22/XL61/ES |  |  |  |  | 730 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | XL62 | XL62_DS |  | DS1 | XL62_DS | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL62_DS | XL62_DS (非取樣點) | FEEDER | D10/22/XL62/DS |  |  |  |  | 731 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | XL62 | XL62_ES |  | LE0 | XL62_ES | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL62_ES | XL62_ES (非取樣點) | FEEDER | D10/22/XL62/ES |  |  |  |  | 732 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | XL63 | XL63_DS |  | DS1 | XL63_DS | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL63_DS | XL63_DS (非取樣點) | FEEDER | D10/22/XL63/DS |  |  |  |  | 733 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | XL63 | XL63_ES |  | LE0 | XL63_ES | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL63_ES | XL63_ES (非取樣點) | FEEDER | D10/22/XL63/ES |  |  |  |  | 734 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | XL64 | XL64_DS |  | DS1 | XL64_DS | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL64_DS | XL64_DS (非取樣點) | FEEDER | D10/22/XL64/DS |  |  |  |  | 735 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | XL64 | XL64_ES |  | LE0 | XL64_ES | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL64_ES | XL64_ES (非取樣點) | FEEDER | D10/22/XL64/ES |  |  |  |  | 736 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | XL65 | XL65_DS |  | DS1 | XL65_DS | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL65_DS | XL65_DS (非取樣點) | FEEDER | D10/22/XL65/DS |  |  |  |  | 737 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | XL65 | XL65_ES |  | LE0 | XL65_ES | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL65_ES | XL65_ES (非取樣點) | FEEDER | D10/22/XL65/ES |  |  |  |  | 738 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | XL66 | XL66_DS |  | DS1 | XL66_DS | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL66_DS | XL66_DS (非取樣點) | FEEDER | D10/22/XL66/DS |  |  |  |  | 739 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | XL66 | XL66_ES |  | LE0 | XL66_ES | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL66_ES | XL66_ES (非取樣點) | FEEDER | D10/22/XL66/ES |  |  |  |  | 740 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | XL67 | XL67_DS |  | DS1 | XL67_DS | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL67_DS | XL67_DS (非取樣點) | FEEDER | D10/22/XL67/DS |  |  |  |  | 741 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | XL67 | XL67_ES |  | LE0 | XL67_ES | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL67_ES | XL67_ES (非取樣點) | FEEDER | D10/22/XL67/ES |  |  |  |  | 742 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | XL68 | XL68_DS |  | DS1 | XL68_DS | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL68_DS | XL68_DS (非取樣點) | FEEDER | D10/22/XL68/DS |  |  |  |  | 743 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | XL68 | XL68_ES |  | LE0 | XL68_ES | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL68_ES | XL68_ES (非取樣點) | FEEDER | D10/22/XL68/ES |  |  |  |  | 744 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | XL71 | XL71_DS |  | DS1 | XL71_DS | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL71_DS | XL71_DS (非取樣點) | FEEDER | D10/22/XL71/DS |  |  |  |  | 745 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | XL71 | XL71_ES |  | LE0 | XL71_ES | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL71_ES | XL71_ES (非取樣點) | FEEDER | D10/22/XL71/ES |  |  |  |  | 746 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | XL72 | XL72_DS |  | DS1 | XL72_DS | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL72_DS | XL72_DS (非取樣點) | FEEDER | D10/22/XL72/DS |  |  |  |  | 747 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | XL72 | XL72_ES |  | LE0 | XL72_ES | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL72_ES | XL72_ES (非取樣點) | FEEDER | D10/22/XL72/ES |  |  |  |  | 748 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | XL73 | XL73_DS |  | DS1 | XL73_DS | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL73_DS | XL73_DS (非取樣點) | FEEDER | D10/22/XL73/DS |  |  |  |  | 749 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | XL73 | XL73_ES |  | LE0 | XL73_ES | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL73_ES | XL73_ES (非取樣點) | FEEDER | D10/22/XL73/ES |  |  |  |  | 750 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | XL74 | XL74_DS |  | DS1 | XL74_DS | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL74_DS | XL74_DS (非取樣點) | FEEDER | D10/22/XL74/DS |  |  |  |  | 751 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | XL74 | XL74_ES |  | LE0 | XL74_ES | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL74_ES | XL74_ES (非取樣點) | FEEDER | D10/22/XL74/ES |  |  |  |  | 752 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | XL75 | XL75_DS |  | DS1 | XL75_DS | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL75_DS | XL75_DS (非取樣點) | FEEDER | D10/22/XL75/DS |  |  |  |  | 753 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | XL75 | XL75_ES |  | LE0 | XL75_ES | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL75_ES | XL75_ES (非取樣點) | FEEDER | D10/22/XL75/ES |  |  |  |  | 754 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | XL76 | XL76_DS |  | DS1 | XL76_DS | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL76_DS | XL76_DS (非取樣點) | FEEDER | D10/22/XL76/DS |  |  |  |  | 755 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | XL76 | XL76_ES |  | LE0 | XL76_ES | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL76_ES | XL76_ES (非取樣點) | FEEDER | D10/22/XL76/ES |  |  |  |  | 756 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | XL77 | XL77_DS |  | DS1 | XL77_DS | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL77_DS | XL77_DS (非取樣點) | FEEDER | D10/22/XL77/DS |  |  |  |  | 757 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | XL77 | XL77_ES |  | LE0 | XL77_ES | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL77_ES | XL77_ES (非取樣點) | FEEDER | D10/22/XL77/ES |  |  |  |  | 758 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | XL78 | XL78_DS |  | DS1 | XL78_DS | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL78_DS | XL78_DS (非取樣點) | FEEDER | D10/22/XL78/DS |  |  |  |  | 759 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | XL78 | XL78_ES |  | LE0 | XL78_ES | [24 empty] | DDCS1_1 | [8 empty] | 北勢DS.XL78_ES | XL78_ES (非取樣點) | FEEDER | D10/22/XL78/ES |  |  |  |  | 760 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 101 | 101 |  | 101 | 101 | [24 empty] | ADCS_N | [8 empty] | 北勢DS.101 | 101 (非取樣點) | TIE | D10/11/100/D1 |  |  |  |  | 761 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [24 empty] | ADCS_N | [8 empty] | 北勢DS.1501E | 1501E (非取樣點) | TIE | D10/161/1500/E1 |  |  |  |  | 762 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [24 empty] | ADCS_N | [8 empty] | 北勢DS.1502E | 1502E (非取樣點) | TIE | D10/161/1500/E2 |  |  |  |  | 763 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 301 | 301 |  | 301 | 301 | [24 empty] | ADCS_N | [8 empty] | 北勢DS.301 | 301 (非取樣點) | TIE | D10/22/300/D1 |  |  |  |  | 764 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | 302 | 302 |  | 302 | 302 | [24 empty] | ADCS_N | [8 empty] | 北勢DS.302 | 302 (非取樣點) | TIE | D10/22/300/D2 |  |  |  |  | 765 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | 391 | 391 |  | 391 | 391 | [24 empty] | ADCS_N | [8 empty] | 北勢DS.391 | 391 (非取樣點) | OTHER | D10/11/390/D1 |  |  |  |  | 766 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 491 | 491 |  | 491 | 491 | [24 empty] | ADCS_N | [8 empty] | 北勢DS.491 | 491 (非取樣點) | OTHER | D10/22/490/D1 |  |  |  |  | 767 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | 1750TE | [24 empty] | ADCS_N | [8 empty] | 北勢DS.1750TE | 1750TE (非取樣點) | MTR | D10/161/1750/TE0 |  |  |  |  | 768 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | 1750BE | [24 empty] | ADCS_N | [8 empty] | 北勢DS.1750BE | 1750BE (非取樣點) | MTR | D10/161/1750/BE0 |  |  |  |  | 769 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 311 | 311 |  | 311 | 311 | [24 empty] | ADCS_N | [8 empty] | 北勢DS.311 | 311 (非取樣點) | MTR | D10/11/310/D1 |  |  |  |  | 770 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | 310 | #1DTR(310) |  | E1 | 311E | [24 empty] | ADCS_N | [8 empty] | 北勢DS.311E | 311E (非取樣點) | MTR | D10/11/310/E1 |  |  |  |  | 771 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 321 | 321 |  | 321 | 321 | [24 empty] | ADCS_N | [8 empty] | 北勢DS.321 | 321 (非取樣點) | MTR | D10/11/320/D1 |  |  |  |  | 772 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | 320 | #1DTR(320) |  | E1 | 321E | [24 empty] | ADCS_N | [8 empty] | 北勢DS.321E | 321E (非取樣點) | MTR | D10/11/320/E1 |  |  |  |  | 773 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | 1770TE | [24 empty] | ADCS_N | [8 empty] | 北勢DS.1770TE | 1770TE (非取樣點) | MTR | D10/161/1770/TE0 |  |  |  |  | 774 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | 1770BE | [24 empty] | ADCS_N | [8 empty] | 北勢DS.1770BE | 1770BE (非取樣點) | MTR | D10/161/1770/BE0 |  |  |  |  | 775 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 351 | 351 |  | 351 | 351 | [24 empty] | ADCS_N | [8 empty] | 北勢DS.351 | 351 (非取樣點) | MTR | D10/22/350/D1 |  |  |  |  | 776 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | 350 | #3DTR(350) |  | E1 | 351E | [24 empty] | ADCS_N | [8 empty] | 北勢DS.351E | 351E (非取樣點) | MTR | D10/22/350/E1 |  |  |  |  | 777 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 161 | 161kV | 1780 | #4DTR(1780) |  | TE0 | 1780TE | [24 empty] | ADCS_N | [8 empty] | 北勢DS.1780TE | 1780TE (非取樣點) | MTR | D10/161/1780/TE0 |  |  |  |  | 778 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 161 | 161kV | 1780 | #4DTR(1780) |  | BE0 | 1780BE | [24 empty] | ADCS_N | [8 empty] | 北勢DS.1780BE | 1780BE (非取樣點) | MTR | D10/161/1780/BE0 |  |  |  |  | 779 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 211E | 211E |  | 211E | 211E | [24 empty] | ADCS_N | [8 empty] | 北勢DS.211E | 211E (非取樣點) | SC | D10/11/210/E1 |  |  |  |  | 780 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 210 | #1SC(210) |  | SC10 | 210SC1 | [24 empty] | ADCS_N | [8 empty] | 北勢DS.210SC1_ES | 210SC1_ES (非取樣點) | SC | [5 empty] | 781 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 211 | 211 |  | 211 | 211 | [24 empty] | ADCS_N | [8 empty] | 北勢DS.211 | 211 (非取樣點) | SC | D10/11/210/D1 |  |  |  |  | 782 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | 210 | #1SC(210) |  | SC20 | 210SC2 | [24 empty] | ADCS_N | [8 empty] | 北勢DS.210SC2_ES | 210SC2_ES (非取樣點) | SC | [5 empty] | 783 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 221E | 221E |  | 221E | 221E | [24 empty] | ADCS_N | [8 empty] | 北勢DS.221E | 221E (非取樣點) | SC | D10/11/220/E1 |  |  |  |  | 784 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 220 | #2SC(220) |  | SC10 | 220SC1 | [24 empty] | ADCS_N | [8 empty] | 北勢DS.220SC1_ES | 220SC1_ES (非取樣點) | SC | [5 empty] | 785 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 221 | 221 |  | 221 | 221 | [24 empty] | ADCS_N | [8 empty] | 北勢DS.221 | 221 (非取樣點) | SC | D10/11/220/D1 |  |  |  |  | 786 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | 220 | #2SC(220) |  | SC20 | 220SC2 | [24 empty] | ADCS_N | [8 empty] | 北勢DS.220SC2_ES | 220SC2_ES (非取樣點) | SC | [5 empty] | 787 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 251E | 251E |  | 251E | 251E | [24 empty] | ADCS_N | [8 empty] | 北勢DS.251E | 251E (非取樣點) | SC | D10/22/250/E1 |  |  |  |  | 788 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 250 | #5SC(250) |  | SC0 | 250SC | [24 empty] | ADCS_N | [8 empty] | 北勢DS.250SC_ES | 250SC_ES (非取樣點) | SC | [5 empty] | 789 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 251 | 251 |  | 251 | 251 | [24 empty] | ADCS_N | [8 empty] | 北勢DS.251 | 251 (非取樣點) | SC | D10/22/250/D1 |  |  |  |  | 790 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | 261E | 261E |  | 261E | 261E | [24 empty] | ADCS_N | [8 empty] | 北勢DS.261E | 261E (非取樣點) | SC | D10/22/260/E1 |  |  |  |  | 791 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 260 | #6SC(260) |  | SC0 | 260SC | [24 empty] | ADCS_N | [8 empty] | 北勢DS.260SC_ES | 260SC_ES (非取樣點) | SC | [5 empty] | 792 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 261 | 261 |  | 261 | 261 | [24 empty] | ADCS_N | [8 empty] | 北勢DS.261 | 261 (非取樣點) | SC | D10/22/260/D1 |  |  |  |  | 793 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | 271E | 271E |  | 271E | 271E | [24 empty] | ADCS_N | [8 empty] | 北勢DS.271E | 271E (非取樣點) | SC | D10/22/270/E1 |  |  |  |  | 794 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 270 | #7SC(270) |  | SC0 | 270SC | [24 empty] | ADCS_N | [8 empty] | 北勢DS.270SC_ES | 270SC_ES (非取樣點) | SC | [5 empty] | 795 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 271 | 271 |  | 271 | 271 | [24 empty] | ADCS_N | [8 empty] | 北勢DS.271 | 271 (非取樣點) | SC | D10/22/270/D1 |  |  |  |  | 796 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | 281E | 281E |  | 281E | 281E | [24 empty] | ADCS_N | [8 empty] | 北勢DS.281E | 281E (非取樣點) | SC | D10/22/280/E1 |  |  |  |  | 797 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 280 | #8SC(280) |  | SC0 | 280SC | [24 empty] | ADCS_N | [8 empty] | 北勢DS.280SC_ES | 280SC_ES (非取樣點) | SC | [5 empty] | 798 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 281 | 281 |  | 281 | 281 | [24 empty] | ADCS_N | [8 empty] | 北勢DS.281 | 281 (非取樣點) | SC | D10/22/280/D1 |  |  |  |  | 799 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | 15B1E | 15B1E |  | BE1 | 15B1E | [24 empty] | ADCS_N | [8 empty] | 北勢DS.15B1E | 15B1E (非取樣點) | BUS | D10/161/161B1E/BE1 |  |  |  |  | 800 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 15B2E | 15B2E |  | BE2 | 15B2E | [24 empty] | ADCS_N | [8 empty] | 北勢DS.15B2E | 15B2E (非取樣點) | BUS | D10/161/161B2E/BE2 |  |  |  |  | 801 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | ADCS_N | [8 empty] | 北勢DS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 802 | NotelDIPoint | [38 empty] | START/STOP | STOP
D10 | 北勢DS | 0 |  |  |  |  | 101E | 101E | [24 empty] | ADCS_N | [8 empty] | 北勢DS.101E | 101E(非取樣點) | OTHER | D10/11/100/E1 |  |  |  |  | 803 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  |  |  |  | 301E | 301E | [24 empty] | ADCS_N | [8 empty] | 北勢DS.301E | 301E(非取樣點) | OTHER | D10/22/300/E1 |  |  |  |  | 804 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  |  |  |  | 302E | 302E | [24 empty] | ADCS_N | [8 empty] | 北勢DS.302E | 302E(非取樣點) | OTHER | D10/22/300/E2 |  |  |  |  | 805 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 391E | 391E |  | 391E | 391E | [24 empty] | ADCS_N | [8 empty] | 北勢DS.391E | 391E (非取樣點) | OTHER | D10/11/390/E1 |  |  |  |  | 806 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 491E | 491E |  | 491E | 491E | [24 empty] | ADCS_N | [8 empty] | 北勢DS.491E | 491E (非取樣點) | OTHER | D10/22/490/E1 |  |  |  |  | 807 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 161 | 161kV | 1530 | 旭硝子旭硝二紅(1530) |  | LE0 | 1530LE | [24 empty] | ADCS_N | [8 empty] | 北勢DS.1530LE | 1530LE (非取樣點) | LINE161 | D10/161/1530/LE0 |  |  |  |  | 808 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 161 | 161kV | 1530 | 旭硝子旭硝二紅(1530) |  | BE0 | 1530BE | [24 empty] | ADCS_N | [8 empty] | 北勢DS.1530BE | 1530BE (非取樣點) | LINE161 | D10/161/1530/BE0 |  |  |  |  | 809 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 371 | 371 |  | 371 | 371 | [24 empty] | ADCS_N | [8 empty] | 北勢DS.371 | 371 (非取樣點) | MTR | D10/22/370/D1 |  |  |  |  | 810 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | 370 | #4DTR(370) |  | E1 | 371E | [24 empty] | ADCS_N | [8 empty] | 北勢DS.371E | 371E (非取樣點) | MTR | D10/22/370/E1 |  |  |  |  | 811 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 161 | 161kV | 1540 | 旭硝子旭硝二白(1540) |  | LE0 | 1540LE | [24 empty] | ADCS_N | [8 empty] | 北勢DS.1540LE | 1540LE (非取樣點) | LINE161 | D10/161/1540/LE0 |  |  |  |  | 812 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 161 | 161kV | 1540 | 旭硝子旭硝二白(1540) |  | BE0 | 1540BE | [24 empty] | ADCS_N | [8 empty] | 北勢DS.1540BE | 1540BE (非取樣點) | LINE161 | D10/161/1540/BE0 |  |  |  |  | 813 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 1A | #1A |  | BE | #1A_BE | [24 empty] | ADCS_N | [8 empty] | 北勢DS.#1A_BE | #1A BE(非取樣點) | OTHER | [5 empty] | 814 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 1B | #1B |  | BE | #1B_BE | [24 empty] | ADCS_N | [8 empty] | 北勢DS.#1B_BE | #1B BE(非取樣點) | OTHER | [5 empty] | 815 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 3 | #3 |  | BE | #3_BE | [24 empty] | ADCS_N | [8 empty] | 北勢DS.#3_BE | #3 BE(非取樣點) | OTHER | [5 empty] | 816 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 4 | #4 |  | BE | #4_BE | [24 empty] | ADCS_N | [8 empty] | 北勢DS.#4_BE | #4 BE(非取樣點) | OTHER | [5 empty] | 817 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 1ABUS | 1ABUS |  | PTD | 1ABUS_PTD | [24 empty] | ADCS_N | [8 empty] | 北勢DS.1ABUS_PTD | #1ABUS_PTD(非取樣點) | OTHER | [5 empty] | 818 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | 1ABUS | 1ABUS |  | PTE | 1ABUS_PTE | [24 empty] | ADCS_N | [8 empty] | 北勢DS.1ABUS_PTE | #1ABUS_PTE(非取樣點) | OTHER | [5 empty] | 819 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 1BBUS | 1BBUS |  | PTD | 1BBUS_PTD | [24 empty] | ADCS_N | [8 empty] | 北勢DS.1BBUS_PTD | #1BBUS_PTD(非取樣點) | OTHER | [5 empty] | 820 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | 1BBUS | 1BBUS |  | PTE | 1BBUS_PTE | [24 empty] | ADCS_N | [8 empty] | 北勢DS.1BBUS_PTE | #1BBUS_PTE(非取樣點) | OTHER | [5 empty] | 821 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 3BUS | 3BUS |  | PTD | 3BUS_PTD | [24 empty] | ADCS_N | [8 empty] | 北勢DS.3BUS_PTD | #3BUS_PTD(非取樣點) | OTHER | [5 empty] | 822 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | 3BUS | 3BUS |  | PTE | 3BUS_PTE | [24 empty] | ADCS_N | [8 empty] | 北勢DS.3BUS_PTE | #3BUS_PTE(非取樣點) | OTHER | [5 empty] | 823 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D10 | 北勢DS | 0 |  | 4BUS | 4BUS |  | PTD | 4BUS_PTD | [24 empty] | ADCS_N | [8 empty] | 北勢DS.4BUS_PTD | #4BUS_PTD(非取樣點) | OTHER | [5 empty] | 824 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D10 | 北勢DS | 0 |  | 4BUS | 4BUS |  | PTE | 4BUS_PTE | [24 empty] | ADCS_N | [8 empty] | 北勢DS.4BUS_PTE | #4BUS_PTE(非取樣點) | OTHER | [5 empty] | 825 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo