## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D11 | 榴中DS | 161 | 161kV | 1510 | 榴中～斗工一路(1510) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D11_A1 | [8 empty] | 榴中DS.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 2 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 161 | 161kV | 1510 | 榴中～斗工一路(1510) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D11_A1 | [8 empty] | 榴中DS.1510BE | 1510BE (非取樣點) | LINE161 | [5 empty] | 3 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 161 | 161kV | 1520 | 榴中～斗工二路(1520) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D11_A1 | [8 empty] | 榴中DS.1520LE | 1520LE (非取樣點) | LINE161 | [5 empty] | 4 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 161 | 161kV | 1520 | 榴中～斗工二路(1520) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D11_A1 | [8 empty] | 榴中DS.1520BE | 1520BE (非取樣點) | LINE161 | [5 empty] | 5 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D11_A1 | [8 empty] | 榴中DS.1750TE | 1750TE (非取樣點) | MTR | [5 empty] | 6 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D11_A1 | [8 empty] | 榴中DS.1750BE | 1750BE (非取樣點) | MTR | [5 empty] | 7 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D11_A1 | [8 empty] | 榴中DS.1760TE | 1760TE (非取樣點) | MTR | [5 empty] | 8 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D11_A1 | [8 empty] | 榴中DS.1760BE | 1760BE (非取樣點) | MTR | [5 empty] | 9 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D11_A1 | [8 empty] | 榴中DS.1501E | 1501E (非取樣點) | TIE | [5 empty] | 10 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D11_A1 | [8 empty] | 榴中DS.1502E | 1502E (非取樣點) | TIE | [5 empty] | 11 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | D1 | 311(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D11_A1 | [8 empty] | 榴中DS.311 | 311 (非取樣點) | MTR | [5 empty] | 12 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | E1 | 311E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D11_A1 | [8 empty] | 榴中DS.311E | 311E (非取樣點) | MTR | [5 empty] | 13 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | D1 | 321(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D11_A1 | [8 empty] | 榴中DS.321 | 321 (非取樣點) | MTR | [5 empty] | 14 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | E1 | 321E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D11_A1 | [8 empty] | 榴中DS.321E | 321E (非取樣點) | MTR | [5 empty] | 15 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | D1 | 331(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D11_A1 | [8 empty] | 榴中DS.331 | 331 (非取樣點) | MTR | [5 empty] | 16 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | E1 | 331E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D11_A1 | [8 empty] | 榴中DS.331E | 331E (非取樣點) | MTR | [5 empty] | 17 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | D1 | 341(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D11_A1 | [8 empty] | 榴中DS.341 | 341 (非取樣點) | MTR | [5 empty] | 18 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | E1 | 341E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D11_A1 | [8 empty] | 榴中DS.341E | 341E (非取樣點) | MTR | [5 empty] | 19 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 11 | 11kV | 390 | #1SSTR(390) |  | D1 | 391(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D11_A1 | [8 empty] | 榴中DS.391 | 391 (非取樣點) | OTHER | [5 empty] | 20 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | 390 | #1SSTR(390) |  | E1 | 391E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D11_A1 | [8 empty] | 榴中DS.391E | 391E (非取樣點) | OTHER | [5 empty] | 21 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 11 | 11kV | 210 | #1SC(210) |  | E1 | 211E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D11_A1 | [8 empty] | 榴中DS.211E | 211E (非取樣點) | SC | [5 empty] | 22 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 11 | 11kV | 210 | #1SC(210) |  | DS1 | 211(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D11_A1 | [8 empty] | 榴中DS.211 | 211 (非取樣點) | SC | [5 empty] | 23 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | XB51 | 榴五一線(XB51) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB51_DS | XB51_DS (非取樣點) | FEEDER | [5 empty] | 24 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | XB51 | 榴五一線(XB51) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB51_ES | XB51_ES (非取樣點) | FEEDER | [5 empty] | 25 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 22 | 22kV | XB52 | 榴五二線(XB52) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB52_DS | XB52_DS (非取樣點) | FEEDER | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | XB52 | 榴五二線(XB52) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB52_ES | XB52_ES (非取樣點) | FEEDER | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 22 | 22kV | XB53 | 榴五三線(XB53) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB53_DS | XB53_DS (非取樣點) | FEEDER | [5 empty] | 28 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | XB53 | 榴五三線(XB53) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB53_ES | XB53_ES (非取樣點) | FEEDER | [5 empty] | 29 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 22 | 22kV | XB54 | 榴五四線(XB54) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB54_DS | XB54_DS (非取樣點) | FEEDER | [5 empty] | 30 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | XB54 | 榴五四線(XB54) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB54_ES | XB54_ES (非取樣點) | FEEDER | [5 empty] | 31 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 22 | 22kV | XB55 | 榴五五線(XB55) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB55_DS | XB55_DS (非取樣點) | FEEDER | [5 empty] | 32 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | XB55 | 榴五五線(XB55) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB55_ES | XB55_ES (非取樣點) | FEEDER | [5 empty] | 33 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 11 | 11kV | 100 | TIE(100) |  | D1 | 101(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D11_A1 | [8 empty] | 榴中DS.101 | 101 (非取樣點) | TIE | [5 empty] | 34 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | 100 | TIE(100) |  | D2 | 102(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D11_A1 | [8 empty] | 榴中DS.102 | 102 (非取樣點) | TIE | [5 empty] | 35 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | 100 | TIE(100) |  | E1 | 101E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D11_A1 | [8 empty] | 榴中DS.101E | 101E(非取樣點) | OTHER | [5 empty] | 36 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 11 | 11kV | 100 | TIE(100) |  | E2 | 102E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D11_A1 | [8 empty] | 榴中DS.102E | 102E(非取樣點) | OTHER | [5 empty] | 37 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 22 | 22kV | 220 | #2SC(220) |  | E1 | 221E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D11_A1 | [8 empty] | 榴中DS.221E | 221E (非取樣點) | SC | [5 empty] | 38 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 22 | 22kV | 220 | #2SC(220) |  | D1 | 221(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D11_A1 | [8 empty] | 榴中DS.221 | 221 (非取樣點) | SC | [5 empty] | 39 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | XB56 | 榴五六線(XB56) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB56_DS | XB56_DS (非取樣點) | FEEDER | [5 empty] | 40 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | XB56 | 榴五六線(XB56) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB56_ES | XB56_ES (非取樣點) | FEEDER | [5 empty] | 41 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 22 | 22kV | XB57 | 榴五七線(XB57) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB57_DS | XB57_DS (非取樣點) | FEEDER | [5 empty] | 42 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | XB57 | 榴五七線(XB57) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB57_ES | XB57_ES (非取樣點) | FEEDER | [5 empty] | 43 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 22 | 22kV | XB58 | 榴五八線(XB58) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB58_DS | XB58_DS (非取樣點) | FEEDER | [5 empty] | 44 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | XB58 | 榴五八線(XB58) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB58_ES | XB58_ES (非取樣點) | FEEDER | [5 empty] | 45 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 22 | 22kV | XB59 | 榴五九線(XB59) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB59_DS | XB59_DS (非取樣點) | FEEDER | [5 empty] | 46 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | XB59 | 榴五九線(XB59) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB59_ES | XB59_ES (非取樣點) | FEEDER | [5 empty] | 47 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 22 | 22kV | XB60 | 榴六十線(XB60) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB60_DS | XB60_DS (非取樣點) | FEEDER | [5 empty] | 48 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | XB60 | 榴六十線(XB60) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB60_ES | XB60_ES (非取樣點) | FEEDER | [5 empty] | 49 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 22 | 22kV | 490 | #2SSTR(490) |  | D1 | 491(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D11_A1 | [8 empty] | 榴中DS.491 | 491 (非取樣點) | OTHER | [5 empty] | 50 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | 490 | #2SSTR(490) |  | E1 | 491E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D11_A1 | [8 empty] | 榴中DS.491E | 491E (非取樣點) | OTHER | [5 empty] | 51 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 11 | 11kV | 230 | #3SC(230) |  | E1 | 231E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D11_A1 | [8 empty] | 榴中DS.231E | 231E (非取樣點) | SC | [5 empty] | 52 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 11 | 11kV | 230 | #3SC(230) |  | DS1 | 231(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D11_A1 | [8 empty] | 榴中DS.231 | 231 (非取樣點) | SC | [5 empty] | 53 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB21 | 榴一線(XB21) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB21_DS | XB21_DS (非取樣點) | FEEDER | [5 empty] | 54 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB21 | 榴一線(XB21) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB21_ES | XB21_ES (非取樣點) | FEEDER | [5 empty] | 55 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 11 | 11kV | XB22 | 榴二線(XB22) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB22_DS | XB22_DS (非取樣點) | FEEDER | [5 empty] | 56 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB22 | 榴二線(XB22) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB22_ES | XB22_ES (非取樣點) | FEEDER | [5 empty] | 57 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 11 | 11kV | XB23 | 榴三線(XB23) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB23_DS | XB23_DS (非取樣點) | FEEDER | [5 empty] | 58 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB23 | 榴三線(XB23) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB23_ES | XB23_ES (非取樣點) | FEEDER | [5 empty] | 59 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 11 | 11kV | XB24 | 榴四線(XB24) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB24_DS | XB24_DS (非取樣點) | FEEDER | [5 empty] | 60 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB24 | 榴四線(XB24) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB24_ES | XB24_ES (非取樣點) | FEEDER | [5 empty] | 61 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 11 | 11kV | XB25 | 榴五線(XB25) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB25_DS | XB25_DS (非取樣點) | FEEDER | [5 empty] | 62 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB25 | 榴五線(XB25) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB25_ES | XB25_ES (非取樣點) | FEEDER | [5 empty] | 63 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 22 | 22kV | 200 | TIE(200) |  | D1 | 201(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D11_A1 | [8 empty] | 榴中DS.201 | 201 (非取樣點) | TIE | [5 empty] | 64 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | 200 | TIE(200) |  | D2 | 202(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D11_A1 | [8 empty] | 榴中DS.202 | 202 (非取樣點) | TIE | [5 empty] | 65 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | 200 | TIE(200) |  | E1 | 201E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D11_A1 | [8 empty] | 榴中DS.201E | 201E(非取樣點) | OTHER | [5 empty] | 66 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 22 | 22kV | 200 | TIE(200) |  | E2 | 202E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D11_A1 | [8 empty] | 榴中DS.202E | 202E(非取樣點) | OTHER | [5 empty] | 67 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 22 | 22kV | 240 | #4SC(240) |  | E1 | 241E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D11_A1 | [8 empty] | 榴中DS.241E | 241E (非取樣點) | SC | [5 empty] | 68 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 22 | 22kV | 240 | #4SC(240) |  | D1 | 241(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D11_A1 | [8 empty] | 榴中DS.241 | 241 (非取樣點) | SC | [5 empty] | 69 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB26 | 榴六線(XB26) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB26_DS | XB26_DS (非取樣點) | FEEDER | [5 empty] | 70 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB26 | 榴六線(XB26) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB26_ES | XB26_ES (非取樣點) | FEEDER | [5 empty] | 71 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 11 | 11kV | XB27 | 榴七線(XB27) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB27_DS | XB27_DS (非取樣點) | FEEDER | [5 empty] | 72 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB27 | 榴七線(XB27) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB27_ES | XB27_ES (非取樣點) | FEEDER | [5 empty] | 73 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 11 | 11kV | XB28 | 榴八線(XB28) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB28_DS | XB28_DS (非取樣點) | FEEDER | [5 empty] | 74 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB28 | 榴八線(XB28) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB28_ES | XB28_ES (非取樣點) | FEEDER | [5 empty] | 75 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 11 | 11kV | XB29 | 榴九線(XB29) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB29_DS | XB29_DS (非取樣點) | FEEDER | [5 empty] | 76 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB29 | 榴九線(XB29) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB29_ES | XB29_ES (非取樣點) | FEEDER | [5 empty] | 77 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 11 | 11kV | XB30 | 榴十線(XB30) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB30_DS | XB30_DS (非取樣點) | FEEDER | [5 empty] | 78 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB30 | 榴十線(XB30) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D11_D1 | [8 empty] | 榴中DS.XB30_ES | XB30_ES (非取樣點) | FEEDER | [5 empty] | 79 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0512 |  | 0000 | 1-30-00 |  | 1-00 | MCC-1 | TEST | TEST CB (開啟/ 閉合) |  |  | ELEM/ALL | [8 empty] | 榴中DS.TEST_CB | TEST CB | OTHER | [5 empty] | 80 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS |  |  | 1DTR(A) | #1DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0515 |  | 0001 | 1-30-03 |  | 1-01 | M1 | 43AS1 | #1 DTR WIND-A ULTC(自動/手動) |  |  | B1/D11_A1 | [8 empty] | 榴中DS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | [5 empty] | 81 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D11 | 榴中DS |  |  | 1DTR(A) | #1DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0002 |  |  | 1-82 |  |  | M1 | ℃ | #1A DTR 線溫指示量 0~120℃ | COIL_-120_120(-2000_2000) |  | B1/D11_A1 | [8 empty] | 榴中DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | [5 empty] | 82 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D11 | 榴中DS |  |  | 1DTR(B) | #1DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0003 |  |  | 1-83 |  |  | M1 | ℃ | #1B DTR 線溫指示量 0~120℃ | COIL_-120_120(-2000_2000) |  | B1/D11_A1 | [8 empty] | 榴中DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | [5 empty] | 83 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D11 | 榴中DS |  |  | 1DTR | #1DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | M1 | ℃ | #1 DTR 油溫指示量 0~120℃ | OIL_-120_120(-2000_2000) |  | B1/D11_A1 | [8 empty] | 榴中DS.#1DTR_OIL | #1DTR 油溫 | MTR | [5 empty] | 84 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D11 | 榴中DS |  |  | 1DTR(A) | #1DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0000 |  | 0002 | 1-80 |  | 1-02 | M1 | ------ | #1 DTR ULTC TAP-A指示量 t=-8~+8 | TAP_-8.5_8.5(0_2000) |  | B1/D11_A1 | [8 empty] | 榴中DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | [5 empty] | 85 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D11 | 榴中DS |  |  | 1DTR(B) | #1DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0516 |  | 0003 | 1-30-04 |  | 1-03 | M1 | 43AS2 | #1 DTR WIND-B ULTC(自動/手動) |  |  | B1/D11_A1 | [8 empty] | 榴中DS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | [5 empty] | 86 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D11 | 榴中DS |  |  | 2DTR(A) | #2DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | M2 | ℃ | #2A DTR 線溫指示量 0~120℃ | COIL_-120_120(-2000_2000) |  | B1/D11_A1 | [8 empty] | 榴中DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | [5 empty] | 87 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D11 | 榴中DS |  |  | 2DTR(B) | #2DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | M2 | ℃ | #2B DTR 線溫指示量 0~120℃ | COIL_-120_120(-2000_2000) |  | B1/D11_A1 | [8 empty] | 榴中DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | [5 empty] | 88 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D11 | 榴中DS |  |  | 2DTR | #2DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | M2 | ℃ | #2 DTR 油溫指示量 0~120℃ | OIL_-120_120(-2000_2000) |  | B1/D11_A1 | [8 empty] | 榴中DS.#2DTR_OIL | #2DTR 油溫 | MTR | [5 empty] | 89 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D11 | 榴中DS | 161 | 161kV | 1510 | 榴中～斗工一路(1510) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0016 |  |  | 1-90 |  |  | ------ | MW | 1510 斗工一路瓦量 0~±2000MW | MW_-560_560(-2000_2000) |  | B2/D11_A1 | [8 empty] | 榴中DS.1510_MW | 榴中斗工一路 MW | LINE161 | [5 empty] | 90 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D11 | 榴中DS | 161 | 161kV | 1510 | 榴中～斗工一路(1510) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0017 |  |  | 1-91 |  |  | ------ | MVAR | 1510 斗工一路乏量0~±2000MVAR | MVAR_-560_560(-2000_2000) |  | B2/D11_A1 | [8 empty] | 榴中DS.1510_MVAR | 榴中斗工一路 MVAR | LINE161 | [5 empty] | 91 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D11 | 榴中DS | 161 | 161kV | 1520 | 榴中～斗工二路(1520) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | ------ | MW | 1520 斗工二路瓦量 0~±2000MKW | MW_-560_560(-2000_2000) |  | B2/D11_A1 | [8 empty] | 榴中DS.1520_MW | 榴中斗工二路 MW | LINE161 | [5 empty] | 92 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D11 | 榴中DS | 161 | 161kV | 1520 | 榴中～斗工二路(1520) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | ------ | MVAR | 1520 斗工二路乏量 0~±2000MKVAR | MVAR_-560_560(-2000_2000) |  | B2/D11_A1 | [8 empty] | 榴中DS.1520_MVAR | 榴中斗工二路 MVAR | LINE161 | [5 empty] | 93 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D11 | 榴中DS | 161 | 161kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0037 |  |  | 1-A5 |  |  | 161KV #1B BUS | KV | 161KV #1B BUS電壓量 | kV_-210_210(-2000_2000) | aaa | B2/D11_A1 | [8 empty] | 榴中DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | [5 empty] | 94 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D11 | 榴中DS | 161 | 161kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0038 |  |  | 1-A6 |  |  | 161KV #2B BUS | KV | 161KV #2B BUS電壓量 | kV_-210_210(-2000_2000) | aab | B2/D11_A1 | [8 empty] | 榴中DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | [5 empty] | 95 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D11 | 榴中DS | 161 | 161kV | 1500 | TIE(1500) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | 1500 TIE | A | 1500 TIE R相電流量 | A_-2000_2000(-2000_2000) |  | B2/D11_A1 | [8 empty] | 榴中DS.1500TIE_AMP | 1500TIE AMP | TIE | [5 empty] | 96 |  |  |  |  | AI | [5 empty] | C20R1600 | 1520 | 1600 | 1760 | 1968 | 2.27 | -1520 | -1600 | -1760 | -1968 | 1 | 0.01 | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 1ABUS | #1ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0040 |  |  | 1-A8 |  |  | 23KV #1A BUS | KV | 23KV #1A BUS電壓量 | kV_-9_9(-2000_2000) | aaa | B3/D11_A1 | [8 empty] | 榴中DS.11KV#1ABUS_KV | 11KV #1ABUS KV | BUS | [5 empty] | 97 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D11 | 榴中DS | 22 | 11kV | 1BBUS | #1BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0041 |  |  | 1-A9 |  |  | 23KV #1B BUS | KV | 23KV #1B BUS電壓量 | kV_-18_18(-2000_2000) | baa | B3/D11_A1 | [8 empty] | 榴中DS.23KV#1BBUS_KV | 23KV #1BBUS KV | BUS | [5 empty] | 98 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D11 | 榴中DS | 11 | 22kV | 2ABUS | #2ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0042 |  |  | 1-AA |  |  | 23KV #2A BUS | KV | 23KV #2A BUS電壓量 | kV_-9_9(-2000_2000) | aba | B3/D11_A1 | [8 empty] | 榴中DS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS | [5 empty] | 99 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D11 | 榴中DS | 22 | 22kV | 2BBUS | #2BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0043 |  |  | 1-AB |  |  | 23KV #2B BUS | KV | 23KV #2B BUS電壓量 | kV_-18_18(-2000_2000) | bba | B3/D11_A1 | [8 empty] | 榴中DS.23KV#2BBUS_KV | 23KV #2BBUS KV | BUS | [5 empty] | 100 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D11 | 榴中DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | 310 | KW | 310 瓦量 | MW_-54_54(-2000_2000) |  | B3/D11_A1 | [8 empty] | 榴中DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | [5 empty] | 101 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | 310 | KVAR | 310 乏量 | MVAR_-36_36(-2000_2000) |  | B3/D11_A1 | [8 empty] | 榴中DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | [5 empty] | 102 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | 310 | A | 310 R相電流量 | A_-2000_2000(-2000_2000) |  | B3/D11_A1 | [8 empty] | 榴中DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | [5 empty] | 103 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | 310 | A | 310 S相電流量 | A_-2000_2000(-2000_2000) |  | B3/D11_A1 | [8 empty] | 榴中DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | [5 empty] | 104 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | 310 | A | 310 T相電流量 | A_-2000_2000(-2000_2000) |  | B3/D11_A1 | [8 empty] | 榴中DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | [5 empty] | 105 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB51 | 榴五一線(XB51) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | XB51 | KVAR | 榴五一線XB51 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴51線KVAR | 23KV榴51線 KVAR | FEEDER | [5 empty] | 106 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB51 | 榴五一線(XB51) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | XB51 | A | 榴五一線XB51 R相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴51線A1 | 23KV榴51線 R相AMP | FEEDER | [5 empty] | 107 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB51 | 榴五一線(XB51) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | XB51 | A | 榴五一線XB51 S相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴51線A2 | 23KV榴51線 S相AMP | FEEDER | [5 empty] | 108 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB51 | 榴五一線(XB51) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | XB51 | A | 榴五一線XB51 T相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴51線A3 | 23KV榴51線 T相AMP | FEEDER | [5 empty] | 109 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB51 | 榴五一線(XB51) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | XB51 | A | 榴五一線XB51 N相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴51線A0 | 23KV榴51線 N相AMP | FEEDER | [5 empty] | 110 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB52 | 榴五二線(XB52) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | XB52 | KVAR | 榴五二線XB52 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴52線KVAR | 23KV榴52線 KVAR | FEEDER | [5 empty] | 111 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB52 | 榴五二線(XB52) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | XB52 | A | 榴五二線XB52 R相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴52線A1 | 23KV榴52線 R相AMP | FEEDER | [5 empty] | 112 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB52 | 榴五二線(XB52) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | XB52 | A | 榴五二線XB52 S相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴52線A2 | 23KV榴52線 S相AMP | FEEDER | [5 empty] | 113 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB52 | 榴五二線(XB52) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | XB52 | A | 榴五二線XB52 T相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴52線A3 | 23KV榴52線 T相AMP | FEEDER | [5 empty] | 114 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB52 | 榴五二線(XB52) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | XB52 | A | 榴五二線XB52 N相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴52線A0 | 23KV榴52線 N相AMP | FEEDER | [5 empty] | 115 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB53 | 榴五三線(XB53) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | XB53 | KVAR | 榴五三線XB53 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴53線KVAR | 23KV榴53線 KVAR | FEEDER | [5 empty] | 116 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB53 | 榴五三線(XB53) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0060 |  |  | 1-BC |  |  | XB53 | A | 榴五三線XB53 R相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴53線A1 | 23KV榴53線 R相AMP | FEEDER | [5 empty] | 117 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB53 | 榴五三線(XB53) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | XB53 | A | 榴五三線XB53 S相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴53線A2 | 23KV榴53線 S相AMP | FEEDER | [5 empty] | 118 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB53 | 榴五三線(XB53) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | XB53 | A | 榴五三線XB53 T相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴53線A3 | 23KV榴53線 T相AMP | FEEDER | [5 empty] | 119 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB53 | 榴五三線(XB53) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0063 |  |  | 1-BF |  |  | XB53 | A | 榴五三線XB53 N相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴53線A0 | 23KV榴53線 N相AMP | FEEDER | [5 empty] | 120 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB54 | 榴五四線(XB54) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | XB54 | KVAR | 榴五四線XB54 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴54線KVAR | 23KV榴54線 KVAR | FEEDER | [5 empty] | 121 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB54 | 榴五四線(XB54) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | XB54 | A | 榴五四線XB54 R相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴54線A1 | 23KV榴54線 R相AMP | FEEDER | [5 empty] | 122 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB54 | 榴五四線(XB54) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | XB54 | A | 榴五四線XB54 S相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴54線A2 | 23KV榴54線 S相AMP | FEEDER | [5 empty] | 123 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB54 | 榴五四線(XB54) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | XB54 | A | 榴五四線XB54 T相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴54線A3 | 23KV榴54線 T相AMP | FEEDER | [5 empty] | 124 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB54 | 榴五四線(XB54) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | XB54 | A | 榴五四線XB54 N相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴54線A0 | 23KV榴54線 N相AMP | FEEDER | [5 empty] | 125 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB55 | 榴五五線(XB55) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | XB55 | KVAR | 榴五五線XB55 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴55線KVAR | 23KV榴55線 KVAR | FEEDER | [5 empty] | 126 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB55 | 榴五五線(XB55) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | XB55 | A | 榴五五線XB55 R相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴55線A1 | 23KV榴55線 R相AMP | FEEDER | [5 empty] | 127 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB55 | 榴五五線(XB55) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | XB55 | A | 榴五五線XB55 S相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴55線A2 | 23KV榴55線 S相AMP | FEEDER | [5 empty] | 128 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB55 | 榴五五線(XB55) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | XB55 | A | 榴五五線XB55 T相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴55線A3 | 23KV榴55線 T相AMP | FEEDER | [5 empty] | 129 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB55 | 榴五五線(XB55) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | XB55 | A | 榴五五線XB55 N相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴55線A0 | 23KV榴55線 N相AMP | FEEDER | [5 empty] | 130 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 100 | TIE(100) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | 100 | A | 100 R相電流量 | A_-2000_2000(-2000_2000) |  | B3/D11_A1 | [8 empty] | 榴中DS.11KV_100_A1 | 11KV 100 R相AMP | TIE | [5 empty] | 131 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 100 | TIE(100) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | 100 | A | 100 S相電流量 | A_-2000_2000(-2000_2000) |  | B3/D11_A1 | [8 empty] | 榴中DS.11KV_100_A2 | 11KV 100 S相AMP | TIE | [5 empty] | 132 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 100 | TIE(100) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | 100 | A | 100 T相電流量 | A_-2000_2000(-2000_2000) |  | B3/D11_A1 | [8 empty] | 榴中DS.11KV_100_A3 | 11KV 100 T相AMP | TIE | [5 empty] | 133 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | 330 | KW | 330 瓦量 | MW_-54_54(-2000_2000) |  | B3/D11_A1 | [8 empty] | 榴中DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | [5 empty] | 134 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | 330 | KVAR | 330 乏量 | MVAR_-36_36(-2000_2000) |  | B3/D11_A1 | [8 empty] | 榴中DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | [5 empty] | 135 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | 330 | A | 330 R相電流量 | A_-2000_2000(-2000_2000) |  | B3/D11_A1 | [8 empty] | 榴中DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | [5 empty] | 136 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | 330 | A | 330 S相電流量 | A_-2000_2000(-2000_2000) |  | B3/D11_A1 | [8 empty] | 榴中DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | [5 empty] | 137 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | 330 | A | 330 T相電流量 | A_-2000_2000(-2000_2000) |  | B3/D11_A1 | [8 empty] | 榴中DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | [5 empty] | 138 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB56 | 榴五六線(XB56) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | XB56 | KVAR | 榴五六線XB56 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴56線KVAR | 23KV榴56線 KVAR | FEEDER | [5 empty] | 139 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB56 | 榴五六線(XB56) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | XB56 | A | 榴五六線XB56 R相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴56線A1 | 23KV榴56線 R相AMP | FEEDER | [5 empty] | 140 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB56 | 榴五六線(XB56) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | XB56 | A | 榴五六線XB56 S相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴56線A2 | 23KV榴56線 S相AMP | FEEDER | [5 empty] | 141 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB56 | 榴五六線(XB56) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | XB56 | A | 榴五六線XB56 T相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴56線A3 | 23KV榴56線 T相AMP | FEEDER | [5 empty] | 142 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB56 | 榴五六線(XB56) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | XB56 | A | 榴五六線XB56 N相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴56線A0 | 23KV榴56線 N相AMP | FEEDER | [5 empty] | 143 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB57 | 榴五七線(XB57) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | XB57 | KVAR | 榴五七線XB57 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴57線KVAR | 23KV榴57線 KVAR | FEEDER | [5 empty] | 144 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB57 | 榴五七線(XB57) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | XB57 | A | 榴五七線XB57 R相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴57線A1 | 23KV榴57線 R相AMP | FEEDER | [5 empty] | 145 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB57 | 榴五七線(XB57) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | XB57 | A | 榴五七線XB57 S相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴57線A2 | 23KV榴57線 S相AMP | FEEDER | [5 empty] | 146 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB57 | 榴五七線(XB57) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | XB57 | A | 榴五七線XB57 T相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴57線A3 | 23KV榴57線 T相AMP | FEEDER | [5 empty] | 147 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB57 | 榴五七線(XB57) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | XB57 | A | 榴五七線XB57 N相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴57線A0 | 23KV榴57線 N相AMP | FEEDER | [5 empty] | 148 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB58 | 榴五八線(XB58) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | XB58 | KVAR | 榴五八線XB58 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴58線KVAR | 23KV榴58線 KVAR | FEEDER | [5 empty] | 149 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB58 | 榴五八線(XB58) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | XB58 | A | 榴五八線XB58 R相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴58線A1 | 23KV榴58線 R相AMP | FEEDER | [5 empty] | 150 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB58 | 榴五八線(XB58) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | XB58 | A | 榴五八線XB58 S相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴58線A2 | 23KV榴58線 S相AMP | FEEDER | [5 empty] | 151 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB58 | 榴五八線(XB58) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | XB58 | A | 榴五八線XB58 T相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴58線A3 | 23KV榴58線 T相AMP | FEEDER | [5 empty] | 152 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB58 | 榴五八線(XB58) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | XB58 | A | 榴五八線XB58 N相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴58線A0 | 23KV榴58線 N相AMP | FEEDER | [5 empty] | 153 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB59 | 榴五九線(XB59) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | XB59 | KVAR | XB59 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴59線KVAR | 23KV榴59線 KVAR | FEEDER | [5 empty] | 154 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB59 | 榴五九線(XB59) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0098 |  |  | 1-E2 |  |  | XB59 | A | XB59 R相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴59線A1 | 23KV榴59線 R相AMP | FEEDER | [5 empty] | 155 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB59 | 榴五九線(XB59) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | XB59 | A | XB59 S相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴59線A2 | 23KV榴59線 S相AMP | FEEDER | [5 empty] | 156 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB59 | 榴五九線(XB59) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | XB59 | A | XB59 T相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴59線A3 | 23KV榴59線 T相AMP | FEEDER | [5 empty] | 157 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB59 | 榴五九線(XB59) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0101 |  |  | 1-E5 |  |  | XB59 | A | XB59 N相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴59線A0 | 23KV榴59線 N相AMP | FEEDER | [5 empty] | 158 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB60 | 榴六十線(XB60) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | XB60 | KVAR | XB60 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴60線KVAR | 23KV榴60線 KVAR | FEEDER | [5 empty] | 159 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB60 | 榴六十線(XB60) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | XB60 | A | XB60 R相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴60線A1 | 23KV榴60線 R相AMP | FEEDER | [5 empty] | 160 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB60 | 榴六十線(XB60) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | XB60 | A | XB60 S相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴60線A2 | 23KV榴60線 S相AMP | FEEDER | [5 empty] | 161 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB60 | 榴六十線(XB60) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | XB60 | A | XB60 T相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴60線A3 | 23KV榴60線 T相AMP | FEEDER | [5 empty] | 162 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | XB60 | 榴六十線(XB60) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | XB60 | A | XB60 N相電流量 | A_-600_600(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴60線A0 | 23KV榴60線 N相AMP | FEEDER | [5 empty] | 163 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | 320 | KW | 320 瓦量 | MW_-108_108(-2000_2000) |  | B3/D11_A1 | [8 empty] | 榴中DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | [5 empty] | 164 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.216 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | 320 | KVAR | 320 乏量 | MVAR_-72_72(-2000_2000) |  | B3/D11_A1 | [8 empty] | 榴中DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | [5 empty] | 165 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | 320 | A | 320 R相電流量 | A_-2000_2000(-2000_2000) |  | B3/D11_A1 | [8 empty] | 榴中DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | [5 empty] | 166 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | 320 | A | 320 S相電流量 | A_-2000_2000(-2000_2000) |  | B3/D11_A1 | [8 empty] | 榴中DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | [5 empty] | 167 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | 320 | A | 320 T相電流量 | A_-2000_2000(-2000_2000) |  | B3/D11_A1 | [8 empty] | 榴中DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | [5 empty] | 168 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB21 | 榴一線(XB21) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | XB21 | KVAR | XB21 乏量 | KVAR_-9000_9000(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴一線KVAR | 11KV榴一線 KVAR | FEEDER | [5 empty] | 169 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB21 | 榴一線(XB21) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | XB21 | A | XB21 R相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴一線A1 | 11KV榴一線 R相AMP | FEEDER | [5 empty] | 170 |  |  |  |  | AI | [5 empty] | C05R450R | 405 | 406 | 450 | 500 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB21 | 榴一線(XB21) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | XB21 | A | XB21 S相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴一線A2 | 11KV榴一線 S相AMP | FEEDER | [5 empty] | 171 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB21 | 榴一線(XB21) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | XB21 | A | XB21 T相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴一線A3 | 11KV榴一線 T相AMP | FEEDER | [5 empty] | 172 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB21 | 榴一線(XB21) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | XB21 | A | XB21 N相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴一線A0 | 11KV榴一線 N相AMP | FEEDER | [5 empty] | 173 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB22 | 榴二線(XB22) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | XB22 | KVAR | XB22 乏量 | KVAR_-9000_9000(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴二線KVAR | 11KV榴二線 KVAR | FEEDER | [5 empty] | 174 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB22 | 榴二線(XB22) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | XB22 | A | XB22 R相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴二線A1 | 11KV榴二線 R相AMP | FEEDER | [5 empty] | 175 |  |  |  |  | AI | [5 empty] | C05R450R | 405 | 406 | 450 | 500 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB22 | 榴二線(XB22) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | XB22 | A | XB22 S相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴二線A2 | 11KV榴二線 S相AMP | FEEDER | [5 empty] | 176 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB22 | 榴二線(XB22) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | XB22 | A | XB22 T相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴二線A3 | 11KV榴二線 T相AMP | FEEDER | [5 empty] | 177 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB22 | 榴二線(XB22) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | XB22 | A | XB22 N相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴二線A0 | 11KV榴二線 N相AMP | FEEDER | [5 empty] | 178 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB23 | 榴三線(XB23) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | XB23 | KVAR | XB23 乏量 | KVAR_-9000_9000(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴三線KVAR | 11KV榴三線 KVAR | FEEDER | [5 empty] | 179 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB23 | 榴三線(XB23) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | XB23 | A | XB23 R相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴三線A1 | 11KV榴三線 R相AMP | FEEDER | [5 empty] | 180 |  |  |  |  | AI | [5 empty] | C05R450R | 405 | 406 | 450 | 500 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB23 | 榴三線(XB23) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | XB23 | A | XB23 S相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴三線A2 | 11KV榴三線 S相AMP | FEEDER | [5 empty] | 181 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB23 | 榴三線(XB23) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | XB23 | A | XB23 T相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴三線A3 | 11KV榴三線 T相AMP | FEEDER | [5 empty] | 182 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB23 | 榴三線(XB23) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | XB23 | A | XB23 N相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴三線A0 | 11KV榴三線 N相AMP | FEEDER | [5 empty] | 183 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB24 | 榴四線(XB24) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | XB24 | KVAR | XB24 乏量 | KVAR_-9000_9000(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴四線KVAR | 11KV榴四線 KVAR | FEEDER | [5 empty] | 184 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB24 | 榴四線(XB24) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | XB24 | A | XB24 R相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴四線A1 | 11KV榴四線 R相AMP | FEEDER | [5 empty] | 185 |  |  |  |  | AI | [5 empty] | C05R450R | 405 | 406 | 450 | 500 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB24 | 榴四線(XB24) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | XB24 | A | XB24 S相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴四線A2 | 11KV榴四線 S相AMP | FEEDER | [5 empty] | 186 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB24 | 榴四線(XB24) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | XB24 | A | XB24 T相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴四線A3 | 11KV榴四線 T相AMP | FEEDER | [5 empty] | 187 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB24 | 榴四線(XB24) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | XB24 | A | XB24 N相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴四線A0 | 11KV榴四線 N相AMP | FEEDER | [5 empty] | 188 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB25 | 榴五線(XB25) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | XB25 | KVAR | XB25 乏量 | KVAR_-9000_9000(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴五線KVAR | 11KV榴五線 KVAR | FEEDER | [5 empty] | 189 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB25 | 榴五線(XB25) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0133 |  |  | 2-85 |  |  | XB25 | A | XB25 R相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴五線A1 | 11KV榴五線 R相AMP | FEEDER | [5 empty] | 190 |  |  |  |  | AI | [5 empty] | C05R450R | 405 | 406 | 450 | 500 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB25 | 榴五線(XB25) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | XB25 | A | XB25 S相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴五線A2 | 11KV榴五線 S相AMP | FEEDER | [5 empty] | 191 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB25 | 榴五線(XB25) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0135 |  |  | 2-87 |  |  | XB25 | A | XB25 T相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴五線A3 | 11KV榴五線 T相AMP | FEEDER | [5 empty] | 192 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB25 | 榴五線(XB25) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0136 |  |  | 2-88 |  |  | XB25 | A | XB25 N相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴五線A0 | 11KV榴五線 N相AMP | FEEDER | [5 empty] | 193 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 200 | TIE(200) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0137 |  |  | 2-89 |  |  | 200 | A | 200 R相電流量 | A_-2000_2000(-2000_2000) |  | B3/D11_A1 | [8 empty] | 榴中DS.23KV_200_A1 | 23KV 200 R相AMP | TIE | [5 empty] | 194 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 200 | TIE(200) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0138 |  |  | 2-8A |  |  | 200 | A | 200 R相電流量 | A_-2000_2000(-2000_2000) |  | B3/D11_A1 | [8 empty] | 榴中DS.23KV_200_A2 | 23KV 200 S相AMP | TIE | [5 empty] | 195 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 200 | TIE(200) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0139 |  |  | 2-8B |  |  | 200 | A | 200 R相電流量 | A_-2000_2000(-2000_2000) |  | B3/D11_A1 | [8 empty] | 榴中DS.23KV_200_A3 | 23KV 200 T相AMP | TIE | [5 empty] | 196 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0140 |  |  | 2-8C |  |  | 340 | KW | 340 瓦量 | MW_-108_108(-2000_2000) |  | B3/D11_A1 | [8 empty] | 榴中DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | [5 empty] | 197 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.216 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0141 |  |  | 2-8D |  |  | 340 | KVAR | 340 乏量 | MVAR_-72_72(-2000_2000) |  | B3/D11_A1 | [8 empty] | 榴中DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | [5 empty] | 198 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0142 |  |  | 2-8E |  |  | 340 | A | 340 R相電流量 | A_-2000_2000(-2000_2000) |  | B3/D11_A1 | [8 empty] | 榴中DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | [5 empty] | 199 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0143 |  |  | 2-8F |  |  | 340 | A | 340 S相電流量 | A_-2000_2000(-2000_2000) |  | B3/D11_A1 | [8 empty] | 榴中DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | [5 empty] | 200 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0144 |  |  | 2-90 |  |  | 340 | A | 340 T相電流量 | A_-2000_2000(-2000_2000) |  | B3/D11_A1 | [8 empty] | 榴中DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | [5 empty] | 201 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB26 | 榴六線(XB26) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0145 |  |  | 2-91 |  |  | XB26 | KVAR | XB26 乏量 | KVAR_-9000_9000(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴六線KVAR | 11KV榴六線 KVAR | FEEDER | [5 empty] | 202 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB26 | 榴六線(XB26) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0146 |  |  | 2-92 |  |  | XB26 | A | XB26 R相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴六線A1 | 11KV榴六線 R相AMP | FEEDER | [5 empty] | 203 |  |  |  |  | AI | [5 empty] | C05R450R | 405 | 406 | 450 | 500 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB26 | 榴六線(XB26) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0147 |  |  | 2-93 |  |  | XB26 | A | XB26 S相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴六線A2 | 11KV榴六線 S相AMP | FEEDER | [5 empty] | 204 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB26 | 榴六線(XB26) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0148 |  |  | 2-94 |  |  | XB26 | A | XB26 T相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴六線A3 | 11KV榴六線 T相AMP | FEEDER | [5 empty] | 205 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB26 | 榴六線(XB26) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0149 |  |  | 2-95 |  |  | XB26 | A | XB26 N相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴六線A0 | 11KV榴六線 N相AMP | FEEDER | [5 empty] | 206 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB27 | 榴七線(XB27) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0150 |  |  | 2-96 |  |  | XB27 | KVAR | XB27 乏量 | KVAR_-9000_9000(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴七線KVAR | 11KV榴七線 KVAR | FEEDER | [5 empty] | 207 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB27 | 榴七線(XB27) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0151 |  |  | 2-97 |  |  | XB27 | A | XB27 R相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴七線A1 | 11KV榴七線 R相AMP | FEEDER | [5 empty] | 208 |  |  |  |  | AI | [5 empty] | C05R450R | 405 | 406 | 450 | 500 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB27 | 榴七線(XB27) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0152 |  |  | 2-98 |  |  | XB27 | A | XB27 S相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴七線A2 | 11KV榴七線 S相AMP | FEEDER | [5 empty] | 209 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB27 | 榴七線(XB27) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0153 |  |  | 2-99 |  |  | XB27 | A | XB27 T相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴七線A3 | 11KV榴七線 T相AMP | FEEDER | [5 empty] | 210 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB27 | 榴七線(XB27) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0154 |  |  | 2-9A |  |  | XB27 | A | XB27 N相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴七線A0 | 11KV榴七線 N相AMP | FEEDER | [5 empty] | 211 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB28 | 榴八線(XB28) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0155 |  |  | 2-9B |  |  | XB28 | KVAR | XB28 乏量 | KVAR_-9000_9000(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴八線KVAR | 11KV榴八線 KVAR | FEEDER | [5 empty] | 212 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB28 | 榴八線(XB28) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0156 |  |  | 2-9C |  |  | XB28 | A | XB28 R相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴八線A1 | 11KV榴八線 R相AMP | FEEDER | [5 empty] | 213 |  |  |  |  | AI | [5 empty] | C05R450R | 405 | 406 | 450 | 500 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB28 | 榴八線(XB28) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0157 |  |  | 2-9D |  |  | XB28 | A | XB28 S相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴八線A2 | 11KV榴八線 S相AMP | FEEDER | [5 empty] | 214 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB28 | 榴八線(XB28) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0158 |  |  | 2-9E |  |  | XB28 | A | XB28 T相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴八線A3 | 11KV榴八線 T相AMP | FEEDER | [5 empty] | 215 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB28 | 榴八線(XB28) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0159 |  |  | 2-9F |  |  | XB28 | A | XB28 N相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴八線A0 | 11KV榴八線 N相AMP | FEEDER | [5 empty] | 216 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB29 | 榴九線(XB29) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0160 |  |  | 2-A0 |  |  | XB29 | KVAR | XB29 乏量 | KVAR_-9000_9000(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴九線KVAR | 11KV榴九線 KVAR | FEEDER | [5 empty] | 217 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB29 | 榴九線(XB29) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0161 |  |  | 2-A1 |  |  | XB29 | A | XB29 R相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴九線A1 | 11KV榴九線 R相AMP | FEEDER | [5 empty] | 218 |  |  |  |  | AI | [5 empty] | C05R450R | 405 | 406 | 450 | 500 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB29 | 榴九線(XB29) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0162 |  |  | 2-A2 |  |  | XB29 | A | XB29 S相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴九線A2 | 11KV榴九線 S相AMP | FEEDER | [5 empty] | 219 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB29 | 榴九線(XB29) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0163 |  |  | 2-A3 |  |  | XB29 | A | XB29 T相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴九線A3 | 11KV榴九線 T相AMP | FEEDER | [5 empty] | 220 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB29 | 榴九線(XB29) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0164 |  |  | 2-A4 |  |  | XB29 | A | XB29 N相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴九線A0 | 11KV榴九線 N相AMP | FEEDER | [5 empty] | 221 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB30 | 榴十線(XB30) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0165 |  |  | 2-A5 |  |  | XB30 | KVAR | XB30 乏量 | KVAR_-9000_9000(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴十線KVAR | 11KV榴十線 KVAR | FEEDER | [5 empty] | 222 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB30 | 榴十線(XB30) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0166 |  |  | 2-A6 |  |  | XB30 | A | XB30 R相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴十線A1 | 11KV榴十線 R相AMP | FEEDER | [5 empty] | 223 |  |  |  |  | AI | [5 empty] | C05R450R | 405 | 406 | 450 | 500 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB30 | 榴十線(XB30) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0167 |  |  | 2-A7 |  |  | XB30 | A | XB30 S相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴十線A2 | 11KV榴十線 S相AMP | FEEDER | [5 empty] | 224 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB30 | 榴十線(XB30) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0168 |  |  | 2-A8 |  |  | XB30 | A | XB30 T相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴十線A3 | 11KV榴十線 T相AMP | FEEDER | [5 empty] | 225 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | XB30 | 榴十線(XB30) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0169 |  |  | 2-A9 |  |  | XB30 | A | XB30 N相電流量 | A_-500_500(-2000_2000) |  | B2/D11_D1 | [8 empty] | 榴中DS.榴十線A0 | 11KV榴十線 N相AMP | FEEDER | [5 empty] | 226 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | DCV_P |  |  | MvMoment | 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0170 |  |  | 2-AA |  |  | Locate Empty | DCP | 直流P電源電壓 | kV_-150_150(-2000_2000) |  | B3/D11_A1 | [8 empty] | 榴中DS.直流P電源電壓 | 直流P電源電壓 | OTHER | [5 empty] | 227 |  |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 | 0.01 | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | DCV_N |  |  | MvMoment | 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0171 |  |  | 2-AB |  |  | Locate Empty | DCN | 直流N電源電壓 | kV_-150_150(-2000_2000) |  | B3/D11_A1 | [8 empty] | 榴中DS.直流N電源電壓 | 直流N電源電壓 | OTHER | [5 empty] | 228 |  |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 | 0.01 | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D11 | 榴中DS | 161 | 161kV | 1510 | 榴中～斗工一路(1510) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0001 |  |  | 1-00-01 |  |  | R5 | L187A | 1510 斗工一路主保護(動作/正常) |  |  | B2/D11_A1 | [8 empty] | 榴中DS.1510_87A | 榴中斗工一路(1510) 87RY | LINE161 | [5 empty] | 229 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1510 | 榴中～斗工一路(1510) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0002 |  |  | 1-00-02 |  |  | R5 | L1PHA | 1510 斗工一路相間電驛(動作/正常) |  |  | B2/D11_A1 | [8 empty] | 榴中DS.1510_PHA | 榴中斗工一路(1510) 相間RY | LINE161 | [5 empty] | 230 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1510 | 榴中～斗工一路(1510) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | R5 | L1GDA | 1510 斗工一路接地電驛(動作/正常) |  |  | B2/D11_A1 | [8 empty] | 榴中DS.1510_GDA | 榴中斗工一路(1510) 接地RY | LINE161 | [5 empty] | 231 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1520 | 榴中～斗工二路(1520) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0005 |  |  | 1-00-05 |  |  | R6 | L287A | 1520 斗工二路主保護(動作/正常) |  |  | B2/D11_A1 | [8 empty] | 榴中DS.1520_87A | 榴中斗工二路(1520) 87RY | LINE161 | [5 empty] | 232 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1520 | 榴中～斗工二路(1520) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | R6 | L2PHA | 1520 斗工二路相間電驛(動作/正常) |  |  | B2/D11_A1 | [8 empty] | 榴中DS.1520_PHA | 榴中斗工二路(1520) 相間RY | LINE161 | [5 empty] | 233 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1520 | 榴中～斗工二路(1520) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-07 |  |  | R6 | L2GDA | 1520 斗工二路接地電驛(動作/正常) |  |  | B2/D11_A1 | [8 empty] | 榴中DS.1520_GDA | 榴中斗工二路(1520) 接地RY | LINE161 | [5 empty] | 234 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | PHA1 |  |  | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0048 |  |  | 1-06-00 |  |  | R5 | M1APHA | #1 DTR.二次側 M1-A相間電驛(動作/正常) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.310_51A | #1DTR二次側(310) 51RY | MTR | [5 empty] | 235 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | PHA1 |  |  | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0049 |  |  | 1-06-01 |  |  | R5 | M1BPHA | #1 DTR.二次側 M1-B相間電驛(動作/正常) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.320_51A | #1DTR二次側(320) 51RY | MTR | [5 empty] | 236 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS |  |  | 1DTR | #1DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0050 |  |  | 1-06-02 |  |  | R1 | 187A | #1 DTR.差動電驛(動作/正常) |  |  | B1/D11_A1 | [8 empty] | 榴中DS.#1DTR_87A | #1DTR 87RY | MTR | [5 empty] | 237 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS |  |  | 1DTR | #1DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0051 |  |  | 1-06-03 |  |  | R5 | 196A | #1 DTR.衝擊油壓電驛(動作/正常) |  |  | B1/D11_A1 | [8 empty] | 榴中DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | [5 empty] | 238 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS |  |  | 1DTR | #1DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | R5 | 151ZA | #1 DTR.中性點接地電驛(動作/正常) |  |  | B1/D11_A1 | [8 empty] | 榴中DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | [5 empty] | 239 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS |  |  | 1DTR | #1DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0053 |  |  | 1-06-05 |  |  | R5 | T1PHA | #1 DTR.一次側相間電驛(動作/正常) |  |  | B1/D11_A1 | [8 empty] | 榴中DS.#1DTR_51A | #1DTR 51RY | MTR | [5 empty] | 240 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS |  |  | 1DTR | #1DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0054 |  |  | 1-06-06 |  |  | R5 | T1GDA | #1 DTR.一次側接地電驛(動作/正常) |  |  | B1/D11_A1 | [8 empty] | 榴中DS.#1DTR_51NA | #1DTR 51N RY | MTR | [5 empty] | 241 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | PHA1 |  |  | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0057 |  |  | 1-07-01 |  |  | R6 | M2APHA | #2 DTR.二次側 M2-A相間電驛(動作/正常) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.330_51A | #2DTR二次側(330) 51RY | MTR | [5 empty] | 242 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | PHA1 |  |  | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0058 |  |  | 1-07-02 |  |  | R6 | M2BPHA | #2 DTR.二次側 M2-B相間電驛(動作/正常) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.340_51A | #2DTR二次側(340) 51RY | MTR | [5 empty] | 243 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS |  |  | 2DTR | #2DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0059 |  |  | 1-07-03 |  |  | R2 | 287A | #2 DTR.差動電驛(動作/正常) |  |  | B1/D11_A1 | [8 empty] | 榴中DS.#2DTR_87A | #2DTR 87RY | MTR | [5 empty] | 244 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS |  |  | 2DTR | #2DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0060 |  |  | 1-07-04 |  |  | R6 | 296A | #2 DTR.衝擊油壓電驛(動作/正常) |  |  | B1/D11_A1 | [8 empty] | 榴中DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | [5 empty] | 245 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS |  |  | 2DTR | #2DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0061 |  |  | 1-07-05 |  |  | R6 | 251ZA | #2 DTR.中性點接地電驛(動作/正常) |  |  | B1/D11_A1 | [8 empty] | 榴中DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | [5 empty] | 246 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS |  |  | 2DTR | #2DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0062 |  |  | 1-07-06 |  |  | R6 | T2PHA | #2 DTR.一次側相間電驛(動作/正常) |  |  | B1/D11_A1 | [8 empty] | 榴中DS.#2DTR_51A | #2DTR 51RY | MTR | [5 empty] | 247 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS |  |  | 2DTR | #2DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0063 |  |  | 1-07-07 |  |  | R6 | T2GDA | #2 DTR.一次側接地電驛(動作/正常) |  |  | B1/D11_A1 | [8 empty] | 榴中DS.#2DTR_51NA | #2DTR 51N RY | MTR | [5 empty] | 248 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0088 |  |  | 1-0B-00 |  |  | R5 | 50A | 161KV TIE 瞬時電驛 (動作/正常) |  |  | B2/D11_A1 | [8 empty] | 榴中DS.1500_50A | 161KV TIE(1500) 50RY | TIE | [5 empty] | 249 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0089 |  |  | 1-0B-01 |  |  | R5 | 87B1A | 161KV #1 BUS 電驛 (動作/正常) |  |  | B2/D11_A1 | [8 empty] | 榴中DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | [5 empty] | 250 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0090 |  |  | 1-0B-02 |  |  | R5 | 87B2A | 161KV #2 BUS 電驛 (動作/正常) |  |  | B2/D11_A1 | [8 empty] | 榴中DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | [5 empty] | 251 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0091 |  |  | 1-0B-03 |  |  | M5 | OSCA | OSC啟動警報(動作/正常) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.161KV_OSCA | 161KV示波器啟動警報 | OTHER | [5 empty] | 252 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | ComPoint |  |  | 25TA |  |  | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0116 |  |  | 1-0E-04 |  |  | ------ | 25TA | 161KV GIS 25電驛超時警報 (COMMON) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | [5 empty] | 253 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0117 |  |  | 1-0E-05 |  |  | ------ | RCA | 161KV 復閉電驛(動作/正常)(COMMON) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | [5 empty] | 254 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D11 | 榴中DS |  |  | 1DTR(B) | #1DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0001 |  | 0004 | 1-81 |  | 1-04 | M1 | ------ | #1 DTR ULTC TAP-B指示量 t=-8~+8 | TAP_-8.5_8.5(0_2000) |  | B1/D11_A1 | [8 empty] | 榴中DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | [5 empty] | 255 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D11 | 榴中DS |  |  | 2DTR(A) | #2DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0526 |  | 0005 | 1-30-14 |  | 1-05 | M2 | 243AS1 | #2 DTR WIND-AULTC(自動/手動) |  |  | B1/D11_A1 | [8 empty] | 榴中DS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | [5 empty] | 256 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D11 | 榴中DS |  |  | 2DTR(A) | #2DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0005 |  | 0006 | 1-85 |  | 1-06 | M2 | ------ | #2 DTR ULTC TAP-A指示量 t=-8~+8 | TAP_-8.5_8.5(0_2000) |  | B1/D11_A1 | [8 empty] | 榴中DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | [5 empty] | 257 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D11 | 榴中DS |  |  | 2DTR(B) | #2DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0527 |  | 0007 | 1-30-15 |  | 1-07 | M2 | 243AS2 | #2 DTR WIND-B ULTC(自動/手動) |  |  | B1/D11_A1 | [8 empty] | 榴中DS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | [5 empty] | 258 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D11 | 榴中DS |  |  | 2DTR(B) | #2DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0006 |  | 0008 | 1-86 |  | 1-08 | M2 | ------ | #2 DTR ULTC TAP-B指示量 t=-8~+8 | TAP_-8.5_8.5(0_2000) |  | B1/D11_A1 | [8 empty] | 榴中DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | [5 empty] | 259 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D11 | 榴中DS | 161 | 161kV | 1510 | 榴中～斗工一路(1510) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0553 |  | 0017 | 1-32-09 |  | 1-11 | R1 | L187S | 1510 斗工一路主保護電驛閉鎖開關(使用/閉鎖) |  |  | B2/D11_A1 | [8 empty] | 榴中DS.1510_87UL | 榴中斗工一路(1510) 87RY U/L | LINE161 | [5 empty] | 260 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D11 | 榴中DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | PHA2 |  |  | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0124 |  |  | 1-0F-04 |  |  | 310 | PHA | 310 相間電驛(動作/正常) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.310_PHA2 | 310開關箱IED RY PHA | OTHER | [5 empty] | 261 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0125 |  |  | 1-0F-05 |  |  | 310 | GDA | 310 接地電驛(動作/正常) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.310_GDA | 310開關箱IED RY GDA | OTHER | [5 empty] | 262 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1510 | 榴中～斗工一路(1510) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0555 |  | 0019 | 1-32-11 |  | 1-13 | R1 | L179S | 1510 斗工一路復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D11_A1 | [8 empty] | 榴中DS.1510_79UL | 榴中斗工一路(1510) 79RY U/L | LINE161 | [5 empty] | 263 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D11 | 榴中DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | PHA2 |  |  | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0127 |  |  | 1-0F-07 |  |  | 320 | PHA | 320 相間電驛(動作/正常) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.320_PHA2 | 320開關箱IED RY PHA | OTHER | [5 empty] | 264 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0128 |  |  | 1-10-00 |  |  | 320 | GDA | 320 接地電驛(動作/正常) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.320_GDA | 320開關箱IED RY GDA | OTHER | [5 empty] | 265 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1520 | 榴中～斗工二路(1520) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0554 |  | 0020 | 1-32-10 |  | 1-14 | R2 | L287S | 1520 斗工二路主保護電驛閉鎖開關(使用/閉鎖) |  |  | B2/D11_A1 | [8 empty] | 榴中DS.1520_87UL | 榴中斗工二路(1520) 87RY U/L | LINE161 | [5 empty] | 266 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D11 | 榴中DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | PHA2 |  |  | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-10-02 |  |  | 330 | PHA | 330 相間電驛(動作/正常) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.330_PHA2 | 330開關箱IED RY PHA | OTHER | [5 empty] | 267 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0131 |  |  | 1-10-03 |  |  | 330 | GDA | 330 接地電驛(動作/正常) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.330_GDA | 330開關箱IED RY GDA | OTHER | [5 empty] | 268 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1520 | 榴中～斗工二路(1520) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0556 |  | 0022 | 1-32-12 |  | 1-16 | R2 | L279S | 1520 斗工二路復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D11_A1 | [8 empty] | 榴中DS.1520_79UL | 榴中斗工二路(1520) 79RY U/L | LINE161 | [5 empty] | 269 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D11 | 榴中DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | PHA2 |  |  | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0133 |  |  | 1-10-05 |  |  | 340 | PHA | 340 相間電驛(動作/正常) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.340_PHA2 | 340開關箱IED RY PHA | OTHER | [5 empty] | 270 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0134 |  |  | 1-10-06 |  |  | 340 | GDA | 340 接地電驛(動作/正常) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.340_GDA | 340開關箱IED RY GDA | OTHER | [5 empty] | 271 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | 390 | #1SSTR(390) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0256 |  |  | 2-00-00 |  |  | 390 | PHA | 390 相間電驛(動作/正常) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.#1SSTR_51A | #1SSTR 51RY | OTHER | [5 empty] | 272 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | 390 | #1SSTR(390) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0257 |  |  | 2-00-01 |  |  | 390 | GDA | 390 接地電驛(動作/正常) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | [5 empty] | 273 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0593 |  | 0023 | 1-35-01 |  | 1-17 | R5 | 87B1S | 161KV #1 BUS 電驛閉鎖開關(使用/閉鎖) |  |  | B2/D11_A1 | [8 empty] | 榴中DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | [5 empty] | 274 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D11 | 榴中DS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0262 |  |  | 2-00-06 |  |  | 210 | SCA | 210 相間及接地電驛(動作/正常) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.210_SCA | 11KV #1SC 51,51N RY | SC | [5 empty] | 275 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0263 |  |  | 2-00-07 |  |  | 210 | 3AUVA | 210 欠壓電驛(動作/正常) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | [5 empty] | 276 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0594 |  | 0024 | 1-35-02 |  | 1-18 | R5 | 87B2S | 161KV #2 BUS 電驛閉鎖開關(使用/閉鎖) |  |  | B2/D11_A1 | [8 empty] | 榴中DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | [5 empty] | 277 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D11 | 榴中DS | 22 | 22kV | XB51 | 榴五一線(XB51) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0265 |  |  | 2-01-01 |  |  | XB51 | PHA | XB51 相間電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB51_PHA | 23KV榴51線(XB51) 相間RY | FEEDER | [5 empty] | 278 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB51 | 榴五一線(XB51) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0266 |  |  | 2-01-02 |  |  | XB51 | GDA | XB51 接地電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB51_GDA | 23KV榴51線(XB51) 接地RY | FEEDER | [5 empty] | 279 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0122 |  | 0053 | 1-0F-02 |  | 1-35 | GB1 | 52AS | 1500 CB (ON/OFF) |  | aaez | B2/D11_A1 | [8 empty] | 榴中DS.1500_CB | 1500(TIE) CB | TIE | [5 empty] | 280 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | XB52 | 榴五二線(XB52) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0269 |  |  | 2-01-05 |  |  | XB52 | PHA | XB52 相間電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB52_PHA | 23KV榴52線(XB52) 相間RY | FEEDER | [5 empty] | 281 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB52 | 榴五二線(XB52) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0270 |  |  | 2-01-06 |  |  | XB52 | GDA | XB52 接地電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB52_GDA | 23KV榴52線(XB52) 接地RY | FEEDER | [5 empty] | 282 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0768 | 769 | 0054 | 2-30-00 | 2-30-01 | 1-36 | GB1 | DS (ON) | 1501 DS ON |  |  | B2/D11_A1 | [8 empty] | 榴中DS.1501_DS | 1501(TIE) DS | TIE | [5 empty] | 283 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D11 | 榴中DS | 22 | 22kV | XB53 | 榴五三線(XB53) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0273 |  |  | 2-02-01 |  |  | XB53 | PHA | XB53 相間電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB53_PHA | 23KV榴53線(XB53) 相間RY | FEEDER | [5 empty] | 284 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB53 | 榴五三線(XB53) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0274 |  |  | 2-02-02 |  |  | XB53 | GDA | XB53 接地電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB53_GDA | 23KV榴53線(XB53) 接地RY | FEEDER | [5 empty] | 285 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0770 | 771 | 0055 | 2-30-02 | 2-30-03 | 1-37 | GB1 | DS (ON) | 1502 DS ON |  |  | B2/D11_A1 | [8 empty] | 榴中DS.1502_DS | 1502(TIE) DS | TIE | [5 empty] | 286 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D11 | 榴中DS | 22 | 22kV | XB54 | 榴五四線(XB54) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0277 |  |  | 2-02-05 |  |  | XB54 | PHA | XB54 相間電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB54_PHA | 23KV榴54線(XB54) 相間RY | FEEDER | [5 empty] | 287 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB54 | 榴五四線(XB54) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0278 |  |  | 2-02-06 |  |  | XB54 | GDA | XB54 接地電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB54_GDA | 23KV榴54線(XB54) 接地RY | FEEDER | [5 empty] | 288 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1510 | 榴中～斗工一路(1510) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D11D091/T1 |  | 0118 |  | 0056 | 1-0E-06 |  | 1-38 | GL1 | 52AS | 1510 CB (ON/OFF) |  | aaca | B2/D11_A1 | [8 empty] | 榴中DS.1510_CB | 1510(榴中斗工一路) CB | LINE161 | [5 empty] | 289 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | XB55 | 榴五五線(XB55) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0281 |  |  | 2-03-01 |  |  | XB55 | PHA | XB55 相間電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB55_PHA | 23KV榴55線(XB55) 相間RY | FEEDER | [5 empty] | 290 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB55 | 榴五五線(XB55) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0282 |  |  | 2-03-02 |  |  | XB55 | GDA | XB55 接地電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB55_GDA | 23KV榴55線(XB55) 接地RY | FEEDER | [5 empty] | 291 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1510 | 榴中～斗工一路(1510) |  | DS1 | 1511 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0772 | 773 | 0057 | 2-30-04 | 2-30-05 | 1-39 | GL1 | DS (ON) | 1511 DS ON |  |  | B2/D11_A1 | [8 empty] | 榴中DS.1511_DS | 1511(榴中斗工一路) DS | LINE161 | [5 empty] | 292 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D11 | 榴中DS | 11 | 11kV | 100 | TIE(100) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0285 |  |  | 2-03-05 |  |  | 100 | PHA | 100 相間電驛(動作/正常) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.100_51A | 11KV TIE(100) 51RY | TIE | [5 empty] | 293 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | 100 | TIE(100) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0286 |  |  | 2-03-06 |  |  | 100 | GDA | 100 接地電驛(動作/正常) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.100_51NA | 11KV TIE(100) 51N RY | TIE | [5 empty] | 294 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1510 | 榴中～斗工一路(1510) |  | DS2 | 1512 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0774 | 775 | 0058 | 2-30-06 | 2-30-07 | 1-3A | GL1 | DS (ON) | 1512 DS ON |  |  | B2/D11_A1 | [8 empty] | 榴中DS.1512_DS | 1512(榴中斗工一路) DS | LINE161 | [5 empty] | 295 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D11 | 榴中DS | 22 | 22kV | 220 | #2SC(220) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0291 |  |  | 2-04-03 |  |  | 220 | SCA | 220 相間及接地電驛(動作/正常) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.220_SCA | 23KV #2SC 51,51N RY | SC | [5 empty] | 296 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | 220 | #2SC(220) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0292 |  |  | 2-04-04 |  |  | 220 | 3BUVA | 220 欠壓電驛(動作/正常) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.220_UVA | 23KV #2SC 27RY(欠壓) | SC | [5 empty] | 297 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1510 | 榴中～斗工一路(1510) |  | DS3 | 1513 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0776 | 777 | 0059 | 2-30-08 | 2-30-09 | 1-3B | GL1 | DS (ON) | 1513 DS ON |  |  | B2/D11_A1 | [8 empty] | 榴中DS.1513_DS | 1513(榴中斗工一路) DS | LINE161 | [5 empty] | 298 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D11 | 榴中DS | 22 | 22kV | XB56 | 榴五六線(XB56) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0294 |  |  | 2-04-06 |  |  | XB56 | PHA | 榴五六線XB56 相間電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB56_PHA | 23KV榴56線(XB56) 相間RY | FEEDER | [5 empty] | 299 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB56 | 榴五六線(XB56) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0295 |  |  | 2-04-07 |  |  | XB56 | GDA | 榴五六線XB56 接地電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB56_GDA | 23KV榴56線(XB56) 接地RY | FEEDER | [5 empty] | 300 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1510 | 榴中～斗工一路(1510) |  | ES3 | 1513E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0778 | 779 | 0060 | 2-30-10 | 2-30-11 | 1-3C | GL1 | ES (ON) | 1513E ES ON |  |  | B2/D11_A1 | [8 empty] | 榴中DS.1513E_ES | 1513E(榴中斗工一路) ES | LINE161 | [5 empty] | 301 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D11 | 榴中DS | 22 | 22kV | XB57 | 榴五七線(XB57) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0298 |  |  | 2-05-02 |  |  | XB57 | PHA | XB57 相間電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB57_PHA | 23KV榴57線(XB57) 相間RY | FEEDER | [5 empty] | 302 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB57 | 榴五七線(XB57) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0299 |  |  | 2-05-03 |  |  | XB57 | GDA | XB57 接地電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB57_GDA | 23KV榴57線(XB57) 接地RY | FEEDER | [5 empty] | 303 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1520 | 榴中～斗工二路(1520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D11D092/T1 |  | 0119 |  | 0061 | 1-0E-07 |  | 1-3D | GL2 | 52AS | 1520CB (ON/OFF) |  | aada | B2/D11_A1 | [8 empty] | 榴中DS.1520_CB | 1520(榴中斗工二路) CB | LINE161 | [5 empty] | 304 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | XB58 | 榴五八線(XB58) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0302 |  |  | 2-05-06 |  |  | XB58 | PHA | 榴五八線XB58 相間電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB58_PHA | 23KV榴58線(XB58) 相間RY | FEEDER | [5 empty] | 305 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB58 | 榴五八線(XB58) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0303 |  |  | 2-05-07 |  |  | XB58 | GDA | 榴五八線XB58 接地電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB58_GDA | 23KV榴58線(XB58) 接地RY | FEEDER | [5 empty] | 306 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1520 | 榴中～斗工二路(1520) |  | DS1 | 1521 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0780 | 781 | 0062 | 2-30-12 | 2-30-13 | 1-3E | GL2 | DS (ON) | 1521 DS ON |  |  | B2/D11_A1 | [8 empty] | 榴中DS.1521_DS | 1521(榴中斗工二路) DS | LINE161 | [5 empty] | 307 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D11 | 榴中DS | 22 | 22kV | XB59 | 榴五九線(XB59) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0306 |  |  | 2-06-02 |  |  | XB59 | PHA | XB59 相間電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB59_PHA | 23KV榴59線(XB59) 相間RY | FEEDER | [5 empty] | 308 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB59 | 榴五九線(XB59) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0307 |  |  | 2-06-03 |  |  | XB59 | GDA | XB59 接地電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB59_GDA | 23KV榴59線(XB59) 接地RY | FEEDER | [5 empty] | 309 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1520 | 榴中～斗工二路(1520) |  | DS2 | 1522 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0782 | 783 | 0063 | 2-30-14 | 2-30-15 | 1-3F | GL2 | DS (ON) | 1522 DS ON |  |  | B2/D11_A1 | [8 empty] | 榴中DS.1522_DS | 1522(榴中斗工二路) DS | LINE161 | [5 empty] | 310 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D11 | 榴中DS | 22 | 22kV | XB60 | 榴六十線(XB60) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0310 |  |  | 2-06-06 |  |  | XB60 | PHA | XB60 相間電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB60_PHA | 23KV榴60線(XB60) 相間RY | FEEDER | [5 empty] | 311 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB60 | 榴六十線(XB60) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0311 |  |  | 2-06-07 |  |  | XB60 | GDA | XB60 接地電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB60_GDA | 23KV榴60線(XB60) 接地RY | FEEDER | [5 empty] | 312 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1520 | 榴中～斗工二路(1520) |  | DS3 | 1523 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0784 | 785 | 0064 | 2-31-00 | 2-31-01 | 1-40 | GL2 | DS (ON) | 1523 DS ON |  |  | B2/D11_A1 | [8 empty] | 榴中DS.1523_DS | 1523(榴中斗工二路) DS | LINE161 | [5 empty] | 313 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D11 | 榴中DS | 22 | 22kV | 490 | #2SSTR(490) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0314 |  |  | 2-07-02 |  |  | 490 | PHA | 490 相間電驛(動作/正常) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.#2SSTR_51A | #2SSTR 51RY | OTHER | [5 empty] | 314 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | 490 | #2SSTR(490) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0315 |  |  | 2-07-03 |  |  | 490 | GDA | 490 接地電驛(動作/正常) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | [5 empty] | 315 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1520 | 榴中～斗工二路(1520) |  | ES3 | 1523E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0786 | 787 | 0065 | 2-31-02 | 2-31-03 | 1-41 | GL2 | ES (ON) | 1523E ES ON |  |  | B2/D11_A1 | [8 empty] | 榴中DS.1523E_ES | 1523E(榴中斗工二路) ES | LINE161 | [5 empty] | 316 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D11 | 榴中DS | 11 | 11kV | 230 | #3SC(230) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0320 |  |  | 2-08-00 |  |  | 230 | SCA | 230 相間及接地電驛(動作/正常) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.230_SCA | 11KV #3SC 51,51N RY | SC | [5 empty] | 317 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | 230 | #3SC(230) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0321 |  |  | 2-08-01 |  |  | 230 | 4AUVA | 230 欠壓電驛(動作/正常) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | [5 empty] | 318 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/1DTR |  | 0120 |  | 0116 | 1-0F-00 |  | 1-74 | GT1 | 52AS | 1750 CB (ON/OFF) |  | aabb | ELEM/D11_A1 | [8 empty] | 榴中DS.1750_CB | 1750(#1DTR) CB | MTR | [5 empty] | 319 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB21 | 榴一線(XB21) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0323 |  |  | 2-08-03 |  |  | XB21 | PHA | XB21 相間電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB21_PHA | 11KV榴ㄧ線(XB21) 相間RY | FEEDER | [5 empty] | 320 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | XB21 | 榴一線(XB21) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0324 |  |  | 2-08-04 |  |  | XB21 | GDA | XB21 接地電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB21_GDA | 11KV榴ㄧ線(XB21) 接地RY | FEEDER | [5 empty] | 321 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0868 | 869 | 0117 | 2-36-04 | 2-36-05 | 1-75 | GT1 | DS (ON) | 1751 DS ON |  |  | B2/D11_A1 | [8 empty] | 榴中DS.1751_DS | 1751(#1DTR) DS | MTR | [5 empty] | 322 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D11 | 榴中DS | 11 | 11kV | XB22 | 榴二線(XB22) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0327 |  |  | 2-08-07 |  |  | XB22 | PHA | XB22 相間電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB22_PHA | 11KV榴二線(XB22) 相間RY | FEEDER | [5 empty] | 323 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | XB22 | 榴二線(XB22) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0328 |  |  | 2-09-00 |  |  | XB22 | GDA | XB22 接地電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB22_GDA | 11KV榴二線(XB22) 接地RY | FEEDER | [5 empty] | 324 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0870 | 871 | 0118 | 2-36-06 | 2-36-07 | 1-76 | GT1 | DS (ON) | 1752 DS ON |  |  | B2/D11_A1 | [8 empty] | 榴中DS.1752_DS | 1752(#1DTR) DS | MTR | [5 empty] | 325 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D11 | 榴中DS | 11 | 11kV | XB23 | 榴三線(XB23) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0331 |  |  | 2-09-03 |  |  | XB23 | PHA | XB23 相間電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB23_PHA | 11KV榴三線(XB23) 相間RY | FEEDER | [5 empty] | 326 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | XB23 | 榴三線(XB23) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0332 |  |  | 2-09-04 |  |  | XB23 | GDA | XB23 接地電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB23_GDA | 11KV榴三線(XB23) 接地RY | FEEDER | [5 empty] | 327 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2DTR |  | 0121 |  | 0119 | 1-0F-01 |  | 1-77 | GT2 | 52AS | 1760 CB (ON/OFF) |  | aafb | ELEM/D11_A1 | [8 empty] | 榴中DS.1760_CB | 1760(#2DTR) CB | MTR | [5 empty] | 328 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB24 | 榴四線(XB24) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0335 |  |  | 2-09-07 |  |  | XB24 | PHA | XB24 相間電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB24_PHA | 11KV榴四線(XB24) 相間RY | FEEDER | [5 empty] | 329 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | XB24 | 榴四線(XB24) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0336 |  |  | 2-0A-00 |  |  | XB24 | GDA | XB24 接地電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB24_GDA | 11KV榴四線(XB24) 接地RY | FEEDER | [5 empty] | 330 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0872 | 873 | 0120 | 2-36-08 | 2-36-09 | 1-78 | GT2 | DS (ON) | 1761 DS ON |  |  | B2/D11_A1 | [8 empty] | 榴中DS.1761_DS | 1761(#2DTR) DS | MTR | [5 empty] | 331 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D11 | 榴中DS | 11 | 11kV | XB25 | 榴五線(XB25) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0339 |  |  | 2-0A-03 |  |  | XB25 | PHA | XB25 相間電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB25_PHA | 11KV榴五線(XB25) 相間RY | FEEDER | [5 empty] | 332 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | XB25 | 榴五線(XB25) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0340 |  |  | 2-0A-04 |  |  | XB25 | GDA | XB25 接地電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB25_GDA | 11KV榴五線(XB25) 接地RY | FEEDER | [5 empty] | 333 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0874 | 875 | 0121 | 2-36-10 | 2-36-11 | 1-79 | GT2 | DS (ON) | 1762 DS ON |  |  | B2/D11_A1 | [8 empty] | 榴中DS.1762_DS | 1762(#2DTR) DS | MTR | [5 empty] | 334 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D11 | 榴中DS | 22 | 22kV | 200 | TIE(200) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0343 |  |  | 2-0A-07 |  |  | 200 | PHA | 200 相間電驛(動作/正常) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.200_51A | 23KV TIE(200) 51RY | TIE | [5 empty] | 335 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | 200 | TIE(200) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0344 |  |  | 2-0B-00 |  |  | 200 | GDA | 200 接地電驛(動作/正常) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.200_51NA | 23KV TIE(200) 51N RY | TIE | [5 empty] | 336 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | LBS210 | #1SC(210) |  | LBS |  | Element | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/210 | C/1SC(B) |  |  | 0878 | 879 | 0124 | 2-36-14 | 2-36-15 | 1-7C | 210 | CB(ON) | 210 LBS ON |  |  | B3/D11_A1 | [8 empty] | 榴中DS.210_LBS | 210(11KV #1SC) LBS | SC | [5 empty] | 337 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D11 | 榴中DS | 22 | 22kV | 240 | #4SC(240) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0349 |  |  | 2-0B-05 |  |  | 240 | SCA | 240 相間及接地電驛(動作/正常) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.240_SCA | 23KV #4SC 51,51N RY | SC | [5 empty] | 338 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | 240 | #4SC(240) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0350 |  |  | 2-0B-06 |  |  | 240 | 3BUVA | 240 欠壓電驛(動作/正常) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.240_UVA | 23KV #4SC 27RY(欠壓) | SC | [5 empty] | 339 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | LBS230 | #3SC(230) |  | LBS |  | Element | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/230 | C/3SC(B) |  |  | 0880 | 881 | 0125 | 2-37-00 | 2-37-01 | 1-7D | 230 | CB(ON) | 230 LBS ON |  |  | B3/D11_A1 | [8 empty] | 榴中DS.230_LBS | 230(11KV #3SC) LBS | SC | [5 empty] | 340 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D11 | 榴中DS | 11 | 11kV | XB26 | 榴六線(XB26) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0352 |  |  | 2-0C-00 |  |  | XB26 | PHA | XB26 相間電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB26_PHA | 11KV榴六線(XB26) 相間RY | FEEDER | [5 empty] | 341 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | XB26 | 榴六線(XB26) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0353 |  |  | 2-0C-01 |  |  | XB26 | GDA | XB26 接地電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB26_GDA | 11KV榴六線(XB26) 接地RY | FEEDER | [5 empty] | 342 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | 390 | #1SSTR(390) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | T/1SSTR |  |  | 0258 |  | 0128 | 2-00-02 |  | 2-00 | 390 | 52AS | 390 CB (ON/OFF) |  | aabb | B3/D11_A1 | [8 empty] | 榴中DS.390_CB | 390(#1SSTR) CB | OTHER | [5 empty] | 343 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB27 | 榴七線(XB27) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0356 |  |  | 2-0C-04 |  |  | XB27 | PHA | XB27 相間電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB27_PHA | 11KV榴七線(XB27) 相間RY | FEEDER | [5 empty] | 344 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | XB27 | 榴七線(XB27) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0357 |  |  | 2-0C-05 |  |  | XB27 | GDA | XB27 接地電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB27_GDA | 11KV榴七線(XB27) 接地RY | FEEDER | [5 empty] | 345 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | T/1DTR(A) |  |  | 0123 |  | 0129 | 1-0F-03 |  | 2-01 | 310 | 52AS | 310 CB (ON/OFF) |  | aaaa | ELEM/D11_A1 | [8 empty] | 榴中DS.310_CB | 310(#1DTR) CB | MTR | [5 empty] | 346 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB28 | 榴八線(XB28) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0360 |  |  | 2-0D-00 |  |  | XB28 | PHA | XB28 相間電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB28_PHA | 11KV榴八線(XB28) 相間RY | FEEDER | [5 empty] | 347 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | XB28 | 榴八線(XB28) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0361 |  |  | 2-0D-01 |  |  | XB28 | GDA | XB28 接地電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB28_GDA | 11KV榴八線(XB28) 接地RY | FEEDER | [5 empty] | 348 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | 210 | #1SC(210) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | A/LBS210^C/1SC(A) |  |  | 0264 |  | 0130 | 2-01-00 |  | 2-02 | 210 | 52AS | 210 CB (ON/OFF) |  | aadb | B3/D11_A1 | [8 empty] | 榴中DS.210_CB | 210(11KV #1SC) CB | SC | [5 empty] | 349 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB29 | 榴九線(XB29) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0364 |  |  | 2-0D-04 |  |  | XB29 | PHA | XB29 相間電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB29_PHA | 11KV榴九線(XB29) 相間RY | FEEDER | [5 empty] | 350 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | XB29 | 榴九線(XB29) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0365 |  |  | 2-0D-05 |  |  | XB29 | GDA | XB29 接地電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB29_GDA | 11KV榴九線(XB29) 接地RY | FEEDER | [5 empty] | 351 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB51 | 榴五一線(XB51) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/XB51/T1 |  |  | 0268 |  | 0131 | 2-01-04 |  | 2-03 | XB51 | 52AS | XB51 CB (ON/OFF) |  | badb | B2/D11_D1 | [8 empty] | 榴中DS.XB51_CB | XB51(23KV榴51線) CB | FEEDER | [5 empty] | 352 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB30 | 榴十線(XB30) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0368 |  |  | 2-0E-00 |  |  | XB30 | PHA | XB30 相間電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB30_PHA | 11KV榴十線(XB30) 相間RY | FEEDER | [5 empty] | 353 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | XB30 | 榴十線(XB30) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0369 |  |  | 2-0E-01 |  |  | XB30 | GDA | XB30 接地電驛(動作/正常) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB30_GDA | 11KV榴十線(XB30) 接地RY | FEEDER | [5 empty] | 354 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB51 | 榴五一線(XB51) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0660 |  | 0132 | 1-39-04 |  | 2-04 | XB51 | 79S | XB51復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB51_79UL | 23KV榴51線(XB51) 79RY U/L | FEEDER | [5 empty] | 355 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D11 | 榴中DS | 0 |  | ComPoint |  |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0372 |  |  | 2-0E-04 |  |  | ------ | 2 RCA | 11/23KV 79電驛動作警報(動作/正常) (COMMON) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.23KV_RCA | 11/23KV 饋線 79RY復閉動作 | OTHER | [5 empty] | 356 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0373 |  |  | 2-0E-05 |  |  | 310 | 81A | 310 低頻電驛動作 |  |  | ELEM/D11_A1 | [8 empty] | 榴中DS.81RY_A/S(1) | 310低頻電驛動作/復歸 | OTHER | [5 empty] | 357 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
D11 | 榴中DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0374 |  |  | 2-0E-06 |  |  | 320 | 81A | 320 低頻電驛動作 |  |  | ELEM/D11_A1 | [8 empty] | 榴中DS.81RY_A/S(2) | 320低頻電驛動作/復歸 | OTHER | [5 empty] | 358 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
D11 | 榴中DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0375 |  |  | 2-0E-07 |  |  | 330 | 81A | 330 低頻電驛動作 |  |  | ELEM/D11_A1 | [8 empty] | 榴中DS.81RY_A/S(3) | 330低頻電驛動作/復歸 | OTHER | [5 empty] | 359 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
D11 | 榴中DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0376 |  |  | 2-0F-00 |  |  | 340 | 81A | 340 低頻電驛動作 |  |  | ELEM/D11_A1 | [8 empty] | 榴中DS.81RY_A/S(4) | 340低頻電驛動作/復歸 | OTHER | [5 empty] | 360 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
D11 | 榴中DS | 22 | 22kV | XB51 | 榴五一線(XB51) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0661 |  | 0133 | 1-39-05 |  | 2-05 | XB51 | TAPS | XB51 LCO TAP (使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB51_LCO_TAP | 23KV榴51線(XB51) LCO TAP | FEEDER | [5 empty] | 361 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D11 | 榴中DS |  |  | 1DTR | #1DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0513 |  |  | 1-30-01 |  |  | M1 | 1TRA | #1 DTR 重故障警報(動作/正常) |  | a | B1/D11_A1 | [8 empty] | 榴中DS.#1DTR_TRA | #1DTR 重故障 | MTR | [5 empty] | 362 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D11 | 榴中DS |  |  | 1DTR | #1DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0514 |  |  | 1-30-02 |  |  | M1 | 1TRF | #1 DTR 輕故障警報(動作/正常) |  |  | B1/D11_A1 | [8 empty] | 榴中DS.#1DTR_TRF | #1DTR 輕故障 | MTR | [5 empty] | 363 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB52 | 榴五二線(XB52) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/XB52/T1 |  |  | 0272 |  | 0134 | 2-02-00 |  | 2-06 | XB52 | 52AS | XB52 CB (ON/OFF) |  | baeb | B2/D11_D1 | [8 empty] | 榴中DS.XB52_CB | XB52(23KV榴52線) CB | FEEDER | [5 empty] | 364 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | XB52 | 榴五二線(XB52) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0662 |  | 0135 | 1-39-06 |  | 2-07 | XB52 | 79S | XB52復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB52_79UL | 23KV榴52線(XB52) 79RY U/L | FEEDER | [5 empty] | 365 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D11 | 榴中DS |  |  | 1DTR | #1DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0517 |  |  | 1-30-05 |  |  | M1 | 163Q | #1 DTR ULTC 保護電驛警報 |  |  | B1/D11_A1 | [8 empty] | 榴中DS.#1DTR_63Q | #1DTR 63Q RY | MTR | [5 empty] | 366 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D11 | 榴中DS |  |  | 1DTR | #1DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0518 |  |  | 1-30-06 |  |  | M1 | 196D | #1 DTR 放壓電驛警報(動作/正常) |  |  | B1/D11_A1 | [8 empty] | 榴中DS.#1DTR_96D | #1DTR 96D RY | MTR | [5 empty] | 367 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D11 | 榴中DS |  |  | 1DTR | #1DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0519 |  |  | 1-30-07 |  |  | M1 | 196B2 | #1 DTR 撲氣電驛第二段警報(動作/正常) |  |  | B1/D11_A1 | [8 empty] | 榴中DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | [5 empty] | 368 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D11 | 榴中DS |  |  | 1DTR | #1DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0520 |  |  | 1-30-08 |  |  | M1 | 196B1 | #1 DTR 撲氣電驛第一段警報(動作/正常) |  |  | B1/D11_A1 | [8 empty] | 榴中DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | [5 empty] | 369 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D11 | 榴中DS |  |  | 1DTR(A) | #1DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0521 |  |  | 1-30-09 |  |  | M1 | 43RS1 | #1 DTR WIND-A位置(SUP/LOC) |  | c | B1/D11_A1 | [8 empty] | 榴中DS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | [5 empty] | 370 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D11 | 榴中DS |  |  | 1DTR(B) | #1DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0522 |  |  | 1-30-10 |  |  | M1 | 43RS2 | #1 DTR WIND-B位置(SUP/LOC) |  | b | B1/D11_A1 | [8 empty] | 榴中DS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | [5 empty] | 371 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D11 | 榴中DS |  |  | 1DTR | #1DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0523 |  |  | 1-30-11 |  |  | M1 | 196P | #1 DTR 衝擊油壓電驛警報(動作/正常) |  |  | B1/D11_A1 | [8 empty] | 榴中DS.#1DTR_96P | #1DTR 96P RY | MTR | [5 empty] | 372 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D11 | 榴中DS |  |  | 2DTR | #2DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0524 |  |  | 1-30-12 |  |  | M2 | 2TRA | #2 DTR 重故障警報(動作/正常) |  | a | B1/D11_A1 | [8 empty] | 榴中DS.#2DTR_TRA | #2DTR 重故障 | MTR | [5 empty] | 373 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D11 | 榴中DS |  |  | 2DTR | #2DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0525 |  |  | 1-30-13 |  |  | M2 | 2TRF | #2 DTR 輕故障警報(動作/正常) |  |  | B1/D11_A1 | [8 empty] | 榴中DS.#2DTR_TRF | #2DTR 輕故障 | MTR | [5 empty] | 374 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB52 | 榴五二線(XB52) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0663 |  | 0136 | 1-39-07 |  | 2-08 | XB52 | TAPS | XB52 LCO TAP (使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB52_LCO_TAP | 23KV榴52線(XB52) LCO TAP | FEEDER | [5 empty] | 375 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D11 | 榴中DS | 22 | 22kV | XB53 | 榴五三線(XB53) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/XB53/T1 |  |  | 0276 |  | 0137 | 2-02-04 |  | 2-09 | XB53 | 52AS | XB53 CB (ON/OFF) |  | bafb | B2/D11_D1 | [8 empty] | 榴中DS.XB53_CB | XB53(23KV榴53線) CB | FEEDER | [5 empty] | 376 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS |  |  | 2DTR | #2DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0528 |  |  | 1-31-00 |  |  | M2 | 263Q | #2 DTR ULTC 保護電驛警報 |  |  | B1/D11_A1 | [8 empty] | 榴中DS.#2DTR_63Q | #2DTR 63Q RY | MTR | [5 empty] | 377 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D11 | 榴中DS |  |  | 2DTR | #2DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0529 |  |  | 1-31-01 |  |  | M2 | 296D | #2 DTR 放壓電驛警報(動作/正常) |  |  | B1/D11_A1 | [8 empty] | 榴中DS.#2DTR_96D | #2DTR 96D RY | MTR | [5 empty] | 378 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D11 | 榴中DS |  |  | 2DTR | #2DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0530 |  |  | 1-31-02 |  |  | M2 | 296B2 | #2 DTR 撲氣電驛第二段警報(動作/正常) |  |  | B1/D11_A1 | [8 empty] | 榴中DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | [5 empty] | 379 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D11 | 榴中DS |  |  | 2DTR | #2DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0531 |  |  | 1-31-03 |  |  | M2 | 296B1 | #2 DTR 撲氣電驛第一段警報(動作/正常) |  |  | B1/D11_A1 | [8 empty] | 榴中DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | [5 empty] | 380 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D11 | 榴中DS |  |  | 2DTR(A) | #2DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0532 |  |  | 1-31-04 |  |  | M2 | 243RS1 | #2 DTR WIND-A 位置(SUP/LOC) |  | c | B1/D11_A1 | [8 empty] | 榴中DS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | [5 empty] | 381 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D11 | 榴中DS |  |  | 2DTR(B) | #2DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0533 |  |  | 1-31-05 |  |  | M2 | 243RS2 | #2 DTR WIND-B 位置(SUP/LOC) |  | b | B1/D11_A1 | [8 empty] | 榴中DS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | [5 empty] | 382 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D11 | 榴中DS |  |  | 2DTR | #2DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0534 |  |  | 1-31-06 |  |  | M2 | 296P | #2 DTR 衝擊油壓電驛警報(動作/正常) |  |  | B1/D11_A1 | [8 empty] | 榴中DS.#2DTR_96P | #2DTR 96P RY | MTR | [5 empty] | 383 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | ComPoint |  |  | OLTC_A |  |  | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0535 |  |  | 1-31-07 |  |  | ------ | OLTCA | OLTC 15分鐘內連動3次警報 |  |  | B3/D11_A1 | [8 empty] | 榴中DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | [5 empty] | 384 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB53 | 榴五三線(XB53) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0664 |  | 0138 | 1-39-08 |  | 2-0A | XB53 | 79S | XB53復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB53_79UL | 23KV榴53線(XB53) 79RY U/L | FEEDER | [5 empty] | 385 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D11 | 榴中DS | 22 | 22kV | XB53 | 榴五三線(XB53) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0665 |  | 0139 | 1-39-09 |  | 2-0B | XB53 | TAPS | XB53 LCO TAP (使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB53_LCO_TAP | 23KV榴53線(XB53) LCO TAP | FEEDER | [5 empty] | 386 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D11 | 榴中DS | 22 | 22kV | XB54 | 榴五四線(XB54) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/XB54/T1 |  |  | 0280 |  | 0140 | 2-03-00 |  | 2-0C | XB54 | 52AS | XB54 CB (ON/OFF) |  | bagb | B2/D11_D1 | [8 empty] | 榴中DS.XB54_CB | XB54(23KV榴54線) CB | FEEDER | [5 empty] | 387 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | XB54 | 榴五四線(XB54) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0666 |  | 0141 | 1-39-10 |  | 2-0D | XB54 | 79S | XB54復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB54_79UL | 23KV榴54線(XB54) 79RY U/L | FEEDER | [5 empty] | 388 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D11 | 榴中DS | 161 | 161kV | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0559 |  |  | 1-32-15 |  |  | M5 | OSCF | OSC故障警報(動作/正常) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.161KV_OSCF | 161KV示波器故障 | OTHER | [5 empty] | 389 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1510 | 榴中～斗工一路(1510) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0561 |  |  | 1-33-01 |  |  | M5 | 1RYA | 1510 RYA |  |  | B2/D11_A1 | [8 empty] | 榴中DS.1510_RYA | 榴中斗工一路(1510)數位電驛故障 | OTHER | [5 empty] | 390 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1520 | 榴中～斗工二路(1520) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0562 |  |  | 1-33-02 |  |  | M6 | 2RYA | 1520 RYA |  |  | B2/D11_A1 | [8 empty] | 榴中DS.1520_RYA | 榴中斗工二路(1520)數位電驛故障 | OTHER | [5 empty] | 391 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D11 | 榴中DS |  |  | 1DTR | #1DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0589 |  |  | 1-34-13 |  |  | R1 | 187S | #1 DTR 差動電驛鎖開關(使用/閉鎖) |  |  | B1/D11_A1 | [8 empty] | 榴中DS.#1DTR_87UL | #1DTR 87RY U/L | MTR | [5 empty] | 392 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D11 | 榴中DS |  |  | 2DTR | #2DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0590 |  |  | 1-34-14 |  |  | R2 | 287S | #2 DTR 差動電驛鎖開關(使用/閉鎖) |  |  | B1/D11_A1 | [8 empty] | 榴中DS.#2DTR_87UL | #2DTR 87RY U/L | MTR | [5 empty] | 393 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D11 | 榴中DS | 161 | 161kV | ComPoint |  |  | BUS_RYFA |  |  | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0591 |  |  | 1-34-15 |  |  | ------ | RYFA | 161KV BUS數位電驛故障 |  |  | B3/D11_A1 | [8 empty] | 榴中DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | [5 empty] | 394 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | ComPoint |  |  | 12B_CTFA | BUS_87CTFA | Element | Status | #1#2 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0592 |  |  | 1-35-00 |  |  | ------ | 87CTFA | 161KV BUS 87RY CT 迴路故障 |  |  | B3/D11_A1 | [8 empty] | 榴中DS.161KV_BUS_CTFA | 161KV BUS 87RY CT回路故障 | OTHER | [5 empty] | 395 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB54 | 榴五四線(XB54) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0667 |  | 0142 | 1-39-11 |  | 2-0E | XB54 | TAPS | XB54 LCO TAP (使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB54_LCO_TAP | 23KV榴54線(XB54) LCO TAP | FEEDER | [5 empty] | 396 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D11 | 榴中DS | 22 | 22kV | XB55 | 榴五五線(XB55) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/XB55/T1 |  |  | 0284 |  | 0143 | 2-03-04 |  | 2-0F | XB55 | 52AS | XB55 CB (ON/OFF) |  | bahb | B2/D11_D1 | [8 empty] | 榴中DS.XB55_CB | XB55(23KV榴55線) CB | FEEDER | [5 empty] | 397 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | ComPoint |  |  | FDR_60A |  |  | Status | 11/22kV電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0596 |  |  | 1-35-04 |  |  | M5 | 60A | 11/23KV SC 60電驛(動作/正常) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.23KV_SC_60A | 11/23KV SC 60A | OTHER | [5 empty] | 398 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0597 |  |  | 1-35-05 |  |  | M6 | CBA | 161KV GIS 重故障 |  |  | B3/D11_A1 | [8 empty] | 榴中DS.161KV_CBA | 161KV斷路器重故障 | OTHER | [5 empty] | 399 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0598 |  |  | 1-35-06 |  |  | M6 | CBF | 161KV GIS 輕故障 |  |  | B3/D11_A1 | [8 empty] | 榴中DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | [5 empty] | 400 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1510 | 榴中～斗工一路(1510) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0599 |  |  | 1-35-07 |  |  | M5 | 1RAOA | 1510 斗工一路通訊頻道故障(動作/正常) |  |  | B2/D11_A1 | [8 empty] | 榴中DS.1510_87LCFA | 榴中斗工一路(1510) 87L通訊故障 | OTHER | [5 empty] | 401 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1520 | 榴中～斗工二路(1520) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0600 |  |  | 1-35-08 |  |  | M5 | 2RAOA | 1520 斗工二路通訊頻道故障(動作/正常) |  |  | B2/D11_A1 | [8 empty] | 榴中DS.1520_87LCFA | 榴中斗工二路(1520) 87L通訊故障 | OTHER | [5 empty] | 402 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0612 |  |  | 1-36-04 |  |  | R5 | 50SA | 161 TIE 瞬時電驛警報 |  |  | B2/D11_A1 | [8 empty] | 榴中DS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | [5 empty] | 403 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Test | Test | 1 |  |  | TEST/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0613 |  |  | 1-36-05 |  |  | M5 | CHG1 | 充電機設備用警報 |  |  | B3/D11_A1 | [8 empty] | 榴中DS.直流充電機故障 | 變電所直流充電機故障 | OTHER | [5 empty] | 404 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0614 |  |  | 1-36-06 |  |  | M5 | CHG2 | 充電機通訊用警報 |  |  | B3/D11_A1 | [8 empty] | 榴中DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | [5 empty] | 405 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0615 |  |  | 1-36-07 |  |  | M5 | DCE | D.C接地警報 |  |  | ELEM/D11_A1 | [8 empty] | 榴中DS.直流電源DCE | 直流電源接地故障警報 | OTHER | [5 empty] | 406 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0616 |  |  | 1-36-08 |  |  | 直流電源盤 | DCA | 直流NFB跳脫警報 |  |  | ELEM/D11_A1 | [8 empty] | 榴中DS.直流電源DCA | 直流電源故障警報 | OTHER | [5 empty] | 407 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | Door1 | 控制室及大門 |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0617 |  |  | 1-36-09 |  |  | 保全控制盤 | DOR | 控制室及大門開啟警報 |  |  | B3/D11_A1 | [8 empty] | 榴中DS.無人化門禁(1) | 無人化門禁(1)建築物,控制室大門 | OTHER | [5 empty] | 408 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | Fire1 | 受信總機 |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0618 |  |  | 1-36-10 |  |  | 火災警報(1) | FIR | 火災警報(1)受信總機 |  |  | B3/D11_A1 | [8 empty] | 榴中DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | [5 empty] | 409 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0619 |  |  | 1-36-11 |  |  | 390&490盤 | STUV | 所內變壓器欠壓警報 |  |  | ELEM/D11_A1 | [8 empty] | 榴中DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | [5 empty] | 410 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB55 | 榴五五線(XB55) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0668 |  | 0144 | 1-39-12 |  | 2-10 | XB55 | 79S | XB55復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB55_79UL | 23KV榴55線(XB55) 79RY U/L | FEEDER | [5 empty] | 411 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | MCC |  |  | Status | MCC電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0621 |  |  | 1-36-13 |  |  | ------ | ------ | MCC IED ALARM |  |  | B3/D11_A1 | [8 empty] | 榴中DS.MCC故障 | MCC電驛故障 | OTHER | [5 empty] | 412 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | PMCC |  |  | Status | PMCC電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0622 |  |  | 1-36-14 |  |  | ------ | ------ | PMCC IED ALARM |  |  | B3/D11_A1 | [8 empty] | 榴中DS.PMCC故障 | PMCC電驛故障 | OTHER | [5 empty] | 413 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0623 |  |  | 1-36-15 |  |  | 通訊盤 | ACF | 通訊設備AC故障 |  |  | B3/D11_A1 | [8 empty] | 榴中DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | [5 empty] | 414 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | R_Temp | 通訊室或控制室 |  | Status | 溫度警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0624 |  |  | 1-37-00 |  |  | 通訊盤 |  | 通訊室或控制室溫度警報 |  |  | B3/D11_A1 | [8 empty] | 榴中DS.通信機房溫度 | 通訊室或控制室溫度警報 | OTHER | [5 empty] | 415 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | Gateway1 |  |  | Status | Gateway 1故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0625 |  |  | 1-37-01 |  |  | 通訊盤 | OLMa | 通訊設備光纖主故障 |  |  | B3/D11_A1 | [16 empty] | 416 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | Gateway2 |  |  | Status | Gateway 2故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0626 |  |  | 1-37-02 |  |  | 通訊盤 | OLMi | 通訊設備光纖次故障 |  |  | B3/D11_A1 | [16 empty] | 417 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | Burglar1 | 保全動作警報 |  | Status | 無人化防盜1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0627 |  |  | 1-37-03 |  |  | 保全防盜箱 | ------ | 無人化防盜(1) 保全動作警報 |  |  | B3/D11_A1 | [8 empty] | 榴中DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | [5 empty] | 418 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0628 |  |  | 1-37-04 |  |  | M5 | VUA1 | 一號匯流排欠壓電驛(動作/正常) |  |  | B2/D11_A1 | [8 empty] | 榴中DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | [5 empty] | 419 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0629 |  |  | 1-37-05 |  |  | M5 | VUA2 | 二號匯流排欠壓電驛(動作/正常) |  |  | B2/D11_A1 | [8 empty] | 榴中DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | [5 empty] | 420 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | 1A5Other | 排水泵故障1 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0630 |  |  | 1-37-06 |  |  | ------ | PUPA1 | 揚水泵故障 |  |  | B3/D11_A1 | [8 empty] | 榴中DS.揚水幫浦 | 揚水幫浦故障 | OTHER | [5 empty] | 421 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | 2A5Other | 排水泵故障2_涵洞1 | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0631 |  |  | 1-37-07 |  |  | ------ | PUPA2 | 涵洞1排水汞故障 |  |  | B3/D11_A1 | [8 empty] | 榴中DS.涵洞排水泵(1) | 涵洞排水幫浦故障(1) | OTHER | [5 empty] | 422 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | 3A5Other | 排水泵故障3_涵洞2 | Element | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0632 |  |  | 1-37-08 |  |  | ------ | PUPA3 | 涵洞2排水汞故障 |  |  | B3/D11_A1 | [8 empty] | 榴中DS.涵洞排水泵(2) | 涵洞排水幫浦故障(2) | OTHER | [5 empty] | 423 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | 4A5Other | 排水泵故障4_涵洞3 | Element | Status | 警報等級5動作4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0633 |  |  | 1-37-09 |  |  | ------ | PUPA4 | 涵洞3排水汞故障 |  |  | B3/D11_A1 | [8 empty] | 榴中DS.涵洞排水泵(3) | 涵洞排水幫浦故障(3) | OTHER | [5 empty] | 424 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | Water1 |  |  | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0634 |  |  | 1-37-10 |  |  | M5 | WP-1 | 地下室淹水警報(第一段) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.水位警報(1) | 地下室水位警報(1) | OTHER | [5 empty] | 425 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | Water2 |  |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0635 |  |  | 1-37-11 |  |  | M5 | WP-2 | 地下室淹水警報(第二段) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.水位警報(2) | 地下室水位警報(2) | OTHER | [5 empty] | 426 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB55 | 榴五五線(XB55) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0669 |  | 0145 | 1-39-13 |  | 2-11 | XB55 | TAPS | XB55 LCO TAP (使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB55_LCO_TAP | 23KV榴55線(XB55) LCO TAP | FEEDER | [5 empty] | 427 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D11 | 榴中DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | T/1DTR(B) |  |  | 0126 |  | 0146 | 1-0F-06 |  | 2-23 | 320 | 52AS | 320 CB (ON/OFF) |  | baaa | ELEM/D11_A1 | [8 empty] | 榴中DS.320_CB | 320(#1DTR) CB | MTR | [5 empty] | 428 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | 220 | #2SC(220) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | C/2SC |  |  | 0293 |  | 0147 | 2-04-05 |  | 2-12 | 220 | 52AS | 220 CB (ON/OFF) |  | bacb | B3/D11_A1 | [8 empty] | 榴中DS.220_CB | 220(23KV #2SC) CB | SC | [5 empty] | 429 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | SCADAA |  |  | Status | LocalSCADA故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0639 |  |  | 1-37-15 |  |  | 監控主機 | ------ | 所內SCADA故障 |  |  | B3/D11_A1 | [8 empty] | 榴中DS.SCADA故障 | LOCAL SCADA故障 | OTHER | [5 empty] | 430 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | Comm_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0641 |  |  | 1-38-01 |  |  | 通訊處理單元 | ------ | 通訊處理單元LOCAL/REMOTE |  |  | B3/D11_A1 | [8 empty] | 榴中DS.COMM_S/L | 通訊處理單元 SUPY/LOCAL | OTHER | [5 empty] | 431 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Rem | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | PMCC_R_L | PMCC Remote/Local | Element | Status | 警報等級5動作7 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0642 |  |  | 1-38-02 |  |  | ------ | ------ | MCC IED LOCAL/REMOTE |  |  | B3/D11_A1 | [8 empty] | 榴中DS.MCC_IED_S/L | 161KV IED SUPY/LOCAL | OTHER | [5 empty] | 432 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | PMCC_R_L |  |  | Status | PMCC Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0643 |  |  | 1-38-03 |  |  | ------ | ------ | PMCC IED LOCAL/REMOTE |  |  | B3/D11_A1 | [8 empty] | 榴中DS.PMCC_IED_S/L | 11/23KV IED SUPY/LOCAL | OTHER | [5 empty] | 433 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Rem | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D11 | 榴中DS | 0 |  | ComPoint |  |  | FDR_CBA |  |  | Status | 11/22kV斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0645 |  |  | 1-38-05 |  |  | ------ | 22 CBA | 11 & 23KV GIS 重故障 |  |  | ELEM/D11_D1 | [8 empty] | 榴中DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | [5 empty] | 434 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | ComPoint |  |  | FDR_CBF |  |  | Status | 11/22kV斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0646 |  |  | 1-38-06 |  |  | ------ | 22 CBF | 11 & 23KV GIS 輕故障 |  |  | ELEM/D11_D1 | [8 empty] | 榴中DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | [5 empty] | 435 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | ComPoint |  |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0647 |  |  | 1-38-07 |  |  | ------ | LOA | 11 & 23KV GIS自動復閉閉鎖警報(動作/正常) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.11/23KV_LOA | 11/23KV饋線復閉失敗閉鎖 | OTHER | [5 empty] | 436 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0648 |  |  | 1-38-08 |  |  | ------ | ACBA | 所內AC電源用ACB(故障警報) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.所內電源ACBA | 所內電源故障警報 | OTHER | [5 empty] | 437 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | OilLeak1 |  |  | Status | 洩油池水位警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0650 |  |  | 1-38-10 |  |  | M5 | OW-1 | 集油池警報(第一段) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.洩油池警報(1) | 洩油池水位警報(1) | OTHER | [5 empty] | 438 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | OilLeak2 |  |  | Status | 洩油池水位警報2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0651 |  |  | 1-38-11 |  |  | M5 | OW-2 | 集油池警報(第二段) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.洩油池警報(2) | 洩油池水位警報(2) | OTHER | [5 empty] | 439 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | 5A5Other | 排水泵故障5_涵洞4 | Element | Status | 警報等級5動作5 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0652 |  |  | 1-38-12 |  |  | M5 | PUPA5 | 涵洞4排水汞故障 |  |  | B3/D11_A1 | [16 empty] | 440 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | GEN | 緊急發電機運轉 | Element | Status | 警報等級5動作6 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0653 |  |  | 1-38-13 |  |  | ------ | ------ | 緊急發電機運轉 |  |  | B3/D11_A1 | [8 empty] | 榴中DS.GEN | 緊急發電機運轉 | OTHER | [5 empty] | 441 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ON/OFF | OFF
D11 | 榴中DS | 22 | 22kV | XB56 | 榴五六線(XB56) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/XB56/T1 |  |  | 0297 |  | 0148 | 2-05-01 |  | 2-13 | XB56 | 52AS | XB56 CB (ON/OFF) |  | bbbb | B2/D11_D1 | [8 empty] | 榴中DS.XB56_CB | XB56(23KV榴56線) CB | FEEDER | [5 empty] | 442 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | XB56 | 榴五六線(XB56) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0670 |  | 0149 | 1-39-14 |  | 2-14 | XB56 | 79S | 榴五六線XB56復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB56_79UL | 23KV榴56線(XB56) 79RY U/L | FEEDER | [5 empty] | 443 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D11 | 榴中DS | 22 | 22kV | XB56 | 榴五六線(XB56) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0671 |  | 0150 | 1-39-15 |  | 2-15 | XB56 | TAPS | 榴五六線XB56 LCO TAP (使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB56_LCO_TAP | 23KV榴56線(XB56) LCO TAP | FEEDER | [5 empty] | 444 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D11 | 榴中DS | 22 | 22kV | XB57 | 榴五七線(XB57) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/XB57/T1 |  |  | 0301 |  | 0151 | 2-05-05 |  | 2-16 | XB57 | 52AS | XB57 CB (ON/OFF) |  | bbcb | B2/D11_D1 | [8 empty] | 榴中DS.XB57_CB | XB57(23KV榴57線) CB | FEEDER | [5 empty] | 445 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | XB57 | 榴五七線(XB57) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0672 |  | 0152 | 1-3A-00 |  | 2-17 | XB57 | 79S | 榴五七線XB57復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB57_79UL | 23KV榴57線(XB57) 79RY U/L | FEEDER | [5 empty] | 446 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D11 | 榴中DS | 22 | 22kV | XB57 | 榴五七線(XB57) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0673 |  | 0153 | 1-3A-01 |  | 2-18 | XB57 | TAPS | 榴五七線XB57 LCO TAP (使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB57_LCO_TAP | 23KV榴57線(XB57) LCO TAP | FEEDER | [5 empty] | 447 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D11 | 榴中DS | 22 | 22kV | XB58 | 榴五八線(XB58) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/XB58/T1 |  |  | 0305 |  | 0154 | 2-06-01 |  | 2-19 | XB58 | 52AS | 榴五八線XB58 CB (ON/OFF) |  | bbdb | B2/D11_D1 | [8 empty] | 榴中DS.XB58_CB | XB58(23KV榴58線) CB | FEEDER | [5 empty] | 448 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | XB58 | 榴五八線(XB58) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0674 |  | 0155 | 1-3A-02 |  | 2-1A | XB58 | 79S | 榴五八線XB58復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB58_79UL | 23KV榴58線(XB58) 79RY U/L | FEEDER | [5 empty] | 449 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D11 | 榴中DS | 22 | 22kV | XB58 | 榴五八線(XB58) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0675 |  | 0156 | 1-3A-03 |  | 2-1B | XB58 | TAPS | 榴五八線XB58 LCO TAP (使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB58_LCO_TAP | 23KV榴58線(XB58) LCO TAP | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D11 | 榴中DS | 22 | 22kV | XB59 | 榴五九線(XB59) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/XB59/T1 |  |  | 0309 |  | 0157 | 2-06-05 |  | 2-1C | XB59 | 52AS | XB59 CB (ON/OFF) |  | bbeb | B2/D11_D1 | [8 empty] | 榴中DS.XB59_CB | XB59(23KV榴59線) CB | FEEDER | [5 empty] | 451 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | XB59 | 榴五九線(XB59) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0676 |  | 0158 | 1-3A-04 |  | 2-1D | XB59 | 79S | XB59復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB59_79UL | 23KV榴59線(XB59) 79RY U/L | FEEDER | [5 empty] | 452 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D11 | 榴中DS | 22 | 22kV | XB59 | 榴五九線(XB59) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0677 |  | 0159 | 1-3A-05 |  | 2-1E | XB59 | TAPS | XB59 LCO TAP (使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB59_LCO_TAP | 23KV榴59線(XB59) LCO TAP | FEEDER | [5 empty] | 453 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D11 | 榴中DS | 22 | 22kV | XB60 | 榴六十線(XB60) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/XB60/T1 |  |  | 0313 |  | 0160 | 2-07-01 |  | 2-1F | XB60 | 52AS | XB60 CB (ON/OFF) |  | bbfb | B2/D11_D1 | [8 empty] | 榴中DS.XB60_CB | XB60(23KV榴60線) CB | FEEDER | [5 empty] | 454 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | XB60 | 榴六十線(XB60) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0678 |  | 0161 | 1-3A-06 |  | 2-20 | XB60 | 79S | XB60復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB60_79UL | 23KV榴60線(XB60) 79RY U/L | FEEDER | [5 empty] | 455 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D11 | 榴中DS | 22 | 22kV | XB60 | 榴六十線(XB60) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0679 |  | 0162 | 1-3A-07 |  | 2-21 | XB60 | TAPS | XB60 LCO TAP (使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB60_LCO_TAP | 23KV榴60線(XB60) LCO TAP | FEEDER | [5 empty] | 456 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D11 | 榴中DS | 11 | 11kV | 100 | TIE(100) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/2ABus | B/1ABus |  |  | 0287 |  | 0163 | 2-03-07 |  | 2-22 | 100 | 52AS | 100 CB (ON/OFF) |  | abab | B3/D11_A1 | [8 empty] | 榴中DS.100_CB | 100(TIE) CB | TIE | [5 empty] | 457 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 22 | 22kV | 490 | #2SSTR(490) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | T/2SSTR |  |  | 0316 |  | 0164 | 2-07-04 |  | 2-47 | 490 | 52AS | 490 CB (ON/OFF) |  | bbib | B3/D11_A1 | [8 empty] | 榴中DS.490_CB | 490(#2SSTR) CB | OTHER | [5 empty] | 458 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | T/2DTR(A) |  |  | 0129 |  | 0165 | 1-10-01 |  | 2-24 | 330 | 52AS | 330 CB (ON/OFF) |  | abia | ELEM/D11_A1 | [8 empty] | 榴中DS.330_CB | 330(#2DTR) CB | MTR | [5 empty] | 459 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | 230 | #3SC(230) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | A/LBS230^C/3SC(A) |  |  | 0322 |  | 0166 | 2-08-02 |  | 2-25 | 230 | 52AS | 230 CB (ON/OFF) |  | abhb | B3/D11_A1 | [8 empty] | 榴中DS.230_CB | 230(11KV #3SC) CB | SC | [5 empty] | 460 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB21 | 榴一線(XB21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/XB21/T1 |  |  | 0326 |  | 0167 | 2-08-06 |  | 2-26 | XB21 | 52AS | XB21 CB (ON/OFF) |  | aaeb | B2/D11_D1 | [8 empty] | 榴中DS.XB21_CB | XB21(11KV榴ㄧ線) CB | FEEDER | [5 empty] | 461 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB21 | 榴一線(XB21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0680 |  | 0168 | 1-3A-08 |  | 2-27 | XB21 | 79S | XB21復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB21_79UL | 11KV榴ㄧ線(XB21) 79RY U/L | FEEDER | [5 empty] | 462 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D11 | 榴中DS | 11 | 11kV | XB21 | 榴一線(XB21) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0681 |  | 0169 | 1-3A-09 |  | 2-28 | XB21 | TAPS | XB21 LCO TAP (使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB21_LCO_TAP | 11KV榴ㄧ線(XB21) LCO TAP | FEEDER | [5 empty] | 463 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D11 | 榴中DS | 11 | 11kV | XB22 | 榴二線(XB22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/XB22/T1 |  |  | 0330 |  | 0170 | 2-09-02 |  | 2-29 | XB22 | 52AS | XB22 CB (ON/OFF) |  | aafb | B2/D11_D1 | [8 empty] | 榴中DS.XB22_CB | XB22(11KV榴二線) CB | FEEDER | [5 empty] | 464 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB22 | 榴二線(XB22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0682 |  | 0171 | 1-3A-10 |  | 2-2A | XB22 | 79S | XB22復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB22_79UL | 11KV榴二線(XB22) 79RY U/L | FEEDER | [5 empty] | 465 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D11 | 榴中DS | 11 | 11kV | XB22 | 榴二線(XB22) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0683 |  | 0172 | 1-3A-11 |  | 2-2B | XB22 | TAPS | XB22 LCO TAP (使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB22_LCO_TAP | 11KV榴二線(XB22) LCO TAP | FEEDER | [5 empty] | 466 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D11 | 榴中DS | 11 | 11kV | XB23 | 榴三線(XB23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/XB23/T1 |  |  | 0334 |  | 0173 | 2-09-06 |  | 2-2C | XB23 | 52AS | XB23 8CB (ON/OFF) |  | aagb | B2/D11_D1 | [8 empty] | 榴中DS.XB23_CB | XB23(11KV榴三線) CB | FEEDER | [5 empty] | 467 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB23 | 榴三線(XB23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0684 |  | 0174 | 1-3A-12 |  | 2-2D | XB23 | 79S | XB23復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB23_79UL | 11KV榴三線(XB23) 79RY U/L | FEEDER | [5 empty] | 468 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D11 | 榴中DS | 11 | 11kV | XB23 | 榴三線(XB23) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0685 |  | 0175 | 1-3A-13 |  | 2-2E | XB23 | TAPS | XB23 LCO TAP (使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB23_LCO_TAP | 11KV榴三線(XB23) LCO TAP | FEEDER | [5 empty] | 469 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D11 | 榴中DS | 11 | 11kV | XB24 | 榴四線(XB24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/XB24/T1 |  |  | 0338 |  | 0176 | 2-0A-02 |  | 2-2F | XB24 | 52AS | XB24 CB (ON/OFF) |  | aahb | B2/D11_D1 | [8 empty] | 榴中DS.XB24_CB | XB24(11KV榴四線) CB | FEEDER | [5 empty] | 470 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB24 | 榴四線(XB24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0686 |  | 0177 | 1-3A-14 |  | 2-30 | XB24 | 79S | XB24復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB24_79UL | 11KV榴四線(XB24) 79RY U/L | FEEDER | [5 empty] | 471 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D11 | 榴中DS | 11 | 11kV | XB24 | 榴四線(XB24) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0687 |  | 0178 | 1-3A-15 |  | 2-31 | XB24 | TAPS | XB24 LCO TAP (使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB24_LCO_TAP | 11KV榴四線(XB24) LCO TAP | FEEDER | [5 empty] | 472 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D11 | 榴中DS | 11 | 11kV | XB25 | 榴五線(XB25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/XB25/T1 |  |  | 0342 |  | 0179 | 2-0A-06 |  | 2-32 | XB25 | 52AS | XB25 CB (ON/OFF) |  | aaib | B2/D11_D1 | [8 empty] | 榴中DS.XB25_CB | XB25(11KV榴五線) CB | FEEDER | [5 empty] | 473 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB25 | 榴五線(XB25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0688 |  | 0180 | 1-3B-00 |  | 2-33 | XB25 | 79S | XB25復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB25_79UL | 11KV榴五線(XB25) 79RY U/L | FEEDER | [5 empty] | 474 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D11 | 榴中DS | 11 | 11kV | XB25 | 榴五線(XB25) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0689 |  | 0181 | 1-3B-01 |  | 2-34 | XB25 | TAPS | XB25 LCO TAP (使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB25_LCO_TAP | 11KV榴五線(XB25) LCO TAP | FEEDER | [5 empty] | 475 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D11 | 榴中DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | T/2DTR(B) |  |  | 0132 |  | 0182 | 1-10-04 |  | 2-35 | 340 | 52AS | 340 CB (ON/OFF) |  | bbja | ELEM/D11_A1 | [8 empty] | 榴中DS.340_CB | 340(#2DTR) CB | MTR | [5 empty] | 476 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | 240 | #4SC(240) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | C/4SC |  |  | 0351 |  | 0183 | 2-0B-07 |  | 2-36 | 240 | 52AS | 240 CB (ON/OFF) |  | bbhb | B3/D11_A1 | [8 empty] | 榴中DS.240_CB | 240(23KV #4SC) CB | SC | [5 empty] | 477 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB26 | 榴六線(XB26) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/XB26/T1 |  |  | 0355 |  | 0184 | 2-0C-03 |  | 2-37 | XB26 | 52AS | XB26 CB (ON/OFF) |  | abbb | B2/D11_D1 | [8 empty] | 榴中DS.XB26_CB | XB26(11KV榴六線) CB | FEEDER | [5 empty] | 478 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB26 | 榴六線(XB26) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0690 |  | 0185 | 1-3B-02 |  | 2-38 | XB26 | 79S | XB26復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB26_79UL | 11KV榴六線(XB26) 79RY U/L | FEEDER | [5 empty] | 479 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D11 | 榴中DS | 11 | 11kV | XB26 | 榴六線(XB26) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0691 |  | 0186 | 1-3B-03 |  | 2-39 | XB26 | TAPS | XB26 LCO TAP (使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB26_LCO_TAP | 11KV榴六線(XB26) LCO TAP | FEEDER | [5 empty] | 480 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D11 | 榴中DS | 11 | 11kV | XB27 | 榴七線(XB27) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/XB27/T1 |  |  | 0359 |  | 0187 | 2-0C-07 |  | 2-3A | XB27 | 52AS | XB27 CB (ON/OFF) |  | abcb | B2/D11_D1 | [8 empty] | 榴中DS.XB27_CB | XB27(11KV榴七線) CB | FEEDER | [5 empty] | 481 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | TCA | 斷路器跳脫迴路故障 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0700 |  |  | 1-3B-12 |  |  | ------ | TCSA | 斷路器跳脫迴圈監視警報(動作/正常)(COMMON) |  |  | B3/D11_A1 | [8 empty] | 榴中DS.TCA | 斷路器跳脫回路故障 | OTHER | [5 empty] | 482 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | XB27 | 榴七線(XB27) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0692 |  | 0188 | 1-3B-04 |  | 2-3B | XB27 | 79S | XB27復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB27_79UL | 11KV榴七線(XB27) 79RY U/L | FEEDER | [5 empty] | 483 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D11 | 榴中DS | 11 | 11kV | XB27 | 榴七線(XB27) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0693 |  | 0189 | 1-3B-05 |  | 2-3C | XB27 | TAPS | XB27 LCO TAP (使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB27_LCO_TAP | 11KV榴七線(XB27) LCO TAP | FEEDER | [5 empty] | 484 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D11 | 榴中DS | 11 | 11kV | XB28 | 榴八線(XB28) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/XB28/T1 |  |  | 0363 |  | 0190 | 2-0D-03 |  | 2-3D | XB28 | 52AS | XB28 CB (ON/OFF) |  | abdb | B2/D11_D1 | [8 empty] | 榴中DS.XB28_CB | XB28(11KV榴八線) CB | FEEDER | [5 empty] | 485 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB28 | 榴八線(XB28) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0694 |  | 0191 | 1-3B-06 |  | 2-3E | XB28 | 79S | XB28復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB28_79UL | 11KV榴八線(XB28) 79RY U/L | FEEDER | [5 empty] | 486 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D11 | 榴中DS | 11 | 11kV | XB28 | 榴八線(XB28) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0695 |  | 0192 | 1-3B-07 |  | 2-3F | XB28 | TAPS | XB28 LCO TAP (使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB28_LCO_TAP | 11KV榴八線(XB28) LCO TAP | FEEDER | [5 empty] | 487 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D11 | 榴中DS | 11 | 11kV | XB29 | 榴九線(XB29) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/XB29/T1 |  |  | 0367 |  | 0193 | 2-0D-07 |  | 2-40 | XB29 | 52AS | XB29 CB (ON/OFF) |  | abeb | B2/D11_D1 | [8 empty] | 榴中DS.XB29_CB | XB29(11KV榴九線) CB | FEEDER | [5 empty] | 488 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB29 | 榴九線(XB29) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0696 |  | 0194 | 1-3B-08 |  | 2-41 | XB29 | 79S | XB29復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB29_79UL | 11KV榴九線(XB29) 79RY U/L | FEEDER | [5 empty] | 489 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D11 | 榴中DS | 11 | 11kV | XB29 | 榴九線(XB29) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0697 |  | 0195 | 1-3B-09 |  | 2-42 | XB29 | TAPS | XB29 LCO TAP (使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB29_LCO_TAP | 11KV榴九線(XB29) LCO TAP | FEEDER | [5 empty] | 490 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D11 | 榴中DS | 11 | 11kV | XB30 | 榴十線(XB30) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/XB30/T1 |  |  | 0371 |  | 0196 | 2-0E-03 |  | 2-43 | XB30 | 52AS | XB30 CB (ON/OFF) |  | abgb | B2/D11_D1 | [8 empty] | 榴中DS.XB30_CB | XB30(11KV榴十線) CB | FEEDER | [5 empty] | 491 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB30 | 榴十線(XB30) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0698 |  | 0197 | 1-3B-10 |  | 2-44 | XB30 | 79S | XB30復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB30_79UL | 11KV榴十線(XB30) 79RY U/L | FEEDER | [5 empty] | 492 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D11 | 榴中DS | 11 | 11kV | XB30 | 榴十線(XB30) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0699 |  | 0198 | 1-3B-11 |  | 2-45 | XB30 | TAPS | XB30 LCO TAP (使用/閉鎖) |  |  | B2/D11_D1 | [8 empty] | 榴中DS.XB30_LCO_TAP | 11KV榴十線(XB30) LCO TAP | FEEDER | [5 empty] | 493 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D11 | 榴中DS | 22 | 22kV | 200 | TIE(200) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/2BBus | B/1BBus |  |  | 0345 |  | 0199 | 2-0B-01 |  | 2-46 | 200 | 52AS | 200 CB (ON/OFF) |  | bbab | B3/D11_A1 | [8 empty] | 榴中DS.200_CB | 200(TIE) CB | TIE | [5 empty] | 494 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | Lights1 |  |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0620 |  | 0202 | 1-36-12 |  | 2-4A | 照明控制箱 | FLA | 各區照明動作 |  |  | B3/D11_A1 | [8 empty] | 榴中DS.開關場照明(A) | 開關場照明(A) | OTHER | [5 empty] | 495 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0636 |  | 0203 | 1-37-12 |  | 2-4B | ACBS1 | ACB1 | 所內電源ACB1 |  |  | B3/D11_A1 | [8 empty] | 榴中DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | [5 empty] | 496 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0637 |  | 0204 | 1-37-13 |  | 2-4C | ACBS2 | ACB2 | 所內電源ACB2 |  |  | B3/D11_A1 | [8 empty] | 榴中DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | [5 empty] | 497 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D11 | 榴中DS | 0 |  | StaDev | 所內設施 |  | ACBT |  |  | Status | 所內電源ACB TIE | Close/Open | Y | 3 | DI-SP | [6 empty] | 0638 |  | 0205 | 1-37-14 |  | 2-4D | ACBS3 | ACB TIE | 所內電源ACB TIE |  |  | B3/D11_A1 | [8 empty] | 榴中DS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | [5 empty] | 498 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ON/OFF | OFF
D11 | 榴中DS | 161 | 161kV | 1510 | 榴中～斗工一路(1510) |  | 25PFA |  | INSERT | Status | 同步校核電驛電源 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0111 |  |  | 1-0D-07 |  |  | ------ | ------ | SPARE |  |  | B2/D11_A1 | [8 empty] | 榴中DS.1510_25PFA | 1510 同步校核電驛電源故障 | OTHER | [5 empty] | 499 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1520 | 榴中～斗工二路(1520) |  | 25PFA |  | INSERT | Status | 同步校核電驛電源 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0113 |  |  | 1-0E-01 |  |  | ------ | ------ | SPARE |  |  | B2/D11_A1 | [8 empty] | 榴中DS.1520_25PFA | 1520 同步校核電驛電源故障 | OTHER | [5 empty] | 500 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | ComPoint |  |  | 2A5Other | 洩油池抽水泵警報 | INSERT | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0640 |  |  | 1-38-09 |  |  | ------ | ------ | SPARE |  |  | B3/D11_A1 | [8 empty] | 榴中DS.OWFA | 洩油池抽水泵警報 | OTHER | [5 empty] | 501 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | 1A5Other | 81A 低頻電驛故障 (重複, TPC確認) | INSERT | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0649 |  |  | 1-38-00 |  |  | ------ | ------ | SPARE |  |  | B3/D11_A1 | [8 empty] | 榴中DS.81RF(1) | 310低頻電驛故障 | OTHER | [5 empty] | 502 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
D11 | 榴中DS | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/D11_A1 | [12 empty] | 榴中DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: D11/161/1BUS/V; OPRD2: D11/161/2BUS/V
D11 | 榴中DS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/D11_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: D11/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
D11 | 榴中DS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/D11_A1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_2 | OPRD1: D11/161/1510/MW; OPRD2: D11/161/1520/MW
D11 | 榴中DS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/D11_A1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: D11/0/CalcPoint/OPRN2_MW
D11 | 榴中DS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/D11_A1 | [17 empty] | none
D11 | 榴中DS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/D11_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: D11/0/CalcPoint/OPRN1; OPRD2: D11/0/CalcPoint/OPRN2; OPRD3: D11/0/CalcPoint/PRFL_UL
D11 | 榴中DS |  |  | 1DTR | 1DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D11_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D11/11/310/I_R; OPRD2: D11/22/320/I_R
D11 | 榴中DS |  |  | 1DTR | 1DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D11_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D11/11/310/I_S; OPRD2: D11/22/320/I_S
D11 | 榴中DS |  |  | 1DTR | 1DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D11_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D11/11/310/I_T; OPRD2: D11/22/320/I_T
D11 | 榴中DS |  |  | 2DTR | 2DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D11_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D11/11/330/I_R; OPRD2: D11/22/340/I_R
D11 | 榴中DS |  |  | 2DTR | 2DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D11_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D11/11/330/I_S; OPRD2: D11/22/340/I_S
D11 | 榴中DS |  |  | 2DTR | 2DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D11_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D11/11/330/I_T; OPRD2: D11/22/340/I_T
D11 | 榴中DS | 161 | 161kV | 1510 | 榴中～斗工一路(1510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D11_A1 | [12 empty] | 榴中DS.1510_AMP | 榴中斗工一路 AMP | LINE161 | AMP_CAL | C20R2000 | amp_cal | OPRD1: D11/161/1510/MW; OPRD2: D11/161/1510/MVAR; OPRD3: D11/0/CalcPoint/Vbs4
D11 | 榴中DS | 161 | 161kV | 1520 | 榴中～斗工二路(1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D11_A1 | [12 empty] | 榴中DS.1520_AMP | 榴中斗工二路 AMP | LINE161 | AMP_CAL | C20R2000 | amp_cal | OPRD1: D11/161/1520/MW; OPRD2: D11/161/1520/MVAR; OPRD3: D11/0/CalcPoint/Vbs4
D11 | 榴中DS | 22 | 22kV | 1ABUS | #1ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D11_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D11/22/1ABUS/V
D11 | 榴中DS | 22 | 22kV | 1BBUS | #1BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D11_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D11/22/1BBUS/V
D11 | 榴中DS | 22 | 22kV | 2ABUS | #2ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D11_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D11/22/2ABUS/V
D11 | 榴中DS | 22 | 22kV | 2BBUS | #2BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D11_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D11/22/2BBUS/V
D11 | 榴中DS |  |  | 1DTR(A) | #1DTR(A) |  | TR_PERM | [9 empty] | B1/D11_A1 | [12 empty] | 榴中DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D11//1DTR(A)/SupLocal; OPRD2: D11//1DTR(A)/Tap Chan
D11 | 榴中DS |  |  | 1DTR(B) | #1DTR(B) |  | TR_PERM | [9 empty] | B1/D11_A1 | [12 empty] | 榴中DS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D11//1DTR(B)/SupLocal; OPRD2: D11//1DTR(B)/Tap Chan
D11 | 榴中DS |  |  | 2DTR(A) | #2DTR(A) |  | TR_PERM | [9 empty] | B1/D11_A1 | [12 empty] | 榴中DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D11//2DTR(A)/SupLocal; OPRD2: D11//2DTR(A)/Tap Chan
D11 | 榴中DS |  |  | 2DTR(B) | #2DTR(B) |  | TR_PERM | [9 empty] | B1/D11_A1 | [12 empty] | 榴中DS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D11//2DTR(B)/SupLocal; OPRD2: D11//2DTR(B)/Tap Chan
D11 | 榴中DS | 11 | 11kV | XB21 | 榴一線(XB21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D11/11/XB21/I_R; OPRD3: D11/11/XB21/I_S; OPRD4: D11/11/XB21/I_T
D11 | 榴中DS | 11 | 11kV | XB22 | 榴二線(XB22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D11/11/XB22/I_R; OPRD3: D11/11/XB22/I_S; OPRD4: D11/11/XB22/I_T
D11 | 榴中DS | 11 | 11kV | XB23 | 榴三線(XB23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D11/11/XB23/I_R; OPRD3: D11/11/XB23/I_S; OPRD4: D11/11/XB23/I_T
D11 | 榴中DS | 11 | 11kV | XB24 | 榴四線(XB24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D11/11/XB24/I_R; OPRD3: D11/11/XB24/I_S; OPRD4: D11/11/XB24/I_T
D11 | 榴中DS | 11 | 11kV | XB25 | 榴五線(XB25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D11/11/XB25/I_R; OPRD3: D11/11/XB25/I_S; OPRD4: D11/11/XB25/I_T
D11 | 榴中DS | 11 | 11kV | XB26 | 榴六線(XB26) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D11/11/XB26/I_R; OPRD3: D11/11/XB26/I_S; OPRD4: D11/11/XB26/I_T
D11 | 榴中DS | 11 | 11kV | XB27 | 榴七線(XB27) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D11/11/XB27/I_R; OPRD3: D11/11/XB27/I_S; OPRD4: D11/11/XB27/I_T
D11 | 榴中DS | 11 | 11kV | XB28 | 榴八線(XB28) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D11/11/XB28/I_R; OPRD3: D11/11/XB28/I_S; OPRD4: D11/11/XB28/I_T
D11 | 榴中DS | 11 | 11kV | XB29 | 榴九線(XB29) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D11/11/XB29/I_R; OPRD3: D11/11/XB29/I_S; OPRD4: D11/11/XB29/I_T
D11 | 榴中DS | 11 | 11kV | XB30 | 榴十線(XB30) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D11/11/XB30/I_R; OPRD3: D11/11/XB30/I_S; OPRD4: D11/11/XB30/I_T
D11 | 榴中DS | 22 | 22kV | XB51 | 榴五一線(XB51) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D11/22/1BBUS/V; OPRD2: D11/22/XB51/I_R; OPRD3: D11/22/XB51/I_S; OPRD4: D11/22/XB51/I_T
D11 | 榴中DS | 22 | 22kV | XB52 | 榴五二線(XB52) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D11/22/1BBUS/V; OPRD2: D11/22/XB52/I_R; OPRD3: D11/22/XB52/I_S; OPRD4: D11/22/XB52/I_T
D11 | 榴中DS | 22 | 22kV | XB53 | 榴五三線(XB53) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D11/22/1BBUS/V; OPRD2: D11/22/XB53/I_R; OPRD3: D11/22/XB53/I_S; OPRD4: D11/22/XB53/I_T
D11 | 榴中DS | 22 | 22kV | XB54 | 榴五四線(XB54) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D11/22/1BBUS/V; OPRD2: D11/22/XB54/I_R; OPRD3: D11/22/XB54/I_S; OPRD4: D11/22/XB54/I_T
D11 | 榴中DS | 22 | 22kV | XB55 | 榴五五線(XB55) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D11/22/1BBUS/V; OPRD2: D11/22/XB55/I_R; OPRD3: D11/22/XB55/I_S; OPRD4: D11/22/XB55/I_T
D11 | 榴中DS | 22 | 22kV | XB56 | 榴五六線(XB56) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D11/22/2BBUS/V; OPRD2: D11/22/XB56/I_R; OPRD3: D11/22/XB56/I_S; OPRD4: D11/22/XB56/I_T
D11 | 榴中DS | 22 | 22kV | XB57 | 榴五七線(XB57) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D11/22/2BBUS/V; OPRD2: D11/22/XB57/I_R; OPRD3: D11/22/XB57/I_S; OPRD4: D11/22/XB57/I_T
D11 | 榴中DS | 22 | 22kV | XB58 | 榴五八線(XB58) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D11/22/2BBUS/V; OPRD2: D11/22/XB58/I_R; OPRD3: D11/22/XB58/I_S; OPRD4: D11/22/XB58/I_T
D11 | 榴中DS | 22 | 22kV | XB59 | 榴五九線(XB59) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D11/22/2BBUS/V; OPRD2: D11/22/XB59/I_R; OPRD3: D11/22/XB59/I_S; OPRD4: D11/22/XB59/I_T
D11 | 榴中DS | 22 | 22kV | XB60 | 榴六十線(XB60) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D11/22/2BBUS/V; OPRD2: D11/22/XB60/I_R; OPRD3: D11/22/XB60/I_S; OPRD4: D11/22/XB60/I_T
D11 | 榴中DS | 11 | 11kV | XB21 | 榴一線(XB21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D11/11/XB21/kVA; OPRD2: D11/11/XB21/KVAR
D11 | 榴中DS | 11 | 11kV | XB22 | 榴二線(XB22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D11/11/XB22/kVA; OPRD2: D11/11/XB22/KVAR
D11 | 榴中DS | 11 | 11kV | XB23 | 榴三線(XB23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D11/11/XB23/kVA; OPRD2: D11/11/XB23/KVAR
D11 | 榴中DS | 11 | 11kV | XB24 | 榴四線(XB24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D11/11/XB24/kVA; OPRD2: D11/11/XB24/KVAR
D11 | 榴中DS | 11 | 11kV | XB25 | 榴五線(XB25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D11/11/XB25/kVA; OPRD2: D11/11/XB25/KVAR
D11 | 榴中DS | 11 | 11kV | XB26 | 榴六線(XB26) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D11/11/XB26/kVA; OPRD2: D11/11/XB26/KVAR
D11 | 榴中DS | 11 | 11kV | XB27 | 榴七線(XB27) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D11/11/XB27/kVA; OPRD2: D11/11/XB27/KVAR
D11 | 榴中DS | 11 | 11kV | XB28 | 榴八線(XB28) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D11/11/XB28/kVA; OPRD2: D11/11/XB28/KVAR
D11 | 榴中DS | 11 | 11kV | XB29 | 榴九線(XB29) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D11/11/XB29/kVA; OPRD2: D11/11/XB29/KVAR
D11 | 榴中DS | 11 | 11kV | XB30 | 榴十線(XB30) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D11/11/XB30/kVA; OPRD2: D11/11/XB30/KVAR
D11 | 榴中DS | 22 | 22kV | XB51 | 榴五一線(XB51) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D11/22/XB51/kVA; OPRD2: D11/22/XB51/KVAR
D11 | 榴中DS | 22 | 22kV | XB52 | 榴五二線(XB52) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D11/22/XB52/kVA; OPRD2: D11/22/XB52/KVAR
D11 | 榴中DS | 22 | 22kV | XB53 | 榴五三線(XB53) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D11/22/XB53/kVA; OPRD2: D11/22/XB53/KVAR
D11 | 榴中DS | 22 | 22kV | XB54 | 榴五四線(XB54) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D11/22/XB54/kVA; OPRD2: D11/22/XB54/KVAR
D11 | 榴中DS | 22 | 22kV | XB55 | 榴五五線(XB55) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D11/22/XB55/kVA; OPRD2: D11/22/XB55/KVAR
D11 | 榴中DS | 22 | 22kV | XB56 | 榴五六線(XB56) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D11/22/XB56/kVA; OPRD2: D11/22/XB56/KVAR
D11 | 榴中DS | 22 | 22kV | XB57 | 榴五七線(XB57) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D11/22/XB57/kVA; OPRD2: D11/22/XB57/KVAR
D11 | 榴中DS | 22 | 22kV | XB58 | 榴五八線(XB58) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D11/22/XB58/kVA; OPRD2: D11/22/XB58/KVAR
D11 | 榴中DS | 22 | 22kV | XB59 | 榴五九線(XB59) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D11/22/XB59/kVA; OPRD2: D11/22/XB59/KVAR
D11 | 榴中DS | 22 | 22kV | XB60 | 榴六十線(XB60) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D11_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D11/22/XB60/kVA; OPRD2: D11/22/XB60/KVAR
D11 | 榴中DS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D11_A1 | [12 empty] | 榴中DS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D11/11/210/CB; OPRD2: 6.9; OPRD3: 0
D11 | 榴中DS | 11 | 11kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D11_A1 | [12 empty] | 榴中DS.230_SC_MVAR | 11KV#3SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D11/11/230/CB; OPRD2: 6.9; OPRD3: 0
D11 | 榴中DS | 22 | 22kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D11_A1 | [12 empty] | 榴中DS.220_SC_MVAR | 23KV#2SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D11/22/220/CB; OPRD2: 13.8; OPRD3: 0
D11 | 榴中DS | 22 | 22kV | 240 | #4SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D11_A1 | [12 empty] | 榴中DS.240_SC_MVAR | 23KV#4SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D11/22/240/CB; OPRD2: 13.8; OPRD3: 0
D11 | 榴中DS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/D11_A1 | [12 empty] | 榴中DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_10 |  | com_alarm_26 | OPRD1: D11//1DTR/96D; OPRD2: D11//1DTR/96B2; OPRD3: D11//1DTR/63Q; OPRD4: D11//1DTR/96B1; OPRD5: D11//1DTR/TRA; OPRD6: D11//1DTR/96PA; OPRD7: D11//1DTR/87A; OPRD8: D11//1DTR/51ZA; OPRD9: D11//1DTR/GDA; OPRD10: D11//1DTR/PHA; OPRD11: D11//2DTR/63Q; OPRD12: D11//2DTR/TRA; OPRD13: D11//2DTR/96D; OPRD14: D11//2DTR/51ZA; OPRD15: D11//2DTR/96PA; OPRD16: D11//2DTR/87A; OPRD17: D11//2DTR/PHA; OPRD18: D11//2DTR/96B2; OPRD19: D11//2DTR/96B1; OPRD20: D11//2DTR/GDA; OPRD21: D11/11/310/GDA; OPRD22: D11/11/330/GDA; OPRD23: D11/161/1BUS/87A; OPRD24: D11/161/2BUS/87A; OPRD25: D11/22/320/GDA; OPRD26: D11/22/340/GDA
D11 | 榴中DS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/D11_A1 | [12 empty] | 榴中DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | STATION_FAULT_2 |  | com_alarm_2 | OPRD1: D11//1DTR/TRF; OPRD2: D11//2DTR/TRF
D11 | 榴中DS | 161 | 161kV | 1750_D1 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D11_D1 | [17 empty] | lamp2CC | OPRD1: D11/161/1750/CB
D11 | 榴中DS | 161 | 161kV | 1760_D1 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D11_D1 | [17 empty] | lamp2CC | OPRD1: D11/161/1760/CB
D11 | 榴中DS | 11 | 11kV | 310_D1 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D11_D1 | [17 empty] | lamp2CC | OPRD1: D11/11/310/CB
D11 | 榴中DS | 11 | 11kV | 310_D1 | #1DTR(A)(310) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/D11_D1 | [17 empty] | lamp2CC | OPRD1: D11/11/310/81A
D11 | 榴中DS | 22 | 22kV | 320_D1 | #1DTR(B)(320) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/D11_D1 | [17 empty] | lamp2CC | OPRD1: D11/22/320/81A
D11 | 榴中DS | 11 | 11kV | 330_D1 | #2DTR(A)(330) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/D11_D1 | [17 empty] | lamp2CC | OPRD1: D11/11/330/81A
D11 | 榴中DS | 22 | 22kV | 340_D1 | #2DTR(B)(340) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/D11_D1 | [17 empty] | lamp2CC | OPRD1: D11/22/340/81A
D11 | 榴中DS | 0 |  | StaDev_D1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D11_D1 | [17 empty] | lamp2CC | OPRD1: D11/0/StaDev/DCE
D11 | 榴中DS | 0 |  | StaDev_D1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D11_D1 | [17 empty] | lamp2CC | OPRD1: D11/0/StaDev/DCA
D11 | 榴中DS | 0 |  | StaDev_D1 | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/D11_D1 | [17 empty] | lamp2CC | OPRD1: D11/0/StaDev/STUV
D11 | 榴中DS | 22 | 22kV | 320_D1 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D11_D1 | [17 empty] | lamp2CC | OPRD1: D11/22/320/CB
D11 | 榴中DS | 11 | 11kV | 330_D1 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D11_D1 | [17 empty] | lamp2CC | OPRD1: D11/11/330/CB
D11 | 榴中DS | 22 | 22kV | 340_D1 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D11_D1 | [17 empty] | lamp2CC | OPRD1: D11/22/340/CB

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D11 | 榴中DS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 榴中DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | D11/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
D11 | 榴中DS | 161 | 161kV | 1510 | 榴中斗工一路(1510) |  | I | [25 empty] | ADCS_N | [8 empty] | 榴中DS.1510_AMP | 榴中斗工一路 AMP | LINE161 | D11/161/1510/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000
D11 | 榴中DS | 161 | 161kV | 1520 | 榴中斗工二路(1520) |  | I | [25 empty] | ADCS_N | [8 empty] | 榴中DS.1520_AMP | 榴中斗工二路 AMP | LINE161 | D11/161/1520/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴一線KVA | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴一線KVA | 11KV榴一線KVA | FEEDER |  |  | KVA_CAL |  |  | 5 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴一線KW | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴一線KW | 11KV榴一線KW | FEEDER |  |  | KW_CAL |  |  | 6 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴七線KVA | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴七線KVA | 11KV榴七線KVA | FEEDER |  |  | KVA_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴七線KW | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴七線KW | 11KV榴七線KW | FEEDER |  |  | KW_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴九線KVA | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴九線KVA | 11KV榴九線KVA | FEEDER |  |  | KVA_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴九線KW | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴九線KW | 11KV榴九線KW | FEEDER |  |  | KW_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴二線KVA | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴二線KVA | 11KV榴二線KVA | FEEDER |  |  | KVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴二線KW | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴二線KW | 11KV榴二線KW | FEEDER |  |  | KW_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴八線KVA | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴八線KVA | 11KV榴八線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴八線KW | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴八線KW | 11KV榴八線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴十線KVA | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴十線KVA | 11KV榴十線KVA | FEEDER |  |  | KVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴十線KW | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴十線KW | 11KV榴十線KW | FEEDER |  |  | KW_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴三線KVA | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴三線KVA | 11KV榴三線KVA | FEEDER |  |  | KVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴三線KW | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴三線KW | 11KV榴三線KW | FEEDER |  |  | KW_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴五線KVA | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴五線KVA | 11KV榴五線KVA | FEEDER |  |  | KVA_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴五線KW | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴五線KW | 11KV榴五線KW | FEEDER |  |  | KW_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴六線KVA | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴六線KVA | 11KV榴六線KVA | FEEDER |  |  | KVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴六線KW | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴六線KW | 11KV榴六線KW | FEEDER |  |  | KW_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴四線KVA | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴四線KVA | 11KV榴四線KVA | FEEDER |  |  | KVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴四線KW | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴四線KW | 11KV榴四線KW | FEEDER |  |  | KW_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴51線KVA | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴51線KVA | 23KV榴51線KVA | FEEDER |  |  | KVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴51線KW | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴51線KW | 23KV榴51線KW | FEEDER |  |  | KW_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴52線KVA | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴52線KVA | 23KV榴52線KVA | FEEDER |  |  | KVA_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴52線KW | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴52線KW | 23KV榴52線KW | FEEDER |  |  | KW_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴53線KVA | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴53線KVA | 23KV榴53線KVA | FEEDER |  |  | KVA_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴53線KW | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴53線KW | 23KV榴53線KW | FEEDER |  |  | KW_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴54線KVA | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴54線KVA | 23KV榴54線KVA | FEEDER |  |  | KVA_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴54線KW | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴54線KW | 23KV榴54線KW | FEEDER |  |  | KW_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴55線KVA | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴55線KVA | 23KV榴55線KVA | FEEDER |  |  | KVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴55線KW | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴55線KW | 23KV榴55線KW | FEEDER |  |  | KW_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴56線KVA | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴56線KVA | 23KV榴56線KVA | FEEDER |  |  | KVA_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴56線KW | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴56線KW | 23KV榴56線KW | FEEDER |  |  | KW_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴57線KVA | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴57線KVA | 23KV榴57線KVA | FEEDER |  |  | KVA_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴57線KW | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴57線KW | 23KV榴57線KW | FEEDER |  |  | KW_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴58線KVA | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴58線KVA | 23KV榴58線KVA | FEEDER |  |  | KVA_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴58線KW | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴58線KW | 23KV榴58線KW | FEEDER |  |  | KW_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴59線KVA | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴59線KVA | 23KV榴59線KVA | FEEDER |  |  | KVA_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴59線KW | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴59線KW | 23KV榴59線KW | FEEDER |  |  | KW_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴60線KVA | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴60線KVA | 23KV榴60線KVA | FEEDER |  |  | KVA_CAL |  |  | 43 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  |  |  |  | 榴60線KW | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.榴60線KW | 23KV榴60線KW | FEEDER |  |  | KW_CAL |  |  | 44 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 榴中DS.#1DTR(A)_MVA | #1DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 45 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D11 | 榴中DS | 0 |  | 1DTR(A) | #1DTR(A) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 榴中DS.#1DTR(A)_LOAD | #1DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 46 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D11 | 榴中DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PF | [25 empty] | ADCS_N | [8 empty] | 榴中DS.#1DTR(A)_PF | #1DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 47 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D11 | 榴中DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 榴中DS.#1DTR(B)_MVA | #1DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 48 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D11 | 榴中DS | 0 |  | 1DTR(B) | #1DTR(B) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 榴中DS.#1DTR(B)_LOAD | #1DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 49 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D11 | 榴中DS | 0 |  | 1DTR(B) | #1DTR(B) |  | PF | [25 empty] | ADCS_N | [8 empty] | 榴中DS.#1DTR(B)_PF | #1DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 50 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D11 | 榴中DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 榴中DS.#2DTR(A)_MVA | #2DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 51 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D11 | 榴中DS | 0 |  | 2DTR(A) | #2DTR(A) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 榴中DS.#2DTR(A)_LOAD | #2DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 52 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D11 | 榴中DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PF | [25 empty] | ADCS_N | [8 empty] | 榴中DS.#2DTR(A)_PF | #2DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 53 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D11 | 榴中DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 榴中DS.#2DTR(B)_MVA | #2DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 54 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D11 | 榴中DS | 0 |  | 2DTR(B) | #2DTR(B) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 榴中DS.#2DTR(B)_LOAD | #2DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 55 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D11 | 榴中DS | 0 |  | 2DTR(B) | #2DTR(B) |  | PF | [25 empty] | ADCS_N | [8 empty] | 榴中DS.#2DTR(B)_PF | #2DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 56 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D11 | 榴中DS | 0 |  | 1DTR | #1DTR |  | MW | [25 empty] | ADCS_N | [8 empty] | 榴中DS.#1DTR_MW | #1DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 57 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  | 1DTR | #1DTR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 榴中DS.#1DTR_MVAR | #1DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 58 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  | 1DTR | #1DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 榴中DS.#1DTR_MVA | #1DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 59 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D11 | 榴中DS | 0 |  | 1DTR | #1DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 榴中DS.#1DTR_LOAD | #1DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 60 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D11 | 榴中DS | 0 |  | 2DTR | #2DTR |  | MW | [25 empty] | ADCS_N | [8 empty] | 榴中DS.#2DTR_MW | #2DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 61 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  | 2DTR | #2DTR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 榴中DS.#2DTR_MVAR | #2DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 62 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  | 2DTR | #2DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 榴中DS.#2DTR_MVA | #2DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 63 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D11 | 榴中DS | 0 |  | 2DTR | #2DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 榴中DS.#2DTR_LOAD | #2DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 64 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D11 | 榴中DS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 榴中DS.210_SC_MVAR | 11KV#1SC MVAR | SC | D11/11/210/MVAR |  | SC_LBS_11 |  |  | 65 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 11 | 11kV | 230_SC | #3SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 榴中DS.230_SC_MVAR | 11KV#3SC MVAR | SC | D11/11/230/MVAR |  | SC_LBS_11 |  |  | 66 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 22 | 22kV | 220_SC | #2SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 榴中DS.220_SC_MVAR | 23KV#2SC MVAR | SC | D11/22/220/MVAR |  | SC_CAL_23 |  |  | 67 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 22 | 22kV | 240_SC | #4SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 榴中DS.240_SC_MVAR | 23KV#4SC MVAR | SC | D11/22/240/MVAR |  | SC_CAL_23 |  |  | 68 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  | TRTOT | 榴中主變瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 榴中DS.TRTOT_MW | 榴中主變瞬時供電量 MW |  |  |  | MTR_PQ_CAL |  |  | 69 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  | TRTOT | 榴中主變瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 榴中DS.TRTOT_MVAR | 榴中主變瞬時供電量 MVAR |  |  |  | MTR_PQ_CAL |  |  | 70 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  | 100_CB | 100(100_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.100_CB_1 | 100 CB (D1) | TIE |  |  | AD_LAMP_DD_1 |  |  | 71 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | 200_CB | 200(200_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.200_CB_1 | 200 CB (D1) | TIE |  |  | AD_LAMP_DD_1 |  |  | 72 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | 1750_CB | #1DTR(1750_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.1750_CB_1 | 1750(#1DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 73 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | 310_CB | #1DTR(310_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.310_CB_1 | 310(#1DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 74 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | 320_CB | #1DTR(320_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.320_CB_1 | 320(#1DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 75 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | 1760_CB | #2DTR(1760_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.1760_CB_1 | 1760(#2DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 76 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | 330_CB | #2DTR(330_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.330_CB_1 | 330(#2DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 77 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | 340_CB | #2DTR(340_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.340_CB_1 | 340(#2DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 78 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | 210_CB | #1SC(210_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.210_CB_1 | 210(11KV #1SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 79 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | 230_CB | #3SC(230_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.230_CB_1 | 230(11KV #3SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 80 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | 220_CB | #2SC(220_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.220_CB_1 | 220(23KV #2SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 81 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | 240_CB | #4SC(240_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.240_CB_1 | 240(23KV #4SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 82 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_N | [8 empty] | 榴中DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | D11/0/CalcPoint/SUBA |  | STATION_FAULT_10 |  |  | 83 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 變電所輕故障點燈 | 變電所輕故障點燈 |  | SUBF | [25 empty] | ADCS_N | [8 empty] | 榴中DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | D11/0/CalcPoint/SUBF |  | STATION_FAULT_2 |  |  | 84 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.變電所重故障_1 | 變電所重故障點燈 (D1) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 85 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.變電所輕故障_1 | 變電所輕故障點燈 (D1) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 86 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1510_AMP | 榴中斗工一路 | [27 empty] | ADCS_N | [8 empty] | 榴中DS.1510_AMP_A | 榴中斗工一路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 87 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D11 | 榴中DS | 161 | 161kV | 1520_AMP | 榴中斗工二路 | [27 empty] | ADCS_N | [8 empty] | 榴中DS.1520_AMP_A | 榴中斗工二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 88 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D11 | 榴中DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PERM | [25 empty] | ADCS_N | [8 empty] | 榴中DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | D11//1DTR(A)/TR_PERM |  | DTR_PERM |  |  | 89 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D11 | 榴中DS | 0 |  | 1DTR(B) | #1DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 榴中DS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | D11//1DTR(B)/TR_PERM |  | DTR_PERM |  |  | 90 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D11 | 榴中DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PERM | [25 empty] | ADCS_N | [8 empty] | 榴中DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | D11//2DTR(A)/TR_PERM |  | DTR_PERM |  |  | 91 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D11 | 榴中DS | 0 |  | 2DTR(B) | #2DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 榴中DS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | D11//2DTR(B)/TR_PERM |  | DTR_PERM |  |  | 92 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D11 | 榴中DS | 0 |  | 1DTR_MVA | #1DTR | [27 empty] | ADCS_N | [8 empty] | 榴中DS.#1DTR_MVA_A | #1DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 93 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D11 | 榴中DS | 0 |  | 1DTR_MVA | #1DTR(A) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.#1DTR_MVA_1 | #1DTR(A) MVA 點燈 (D1) | MTR |  |  | MAP_SET |  |  | 94 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D11 | 榴中DS | 0 |  | 1DTR_MVA | #1DTR(B) | [27 empty] | DDCS1_1 | [8 empty] | 榴中DS.#1DTR_MVA_2 | #1DTR(B) MVA 點燈 (D1) | MTR |  |  | MAP_SET |  |  | 95 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
D11 | 榴中DS | 0 |  | 2DTR_MVA | #2DTR | [27 empty] | ADCS_N | [8 empty] | 榴中DS.#2DTR_MVA_A | #2DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 96 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D11 | 榴中DS | 0 |  | 2DTR_MVA | #2DTR(A) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.#2DTR_MVA_1 | #2DTR(A) MVA 點燈 (D1) | MTR |  |  | MAP_SET |  |  | 97 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D11 | 榴中DS | 0 |  | 2DTR_MVA | #2DTR(B) | [27 empty] | DDCS1_1 | [8 empty] | 榴中DS.#2DTR_MVA_2 | #2DTR(B) MVA 點燈 (D1) | MTR |  |  | MAP_SET |  |  | 98 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
D11 | 榴中DS | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_N | [8 empty] | 榴中DS.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_DS |  |  | 99 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | 11__CBA | 11/斷路器重故障(11__CBA) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.11/23KV_CBA_1 | 11/23KV斷路器重故障 (D1) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 100 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | 11__CBF | 11/斷路器輕故障(11__CBF) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 榴中DS.11/23KV_CBF_1 | 11/23KV斷路器輕故障 (D1) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 101 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 1ABUS | #1ABUS |  | 11KV#1ABUSC | [25 empty] | CDCS | [8 empty] | 榴中DS.11KV#1ABUSC | #1ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 102 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D11 | 榴中DS | 0 |  | 1BBUS | #1BBUS |  | 23KV#1BBUSC | [25 empty] | CDCS | [8 empty] | 榴中DS.23KV#1BBUSC | #1BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 103 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D11 | 榴中DS | 0 |  | 2ABUS | #2ABUS |  | 11KV#2ABUSC | [25 empty] | CDCS | [8 empty] | 榴中DS.11KV#2ABUSC | #2ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 104 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D11 | 榴中DS | 0 |  | 2BBUS | #2BBUS |  | 23KV#2BBUSC | [25 empty] | CDCS | [8 empty] | 榴中DS.23KV#2BBUSC | #2BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 105 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D11 | 榴中DS | 0 |  | TAP_OVER | TAP |  | SET | [25 empty] | ADCS_N | [8 empty] | 榴中DS.TAP_OVER_SET | TAP OVER HI/LO ALARM | MTR |  |  | 5000_CB_T4 |  |  | 106 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D11 | 榴中DS | 0 |  | BUS_OVER | BUS |  | SET | [25 empty] | ADCS_N | [8 empty] | 榴中DS.BUS_OVER_SET | BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B4 |  |  | 107 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D11 | 榴中DS | 0 |  | 5000 | 虛擬5000 |  | CB動作 | [25 empty] | ADCS_N | [8 empty] | 榴中DS.5000_CB動作 | 虛擬5000 CB動作,請查明原因處理 | MTR |  |  | 5000_CB_M |  |  | 108 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | 注意OLTC | 注意OLTC |  | BUS電壓異常 | [25 empty] | ADCS_N | [8 empty] | 榴中DS.BUS電壓異常 | 注意OLTC Tap位置,並將RPDC閉鎖 | OTHER |  |  | STATION_FAULT_2 |  |  | 109 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | 建大石榴 | 建大石榴 |  | 建大石榴KVAR | [14 empty] | 0009 | [8 empty] | KVAR_-12000_12000(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.建大石榴KVAR | 23KV建大石榴 KVAR | FEEDER |  |  |  |  | DNP | 110 | DNPAIPoint | PV001 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 7.200000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 建大石榴 | 建大石榴 |  | 建大石榴A1 | [14 empty] | 0010 | [8 empty] | A_-200_200(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.建大石榴A1 | 23KV建大石榴 R相AMP | FEEDER |  |  |  |  | DNP | 111 | DNPAIPoint | PV001 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 建大石榴 | 建大石榴 |  | 建大石榴A2 | [14 empty] | 0011 | [8 empty] | A_-200_200(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.建大石榴A2 | 23KV建大石榴 S相AMP | FEEDER |  |  |  |  | DNP | 112 | DNPAIPoint | PV001 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 建大石榴 | 建大石榴 |  | 建大石榴A3 | [14 empty] | 0012 | [8 empty] | A_-200_200(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.建大石榴A3 | 23KV建大石榴 T相AMP | FEEDER |  |  |  |  | DNP | 113 | DNPAIPoint | PV001 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 建大石榴 | 建大石榴(XB58) |  | KV1 | [14 empty] | 0013 | [8 empty] | kV_-18_18(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.建大石榴_KV1 | 23KV建大石榴(XB58) VR | OTHER |  |  |  |  | DNP | 114 | DNPAIPoint | PV001 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D11 | 榴中DS | 22 | 22kV | 建大石榴 | 建大石榴(XB58) |  | KV2 | [14 empty] | 0014 | [8 empty] | kV_-18_18(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.建大石榴_KV2 | 23KV建大石榴(XB58) VS | OTHER |  |  |  |  | DNP | 115 | DNPAIPoint | PV001 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D11 | 榴中DS | 22 | 22kV | 建大石榴 | 建大石榴(XB58) |  | KV3 | [14 empty] | 0015 | [8 empty] | kV_-18_18(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.建大石榴_KV3 | 23KV建大石榴(XB58) VT | OTHER |  |  |  |  | DNP | 116 | DNPAIPoint | PV001 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D11 | 榴中DS | 22 | 22kV | 建大石榴 | 建大石榴(XB58) |  | KW | [14 empty] | 0008 | [8 empty] | KW_-12000_12000(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.建大石榴_KW | 23KV建大石榴(XB58) KW | OTHER |  |  |  |  | DNP | 117 | DNPAIPoint | PV001 |  |  | AI | [17 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 3.600000 | 0.010000
D11 | 榴中DS | 0 |  |  |  |  | 建大石榴59V0 | [14 empty] | 0010 | [10 empty] | DDCS1_1 | [8 empty] | 榴中DS.建大石榴59V0 | 23KV建大石榴(XB58)59V0 | OTHER |  |  |  |  | DNP | 118 | DNPDIPoint | PV001 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 建大石榴 | 建大石榴 |  | 81A | [14 empty] | 0013 | [10 empty] | DDCS1_1 | [8 empty] | 榴中DS.建大石榴_81A | 23KV建大石榴(XB58)81A | OTHER |  |  |  |  | DNP | 119 | DNPDIPoint | PV001 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | 建大石榴 | 建大石榴(XB58) |  | CB | [14 empty] | 0008 | [10 empty] | DDCS1_1 | [8 empty] | 榴中DS.建大石榴_CB | 23KV建大石榴(XB58) CB | OTHER |  |  |  |  | DNP | 120 | DNPDIPoint | PV001 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | 建大石榴 | 建大石榴 |  | CFA | [14 empty] | 1039 | [10 empty] | DDCS1_1 | [8 empty] | 榴中DS.建大石榴_CFA | 23KV建大石榴(XB58)通訊警報 | OTHER |  |  |  |  | DNP | 121 | DNPDIPoint | PV001 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | 建大石榴 | 建大石榴(XB58) |  | DS1 | 建大石榴 | [13 empty] | 1032 | 1033 | [9 empty] | DDCS1_1 | [8 empty] | 榴中DS.建大石榴_DS | 23KV建大石榴(XB58) DS | OTHER |  |  |  |  | DNP | 122 | DNPDIPoint | PV001 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D11 | 榴中DS | 0 |  | 建大石榴 | 建大石榴 |  | GDA | [14 empty] | 0012 | [10 empty] | DDCS1_1 | [8 empty] | 榴中DS.建大石榴_GDA | 23KV建大石榴(XB58)GDA | OTHER |  |  |  |  | DNP | 123 | DNPDIPoint | PV001 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 建大石榴 | 建大石榴 |  | PHA | [14 empty] | 0011 | [10 empty] | DDCS1_1 | [8 empty] | 榴中DS.建大石榴_PHA | 23KV建大石榴(XB58)PHA | OTHER |  |  |  |  | DNP | 124 | DNPDIPoint | PV001 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | 建大石榴 | 建大石榴(XB58) |  | PTDS | [14 empty] | 1034 | 1035 | [9 empty] | DDCS1_1 | [8 empty] | 榴中DS.建大石榴_PTDS | 23KV建大石榴(XB58) PTDS | OTHER |  |  |  |  | DNP | 125 | DNPDIPoint | PV001 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D11 | 榴中DS | 0 |  | 建大石榴 | 建大石榴 |  | RYFA | [14 empty] | 0009 | [10 empty] | DDCS1_1 | [8 empty] | 榴中DS.建大石榴_RYA | 23KV建大石榴(XB58)27/59 | OTHER |  |  |  |  | DNP | 126 | DNPDIPoint | PV001 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1BUS | #1BUS |  | V | [17 empty] | 1-A5 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | D11/161/1BUS/V |  |  |  | CDC | 127 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D11 | 榴中DS | 161 | 161kV | 2BUS | #2BUS |  | V | [17 empty] | 1-A6 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | D11/161/2BUS/V |  |  |  | CDC | 128 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D11 | 榴中DS | 11 | 11kV | 1ABUS | #1ABUS |  | V | [17 empty] | 1-A8 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.11KV#1ABUS_KV | 11KV #1ABUS KV | BUS | D11/22/1ABUS/V |  |  |  | CDC | 129 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D11 | 榴中DS | 11 | 11kV | 2ABUS | #2ABUS |  | V | [17 empty] | 1-AA | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS | D11/22/2ABUS/V |  |  |  | CDC | 130 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D11 | 榴中DS | 22 | 22kV | 1BBUS | #1BBUS |  | V | [17 empty] | 1-A9 | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.23KV#1BBUS_KV | 23KV #1BBUS KV | BUS | D11/22/1BBUS/V |  |  |  | CDC | 131 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D11 | 榴中DS | 22 | 22kV | 2BBUS | #2BBUS |  | V | [17 empty] | 1-AB | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.23KV#2BBUS_KV | 23KV #2BBUS KV | BUS | D11/22/2BBUS/V |  |  |  | CDC | 132 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D11 | 榴中DS | 161 | 161kV | 1510 | 榴中斗工一路(1510) |  | MW | [17 empty] | 1-90 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.1510_MW | 榴中斗工一路 MW | LINE161 | D11/161/1510/MW |  |  |  | CDC | 133 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D11 | 榴中DS | 161 | 161kV | 1510 | 榴中斗工一路(1510) |  | MVAR | [17 empty] | 1-91 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.1510_MVAR | 榴中斗工一路 MVAR | LINE161 | D11/161/1510/MVAR |  |  |  | CDC | 134 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D11 | 榴中DS | 161 | 161kV | 1520 | 榴中斗工二路(1520) |  | MW | [17 empty] | 1-92 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.1520_MW | 榴中斗工二路 MW | LINE161 | D11/161/1520/MW |  |  |  | CDC | 135 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D11 | 榴中DS | 161 | 161kV | 1520 | 榴中斗工二路(1520) |  | MVAR | [17 empty] | 1-93 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.1520_MVAR | 榴中斗工二路 MVAR | LINE161 | D11/161/1520/MVAR |  |  |  | CDC | 136 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴一線 | 榴一線 |  | 榴一線KVAR | [17 empty] | 1-F0 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴一線KVAR | 11KV榴一線 KVAR | FEEDER | D11/11/XB21/KVAR |  |  |  | CDC | 137 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴一線 | 榴一線 |  | 榴一線A1 | [17 empty] | 1-F1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴一線A1 | 11KV榴一線 R相AMP | FEEDER | D11/11/XB21/I_R |  |  |  | CDC | 138 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴一線 | 榴一線 |  | 榴一線A2 | [17 empty] | 1-F2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴一線A2 | 11KV榴一線 S相AMP | FEEDER | D11/11/XB21/I_S |  |  |  | CDC | 139 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴一線 | 榴一線 |  | 榴一線A3 | [17 empty] | 1-F3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴一線A3 | 11KV榴一線 T相AMP | FEEDER | D11/11/XB21/I_T |  |  |  | CDC | 140 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴一線 | 榴一線 |  | 榴一線A0 | [17 empty] | 1-F4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴一線A0 | 11KV榴一線 N相AMP | FEEDER | D11/11/XB21/I_N |  |  |  | CDC | 141 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴七線 | 榴七線 |  | 榴七線KVAR | [17 empty] | 2-96 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴七線KVAR | 11KV榴七線 KVAR | FEEDER | D11/11/XB27/KVAR |  |  |  | CDC | 142 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴七線 | 榴七線 |  | 榴七線A1 | [17 empty] | 2-97 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴七線A1 | 11KV榴七線 R相AMP | FEEDER | D11/11/XB27/I_R |  |  |  | CDC | 143 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴七線 | 榴七線 |  | 榴七線A2 | [17 empty] | 2-98 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴七線A2 | 11KV榴七線 S相AMP | FEEDER | D11/11/XB27/I_S |  |  |  | CDC | 144 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴七線 | 榴七線 |  | 榴七線A3 | [17 empty] | 2-99 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴七線A3 | 11KV榴七線 T相AMP | FEEDER | D11/11/XB27/I_T |  |  |  | CDC | 145 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴七線 | 榴七線 |  | 榴七線A0 | [17 empty] | 2-9A | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴七線A0 | 11KV榴七線 N相AMP | FEEDER | D11/11/XB27/I_N |  |  |  | CDC | 146 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴九線 | 榴九線 |  | 榴九線KVAR | [17 empty] | 2-A0 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴九線KVAR | 11KV榴九線 KVAR | FEEDER | D11/11/XB29/KVAR |  |  |  | CDC | 147 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴九線 | 榴九線 |  | 榴九線A1 | [17 empty] | 2-A1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴九線A1 | 11KV榴九線 R相AMP | FEEDER | D11/11/XB29/I_R |  |  |  | CDC | 148 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴九線 | 榴九線 |  | 榴九線A2 | [17 empty] | 2-A2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴九線A2 | 11KV榴九線 S相AMP | FEEDER | D11/11/XB29/I_S |  |  |  | CDC | 149 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴九線 | 榴九線 |  | 榴九線A3 | [17 empty] | 2-A3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴九線A3 | 11KV榴九線 T相AMP | FEEDER | D11/11/XB29/I_T |  |  |  | CDC | 150 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴九線 | 榴九線 |  | 榴九線A0 | [17 empty] | 2-A4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴九線A0 | 11KV榴九線 N相AMP | FEEDER | D11/11/XB29/I_N |  |  |  | CDC | 151 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴二線 | 榴二線 |  | 榴二線KVAR | [17 empty] | 1-F5 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴二線KVAR | 11KV榴二線 KVAR | FEEDER | D11/11/XB22/KVAR |  |  |  | CDC | 152 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴二線 | 榴二線 |  | 榴二線A1 | [17 empty] | 1-F6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴二線A1 | 11KV榴二線 R相AMP | FEEDER | D11/11/XB22/I_R |  |  |  | CDC | 153 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴二線 | 榴二線 |  | 榴二線A2 | [17 empty] | 1-F7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴二線A2 | 11KV榴二線 S相AMP | FEEDER | D11/11/XB22/I_S |  |  |  | CDC | 154 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴二線 | 榴二線 |  | 榴二線A3 | [17 empty] | 1-F8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴二線A3 | 11KV榴二線 T相AMP | FEEDER | D11/11/XB22/I_T |  |  |  | CDC | 155 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴二線 | 榴二線 |  | 榴二線A0 | [17 empty] | 1-F9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴二線A0 | 11KV榴二線 N相AMP | FEEDER | D11/11/XB22/I_N |  |  |  | CDC | 156 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴八線 | 榴八線 |  | 榴八線KVAR | [17 empty] | 2-9B | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴八線KVAR | 11KV榴八線 KVAR | FEEDER | D11/11/XB28/KVAR |  |  |  | CDC | 157 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴八線 | 榴八線 |  | 榴八線A1 | [17 empty] | 2-9C | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴八線A1 | 11KV榴八線 R相AMP | FEEDER | D11/11/XB28/I_R |  |  |  | CDC | 158 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴八線 | 榴八線 |  | 榴八線A2 | [17 empty] | 2-9D | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴八線A2 | 11KV榴八線 S相AMP | FEEDER | D11/11/XB28/I_S |  |  |  | CDC | 159 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴八線 | 榴八線 |  | 榴八線A3 | [17 empty] | 2-9E | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴八線A3 | 11KV榴八線 T相AMP | FEEDER | D11/11/XB28/I_T |  |  |  | CDC | 160 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴八線 | 榴八線 |  | 榴八線A0 | [17 empty] | 2-9F | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴八線A0 | 11KV榴八線 N相AMP | FEEDER | D11/11/XB28/I_N |  |  |  | CDC | 161 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴十線 | 榴十線 |  | 榴十線KVAR | [17 empty] | 2-A5 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴十線KVAR | 11KV榴十線 KVAR | FEEDER | D11/11/XB30/KVAR |  |  |  | CDC | 162 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴十線 | 榴十線 |  | 榴十線A1 | [17 empty] | 2-A6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴十線A1 | 11KV榴十線 R相AMP | FEEDER | D11/11/XB30/I_R |  |  |  | CDC | 163 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴十線 | 榴十線 |  | 榴十線A2 | [17 empty] | 2-A7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴十線A2 | 11KV榴十線 S相AMP | FEEDER | D11/11/XB30/I_S |  |  |  | CDC | 164 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴十線 | 榴十線 |  | 榴十線A3 | [17 empty] | 2-A8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴十線A3 | 11KV榴十線 T相AMP | FEEDER | D11/11/XB30/I_T |  |  |  | CDC | 165 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴十線 | 榴十線 |  | 榴十線A0 | [17 empty] | 2-A9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴十線A0 | 11KV榴十線 N相AMP | FEEDER | D11/11/XB30/I_N |  |  |  | CDC | 166 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴三線 | 榴三線 |  | 榴三線KVAR | [17 empty] | 1-FA | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴三線KVAR | 11KV榴三線 KVAR | FEEDER | D11/11/XB23/KVAR |  |  |  | CDC | 167 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴三線 | 榴三線 |  | 榴三線A1 | [17 empty] | 1-FB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴三線A1 | 11KV榴三線 R相AMP | FEEDER | D11/11/XB23/I_R |  |  |  | CDC | 168 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴三線 | 榴三線 |  | 榴三線A2 | [17 empty] | 1-FC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴三線A2 | 11KV榴三線 S相AMP | FEEDER | D11/11/XB23/I_S |  |  |  | CDC | 169 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴三線 | 榴三線 |  | 榴三線A3 | [17 empty] | 1-FD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴三線A3 | 11KV榴三線 T相AMP | FEEDER | D11/11/XB23/I_T |  |  |  | CDC | 170 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴三線 | 榴三線 |  | 榴三線A0 | [17 empty] | 1-FE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴三線A0 | 11KV榴三線 N相AMP | FEEDER | D11/11/XB23/I_N |  |  |  | CDC | 171 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴五線 | 榴五線 |  | 榴五線KVAR | [17 empty] | 2-84 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴五線KVAR | 11KV榴五線 KVAR | FEEDER | D11/11/XB25/KVAR |  |  |  | CDC | 172 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴五線 | 榴五線 |  | 榴五線A1 | [17 empty] | 2-85 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴五線A1 | 11KV榴五線 R相AMP | FEEDER | D11/11/XB25/I_R |  |  |  | CDC | 173 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴五線 | 榴五線 |  | 榴五線A2 | [17 empty] | 2-86 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴五線A2 | 11KV榴五線 S相AMP | FEEDER | D11/11/XB25/I_S |  |  |  | CDC | 174 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴五線 | 榴五線 |  | 榴五線A3 | [17 empty] | 2-87 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴五線A3 | 11KV榴五線 T相AMP | FEEDER | D11/11/XB25/I_T |  |  |  | CDC | 175 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴五線 | 榴五線 |  | 榴五線A0 | [17 empty] | 2-88 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴五線A0 | 11KV榴五線 N相AMP | FEEDER | D11/11/XB25/I_N |  |  |  | CDC | 176 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴六線 | 榴六線 |  | 榴六線KVAR | [17 empty] | 2-91 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴六線KVAR | 11KV榴六線 KVAR | FEEDER | D11/11/XB26/KVAR |  |  |  | CDC | 177 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴六線 | 榴六線 |  | 榴六線A1 | [17 empty] | 2-92 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴六線A1 | 11KV榴六線 R相AMP | FEEDER | D11/11/XB26/I_R |  |  |  | CDC | 178 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴六線 | 榴六線 |  | 榴六線A2 | [17 empty] | 2-93 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴六線A2 | 11KV榴六線 S相AMP | FEEDER | D11/11/XB26/I_S |  |  |  | CDC | 179 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴六線 | 榴六線 |  | 榴六線A3 | [17 empty] | 2-94 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴六線A3 | 11KV榴六線 T相AMP | FEEDER | D11/11/XB26/I_T |  |  |  | CDC | 180 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴六線 | 榴六線 |  | 榴六線A0 | [17 empty] | 2-95 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴六線A0 | 11KV榴六線 N相AMP | FEEDER | D11/11/XB26/I_N |  |  |  | CDC | 181 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴四線 | 榴四線 |  | 榴四線KVAR | [17 empty] | 1-FF | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴四線KVAR | 11KV榴四線 KVAR | FEEDER | D11/11/XB24/KVAR |  |  |  | CDC | 182 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴四線 | 榴四線 |  | 榴四線A1 | [17 empty] | 2-80 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴四線A1 | 11KV榴四線 R相AMP | FEEDER | D11/11/XB24/I_R |  |  |  | CDC | 183 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴四線 | 榴四線 |  | 榴四線A2 | [17 empty] | 2-81 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴四線A2 | 11KV榴四線 S相AMP | FEEDER | D11/11/XB24/I_S |  |  |  | CDC | 184 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴四線 | 榴四線 |  | 榴四線A3 | [17 empty] | 2-82 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴四線A3 | 11KV榴四線 T相AMP | FEEDER | D11/11/XB24/I_T |  |  |  | CDC | 185 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | 榴四線 | 榴四線 |  | 榴四線A0 | [17 empty] | 2-83 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴四線A0 | 11KV榴四線 N相AMP | FEEDER | D11/11/XB24/I_N |  |  |  | CDC | 186 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴51線 | 榴51線 |  | 榴51線KVAR | [17 empty] | 1-B1 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴51線KVAR | 23KV榴51線 KVAR | FEEDER | D11/22/XB51/KVAR |  |  |  | CDC | 187 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴51線 | 榴51線 |  | 榴51線A1 | [17 empty] | 1-B2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴51線A1 | 23KV榴51線 R相AMP | FEEDER | D11/22/XB51/I_R |  |  |  | CDC | 188 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴51線 | 榴51線 |  | 榴51線A2 | [17 empty] | 1-B3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴51線A2 | 23KV榴51線 S相AMP | FEEDER | D11/22/XB51/I_S |  |  |  | CDC | 189 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴51線 | 榴51線 |  | 榴51線A3 | [17 empty] | 1-B4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴51線A3 | 23KV榴51線 T相AMP | FEEDER | D11/22/XB51/I_T |  |  |  | CDC | 190 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴51線 | 榴51線 |  | 榴51線A0 | [17 empty] | 1-B5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴51線A0 | 23KV榴51線 N相AMP | FEEDER | D11/22/XB51/I_N |  |  |  | CDC | 191 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴52線 | 榴52線 |  | 榴52線KVAR | [17 empty] | 1-B6 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴52線KVAR | 23KV榴52線 KVAR | FEEDER | D11/22/XB52/KVAR |  |  |  | CDC | 192 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴52線 | 榴52線 |  | 榴52線A1 | [17 empty] | 1-B7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴52線A1 | 23KV榴52線 R相AMP | FEEDER | D11/22/XB52/I_R |  |  |  | CDC | 193 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴52線 | 榴52線 |  | 榴52線A2 | [17 empty] | 1-B8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴52線A2 | 23KV榴52線 S相AMP | FEEDER | D11/22/XB52/I_S |  |  |  | CDC | 194 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴52線 | 榴52線 |  | 榴52線A3 | [17 empty] | 1-B9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴52線A3 | 23KV榴52線 T相AMP | FEEDER | D11/22/XB52/I_T |  |  |  | CDC | 195 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴52線 | 榴52線 |  | 榴52線A0 | [17 empty] | 1-BA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴52線A0 | 23KV榴52線 N相AMP | FEEDER | D11/22/XB52/I_N |  |  |  | CDC | 196 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴53線 | 榴53線 |  | 榴53線KVAR | [17 empty] | 1-BB | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴53線KVAR | 23KV榴53線 KVAR | FEEDER | D11/22/XB53/KVAR |  |  |  | CDC | 197 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴53線 | 榴53線 |  | 榴53線A1 | [17 empty] | 1-BC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴53線A1 | 23KV榴53線 R相AMP | FEEDER | D11/22/XB53/I_R |  |  |  | CDC | 198 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴53線 | 榴53線 |  | 榴53線A2 | [17 empty] | 1-BD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴53線A2 | 23KV榴53線 S相AMP | FEEDER | D11/22/XB53/I_S |  |  |  | CDC | 199 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴53線 | 榴53線 |  | 榴53線A3 | [17 empty] | 1-BE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴53線A3 | 23KV榴53線 T相AMP | FEEDER | D11/22/XB53/I_T |  |  |  | CDC | 200 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴53線 | 榴53線 |  | 榴53線A0 | [17 empty] | 1-BF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴53線A0 | 23KV榴53線 N相AMP | FEEDER | D11/22/XB53/I_N |  |  |  | CDC | 201 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴54線 | 榴54線 |  | 榴54線KVAR | [17 empty] | 1-C0 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴54線KVAR | 23KV榴54線 KVAR | FEEDER | D11/22/XB54/KVAR |  |  |  | CDC | 202 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴54線 | 榴54線 |  | 榴54線A1 | [17 empty] | 1-C1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴54線A1 | 23KV榴54線 R相AMP | FEEDER | D11/22/XB54/I_R |  |  |  | CDC | 203 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴54線 | 榴54線 |  | 榴54線A2 | [17 empty] | 1-C2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴54線A2 | 23KV榴54線 S相AMP | FEEDER | D11/22/XB54/I_S |  |  |  | CDC | 204 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴54線 | 榴54線 |  | 榴54線A3 | [17 empty] | 1-C3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴54線A3 | 23KV榴54線 T相AMP | FEEDER | D11/22/XB54/I_T |  |  |  | CDC | 205 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴54線 | 榴54線 |  | 榴54線A0 | [17 empty] | 1-C4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴54線A0 | 23KV榴54線 N相AMP | FEEDER | D11/22/XB54/I_N |  |  |  | CDC | 206 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴55線 | 榴55線 |  | 榴55線KVAR | [17 empty] | 1-C5 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴55線KVAR | 23KV榴55線 KVAR | FEEDER | D11/22/XB55/KVAR |  |  |  | CDC | 207 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴55線 | 榴55線 |  | 榴55線A1 | [17 empty] | 1-C6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴55線A1 | 23KV榴55線 R相AMP | FEEDER | D11/22/XB55/I_R |  |  |  | CDC | 208 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴55線 | 榴55線 |  | 榴55線A2 | [17 empty] | 1-C7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴55線A2 | 23KV榴55線 S相AMP | FEEDER | D11/22/XB55/I_S |  |  |  | CDC | 209 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴55線 | 榴55線 |  | 榴55線A3 | [17 empty] | 1-C8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴55線A3 | 23KV榴55線 T相AMP | FEEDER | D11/22/XB55/I_T |  |  |  | CDC | 210 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴55線 | 榴55線 |  | 榴55線A0 | [17 empty] | 1-C9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴55線A0 | 23KV榴55線 N相AMP | FEEDER | D11/22/XB55/I_N |  |  |  | CDC | 211 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴56線 | 榴56線 |  | 榴56線KVAR | [17 empty] | 1-D2 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴56線KVAR | 23KV榴56線 KVAR | FEEDER | D11/22/XB56/KVAR |  |  |  | CDC | 212 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴56線 | 榴56線 |  | 榴56線A1 | [17 empty] | 1-D3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴56線A1 | 23KV榴56線 R相AMP | FEEDER | D11/22/XB56/I_R |  |  |  | CDC | 213 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴56線 | 榴56線 |  | 榴56線A2 | [17 empty] | 1-D4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴56線A2 | 23KV榴56線 S相AMP | FEEDER | D11/22/XB56/I_S |  |  |  | CDC | 214 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴56線 | 榴56線 |  | 榴56線A3 | [17 empty] | 1-D5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴56線A3 | 23KV榴56線 T相AMP | FEEDER | D11/22/XB56/I_T |  |  |  | CDC | 215 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴56線 | 榴56線 |  | 榴56線A0 | [17 empty] | 1-D6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴56線A0 | 23KV榴56線 N相AMP | FEEDER | D11/22/XB56/I_N |  |  |  | CDC | 216 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴57線 | 榴57線 |  | 榴57線KVAR | [17 empty] | 1-D7 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴57線KVAR | 23KV榴57線 KVAR | FEEDER | D11/22/XB57/KVAR |  |  |  | CDC | 217 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴57線 | 榴57線 |  | 榴57線A1 | [17 empty] | 1-D8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴57線A1 | 23KV榴57線 R相AMP | FEEDER | D11/22/XB57/I_R |  |  |  | CDC | 218 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴57線 | 榴57線 |  | 榴57線A2 | [17 empty] | 1-D9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴57線A2 | 23KV榴57線 S相AMP | FEEDER | D11/22/XB57/I_S |  |  |  | CDC | 219 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴57線 | 榴57線 |  | 榴57線A3 | [17 empty] | 1-DA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴57線A3 | 23KV榴57線 T相AMP | FEEDER | D11/22/XB57/I_T |  |  |  | CDC | 220 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴57線 | 榴57線 |  | 榴57線A0 | [17 empty] | 1-DB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴57線A0 | 23KV榴57線 N相AMP | FEEDER | D11/22/XB57/I_N |  |  |  | CDC | 221 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴58線 | 榴58線 |  | 榴58線KVAR | [17 empty] | 1-DC | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴58線KVAR | 23KV榴58線 KVAR | FEEDER | D11/22/XB58/KVAR |  |  |  | CDC | 222 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴58線 | 榴58線 |  | 榴58線A1 | [17 empty] | 1-DD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴58線A1 | 23KV榴58線 R相AMP | FEEDER | D11/22/XB58/I_R |  |  |  | CDC | 223 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴58線 | 榴58線 |  | 榴58線A2 | [17 empty] | 1-DE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴58線A2 | 23KV榴58線 S相AMP | FEEDER | D11/22/XB58/I_S |  |  |  | CDC | 224 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴58線 | 榴58線 |  | 榴58線A3 | [17 empty] | 1-DF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴58線A3 | 23KV榴58線 T相AMP | FEEDER | D11/22/XB58/I_T |  |  |  | CDC | 225 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴58線 | 榴58線 |  | 榴58線A0 | [17 empty] | 1-E0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴58線A0 | 23KV榴58線 N相AMP | FEEDER | D11/22/XB58/I_N |  |  |  | CDC | 226 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴59線 | 榴59線 |  | 榴59線KVAR | [17 empty] | 1-E1 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴59線KVAR | 23KV榴59線 KVAR | FEEDER | D11/22/XB59/KVAR |  |  |  | CDC | 227 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴59線 | 榴59線 |  | 榴59線A1 | [17 empty] | 1-E2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴59線A1 | 23KV榴59線 R相AMP | FEEDER | D11/22/XB59/I_R |  |  |  | CDC | 228 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴59線 | 榴59線 |  | 榴59線A2 | [17 empty] | 1-E3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴59線A2 | 23KV榴59線 S相AMP | FEEDER | D11/22/XB59/I_S |  |  |  | CDC | 229 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴59線 | 榴59線 |  | 榴59線A3 | [17 empty] | 1-E4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴59線A3 | 23KV榴59線 T相AMP | FEEDER | D11/22/XB59/I_T |  |  |  | CDC | 230 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴59線 | 榴59線 |  | 榴59線A0 | [17 empty] | 1-E5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴59線A0 | 23KV榴59線 N相AMP | FEEDER | D11/22/XB59/I_N |  |  |  | CDC | 231 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴60線 | 榴60線 |  | 榴60線KVAR | [17 empty] | 1-E6 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴60線KVAR | 23KV榴60線 KVAR | FEEDER | D11/22/XB60/KVAR |  |  |  | CDC | 232 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴60線 | 榴60線 |  | 榴60線A1 | [17 empty] | 1-E7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴60線A1 | 23KV榴60線 R相AMP | FEEDER | D11/22/XB60/I_R |  |  |  | CDC | 233 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴60線 | 榴60線 |  | 榴60線A2 | [17 empty] | 1-E8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴60線A2 | 23KV榴60線 S相AMP | FEEDER | D11/22/XB60/I_S |  |  |  | CDC | 234 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴60線 | 榴60線 |  | 榴60線A3 | [17 empty] | 1-E9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴60線A3 | 23KV榴60線 T相AMP | FEEDER | D11/22/XB60/I_T |  |  |  | CDC | 235 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | 榴60線 | 榴60線 |  | 榴60線A0 | [17 empty] | 1-EA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 榴中DS.榴60線A0 | 23KV榴60線 N相AMP | FEEDER | D11/22/XB60/I_N |  |  |  | CDC | 236 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 0 |  | 1500TIE | 1500TIE |  | I | [17 empty] | 1-A7 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.1500TIE_AMP | 1500TIE AMP | TIE | D11/161/1500/I_R |  |  |  | CDC | 237 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | _100 | 100 |  | I_R | [17 empty] | 1-CA | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.11KV_100_A1 | 11KV 100 R相AMP | TIE | D11/11/100/I_R |  |  |  | CDC | 238 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | _100 | 100 |  | I_S | [17 empty] | 1-CB | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.11KV_100_A2 | 11KV 100 S相AMP | TIE | D11/11/100/I_S |  |  |  | CDC | 239 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 11 | 11kV | _100 | 100 |  | I_T | [17 empty] | 1-CC | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.11KV_100_A3 | 11KV 100 T相AMP | TIE | D11/11/100/I_T |  |  |  | CDC | 240 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | _200 | 200 |  | I_R | [17 empty] | 2-89 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.23KV_200_A1 | 23KV 200 R相AMP | TIE | D11/22/200/I_R |  |  |  | CDC | 241 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | _200 | 200 |  | I_S | [17 empty] | 2-8A | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.23KV_200_A2 | 23KV 200 S相AMP | TIE | D11/22/200/I_S |  |  |  | CDC | 242 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 22 | 22kV | _200 | 200 |  | I_T | [17 empty] | 2-8B | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.23KV_200_A3 | 23KV 200 T相AMP | TIE | D11/22/200/I_T |  |  |  | CDC | 243 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MW | [17 empty] | 1-AC | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | D11/11/310/KW |  |  |  | CDC | 244 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D11 | 榴中DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVAR | [17 empty] | 1-AD | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | D11/11/310/KVAR |  |  |  | CDC | 245 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D11 | 榴中DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_R | [17 empty] | 1-AE | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | D11/11/310/I_R |  |  |  | CDC | 246 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_S | [17 empty] | 1-AF | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | D11/11/310/I_S |  |  |  | CDC | 247 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_T | [17 empty] | 1-B0 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | D11/11/310/I_T |  |  |  | CDC | 248 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 0 |  | 1DTR | #1DTR |  | OilTemp | [17 empty] | 1-84 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.#1DTR_OIL | #1DTR 油溫 | MTR | D11//1DTR/OilTemp |  |  |  | CDC | 249 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D11 | 榴中DS | 0 |  | 1DTR(A) | #1DTR(A) |  | CoilTemp | [17 empty] | 1-82 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | D11//1DTR(A)/CoilTemp |  |  |  | CDC | 250 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D11 | 榴中DS | 0 |  | 1DTR(A) | #1DTR(A) |  | TapPosMv | [17 empty] | 1-80 |  | 1-02 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 榴中DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | D11//1DTR(A)/TapPosMv |  |  |  | CDC | 251 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D11 | 榴中DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MW | [17 empty] | 1-EB | [5 empty] | MW_-108_108(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | D11/22/320/KW |  |  |  | CDC | 252 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D11 | 榴中DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVAR | [17 empty] | 1-EC | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | D11/22/320/KVAR |  |  |  | CDC | 253 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D11 | 榴中DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_R | [17 empty] | 1-ED | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | D11/22/320/I_R |  |  |  | CDC | 254 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_S | [17 empty] | 1-EE | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | D11/22/320/I_S |  |  |  | CDC | 255 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_T | [17 empty] | 1-EF | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | D11/22/320/I_T |  |  |  | CDC | 256 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 0 |  | 1DTR(B) | #1DTR(B) |  | CoilTemp | [17 empty] | 1-83 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | D11//1DTR(B)/CoilTemp |  |  |  | CDC | 257 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D11 | 榴中DS | 0 |  | 1DTR(B) | #1DTR(B) |  | TapPosMv | [17 empty] | 1-81 |  | 1-04 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 榴中DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | D11//1DTR(B)/TapPosMv |  |  |  | CDC | 258 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D11 | 榴中DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MW | [17 empty] | 1-CD | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | D11/11/330/KW |  |  |  | CDC | 259 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D11 | 榴中DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVAR | [17 empty] | 1-CE | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | D11/11/330/KVAR |  |  |  | CDC | 260 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D11 | 榴中DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_R | [17 empty] | 1-CF | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | D11/11/330/I_R |  |  |  | CDC | 261 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_S | [17 empty] | 1-D0 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | D11/11/330/I_S |  |  |  | CDC | 262 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_T | [17 empty] | 1-D1 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | D11/11/330/I_T |  |  |  | CDC | 263 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 0 |  | 2DTR | #2DTR |  | OilTemp | [17 empty] | 1-89 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.#2DTR_OIL | #2DTR 油溫 | MTR | D11//2DTR/OilTemp |  |  |  | CDC | 264 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D11 | 榴中DS | 0 |  | 2DTR(A) | #2DTR(A) |  | CoilTemp | [17 empty] | 1-87 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | D11//2DTR(A)/CoilTemp |  |  |  | CDC | 265 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D11 | 榴中DS | 0 |  | 2DTR(A) | #2DTR(A) |  | TapPosMv | [17 empty] | 1-85 |  | 1-06 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 榴中DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | D11//2DTR(A)/TapPosMv |  |  |  | CDC | 266 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D11 | 榴中DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MW | [17 empty] | 2-8C | [5 empty] | MW_-108_108(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | D11/22/340/KW |  |  |  | CDC | 267 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D11 | 榴中DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVAR | [17 empty] | 2-8D | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | D11/22/340/KVAR |  |  |  | CDC | 268 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D11 | 榴中DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_R | [17 empty] | 2-8E | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | D11/22/340/I_R |  |  |  | CDC | 269 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_S | [17 empty] | 2-8F | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | D11/22/340/I_S |  |  |  | CDC | 270 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_T | [17 empty] | 2-90 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | D11/22/340/I_T |  |  |  | CDC | 271 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D11 | 榴中DS | 0 |  | 2DTR(B) | #2DTR(B) |  | CoilTemp | [17 empty] | 1-88 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | D11//2DTR(B)/CoilTemp |  |  |  | CDC | 272 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D11 | 榴中DS | 0 |  | 2DTR(B) | #2DTR(B) |  | TapPosMv | [17 empty] | 1-86 |  | 1-08 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 榴中DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | D11//2DTR(B)/TapPosMv |  |  |  | CDC | 273 | GENERICAIPoint | DS047_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D11 | 榴中DS | 0 |  |  |  |  | DCV_N | [17 empty] | 2-AB | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.直流N電源電壓 | 直流N電源電壓 | OTHER | D11/0/StaDev/DCV_N |  |  |  | CDC | 274 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D11 | 榴中DS | 0 |  |  |  |  | DCV_P | [17 empty] | 2-AA | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 榴中DS.直流P電源電壓 | 直流P電源電壓 | OTHER | D11/0/StaDev/DCV_P |  |  |  | CDC | 275 | GENERICAIPoint | DS047_L2 | CDC2_AI |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D11 | 榴中DS | 161 | 161kV | 1510 | 榴中斗工一路(1510) |  | PHA | [17 empty] | 1-00-02 | [7 empty] | 161KV_N | [8 empty] | 榴中DS.1510_PHA | 榴中斗工一路(1510) 相間RY | LINE161 | D11/161/1510/PHA |  |  |  | CDC | 276 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1510 | 榴中斗工一路(1510) |  | GDA | [17 empty] | 1-00-03 | [7 empty] | 161KV_N | [8 empty] | 榴中DS.1510_GDA | 榴中斗工一路(1510) 接地RY | LINE161 | D11/161/1510/GDA |  |  |  | CDC | 277 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1510 | 榴中斗工一路(1510) |  | 87A | [17 empty] | 1-00-01 | [7 empty] | 161KV_N | [8 empty] | 榴中DS.1510_87A | 榴中斗工一路(1510) 87RY | LINE161 | D11/161/1510/87A |  |  |  | CDC | 278 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1510 | 榴中斗工一路(1510) |  | 87UL | [17 empty] | 1-32-09 |  | 1-11 | [5 empty] | ADCS_N | [8 empty] | 榴中DS.1510_87UL | 榴中斗工一路(1510) 87RY U/L | LINE161 | D11/161/1510/87UL |  |  |  | CDC | 279 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D11 | 榴中DS | 161 | 161kV | 1510 | 榴中斗工一路(1510) |  | CB | [17 empty] | 1-0E-06 |  | 1-38 | [5 empty] | 161KV_N | [8 empty] | 榴中DS.1510_CB | 1510(榴中斗工一路) CB | LINE161 | D11/161/1510/CB |  |  |  | CDC | 280 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 161 | 161kV | 1510 | 榴中斗工一路(1510) |  | 79UL | [17 empty] | 1-32-11 |  | 1-13 | [5 empty] | ADCS_N | [8 empty] | 榴中DS.1510_79UL | 榴中斗工一路(1510) 79RY U/L | LINE161 | D11/161/1510/79UL |  |  |  | CDC | 281 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D11 | 榴中DS | 161 | 161kV | 1510 | 榴中斗工一路(1510) |  | DS1 | 1511 | [16 empty] | 2-30-04 | 2-30-05 | 1-39 | [5 empty] | ADCS_N | [8 empty] | 榴中DS.1511_DS | 1511(榴中斗工一路) DS | LINE161 | D11/161/1510/DS1 |  |  |  | CDC | 282 | GENERICDIPoint | DS047_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D11 | 榴中DS | 161 | 161kV | 1510 | 榴中斗工一路(1510) |  | DS2 | 1512 | [16 empty] | 2-30-06 | 2-30-07 | 1-3A | [5 empty] | ADCS_N | [8 empty] | 榴中DS.1512_DS | 1512(榴中斗工一路) DS | LINE161 | D11/161/1510/DS2 |  |  |  | CDC | 283 | GENERICDIPoint | DS047_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D11 | 榴中DS | 161 | 161kV | 1510 | 榴中斗工一路(1510) |  | DS3 | 1513 | [16 empty] | 2-30-08 | 2-30-09 | 1-3B | [5 empty] | ADCS_N | [8 empty] | 榴中DS.1513_DS | 1513(榴中斗工一路) DS | LINE161 | D11/161/1510/DS3 |  |  |  | CDC | 284 | GENERICDIPoint | DS047_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D11 | 榴中DS | 161 | 161kV | 1510 | 榴中斗工一路(1510) |  | E3 | 1513E | [16 empty] | 2-30-10 | 2-30-11 | 1-3C | [5 empty] | ADCS_N | [8 empty] | 榴中DS.1513E_ES | 1513E(榴中斗工一路) ES | LINE161 | D11/161/1510/ES3 |  |  |  | CDC | 285 | GENERICDIPoint | DS047_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D11 | 榴中DS | 161 | 161kV | 1520 | 榴中斗工二路(1520) |  | PHA | [17 empty] | 1-00-06 | [7 empty] | 161KV_N | [8 empty] | 榴中DS.1520_PHA | 榴中斗工二路(1520) 相間RY | LINE161 | D11/161/1520/PHA |  |  |  | CDC | 286 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1520 | 榴中斗工二路(1520) |  | GDA | [17 empty] | 1-00-07 | [7 empty] | 161KV_N | [8 empty] | 榴中DS.1520_GDA | 榴中斗工二路(1520) 接地RY | LINE161 | D11/161/1520/GDA |  |  |  | CDC | 287 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1520 | 榴中斗工二路(1520) |  | 87A | [17 empty] | 1-00-05 | [7 empty] | 161KV_N | [8 empty] | 榴中DS.1520_87A | 榴中斗工二路(1520) 87RY | LINE161 | D11/161/1520/87A |  |  |  | CDC | 288 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1520 | 榴中斗工二路(1520) |  | 87UL | [17 empty] | 1-32-10 |  | 1-14 | [5 empty] | ADCS_N | [8 empty] | 榴中DS.1520_87UL | 榴中斗工二路(1520) 87RY U/L | LINE161 | D11/161/1520/87UL |  |  |  | CDC | 289 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D11 | 榴中DS | 161 | 161kV | 1520 | 榴中斗工二路(1520) |  | CB | [17 empty] | 1-0E-07 |  | 1-3D | [5 empty] | 161KV_N | [8 empty] | 榴中DS.1520_CB | 1520(榴中斗工二路) CB | LINE161 | D11/161/1520/CB |  |  |  | CDC | 290 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 161 | 161kV | 1520 | 榴中斗工二路(1520) |  | 79UL | [17 empty] | 1-32-12 |  | 1-16 | [5 empty] | ADCS_N | [8 empty] | 榴中DS.1520_79UL | 榴中斗工二路(1520) 79RY U/L | LINE161 | D11/161/1520/79UL |  |  |  | CDC | 291 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D11 | 榴中DS | 161 | 161kV | 1520 | 榴中斗工二路(1520) |  | DS1 | 1521 | [16 empty] | 2-30-12 | 2-30-13 | 1-3E | [5 empty] | ADCS_N | [8 empty] | 榴中DS.1521_DS | 1521(榴中斗工二路) DS | LINE161 | D11/161/1520/DS1 |  |  |  | CDC | 292 | GENERICDIPoint | DS047_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D11 | 榴中DS | 161 | 161kV | 1520 | 榴中斗工二路(1520) |  | DS2 | 1522 | [16 empty] | 2-30-14 | 2-30-15 | 1-3F | [5 empty] | ADCS_N | [8 empty] | 榴中DS.1522_DS | 1522(榴中斗工二路) DS | LINE161 | D11/161/1520/DS2 |  |  |  | CDC | 293 | GENERICDIPoint | DS047_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D11 | 榴中DS | 161 | 161kV | 1520 | 榴中斗工二路(1520) |  | DS3 | 1523 | [16 empty] | 2-31-00 | 2-31-01 | 1-40 | [5 empty] | ADCS_N | [8 empty] | 榴中DS.1523_DS | 1523(榴中斗工二路) DS | LINE161 | D11/161/1520/DS3 |  |  |  | CDC | 294 | GENERICDIPoint | DS047_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D11 | 榴中DS | 161 | 161kV | 1520 | 榴中斗工二路(1520) |  | E3 | 1523E | [16 empty] | 2-31-02 | 2-31-03 | 1-41 | [5 empty] | ADCS_N | [8 empty] | 榴中DS.1523E_ES | 1523E(榴中斗工二路) ES | LINE161 | D11/161/1520/ES3 |  |  |  | CDC | 295 | GENERICDIPoint | DS047_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D11 | 榴中DS | 11 | 11kV | XB21 | 榴ㄧ線(XB21) |  | PHA | [17 empty] | 2-08-03 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB21_PHA | 11KV榴ㄧ線(XB21) 相間RY | FEEDER | D11/11/XB21/PHA |  |  |  | CDC | 296 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | XB21 | 榴ㄧ線(XB21) |  | GDA | [17 empty] | 2-08-04 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB21_GDA | 11KV榴ㄧ線(XB21) 接地RY | FEEDER | D11/11/XB21/GDA |  |  |  | CDC | 297 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | XB21 | 榴ㄧ線(XB21) 79RY |  | 79UL | [17 empty] | 1-3A-08 |  | 2-28 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB21_79UL | 11KV榴ㄧ線(XB21) 79RY U/L | FEEDER | D11/11/XB21/79UL |  |  |  | CDC | 298 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D11 | 榴中DS | 11 | 11kV | XB21_LCO | 榴ㄧ線(XB21) LCO |  | TapPosMv | [17 empty] | 1-3A-09 |  | 2-29 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB21_LCO_TAP | 11KV榴ㄧ線(XB21) LCO TAP | FEEDER | D11/11/XB21/ADJ |  |  |  | CDC | 299 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D11 | 榴中DS | 11 | 11kV | XB21 | XB21(11KV榴ㄧ線) |  | CB | [17 empty] | 2-08-06 |  | 2-27 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB21_CB | XB21(11KV榴ㄧ線) CB | FEEDER | D11/11/XB21/CB |  |  |  | CDC | 300 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB22 | 榴二線(XB22) |  | PHA | [17 empty] | 2-08-07 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB22_PHA | 11KV榴二線(XB22) 相間RY | FEEDER | D11/11/XB22/PHA |  |  |  | CDC | 301 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | XB22 | 榴二線(XB22) |  | GDA | [17 empty] | 2-09-00 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB22_GDA | 11KV榴二線(XB22) 接地RY | FEEDER | D11/11/XB22/GDA |  |  |  | CDC | 302 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | XB22 | 榴二線(XB22) 79RY |  | 79UL | [17 empty] | 1-3A-10 |  | 2-2B | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB22_79UL | 11KV榴二線(XB22) 79RY U/L | FEEDER | D11/11/XB22/79UL |  |  |  | CDC | 303 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D11 | 榴中DS | 11 | 11kV | XB22_LCO | 榴二線(XB22) LCO |  | TapPosMv | [17 empty] | 1-3A-11 |  | 2-2C | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB22_LCO_TAP | 11KV榴二線(XB22) LCO TAP | FEEDER | D11/11/XB22/ADJ |  |  |  | CDC | 304 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D11 | 榴中DS | 11 | 11kV | XB22 | XB22(11KV榴二線) |  | CB | [17 empty] | 2-09-02 |  | 2-2A | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB22_CB | XB22(11KV榴二線) CB | FEEDER | D11/11/XB22/CB |  |  |  | CDC | 305 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB23 | 榴三線(XB23) |  | PHA | [17 empty] | 2-09-03 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB23_PHA | 11KV榴三線(XB23) 相間RY | FEEDER | D11/11/XB23/PHA |  |  |  | CDC | 306 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | XB23 | 榴三線(XB23) |  | GDA | [17 empty] | 2-09-04 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB23_GDA | 11KV榴三線(XB23) 接地RY | FEEDER | D11/11/XB23/GDA |  |  |  | CDC | 307 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | XB23 | 榴三線(XB23) 79RY |  | 79UL | [17 empty] | 1-3A-12 |  | 2-2E | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB23_79UL | 11KV榴三線(XB23) 79RY U/L | FEEDER | D11/11/XB23/79UL |  |  |  | CDC | 308 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D11 | 榴中DS | 11 | 11kV | XB23_LCO | 榴三線(XB23) LCO |  | TapPosMv | [17 empty] | 1-3A-13 |  | 2-2F | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB23_LCO_TAP | 11KV榴三線(XB23) LCO TAP | FEEDER | D11/11/XB23/ADJ |  |  |  | CDC | 309 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D11 | 榴中DS | 11 | 11kV | XB23 | XB23(11KV榴三線) |  | CB | [17 empty] | 2-09-06 |  | 2-2D | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB23_CB | XB23(11KV榴三線) CB | FEEDER | D11/11/XB23/CB |  |  |  | CDC | 310 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB24 | 榴四線(XB24) |  | PHA | [17 empty] | 2-09-07 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB24_PHA | 11KV榴四線(XB24) 相間RY | FEEDER | D11/11/XB24/PHA |  |  |  | CDC | 311 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | XB24 | 榴四線(XB24) |  | GDA | [17 empty] | 2-0A-00 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB24_GDA | 11KV榴四線(XB24) 接地RY | FEEDER | D11/11/XB24/GDA |  |  |  | CDC | 312 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | XB24 | 榴四線(XB24) 79RY |  | 79UL | [17 empty] | 1-3A-14 |  | 2-31 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB24_79UL | 11KV榴四線(XB24) 79RY U/L | FEEDER | D11/11/XB24/79UL |  |  |  | CDC | 313 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D11 | 榴中DS | 11 | 11kV | XB24_LCO | 榴四線(XB24) LCO |  | TapPosMv | [17 empty] | 1-3A-15 |  | 2-32 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB24_LCO_TAP | 11KV榴四線(XB24) LCO TAP | FEEDER | D11/11/XB24/ADJ |  |  |  | CDC | 314 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D11 | 榴中DS | 11 | 11kV | XB24 | XB24(11KV榴四線) |  | CB | [17 empty] | 2-0A-02 |  | 2-30 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB24_CB | XB24(11KV榴四線) CB | FEEDER | D11/11/XB24/CB |  |  |  | CDC | 315 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB25 | 榴五線(XB25) |  | PHA | [17 empty] | 2-0A-03 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB25_PHA | 11KV榴五線(XB25) 相間RY | FEEDER | D11/11/XB25/PHA |  |  |  | CDC | 316 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | XB25 | 榴五線(XB25) |  | GDA | [17 empty] | 2-0A-04 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB25_GDA | 11KV榴五線(XB25) 接地RY | FEEDER | D11/11/XB25/GDA |  |  |  | CDC | 317 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | XB25 | 榴五線(XB25) 79RY |  | 79UL | [17 empty] | 1-3B-00 |  | 2-34 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB25_79UL | 11KV榴五線(XB25) 79RY U/L | FEEDER | D11/11/XB25/79UL |  |  |  | CDC | 318 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D11 | 榴中DS | 11 | 11kV | XB25_LCO | 榴五線(XB25) LCO |  | TapPosMv | [17 empty] | 1-3B-01 |  | 2-35 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB25_LCO_TAP | 11KV榴五線(XB25) LCO TAP | FEEDER | D11/11/XB25/ADJ |  |  |  | CDC | 319 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D11 | 榴中DS | 11 | 11kV | XB25 | XB25(11KV榴五線) |  | CB | [17 empty] | 2-0A-06 |  | 2-33 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB25_CB | XB25(11KV榴五線) CB | FEEDER | D11/11/XB25/CB |  |  |  | CDC | 320 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB26 | 榴六線(XB26) |  | PHA | [17 empty] | 2-0C-00 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB26_PHA | 11KV榴六線(XB26) 相間RY | FEEDER | D11/11/XB26/PHA |  |  |  | CDC | 321 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | XB26 | 榴六線(XB26) |  | GDA | [17 empty] | 2-0C-01 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB26_GDA | 11KV榴六線(XB26) 接地RY | FEEDER | D11/11/XB26/GDA |  |  |  | CDC | 322 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | XB26 | 榴六線(XB26) 79RY |  | 79UL | [17 empty] | 1-3B-02 |  | 2-39 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB26_79UL | 11KV榴六線(XB26) 79RY U/L | FEEDER | D11/11/XB26/79UL |  |  |  | CDC | 323 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D11 | 榴中DS | 11 | 11kV | XB26_LCO | 榴六線(XB26) LCO |  | TapPosMv | [17 empty] | 1-3B-03 |  | 2-3A | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB26_LCO_TAP | 11KV榴六線(XB26) LCO TAP | FEEDER | D11/11/XB26/ADJ |  |  |  | CDC | 324 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D11 | 榴中DS | 11 | 11kV | XB26 | XB26(11KV榴六線) |  | CB | [17 empty] | 2-0C-03 |  | 2-38 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB26_CB | XB26(11KV榴六線) CB | FEEDER | D11/11/XB26/CB |  |  |  | CDC | 325 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB27 | 榴七線(XB27) |  | PHA | [17 empty] | 2-0C-04 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB27_PHA | 11KV榴七線(XB27) 相間RY | FEEDER | D11/11/XB27/PHA |  |  |  | CDC | 326 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | XB27 | 榴七線(XB27) |  | GDA | [17 empty] | 2-0C-05 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB27_GDA | 11KV榴七線(XB27) 接地RY | FEEDER | D11/11/XB27/GDA |  |  |  | CDC | 327 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | XB27 | 榴七線(XB27) 79RY |  | 79UL | [17 empty] | 1-3B-04 |  | 2-3C | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB27_79UL | 11KV榴七線(XB27) 79RY U/L | FEEDER | D11/11/XB27/79UL |  |  |  | CDC | 328 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D11 | 榴中DS | 11 | 11kV | XB27_LCO | 榴七線(XB27) LCO |  | TapPosMv | [17 empty] | 1-3B-05 |  | 2-3D | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB27_LCO_TAP | 11KV榴七線(XB27) LCO TAP | FEEDER | D11/11/XB27/ADJ |  |  |  | CDC | 329 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D11 | 榴中DS | 11 | 11kV | XB27 | XB27(11KV榴七線) |  | CB | [17 empty] | 2-0C-07 |  | 2-3B | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB27_CB | XB27(11KV榴七線) CB | FEEDER | D11/11/XB27/CB |  |  |  | CDC | 330 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB28 | 榴八線(XB28) |  | PHA | [17 empty] | 2-0D-00 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB28_PHA | 11KV榴八線(XB28) 相間RY | FEEDER | D11/11/XB28/PHA |  |  |  | CDC | 331 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | XB28 | 榴八線(XB28) |  | GDA | [17 empty] | 2-0D-01 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB28_GDA | 11KV榴八線(XB28) 接地RY | FEEDER | D11/11/XB28/GDA |  |  |  | CDC | 332 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | XB28 | 榴八線(XB28) 79RY |  | 79UL | [17 empty] | 1-3B-06 |  | 2-3F | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB28_79UL | 11KV榴八線(XB28) 79RY U/L | FEEDER | D11/11/XB28/79UL |  |  |  | CDC | 333 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D11 | 榴中DS | 11 | 11kV | XB28_LCO | 榴八線(XB28) LCO |  | TapPosMv | [17 empty] | 1-3B-07 |  | 2-40 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB28_LCO_TAP | 11KV榴八線(XB28) LCO TAP | FEEDER | D11/11/XB28/ADJ |  |  |  | CDC | 334 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D11 | 榴中DS | 11 | 11kV | XB28 | XB28(11KV榴八線) |  | CB | [17 empty] | 2-0D-03 |  | 2-3E | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB28_CB | XB28(11KV榴八線) CB | FEEDER | D11/11/XB28/CB |  |  |  | CDC | 335 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB29 | 榴九線(XB29) |  | PHA | [17 empty] | 2-0D-04 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB29_PHA | 11KV榴九線(XB29) 相間RY | FEEDER | D11/11/XB29/PHA |  |  |  | CDC | 336 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | XB29 | 榴九線(XB29) |  | GDA | [17 empty] | 2-0D-05 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB29_GDA | 11KV榴九線(XB29) 接地RY | FEEDER | D11/11/XB29/GDA |  |  |  | CDC | 337 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | XB29 | 榴九線(XB29) 79RY |  | 79UL | [17 empty] | 1-3B-08 |  | 2-42 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB29_79UL | 11KV榴九線(XB29) 79RY U/L | FEEDER | D11/11/XB29/79UL |  |  |  | CDC | 338 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D11 | 榴中DS | 11 | 11kV | XB29_LCO | 榴九線(XB29) LCO |  | TapPosMv | [17 empty] | 1-3B-09 |  | 2-43 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB29_LCO_TAP | 11KV榴九線(XB29) LCO TAP | FEEDER | D11/11/XB29/ADJ |  |  |  | CDC | 339 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D11 | 榴中DS | 11 | 11kV | XB29 | XB29(11KV榴九線) |  | CB | [17 empty] | 2-0D-07 |  | 2-41 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB29_CB | XB29(11KV榴九線) CB | FEEDER | D11/11/XB29/CB |  |  |  | CDC | 340 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | XB30 | 榴十線(XB30) |  | PHA | [17 empty] | 2-0E-00 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB30_PHA | 11KV榴十線(XB30) 相間RY | FEEDER | D11/11/XB30/PHA |  |  |  | CDC | 341 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | XB30 | 榴十線(XB30) |  | GDA | [17 empty] | 2-0E-01 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB30_GDA | 11KV榴十線(XB30) 接地RY | FEEDER | D11/11/XB30/GDA |  |  |  | CDC | 342 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | XB30 | 榴十線(XB30) 79RY |  | 79UL | [17 empty] | 1-3B-10 |  | 2-45 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB30_79UL | 11KV榴十線(XB30) 79RY U/L | FEEDER | D11/11/XB30/79UL |  |  |  | CDC | 343 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D11 | 榴中DS | 11 | 11kV | XB30_LCO | 榴十線(XB30) LCO |  | TapPosMv | [17 empty] | 1-3B-11 |  | 2-46 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB30_LCO_TAP | 11KV榴十線(XB30) LCO TAP | FEEDER | D11/11/XB30/ADJ |  |  |  | CDC | 344 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D11 | 榴中DS | 11 | 11kV | XB30 | XB30(11KV榴十線) |  | CB | [17 empty] | 2-0E-03 |  | 2-44 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB30_CB | XB30(11KV榴十線) CB | FEEDER | D11/11/XB30/CB |  |  |  | CDC | 345 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | XB51 | 榴51線(XB51) |  | PHA | [17 empty] | 2-01-01 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB51_PHA | 23KV榴51線(XB51) 相間RY | FEEDER | D11/22/XB51/PHA |  |  |  | CDC | 346 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB51 | 榴51線(XB51) |  | GDA | [17 empty] | 2-01-02 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB51_GDA | 23KV榴51線(XB51) 接地RY | FEEDER | D11/22/XB51/GDA |  |  |  | CDC | 347 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB51 | 榴51線(XB51) 79RY |  | 79UL | [17 empty] | 1-39-04 |  | 2-04 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB51_79UL | 23KV榴51線(XB51) 79RY U/L | FEEDER | D11/22/XB51/79UL |  |  |  | CDC | 348 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D11 | 榴中DS | 22 | 22kV | XB51_LCO | 榴51線(XB51) LCO |  | TapPosMv | [17 empty] | 1-39-05 |  | 2-05 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB51_LCO_TAP | 23KV榴51線(XB51) LCO TAP | FEEDER | D11/22/XB51/ADJ |  |  |  | CDC | 349 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D11 | 榴中DS | 22 | 22kV | XB51 | XB51(23KV榴51線) |  | CB | [17 empty] | 2-01-04 |  | 2-03 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB51_CB | XB51(23KV榴51線) CB | FEEDER | D11/22/XB51/CB |  |  |  | CDC | 350 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | XB52 | 榴52線(XB52) |  | PHA | [17 empty] | 2-01-05 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB52_PHA | 23KV榴52線(XB52) 相間RY | FEEDER | D11/22/XB52/PHA |  |  |  | CDC | 351 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB52 | 榴52線(XB52) |  | GDA | [17 empty] | 2-01-06 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB52_GDA | 23KV榴52線(XB52) 接地RY | FEEDER | D11/22/XB52/GDA |  |  |  | CDC | 352 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB52 | 榴52線(XB52) 79RY |  | 79UL | [17 empty] | 1-39-06 |  | 2-07 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB52_79UL | 23KV榴52線(XB52) 79RY U/L | FEEDER | D11/22/XB52/79UL |  |  |  | CDC | 353 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D11 | 榴中DS | 22 | 22kV | XB52_LCO | 榴52線(XB52) LCO |  | TapPosMv | [17 empty] | 1-39-07 |  | 2-08 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB52_LCO_TAP | 23KV榴52線(XB52) LCO TAP | FEEDER | D11/22/XB52/ADJ |  |  |  | CDC | 354 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D11 | 榴中DS | 22 | 22kV | XB52 | XB52(23KV榴52線) |  | CB | [17 empty] | 2-02-00 |  | 2-06 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB52_CB | XB52(23KV榴52線) CB | FEEDER | D11/22/XB52/CB |  |  |  | CDC | 355 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | XB53 | 榴53線(XB53) |  | PHA | [17 empty] | 2-02-01 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB53_PHA | 23KV榴53線(XB53) 相間RY | FEEDER | D11/22/XB53/PHA |  |  |  | CDC | 356 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB53 | 榴53線(XB53) |  | GDA | [17 empty] | 2-02-02 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB53_GDA | 23KV榴53線(XB53) 接地RY | FEEDER | D11/22/XB53/GDA |  |  |  | CDC | 357 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB53 | 榴53線(XB53) 79RY |  | 79UL | [17 empty] | 1-39-08 |  | 2-0A | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB53_79UL | 23KV榴53線(XB53) 79RY U/L | FEEDER | D11/22/XB53/79UL |  |  |  | CDC | 358 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D11 | 榴中DS | 22 | 22kV | XB53_LCO | 榴53線(XB53) LCO |  | TapPosMv | [17 empty] | 1-39-09 |  | 2-0B | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB53_LCO_TAP | 23KV榴53線(XB53) LCO TAP | FEEDER | D11/22/XB53/ADJ |  |  |  | CDC | 359 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D11 | 榴中DS | 22 | 22kV | XB53 | XB53(23KV榴53線) |  | CB | [17 empty] | 2-02-04 |  | 2-09 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB53_CB | XB53(23KV榴53線) CB | FEEDER | D11/22/XB53/CB |  |  |  | CDC | 360 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | XB54 | 榴54線(XB54) |  | PHA | [17 empty] | 2-02-05 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB54_PHA | 23KV榴54線(XB54) 相間RY | FEEDER | D11/22/XB54/PHA |  |  |  | CDC | 361 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB54 | 榴54線(XB54) |  | GDA | [17 empty] | 2-02-06 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB54_GDA | 23KV榴54線(XB54) 接地RY | FEEDER | D11/22/XB54/GDA |  |  |  | CDC | 362 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB54 | 榴54線(XB54) 79RY |  | 79UL | [17 empty] | 1-39-10 |  | 2-0D | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB54_79UL | 23KV榴54線(XB54) 79RY U/L | FEEDER | D11/22/XB54/79UL |  |  |  | CDC | 363 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D11 | 榴中DS | 22 | 22kV | XB54_LCO | 榴54線(XB54) LCO |  | TapPosMv | [17 empty] | 1-39-11 |  | 2-0E | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB54_LCO_TAP | 23KV榴54線(XB54) LCO TAP | FEEDER | D11/22/XB54/ADJ |  |  |  | CDC | 364 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D11 | 榴中DS | 22 | 22kV | XB54 | XB54(23KV榴54線) |  | CB | [17 empty] | 2-03-00 |  | 2-0C | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB54_CB | XB54(23KV榴54線) CB | FEEDER | D11/22/XB54/CB |  |  |  | CDC | 365 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | XB55 | 榴55線(XB55) |  | PHA | [17 empty] | 2-03-01 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB55_PHA | 23KV榴55線(XB55) 相間RY | FEEDER | D11/22/XB55/PHA |  |  |  | CDC | 366 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB55 | 榴55線(XB55) |  | GDA | [17 empty] | 2-03-02 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB55_GDA | 23KV榴55線(XB55) 接地RY | FEEDER | D11/22/XB55/GDA |  |  |  | CDC | 367 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB55 | 榴55線(XB55) 79RY |  | 79UL | [17 empty] | 1-39-12 |  | 2-10 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB55_79UL | 23KV榴55線(XB55) 79RY U/L | FEEDER | D11/22/XB55/79UL |  |  |  | CDC | 368 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D11 | 榴中DS | 22 | 22kV | XB55_LCO | 榴55線(XB55) LCO |  | TapPosMv | [17 empty] | 1-39-13 |  | 2-11 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB55_LCO_TAP | 23KV榴55線(XB55) LCO TAP | FEEDER | D11/22/XB55/ADJ |  |  |  | CDC | 369 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D11 | 榴中DS | 22 | 22kV | XB55 | XB55(23KV榴55線) |  | CB | [17 empty] | 2-03-04 |  | 2-0F | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB55_CB | XB55(23KV榴55線) CB | FEEDER | D11/22/XB55/CB |  |  |  | CDC | 370 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | XB56 | 榴56線(XB56) |  | PHA | [17 empty] | 2-04-06 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB56_PHA | 23KV榴56線(XB56) 相間RY | FEEDER | D11/22/XB56/PHA |  |  |  | CDC | 371 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB56 | 榴56線(XB56) |  | GDA | [17 empty] | 2-04-07 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB56_GDA | 23KV榴56線(XB56) 接地RY | FEEDER | D11/22/XB56/GDA |  |  |  | CDC | 372 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB56 | 榴56線(XB56) 79RY |  | 79UL | [17 empty] | 1-39-14 |  | 2-15 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB56_79UL | 23KV榴56線(XB56) 79RY U/L | FEEDER | D11/22/XB56/79UL |  |  |  | CDC | 373 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D11 | 榴中DS | 22 | 22kV | XB56_LCO | 榴56線(XB56) LCO |  | TapPosMv | [17 empty] | 1-39-15 |  | 2-16 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB56_LCO_TAP | 23KV榴56線(XB56) LCO TAP | FEEDER | D11/22/XB56/ADJ |  |  |  | CDC | 374 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D11 | 榴中DS | 22 | 22kV | XB56 | XB56(23KV榴56線) |  | CB | [17 empty] | 2-05-01 |  | 2-14 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB56_CB | XB56(23KV榴56線) CB | FEEDER | D11/22/XB56/CB |  |  |  | CDC | 375 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | XB57 | 榴57線(XB57) |  | PHA | [17 empty] | 2-05-02 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB57_PHA | 23KV榴57線(XB57) 相間RY | FEEDER | D11/22/XB57/PHA |  |  |  | CDC | 376 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB57 | 榴57線(XB57) |  | GDA | [17 empty] | 2-05-03 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB57_GDA | 23KV榴57線(XB57) 接地RY | FEEDER | D11/22/XB57/GDA |  |  |  | CDC | 377 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB57 | 榴57線(XB57) 79RY |  | 79UL | [17 empty] | 1-3A-00 |  | 2-18 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB57_79UL | 23KV榴57線(XB57) 79RY U/L | FEEDER | D11/22/XB57/79UL |  |  |  | CDC | 378 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D11 | 榴中DS | 22 | 22kV | XB57_LCO | 榴57線(XB57) LCO |  | TapPosMv | [17 empty] | 1-3A-01 |  | 2-19 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB57_LCO_TAP | 23KV榴57線(XB57) LCO TAP | FEEDER | D11/22/XB57/ADJ |  |  |  | CDC | 379 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D11 | 榴中DS | 22 | 22kV | XB57 | XB57(23KV榴57線) |  | CB | [17 empty] | 2-05-05 |  | 2-17 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB57_CB | XB57(23KV榴57線) CB | FEEDER | D11/22/XB57/CB |  |  |  | CDC | 380 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | XB58 | 榴58線(XB58) |  | PHA | [17 empty] | 2-05-06 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB58_PHA | 23KV榴58線(XB58) 相間RY | FEEDER | D11/22/XB58/PHA |  |  |  | CDC | 381 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB58 | 榴58線(XB58) |  | GDA | [17 empty] | 2-05-07 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB58_GDA | 23KV榴58線(XB58) 接地RY | FEEDER | D11/22/XB58/GDA |  |  |  | CDC | 382 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB58 | 榴58線(XB58) 79RY |  | 79UL | [17 empty] | 1-3A-02 |  | 2-1B | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB58_79UL | 23KV榴58線(XB58) 79RY U/L | FEEDER | D11/22/XB58/79UL |  |  |  | CDC | 383 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D11 | 榴中DS | 22 | 22kV | XB58_LCO | 榴58線(XB58) LCO |  | TapPosMv | [17 empty] | 1-3A-03 |  | 2-1C | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB58_LCO_TAP | 23KV榴58線(XB58) LCO TAP | FEEDER | D11/22/XB58/ADJ |  |  |  | CDC | 384 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D11 | 榴中DS | 22 | 22kV | XB58 | XB58(23KV榴58線) |  | CB | [17 empty] | 2-06-01 |  | 2-1A | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB58_CB | XB58(23KV榴58線) CB | FEEDER | D11/22/XB58/CB |  |  |  | CDC | 385 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | XB59 | 榴59線(XB59) |  | PHA | [17 empty] | 2-06-02 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB59_PHA | 23KV榴59線(XB59) 相間RY | FEEDER | D11/22/XB59/PHA |  |  |  | CDC | 386 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB59 | 榴59線(XB59) |  | GDA | [17 empty] | 2-06-03 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB59_GDA | 23KV榴59線(XB59) 接地RY | FEEDER | D11/22/XB59/GDA |  |  |  | CDC | 387 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB59 | 榴59線(XB59) 79RY |  | 79UL | [17 empty] | 1-3A-04 |  | 2-1E | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB59_79UL | 23KV榴59線(XB59) 79RY U/L | FEEDER | D11/22/XB59/79UL |  |  |  | CDC | 388 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D11 | 榴中DS | 22 | 22kV | XB59_LCO | 榴59線(XB59) LCO |  | TapPosMv | [17 empty] | 1-3A-05 |  | 2-1F | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB59_LCO_TAP | 23KV榴59線(XB59) LCO TAP | FEEDER | D11/22/XB59/ADJ |  |  |  | CDC | 389 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D11 | 榴中DS | 22 | 22kV | XB59 | XB59(23KV榴59線) |  | CB | [17 empty] | 2-06-05 |  | 2-1D | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB59_CB | XB59(23KV榴59線) CB | FEEDER | D11/22/XB59/CB |  |  |  | CDC | 390 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | XB60 | 榴60線(XB60) |  | PHA | [17 empty] | 2-06-06 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB60_PHA | 23KV榴60線(XB60) 相間RY | FEEDER | D11/22/XB60/PHA |  |  |  | CDC | 391 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB60 | 榴60線(XB60) |  | GDA | [17 empty] | 2-06-07 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB60_GDA | 23KV榴60線(XB60) 接地RY | FEEDER | D11/22/XB60/GDA |  |  |  | CDC | 392 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | XB60 | 榴60線(XB60) 79RY |  | 79UL | [17 empty] | 1-3A-06 |  | 2-21 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB60_79UL | 23KV榴60線(XB60) 79RY U/L | FEEDER | D11/22/XB60/79UL |  |  |  | CDC | 393 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D11 | 榴中DS | 22 | 22kV | XB60_LCO | 榴60線(XB60) LCO |  | TapPosMv | [17 empty] | 1-3A-07 |  | 2-22 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB60_LCO_TAP | 23KV榴60線(XB60) LCO TAP | FEEDER | D11/22/XB60/ADJ |  |  |  | CDC | 394 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D11 | 榴中DS | 22 | 22kV | XB60 | XB60(23KV榴60線) |  | CB | [17 empty] | 2-07-01 |  | 2-20 | [5 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB60_CB | XB60(23KV榴60線) CB | FEEDER | D11/22/XB60/CB |  |  |  | CDC | 395 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | 100 | TIE(100) |  | CB | [17 empty] | 2-03-07 |  | 2-23 | [5 empty] | ADCS_N | [8 empty] | 榴中DS.100_CB | 100(TIE) CB | TIE | D11/11/100/CB |  |  |  | CDC | 396 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | 100 | TIE(100) |  | 51A | [17 empty] | 2-03-05 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.100_51A | 11KV TIE(100) 51RY | TIE | D11/11/100/PHA |  |  |  | CDC | 397 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 100 | TIE(100) |  | 51NA | [17 empty] | 2-03-06 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.100_51NA | 11KV TIE(100) 51N RY | TIE | D11/11/100/GDA |  |  |  | CDC | 398 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [17 empty] | 1-0F-02 |  | 1-35 | [5 empty] | 161KV_N | [8 empty] | 榴中DS.1500_CB | 1500(TIE) CB | TIE | D11/161/1500/CB |  |  |  | CDC | 399 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | 1500 | TIE(1500) |  | 50A | [17 empty] | 1-0B-00 | [7 empty] | 161KV_N | [8 empty] | 榴中DS.1500_50A | 161KV TIE(1500) 50RY | TIE | D11/161/1500/50A |  |  |  | CDC | 400 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [16 empty] | 2-30-00 | 2-30-01 | 1-36 | [5 empty] | ADCS_N | [8 empty] | 榴中DS.1501_DS | 1501(TIE) DS | TIE | D11/161/1500/DS1 |  |  |  | CDC | 401 | GENERICDIPoint | DS047_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D11 | 榴中DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [16 empty] | 2-30-02 | 2-30-03 | 1-37 | [5 empty] | ADCS_N | [8 empty] | 榴中DS.1502_DS | 1502(TIE) DS | TIE | D11/161/1500/DS2 |  |  |  | CDC | 402 | GENERICDIPoint | DS047_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D11 | 榴中DS | 0 |  | 200 | TIE(200) |  | CB | [17 empty] | 2-0B-01 |  | 2-47 | [5 empty] | ADCS_N | [8 empty] | 榴中DS.200_CB | 200(TIE) CB | TIE | D11/22/200/CB |  |  |  | CDC | 403 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | 200 | TIE(200) |  | 51A | [17 empty] | 2-0A-07 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.200_51A | 23KV TIE(200) 51RY | TIE | D11/22/200/PHA |  |  |  | CDC | 404 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 200 | TIE(200) |  | 51NA | [17 empty] | 2-0B-00 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.200_51NA | 23KV TIE(200) 51N RY | TIE | D11/22/200/GDA |  |  |  | CDC | 405 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 390 | #1SSTR(390) |  | CB | [17 empty] | 2-00-02 |  | 2-00 | [5 empty] | 161KV_N | [8 empty] | 榴中DS.390_CB | 390(#1SSTR) CB | OTHER | D11/11/390/CB |  |  |  | CDC | 406 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | 1SSTR | #1SSTR |  | 51A | [17 empty] | 2-00-00 | [7 empty] | 161KV_N | [8 empty] | 榴中DS.#1SSTR_51A | #1SSTR 51RY | OTHER | D11/11/390/PHA |  |  |  | CDC | 407 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 1SSTR | #1SSTR |  | 51NA | [17 empty] | 2-00-01 | [7 empty] | 161KV_N | [8 empty] | 榴中DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | D11/11/390/GDA |  |  |  | CDC | 408 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 490 | #2SSTR(490) |  | CB | [17 empty] | 2-07-04 |  | 2-24 | [5 empty] | 161KV_N | [8 empty] | 榴中DS.490_CB | 490(#2SSTR) CB | OTHER | D11/22/490/CB |  |  |  | CDC | 409 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | 2SSTR | #2SSTR |  | 51A | [17 empty] | 2-07-02 | [7 empty] | 161KV_N | [8 empty] | 榴中DS.#2SSTR_51A | #2SSTR 51RY | OTHER | D11/22/490/PHA |  |  |  | CDC | 410 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 2SSTR | #2SSTR |  | 51NA | [17 empty] | 2-07-03 | [7 empty] | 161KV_N | [8 empty] | 榴中DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | D11/22/490/GDA |  |  |  | CDC | 411 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB | [17 empty] | 1-0F-00 |  | 1-74 | [5 empty] | 161KV_N | [8 empty] | 榴中DS.1750_CB | 1750(#1DTR) CB | MTR | D11/161/1750/CB |  |  |  | CDC | 412 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | 310 | #1DTR(310) |  | CB | [17 empty] | 1-0F-03 |  | 2-01 | [5 empty] | ADCS_N | [8 empty] | 榴中DS.310_CB | 310(#1DTR) CB | MTR | D11/11/310/CB |  |  |  | CDC | 413 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | 320 | #1DTR(320) |  | CB | [17 empty] | 1-0F-06 |  | 2-12 | [5 empty] | ADCS_N | [8 empty] | 榴中DS.320_CB | 320(#1DTR) CB | MTR | D11/22/320/CB |  |  |  | CDC | 414 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | 1DTR | #1DTR |  | 51A | [17 empty] | 1-06-05 | [7 empty] | 161KV_N | [8 empty] | 榴中DS.#1DTR_51A | #1DTR 51RY | MTR | D11//1DTR/PHA |  |  |  | CDC | 415 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 1DTR | #1DTR |  | 51NA | [17 empty] | 1-06-06 | [7 empty] | 161KV_N | [8 empty] | 榴中DS.#1DTR_51NA | #1DTR 51N RY | MTR | D11//1DTR/GDA |  |  |  | CDC | 416 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 1DTR | #1DTR |  | 51ZA | [17 empty] | 1-06-04 | [7 empty] | 161KV_N | [8 empty] | 榴中DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | D11//1DTR/51ZA |  |  |  | CDC | 417 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 1DTR | #1DTR |  | 87A | [17 empty] | 1-06-02 | [7 empty] | 161KV_N | [8 empty] | 榴中DS.#1DTR_87A | #1DTR 87RY | MTR | D11//1DTR/87A |  |  |  | CDC | 418 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 1DTR | #1DTR |  | 87UL | [17 empty] | 1-34-13 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.#1DTR_87UL | #1DTR 87RY U/L | MTR | D11//1DTR/87UL |  |  |  | CDC | 419 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D11 | 榴中DS | 0 |  | 310 | #1DTR(310) |  | 51A | [17 empty] | 1-06-00 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.310_51A | #1DTR二次側(310) 51RY | MTR | D11/11/310/PHA1 |  |  |  | CDC | 420 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 320 | #1DTR(320) |  | 51A | [17 empty] | 1-06-01 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.320_51A | #1DTR二次側(320) 51RY | MTR | D11/22/320/PHA1 |  |  |  | CDC | 421 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 1DTR | #1DTR |  | 96PA | [17 empty] | 1-06-03 | [7 empty] | 161KV_N | [8 empty] | 榴中DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | D11//1DTR/96PA |  |  |  | CDC | 422 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 1DTR | #1DTR |  | 96D | [17 empty] | 1-30-06 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.#1DTR_96D | #1DTR 96D RY | MTR | D11//1DTR/96D |  |  |  | CDC | 423 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 1DTR | #1DTR |  | 96P | [17 empty] | 1-30-11 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.#1DTR_96P | #1DTR 96P RY | MTR | D11//1DTR/96P |  |  |  | CDC | 424 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 1DTR | #1DTR |  | 63Q | [17 empty] | 1-30-05 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.#1DTR_63Q | #1DTR 63Q RY | MTR | D11//1DTR/63Q |  |  |  | CDC | 425 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 1DTR | #1DTR |  | 96B1 | [17 empty] | 1-30-08 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | D11//1DTR/96B1 |  |  |  | CDC | 426 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 1DTR | #1DTR |  | 96B2 | [17 empty] | 1-30-07 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | D11//1DTR/96B2 |  |  |  | CDC | 427 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 1DTR | #1DTR |  | TRA | [17 empty] | 1-30-01 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.#1DTR_TRA | #1DTR 重故障 | MTR | D11//1DTR/TRA |  |  |  | CDC | 428 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 1DTR | #1DTR |  | TRF | [17 empty] | 1-30-02 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.#1DTR_TRF | #1DTR 輕故障 | MTR | D11//1DTR/TRF |  |  |  | CDC | 429 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 1DTR(A) | #1DTR(A) |  | SupLocal | [17 empty] | 1-30-09 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | D11//1DTR(A)/SupLocal |  |  |  | CDC | 430 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D11 | 榴中DS | 0 |  | 1DTR(A) | #1DTR(A) |  | A_M | [17 empty] | 1-30-03 |  | 1-01 | [5 empty] | ADCS_N | [8 empty] | 榴中DS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | D11//1DTR(A)/Tap Chan |  |  |  | CDC | 431 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D11 | 榴中DS | 0 |  | 1DTR(B) | #1DTR(B) |  | SupLocal | [17 empty] | 1-30-10 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | D11//1DTR(B)/SupLocal |  |  |  | CDC | 432 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D11 | 榴中DS | 0 |  | 1DTR(B) | #1DTR(B) |  | A_M | [17 empty] | 1-30-04 |  | 1-03 | [5 empty] | ADCS_N | [8 empty] | 榴中DS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | D11//1DTR(B)/Tap Chan |  |  |  | CDC | 433 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D11 | 榴中DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 | [16 empty] | 2-36-04 | 2-36-05 | 1-75 | [5 empty] | ADCS_N | [8 empty] | 榴中DS.1751_DS | 1751(#1DTR) DS | MTR | D11/161/1750/DS1 |  |  |  | CDC | 434 | GENERICDIPoint | DS047_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D11 | 榴中DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 | [16 empty] | 2-36-06 | 2-36-07 | 1-76 | [5 empty] | ADCS_N | [8 empty] | 榴中DS.1752_DS | 1752(#1DTR) DS | MTR | D11/161/1750/DS2 |  |  |  | CDC | 435 | GENERICDIPoint | DS047_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D11 | 榴中DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB | [17 empty] | 1-0F-01 |  | 1-77 | [5 empty] | 161KV_N | [8 empty] | 榴中DS.1760_CB | 1760(#2DTR) CB | MTR | D11/161/1760/CB |  |  |  | CDC | 436 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | 330 | #2DTR(330) |  | CB | [17 empty] | 1-10-01 |  | 2-25 | [5 empty] | ADCS_N | [8 empty] | 榴中DS.330_CB | 330(#2DTR) CB | MTR | D11/11/330/CB |  |  |  | CDC | 437 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | 340 | #2DTR(340) |  | CB | [17 empty] | 1-10-04 |  | 2-36 | [5 empty] | ADCS_N | [8 empty] | 榴中DS.340_CB | 340(#2DTR) CB | MTR | D11/22/340/CB |  |  |  | CDC | 438 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | 2DTR | #2DTR |  | 51A | [17 empty] | 1-07-06 | [7 empty] | 161KV_N | [8 empty] | 榴中DS.#2DTR_51A | #2DTR 51RY | MTR | D11//2DTR/PHA |  |  |  | CDC | 439 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 2DTR | #2DTR |  | 51NA | [17 empty] | 1-07-07 | [7 empty] | 161KV_N | [8 empty] | 榴中DS.#2DTR_51NA | #2DTR 51N RY | MTR | D11//2DTR/GDA |  |  |  | CDC | 440 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 2DTR | #2DTR |  | 51ZA | [17 empty] | 1-07-05 | [7 empty] | 161KV_N | [8 empty] | 榴中DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | D11//2DTR/51ZA |  |  |  | CDC | 441 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 2DTR | #2DTR |  | 87A | [17 empty] | 1-07-03 | [7 empty] | 161KV_N | [8 empty] | 榴中DS.#2DTR_87A | #2DTR 87RY | MTR | D11//2DTR/87A |  |  |  | CDC | 442 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 2DTR | #2DTR |  | 87UL | [17 empty] | 1-34-14 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.#2DTR_87UL | #2DTR 87RY U/L | MTR | D11//2DTR/87UL |  |  |  | CDC | 443 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D11 | 榴中DS | 0 |  | 330 | #2DTR(330) |  | 51A | [17 empty] | 1-07-01 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.330_51A | #2DTR二次側(330) 51RY | MTR | D11/11/330/PHA1 |  |  |  | CDC | 444 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 340 | #2DTR(340) |  | 51A | [17 empty] | 1-07-02 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.340_51A | #2DTR二次側(340) 51RY | MTR | D11/22/340/PHA1 |  |  |  | CDC | 445 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 2DTR | #2DTR |  | 96PA | [17 empty] | 1-07-04 | [7 empty] | 161KV_N | [8 empty] | 榴中DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | D11//2DTR/96PA |  |  |  | CDC | 446 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 2DTR | #2DTR |  | 96D | [17 empty] | 1-31-01 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.#2DTR_96D | #2DTR 96D RY | MTR | D11//2DTR/96D |  |  |  | CDC | 447 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 2DTR | #2DTR |  | 96P | [17 empty] | 1-31-06 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.#2DTR_96P | #2DTR 96P RY | MTR | D11//2DTR/96P |  |  |  | CDC | 448 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 2DTR | #2DTR |  | 63Q | [17 empty] | 1-31-00 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.#2DTR_63Q | #2DTR 63Q RY | MTR | D11//2DTR/63Q |  |  |  | CDC | 449 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 2DTR | #2DTR |  | 96B1 | [17 empty] | 1-31-03 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | D11//2DTR/96B1 |  |  |  | CDC | 450 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 2DTR | #2DTR |  | 96B2 | [17 empty] | 1-31-02 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | D11//2DTR/96B2 |  |  |  | CDC | 451 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 2DTR | #2DTR |  | TRA | [17 empty] | 1-30-12 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.#2DTR_TRA | #2DTR 重故障 | MTR | D11//2DTR/TRA |  |  |  | CDC | 452 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 2DTR | #2DTR |  | TRF | [17 empty] | 1-30-13 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.#2DTR_TRF | #2DTR 輕故障 | MTR | D11//2DTR/TRF |  |  |  | CDC | 453 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 2DTR(A) | #2DTR(A) |  | SupLocal | [17 empty] | 1-31-04 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | D11//2DTR(A)/SupLocal |  |  |  | CDC | 454 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D11 | 榴中DS | 0 |  | 2DTR(A) | #2DTR(A) |  | A_M | [17 empty] | 1-30-14 |  | 1-05 | [5 empty] | ADCS_N | [8 empty] | 榴中DS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | D11//2DTR(A)/Tap Chan |  |  |  | CDC | 455 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D11 | 榴中DS | 0 |  | 2DTR(B) | #2DTR(B) |  | SupLocal | [17 empty] | 1-31-05 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | D11//2DTR(B)/SupLocal |  |  |  | CDC | 456 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D11 | 榴中DS | 0 |  | 2DTR(B) | #2DTR(B) |  | A_M | [17 empty] | 1-30-15 |  | 1-07 | [5 empty] | ADCS_N | [8 empty] | 榴中DS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | D11//2DTR(B)/Tap Chan |  |  |  | CDC | 457 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D11 | 榴中DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 | [16 empty] | 2-36-08 | 2-36-09 | 1-78 | [5 empty] | ADCS_N | [8 empty] | 榴中DS.1761_DS | 1761(#2DTR) DS | MTR | D11/161/1760/DS1 |  |  |  | CDC | 458 | GENERICDIPoint | DS047_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D11 | 榴中DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 | [16 empty] | 2-36-10 | 2-36-11 | 1-79 | [5 empty] | ADCS_N | [8 empty] | 榴中DS.1762_DS | 1762(#2DTR) DS | MTR | D11/161/1760/DS2 |  |  |  | CDC | 459 | GENERICDIPoint | DS047_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D11 | 榴中DS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 2-01-00 |  | 2-02 | [5 empty] | ADCS_N | [8 empty] | 榴中DS.210_CB | 210(11KV #1SC) CB | SC | D11/11/210/CB |  |  |  | CDC | 460 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 2-00-06 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.210_SCA | 11KV #1SC 51,51N RY | SC | D11/11/210/SCA |  |  |  | CDC | 461 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 2-00-07 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | D11/11/210/UVA |  |  |  | CDC | 462 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | 210 | #1SC(210) |  | LBS | [17 empty] | 2-36-14 | 2-36-15 | 1-7C | [5 empty] | ADCS_N | [8 empty] | 榴中DS.210_LBS | 210(11KV #1SC) LBS | SC | D11/11/210/LBS |  |  |  | CDC | 463 | GENERICDIPoint | DS047_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D11 | 榴中DS | 11 | 11kV | 230 | #3SC(230) |  | CB | [17 empty] | 2-08-02 |  | 2-26 | [5 empty] | ADCS_N | [8 empty] | 榴中DS.230_CB | 230(11KV #3SC) CB | SC | D11/11/230/CB |  |  |  | CDC | 464 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 11 | 11kV | 230 | #3SC(230) |  | SCA | [17 empty] | 2-08-00 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.230_SCA | 11KV #3SC 51,51N RY | SC | D11/11/230/SCA |  |  |  | CDC | 465 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | 230 | #3SC(230) |  | UVA | [17 empty] | 2-08-01 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | D11/11/230/UVA |  |  |  | CDC | 466 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | 230 | #3SC(230) |  | LBS | [17 empty] | 2-37-00 | 2-37-01 | 1-7D | [5 empty] | ADCS_N | [8 empty] | 榴中DS.230_LBS | 230(11KV #3SC) LBS | SC | D11/11/230/LBS |  |  |  | CDC | 467 | GENERICDIPoint | DS047_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D11 | 榴中DS | 22 | 22kV | 220 | #2SC(220) |  | CB | [17 empty] | 2-04-05 |  | 2-13 | [5 empty] | ADCS_N | [8 empty] | 榴中DS.220_CB | 220(23KV #2SC) CB | SC | D11/22/220/CB |  |  |  | CDC | 468 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | 220 | #2SC(220) |  | SCA | [17 empty] | 2-04-03 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.220_SCA | 23KV #2SC 51,51N RY | SC | D11/22/220/SCA |  |  |  | CDC | 469 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | 220 | #2SC(220) |  | UVA | [17 empty] | 2-04-04 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.220_UVA | 23KV #2SC 27RY(欠壓) | SC | D11/22/220/UVA |  |  |  | CDC | 470 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | 240 | #4SC(240) |  | CB | [17 empty] | 2-0B-07 |  | 2-37 | [5 empty] | ADCS_N | [8 empty] | 榴中DS.240_CB | 240(23KV #4SC) CB | SC | D11/22/240/CB |  |  |  | CDC | 471 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 22 | 22kV | 240 | #4SC(240) |  | SCA | [17 empty] | 2-0B-05 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.240_SCA | 23KV #4SC 51,51N RY | SC | D11/22/240/SCA |  |  |  | CDC | 472 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | 240 | #4SC(240) |  | UVA | [17 empty] | 2-0B-06 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.240_UVA | 23KV #4SC 27RY(欠壓) | SC | D11/22/240/UVA |  |  |  | CDC | 473 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1611BUS | #1BUS |  | VUA | [17 empty] | 1-37-04 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | D11/161/1BUS/BUS_VUA |  |  |  | CDC | 474 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1611BUS | #1BUS |  | 87A | [17 empty] | 1-0B-01 | [7 empty] | 161KV_N | [8 empty] | 榴中DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | D11/161/1BUS/87A |  |  |  | CDC | 475 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1611BUS | #1BUS |  | 87UL | [17 empty] | 1-35-01 |  | 1-17 | [5 empty] | ADCS_N | [8 empty] | 榴中DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | D11/161/1BUS/87UL |  |  |  | CDC | 476 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D11 | 榴中DS | 0 |  |  |  |  | 15B1E | [17 empty] | 2-31-04 | 2-31-05 | [6 empty] | ADCS_N | [8 empty] | 榴中DS.15B1E | 15B1E | OTHER |  |  |  |  | CDC | 477 | GENERICDIPoint | DS047_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D11 | 榴中DS | 161 | 161kV | 1612BUS | #2BUS |  | VUA | [17 empty] | 1-37-05 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | D11/161/2BUS/BUS_VUA |  |  |  | CDC | 478 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1612BUS | #2BUS |  | 87A | [17 empty] | 1-0B-02 | [7 empty] | 161KV_N | [8 empty] | 榴中DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | D11/161/2BUS/87A |  |  |  | CDC | 479 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | 1612BUS | #2BUS |  | 87UL | [17 empty] | 1-35-02 |  | 1-18 | [5 empty] | ADCS_N | [8 empty] | 榴中DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | D11/161/2BUS/87UL |  |  |  | CDC | 480 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D11 | 榴中DS | 0 |  |  |  |  | 15B2E | [17 empty] | 2-31-06 | 2-31-07 | [6 empty] | ADCS_N | [8 empty] | 榴中DS.15B2E | 15B2E | OTHER |  |  |  |  | CDC | 481 | GENERICDIPoint | DS047_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D11 | 榴中DS | 161 | 161kV |  |  |  | CBA | [17 empty] | 1-35-05 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.161KV_CBA | 161KV斷路器重故障 | OTHER | D11/161/ComPoint/CBA |  |  |  | CDC | 482 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV |  |  |  | CBF | [17 empty] | 1-35-06 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | D11/161/ComPoint/CBF |  |  |  | CDC | 483 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | LINE | LINE |  | RCA | [17 empty] | 1-0E-05 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | D11/161/ComPoint/RCA |  |  |  | CDC | 484 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | _SC | 11/ SC |  | 60A | [17 empty] | 1-35-04 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.23KV_SC_60A | 11/23KV SC 60A | OTHER | D11/0/ComPoint/FDR_60A |  |  |  | CDC | 485 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | ADCS_N | [8 empty] | 榴中DS.TEST_CB | TEST CB | OTHER | D11/0/RTU/Test_CB |  |  |  | CDC | 486 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  |  |  |  | Fire1 | [17 empty] | 1-36-10 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | D11/0/StaDev/Fire1 |  |  |  | CDC | 487 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  |  |  |  | 25TA | [17 empty] | 1-0E-04 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | D11/161/ComPoint/25TA |  |  |  | CDC | 488 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  |  |  |  | ACB1 | [17 empty] | 1-37-12 |  | 2-4B | [5 empty] | ADCS_N | [8 empty] | 榴中DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | D11/0/StaDev/ACB1 |  |  |  | CDC | 489 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
D11 | 榴中DS | 0 |  |  |  |  | ACB2 | [17 empty] | 1-37-13 |  | 2-4C | [5 empty] | ADCS_N | [8 empty] | 榴中DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | D11/0/StaDev/ACB2 |  |  |  | CDC | 490 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
D11 | 榴中DS | 0 |  |  |  |  | ACBA | [17 empty] | 1-38-08 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.所內電源ACBA | 所內電源故障警報 | OTHER | D11/0/StaDev/ACBA |  |  |  | CDC | 491 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 所內電源開關ACB | 所內電源開關ACB |  | ACBT | [17 empty] | 1-37-14 |  | 2-4D | [5 empty] | ADCS_N | [8 empty] | 榴中DS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | D11/0/StaDev/ACBT |  |  |  | CDC | 492 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D11 | 榴中DS | 0 |  |  |  |  | STUV | [17 empty] | 1-36-11 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | D11/0/StaDev/STUV |  |  |  | CDC | 493 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-36-05 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.直流充電機故障 | 變電所直流充電機故障 | OTHER | D11/0/StaDev/CHG1 |  |  |  | CDC | 494 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  |  |  |  | DCA | [17 empty] | 1-36-08 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.直流電源DCA | 直流電源故障警報 | OTHER | D11/0/StaDev/DCA |  |  |  | CDC | 495 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  |  |  |  | DCE | [17 empty] | 1-36-07 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.直流電源DCE | 直流電源接地故障警報 | OTHER | D11/0/StaDev/DCE |  |  |  | CDC | 496 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-36-06 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | D11/0/StaDev/CHG2 |  |  |  | CDC | 497 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  |  |  |  | CommACF | [17 empty] | 1-36-15 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | D11/0/StaDev/CommACF |  |  |  | CDC | 498 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  |  |  |  | Door1 | [17 empty] | 1-36-09 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.無人化門禁(1) | 無人化門禁(1)建築物,控制室大門 | OTHER | D11/0/StaDev/Door1 |  |  |  | CDC | 499 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  |  |  |  | Lights1 | [17 empty] | 1-36-12 |  | 2-4A | [5 empty] | ADCS_N | [8 empty] | 榴中DS.開關場照明(A) | 開關場照明(A) | OTHER | D11/0/StaDev/Lights1 |  |  |  | CDC | 500 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D11 | 榴中DS | 22 | 22kV | 11_ | 11/ |  | LOA | [17 empty] | 1-38-07 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.11/23KV_LOA | 11/23KV饋線復閉失敗閉鎖 | OTHER | D11/0/ComPoint/LOA |  |  |  | CDC | 501 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 1500TIE | 1500 |  | 50SA | [17 empty] | 1-36-04 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | D11/161/1500/50SA |  |  |  | CDC | 502 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | TEST/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 1510 | 榴中斗工一路(1510) |  | 25PFA | [17 empty] | 1-0D-07 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.1510_25PFA | 1510 同步校核電驛電源故障 | OTHER | D11/161/1510/25PFA |  |  |  | CDC | 503 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 1510 | 榴中斗工一路(1510) |  | 87LCFA | [17 empty] | 1-35-07 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.1510_87LCFA | 榴中斗工一路(1510) 87L通訊故障 | OTHER | D11/161/1510/87CFA |  |  |  | CDC | 504 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 1520 | 榴中斗工二路(1520) |  | 25PFA | [17 empty] | 1-0E-01 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.1520_25PFA | 1520 同步校核電驛電源故障 | OTHER | D11/161/1520/25PFA |  |  |  | CDC | 505 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 1520 | 榴中斗工二路(1520) |  | 87LCFA | [17 empty] | 1-35-08 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.1520_87LCFA | 榴中斗工二路(1520) 87L通訊故障 | OTHER | D11/161/1520/87CFA |  |  |  | CDC | 506 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV |  |  |  | OSCA | [17 empty] | 1-0B-03 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.161KV_OSCA | 161KV示波器啟動警報 | OTHER | D11/161/ComPoint/OSCA |  |  |  | CDC | 507 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | 11_ | 11/ 饋線 |  | RCA | [17 empty] | 2-0E-04 | [7 empty] | DDCS1_1 | [8 empty] | 榴中DS.23KV_RCA | 11/23KV 饋線 79RY復閉動作 | OTHER | D11/0/ComPoint/FDR_RCA |  |  |  | CDC | 508 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 310 | #1DTR(310) |  | GDA | [17 empty] | 1-0F-05 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.310_GDA | 310開關箱IED RY GDA | OTHER | D11/11/310/GDA |  |  |  | CDC | 509 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 310 | #1DTR(310) |  | PHA2 | [17 empty] | 1-0F-04 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.310_PHA2 | 310開關箱IED RY PHA | OTHER | D11/11/310/PHA2 |  |  |  | CDC | 510 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 320 | #1DTR(320) |  | GDA | [17 empty] | 1-10-00 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.320_GDA | 320開關箱IED RY GDA | OTHER | D11/22/320/GDA |  |  |  | CDC | 511 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 320 | #1DTR(320) |  | PHA2 | [17 empty] | 1-0F-07 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.320_PHA2 | 320開關箱IED RY PHA | OTHER | D11/22/320/PHA2 |  |  |  | CDC | 512 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 330 | #2DTR(330) |  | GDA | [17 empty] | 1-10-03 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.330_GDA | 330開關箱IED RY GDA | OTHER | D11/11/330/GDA |  |  |  | CDC | 513 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 330 | #2DTR(330) |  | PHA2 | [17 empty] | 1-10-02 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.330_PHA2 | 330開關箱IED RY PHA | OTHER | D11/11/330/PHA2 |  |  |  | CDC | 514 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 340 | #2DTR(340) |  | GDA | [17 empty] | 1-10-06 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.340_GDA | 340開關箱IED RY GDA | OTHER | D11/22/340/GDA |  |  |  | CDC | 515 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 340 | #2DTR(340) |  | PHA2 | [17 empty] | 1-10-05 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.340_PHA2 | 340開關箱IED RY PHA | OTHER | D11/22/340/PHA2 |  |  |  | CDC | 516 | GENERICDIPoint | DS047_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | COMM | 通訊處理單元 |  | SupLocal | [17 empty] | 1-38-01 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.COMM_S/L | 通訊處理單元 SUPY/LOCAL | OTHER | D11/0/StaDev/Comm_R_L |  |  |  | CDC | 517 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D11 | 榴中DS | 0 |  |  |  |  | OWFA | [17 empty] | 1-38-09 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.OWFA | 洩油池抽水泵警報 | OTHER | D11/0/ComPoint/2A5Other |  |  |  | CDC | 518 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  |  |  |  | 水位警報(1) | [17 empty] | 1-37-10 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.水位警報(1) | 地下室水位警報(1) | OTHER | D11/0/StaDev/Water1 |  |  |  | CDC | 519 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  |  |  |  | 水位警報(2) | [17 empty] | 1-37-11 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.水位警報(2) | 地下室水位警報(2) | OTHER | D11/0/StaDev/Water2 |  |  |  | CDC | 520 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 0 |  |  |  |  | OilLeak1 | [17 empty] | 1-38-10 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.洩油池警報(1) | 洩油池水位警報(1) | OTHER | D11/0/StaDev/OilLeak1 |  |  |  | CDC | 521 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  |  |  |  | OilLeak2 | [17 empty] | 1-38-11 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.洩油池警報(2) | 洩油池水位警報(2) | OTHER | D11/0/StaDev/OilLeak2 |  |  |  | CDC | 522 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  |  |  |  | 涵洞排水泵(1) | [17 empty] | 1-37-07 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.涵洞排水泵(1) | 涵洞排水幫浦故障(1) | OTHER | D11/0/StaDev/2A5Other |  |  |  | CDC | 523 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  |  |  |  | 涵洞排水泵(2) | [17 empty] | 1-37-08 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.涵洞排水泵(2) | 涵洞排水幫浦故障(2) | OTHER | D11/0/StaDev/3A5Other |  |  |  | CDC | 524 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  |  |  |  | 涵洞排水泵(3) | [17 empty] | 1-37-09 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.涵洞排水泵(3) | 涵洞排水幫浦故障(3) | OTHER | D11/0/StaDev/4A5Other |  |  |  | CDC | 525 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  |  |  |  | 揚水幫浦 | [17 empty] | 1-37-06 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.揚水幫浦 | 揚水幫浦故障 | OTHER | D11/0/StaDev/1A5Other |  |  |  | CDC | 526 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | 11_ | 11/ |  | CBA | [17 empty] | 1-38-05 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | D11/0/ComPoint/FDR_CBA |  |  |  | CDC | 527 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 22 | 22kV | 11_ | 11/ |  | CBF | [17 empty] | 1-38-06 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | D11/0/ComPoint/FDR_CBF |  |  |  | CDC | 528 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 1510 | 榴中斗工一路(1510) |  | RYFA | [17 empty] | 1-33-01 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.1510_RYA | 榴中斗工一路(1510)數位電驛故障 | OTHER | D11/161/1510/RYFA |  |  |  | CDC | 529 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 1520 | 榴中斗工二路(1520) |  | RYFA | [17 empty] | 1-33-02 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.1520_RYA | 榴中斗工二路(1520)數位電驛故障 | OTHER | D11/161/1520/RYFA |  |  |  | CDC | 530 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  |  |  |  | 通信機房溫度 | [17 empty] | 1-37-00 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.通信機房溫度 | 通訊室或控制室溫度警報 | OTHER | D11/0/StaDev/R_Temp |  |  |  | CDC | 531 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV |  |  |  | OSCF | [17 empty] | 1-32-15 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.161KV_OSCF | 161KV示波器故障 | OTHER | D11/161/ComPoint/OSCF |  |  |  | CDC | 532 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  |  |  |  | MCC | [17 empty] | 1-36-13 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.MCC故障 | MCC電驛故障 | OTHER | D11/0/StaDev/MCC |  |  |  | CDC | 533 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  |  |  |  | PMCC | [17 empty] | 1-36-14 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.PMCC故障 | PMCC電驛故障 | OTHER | D11/0/StaDev/PMCC |  |  |  | CDC | 534 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | LOCAL | LOCAL |  | SCADAA | [17 empty] | 1-37-15 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.SCADA故障 | LOCAL SCADA故障 | OTHER | D11/0/StaDev/SCADAA |  |  |  | CDC | 535 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  |  |  |  | TCA | [17 empty] | 1-3B-12 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.TCA | 斷路器跳脫回路故障 | OTHER | D11/0/ComPoint/1A5Other |  |  |  | CDC | 536 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  |  |  |  | Burglar1 | [17 empty] | 1-37-03 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | D11/0/StaDev/Burglar1 |  |  |  | CDC | 537 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | MCC_IED | IED |  | SupLocal | [17 empty] | 1-38-02 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.MCC_IED_S/L | 161KV IED SUPY/LOCAL | OTHER | D11/0/StaDev/7A5Other |  |  |  | CDC | 538 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D11 | 榴中DS | 22 | 22kV | PMCC_IED | 11/ IED |  | SupLocal | [17 empty] | 1-38-03 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.PMCC_IED_S/L | 11/23KV IED SUPY/LOCAL | OTHER | D11/0/StaDev/PMCC_R_L |  |  |  | CDC | 539 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D11 | 榴中DS | 0 |  |  |  |  | 81RF(1) | [17 empty] | 1-38-00 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.81RF(1) | 310低頻電驛故障 | OTHER | D11/11/310/1A5Other |  |  |  | CDC | 540 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | 81RY | 81RY |  | A/S(1) | [17 empty] | 2-0E-05 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.81RY_A/S(1) | 310低頻電驛動作/復歸 | OTHER | D11/11/310/81A |  |  |  | CDC | 541 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
D11 | 榴中DS | 0 |  | 81RY | 81RY |  | A/S(2) | [17 empty] | 2-0E-06 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.81RY_A/S(2) | 320低頻電驛動作/復歸 | OTHER | D11/22/320/81A |  |  |  | CDC | 542 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
D11 | 榴中DS | 0 |  | 81RY | 81RY |  | A/S(3) | [17 empty] | 2-0E-07 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.81RY_A/S(3) | 330低頻電驛動作/復歸 | OTHER | D11/11/330/81A |  |  |  | CDC | 543 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
D11 | 榴中DS | 0 |  | 81RY | 81RY |  | A/S(4) | [17 empty] | 2-0F-00 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.81RY_A/S(4) | 340低頻電驛動作/復歸 | OTHER | D11/22/340/81A |  |  |  | CDC | 544 | GENERICDIPoint | DS047_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
D11 | 榴中DS | 0 |  |  |  |  | GEN | [17 empty] | 1-38-13 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.GEN | 緊急發電機運轉 | OTHER | D11/0/StaDev/6A5Other |  |  |  | CDC | 545 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D11 | 榴中DS | 161 | 161kV | _BUS | BUS |  | 87CTFA | [17 empty] | 1-35-00 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.161KV_BUS_CTFA | 161KV BUS 87RY CT回路故障 | OTHER | D11/161/ComPoint/12B_CTFA |  |  |  | CDC | 546 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 161 | 161kV | _BUS | BUS |  | RYFA | [17 empty] | 1-34-15 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | D11/161/ComPoint/BUS_RYFA |  |  |  | CDC | 547 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D11 | 榴中DS | 0 |  | OLTC | OLTC |  | OLTCA | [17 empty] | 1-31-07 | [7 empty] | ADCS_N | [8 empty] | 榴中DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | D11/0/ComPoint/OLTC_A |  |  |  | CDC | 548 | GENERICDIPoint | DS047_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D11 | 榴中DS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 榴中DS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 549 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 11 | 11kV | 230_SC | #3SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 榴中DS.230_SC_CAP | 11KV#3SC 容量 | SC | [5 empty] | 550 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 22 | 22kV | 220_SC | #2SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 榴中DS.220_SC_CAP | 23KV#2SC 容量 | SC | [5 empty] | 551 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 22 | 22kV | 240_SC | #4SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 榴中DS.240_SC_CAP | 23KV#4SC 容量 | SC | [5 empty] | 552 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D11 | 榴中DS | 0 |  | TRD | 榴中DS |  | 177 | [25 empty] | TRAIN_AD | [8 empty] | 榴中DS.TRD_177 | 榴中DS NT #1ADTR 11KV_Hi_Limit | [6 empty] | 553 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D11 | 榴中DS | 0 |  | TRD | 榴中DS |  | 178 | [25 empty] | TRAIN_AD | [8 empty] | 榴中DS.TRD_178 | 榴中DS NT #1ADTR 11KV_Lo_Limit | [6 empty] | 554 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D11 | 榴中DS | 0 |  | TRD | 榴中DS |  | 179 | [25 empty] | TRAIN_AD | [8 empty] | 榴中DS.TRD_179 | 榴中DS NT #1BDTR 23KV_Hi_Limit | [6 empty] | 555 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D11 | 榴中DS | 0 |  | TRD | 榴中DS |  | 180 | [25 empty] | TRAIN_AD | [8 empty] | 榴中DS.TRD_180 | 榴中DS NT #1BDTR 23KV_Lo_Limit | [6 empty] | 556 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D11 | 榴中DS | 0 |  | TRD | 榴中DS |  | 181 | [25 empty] | TRAIN_AD | [8 empty] | 榴中DS.TRD_181 | 榴中DS NT #2ADTR 11KV_Hi_Limit | [6 empty] | 557 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D11 | 榴中DS | 0 |  | TRD | 榴中DS |  | 182 | [25 empty] | TRAIN_AD | [8 empty] | 榴中DS.TRD_182 | 榴中DS NT #2ADTR 11KV_Lo_Limit | [6 empty] | 558 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D11 | 榴中DS | 0 |  | TRD | 榴中DS |  | 183 | [25 empty] | TRAIN_AD | [8 empty] | 榴中DS.TRD_183 | 榴中DS NT #2BDTR 23KV_Hi_Limit | [6 empty] | 559 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D11 | 榴中DS | 0 |  | TRD | 榴中DS |  | 184 | [25 empty] | TRAIN_AD | [8 empty] | 榴中DS.TRD_184 | 榴中DS NT #2BDTR 23KV_Lo_Limit | [6 empty] | 560 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D11 | 榴中DS | 161 | 161kV | 1510 | 榴中斗工一路(1510) |  | LE0 | 1510LE | [24 empty] | ADCS_N | [8 empty] | 榴中DS.1510LE | 1510LE (非取樣點) | LINE161 | D11/161/1510/LE0 |  |  |  |  | 561 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 161 | 161kV | 1510 | 榴中斗工一路(1510) |  | BE0 | 1510BE | [24 empty] | ADCS_N | [8 empty] | 榴中DS.1510BE | 1510BE (非取樣點) | LINE161 | D11/161/1510/BE0 |  |  |  |  | 562 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 161 | 161kV | 1520 | 榴中斗工二路(1520) |  | LE0 | 1520LE | [24 empty] | ADCS_N | [8 empty] | 榴中DS.1520LE | 1520LE (非取樣點) | LINE161 | D11/161/1520/LE0 |  |  |  |  | 563 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 161 | 161kV | 1520 | 榴中斗工二路(1520) |  | BE0 | 1520BE | [24 empty] | ADCS_N | [8 empty] | 榴中DS.1520BE | 1520BE (非取樣點) | LINE161 | D11/161/1520/BE0 |  |  |  |  | 564 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | XB21 | XB21_DS |  | DS1 | XB21_DS | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB21_DS | XB21_DS (非取樣點) | FEEDER | D11/11/XB21/DS |  |  |  |  | 565 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | XB21 | XB21_ES |  | LE0 | XB21_ES | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB21_ES | XB21_ES (非取樣點) | FEEDER | D11/11/XB21/ES |  |  |  |  | 566 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | XB22 | XB22_DS |  | DS1 | XB22_DS | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB22_DS | XB22_DS (非取樣點) | FEEDER | D11/11/XB22/DS |  |  |  |  | 567 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | XB22 | XB22_ES |  | LE0 | XB22_ES | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB22_ES | XB22_ES (非取樣點) | FEEDER | D11/11/XB22/ES |  |  |  |  | 568 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | XB23 | XB23_DS |  | DS1 | XB23_DS | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB23_DS | XB23_DS (非取樣點) | FEEDER | D11/11/XB23/DS |  |  |  |  | 569 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | XB23 | XB23_ES |  | LE0 | XB23_ES | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB23_ES | XB23_ES (非取樣點) | FEEDER | D11/11/XB23/ES |  |  |  |  | 570 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | XB24 | XB24_DS |  | DS1 | XB24_DS | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB24_DS | XB24_DS (非取樣點) | FEEDER | D11/11/XB24/DS |  |  |  |  | 571 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | XB24 | XB24_ES |  | LE0 | XB24_ES | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB24_ES | XB24_ES (非取樣點) | FEEDER | D11/11/XB24/ES |  |  |  |  | 572 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | XB25 | XB25_DS |  | DS1 | XB25_DS | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB25_DS | XB25_DS (非取樣點) | FEEDER | D11/11/XB25/DS |  |  |  |  | 573 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | XB25 | XB25_ES |  | LE0 | XB25_ES | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB25_ES | XB25_ES (非取樣點) | FEEDER | D11/11/XB25/ES |  |  |  |  | 574 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | XB26 | XB26_DS |  | DS1 | XB26_DS | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB26_DS | XB26_DS (非取樣點) | FEEDER | D11/11/XB26/DS |  |  |  |  | 575 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | XB26 | XB26_ES |  | LE0 | XB26_ES | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB26_ES | XB26_ES (非取樣點) | FEEDER | D11/11/XB26/ES |  |  |  |  | 576 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | XB27 | XB27_DS |  | DS1 | XB27_DS | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB27_DS | XB27_DS (非取樣點) | FEEDER | D11/11/XB27/DS |  |  |  |  | 577 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | XB27 | XB27_ES |  | LE0 | XB27_ES | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB27_ES | XB27_ES (非取樣點) | FEEDER | D11/11/XB27/ES |  |  |  |  | 578 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | XB28 | XB28_DS |  | DS1 | XB28_DS | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB28_DS | XB28_DS (非取樣點) | FEEDER | D11/11/XB28/DS |  |  |  |  | 579 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | XB28 | XB28_ES |  | LE0 | XB28_ES | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB28_ES | XB28_ES (非取樣點) | FEEDER | D11/11/XB28/ES |  |  |  |  | 580 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | XB29 | XB29_DS |  | DS1 | XB29_DS | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB29_DS | XB29_DS (非取樣點) | FEEDER | D11/11/XB29/DS |  |  |  |  | 581 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | XB29 | XB29_ES |  | LE0 | XB29_ES | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB29_ES | XB29_ES (非取樣點) | FEEDER | D11/11/XB29/ES |  |  |  |  | 582 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | XB30 | XB30_DS |  | DS1 | XB30_DS | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB30_DS | XB30_DS (非取樣點) | FEEDER | D11/11/XB30/DS |  |  |  |  | 583 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | XB30 | XB30_ES |  | LE0 | XB30_ES | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB30_ES | XB30_ES (非取樣點) | FEEDER | D11/11/XB30/ES |  |  |  |  | 584 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | XB51 | XB51_DS |  | DS1 | XB51_DS | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB51_DS | XB51_DS (非取樣點) | FEEDER | D11/22/XB51/DS |  |  |  |  | 585 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | XB51 | XB51_ES |  | LE0 | XB51_ES | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB51_ES | XB51_ES (非取樣點) | FEEDER | D11/22/XB51/ES |  |  |  |  | 586 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | XB52 | XB52_DS |  | DS1 | XB52_DS | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB52_DS | XB52_DS (非取樣點) | FEEDER | D11/22/XB52/DS |  |  |  |  | 587 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | XB52 | XB52_ES |  | LE0 | XB52_ES | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB52_ES | XB52_ES (非取樣點) | FEEDER | D11/22/XB52/ES |  |  |  |  | 588 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | XB53 | XB53_DS |  | DS1 | XB53_DS | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB53_DS | XB53_DS (非取樣點) | FEEDER | D11/22/XB53/DS |  |  |  |  | 589 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | XB53 | XB53_ES |  | LE0 | XB53_ES | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB53_ES | XB53_ES (非取樣點) | FEEDER | D11/22/XB53/ES |  |  |  |  | 590 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | XB54 | XB54_DS |  | DS1 | XB54_DS | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB54_DS | XB54_DS (非取樣點) | FEEDER | D11/22/XB54/DS |  |  |  |  | 591 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | XB54 | XB54_ES |  | LE0 | XB54_ES | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB54_ES | XB54_ES (非取樣點) | FEEDER | D11/22/XB54/ES |  |  |  |  | 592 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | XB55 | XB55_DS |  | DS1 | XB55_DS | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB55_DS | XB55_DS (非取樣點) | FEEDER | D11/22/XB55/DS |  |  |  |  | 593 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | XB55 | XB55_ES |  | LE0 | XB55_ES | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB55_ES | XB55_ES (非取樣點) | FEEDER | D11/22/XB55/ES |  |  |  |  | 594 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | XB56 | XB56_DS |  | DS1 | XB56_DS | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB56_DS | XB56_DS (非取樣點) | FEEDER | D11/22/XB56/DS |  |  |  |  | 595 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | XB56 | XB56_ES |  | LE0 | XB56_ES | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB56_ES | XB56_ES (非取樣點) | FEEDER | D11/22/XB56/ES |  |  |  |  | 596 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | XB57 | XB57_DS |  | DS1 | XB57_DS | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB57_DS | XB57_DS (非取樣點) | FEEDER | D11/22/XB57/DS |  |  |  |  | 597 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | XB57 | XB57_ES |  | LE0 | XB57_ES | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB57_ES | XB57_ES (非取樣點) | FEEDER | D11/22/XB57/ES |  |  |  |  | 598 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | XB58 | XB58_DS |  | DS1 | XB58_DS | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB58_DS | XB58_DS (非取樣點) | FEEDER | D11/22/XB58/DS |  |  |  |  | 599 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | XB58 | XB58_ES |  | LE0 | XB58_ES | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB58_ES | XB58_ES (非取樣點) | FEEDER | D11/22/XB58/ES |  |  |  |  | 600 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | XB59 | XB59_DS |  | DS1 | XB59_DS | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB59_DS | XB59_DS (非取樣點) | FEEDER | D11/22/XB59/DS |  |  |  |  | 601 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | XB59 | XB59_ES |  | LE0 | XB59_ES | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB59_ES | XB59_ES (非取樣點) | FEEDER | D11/22/XB59/ES |  |  |  |  | 602 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | XB60 | XB60_DS |  | DS1 | XB60_DS | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB60_DS | XB60_DS (非取樣點) | FEEDER | D11/22/XB60/DS |  |  |  |  | 603 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | XB60 | XB60_ES |  | LE0 | XB60_ES | [24 empty] | DDCS1_1 | [8 empty] | 榴中DS.XB60_ES | XB60_ES (非取樣點) | FEEDER | D11/22/XB60/ES |  |  |  |  | 604 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | 101 | 101 |  | 101 | 101 | [24 empty] | ADCS_N | [8 empty] | 榴中DS.101 | 101 (非取樣點) | TIE | D11/11/100/D1 |  |  |  |  | 605 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | 102 | 102 |  | 102 | 102 | [24 empty] | ADCS_N | [8 empty] | 榴中DS.102 | 102 (非取樣點) | TIE | D11/11/100/D2 |  |  |  |  | 606 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [24 empty] | ADCS_N | [8 empty] | 榴中DS.1501E | 1501E (非取樣點) | TIE | D11/161/1500/E1 |  |  |  |  | 607 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [24 empty] | ADCS_N | [8 empty] | 榴中DS.1502E | 1502E (非取樣點) | TIE | D11/161/1500/E2 |  |  |  |  | 608 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | 201 | 201 |  | 201 | 201 | [24 empty] | ADCS_N | [8 empty] | 榴中DS.201 | 201 (非取樣點) | TIE | D11/22/200/D1 |  |  |  |  | 609 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | 202 | 202 |  | 202 | 202 | [24 empty] | ADCS_N | [8 empty] | 榴中DS.202 | 202 (非取樣點) | TIE | D11/22/200/D2 |  |  |  |  | 610 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | 391 | 391 |  | 391 | 391 | [24 empty] | ADCS_N | [8 empty] | 榴中DS.391 | 391 (非取樣點) | OTHER | D11/11/390/D1 |  |  |  |  | 611 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | 391E | 391E |  | 391E | 391E | [24 empty] | ADCS_N | [8 empty] | 榴中DS.391E | 391E (非取樣點) | OTHER | D11/11/390/E1 |  |  |  |  | 612 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | 491 | 491 |  | 491 | 491 | [24 empty] | ADCS_N | [8 empty] | 榴中DS.491 | 491 (非取樣點) | OTHER | D11/22/490/D1 |  |  |  |  | 613 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | 491E | 491E |  | 491E | 491E | [24 empty] | ADCS_N | [8 empty] | 榴中DS.491E | 491E (非取樣點) | OTHER | D11/22/490/E1 |  |  |  |  | 614 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | 1750TE | [24 empty] | ADCS_N | [8 empty] | 榴中DS.1750TE | 1750TE (非取樣點) | MTR | D11/161/1750/TE0 |  |  |  |  | 615 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | 1750BE | [24 empty] | ADCS_N | [8 empty] | 榴中DS.1750BE | 1750BE (非取樣點) | MTR | D11/161/1750/BE0 |  |  |  |  | 616 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | 311 | 311 |  | 311 | 311 | [24 empty] | ADCS_N | [8 empty] | 榴中DS.311 | 311 (非取樣點) | MTR | D11/11/310/D1 |  |  |  |  | 617 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | 310 | #1DTR(310) |  | E1 | 311E | [24 empty] | ADCS_N | [8 empty] | 榴中DS.311E | 311E (非取樣點) | MTR | D11/11/310/E1 |  |  |  |  | 618 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | 321 | 321 |  | 321 | 321 | [24 empty] | ADCS_N | [8 empty] | 榴中DS.321 | 321 (非取樣點) | MTR | D11/22/320/D1 |  |  |  |  | 619 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | 320 | #1DTR(320) |  | E1 | 321E | [24 empty] | ADCS_N | [8 empty] | 榴中DS.321E | 321E (非取樣點) | MTR | D11/22/320/E1 |  |  |  |  | 620 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | 1760TE | [24 empty] | ADCS_N | [8 empty] | 榴中DS.1760TE | 1760TE (非取樣點) | MTR | D11/161/1760/TE0 |  |  |  |  | 621 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | 1760BE | [24 empty] | ADCS_N | [8 empty] | 榴中DS.1760BE | 1760BE (非取樣點) | MTR | D11/161/1760/BE0 |  |  |  |  | 622 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | 331 | 331 |  | 331 | 331 | [24 empty] | ADCS_N | [8 empty] | 榴中DS.331 | 331 (非取樣點) | MTR | D11/11/330/D1 |  |  |  |  | 623 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | 330 | #2DTR(330) |  | E1 | 331E | [24 empty] | ADCS_N | [8 empty] | 榴中DS.331E | 331E (非取樣點) | MTR | D11/11/330/E1 |  |  |  |  | 624 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | 341 | 341 |  | 341 | 341 | [24 empty] | ADCS_N | [8 empty] | 榴中DS.341 | 341 (非取樣點) | MTR | D11/22/340/D1 |  |  |  |  | 625 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | 340 | #2DTR(340) |  | E1 | 341E | [24 empty] | ADCS_N | [8 empty] | 榴中DS.341E | 341E (非取樣點) | MTR | D11/22/340/E1 |  |  |  |  | 626 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | 211E | 211E |  | 211E | 211E | [24 empty] | ADCS_N | [8 empty] | 榴中DS.211E | 211E (非取樣點) | SC | D11/11/210/E1 |  |  |  |  | 627 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | 211 | 211 |  | 211 | 211 | [24 empty] | ADCS_N | [8 empty] | 榴中DS.211 | 211 (非取樣點) | SC | D11/11/210/D1 |  |  |  |  | 628 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | 231E | 231E |  | 231E | 231E | [24 empty] | ADCS_N | [8 empty] | 榴中DS.231E | 231E (非取樣點) | SC | D11/11/230/E1 |  |  |  |  | 629 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | 231 | 231 |  | 231 | 231 | [24 empty] | ADCS_N | [8 empty] | 榴中DS.231 | 231 (非取樣點) | SC | D11/11/230/D1 |  |  |  |  | 630 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | 221E | 221E |  | 221E | 221E | [24 empty] | ADCS_N | [8 empty] | 榴中DS.221E | 221E (非取樣點) | SC | D11/22/220/E1 |  |  |  |  | 631 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | 221 | 221 |  | 221 | 221 | [24 empty] | ADCS_N | [8 empty] | 榴中DS.221 | 221 (非取樣點) | SC | D11/22/220/D1 |  |  |  |  | 632 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | 241E | 241E |  | 241E | 241E | [24 empty] | ADCS_N | [8 empty] | 榴中DS.241E | 241E (非取樣點) | SC | D11/22/240/E1 |  |  |  |  | 633 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | 241 | 241 |  | 241 | 241 | [24 empty] | ADCS_N | [8 empty] | 榴中DS.241 | 241 (非取樣點) | SC | D11/22/240/D1 |  |  |  |  | 634 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | ADCS_N | [8 empty] | 榴中DS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 635 | NotelDIPoint | [38 empty] | START/STOP | STOP
D11 | 榴中DS | 0 |  |  |  |  | 101E | 101E | [24 empty] | ADCS_N | [8 empty] | 榴中DS.101E | 101E(非取樣點) | OTHER | D11/11/100/E1 |  |  |  |  | 636 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  |  |  |  | 102E | 102E | [24 empty] | ADCS_N | [8 empty] | 榴中DS.102E | 102E(非取樣點) | OTHER | D11/11/100/E2 |  |  |  |  | 637 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  |  |  |  | 201E | 201E | [24 empty] | ADCS_N | [8 empty] | 榴中DS.201E | 201E(非取樣點) | OTHER | D11/22/200/E1 |  |  |  |  | 638 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  |  |  |  | 202E | 202E | [24 empty] | ADCS_N | [8 empty] | 榴中DS.202E | 202E(非取樣點) | OTHER | D11/22/200/E2 |  |  |  |  | 639 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | 1A | #1A |  | BE | #1A_BE | [24 empty] | ADCS_N | [8 empty] | 榴中DS.#1A_BE | #1A BE(非取樣點) | OTHER | [5 empty] | 640 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | 1B | #1B |  | BE | #1B_BE | [24 empty] | ADCS_N | [8 empty] | 榴中DS.#1B_BE | #1B BE(非取樣點) | OTHER | [5 empty] | 641 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | 2A | #2A |  | BE | #2A_BE | [24 empty] | ADCS_N | [8 empty] | 榴中DS.#2A_BE | #2A BE(非取樣點) | OTHER | [5 empty] | 642 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | 2B | #2B |  | BE | #2B_BE | [24 empty] | ADCS_N | [8 empty] | 榴中DS.#2B_BE | #2B BE(非取樣點) | OTHER | [5 empty] | 643 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | 1ABUS | 1ABUS |  | PTD | 1ABUS_PTD | [24 empty] | ADCS_N | [8 empty] | 榴中DS.1ABUS_PTD | #1ABUS_PTD(非取樣點) | OTHER | [5 empty] | 644 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | 1ABUS | 1ABUS |  | PTE | 1ABUS_PTE | [24 empty] | ADCS_N | [8 empty] | 榴中DS.1ABUS_PTE | #1ABUS_PTE(非取樣點) | OTHER | [5 empty] | 645 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | 1BBUS | 1BBUS |  | PTD | 1BBUS_PTD | [24 empty] | ADCS_N | [8 empty] | 榴中DS.1BBUS_PTD | #1BBUS_PTD(非取樣點) | OTHER | [5 empty] | 646 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | 1BBUS | 1BBUS |  | PTE | 1BBUS_PTE | [24 empty] | ADCS_N | [8 empty] | 榴中DS.1BBUS_PTE | #1BBUS_PTE(非取樣點) | OTHER | [5 empty] | 647 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | 2ABUS | 2ABUS |  | PTD | 2ABUS_PTD | [24 empty] | ADCS_N | [8 empty] | 榴中DS.2ABUS_PTD | #2ABUS_PTD(非取樣點) | OTHER | [5 empty] | 648 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | 2ABUS | 2ABUS |  | PTE | 2ABUS_PTE | [24 empty] | ADCS_N | [8 empty] | 榴中DS.2ABUS_PTE | #2ABUS_PTE(非取樣點) | OTHER | [5 empty] | 649 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D11 | 榴中DS | 0 |  | 2BBUS | 2BBUS |  | PTD | 2BBUS_PTD | [24 empty] | ADCS_N | [8 empty] | 榴中DS.2BBUS_PTD | #2BBUS_PTD(非取樣點) | OTHER | [5 empty] | 650 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D11 | 榴中DS | 0 |  | 2BBUS | 2BBUS |  | PTE | 2BBUS_PTE | [24 empty] | ADCS_N | [8 empty] | 榴中DS.2BBUS_PTE | #2BBUS_PTE(非取樣點) | OTHER | [5 empty] | 651 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo