## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D12 | 仁愛DS | 161 | 161kV | 1520 | 嘉義～仁愛海線(1520) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_A1 | [8 empty] | 仁愛DS.1520LE | 1520LE (非取樣點) | LINE161 | [5 empty] | 2 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 1520 | 嘉義～仁愛海線(1520) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_A1 | [8 empty] | 仁愛DS.1520BE | 1520BE (非取樣點) | LINE161 | [5 empty] | 3 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 1510 | 嘉義～仁愛山線(1510) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_A1 | [8 empty] | 仁愛DS.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 4 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 1510 | 嘉義～仁愛山線(1510) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_A1 | [8 empty] | 仁愛DS.1510BE | 1510BE (非取樣點) | LINE161 | [5 empty] | 5 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 1540 | 仁愛～北回二路(1540) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_A1 | [8 empty] | 仁愛DS.1540LE | 1540LE (非取樣點) | LINE161 | [5 empty] | 6 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 1540 | 仁愛～北回二路(1540) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_A1 | [8 empty] | 仁愛DS.1540BE | 1540BE (非取樣點) | LINE161 | [5 empty] | 7 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 1530 | 仁愛～北回一路(1530) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_A1 | [8 empty] | 仁愛DS.1530LE | 1530LE (非取樣點) | LINE161 | [5 empty] | 8 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 1530 | 仁愛～北回一路(1530) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_A1 | [8 empty] | 仁愛DS.1530BE | 1530BE (非取樣點) | LINE161 | [5 empty] | 9 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_A1 | [8 empty] | 仁愛DS.1501E | 1501E (非取樣點) | TIE | [5 empty] | 10 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_A1 | [8 empty] | 仁愛DS.1502E | 1502E (非取樣點) | TIE | [5 empty] | 11 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_A1 | [8 empty] | 仁愛DS.1750TE | 1750TE (非取樣點) | MTR | [5 empty] | 12 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_A1 | [8 empty] | 仁愛DS.1750BE | 1750BE (非取樣點) | MTR | [5 empty] | 13 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | D1 | 311(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.311 | 311 (非取樣點) | MTR | [5 empty] | 14 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | E1 | 311E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.311E | 311E (非取樣點) | MTR | [5 empty] | 15 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | D1 | 321(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.321 | 321 (非取樣點) | MTR | [5 empty] | 16 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | E1 | 321E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.321E | 321E (非取樣點) | MTR | [5 empty] | 17 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_A1 | [8 empty] | 仁愛DS.1760TE | 1760TE (非取樣點) | MTR | [5 empty] | 18 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_A1 | [8 empty] | 仁愛DS.1760BE | 1760BE (非取樣點) | MTR | [5 empty] | 19 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | D1 | 331(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.331 | 331 (非取樣點) | MTR | [5 empty] | 20 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | E1 | 331E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.331E | 331E (非取樣點) | MTR | [5 empty] | 21 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | D1 | 341(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.341 | 341 (非取樣點) | MTR | [5 empty] | 22 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | E1 | 341E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.341E | 341E (非取樣點) | MTR | [5 empty] | 23 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_A1 | [8 empty] | 仁愛DS.1770TE | 1770TE (非取樣點) | MTR | [5 empty] | 24 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_A1 | [8 empty] | 仁愛DS.1770BE | 1770BE (非取樣點) | MTR | [5 empty] | 25 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 22 | 22kV | 350 | #3DTR(350) |  | D1 | 351(非取樣點) | B2 | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.351 | 351 (非取樣點) | MTR | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | 350 | #3DTR(350) |  | E1 | 351E(非取樣點) | B2,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.351E | 351E (非取樣點) | MTR | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 1780 | #4DTR(1780) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_A1 | [8 empty] | 仁愛DS.1780TE | 1780TE (非取樣點) | MTR | [5 empty] | 28 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 1780 | #4DTR(1780) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_A1 | [8 empty] | 仁愛DS.1780BE | 1780BE (非取樣點) | MTR | [5 empty] | 29 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 22 | 22kV | 370 | #4DTR(370) |  | D1 | 371(非取樣點) | B2 | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.371 | 371 (非取樣點) | MTR | [5 empty] | 30 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | 370 | #4DTR(370) |  | E1 | 371E(非取樣點) | B2,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.371E | 371E (非取樣點) | MTR | [5 empty] | 31 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | JA21 | 愛21線(JA21) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA21_DS | JA21_DS (非取樣點) | FEEDER | [5 empty] | 32 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA21 | 愛21線(JA21) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA21_ES | JA21_ES (非取樣點) | FEEDER | [5 empty] | 33 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | JA22 | 愛22線(JA22) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA22_DS | JA22_DS (非取樣點) | FEEDER | [5 empty] | 34 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA22 | 愛22線(JA22) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA22_ES | JA22_ES (非取樣點) | FEEDER | [5 empty] | 35 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | JA23 | 愛23線(JA23) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA23_DS | JA23_DS (非取樣點) | FEEDER | [5 empty] | 36 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA23 | 愛23線(JA23) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA23_ES | JA23_ES (非取樣點) | FEEDER | [5 empty] | 37 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | JA24 | 愛24線(JA24) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA24_DS | JA24_DS (非取樣點) | FEEDER | [5 empty] | 38 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA24 | 愛24線(JA24) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA24_ES | JA24_ES (非取樣點) | FEEDER | [5 empty] | 39 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | JA25 | 愛25線(JA25) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA25_DS | JA25_DS (非取樣點) | FEEDER | [5 empty] | 40 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA25 | 愛25線(JA25) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA25_ES | JA25_ES (非取樣點) | FEEDER | [5 empty] | 41 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | 210 | #1SC(210) |  | E1 | 211E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.211E | 211E (非取樣點) | SC | [5 empty] | 42 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | 210 | #1SC(210) |  | D1 | 211(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.211 | 211 (非取樣點) | SC | [5 empty] | 43 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | 100 | TIE-1(100) |  | D1 | 101(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.101 | 101 (非取樣點) | TIE | [5 empty] | 44 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | 100 | TIE-1(100) |  | D2 | 102(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.102 | 102 (非取樣點) | TIE | [5 empty] | 45 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | 100 | TIE-1(100) |  | E1 | 101E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.101E | 101E(非取樣點) | OTHER | [5 empty] | 46 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | 100 | TIE-1(100) |  | E2 | 102E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.102E | 102E(非取樣點) | OTHER | [5 empty] | 47 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | JA26 | 愛26線(JA26) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA26_DS | JA26_DS (非取樣點) | FEEDER | [5 empty] | 48 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA26 | 愛26線(JA26) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA26_ES | JA26_ES (非取樣點) | FEEDER | [5 empty] | 49 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | JA27 | 愛27線(JA27) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA27_DS | JA27_DS (非取樣點) | FEEDER | [5 empty] | 50 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA27 | 愛27線(JA27) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA27_ES | JA27_ES (非取樣點) | FEEDER | [5 empty] | 51 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | JA28 | 愛28線(JA28) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA28_DS | JA28_DS (非取樣點) | FEEDER | [5 empty] | 52 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA28 | 愛28線(JA28) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA28_ES | JA28_ES (非取樣點) | FEEDER | [5 empty] | 53 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | JA29 | 愛29線(JA29) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA29_DS | JA29_DS (非取樣點) | FEEDER | [5 empty] | 54 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA29 | 愛29線(JA29) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA29_ES | JA29_ES (非取樣點) | FEEDER | [5 empty] | 55 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | JA30 | 愛30線(JA30) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA30_DS | JA30_DS (非取樣點) | FEEDER | [5 empty] | 56 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA30 | 愛30線(JA30) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA30_ES | JA30_ES (非取樣點) | FEEDER | [5 empty] | 57 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | 220 | #2SC(220) |  | E1 | 221E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.221E | 221E (非取樣點) | SC | [5 empty] | 58 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | 220 | #2SC(220) |  | D1 | 221(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.221 | 221 (非取樣點) | SC | [5 empty] | 59 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | 390 | #1SSTR(390) |  | D1 | 391(非取樣點) | B3 | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.391 | 391 (非取樣點) | OTHER | [5 empty] | 60 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | 390 | #1SSTR(390) |  | E1 | 391E(非取樣點) | B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.391E | 391E (非取樣點) | OTHER | [5 empty] | 61 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | JA31 | 愛31線(JA31) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA31_DS | JA31_DS (非取樣點) | FEEDER | [5 empty] | 62 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA31 | 愛31線(JA31) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA31_ES | JA31_ES (非取樣點) | FEEDER | [5 empty] | 63 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | JA32 | 愛32線(JA32) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA32_DS | JA32_DS (非取樣點) | FEEDER | [5 empty] | 64 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA32 | 愛32線(JA32) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA32_ES | JA32_ES (非取樣點) | FEEDER | [5 empty] | 65 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | JA33 | 愛33線(JA33) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA33_DS | JA33_DS (非取樣點) | FEEDER | [5 empty] | 66 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA33 | 愛33線(JA33) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA33_ES | JA33_ES (非取樣點) | FEEDER | [5 empty] | 67 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | JA34 | 愛34線(JA34) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA34_DS | JA34_DS (非取樣點) | FEEDER | [5 empty] | 68 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA34 | 愛34線(JA34) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA34_ES | JA34_ES (非取樣點) | FEEDER | [5 empty] | 69 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | JA35 | 愛35線(JA35) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA35_DS | JA35_DS (非取樣點) | FEEDER | [5 empty] | 70 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA35 | 愛35線(JA35) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA35_ES | JA35_ES (非取樣點) | FEEDER | [5 empty] | 71 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | 230 | #3SC(230) |  | E1 | 231E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.231E | 231E (非取樣點) | SC | [5 empty] | 72 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | 230 | #3SC(230) |  | D1 | 231(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.231 | 231 (非取樣點) | SC | [5 empty] | 73 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | 490 | #2SSTR(490) |  | D1 | 491(非取樣點) | B3 | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.491 | 491 (非取樣點) | OTHER | [5 empty] | 74 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | 490 | #2SSTR(490) |  | E1 | 491E(非取樣點) | B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.491E | 491E (非取樣點) | OTHER | [5 empty] | 75 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | JA36 | 愛36線(JA36) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA36_DS | JA36_DS (非取樣點) | FEEDER | [5 empty] | 76 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA36 | 愛36線(JA36) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA36_ES | JA36_ES (非取樣點) | FEEDER | [5 empty] | 77 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | JA37 | 愛37線(JA37) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA37_DS | JA37_DS (非取樣點) | FEEDER | [5 empty] | 78 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA37 | 愛37線(JA37) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA37_ES | JA37_ES (非取樣點) | FEEDER | [5 empty] | 79 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | JA38 | 愛38線(JA38) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA38_DS | JA38_DS (非取樣點) | FEEDER | [5 empty] | 80 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA38 | 愛38線(JA38) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA38_ES | JA38_ES (非取樣點) | FEEDER | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | JA39 | 愛39線(JA39) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA39_DS | JA39_DS (非取樣點) | FEEDER | [5 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA39 | 愛39線(JA39) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA39_ES | JA39_ES (非取樣點) | FEEDER | [5 empty] | 83 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | JA40 | 愛40線(JA40) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA40_DS | JA40_DS (非取樣點) | FEEDER | [5 empty] | 84 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA40 | 愛40線(JA40) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA40_ES | JA40_ES (非取樣點) | FEEDER | [5 empty] | 85 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | 240 | #4SC(240) |  | E1 | 241E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.241E | 241E (非取樣點) | SC | [5 empty] | 86 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | 240 | #4SC(240) |  | D1 | 241(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.241 | 241 (非取樣點) | SC | [5 empty] | 87 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | 200 | TIE-2(200) |  | D1 | 201(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.201 | 201 (非取樣點) | TIE | [5 empty] | 88 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | 200 | TIE-2(200) |  | D2 | 202(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.202 | 202 (非取樣點) | TIE | [5 empty] | 89 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | 200 | TIE-2(200) |  | E1 | 201E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.201E | 201E(非取樣點) | OTHER | [5 empty] | 90 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | 200 | TIE-2(200) |  | E2 | 202E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.202E | 202E(非取樣點) | OTHER | [5 empty] | 91 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 22 | 22kV | JA71 | 愛71線(JA71) |  | DS | (非取樣點) | B2,Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA71_DS | JA71_DS (非取樣點) | FEEDER | [5 empty] | 92 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA71 | 愛71線(JA71) |  | ES | (非取樣點) | B2,Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA71_ES | JA71_ES (非取樣點) | FEEDER | [5 empty] | 93 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 22 | 22kV | JA72 | 愛72線(JA72) |  | DS | (非取樣點) | B2,Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA72_DS | JA72_DS (非取樣點) | FEEDER | [5 empty] | 94 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA72 | 愛72線(JA72) |  | ES | (非取樣點) | B2,Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA72_ES | JA72_ES (非取樣點) | FEEDER | [5 empty] | 95 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 22 | 22kV | JA73 | 愛73線(JA73) |  | DS | (非取樣點) | B2,Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA73_DS | JA73_DS (非取樣點) | FEEDER | [5 empty] | 96 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA73 | 愛73線(JA73) |  | ES | (非取樣點) | B2,Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA73_ES | JA73_ES (非取樣點) | FEEDER | [5 empty] | 97 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 22 | 22kV | JA74 | 愛74線(JA74) |  | DS | (非取樣點) | B2,Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA74_DS | JA74_DS (非取樣點) | FEEDER | [5 empty] | 98 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA74 | 愛74線(JA74) |  | ES | (非取樣點) | B2,Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA74_ES | JA74_ES (非取樣點) | FEEDER | [5 empty] | 99 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 22 | 22kV | 250 | #5SC(250) |  | E1 | 251E(非取樣點) | B2,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.251E | 251E (非取樣點) | SC | [5 empty] | 100 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 22 | 22kV | 250 | #5SC(250) |  | D1 | 251(非取樣點) | B2 | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.251 | 251 (非取樣點) | SC | [5 empty] | 101 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA75 | 愛75線(JA75) |  | DS | (非取樣點) | B2,Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA75_DS | JA75_DS (非取樣點) | FEEDER | [5 empty] | 102 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA75 | 愛75線(JA75) |  | ES | (非取樣點) | B2,Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA75_ES | JA75_ES (非取樣點) | FEEDER | [5 empty] | 103 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 22 | 22kV | JA76 | 愛76線(JA76) |  | DS | (非取樣點) | B2,Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA76_DS | JA76_DS (非取樣點) | FEEDER | [5 empty] | 104 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA76 | 愛76線(JA76) |  | ES | (非取樣點) | B2,Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA76_ES | JA76_ES (非取樣點) | FEEDER | [5 empty] | 105 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 22 | 22kV | JA77 | 愛77線(JA77) |  | DS | (非取樣點) | B2,Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA77_DS | JA77_DS (非取樣點) | FEEDER | [5 empty] | 106 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA77 | 愛77線(JA77) |  | ES | (非取樣點) | B2,Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA77_ES | JA77_ES (非取樣點) | FEEDER | [5 empty] | 107 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 22 | 22kV | JA78 | 愛78線(JA78) |  | DS | (非取樣點) | B2,Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA78_DS | JA78_DS (非取樣點) | FEEDER | [5 empty] | 108 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA78 | 愛78線(JA78) |  | ES | (非取樣點) | B2,Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA78_ES | JA78_ES (非取樣點) | FEEDER | [5 empty] | 109 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 22 | 22kV | 260 | #6SC(260) |  | E1 | 261E(非取樣點) | B2,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.261E | 261E (非取樣點) | SC | [5 empty] | 110 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 22 | 22kV | 260 | #6SC(260) |  | D1 | 261(非取樣點) | B2 | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.261 | 261 (非取樣點) | SC | [5 empty] | 111 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA5A | 愛5A線(JA5A) |  | DS | (非取樣點) | B2,Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA5A_DS | JA5A_DS (非取樣點) | FEEDER | [5 empty] | 112 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA5A | 愛5A線(JA5A) |  | ES | (非取樣點) | B2,Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA5A_ES | JA5A_ES (非取樣點) | FEEDER | [5 empty] | 113 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 22 | 22kV | JA5B | 愛5B線(JA5B) |  | DS | (非取樣點) | B2,Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA5B_DS | JA5B_DS (非取樣點) | FEEDER | [5 empty] | 114 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA5B | 愛5B線(JA5B) |  | ES | (非取樣點) | B2,Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA5B_ES | JA5B_ES (非取樣點) | FEEDER | [5 empty] | 115 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 22 | 22kV | JA5C | 愛5C線(JA5C) |  | DS | (非取樣點) | B2,Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA5C_DS | JA5C_DS (非取樣點) | FEEDER | [5 empty] | 116 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA5C | 愛5C線(JA5C) |  | ES | (非取樣點) | B2,Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA5C_ES | JA5C_ES (非取樣點) | FEEDER | [5 empty] | 117 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 22 | 22kV | JA5D | 愛5D線(JA5D) |  | DS | (非取樣點) | B2,Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA5D_DS | JA5D_DS (非取樣點) | FEEDER | [5 empty] | 118 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA5D | 愛5D線(JA5D) |  | ES | (非取樣點) | B2,Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA5D_ES | JA5D_ES (非取樣點) | FEEDER | [5 empty] | 119 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 22 | 22kV | 270 | #7SC(270) |  | E1 | 271E(非取樣點) | B2,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.271E | 271E (非取樣點) | SC | [5 empty] | 120 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 22 | 22kV | 270 | #7SC(270) |  | D1 | 271(非取樣點) | B2 | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.271 | 271 (非取樣點) | SC | [5 empty] | 121 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA5F | 愛5F線(JA5F) |  | DS | (非取樣點) | B2,Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA5F_DS | JA5F_DS (非取樣點) | FEEDER | [5 empty] | 122 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA5F | 愛5F線(JA5F) |  | ES | (非取樣點) | B2,Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA5F_ES | JA5F_ES (非取樣點) | FEEDER | [5 empty] | 123 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 22 | 22kV | JA5G | 愛5G線(JA5G) |  | DS | (非取樣點) | B2,Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA5G_DS | JA5G_DS (非取樣點) | FEEDER | [5 empty] | 124 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA5G | 愛5G線(JA5G) |  | ES | (非取樣點) | B2,Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA5G_ES | JA5G_ES (非取樣點) | FEEDER | [5 empty] | 125 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 22 | 22kV | JA5H | 愛5H線(JA5H) |  | DS | (非取樣點) | B2,Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA5H_DS | JA5H_DS (非取樣點) | FEEDER | [5 empty] | 126 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA5H | 愛5H線(JA5H) |  | ES | (非取樣點) | B2,Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA5H_ES | JA5H_ES (非取樣點) | FEEDER | [5 empty] | 127 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 22 | 22kV | JA5K | 愛5K線(JA5K) |  | DS | (非取樣點) | B2,Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA5K_DS | JA5K_DS (非取樣點) | FEEDER | [5 empty] | 128 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA5K | 愛5K線(JA5K) |  | ES | (非取樣點) | B2,Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D12_D1 | [8 empty] | 仁愛DS.JA5K_ES | JA5K_ES (非取樣點) | FEEDER | [5 empty] | 129 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 22 | 22kV | 280 | #8SC(280) |  | E1 | 281E(非取樣點) | B2,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.281E | 281E (非取樣點) | SC | [5 empty] | 130 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 22 | 22kV | 280 | #8SC(280) |  | D1 | 281(非取樣點) | B2 | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.281 | 281 (非取樣點) | SC | [5 empty] | 131 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | 400 | TIE-4(400) |  | D1 | 401(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.401 | 401 (非取樣點) | TIE | [5 empty] | 132 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | 400 | TIE-4(400) |  | D2 | 402(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.402 | 402 (非取樣點) | TIE | [5 empty] | 133 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | 400 | TIE-4(400) |  | E1 | 401E(非取樣點) | B2,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.401E | 401E(非取樣點) | OTHER | [5 empty] | 134 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 22 | 22kV | 400 | TIE-4(400) |  | E2 | 402E(非取樣點) | B2,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D12_A1 | [8 empty] | 仁愛DS.402E | 402E(非取樣點) | OTHER | [5 empty] | 135 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | 15B1E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aaaz | B2/D12_A1 | [8 empty] | 仁愛DS.15B1E | 15B1E (非取樣點) | BUS | [5 empty] | 136 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | 15B2E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/2Bus | [13 empty] | aaaz | B2/D12_A1 | [8 empty] | 仁愛DS.15B2E | 15B2E (非取樣點) | BUS | [5 empty] | 137 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | RTU | RTU |  | ADCL1 |  |  | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.1 AI Card) |  |  |  |  | B3/D12_A1 | [16 empty] | 138 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D12 | 仁愛DS | 0 |  | RTU | RTU |  | ADCH1 |  |  | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.1 AI Card) |  |  |  |  | B3/D12_A1 | [16 empty] | 139 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D12 | 仁愛DS | 161 | 161kV | 1BUS | #1BUS |  | V |  | B3 | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 161KV #1BUS | KV | 161KV #1BUS 電壓 | kV_-210_210(-2000_2000) | aaa | B2/D12_A1 | [8 empty] | 仁愛DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | [5 empty] | 140 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D12 | 仁愛DS | 161 | 161kV | 2BUS | #2BUS |  | V |  | B3 | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0003 |  |  | 1-83 |  |  | 161KV #2BUS | KV | 161KV #2BUS 電壓 | kV_-210_210(-2000_2000) | aab | B2/D12_A1 | [8 empty] | 仁愛DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | [5 empty] | 141 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D12 | 仁愛DS | 161 | 161kV | 1520 | 嘉義～仁愛海線(1520) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | L1 | MW | 嘉義仁愛海線 1520 CB 瓦 | MW_-560_560(-2000_2000) |  | B2/D12_A1 | [8 empty] | 仁愛DS.1520_MW | 嘉義仁愛海線 MW | LINE161 | [5 empty] | 142 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D12 | 仁愛DS | 161 | 161kV | 1520 | 嘉義～仁愛海線(1520) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | L1 | KVAR | 嘉義仁愛海線 1520 CB 乏 | MVAR_-560_560(-2000_2000) |  | B2/D12_A1 | [8 empty] | 仁愛DS.1520_MVAR | 嘉義仁愛海線 MVAR | LINE161 | [5 empty] | 143 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D12 | 仁愛DS | 161 | 161kV | 1510 | 嘉義～仁愛山線(1510) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | L2 | MW | 嘉義仁愛山線 1510 CB 瓦 | MW_-560_560(-2000_2000) |  | B2/D12_A1 | [8 empty] | 仁愛DS.1510_MW | 嘉義仁愛山線 MW | LINE161 | [5 empty] | 144 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D12 | 仁愛DS | 161 | 161kV | 1510 | 嘉義～仁愛山線(1510) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | L2 | KVAR | 嘉義仁愛山線 1510 CB 乏 | MVAR_-560_560(-2000_2000) |  | B2/D12_A1 | [8 empty] | 仁愛DS.1510_MVAR | 嘉義仁愛山線 MVAR | LINE161 | [5 empty] | 145 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D12 | 仁愛DS | 161 | 161kV | 1540 | 仁愛～北回二路(1540) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | Line3 | MW | 仁愛北回二路 (1540) CB 瓦 | MW_-560_560(-2000_2000) |  | B2/D12_A1 | [8 empty] | 仁愛DS.1540_MW | 仁愛北回二路 MW | LINE161 | [5 empty] | 146 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D12 | 仁愛DS | 161 | 161kV | 1540 | 仁愛～北回二路(1540) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | Line3 | KVAR | 仁愛北回二路 (1540) CB 乏 | MVAR_-560_560(-2000_2000) |  | B2/D12_A1 | [8 empty] | 仁愛DS.1540_MVAR | 仁愛北回二路 MVAR | LINE161 | [5 empty] | 147 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D12 | 仁愛DS | 161 | 161kV | 1530 | 仁愛～北回一路(1530) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | Line4 | MW | 仁愛北回一路 (1530) CB 瓦 | MW_-560_560(-2000_2000) |  | B2/D12_A1 | [8 empty] | 仁愛DS.1530_MW | 仁愛北回一路 MW | LINE161 | [5 empty] | 148 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D12 | 仁愛DS | 161 | 161kV | 1530 | 仁愛～北回一路(1530) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | Line4 | KVAR | 仁愛北回一路 (1530) CB 乏 | MVAR_-560_560(-2000_2000) |  | B2/D12_A1 | [8 empty] | 仁愛DS.1530_MVAR | 仁愛北回一路 MVAR | LINE161 | [5 empty] | 149 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D12 | 仁愛DS | 161 | 161kV | 1500 | TIE(1500) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0024 |  |  | 1-98 |  |  | 161KV TIE | A | (1500) R相電流 | A_-2000_2000(-2000_2000) |  | B2/D12_A1 | [8 empty] | 仁愛DS.1500TIE_AMP | 1500TIE AMP | TIE | [5 empty] | 150 |  |  |  |  | AI | [5 empty] | C20R1600 | 1520 | 1600 | 1760 | 1968 | 2.27 | -1520 | -1600 | -1760 | -1968 | 1 | 0.01 | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS |  |  | 1DTR | #1DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | NO.1 DTR. | ℃ | NO.1 DTR. 油溫 | OIL_-120_120(-2000_2000) |  | B1/D12_A1 | [8 empty] | 仁愛DS.#1DTR_OIL | #1DTR 油溫 | MTR | [5 empty] | 151 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D12 | 仁愛DS |  |  | 1DTR(A) | #1DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | NO.1 DTR.A | ℃ | NO.1 DTR.A 線溫 | COIL_-120_120(-2000_2000) |  | B1/D12_A1 | [8 empty] | 仁愛DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | [5 empty] | 152 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D12 | 仁愛DS |  |  | 1DTR(B) | #1DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0027 |  |  | 1-9B |  |  | NO.1 DTR.B | ℃ | NO.1 DTR.B 線溫 | COIL_-120_120(-2000_2000) |  | B1/D12_A1 | [8 empty] | 仁愛DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | [5 empty] | 153 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D12 | 仁愛DS |  |  | 1DTR(A) | #1DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0028 |  | 0059 | 1-9C |  | 1-3B | NO.1 DTR.A | 升/降 | NO.1 DTR.A TAP | TAP_-8.5_8.5(0_2000) |  | B1/D12_A1 | [8 empty] | 仁愛DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | [5 empty] | 154 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D12 | 仁愛DS |  |  | 1DTR(B) | #1DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0029 |  | 0061 | 1-9D |  | 1-3D | NO.1 DTR.B | 升/降 | NO.1 DTR.B TAP | TAP_-8.5_8.5(0_2000) |  | B1/D12_A1 | [8 empty] | 仁愛DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | [5 empty] | 155 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D12 | 仁愛DS |  |  | 2DTR | #2DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | NO.2 DTR. | ℃ | NO.2 DTR. 油溫 | OIL_-120_120(-2000_2000) |  | B1/D12_A1 | [8 empty] | 仁愛DS.#2DTR_OIL | #2DTR 油溫 | MTR | [5 empty] | 156 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D12 | 仁愛DS |  |  | 2DTR(A) | #2DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | NO.2 DTR.A | ℃ | NO.2 DTR.A 線溫 | COIL_-120_120(-2000_2000) |  | B1/D12_A1 | [8 empty] | 仁愛DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | [5 empty] | 157 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D12 | 仁愛DS |  |  | 2DTR(B) | #2DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | NO.2 DTR.B | ℃ | NO.2 DTR.B 線溫 | COIL_-120_120(-2000_2000) |  | B1/D12_A1 | [8 empty] | 仁愛DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | [5 empty] | 158 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D12 | 仁愛DS |  |  | 2DTR(A) | #2DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0033 |  | 0063 | 1-A1 |  | 1-3F | NO.2 DTR.A | 升/降 | NO.2 DTR.A TAP | TAP_-8.5_8.5(0_2000) |  | B1/D12_A1 | [8 empty] | 仁愛DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | [5 empty] | 159 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D12 | 仁愛DS |  |  | 2DTR(B) | #2DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0034 |  | 0065 | 1-A2 |  | 1-41 | NO.2 DTR.B | 升/降 | NO.2 DTR.B TAP | TAP_-8.5_8.5(0_2000) |  | B1/D12_A1 | [8 empty] | 仁愛DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | [5 empty] | 160 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D12 | 仁愛DS |  |  | 3DTR | #3DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | NO.3 DTR. | ℃ | NO.3 DTR. 油溫 | OIL_-120_120(-2000_2000) |  | B1/D12_A1 | [8 empty] | 仁愛DS.#3DTR_OIL | #3DTR 油溫 | MTR | [5 empty] | 161 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D12 | 仁愛DS |  |  | 3DTR | #3DTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | NO.3 DTR. | ℃ | NO.3 DTR. 線溫 | COIL_-120_120(-2000_2000) |  | B1/D12_A1 | [8 empty] | 仁愛DS.#3DTR_COIL | #3DTR 線溫 | MTR | [5 empty] | 162 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D12 | 仁愛DS |  |  | 3DTR | #3DTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0037 |  | 0067 | 1-A5 |  | 1-43 | NO.3 DTR. | 升/降 | NO.3 DTR. TAP | TAP_-8.5_8.5(0_2000) |  | B1/D12_A1 | [8 empty] | 仁愛DS.#3DTR_TAP | #3DTR OLTC TAP | MTR | [5 empty] | 163 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D12 | 仁愛DS |  |  | 4DTR | #4DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | NO.4 DTR. | ℃ | NO.4 DTR. 油溫 | OIL_-120_120(-2000_2000) |  | B1/D12_A1 | [8 empty] | 仁愛DS.#4DTR_OIL | #4DTR 油溫 | MTR | [5 empty] | 164 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D12 | 仁愛DS |  |  | 4DTR | #4DTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | NO.4 DTR. | ℃ | NO.4 DTR. 線溫 | COIL_-120_120(-2000_2000) |  | B1/D12_A1 | [8 empty] | 仁愛DS.#4DTR_COIL | #4DTR 線溫 | MTR | [5 empty] | 165 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D12 | 仁愛DS |  |  | 4DTR | #4DTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0040 |  | 0069 | 1-A8 |  | 1-45 | NO.4 DTR. | 升/降 | NO.4 DTR. TAP | TAP_-8.5_8.5(0_2000) |  | B1/D12_A1 | [8 empty] | 仁愛DS.#4DTR_TAP | #4DTR OLTC TAP | MTR | [5 empty] | 166 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D12 | 仁愛DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | 1 DTR-1A | DW | 1 DTR-1A 310 瓦 | MW_-54_54(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | [5 empty] | 167 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | 1 DTR-1A | DVAR | 1 DTR-1A 310 乏 | MVAR_-36_36(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | [5 empty] | 168 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | 1 DTR-1A | A | 1 DTR-1A 310 R相電流 | A_-3000_3000(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | [5 empty] | 169 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | 1 DTR-1A | A | 1 DTR-1A 310 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | [5 empty] | 170 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | 1 DTR-1A | A | 1 DTR-1A 310 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | [5 empty] | 171 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 1ABUS | #1ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0047 |  |  | 1-AF |  |  | PT-1A | KV | #1A PT R相電壓 | kV_-9_9(-2000_2000) | aaa | B3/D12_A1 | [8 empty] | 仁愛DS.11KV#1ABUS_KV | 11KV #1ABUS KV | BUS | [5 empty] | 172 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D12 | 仁愛DS | 11 | 11kV | JA21 | 愛21線(JA21) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | F1 | KVAR | 愛21線 JA21 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛21線KVAR | 11KV愛21線 KVAR | FEEDER | [5 empty] | 173 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA21 | 愛21線(JA21) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | F1 | A | 愛21線 JA21 R相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛21線A1 | 11KV愛21線 R相AMP | FEEDER | [5 empty] | 174 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA21 | 愛21線(JA21) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | F1 | A | 愛21線 JA21 S相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛21線A2 | 11KV愛21線 S相AMP | FEEDER | [5 empty] | 175 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA21 | 愛21線(JA21) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | F1 | A | 愛21線 JA21 T相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛21線A3 | 11KV愛21線 T相AMP | FEEDER | [5 empty] | 176 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA21 | 愛21線(JA21) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | F1 | A | 愛21線 JA21 N相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛21線A0 | 11KV愛21線 N相AMP | FEEDER | [5 empty] | 177 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA22 | 愛22線(JA22) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | F2 | KVAR | 愛22線 JA22 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛22線KVAR | 11KV愛22線 KVAR | FEEDER | [5 empty] | 178 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA22 | 愛22線(JA22) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | F2 | A | 愛22線 JA22 R相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛22線A1 | 11KV愛22線 R相AMP | FEEDER | [5 empty] | 179 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA22 | 愛22線(JA22) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | F2 | A | 愛22線 JA22 S 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛22線A2 | 11KV愛22線 S相AMP | FEEDER | [5 empty] | 180 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA22 | 愛22線(JA22) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | F2 | A | 愛22線 JA22 T 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛22線A3 | 11KV愛22線 T相AMP | FEEDER | [5 empty] | 181 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA22 | 愛22線(JA22) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | F2 | A | 愛22線 JA22 N 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛22線A0 | 11KV愛22線 N相AMP | FEEDER | [5 empty] | 182 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA23 | 愛23線(JA23) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | F3 | KVAR | 愛23線 JA23 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛23線KVAR | 11KV愛23線 KVAR | FEEDER | [5 empty] | 183 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA23 | 愛23線(JA23) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | F3 | A | 愛23線 JA23 R相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛23線A1 | 11KV愛23線 R相AMP | FEEDER | [5 empty] | 184 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA23 | 愛23線(JA23) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0060 |  |  | 1-BC |  |  | F3 | A | 愛23線 JA23 S 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛23線A2 | 11KV愛23線 S相AMP | FEEDER | [5 empty] | 185 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA23 | 愛23線(JA23) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | F3 | A | 愛23線 JA23 T 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛23線A3 | 11KV愛23線 T相AMP | FEEDER | [5 empty] | 186 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA23 | 愛23線(JA23) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | F3 | A | 愛23線 JA23 N 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛23線A0 | 11KV愛23線 N相AMP | FEEDER | [5 empty] | 187 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA24 | 愛24線(JA24) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0063 |  |  | 1-BF |  |  | F4 | KVAR | 愛24線 JA24 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛24線KVAR | 11KV愛24線 KVAR | FEEDER | [5 empty] | 188 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 0 |  | RTU | RTU |  | ADCL2 |  |  | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.2 AI Card) |  |  |  |  | B3/D12_A1 | [16 empty] | 189 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D12 | 仁愛DS | 0 |  | RTU | RTU |  | ADCH2 |  |  | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.2 AI Card) |  |  |  |  | B3/D12_A1 | [16 empty] | 190 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D12 | 仁愛DS | 11 | 11kV | JA24 | 愛24線(JA24) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | F4 | A | 愛24線 JA24 R 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛24線A1 | 11KV愛24線 R相AMP | FEEDER | [5 empty] | 191 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA24 | 愛24線(JA24) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | F4 | A | 愛24線 JA24 S 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛24線A2 | 11KV愛24線 S相AMP | FEEDER | [5 empty] | 192 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA24 | 愛24線(JA24) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | F4 | A | 愛24線 JA24 T 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛24線A3 | 11KV愛24線 T相AMP | FEEDER | [5 empty] | 193 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA24 | 愛24線(JA24) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | F4 | A | 愛24線 JA24 N 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛24線A0 | 11KV愛24線 N相AMP | FEEDER | [5 empty] | 194 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA25 | 愛25線(JA25) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | F5 | KVAR | 愛25線 JA25 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛25線KVAR | 11KV愛25線 KVAR | FEEDER | [5 empty] | 195 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA25 | 愛25線(JA25) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | F5 | A | 愛25線 JA25 R 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛25線A1 | 11KV愛25線 R相AMP | FEEDER | [5 empty] | 196 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA25 | 愛25線(JA25) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | F5 | A | 愛25線 JA25 S 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛25線A2 | 11KV愛25線 S相AMP | FEEDER | [5 empty] | 197 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA25 | 愛25線(JA25) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | F5 | A | 愛25線 JA25 T 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛25線A3 | 11KV愛25線 T相AMP | FEEDER | [5 empty] | 198 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA25 | 愛25線(JA25) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | F5 | A | 愛25線 JA25 N相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛25線A0 | 11KV愛25線 N相AMP | FEEDER | [5 empty] | 199 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 100 | TIE-1(100) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | TIE-1 | A | TIE-1 100 R 相電流 | A_-2000_2000(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.11KV_100_A1 | 11KV 100 R相AMP | TIE | [5 empty] | 200 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 100 | TIE-1(100) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | TIE-1 | A | TIE-1 100 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.11KV_100_A2 | 11KV 100 S相AMP | TIE | [5 empty] | 201 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 100 | TIE-1(100) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | TIE-1 | A | TIE-1 100 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.11KV_100_A3 | 11KV 100 T相AMP | TIE | [5 empty] | 202 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | 1 DTR-1B | DW | 1 DTR-1B 320 瓦 | MW_-54_54(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | [5 empty] | 203 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | 1 DTR-1B | DVAR | 1 DTR-1B 320 乏 | MVAR_-36_36(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | [5 empty] | 204 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | 1 DTR-1B | A | 1 DTR-1B 320 R相電流 | A_-3000_3000(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | [5 empty] | 205 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | 1 DTR-1B | A | 1 DTR-1B 320 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | [5 empty] | 206 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | 1 DTR-1B | A | 1 DTR-1B 320 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | [5 empty] | 207 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 1BBUS | #1BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0083 |  |  | 1-D3 |  |  | PT-1B | KV | #1B PT R相電壓 | kV_-9_9(-2000_2000) | baa | B3/D12_A1 | [8 empty] | 仁愛DS.11KV#1BBUS_KV | 11KV #1BBUS KV | BUS | [5 empty] | 208 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D12 | 仁愛DS | 11 | 11kV | JA26 | 愛26線(JA26) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | F6 | KVAR | 愛26線 JA26 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛26線KVAR | 11KV愛26線 KVAR | FEEDER | [5 empty] | 209 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA26 | 愛26線(JA26) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | F6 | A | 愛26線 JA26 R 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛26線A1 | 11KV愛26線 R相AMP | FEEDER | [5 empty] | 210 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA26 | 愛26線(JA26) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | F6 | A | 愛26線 JA26 S相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛26線A2 | 11KV愛26線 S相AMP | FEEDER | [5 empty] | 211 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA26 | 愛26線(JA26) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | F6 | A | 愛26線 JA26 T相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛26線A3 | 11KV愛26線 T相AMP | FEEDER | [5 empty] | 212 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA26 | 愛26線(JA26) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | F6 | A | 愛26線 JA26 N相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛26線A0 | 11KV愛26線 N相AMP | FEEDER | [5 empty] | 213 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA27 | 愛27線(JA27) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | F7 | KVAR | 愛27線 JA27 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛27線KVAR | 11KV愛27線 KVAR | FEEDER | [5 empty] | 214 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA27 | 愛27線(JA27) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | F7 | A | 愛27線 JA27 R相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛27線A1 | 11KV愛27線 R相AMP | FEEDER | [5 empty] | 215 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA27 | 愛27線(JA27) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | F7 | A | 愛27線 JA27 S相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛27線A2 | 11KV愛27線 S相AMP | FEEDER | [5 empty] | 216 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA27 | 愛27線(JA27) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | F7 | A | 愛27線 JA27 T相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛27線A3 | 11KV愛27線 T相AMP | FEEDER | [5 empty] | 217 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA27 | 愛27線(JA27) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | F7 | A | 愛27線 JA27 N相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛27線A0 | 11KV愛27線 N相AMP | FEEDER | [5 empty] | 218 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA28 | 愛28線(JA28) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | F8 | KVAR | 愛28線 JA28 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛28線KVAR | 11KV愛28線 KVAR | FEEDER | [5 empty] | 219 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA28 | 愛28線(JA28) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | F8 | A | 愛28線 JA28 R相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛28線A1 | 11KV愛28線 R相AMP | FEEDER | [5 empty] | 220 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA28 | 愛28線(JA28) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | F8 | A | 愛28線 JA28 S相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛28線A2 | 11KV愛28線 S相AMP | FEEDER | [5 empty] | 221 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA28 | 愛28線(JA28) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | F8 | A | 愛28線 JA28 T相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛28線A3 | 11KV愛28線 T相AMP | FEEDER | [5 empty] | 222 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA28 | 愛28線(JA28) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0098 |  |  | 1-E2 |  |  | F8 | A | 愛28線 JA28 N相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛28線A0 | 11KV愛28線 N相AMP | FEEDER | [5 empty] | 223 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA29 | 愛29線(JA29) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | F9 | KVAR | 愛29線 JA29 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛29線KVAR | 11KV愛29線 KVAR | FEEDER | [5 empty] | 224 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA29 | 愛29線(JA29) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | F9 | A | 愛29線 JA29 R相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛29線A1 | 11KV愛29線 R相AMP | FEEDER | [5 empty] | 225 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA29 | 愛29線(JA29) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0101 |  |  | 1-E5 |  |  | F9 | A | 愛29線 JA29 S 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛29線A2 | 11KV愛29線 S相AMP | FEEDER | [5 empty] | 226 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA29 | 愛29線(JA29) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | F9 | A | 愛29線 JA29 T相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛29線A3 | 11KV愛29線 T相AMP | FEEDER | [5 empty] | 227 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA29 | 愛29線(JA29) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | F9 | A | 愛29線 JA29 N相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛29線A0 | 11KV愛29線 N相AMP | FEEDER | [5 empty] | 228 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA30 | 愛30線(JA30) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | F10 | KVAR | 愛30線 JA30 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛30線KVAR | 11KV愛30線 KVAR | FEEDER | [5 empty] | 229 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA30 | 愛30線(JA30) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | F10 | A | 愛30線 JA30 R相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛30線A1 | 11KV愛30線 R相AMP | FEEDER | [5 empty] | 230 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA30 | 愛30線(JA30) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | F10 | A | 愛30線 JA30 S 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛30線A2 | 11KV愛30線 S相AMP | FEEDER | [5 empty] | 231 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA30 | 愛30線(JA30) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | F10 | A | 愛30線 JA30 T相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛30線A3 | 11KV愛30線 T相AMP | FEEDER | [5 empty] | 232 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA30 | 愛30線(JA30) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | F10 | A | 愛30線 JA30 N相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛30線A0 | 11KV愛30線 N相AMP | FEEDER | [5 empty] | 233 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | 2 DTR-2A | DW | 2 DTR-2A 330 瓦 | MW_-54_54(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | [5 empty] | 234 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | 2 DTR-2A | DVAR | 2 DTR-2A 330 乏 | MVAR_-36_36(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | [5 empty] | 235 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | 2 DTR-2A | A | 2 DTR-2A 330 R 相電流 | A_-3000_3000(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | [5 empty] | 236 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | 2 DTR-2A | A | 2 DTR-2A 330 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | [5 empty] | 237 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | 2 DTR-2A | A | 2 DTR-2A 330 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | [5 empty] | 238 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 2ABUS | #2ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0114 |  |  | 1-F2 |  |  | PT-2A | KV | #2A PT R相電壓 | kV_-9_9(-2000_2000) | aba | B3/D12_A1 | [8 empty] | 仁愛DS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS | [5 empty] | 239 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D12 | 仁愛DS | 11 | 11kV | JA31 | 愛31線(JA31) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | F11 | KVAR | 愛31線 JA31 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛31線KVAR | 11KV愛31線 KVAR | FEEDER | [5 empty] | 240 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA31 | 愛31線(JA31) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | F11 | A | 愛31線 JA31 R 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛31線A1 | 11KV愛31線 R相AMP | FEEDER | [5 empty] | 241 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA31 | 愛31線(JA31) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | F11 | A | 愛31線 JA31 S相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛31線A2 | 11KV愛31線 S相AMP | FEEDER | [5 empty] | 242 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA31 | 愛31線(JA31) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | F11 | A | 愛31線 JA31 T相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛31線A3 | 11KV愛31線 T相AMP | FEEDER | [5 empty] | 243 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA31 | 愛31線(JA31) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | F11 | A | 愛31線 JA31 N相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛31線A0 | 11KV愛31線 N相AMP | FEEDER | [5 empty] | 244 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA32 | 愛32線(JA32) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | F12 | KVAR | 愛32線 JA32 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛32線KVAR | 11KV愛32線 KVAR | FEEDER | [5 empty] | 245 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA32 | 愛32線(JA32) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | F12 | A | 愛32線 JA32 R相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛32線A1 | 11KV愛32線 R相AMP | FEEDER | [5 empty] | 246 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA32 | 愛32線(JA32) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | F12 | A | 愛32線 JA32 S相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛32線A2 | 11KV愛32線 S相AMP | FEEDER | [5 empty] | 247 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA32 | 愛32線(JA32) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | F12 | A | 愛32線 JA32 T相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛32線A3 | 11KV愛32線 T相AMP | FEEDER | [5 empty] | 248 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA32 | 愛32線(JA32) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | F12 | A | 愛32線 JA32 N相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛32線A0 | 11KV愛32線 N相AMP | FEEDER | [5 empty] | 249 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA33 | 愛33線(JA33) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | F13 | KVAR | 愛33線 JA33 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛33線KVAR | 11KV愛33線 KVAR | FEEDER | [5 empty] | 250 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA33 | 愛33線(JA33) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | F13 | A | 愛33線 JA33 R 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛33線A1 | 11KV愛33線 R相AMP | FEEDER | [5 empty] | 251 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA33 | 愛33線(JA33) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | F13 | A | 愛33線 JA33 S 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛33線A2 | 11KV愛33線 S相AMP | FEEDER | [5 empty] | 252 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 0 |  | RTU | RTU |  | ADCL3 |  |  | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.3 AI Card) |  |  |  |  | B3/D12_A1 | [16 empty] | 253 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D12 | 仁愛DS | 0 |  | RTU | RTU |  | ADCH3 |  |  | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.3 AI Card) |  |  |  |  | B3/D12_A1 | [16 empty] | 254 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D12 | 仁愛DS | 11 | 11kV | JA33 | 愛33線(JA33) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | F13 | A | 愛33線 JA33 T相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛33線A3 | 11KV愛33線 T相AMP | FEEDER | [5 empty] | 255 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA33 | 愛33線(JA33) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | F13 | A | 愛33線 JA33 N相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛33線A0 | 11KV愛33線 N相AMP | FEEDER | [5 empty] | 256 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA34 | 愛34線(JA34) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | F14 | KVAR | 愛34線 JA34 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛34線KVAR | 11KV愛34線 KVAR | FEEDER | [5 empty] | 257 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA34 | 愛34線(JA34) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0133 |  |  | 2-85 |  |  | F14 | A | 愛34線 JA34 R 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛34線A1 | 11KV愛34線 R相AMP | FEEDER | [5 empty] | 258 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA34 | 愛34線(JA34) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | F14 | A | 愛34線 JA34 S 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛34線A2 | 11KV愛34線 S相AMP | FEEDER | [5 empty] | 259 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA34 | 愛34線(JA34) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0135 |  |  | 2-87 |  |  | F14 | A | 愛34線 JA34 T 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛34線A3 | 11KV愛34線 T相AMP | FEEDER | [5 empty] | 260 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA34 | 愛34線(JA34) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0136 |  |  | 2-88 |  |  | F14 | A | 愛34線 JA34 N相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛34線A0 | 11KV愛34線 N相AMP | FEEDER | [5 empty] | 261 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA35 | 愛35線(JA35) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0137 |  |  | 2-89 |  |  | F15 | KVAR | 愛35線 JA35 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛35線KVAR | 11KV愛35線 KVAR | FEEDER | [5 empty] | 262 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA35 | 愛35線(JA35) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0138 |  |  | 2-8A |  |  | F15 | A | 愛35線 JA35 R 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛35線A1 | 11KV愛35線 R相AMP | FEEDER | [5 empty] | 263 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA35 | 愛35線(JA35) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0139 |  |  | 2-8B |  |  | F15 | A | 愛35線 JA35 S 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛35線A2 | 11KV愛35線 S相AMP | FEEDER | [5 empty] | 264 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA35 | 愛35線(JA35) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0140 |  |  | 2-8C |  |  | F15 | A | 愛35線 JA35 T 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛35線A3 | 11KV愛35線 T相AMP | FEEDER | [5 empty] | 265 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA35 | 愛35線(JA35) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0141 |  |  | 2-8D |  |  | F15 | A | 愛35線 JA35 N相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛35線A0 | 11KV愛35線 N相AMP | FEEDER | [5 empty] | 266 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0142 |  |  | 2-8E |  |  | 2 DTR-2B | DW | 2 DTR-2B 340 瓦 | MW_-54_54(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | [5 empty] | 267 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0143 |  |  | 2-8F |  |  | 2 DTR-2B | DVAR | 2 DTR-2B 340 乏 | MVAR_-36_36(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | [5 empty] | 268 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0144 |  |  | 2-90 |  |  | 2 DTR-2B | A | 2 DTR-2B 340 R 相電流 | A_-3000_3000(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | [5 empty] | 269 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0145 |  |  | 2-91 |  |  | 2 DTR-2B | A | 2 DTR-2B 340 S 相電流 | A_-3000_3000(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | [5 empty] | 270 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0146 |  |  | 2-92 |  |  | 2 DTR-2B | A | 2 DTR-2B 340 T 相電流 | A_-3000_3000(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | [5 empty] | 271 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 2BBUS | #2BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0147 |  |  | 2-93 |  |  | PT-2B | KV | #2B PT R相電壓 | kV_-9_9(-2000_2000) | bba | B3/D12_A1 | [8 empty] | 仁愛DS.11KV#2BBUS_KV | 11KV #2BBUS KV | BUS | [5 empty] | 272 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D12 | 仁愛DS | 11 | 11kV | JA36 | 愛36線(JA36) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0148 |  |  | 2-94 |  |  | F16 | KVAR | 愛36線 JA36 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛36線KVAR | 11KV愛36線 KVAR | FEEDER | [5 empty] | 273 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA36 | 愛36線(JA36) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0149 |  |  | 2-95 |  |  | F16 | A | 愛36線 JA36 R 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛36線A1 | 11KV愛36線 R相AMP | FEEDER | [5 empty] | 274 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA36 | 愛36線(JA36) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0150 |  |  | 2-96 |  |  | F16 | A | 愛36線 JA36 S 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛36線A2 | 11KV愛36線 S相AMP | FEEDER | [5 empty] | 275 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA36 | 愛36線(JA36) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0151 |  |  | 2-97 |  |  | F16 | A | 愛36線 JA36 T 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛36線A3 | 11KV愛36線 T相AMP | FEEDER | [5 empty] | 276 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA36 | 愛36線(JA36) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0152 |  |  | 2-98 |  |  | F16 | A | 愛36線 JA36 N相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛36線A0 | 11KV愛36線 N相AMP | FEEDER | [5 empty] | 277 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA37 | 愛37線(JA37) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0153 |  |  | 2-99 |  |  | F17 | KVAR | 愛37線 JA37 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛37線KVAR | 11KV愛37線 KVAR | FEEDER | [5 empty] | 278 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA37 | 愛37線(JA37) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0154 |  |  | 2-9A |  |  | F17 | A | 愛37線 JA37 R 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛37線A1 | 11KV愛37線 R相AMP | FEEDER | [5 empty] | 279 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA37 | 愛37線(JA37) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0155 |  |  | 2-9B |  |  | F17 | A | 愛37線 JA37 S 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛37線A2 | 11KV愛37線 S相AMP | FEEDER | [5 empty] | 280 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA37 | 愛37線(JA37) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0156 |  |  | 2-9C |  |  | F17 | A | 愛37線 JA37 T 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛37線A3 | 11KV愛37線 T相AMP | FEEDER | [5 empty] | 281 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA37 | 愛37線(JA37) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0157 |  |  | 2-9D |  |  | F17 | A | 愛37線 JA37 N相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛37線A0 | 11KV愛37線 N相AMP | FEEDER | [5 empty] | 282 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA38 | 愛38線(JA38) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0158 |  |  | 2-9E |  |  | F18 | KVAR | 愛38線 JA38 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛38線KVAR | 11KV愛38線 KVAR | FEEDER | [5 empty] | 283 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA38 | 愛38線(JA38) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0159 |  |  | 2-9F |  |  | F18 | A | 愛38線 JA38 R 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛38線A1 | 11KV愛38線 R相AMP | FEEDER | [5 empty] | 284 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA38 | 愛38線(JA38) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0160 |  |  | 2-A0 |  |  | F18 | A | 愛38線 JA38 S 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛38線A2 | 11KV愛38線 S相AMP | FEEDER | [5 empty] | 285 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA38 | 愛38線(JA38) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0161 |  |  | 2-A1 |  |  | F18 | A | 愛38線 JA38 T 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛38線A3 | 11KV愛38線 T相AMP | FEEDER | [5 empty] | 286 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA38 | 愛38線(JA38) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0162 |  |  | 2-A2 |  |  | F18 | A | 愛38線 JA38 N相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛38線A0 | 11KV愛38線 N相AMP | FEEDER | [5 empty] | 287 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA39 | 愛39線(JA39) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0163 |  |  | 2-A3 |  |  | F19 | KVAR | 愛39線 JA39 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛39線KVAR | 11KV愛39線 KVAR | FEEDER | [5 empty] | 288 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA39 | 愛39線(JA39) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0164 |  |  | 2-A4 |  |  | F19 | A | 愛39線 JA39 R 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛39線A1 | 11KV愛39線 R相AMP | FEEDER | [5 empty] | 289 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA39 | 愛39線(JA39) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0165 |  |  | 2-A5 |  |  | F19 | A | 愛39線 JA39 S 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛39線A2 | 11KV愛39線 S相AMP | FEEDER | [5 empty] | 290 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA39 | 愛39線(JA39) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0166 |  |  | 2-A6 |  |  | F19 | A | 愛39線 JA39 T 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛39線A3 | 11KV愛39線 T相AMP | FEEDER | [5 empty] | 291 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA39 | 愛39線(JA39) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0167 |  |  | 2-A7 |  |  | F19 | A | 愛39線 JA39 N相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛39線A0 | 11KV愛39線 N相AMP | FEEDER | [5 empty] | 292 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA40 | 愛40線(JA40) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0168 |  |  | 2-A8 |  |  | F20 | KVAR | 愛40線 JA40 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛40線KVAR | 11KV愛40線 KVAR | FEEDER | [5 empty] | 293 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA40 | 愛40線(JA40) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0169 |  |  | 2-A9 |  |  | F20 | A | 愛40線 JA40 R 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛40線A1 | 11KV愛40線 R相AMP | FEEDER | [5 empty] | 294 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA40 | 愛40線(JA40) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0170 |  |  | 2-AA |  |  | F20 | A | 愛40線 JA40 S 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛40線A2 | 11KV愛40線 S相AMP | FEEDER | [5 empty] | 295 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA40 | 愛40線(JA40) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0171 |  |  | 2-AB |  |  | F20 | A | 愛40線 JA40 T 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛40線A3 | 11KV愛40線 T相AMP | FEEDER | [5 empty] | 296 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | JA40 | 愛40線(JA40) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0172 |  |  | 2-AC |  |  | F20 | A | 愛40線 JA40 N相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛40線A0 | 11KV愛40線 N相AMP | FEEDER | [5 empty] | 297 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 200 | TIE-2(200) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0173 |  |  | 2-AD |  |  | TIE-2 | A | TIE-2 200 R 相電流 | A_-2000_2000(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.11KV_200_A1 | 11KV 200 R相AMP | TIE | [5 empty] | 298 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 200 | TIE-2(200) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0174 |  |  | 2-AE |  |  | TIE-2 | A | TIE-2 200 S 相電流 | A_-2000_2000(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.11KV_200_A2 | 11KV 200 S相AMP | TIE | [5 empty] | 299 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 200 | TIE-2(200) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0175 |  |  | 2-AF |  |  | TIE-2 | A | TIE-2 200 T 相電流 | A_-2000_2000(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.11KV_200_A3 | 11KV 200 T相AMP | TIE | [5 empty] | 300 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 350 | #3DTR(350) |  | KW |  | B2 | MvMoment | KW |  | Y |  | AI | [6 empty] | 0176 |  |  | 2-B0 |  |  | 3 DTR | DW | 3 DTR 350 瓦 | MW_-108_108(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.#3DTR_MW | #3DTR二次側 MW | MTR | [5 empty] | 301 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.216 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 350 | #3DTR(350) |  | KVAR |  | B2 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0177 |  |  | 2-B1 |  |  | 3 DTR | DVAR | 3 DTR 350 乏 | MVAR_-72_72(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.#3DTR_MVAR | #3DTR二次側 MVAR | MTR | [5 empty] | 302 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 350 | #3DTR(350) |  | I_R |  | B2 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0178 |  |  | 2-B2 |  |  | 3 DTR | A | 3 DTR 350 R 相電流 | A_-3000_3000(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.#3DTR_A1 | #3DTR二次側 R相AMP | MTR | [5 empty] | 303 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 350 | #3DTR(350) |  | I_S |  | B2 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0179 |  |  | 2-B3 |  |  | 3 DTR | A | 3 DTR 350 S 相電流 | A_-3000_3000(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.#3DTR_A2 | #3DTR二次側 S相AMP | MTR | [5 empty] | 304 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 350 | #3DTR(350) |  | I_T |  | B2 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0180 |  |  | 2-B4 |  |  | 3 DTR | A | 3 DTR 350 T 相電流 | A_-3000_3000(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.#3DTR_A3 | #3DTR二次側 T相AMP | MTR | [5 empty] | 305 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 3BUS | #3BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0181 |  |  | 2-B5 |  |  | PT-3 | KV | #3 PT R相電壓 | kV_-18_18(-2000_2000) | aca | B3/D12_A1 | [8 empty] | 仁愛DS.23KV#3BUS_KV | 23KV #3BUS KV | BUS | [5 empty] | 306 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D12 | 仁愛DS | 22 | 22kV | JA71 | 愛71線(JA71) |  | KVAR |  | B2 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0182 |  |  | 2-B6 |  |  | F21 | A | 愛71線 JA71 乏 | KVAR_-18000_18000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛71線KVAR | 23KV愛71線 KVAR | FEEDER | [5 empty] | 307 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA71 | 愛71線(JA71) |  | I_R |  | B2 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0183 |  |  | 2-B7 |  |  | F21 | A | 愛71線 JA71 R 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛71線A1 | 23KV愛71線 R相AMP | FEEDER | [5 empty] | 308 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA71 | 愛71線(JA71) |  | I_S |  | B2 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0184 |  |  | 2-B8 |  |  | F21 | A | 愛71線 JA71 S 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛71線A2 | 23KV愛71線 S相AMP | FEEDER | [5 empty] | 309 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA71 | 愛71線(JA71) |  | I_T |  | B2 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0185 |  |  | 2-B9 |  |  | F21 | A | 愛71線 JA71 T 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛71線A3 | 23KV愛71線 T相AMP | FEEDER | [5 empty] | 310 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA71 | 愛71線(JA71) |  | I_N |  | B2 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0186 |  |  | 2-BA |  |  | F21 | A | 愛71線 JA71 N相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛71線A0 | 23KV愛71線 N相AMP | FEEDER | [5 empty] | 311 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA72 | 愛72線(JA72) |  | KVAR |  | B2 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0187 |  |  | 2-BB |  |  | F22 | KVAR | 愛72線 JA72 乏 | KVAR_-18000_18000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛72線KVAR | 23KV愛72線 KVAR | FEEDER | [5 empty] | 312 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA72 | 愛72線(JA72) |  | I_R |  | B2 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0188 |  |  | 2-BC |  |  | F22 | A | 愛72線 JA72 R 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛72線A1 | 23KV愛72線 R相AMP | FEEDER | [5 empty] | 313 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA72 | 愛72線(JA72) |  | I_S |  | B2 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0189 |  |  | 2-BD |  |  | F22 | A | 愛72線 JA72 S 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛72線A2 | 23KV愛72線 S相AMP | FEEDER | [5 empty] | 314 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA72 | 愛72線(JA72) |  | I_T |  | B2 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0190 |  |  | 2-BE |  |  | F22 | A | 愛72線 JA72 T 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛72線A3 | 23KV愛72線 T相AMP | FEEDER | [5 empty] | 315 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA72 | 愛72線(JA72) |  | I_N |  | B2 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0191 |  |  | 2-BF |  |  | F22 | A | 愛72線 JA72 N相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛72線A0 | 23KV愛72線 N相AMP | FEEDER | [5 empty] | 316 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 0 |  | RTU | RTU |  | ADCL4 |  |  | MvMoment | No4 AI參考點 10% |  | Y |  | AI | [6 empty] | 0192 |  |  | 2-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.4 AI Card) |  |  |  |  | B3/D12_A1 | [16 empty] | 317 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D12 | 仁愛DS | 0 |  | RTU | RTU |  | ADCH4 |  |  | MvMoment | No4 AI參考點 90% |  | Y |  | AI | [6 empty] | 0193 |  |  | 2-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.4 AI Card) |  |  |  |  | B3/D12_A1 | [16 empty] | 318 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D12 | 仁愛DS | 22 | 22kV | JA73 | 愛73線(JA73) |  | KVAR |  | B2 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0194 |  |  | 2-C2 |  |  | F23 | KVAR | 愛73線 JA73 乏 | KVAR_-18000_18000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛73線KVAR | 23KV愛73線 KVAR | FEEDER | [5 empty] | 319 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA73 | 愛73線(JA73) |  | I_R |  | B2 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0195 |  |  | 2-C3 |  |  | F23 | A | 愛73線 JA73 R 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛73線A1 | 23KV愛73線 R相AMP | FEEDER | [5 empty] | 320 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA73 | 愛73線(JA73) |  | I_S |  | B2 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0196 |  |  | 2-C4 |  |  | F23 | A | 愛73線 JA73 S 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛73線A2 | 23KV愛73線 S相AMP | FEEDER | [5 empty] | 321 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA73 | 愛73線(JA73) |  | I_T |  | B2 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0197 |  |  | 2-C5 |  |  | F23 | A | 愛73線 JA73 T 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛73線A3 | 23KV愛73線 T相AMP | FEEDER | [5 empty] | 322 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA73 | 愛73線(JA73) |  | I_N |  | B2 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0198 |  |  | 2-C6 |  |  | F23 | A | 愛73線 JA73 N相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛73線A0 | 23KV愛73線 N相AMP | FEEDER | [5 empty] | 323 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA74 | 愛74線(JA74) |  | KVAR |  | B2 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0199 |  |  | 2-C7 |  |  | F24 | KVAR | 愛74線 JA74 乏 | KVAR_-18000_18000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛74線KVAR | 23KV愛74線 KVAR | FEEDER | [5 empty] | 324 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA74 | 愛74線(JA74) |  | I_R |  | B2 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0200 |  |  | 2-C8 |  |  | F24 | A | 愛74線 JA74 R 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛74線A1 | 23KV愛74線 R相AMP | FEEDER | [5 empty] | 325 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA74 | 愛74線(JA74) |  | I_S |  | B2 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0201 |  |  | 2-C9 |  |  | F24 | A | 愛74線 JA74 S 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛74線A2 | 23KV愛74線 S相AMP | FEEDER | [5 empty] | 326 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA74 | 愛74線(JA74) |  | I_T |  | B2 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0202 |  |  | 2-CA |  |  | F24 | A | 愛74線 JA74 T 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛74線A3 | 23KV愛74線 T相AMP | FEEDER | [5 empty] | 327 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA74 | 愛74線(JA74) |  | I_N |  | B2 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0203 |  |  | 2-CB |  |  | F24 | A | 愛74線 JA74 N相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛74線A0 | 23KV愛74線 N相AMP | FEEDER | [5 empty] | 328 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA75 | 愛75線(JA75) |  | KVAR |  | B2 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0204 |  |  | 2-CC |  |  | F25 | KVAR | 愛75線 JA75 乏 | KVAR_-18000_18000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛75線KVAR | 23KV愛75線 KVAR | FEEDER | [5 empty] | 329 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA75 | 愛75線(JA75) |  | I_R |  | B2 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0205 |  |  | 2-CD |  |  | F25 | A | 愛75線 JA75 R 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛75線A1 | 23KV愛75線 R相AMP | FEEDER | [5 empty] | 330 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA75 | 愛75線(JA75) |  | I_S |  | B2 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0206 |  |  | 2-CE |  |  | F25 | A | 愛75線 JA75 S 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛75線A2 | 23KV愛75線 S相AMP | FEEDER | [5 empty] | 331 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA75 | 愛75線(JA75) |  | I_T |  | B2 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0207 |  |  | 2-CF |  |  | F25 | A | 愛75線 JA75 T 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛75線A3 | 23KV愛75線 T相AMP | FEEDER | [5 empty] | 332 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA75 | 愛75線(JA75) |  | I_N |  | B2 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0208 |  |  | 2-D0 |  |  | F25 | A | 愛75線 JA75 N相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛75線A0 | 23KV愛75線 N相AMP | FEEDER | [5 empty] | 333 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA76 | 愛76線(JA76) |  | KVAR |  | B2 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0209 |  |  | 2-D1 |  |  | F26 | KVAR | 愛76線 JA76 乏 | KVAR_-18000_18000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛76線KVAR | 23KV愛76線 KVAR | FEEDER | [5 empty] | 334 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA76 | 愛76線(JA76) |  | I_R |  | B2 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0210 |  |  | 2-D2 |  |  | F26 | A | 愛76線 JA76 R 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛76線A1 | 23KV愛76線 R相AMP | FEEDER | [5 empty] | 335 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA76 | 愛76線(JA76) |  | I_S |  | B2 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0211 |  |  | 2-D3 |  |  | F26 | A | 愛76線 JA76 S 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛76線A2 | 23KV愛76線 S相AMP | FEEDER | [5 empty] | 336 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA76 | 愛76線(JA76) |  | I_T |  | B2 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0212 |  |  | 2-D4 |  |  | F26 | A | 愛76線 JA76 T 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛76線A3 | 23KV愛76線 T相AMP | FEEDER | [5 empty] | 337 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA76 | 愛76線(JA76) |  | I_N |  | B2 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0213 |  |  | 2-D5 |  |  | F26 | A | 愛76線 JA76 N相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛76線A0 | 23KV愛76線 N相AMP | FEEDER | [5 empty] | 338 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA77 | 愛77線(JA77) |  | KVAR |  | B2 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0214 |  |  | 2-D6 |  |  | F27 | KVAR | 愛77線 JA77 乏 | KVAR_-18000_18000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛77線KVAR | 23KV愛77線 KVAR | FEEDER | [5 empty] | 339 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA77 | 愛77線(JA77) |  | I_R |  | B2 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0215 |  |  | 2-D7 |  |  | F27 | A | 愛77線 JA77 R 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛77線A1 | 23KV愛77線 R相AMP | FEEDER | [5 empty] | 340 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA77 | 愛77線(JA77) |  | I_S |  | B2 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0216 |  |  | 2-D8 |  |  | F27 | A | 愛77線 JA77 S 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛77線A2 | 23KV愛77線 S相AMP | FEEDER | [5 empty] | 341 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA77 | 愛77線(JA77) |  | I_T |  | B2 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0217 |  |  | 2-D9 |  |  | F27 | A | 愛77線 JA77 T 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛77線A3 | 23KV愛77線 T相AMP | FEEDER | [5 empty] | 342 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA77 | 愛77線(JA77) |  | I_N |  | B2 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0218 |  |  | 2-DA |  |  | F27 | A | 愛77線 JA77 N相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛77線A0 | 23KV愛77線 N相AMP | FEEDER | [5 empty] | 343 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA78 | 愛78線(JA78) |  | KVAR |  | B2 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0219 |  |  | 2-DB |  |  | F28 | KVAR | 愛78線 JA78 乏 | KVAR_-18000_18000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛78線KVAR | 23KV愛78線 KVAR | FEEDER | [5 empty] | 344 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA78 | 愛78線(JA78) |  | I_R |  | B2 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0220 |  |  | 2-DC |  |  | F28 | A | 愛78線 JA78 R 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛78線A1 | 23KV愛78線 R相AMP | FEEDER | [5 empty] | 345 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA78 | 愛78線(JA78) |  | I_S |  | B2 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0221 |  |  | 2-DD |  |  | F28 | A | 愛78線 JA78 S 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛78線A2 | 23KV愛78線 S相AMP | FEEDER | [5 empty] | 346 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA78 | 愛78線(JA78) |  | I_T |  | B2 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0222 |  |  | 2-DE |  |  | F28 |  | 愛78線 JA78 T 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛78線A3 | 23KV愛78線 T相AMP | FEEDER | [5 empty] | 347 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA78 | 愛78線(JA78) |  | I_N |  | B2 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0223 |  |  | 2-DF |  |  | F28 | A | 愛78線 JA78 N相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛78線A0 | 23KV愛78線 N相AMP | FEEDER | [5 empty] | 348 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 370 | #4DTR(370) |  | KW |  | B2 | MvMoment | KW |  | Y |  | AI | [6 empty] | 0224 |  |  | 2-E0 |  |  | 4 DTR | DW | 4 DTR 370 瓦 | MW_-108_108(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.#4DTR_MW | #4DTR二次側 MW | MTR | [5 empty] | 349 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.216 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 370 | #4DTR(370) |  | KVAR |  | B2 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0225 |  |  | 2-E1 |  |  | 4 DTR | DVAR | 4 DTR 370 乏 | MVAR_-72_72(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.#4DTR_MVAR | #4DTR二次側 MVAR | MTR | [5 empty] | 350 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 370 | #4DTR(370) |  | I_R |  | B2 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0226 |  |  | 2-E2 |  |  | 4 DTR | A | 4 DTR 370 R 相電流 | A_-3000_3000(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.#4DTR_A1 | #4DTR二次側 R相AMP | MTR | [5 empty] | 351 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 370 | #4DTR(370) |  | I_S |  | B2 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0227 |  |  | 2-E3 |  |  | 4 DTR | A | 4 DTR 370 S 相電流 | A_-3000_3000(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.#4DTR_A2 | #4DTR二次側 S相AMP | MTR | [5 empty] | 352 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 370 | #4DTR(370) |  | I_T |  | B2 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0228 |  |  | 2-E4 |  |  | 4 DTR | A | 4 DTR 370 T 相電流 | A_-3000_3000(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.#4DTR_A3 | #4DTR二次側 T相AMP | MTR | [5 empty] | 353 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22KV | 4BUS | #4BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0229 |  |  | 2-E5 |  |  | PT-4 | KV | #4 PT R相電壓 | kV_-18_18(-2000_2000) | ada | B3/D12_A1 | [8 empty] | 仁愛DS.23KV#4BUS_KV | 23KV #4BUS KV | BUS | [5 empty] | 354 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D12 | 仁愛DS | 22 | 22kV | JA5A | 愛5A線(JA5A) |  | KVAR |  | B2 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0230 |  |  | 2-E6 |  |  | F29 | KVAR | 愛5A線 JA5A 乏 | KVAR_-18000_18000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5A線KVAR | 23KV愛5A線 KVAR | FEEDER | [5 empty] | 355 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5A | 愛5A線(JA5A) |  | I_R |  | B2 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0231 |  |  | 2-E7 |  |  | F29 | A | 愛5A線 JA5A R 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5A線A1 | 23KV愛5A線 R相AMP | FEEDER | [5 empty] | 356 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5A | 愛5A線(JA5A) |  | I_S |  | B2 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0232 |  |  | 2-E8 |  |  | F29 | A | 愛5A線 JA5A S 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5A線A2 | 23KV愛5A線 S相AMP | FEEDER | [5 empty] | 357 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5A | 愛5A線(JA5A) |  | I_T |  | B2 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0233 |  |  | 2-E9 |  |  | F29 | A | 愛5A線 JA5A T 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5A線A3 | 23KV愛5A線 T相AMP | FEEDER | [5 empty] | 358 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5A | 愛5A線(JA5A) |  | I_N |  | B2 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0234 |  |  | 2-EA |  |  | F29 | A | 愛5A線 JA5A N相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5A線A0 | 23KV愛5A線 N相AMP | FEEDER | [5 empty] | 359 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5B | 愛5B線(JA5B) |  | KVAR |  | B2 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0235 |  |  | 2-EB |  |  | F30 | KVAR | 愛5B線 JA5B 乏 | KVAR_-18000_18000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5B線KVAR | 23KV愛5B線 KVAR | FEEDER | [5 empty] | 360 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5B | 愛5B線(JA5B) |  | I_R |  | B2 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0236 |  |  | 2-EC |  |  | F30 | A | 愛5B線 JA5B R 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5B線A1 | 23KV愛5B線 R相AMP | FEEDER | [5 empty] | 361 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5B | 愛5B線(JA5B) |  | I_S |  | B2 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0237 |  |  | 2-ED |  |  | F30 | A | 愛5B線 JA5B S 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5B線A2 | 23KV愛5B線 S相AMP | FEEDER | [5 empty] | 362 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5B | 愛5B線(JA5B) |  | I_T |  | B2 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0238 |  |  | 2-EE |  |  | F30 | A | 愛5B線 JA5B T 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5B線A3 | 23KV愛5B線 T相AMP | FEEDER | [5 empty] | 363 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5B | 愛5B線(JA5B) |  | I_N |  | B2 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0239 |  |  | 2-EF |  |  | F30 | A | 愛5B線 JA5B N相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5B線A0 | 23KV愛5B線 N相AMP | FEEDER | [5 empty] | 364 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5C | 愛5C線(JA5C) |  | KVAR |  | B2 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0240 |  |  | 2-F0 |  |  | F31 | KVAR | 愛5C線 JA5C 乏 | KVAR_-18000_18000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5C線KVAR | 23KV愛5C線 KVAR | FEEDER | [5 empty] | 365 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5C | 愛5C線(JA5C) |  | I_R |  | B2 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0241 |  |  | 2-F1 |  |  | F31 | A | 愛5C線 JA5C R 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5C線A1 | 23KV愛5C線 R相AMP | FEEDER | [5 empty] | 366 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5C | 愛5C線(JA5C) |  | I_S |  | B2 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0242 |  |  | 2-F2 |  |  | F31 | A | 愛5C線 JA5C S 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5C線A2 | 23KV愛5C線 S相AMP | FEEDER | [5 empty] | 367 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5C | 愛5C線(JA5C) |  | I_T |  | B2 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0243 |  |  | 2-F3 |  |  | F31 | A | 愛5C線 JA5C T 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5C線A3 | 23KV愛5C線 T相AMP | FEEDER | [5 empty] | 368 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5C | 愛5C線(JA5C) |  | I_N |  | B2 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0244 |  |  | 2-F4 |  |  | F31 | A | 愛5C線 JA5C N相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5C線A0 | 23KV愛5C線 N相AMP | FEEDER | [5 empty] | 369 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5D | 愛5D線(JA5D) |  | KVAR |  | B2 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0245 |  |  | 2-F5 |  |  | F32 | KVAR | 愛5D線 JA5D 乏 | KVAR_-18000_18000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5D線KVAR | 23KV愛5D線 KVAR | FEEDER | [5 empty] | 370 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5D | 愛5D線(JA5D) |  | I_R |  | B2 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0246 |  |  | 2-F6 |  |  | F32 | A | 愛5D線 JA5D R 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5D線A1 | 23KV愛5D線 R相AMP | FEEDER | [5 empty] | 371 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5D | 愛5D線(JA5D) |  | I_S |  | B2 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0247 |  |  | 2-F7 |  |  | F32 | A | 愛5D線 JA5D S 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5D線A2 | 23KV愛5D線 S相AMP | FEEDER | [5 empty] | 372 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5D | 愛5D線(JA5D) |  | I_T |  | B2 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0248 |  |  | 2-F8 |  |  | F32 | A | 愛5D線 JA5D T 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5D線A3 | 23KV愛5D線 T相AMP | FEEDER | [5 empty] | 373 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5D | 愛5D線(JA5D) |  | I_N |  | B2 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0249 |  |  | 2-F9 |  |  | F32 | A | 愛5D線 JA5D N相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5D線A0 | 23KV愛5D線 N相AMP | FEEDER | [5 empty] | 374 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5F | 愛5F線(JA5F) |  | KVAR |  | B2 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0250 |  |  | 2-FA |  |  | F33 | KVAR | 愛5F線 JA5F 乏 | KVAR_-18000_18000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5F線KVAR | 23KV愛5F線 KVAR | FEEDER | [5 empty] | 375 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5F | 愛5F線(JA5F) |  | I_R |  | B2 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0251 |  |  | 2-FB |  |  | F33 | A | 愛5F線 JA5F R 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5F線A1 | 23KV愛5F線 R相AMP | FEEDER | [5 empty] | 376 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5F | 愛5F線(JA5F) |  | I_S |  | B2 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0252 |  |  | 2-FC |  |  | F33 | A | 愛5F線 JA5F S 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5F線A2 | 23KV愛5F線 S相AMP | FEEDER | [5 empty] | 377 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5F | 愛5F線(JA5F) |  | I_T |  | B2 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0253 |  |  | 2-FD |  |  | F33 | A | 愛5F線 JA5F T 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5F線A3 | 23KV愛5F線 T相AMP | FEEDER | [5 empty] | 378 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5F | 愛5F線(JA5F) |  | I_N |  | B2 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0254 |  |  | 2-FE |  |  | F33 | A | 愛5F線 JA5F N相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5F線A0 | 23KV愛5F線 N相AMP | FEEDER | [5 empty] | 379 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 0 |  | RTU | RTU |  | ADCL5 |  |  | MvMoment | No5 AI參考點 10% |  | Y |  | AI | [6 empty] | 0256 |  |  | 3-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.4 AI Card) |  |  |  |  | B3/D12_A1 | [16 empty] | 380 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D12 | 仁愛DS | 0 |  | RTU | RTU |  | ADCH5 |  |  | MvMoment | No5 AI參考點 90% |  | Y |  | AI | [6 empty] | 0257 |  |  | 3-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.4 AI Card) |  |  |  |  | B3/D12_A1 | [16 empty] | 381 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D12 | 仁愛DS | 22 | 22kV | JA5G | 愛5G線(JA5G) |  | KVAR |  | B2 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0258 |  |  | 3-82 |  |  | F34 | KVAR | 愛5G線 JA5G 乏 | KVAR_-18000_18000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5G線KVAR | 23KV愛5G線 KVAR | FEEDER | [5 empty] | 382 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5G | 愛5G線(JA5G) |  | I_R |  | B2 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0259 |  |  | 3-83 |  |  | F34 | A | 愛5G線 JA5G R 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5G線A1 | 23KV愛5G線 R相AMP | FEEDER | [5 empty] | 383 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5G | 愛5G線(JA5G) |  | I_S |  | B2 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0260 |  |  | 3-84 |  |  | F34 | A | 愛5G線 JA5G S 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5G線A2 | 23KV愛5G線 S相AMP | FEEDER | [5 empty] | 384 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5G | 愛5G線(JA5G) |  | I_T |  | B2 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0261 |  |  | 3-85 |  |  | F34 | A | 愛5G線 JA5G T 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5G線A3 | 23KV愛5G線 T相AMP | FEEDER | [5 empty] | 385 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5G | 愛5G線(JA5G) |  | I_N |  | B2 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0262 |  |  | 3-86 |  |  | F34 | A | 愛5G線 JA5G N相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5G線A0 | 23KV愛5G線 N相AMP | FEEDER | [5 empty] | 386 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5H | 愛5H線(JA5H) |  | KVAR |  | B2 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0263 |  |  | 3-87 |  |  | F35 | KVAR | 愛5H線 JA5H 乏 | KVAR_-18000_18000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5H線KVAR | 23KV愛5H線 KVAR | FEEDER | [5 empty] | 387 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5H | 愛5H線(JA5H) |  | I_R |  | B2 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0264 |  |  | 3-88 |  |  | F35 | A | 愛5H線 JA5H R 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5H線A1 | 23KV愛5H線 R相AMP | FEEDER | [5 empty] | 388 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5H | 愛5H線(JA5H) |  | I_S |  | B2 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0265 |  |  | 3-89 |  |  | F35 | A | 愛5H線 JA5H S 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5H線A2 | 23KV愛5H線 S相AMP | FEEDER | [5 empty] | 389 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5H | 愛5H線(JA5H) |  | I_T |  | B2 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0266 |  |  | 3-8A |  |  | F35 | A | 愛5H線 JA5H T 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5H線A3 | 23KV愛5H線 T相AMP | FEEDER | [5 empty] | 390 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5H | 愛5H線(JA5H) |  | I_N |  | B2 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0267 |  |  | 3-8B |  |  | F35 | A | 愛5H線 JA5H N相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5H線A0 | 23KV愛5H線 N相AMP | FEEDER | [5 empty] | 391 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5K | 愛5K線(JA5K) |  | KVAR |  | B2 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0268 |  |  | 3-8C |  |  | F36 | KVAR | 愛5K線 JA5K 乏 | KVAR_-18000_18000(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5K線KVAR | 23KV愛5K線 KVAR | FEEDER | [5 empty] | 392 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5K | 愛5K線(JA5K) |  | I_R |  | B2 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0269 |  |  | 3-8D |  |  | F36 | A | 愛5K線 JA5K R 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5K線A1 | 23KV愛5K線 R相AMP | FEEDER | [5 empty] | 393 |  |  |  |  | AI | [5 empty] | C05R500R | 450 | 451 | 500 | 501 | 0 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5K | 愛5K線(JA5K) |  | I_S |  | B2 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0270 |  |  | 3-8E |  |  | F36 | A | 愛5K線 JA5K S 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5K線A2 | 23KV愛5K線 S相AMP | FEEDER | [5 empty] | 394 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5K | 愛5K線(JA5K) |  | I_T |  | B2 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0271 |  |  | 3-8F |  |  | F36 | A | 愛5K線 JA5K T 相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5K線A3 | 23KV愛5K線 T相AMP | FEEDER | [5 empty] | 395 |  |  |  |  | AI | [5 empty] | C05R0500 | 475 | 500 | 501 | 502 | 0 | -475 | -500 | -501 | -502 | 1 | 0.01 | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | JA5K | 愛5K線(JA5K) |  | I_N |  | B2 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0272 |  |  | 3-90 |  |  | F36 | A | 愛5K線 JA5K N相電流 | A_-500_500(-2000_2000) |  | B2/D12_D1 | [8 empty] | 仁愛DS.愛5K線A0 | 23KV愛5K線 N相AMP | FEEDER | [5 empty] | 396 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 400 | TIE-4(400) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0273 |  |  | 3-91 |  |  | TIE-4 | A | TIE-4 400 R 相電流 | A_-2000_2000(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.23KV_400_A1 | 23KV 400 R相AMP | TIE | [5 empty] | 397 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 400 | TIE-4(400) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0274 |  |  | 3-92 |  |  | TIE-4 | A | TIE-4 400 S 相電流 | A_-2000_2000(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.23KV_400_A2 | 23KV 400 S相AMP | TIE | [5 empty] | 398 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 400 | TIE-4(400) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0275 |  |  | 3-93 |  |  | TIE-4 | A | TIE-4 400 T 相電流 | A_-2000_2000(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.23KV_400_A3 | 23KV 400 T相AMP | TIE | [5 empty] | 399 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 0 |  | StaDev | 所內設施 |  | DCV_P |  |  | MvMoment | 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0276 |  |  | 3-94 |  |  | DCV | 65 | 直流P電源電壓 | kV_-150_150(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.直流P電源電壓 | 直流P電源電壓 | OTHER | [5 empty] | 400 |  |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 | 0.01 | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D12 | 仁愛DS | 0 |  | StaDev | 所內設施 |  | DCV_N |  |  | MvMoment | 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0277 |  |  | 3-95 |  |  | DCV | -65 | 直流N電源電壓 | kV_-150_150(-2000_2000) |  | B3/D12_A1 | [8 empty] | 仁愛DS.直流N電源電壓 | 直流N電源電壓 | OTHER | [5 empty] | 401 |  |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 | 0.01 | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D12 | 仁愛DS | 161 | 161kV | 1520 | 嘉義～仁愛海線(1520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P05D12O/T2 |  | 0000 |  | 0002 | 1-00-00 |  | 1-02 | 1520 | ON/OFF | 嘉義仁愛海線 1520 CB 52AS |  | aaca | B2/D12_A1 | [8 empty] | 仁愛DS.1520_CB | 1520(嘉義仁愛海線) CB | LINE161 | [5 empty] | 402 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1520 | 嘉義～仁愛海線(1520) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0001 |  |  | 1-00-01 |  |  | 1520 | 87A | 嘉義仁愛海線 1520 CB 87A |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1520_87A | 嘉義仁愛海線(1520) 87RY | LINE161 | [5 empty] | 403 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1520 | 嘉義～仁愛海線(1520) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0002 |  |  | 1-00-02 |  |  | 1520 | PHA | 嘉義仁愛海線 1520 CB PHA |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1520_PHA | 嘉義仁愛海線(1520) 相間RY | LINE161 | [5 empty] | 404 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1520 | 嘉義～仁愛海線(1520) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | 1520 | GDA | 嘉義仁愛海線 1520 CB GDA |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1520_GDA | 嘉義仁愛海線(1520) 接地RY | LINE161 | [5 empty] | 405 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1510 | 嘉義～仁愛山線(1510) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P05D12M/T2 |  | 0004 |  | 0003 | 1-00-04 |  | 1-03 | 1510 | ON/OFF | 嘉義仁愛山線 1510 CB 52AS |  | aada | B2/D12_A1 | [8 empty] | 仁愛DS.1510_CB | 1510(嘉義仁愛山線) CB | LINE161 | [5 empty] | 406 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1510 | 嘉義～仁愛山線(1510) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0005 |  |  | 1-00-05 |  |  | 1510 | 87A | 嘉義仁愛山線 1510 CB 87A |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1510_87A | 嘉義仁愛山線(1510) 87RY | LINE161 | [5 empty] | 407 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1510 | 嘉義～仁愛山線(1510) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | 1510 | PHA | 嘉義仁愛山線 1510 CB PHA |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1510_PHA | 嘉義仁愛山線(1510) 相間RY | LINE161 | [5 empty] | 408 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1510 | 嘉義～仁愛山線(1510) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-07 |  |  | 1510 | GDA | 嘉義仁愛山線 1510 CB GDA |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1510_GDA | 嘉義仁愛山線(1510) 接地RY | LINE161 | [5 empty] | 409 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1540 | 仁愛～北回二路(1540) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D12D142/T1 |  | 0008 |  | 0004 | 1-01-00 |  | 1-04 | 1540 | ON/OFF | 仁愛北回二路 (1540) CB 52AS |  | aaha | B2/D12_A1 | [8 empty] | 仁愛DS.1540_CB | 1540(仁愛北回二路) CB | LINE161 | [5 empty] | 410 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1540 | 仁愛～北回二路(1540) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | 1540 | 87A | 仁愛北回二路 (1540) CB 87A |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1540_87A | 仁愛北回二路(1540) 87RY | LINE161 | [5 empty] | 411 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1540 | 仁愛～北回二路(1540) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0010 |  |  | 1-01-02 |  |  | 1540 | PHA | 仁愛北回二路 (1540) CB PHA |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1540_PHA | 仁愛北回二路(1540) 相間RY | LINE161 | [5 empty] | 412 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1540 | 仁愛～北回二路(1540) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-03 |  |  | 1540 | GDA | 仁愛北回二路 (1540) CB GDA |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1540_GDA | 仁愛北回二路(1540) 接地RY | LINE161 | [5 empty] | 413 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1530 | 仁愛～北回一路(1530) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D12D141/T1 |  | 0012 |  | 0005 | 1-01-04 |  | 1-05 | 1530 | ON/OFF | 仁愛北回一路 (1530) CB 52AS |  | aaia | B2/D12_A1 | [8 empty] | 仁愛DS.1530_CB | 1530(仁愛北回一路) CB | LINE161 | [5 empty] | 414 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1530 | 仁愛～北回一路(1530) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0013 |  |  | 1-01-05 |  |  | 1530 | 87A | 仁愛北回一路 (1530) CB 87A |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1530_87A | 仁愛北回一路(1530) 87RY | LINE161 | [5 empty] | 415 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1530 | 仁愛～北回一路(1530) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-06 |  |  | 1530 | PHA | 仁愛北回一路 (1530) CB PHA |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1530_PHA | 仁愛北回一路(1530) 相間RY | LINE161 | [5 empty] | 416 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1530 | 仁愛～北回一路(1530) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0015 |  |  | 1-01-07 |  |  | 1530 | GDA | 仁愛北回一路 (1530) CB GDA |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1530_GDA | 仁愛北回一路(1530) 接地RY | LINE161 | [5 empty] | 417 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0040 |  | 0012 | 1-05-00 |  | 1-0C | 161KV TIE | ON/OFF | TIE(1500)CB 52AS |  | aafz | B2/D12_A1 | [8 empty] | 仁愛DS.1500_CB | 1500(TIE) CB | TIE | [5 empty] | 418 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0041 |  |  | 1-05-01 |  |  | 161KV TIE | A/N | TIE(1500)RY 50A |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1500_50A | 161KV TIE(1500) 50RY | TIE | [5 empty] | 419 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0042 |  |  | 1-05-02 |  |  | NO.1 BUS | A/N | 161KV NO.1 BUS 87B1A |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | [5 empty] | 420 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0043 |  |  | 1-05-03 |  |  | NO.2 BUS | A/N | 161KV NO.2 BUS 87B2A |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | [5 empty] | 421 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0044 |  |  | 1-05-04 |  |  | Locate Empty | A/N | 161KV 79 RY RCA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | [5 empty] | 422 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0045 |  |  | 1-05-05 |  |  | OSCA | A/N | 161KV示波器啟動警報OSC1A |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.161KV_OSCA_1 | 161KV示波器啟動警報(1) | OTHER | [5 empty] | 423 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0046 |  |  | 1-05-06 |  |  | OSC | A/N | 161KV NO.2 O.S.C. OSC2A |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.161KV_OSCA_2 | 161KV示波器啟動警報(2) | OTHER | [5 empty] | 424 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/1DTR |  | 0048 |  | 0013 | 1-06-00 |  | 1-0D | #1DTR | ON/OFF | NO.1 1750 CB 52AS |  | aabb | ELEM/D12_A1 | [8 empty] | 仁愛DS.1750_CB | 1750(#1DTR) CB | MTR | [5 empty] | 425 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS |  |  | 1DTR | #1DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0049 |  |  | 1-06-01 |  |  | #1DTR | A/N | NO.1 DTR 87A 87A |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#1DTR_87A | #1DTR 87RY | MTR | [5 empty] | 426 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 1DTR | #1DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0050 |  |  | 1-06-02 |  |  | #1DTR | A/N | NO.1 DTR 機械保護動作(96PA) |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | [5 empty] | 427 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 1DTR | #1DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0051 |  |  | 1-06-03 |  |  | #1DTR | A/N | NO.1 DTR 51ZA 51ZA |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | [5 empty] | 428 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 1DTR | #1DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | #1DTR | PHA | NO.1 DTR PHA PHA |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#1DTR_51A | #1DTR 51RY | MTR | [5 empty] | 429 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 1DTR | #1DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0053 |  |  | 1-06-05 |  |  | #1DTR | GDA | NO.1 DTR GDA GDA |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#1DTR_51NA | #1DTR 51N RY | MTR | [5 empty] | 430 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0054 |  |  | 1-06-06 |  |  | 1 DTR-1A | PHA | 1 DTR-1A 310 (51-3φ)PHA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.310_51A | #1DTR二次側(310) 51RY | MTR | [5 empty] | 431 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0055 |  |  | 1-06-07 |  |  | 1 DTR-1B | PHA | 1 DTR-1B 320 (51-3φ)PHA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.320_51A | #1DTR二次側(320) 51RY | MTR | [5 empty] | 432 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | T/1DTR(A) |  |  | 0056 |  | 0017 | 1-07-00 |  | 1-11 | 1 DTR-1A | ON/OFF | 1 DTR-1A 310 CB 52AS |  | aaba | ELEM/D12_A1 | [8 empty] | 仁愛DS.310_CB | 310(#1DTR) CB | MTR | [5 empty] | 433 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0057 |  |  | 1-07-01 |  |  | 1 DTR-1A | PHA | 1 DTR-1A 310 PHA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.310_PHA2 | 310開關箱IED RY PHA | OTHER | [5 empty] | 434 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0058 |  |  | 1-07-02 |  |  | 1 DTR-1A | GDA | 1 DTR-1A 310 G1 DTR-A |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.310_GDA | 310開關箱IED RY GDA | OTHER | [5 empty] | 435 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | T/1DTR(B) |  |  | 0059 |  | 0026 | 1-07-03 |  | 1-1A | 1 DTR-1B | ON/OFF | 1 DTR-1B 320 CB 52AS |  | baca | ELEM/D12_A1 | [8 empty] | 仁愛DS.320_CB | 320(#1DTR) CB | MTR | [5 empty] | 436 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0060 |  |  | 1-07-04 |  |  | 1 DTR-1B | PHA | 1 DTR-1B 320 PHA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.320_PHA2 | 320開關箱IED RY PHA | OTHER | [5 empty] | 437 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0061 |  |  | 1-07-05 |  |  | 1 DTR-1B | GDA | 1 DTR-1B 320 G1 DTR-A |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.320_GDA | 320開關箱IED RY GDA | OTHER | [5 empty] | 438 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2DTR |  | 0062 |  | 0014 | 1-07-06 |  | 1-0E | #2DTR | ON/OFF | NO.2 1760 CB 52AS |  | aaeb | ELEM/D12_A1 | [8 empty] | 仁愛DS.1760_CB | 1760(#2DTR) CB | MTR | [5 empty] | 439 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS |  |  | 2DTR | #2DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0063 |  |  | 1-07-07 |  |  | #2DTR | A/N | NO.2 DTR 87A 87A |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#2DTR_87A | #2DTR 87RY | MTR | [5 empty] | 440 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 2DTR | #2DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0064 |  |  | 1-08-00 |  |  | #2DTR | A/N | NO.2 DTR 機械保護動作(96PA) |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | [5 empty] | 441 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 2DTR | #2DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0065 |  |  | 1-08-01 |  |  | #2DTR | A/N | NO.2 DTR 51ZA 51ZA |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | [5 empty] | 442 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 2DTR | #2DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0066 |  |  | 1-08-02 |  |  | #2DTR | PHA | NO.2 DTR PHA PHA |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#2DTR_51A | #2DTR 51RY | MTR | [5 empty] | 443 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 2DTR | #2DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0067 |  |  | 1-08-03 |  |  | #2DTR | GDA | NO.2 DTR GDA GDA |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#2DTR_51NA | #2DTR 51N RY | MTR | [5 empty] | 444 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 |  |  | 1-08-04 |  |  | 2 DTR-2A | PHA | 2 DTR-2A 330 (51-3φ)PHA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.330_51A | #2DTR二次側(330) 51RY | MTR | [5 empty] | 445 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 |  |  | 1-08-05 |  |  | 2 DTR-2B | PHA | 2 DTR-2B 340 (51-3φ)PHA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.340_51A | #2DTR二次側(340) 51RY | MTR | [5 empty] | 446 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | T/2DTR(A) |  |  | 0070 |  | 0054 | 1-08-06 |  | 1-36 | 2 DTR-2A | ON/OFF | 2 DTR-2A 330 CB 52AS |  | abba | ELEM/D12_A1 | [8 empty] | 仁愛DS.330_CB | 330(#2DTR) CB | MTR | [5 empty] | 447 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0071 |  |  | 1-08-07 |  |  | 2 DTR-2A | PHA | 2 DTR-2A 330 PHA PHA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.330_PHA2 | 330開關箱IED RY PHA | OTHER | [5 empty] | 448 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0072 |  |  | 1-09-00 |  |  | 2 DTR-2A | GDA | 2 DTR-2A 330 G2 DTR-A |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.330_GDA | 330開關箱IED RY GDA | OTHER | [5 empty] | 449 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | T/2DTR(B) |  |  | 0073 |  | 0055 | 1-09-01 |  | 1-37 | 2 DTR-2B | ON/OFF | 2 DTR-2B 340 CB 52AS |  | bbca | ELEM/D12_A1 | [8 empty] | 仁愛DS.340_CB | 340(#2DTR) CB | MTR | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-09-02 |  |  | 2 DTR-2B | PHA | 2 DTR-2B 340 PHA PHA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.340_PHA2 | 340開關箱IED RY PHA | OTHER | [5 empty] | 451 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0075 |  |  | 1-09-03 |  |  | 2 DTR-2B | GDA | 2 DTR-2B 340 G2 DTR-A |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.340_GDA | 340開關箱IED RY GDA | OTHER | [5 empty] | 452 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/3DTR |  | 0076 |  | 0015 | 1-09-04 |  | 1-0F | #3DTR | ON/OFF | NO.3 1770 CB 52AS |  | aagb | ELEM/D12_A1 | [8 empty] | 仁愛DS.1770_CB | 1770(#3DTR) CB | MTR | [5 empty] | 453 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS |  |  | 3DTR | #3DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0077 |  |  | 1-09-05 |  |  | #3DTR | A/N | NO.3 DTR 87A 87A |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#3DTR_87A | #3DTR 87RY | MTR | [5 empty] | 454 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 3DTR | #3DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0078 |  |  | 1-09-06 |  |  | #3DTR | A/N | NO.3 DTR 機械保護動作(96PA) |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#3DTR_96PA | #3DTR 機械保護動作 | MTR | [5 empty] | 455 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 3DTR | #3DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0079 |  |  | 1-09-07 |  |  | #3DTR | A/N | NO.3 DTR 51ZA 51ZA |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#3DTR_51ZA | #3DTR 51Z RY | MTR | [5 empty] | 456 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 3DTR | #3DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0080 |  |  | 1-0A-00 |  |  | #3DTR | PHA | NO.3 DTR PHA PHA |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#3DTR_51A | #3DTR 51RY | MTR | [5 empty] | 457 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 3DTR | #3DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0081 |  |  | 1-0A-01 |  |  | #3DTR | GDA | NO.3 DTR GDA GDA |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#3DTR_51NA | #3DTR 51N RY | MTR | [5 empty] | 458 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | 350 | #3DTR(350) |  | 51A |  | B2 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0082 |  |  | 1-0A-02 |  |  | 3 DTR | PHA | 3 DTR 350 (51-3φ)PHA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.350_51A | #3DTR二次側(350) 51RY | MTR | [5 empty] | 459 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | 350 | #3DTR(350) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3Bus | T/3DTR |  |  | 0083 |  | 0056 | 1-0A-03 |  | 1-38 | 3 DTR | ON/OFF | 3 DTR 350 CB 52AS |  | acaa | ELEM/D12_A1 | [8 empty] | 仁愛DS.350_CB | 350(#3DTR) CB | MTR | [5 empty] | 460 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | 350 | #3DTR(350) |  | PHA |  | B2 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0084 |  |  | 1-0A-04 |  |  | 3 DTR | PHA | 3 DTR 350 PHA PHA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.350_PHA2 | 350開關箱IED RY PHA | OTHER | [5 empty] | 461 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | 350 | #3DTR(350) |  | GDA |  | B2 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0085 |  |  | 1-0A-05 |  |  | 3 DTR | GDA | 3 DTR 350 GDA GDA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.350_GDA | 350開關箱IED RY GDA | OTHER | [5 empty] | 462 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1780 | #4DTR(1780) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/4DTR |  | 0086 |  | 0016 | 1-0A-06 |  | 1-10 | #4DTR | ON/OFF | NO.4 1780 CB 52AS |  | aajb | ELEM/D12_A1 | [8 empty] | 仁愛DS.1780_CB | 1780(#4DTR) CB | MTR | [5 empty] | 463 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS |  |  | 4DTR | #4DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0087 |  |  | 1-0A-07 |  |  | #4DTR | A/N | NO.4 DTR 87A 87A |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#4DTR_87A | #4DTR 87RY | MTR | [5 empty] | 464 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 4DTR | #4DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0088 |  |  | 1-0B-00 |  |  | #4DTR | A/N | NO.4 DTR 機械保護動作(96PA) |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#4DTR_96PA | #4DTR 機械保護動作 | MTR | [5 empty] | 465 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 4DTR | #4DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0089 |  |  | 1-0B-01 |  |  | #4DTR | A/N | NO.4 DTR 51ZA 51ZA |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#4DTR_51ZA | #4DTR 51Z RY | MTR | [5 empty] | 466 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 4DTR | #4DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0090 |  |  | 1-0B-02 |  |  | #4DTR | PHA | NO.4 DTR PHA PHA |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#4DTR_51A | #4DTR 51RY | MTR | [5 empty] | 467 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 4DTR | #4DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0091 |  |  | 1-0B-03 |  |  | #4DTR | GDA | NO.4 DTR GDA GDA |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#4DTR_51NA | #4DTR 51N RY | MTR | [5 empty] | 468 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | 370 | #4DTR(370) |  | 51A |  | B2 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0092 |  |  | 1-0B-04 |  |  | 4 DTR | PHA | 4 DTR 370 (51-3φ)PHA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.370_51A | #4DTR二次側(370) 51RY | MTR | [5 empty] | 469 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | 370 | #4DTR(370) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4Bus | T/4DTR |  |  | 0093 |  | 0057 | 1-0B-05 |  | 1-39 | 4 DTR | ON/OFF | 4 DTR 370 CB 52AS |  | adba | ELEM/D12_A1 | [8 empty] | 仁愛DS.370_CB | 370(#4DTR) CB | MTR | [5 empty] | 470 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | 370 | #4DTR(370) |  | PHA |  | B2 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0094 |  |  | 1-0B-06 |  |  | 4 DTR | PHA | 4 DTR 370 PHA PHA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.370_PHA2 | 370開關箱IED RY PHA | OTHER | [5 empty] | 471 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | 370 | #4DTR(370) |  | GDA |  | B2 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0095 |  |  | 1-0B-07 |  |  | 4 DTR | GDA | 4 DTR 370 GDA GDA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.370_GDA | 370開關箱IED RY GDA | OTHER | [5 empty] | 472 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | RTU | RTU |  | RTU_MCT |  |  | Status | RTU Master Ry | Open/Close | Y | E | DI-SP | [6 empty] | 0096 |  |  | 1-0C-00 |  |  | 161RTU | MCT_ SOE | RTU Master Ry SOE |  |  | B3/D12_A1 | [16 empty] | 473 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D12 | 仁愛DS | 0 |  | RTU | RTU |  | RTUA |  |  | Status | RTU故障警報 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0097 |  |  | 1-0C-01 |  |  | RTU | RTUA | RTU發生異常 |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.RTUA | RTU發生異常 | OTHER | [5 empty] | 474 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA21 | 愛21線(JA21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/JA21/T1 |  |  | 0128 |  | 0019 | 1-10-00 |  | 1-13 | F1 | ON/OFF | 愛21線 JA21 CB 52AS |  | aadb | B2/D12_D1 | [8 empty] | 仁愛DS.JA21_CB | JA21(11KV愛21線) CB | FEEDER | [5 empty] | 475 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA21 | 愛21線(JA21) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0129 |  |  | 1-10-01 |  |  | F1 | PHA | 愛21線 JA21 RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA21_PHA | 11KV愛21線(JA21) 相間RY | FEEDER | [5 empty] | 476 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA21 | 愛21線(JA21) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-10-02 |  |  | F1 | GDA | 愛21線 JA21 RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA21_GDA | 11KV愛21線(JA21) 接地RY | FEEDER | [5 empty] | 477 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA22 | 愛22線(JA22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/JA22/T1 |  |  | 0131 |  | 0020 | 1-10-03 |  | 1-14 | F2 | ON/OFF | 愛22線 JA22 CB 52AS |  | aaeb | B2/D12_D1 | [8 empty] | 仁愛DS.JA22_CB | JA22(11KV愛22線) CB | FEEDER | [5 empty] | 478 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA22 | 愛22線(JA22) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0132 |  |  | 1-10-04 |  |  | F2 | PHA | 愛22線 JA22 RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA22_PHA | 11KV愛22線(JA22) 相間RY | FEEDER | [5 empty] | 479 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA22 | 愛22線(JA22) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0133 |  |  | 1-10-05 |  |  | F2 | GDA | 愛22線 JA22 RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA22_GDA | 11KV愛22線(JA22) 接地RY | FEEDER | [5 empty] | 480 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA23 | 愛23線(JA23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/JA23/T1 |  |  | 0134 |  | 0021 | 1-10-06 |  | 1-15 | F3 | ON/OFF | 愛23線 JA23 CB 52AS |  | aafb | B2/D12_D1 | [8 empty] | 仁愛DS.JA23_CB | JA23(11KV愛23線) CB | FEEDER | [5 empty] | 481 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA23 | 愛23線(JA23) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0135 |  |  | 1-10-07 |  |  | F3 | PHA | 愛23線 JA23 RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA23_PHA | 11KV愛23線(JA23) 相間RY | FEEDER | [5 empty] | 482 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA23 | 愛23線(JA23) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0136 |  |  | 1-11-00 |  |  | F3 | GDA | 愛23線 JA23 RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA23_GDA | 11KV愛23線(JA23) 接地RY | FEEDER | [5 empty] | 483 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA24 | 愛24線(JA24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/JA24/T1 |  |  | 0137 |  | 0022 | 1-11-01 |  | 1-16 | F4 | ON/OFF | 愛24線 JA24 CB 52AS |  | aagb | B2/D12_D1 | [8 empty] | 仁愛DS.JA24_CB | JA24(11KV愛24線) CB | FEEDER | [5 empty] | 484 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA24 | 愛24線(JA24) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0138 |  |  | 1-11-02 |  |  | F4 | PHA | 愛24線 JA24 RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA24_PHA | 11KV愛24線(JA24) 相間RY | FEEDER | [5 empty] | 485 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA24 | 愛24線(JA24) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0139 |  |  | 1-11-03 |  |  | F4 | GDA | 愛24線 JA24 RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA24_GDA | 11KV愛24線(JA24) 接地RY | FEEDER | [5 empty] | 486 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA25 | 愛25線(JA25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/JA25/T1 |  |  | 0140 |  | 0023 | 1-11-04 |  | 1-17 | F5 | ON/OFF | 愛25線 JA25 CB 52AS |  | aahb | B2/D12_D1 | [8 empty] | 仁愛DS.JA25_CB | JA25(11KV愛25線) CB | FEEDER | [5 empty] | 487 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA25 | 愛25線(JA25) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0141 |  |  | 1-11-05 |  |  | F5 | PHA | 愛25線 JA25 RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA25_PHA | 11KV愛25線(JA25) 相間RY | FEEDER | [5 empty] | 488 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA25 | 愛25線(JA25) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0142 |  |  | 1-11-06 |  |  | F5 | GDA | 愛25線 JA25 RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA25_GDA | 11KV愛25線(JA25) 接地RY | FEEDER | [5 empty] | 489 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 210 | #1SC(210) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | C/1SC |  |  | 0143 |  | 0018 | 1-11-07 |  | 1-12 | #1ASC | ON/OFF | #1SC 210 CB 52AS |  | aacb | B3/D12_A1 | [8 empty] | 仁愛DS.210_CB | 210(11KV #1SC) CB | SC | [5 empty] | 490 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0144 |  |  | 1-12-00 |  |  | #1ASC | SCA | #1SC 210 CB RY SCA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.210_SCA | 11KV #1SC 51,51N RY | SC | [5 empty] | 491 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0145 |  |  | 1-12-01 |  |  | #1ASC | UVA | #1SC 210 CB RY UVA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | [5 empty] | 492 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 100 | TIE-1(100) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/1ABus | B/2ABus |  |  | 0146 |  | 0024 | 1-12-02 |  | 1-18 | TIE-1 | ON/OFF | TIE-1 100 CB 52AS |  | aaib | B3/D12_A1 | [8 empty] | 仁愛DS.100_CB | 100(TIE) CB | TIE | [5 empty] | 493 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | 100 | TIE-1(100) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0147 |  |  | 1-12-03 |  |  | TIE-1 | PHA | TIE-1 100 RY PHA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.100_51A | 11KV TIE(100) 51RY | TIE | [5 empty] | 494 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 100 | TIE-1(100) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0148 |  |  | 1-12-04 |  |  | TIE-1 | GDA | TIE-1 100 RY GDA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.100_51NA | 11KV TIE(100) 51N RY | TIE | [5 empty] | 495 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA26 | 愛26線(JA26) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/JA26/T1 |  |  | 0149 |  | 0028 | 1-12-05 |  | 1-1C | F6 | ON/OFF | 愛26線 JA26 CB 52AS |  | baeb | B2/D12_D1 | [8 empty] | 仁愛DS.JA26_CB | JA26(11KV愛26線) CB | FEEDER | [5 empty] | 496 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA26 | 愛26線(JA26) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0150 |  |  | 1-12-06 |  |  | F6 | PHA | 愛26線 JA26 RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA26_PHA | 11KV愛26線(JA26) 相間RY | FEEDER | [5 empty] | 497 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA26 | 愛26線(JA26) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0151 |  |  | 1-12-07 |  |  | F6 | GDA | 愛26線 JA26 RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA26_GDA | 11KV愛26線(JA26) 接地RY | FEEDER | [5 empty] | 498 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA27 | 愛27線(JA27) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/JA27/T1 |  |  | 0152 |  | 0029 | 1-13-00 |  | 1-1D | F7 | ON/OFF | 愛27線 JA27 CB 52AS |  | bafb | B2/D12_D1 | [8 empty] | 仁愛DS.JA27_CB | JA27(11KV愛27線) CB | FEEDER | [5 empty] | 499 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA27 | 愛27線(JA27) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0153 |  |  | 1-13-01 |  |  | F7 | PHA | 愛27線 JA27 RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA27_PHA | 11KV愛27線(JA27) 相間RY | FEEDER | [5 empty] | 500 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA27 | 愛27線(JA27) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0154 |  |  | 1-13-02 |  |  | F7 | GDA | 愛27線 JA27 RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA27_GDA | 11KV愛27線(JA27) 接地RY | FEEDER | [5 empty] | 501 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA28 | 愛28線(JA28) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/JA28/T1 |  |  | 0155 |  | 0030 | 1-13-03 |  | 1-1E | F8 | ON/OFF | 愛28線 JA28 CB 52AS |  | bagb | B2/D12_D1 | [8 empty] | 仁愛DS.JA28_CB | JA28(11KV愛28線) CB | FEEDER | [5 empty] | 502 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA28 | 愛28線(JA28) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0156 |  |  | 1-13-04 |  |  | F8 | PHA | 愛28線 JA28 RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA28_PHA | 11KV愛28線(JA28) 相間RY | FEEDER | [5 empty] | 503 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA28 | 愛28線(JA28) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0157 |  |  | 1-13-05 |  |  | F8 | GDA | 愛28線 JA28 RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA28_GDA | 11KV愛28線(JA28) 接地RY | FEEDER | [5 empty] | 504 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA29 | 愛29線(JA29) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/JA29/T1 |  |  | 0158 |  | 0031 | 1-13-06 |  | 1-1F | F9 | ON/OFF | 愛29線 JA29 CB 52AS |  | bahb | B2/D12_D1 | [8 empty] | 仁愛DS.JA29_CB | JA29(11KV愛29線) CB | FEEDER | [5 empty] | 505 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA29 | 愛29線(JA29) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0159 |  |  | 1-13-07 |  |  | F9 | PHA | 愛29線 JA29 RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA29_PHA | 11KV愛29線(JA29) 相間RY | FEEDER | [5 empty] | 506 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA29 | 愛29線(JA29) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0160 |  |  | 1-14-00 |  |  | F9 | GDA | 愛29線 JA29 RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA29_GDA | 11KV愛29線(JA29) 接地RY | FEEDER | [5 empty] | 507 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA30 | 愛30線(JA30) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/JA30/T1 |  |  | 0161 |  | 0032 | 1-14-01 |  | 1-20 | F10 | ON/OFF | 愛30線 JA30 CB 52AS |  | baib | B2/D12_D1 | [8 empty] | 仁愛DS.JA30_CB | JA30(11KV愛30線) CB | FEEDER | [5 empty] | 508 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA30 | 愛30線(JA30) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0162 |  |  | 1-14-02 |  |  | F10 | PHA | 愛30線 JA30 RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA30_PHA | 11KV愛30線(JA30) 相間RY | FEEDER | [5 empty] | 509 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA30 | 愛30線(JA30) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0163 |  |  | 1-14-03 |  |  | F10 | GDA | 愛30線 JA30 RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA30_GDA | 11KV愛30線(JA30) 接地RY | FEEDER | [5 empty] | 510 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 220 | #2SC(220) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | C/2SC |  |  | 0164 |  | 0027 | 1-14-04 |  | 1-1B | #1BSC | ON/OFF | #2SC 220 CB 52AS |  | badb | B3/D12_A1 | [8 empty] | 仁愛DS.220_CB | 220(11KV #2SC) CB | SC | [5 empty] | 511 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0165 |  |  | 1-14-05 |  |  | #1BSC | SCA | #2SC 220 CB RY SCA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.220_SCA | 11KV #2SC 51,51N RY | SC | [5 empty] | 512 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0166 |  |  | 1-14-06 |  |  | #1BSC | UVA | #2SC 220 CB RY UVA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | [5 empty] | 513 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 390 | #1SSTR(390) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | T/1SSTR |  |  | 0167 |  | 0025 | 1-14-07 |  | 1-19 | #1SSTR | ON/OFF | SSTR-1 390 CB 52AS |  | baab | B3/D12_A1 | [8 empty] | 仁愛DS.390_CB | 390(#1SSTR) CB | OTHER | [5 empty] | 514 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | 390 | #1SSTR(390) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0168 |  |  | 1-15-00 |  |  | #1SSTR | PHA | SSTR-1 390 RY PHA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.#1SSTR_51A | #1SSTR 51RY | OTHER | [5 empty] | 515 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 390 | #1SSTR(390) |  | GDA |  | B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0169 |  |  | 1-15-01 |  |  | #1SSTR | GDA | SSTR-1 390 RY GDA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | [5 empty] | 516 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | ComPoint |  |  | 25PFA |  |  | Status | 同步校核電驛電源 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0170 |  |  | 1-15-02 |  |  | 25RY | A/N | 同步校核裝置電源 25PFA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER | [5 empty] | 517 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | ComPoint |  |  | 25TA |  |  | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0171 |  |  | 1-15-03 |  |  | 25RY | A/N | 同步校核裝置超時 25TA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | [5 empty] | 518 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0172 |  |  | 1-15-04 |  |  | 310 | 81A | 310 81A |  |  | ELEM/D12_A1 | [8 empty] | 仁愛DS.81RY_A/S(1) | 310 81RY A/S | OTHER | [5 empty] | 519 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
D12 | 仁愛DS | 11 | 11kV | JA31 | 愛31線(JA31) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/JA31/T1 |  |  | 0256 |  | 0135 | 2-00-00 |  | 2-07 | F11 | ON/OFF | 愛31線 JA31 CB 52AS |  | abdb | B2/D12_D1 | [8 empty] | 仁愛DS.JA31_CB | JA31(11KV愛31線) CB | FEEDER | [5 empty] | 520 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA31 | 愛31線(JA31) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0257 |  |  | 2-00-01 |  |  | F11 | PHA | 愛31線 JA31 RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA31_PHA | 11KV愛31線(JA31) 相間RY | FEEDER | [5 empty] | 521 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA31 | 愛31線(JA31) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0258 |  |  | 2-00-02 |  |  | F11 | GDA | 愛31線 JA31 RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA31_GDA | 11KV愛31線(JA31) 接地RY | FEEDER | [5 empty] | 522 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA32 | 愛32線(JA32) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/JA32/T1 |  |  | 0259 |  | 0136 | 2-00-03 |  | 2-08 | F12 | ON/OFF | 愛32線 JA32 CB 52AS |  | abeb | B2/D12_D1 | [8 empty] | 仁愛DS.JA32_CB | JA32(11KV愛32線) CB | FEEDER | [5 empty] | 523 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA32 | 愛32線(JA32) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0260 |  |  | 2-00-04 |  |  | F12 | PHA | 愛32線 JA32 RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA32_PHA | 11KV愛32線(JA32) 相間RY | FEEDER | [5 empty] | 524 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA32 | 愛32線(JA32) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0261 |  |  | 2-00-05 |  |  | F12 | GDA | 愛32線 JA32 RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA32_GDA | 11KV愛32線(JA32) 接地RY | FEEDER | [5 empty] | 525 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA33 | 愛33線(JA33) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/JA33/T1 |  |  | 0262 |  | 0137 | 2-00-06 |  | 2-09 | F13 | ON/OFF | 愛33線 JA33 CB 52AS |  | abfb | B2/D12_D1 | [8 empty] | 仁愛DS.JA33_CB | JA33(11KV愛33線) CB | FEEDER | [5 empty] | 526 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA33 | 愛33線(JA33) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0263 |  |  | 2-00-07 |  |  | F13 | PHA | 愛33線 JA33 RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA33_PHA | 11KV愛33線(JA33) 相間RY | FEEDER | [5 empty] | 527 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA33 | 愛33線(JA33) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0264 |  |  | 2-01-00 |  |  | F13 | GDA | 愛33線 JA33 RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA33_GDA | 11KV愛33線(JA33) 接地RY | FEEDER | [5 empty] | 528 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA34 | 愛34線(JA34) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/JA34/T1 |  |  | 0265 |  | 0138 | 2-01-01 |  | 2-0A | F14 | ON/OFF | 愛34線 JA34 CB 52AS |  | abgb | B2/D12_D1 | [8 empty] | 仁愛DS.JA34_CB | JA34(11KV愛34線) CB | FEEDER | [5 empty] | 529 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA34 | 愛34線(JA34) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0266 |  |  | 2-01-02 |  |  | F14 | PHA | 愛34線 JA34 RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA34_PHA | 11KV愛34線(JA34) 相間RY | FEEDER | [5 empty] | 530 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA34 | 愛34線(JA34) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0267 |  |  | 2-01-03 |  |  | F14 | GDA | 愛34線 JA34 RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA34_GDA | 11KV愛34線(JA34) 接地RY | FEEDER | [5 empty] | 531 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA35 | 愛35線(JA35) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/JA35/T1 |  |  | 0268 |  | 0139 | 2-01-04 |  | 2-0B | F15 | ON/OFF | 愛35線 JA35 CB 52AS |  | abhb | B2/D12_D1 | [8 empty] | 仁愛DS.JA35_CB | JA35(11KV愛35線) CB | FEEDER | [5 empty] | 532 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA35 | 愛35線(JA35) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0269 |  |  | 2-01-05 |  |  | F15 | PHA | 愛35線 JA35 RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA35_PHA | 11KV愛35線(JA35) 相間RY | FEEDER | [5 empty] | 533 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA35 | 愛35線(JA35) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0270 |  |  | 2-01-06 |  |  | F15 | GDA | 愛35線 JA35 RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA35_GDA | 11KV愛35線(JA35) 接地RY | FEEDER | [5 empty] | 534 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 230 | #3SC(230) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | C/3SC |  |  | 0271 |  | 0134 | 2-01-07 |  | 2-06 | #2ASC | ON/OFF | #3SC 230 CB 52AS |  | abcb | B3/D12_A1 | [8 empty] | 仁愛DS.230_CB | 230(11KV #3SC) CB | SC | [5 empty] | 535 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | 230 | #3SC(230) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0272 |  |  | 2-02-00 |  |  | #2ASC | SCA | #3SC 230 RY SCA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.230_SCA | 11KV #3SC 51,51N RY | SC | [5 empty] | 536 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 230 | #3SC(230) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0273 |  |  | 2-02-01 |  |  | #2ASC | UVA | #3SC 230 RY UVA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | [5 empty] | 537 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 490 | #2SSTR(490) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | T/2SSTR |  |  | 0274 |  | 0140 | 2-02-02 |  | 2-0C | #2SSTR | ON/OFF | SSTR-2 490 CB 52AS |  | abib | B3/D12_A1 | [8 empty] | 仁愛DS.490_CB | 490(#2SSTR) CB | OTHER | [5 empty] | 538 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | 490 | #2SSTR(490) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0275 |  |  | 2-02-03 |  |  | #2SSTR | PHA | SSTR-2 490 RY PHA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.#2SSTR_51A | #2SSTR 51RY | OTHER | [5 empty] | 539 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 490 | #2SSTR(490) |  | GDA |  | B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0276 |  |  | 2-02-04 |  |  | #2SSTR | GDA | SSTR-2 490 RY GDA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | [5 empty] | 540 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA36 | 愛36線(JA36) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/JA36/T1 |  |  | 0277 |  | 0143 | 2-02-05 |  | 2-0F | F16 | ON/OFF | 愛36線 JA36 CB 52AS |  | bbeb | B2/D12_D1 | [8 empty] | 仁愛DS.JA36_CB | JA36(11KV愛36線) CB | FEEDER | [5 empty] | 541 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA36 | 愛36線(JA36) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0278 |  |  | 2-02-06 |  |  | F16 | PHA | 愛36線 JA36 RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA36_PHA | 11KV愛36線(JA36) 相間RY | FEEDER | [5 empty] | 542 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA36 | 愛36線(JA36) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0279 |  |  | 2-02-07 |  |  | F16 | GDA | 愛36線 JA36 RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA36_GDA | 11KV愛36線(JA36) 接地RY | FEEDER | [5 empty] | 543 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA37 | 愛37線(JA37) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/JA37/T1 |  |  | 0280 |  | 0144 | 2-03-00 |  | 2-10 | F17 | ON/OFF | 愛37線 JA37 CB 52AS |  | bbfb | B2/D12_D1 | [8 empty] | 仁愛DS.JA37_CB | JA37(11KV愛37線) CB | FEEDER | [5 empty] | 544 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA37 | 愛37線(JA37) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0281 |  |  | 2-03-01 |  |  | F17 | PHA | 愛37線 JA37 RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA37_PHA | 11KV愛37線(JA37) 相間RY | FEEDER | [5 empty] | 545 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA37 | 愛37線(JA37) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0282 |  |  | 2-03-02 |  |  | F17 | GDA | 愛37線 JA37 RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA37_GDA | 11KV愛37線(JA37) 接地RY | FEEDER | [5 empty] | 546 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA38 | 愛38線(JA38) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/JA38/T1 |  |  | 0283 |  | 0145 | 2-03-03 |  | 2-11 | F18 | ON/OFF | 愛38線 JA38 CB 52AS |  | bbgb | B2/D12_D1 | [8 empty] | 仁愛DS.JA38_CB | JA38(11KV愛38線) CB | FEEDER | [5 empty] | 547 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA38 | 愛38線(JA38) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0284 |  |  | 2-03-04 |  |  | F18 | PHA | 愛38線 JA38 RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA38_PHA | 11KV愛38線(JA38) 相間RY | FEEDER | [5 empty] | 548 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA38 | 愛38線(JA38) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0285 |  |  | 2-03-05 |  |  | F18 | GDA | 愛38線 JA38 RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA38_GDA | 11KV愛38線(JA38) 接地RY | FEEDER | [5 empty] | 549 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA39 | 愛39線(JA39) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/JA39/T1 |  |  | 0286 |  | 0146 | 2-03-06 |  | 2-12 | F19 | ON/OFF | 愛39線 JA39 CB 52AS |  | bbhb | B2/D12_D1 | [8 empty] | 仁愛DS.JA39_CB | JA39(11KV愛39線) CB | FEEDER | [5 empty] | 550 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA39 | 愛39線(JA39) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0287 |  |  | 2-03-07 |  |  | F19 | PHA | 愛39線 JA39 RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA39_PHA | 11KV愛39線(JA39) 相間RY | FEEDER | [5 empty] | 551 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA39 | 愛39線(JA39) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0288 |  |  | 2-04-00 |  |  | F19 | GDA | 愛39線 JA39 RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA39_GDA | 11KV愛39線(JA39) 接地RY | FEEDER | [5 empty] | 552 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA40 | 愛40線(JA40) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/JA40/T1 |  |  | 0289 |  | 0147 | 2-04-01 |  | 2-13 | F20 | ON/OFF | 愛40線 JA40 CB 52AS |  | bbib | B2/D12_D1 | [8 empty] | 仁愛DS.JA40_CB | JA40(11KV愛40線) CB | FEEDER | [5 empty] | 553 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA40 | 愛40線(JA40) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0290 |  |  | 2-04-02 |  |  | F20 | PHA | 愛40線 JA40 RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA40_PHA | 11KV愛40線(JA40) 相間RY | FEEDER | [5 empty] | 554 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA40 | 愛40線(JA40) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0291 |  |  | 2-04-03 |  |  | F20 | GDA | 愛40線 JA40 RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA40_GDA | 11KV愛40線(JA40) 接地RY | FEEDER | [5 empty] | 555 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 240 | #4SC(240) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | C/4SC |  |  | 0292 |  | 0142 | 2-04-04 |  | 2-0E | #2BSC | ON/OFF | #4SC 240 CB 52AS |  | bbdb | B3/D12_A1 | [8 empty] | 仁愛DS.240_CB | 240(11KV #4SC) CB | SC | [5 empty] | 556 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | 240 | #4SC(240) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0293 |  |  | 2-04-05 |  |  | #2BSC | SCA | #4SC 240 RY SCA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.240_SCA | 11KV #4SC 51,51N RY | SC | [5 empty] | 557 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 240 | #4SC(240) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0294 |  |  | 2-04-06 |  |  | #2BSC | UVA | #4SC 240 RY UVA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.240_UVA | 11KV #4SC 27RY(欠壓) | SC | [5 empty] | 558 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 200 | TIE-2(200) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/2BBus | B/1BBus |  |  | 0295 |  | 0141 | 2-04-07 |  | 2-0D | TIE-2 | ON/OFF | TIE-2 200 CB 52AS |  | bbab | B3/D12_A1 | [8 empty] | 仁愛DS.200_CB | 200(TIE) CB | TIE | [5 empty] | 559 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 11 | 11kV | 200 | TIE-2(200) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0296 |  |  | 2-05-00 |  |  | TIE-2 | PHA | TIE-2 200 RY PHA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.200_51A | 11KV TIE(200) 51RY | TIE | [5 empty] | 560 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 200 | TIE-2(200) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0297 |  |  | 2-05-01 |  |  | TIE-2 | GDA | TIE-2 200 RY GDA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.200_51NA | 11KV TIE(200) 51N RY | TIE | [5 empty] | 561 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA71 | 愛71線(JA71) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/JA71/T1 |  |  | 0298 |  | 0149 | 2-05-02 |  | 2-15 | F21 | ON/OFF | 愛71線 JA71 CB 52AS |  | accb | B2/D12_D1 | [8 empty] | 仁愛DS.JA71_CB | JA71(23KV愛71線) CB | FEEDER | [5 empty] | 562 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA71 | 愛71線(JA71) |  | PHA |  | B2 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0299 |  |  | 2-05-03 |  |  | F21 | PHA | 愛71線 JA71 RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA71_PHA | 23KV愛71線(JA71) 相間RY | FEEDER | [5 empty] | 563 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA71 | 愛71線(JA71) |  | GDA |  | B2 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0300 |  |  | 2-05-04 |  |  | F21 | GDA | 愛71線 JA71 RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA71_GDA | 23KV愛71線(JA71) 接地RY | FEEDER | [5 empty] | 564 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA72 | 愛72線(JA72) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/JA72/T1 |  |  | 0301 |  | 0150 | 2-05-05 |  | 2-16 | F22 | ON/OFF | 愛72線 JA72 CB 52AS |  | acdb | B2/D12_D1 | [8 empty] | 仁愛DS.JA72_CB | JA72(23KV愛72線) CB | FEEDER | [5 empty] | 565 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA72 | 愛72線(JA72) |  | PHA |  | B2 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0302 |  |  | 2-05-06 |  |  | F22 | PHA | 愛72線 JA72 RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA72_PHA | 23KV愛72線(JA72) 相間RY | FEEDER | [5 empty] | 566 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA72 | 愛72線(JA72) |  | GDA |  | B2 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0303 |  |  | 2-05-07 |  |  | F22 | GDA | 愛72線 JA72 RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA72_GDA | 23KV愛72線(JA72) 接地RY | FEEDER | [5 empty] | 567 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA73 | 愛73線(JA73) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/JA73/T1 |  |  | 0304 |  | 0151 | 2-06-00 |  | 2-17 | F23 | ON/OFF | 愛73線 JA73 CB 52AS |  | aceb | B2/D12_D1 | [8 empty] | 仁愛DS.JA73_CB | JA73(23KV愛73線) CB | FEEDER | [5 empty] | 568 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA73 | 愛73線(JA73) |  | PHA |  | B2 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0305 |  |  | 2-06-01 |  |  | F23 | PHA | 愛73線 JA73 RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA73_PHA | 23KV愛73線(JA73) 相間RY | FEEDER | [5 empty] | 569 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA73 | 愛73線(JA73) |  | GDA |  | B2 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0306 |  |  | 2-06-02 |  |  | F23 | GDA | 愛73線 JA73 RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA73_GDA | 23KV愛73線(JA73) 接地RY | FEEDER | [5 empty] | 570 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA74 | 愛74線(JA74) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/JA74/T1 |  |  | 0307 |  | 0152 | 2-06-03 |  | 2-18 | F24 | ON/OFF | 愛74線 JA74 CB 52AS |  | acfb | B2/D12_D1 | [8 empty] | 仁愛DS.JA74_CB | JA74(23KV愛74線) CB | FEEDER | [5 empty] | 571 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA74 | 愛74線(JA74) |  | PHA |  | B2 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0308 |  |  | 2-06-04 |  |  | F24 | PHA | 愛74線 JA74 RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA74_PHA | 23KV愛74線(JA74) 相間RY | FEEDER | [5 empty] | 572 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA74 | 愛74線(JA74) |  | GDA |  | B2 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0309 |  |  | 2-06-05 |  |  | F24 | GDA | 愛74線 JA74 RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA74_GDA | 23KV愛74線(JA74) 接地RY | FEEDER | [5 empty] | 573 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | 250 | #5SC(250) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3Bus | C/5SC |  |  | 0310 |  | 0148 | 2-06-06 |  | 2-14 | #3ASC | ON/OFF | #5SC 250 CB 52AS |  | acbb | B3/D12_A1 | [8 empty] | 仁愛DS.250_CB | 250(23KV #5SC) CB | SC | [5 empty] | 574 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | 250 | #5SC(250) |  | SCA |  | B2 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0311 |  |  | 2-06-07 |  |  | #3ASC | SCA | #5SC 250 RY SCA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.250_SCA | 23KV #5SC 51,51N RY | SC | [5 empty] | 575 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | 250 | #5SC(250) |  | UVA |  | B2 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0312 |  |  | 2-07-00 |  |  | #3ASC | UVA | #5SC 250 RY UVA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.250_UVA | 23KV #5SC 27RY(欠壓) | SC | [5 empty] | 576 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA75 | 愛75線(JA75) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/JA75/T1 |  |  | 0313 |  | 0153 | 2-07-01 |  | 2-19 | F25 | ON/OFF | 愛75線 JA75 CB 52AS |  | acgb | B2/D12_D1 | [8 empty] | 仁愛DS.JA75_CB | JA75(23KV愛75線) CB | FEEDER | [5 empty] | 577 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA75 | 愛75線(JA75) |  | PHA |  | B2 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0314 |  |  | 2-07-02 |  |  | F25 | PHA | 愛75線 JA75 RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA75_PHA | 23KV愛75線(JA75) 相間RY | FEEDER | [5 empty] | 578 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA75 | 愛75線(JA75) |  | GDA |  | B2 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0315 |  |  | 2-07-03 |  |  | F25 | GDA | 愛75線 JA75 RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA75_GDA | 23KV愛75線(JA75) 接地RY | FEEDER | [5 empty] | 579 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA76 | 愛76線(JA76) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/JA76/T1 |  |  | 0316 |  | 0154 | 2-07-04 |  | 2-1A | F26 | ON/OFF | 愛76線 JA76 CB 52AS |  | achb | B2/D12_D1 | [8 empty] | 仁愛DS.JA76_CB | JA76(23KV愛76線) CB | FEEDER | [5 empty] | 580 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA76 | 愛76線(JA76) |  | PHA |  | B2 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0317 |  |  | 2-07-05 |  |  | F26 | PHA | 愛76線 JA76 RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA76_PHA | 23KV愛76線(JA76) 相間RY | FEEDER | [5 empty] | 581 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA76 | 愛76線(JA76) |  | GDA |  | B2 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0318 |  |  | 2-07-06 |  |  | F26 | GDA | 愛76線 JA76 RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA76_GDA | 23KV愛76線(JA76) 接地RY | FEEDER | [5 empty] | 582 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA77 | 愛77線(JA77) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/JA77/T1 |  |  | 0319 |  | 0155 | 2-07-07 |  | 2-1B | F27 | ON/OFF | 愛77線 JA77 CB 52AS |  | acib | B2/D12_D1 | [8 empty] | 仁愛DS.JA77_CB | JA77(23KV愛77線) CB | FEEDER | [5 empty] | 583 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA77 | 愛77線(JA77) |  | PHA |  | B2 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0320 |  |  | 2-08-00 |  |  | F27 | PHA | 愛77線 JA77 RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA77_PHA | 23KV愛77線(JA77) 相間RY | FEEDER | [5 empty] | 584 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA77 | 愛77線(JA77) |  | GDA |  | B2 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0321 |  |  | 2-08-01 |  |  | F27 | GDA | 愛77線 JA77 RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA77_GDA | 23KV愛77線(JA77) 接地RY | FEEDER | [5 empty] | 585 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA78 | 愛78線(JA78) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/JA78/T1 |  |  | 0322 |  | 0156 | 2-08-02 |  | 2-1C | F28 | ON/OFF | 愛78線 JA78 CB 52AS |  | ackb | B2/D12_D1 | [8 empty] | 仁愛DS.JA78_CB | JA78(23KV愛78線) CB | FEEDER | [5 empty] | 586 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA78 | 愛78線(JA78) |  | PHA |  | B2 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0323 |  |  | 2-08-03 |  |  | F28 | PHA | 愛78線 JA78 RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA78_PHA | 23KV愛78線(JA78) 相間RY | FEEDER | [5 empty] | 587 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA78 | 愛78線(JA78) |  | GDA |  | B2 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0324 |  |  | 2-08-04 |  |  | F28 | GDA | 愛78線 JA78 RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA78_GDA | 23KV愛78線(JA78) 接地RY | FEEDER | [5 empty] | 588 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | 260 | #6SC(260) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3Bus | C/6SC |  |  | 0325 |  | 0157 | 2-08-05 |  | 2-1D | #3BSC | ON/OFF | #6SC 260 CB 52AS |  | aclb | B3/D12_A1 | [8 empty] | 仁愛DS.260_CB | 260(23KV #6SC) CB | SC | [5 empty] | 589 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | 260 | #6SC(260) |  | SCA |  | B2 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0326 |  |  | 2-08-06 |  |  | #3BSC | SCA | #6SC 260 RY SCA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.260_SCA | 23KV #6SC 51,51N RY | SC | [5 empty] | 590 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | 260 | #6SC(260) |  | UVA |  | B2 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0327 |  |  | 2-08-07 |  |  | #3BSC | UVA | #6SC 260 RY UVA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.260_UVA | 23KV #6SC 27RY(欠壓) | SC | [5 empty] | 591 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA5A | 愛5A線(JA5A) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4Bus | L/JA5A/T1 |  |  | 0328 |  | 0160 | 2-09-00 |  | 2-20 | F29 | ON/OFF | 愛5A線 JA5A CB 52AS |  | addb | B2/D12_D1 | [8 empty] | 仁愛DS.JA5A_CB | JA5A(23KV愛5A線) CB | FEEDER | [5 empty] | 592 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA5A | 愛5A線(JA5A) |  | PHA |  | B2 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0329 |  |  | 2-09-01 |  |  | F29 | PHA | 愛5A線 JA5A RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA5A_PHA | 23KV愛5A線(JA5A) 相間RY | FEEDER | [5 empty] | 593 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA5A | 愛5A線(JA5A) |  | GDA |  | B2 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0330 |  |  | 2-09-02 |  |  | F29 | GDA | 愛5A線 JA5A RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA5A_GDA | 23KV愛5A線(JA5A) 接地RY | FEEDER | [5 empty] | 594 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA5B | 愛5B線(JA5B) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4Bus | L/JA5B/T1 |  |  | 0331 |  | 0161 | 2-09-03 |  | 2-21 | F30 | ON/OFF | 愛5B線 JA5B CB 52AS |  | adeb | B2/D12_D1 | [8 empty] | 仁愛DS.JA5B_CB | JA5B(23KV愛5B線) CB | FEEDER | [5 empty] | 595 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA5B | 愛5B線(JA5B) |  | PHA |  | B2 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0332 |  |  | 2-09-04 |  |  | F30 | PHA | 愛5B線 JA5B RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA5B_PHA | 23KV愛5B線(JA5B) 相間RY | FEEDER | [5 empty] | 596 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA5B | 愛5B線(JA5B) |  | GDA |  | B2 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0333 |  |  | 2-09-05 |  |  | F30 | GDA | 愛5B線 JA5B RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA5B_GDA | 23KV愛5B線(JA5B) 接地RY | FEEDER | [5 empty] | 597 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA5C | 愛5C線(JA5C) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4Bus | L/JA5C/T1 |  |  | 0334 |  | 0162 | 2-09-06 |  | 2-22 | F31 | ON/OFF | 愛5C線 JA5C CB 52AS |  | adfb | B2/D12_D1 | [8 empty] | 仁愛DS.JA5C_CB | JA5C(23KV愛5C線) CB | FEEDER | [5 empty] | 598 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA5C | 愛5C線(JA5C) |  | PHA |  | B2 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0335 |  |  | 2-09-07 |  |  | F31 | PHA | 愛5C線 JA5C RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA5C_PHA | 23KV愛5C線(JA5C) 相間RY | FEEDER | [5 empty] | 599 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA5C | 愛5C線(JA5C) |  | GDA |  | B2 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0336 |  |  | 2-0A-00 |  |  | F31 | GDA | 愛5C線 JA5C RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA5C_GDA | 23KV愛5C線(JA5C) 接地RY | FEEDER | [5 empty] | 600 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA5D | 愛5D線(JA5D) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4Bus | L/JA5D/T1 |  |  | 0337 |  | 0163 | 2-0A-01 |  | 2-23 | F32 | ON/OFF | 愛5D線 JA5D CB 52AS |  | adgb | B2/D12_D1 | [8 empty] | 仁愛DS.JA5D_CB | JA5D(23KV愛5D線) CB | FEEDER | [5 empty] | 601 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA5D | 愛5D線(JA5D) |  | PHA |  | B2 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0338 |  |  | 2-0A-02 |  |  | F32 | PHA | 愛5D線 JA5D RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA5D_PHA | 23KV愛5D線(JA5D) 相間RY | FEEDER | [5 empty] | 602 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA5D | 愛5D線(JA5D) |  | GDA |  | B2 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0339 |  |  | 2-0A-03 |  |  | F32 | GDA | 愛5D線 JA5D RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA5D_GDA | 23KV愛5D線(JA5D) 接地RY | FEEDER | [5 empty] | 603 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | 270 | #7SC(270) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4Bus | C/7SC |  |  | 0340 |  | 0159 | 2-0A-04 |  | 2-1F | #4ASC | ON/OFF | #7SC 270 CB 52AS |  | adcb | B3/D12_A1 | [8 empty] | 仁愛DS.270_CB | 270(23KV #7SC) CB | SC | [5 empty] | 604 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | 270 | #7SC(270) |  | SCA |  | B2 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0341 |  |  | 2-0A-05 |  |  | #4ASC | SCA | #7SC 270 RY SCA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.270_SCA | 23KV #7SC 51,51N RY | SC | [5 empty] | 605 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | 270 | #7SC(270) |  | UVA |  | B2 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0342 |  |  | 2-0A-06 |  |  | #4ASC | UVA | #7SC 270 RY UVA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.270_UVA | 23KV #7SC 27RY(欠壓) | SC | [5 empty] | 606 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA5F | 愛5F線(JA5F) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4Bus | L/JA5F/T1 |  |  | 0343 |  | 0164 | 2-0A-07 |  | 2-24 | F33 | ON/OFF | 愛5F線 JA5F CB 52AS |  | adhb | B2/D12_D1 | [8 empty] | 仁愛DS.JA5F_CB | JA5F(23KV愛5F線) CB | FEEDER | [5 empty] | 607 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA5F | 愛5F線(JA5F) |  | PHA |  | B2 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0344 |  |  | 2-0B-00 |  |  | F33 | PHA | 愛5F線 JA5F RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA5F_PHA | 23KV愛5F線(JA5F) 相間RY | FEEDER | [5 empty] | 608 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA5F | 愛5F線(JA5F) |  | GDA |  | B2 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0345 |  |  | 2-0B-01 |  |  | F33 | GDA | 愛5F線 JA5F RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA5F_GDA | 23KV愛5F線(JA5F) 接地RY | FEEDER | [5 empty] | 609 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA5G | 愛5G線(JA5G) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4Bus | L/JA5G/T1 |  |  | 0346 |  | 0165 | 2-0B-02 |  | 2-25 | F34 | ON/OFF | 愛5G線 JA5G CB 52AS |  | adib | B2/D12_D1 | [8 empty] | 仁愛DS.JA5G_CB | JA5G(23KV愛5G線) CB | FEEDER | [5 empty] | 610 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA5G | 愛5G線(JA5G) |  | PHA |  | B2 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0347 |  |  | 2-0B-03 |  |  | F34 | PHA | 愛5G線 JA5G RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA5G_PHA | 23KV愛5G線(JA5G) 相間RY | FEEDER | [5 empty] | 611 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA5G | 愛5G線(JA5G) |  | GDA |  | B2 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0348 |  |  | 2-0B-04 |  |  | F34 | GDA | 愛5G線 JA5G RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA5G_GDA | 23KV愛5G線(JA5G) 接地RY | FEEDER | [5 empty] | 612 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA5H | 愛5H線(JA5H) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4Bus | L/JA5H/T1 |  |  | 0349 |  | 0166 | 2-0B-05 |  | 2-26 | F35 | ON/OFF | 愛5H線 JA5H CB 52AS |  | adjb | B2/D12_D1 | [8 empty] | 仁愛DS.JA5H_CB | JA5H(23KV愛5H線) CB | FEEDER | [5 empty] | 613 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA5H | 愛5H線(JA5H) |  | PHA |  | B2 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0350 |  |  | 2-0B-06 |  |  | F35 | PHA | 愛5H線 JA5H RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA5H_PHA | 23KV愛5H線(JA5H) 相間RY | FEEDER | [5 empty] | 614 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA5H | 愛5H線(JA5H) |  | GDA |  | B2 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0351 |  |  | 2-0B-07 |  |  | F35 | GDA | 愛5H線 JA5H RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA5H_GDA | 23KV愛5H線(JA5H) 接地RY | FEEDER | [5 empty] | 615 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA5K | 愛5K線(JA5K) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4Bus | L/JA5K/T1 |  |  | 0352 |  | 0167 | 2-0C-00 |  | 2-27 | F36 | ON/OFF | 愛5K線 JA5K CB 52AS |  | adlb | B2/D12_D1 | [8 empty] | 仁愛DS.JA5K_CB | JA5K(23KV愛5K線) CB | FEEDER | [5 empty] | 616 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA5K | 愛5K線(JA5K) |  | PHA |  | B2 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0353 |  |  | 2-0C-01 |  |  | F36 | PHA | 愛5K線 JA5K RY PHA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA5K_PHA | 23KV愛5K線(JA5K) 相間RY | FEEDER | [5 empty] | 617 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA5K | 愛5K線(JA5K) |  | GDA |  | B2 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0354 |  |  | 2-0C-02 |  |  | F36 | GDA | 愛5K線 JA5K RY GDA |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA5K_GDA | 23KV愛5K線(JA5K) 接地RY | FEEDER | [5 empty] | 618 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | 280 | #8SC(280) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4Bus | C/8SC |  |  | 0355 |  | 0168 | 2-0C-03 |  | 2-28 | #4BSC | ON/OFF | #8SC 280 CB 52AS |  | admb | B3/D12_A1 | [8 empty] | 仁愛DS.280_CB | 280(23KV #8SC) CB | SC | [5 empty] | 619 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | 280 | #8SC(280) |  | SCA |  | B2 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0356 |  |  | 2-0C-04 |  |  | #4BSC | SCA | #8SC 280 RY SCA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.280_SCA | 23KV #8SC 51,51N RY | SC | [5 empty] | 620 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | 280 | #8SC(280) |  | UVA |  | B2 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0357 |  |  | 2-0C-05 |  |  | #4BSC | UVA | #8SC 280 RY UVA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.280_UVA | 23KV #8SC 27RY(欠壓) | SC | [5 empty] | 621 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | 400 | TIE-4(400) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/4Bus | B/3Bus |  |  | 0358 |  | 0158 | 2-0C-06 |  | 2-1E | TIE-4 | ON/OFF | TIE-4 400 CB 52AS |  | adab | B3/D12_A1 | [8 empty] | 仁愛DS.400_CB | 400(TIE) CB | TIE | [5 empty] | 622 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 22 | 22kV | 400 | TIE-4(400) |  | PHA |  | B2 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0359 |  |  | 2-0C-07 |  |  | TIE-4 | PHA | TIE-4 400 RY PHA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.400_51A | 23KV TIE(400) 51RY | TIE | [5 empty] | 623 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | 400 | TIE-4(400) |  | GDA |  | B2 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0360 |  |  | 2-0D-00 |  |  | TIE-4 | GDA | TIE-4 400 RY GDA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.400_51NA | 23KV TIE(400) 51N RY | TIE | [5 empty] | 624 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0768 |  | 0000 | 1-30-00 |  | 1-00 | Test CB | ON/OFF | TEST C.B. |  |  | ELEM/ALL | [8 empty] | 仁愛DS.TEST_CB | TEST CB | OTHER | [5 empty] | 625 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | RTU | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0769 |  |  | 1-30-01 |  |  | RTU | L/R | LOCAL/REMOTE STATUS |  |  | ELEM/D12_A1 | [8 empty] | 仁愛DS.RTU_S/L | RTU SUPY/LOCAL | OTHER | [5 empty] | 626 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
D12 | 仁愛DS | 161 | 161kV | 1520 | 嘉義～仁愛海線(1520) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0770 |  | 0034 | 1-30-02 |  | 1-22 | 1520 | USE/LOCK | 嘉義仁愛海線 1520 87S |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1520_87UL | 嘉義仁愛海線(1520) 87RY U/L | LINE161 | [5 empty] | 627 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 161 | 161kV | 1520 | 嘉義～仁愛海線(1520) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0771 |  | 0035 | 1-30-03 |  | 1-23 | 1520 | USE/LOCK | 嘉義仁愛海線 1520 79S |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1520_79UL | 嘉義仁愛海線(1520) 79RY U/L | LINE161 | [5 empty] | 628 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 161 | 161kV | 1510 | 嘉義～仁愛山線(1510) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0772 |  | 0036 | 1-30-04 |  | 1-24 | 1510 | USE/LOCK | 嘉義仁愛山線 1510 87S |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1510_87UL | 嘉義仁愛山線(1510) 87RY U/L | LINE161 | [5 empty] | 629 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 161 | 161kV | 1510 | 嘉義～仁愛山線(1510) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0773 |  | 0037 | 1-30-05 |  | 1-25 | 1510 | USE/LOCK | 嘉義仁愛山線 1510 79S |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1510_79UL | 嘉義仁愛山線(1510) 79RY U/L | LINE161 | [5 empty] | 630 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 161 | 161kV | 1540 | 仁愛～北回二路(1540) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0774 |  | 0038 | 1-30-06 |  | 1-26 | Line3 | USE/LOCK | 仁愛北回二路 (1540) 87S |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1540_87UL | 仁愛北回二路(1540) 87RY U/L | LINE161 | [5 empty] | 631 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 161 | 161kV | 1540 | 仁愛～北回二路(1540) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0775 |  | 0039 | 1-30-07 |  | 1-27 | Line3 | USE/LOCK | 仁愛北回二路 (1540) 79S |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1540_79UL | 仁愛北回二路(1540) 79RY U/L | LINE161 | [5 empty] | 632 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 161 | 161kV | 1530 | 仁愛～北回一路(1530) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0776 |  | 0040 | 1-30-08 |  | 1-28 | Line4 | USE/LOCK | 仁愛北回一路(1530) 87S |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1530_87UL | 仁愛北回一路(1530) 87RY U/L | LINE161 | [5 empty] | 633 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 161 | 161kV | 1530 | 仁愛～北回一路(1530) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0777 |  | 0041 | 1-30-09 |  | 1-29 | Line4 | USE/LOCK | 仁愛北回一路(1530) 79S |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1530_79UL | 仁愛北回一路(1530) 79RY U/L | LINE161 | [5 empty] | 634 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 0 |  | ComPoint |  |  | OLTC_A |  |  | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0790 |  |  | 1-31-06 |  |  | OLTC | OLTCA | OLTC 15分鐘內連動3次警報 |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | [5 empty] | 635 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | StaDev | 所內設施 |  | GEN | 緊急發電機運轉 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0791 |  |  | 1-31-07 |  |  | Locate Empty | ON/OFF | 緊急發電機運轉 |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.GEN | 緊急發電機運轉 | OTHER | [5 empty] | 636 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ON/OFF | OFF
D12 | 仁愛DS |  |  | 1DTR | #1DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0792 |  |  | 1-31-08 |  |  | Locate Empty | USE/LOCK | NO.1 D.TR. 187S |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#1DTR_87UL | #1DTR 87RY U/L | MTR | [5 empty] | 637 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS |  |  | 1DTR(A) | #1DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0793 |  |  | 1-31-09 |  |  | Locate Empty | 遙控/現場 | NO.1 D.TR. S/L (A) 143R1S3 |  | c | B1/D12_A1 | [8 empty] | 仁愛DS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | [5 empty] | 638 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D12 | 仁愛DS |  |  | 1DTR(A) | #1DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0794 |  | 0058 | 1-31-10 |  | 1-3A | Locate Empty | OLTC A/M | NO.1 D.TR. A/M (A) 1AX-S1 |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | [5 empty] | 639 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D12 | 仁愛DS |  |  | 1DTR(B) | #1DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0795 |  |  | 1-31-11 |  |  | Locate Empty | 遙控/現場 | NO.1 D.TR. S/L (B) 143R2S3 |  | b | B1/D12_A1 | [8 empty] | 仁愛DS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | [5 empty] | 640 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D12 | 仁愛DS |  |  | 1DTR(B) | #1DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0796 |  | 0060 | 1-31-12 |  | 1-3C | Locate Empty | OLTC A/M | NO.1 D.TR. A/M (B) 1AX-S2 |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | [5 empty] | 641 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D12 | 仁愛DS |  |  | 1DTR | #1DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0797 |  |  | 1-31-13 |  |  | Locate Empty | A/N | NO.1 D.TR.撲氣電驛(1) 196B1 |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | [5 empty] | 642 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 1DTR | #1DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0798 |  |  | 1-31-14 |  |  | Locate Empty | A/N | NO.1 D.TR.撲氣電驛(2) 196B2 |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | [5 empty] | 643 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 1DTR | #1DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0799 |  |  | 1-31-15 |  |  | Locate Empty | A/N | NO.1 D.TR.放壓裝置 196D |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#1DTR_96D | #1DTR 96D RY | MTR | [5 empty] | 644 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 1DTR | #1DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0800 |  |  | 1-32-00 |  |  | Locate Empty | A/N | NO.1 D.TR.衝擊油壓 196P |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#1DTR_96P | #1DTR 96P RY | MTR | [5 empty] | 645 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 1DTR | #1DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0801 |  |  | 1-32-01 |  |  | Locate Empty | A/N | NO.1 D.TR. ULTC 163Q |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#1DTR_63Q | #1DTR 63Q RY | MTR | [5 empty] | 646 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 1DTR | #1DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0802 |  |  | 1-32-02 |  |  | Locate Empty | A/N | NO.1 D.TR.輕故障 1TRF |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#1DTR_TRF | #1DTR 輕故障 | MTR | [5 empty] | 647 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 1DTR | #1DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0803 |  |  | 1-32-03 |  |  | Locate Empty | A/N | NO.1 D.TR.重故障 1TRA |  | a | B1/D12_A1 | [8 empty] | 仁愛DS.#1DTR_TRA | #1DTR 重故障 | MTR | [5 empty] | 648 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 2DTR | #2DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0804 |  |  | 1-32-04 |  |  | Locate Empty | USE/LOCK | NO.2 D.TR. 287S |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#2DTR_87UL | #2DTR 87RY U/L | MTR | [5 empty] | 649 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS |  |  | 2DTR(A) | #2DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0805 |  |  | 1-32-05 |  |  | Locate Empty | 遙控/現場 | NO.2 D.TR. S/L (A) 243R1S3 |  | c | B1/D12_A1 | [8 empty] | 仁愛DS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | [5 empty] | 650 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D12 | 仁愛DS |  |  | 2DTR(A) | #2DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0806 |  | 0062 | 1-32-06 |  | 1-3E | Locate Empty | OLTC A/M | NO.2 D.TR. A/M (A) 2AX-S1 |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | [5 empty] | 651 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D12 | 仁愛DS |  |  | 2DTR(B) | #2DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0807 |  |  | 1-32-07 |  |  | Locate Empty | 遙控/現場 | NO.2 D.TR. S/L (B) 243R2S3 |  | b | B1/D12_A1 | [8 empty] | 仁愛DS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | [5 empty] | 652 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D12 | 仁愛DS |  |  | 2DTR(B) | #2DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0808 |  | 0064 | 1-32-08 |  | 1-40 | Locate Empty | OLTC A/M | NO.2 D.TR. A/M (B) 2AX-S2 |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | [5 empty] | 653 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D12 | 仁愛DS |  |  | 2DTR | #2DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0809 |  |  | 1-32-09 |  |  | Locate Empty | A/N | NO.2 D.TR.撲氣電驛(1) 296B1 |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | [5 empty] | 654 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 2DTR | #2DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0810 |  |  | 1-32-10 |  |  | Locate Empty | A/N | NO.2 D.TR.撲氣電驛(2) 296B2 |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | [5 empty] | 655 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 2DTR | #2DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0811 |  |  | 1-32-11 |  |  | Locate Empty | A/N | NO.2 D.TR.放壓裝置 296D |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#2DTR_96D | #2DTR 96D RY | MTR | [5 empty] | 656 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 2DTR | #2DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0812 |  |  | 1-32-12 |  |  | Locate Empty | A/N | NO.2 D.TR.衝擊油壓 296P |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#2DTR_96P | #2DTR 96P RY | MTR | [5 empty] | 657 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 2DTR | #2DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0813 |  |  | 1-32-13 |  |  | Locate Empty | A/N | NO.2 D.TR. ULTC 263Q |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#2DTR_63Q | #2DTR 63Q RY | MTR | [5 empty] | 658 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 2DTR | #2DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0814 |  |  | 1-32-14 |  |  | Locate Empty | A/N | NO.2 D.TR.輕故障 2TRF |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#2DTR_TRF | #2DTR 輕故障 | MTR | [5 empty] | 659 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 2DTR | #2DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0815 |  |  | 1-32-15 |  |  | Locate Empty | A/N | NO.2 D.TR.重故障 2TRA |  | a | B1/D12_A1 | [8 empty] | 仁愛DS.#2DTR_TRA | #2DTR 重故障 | MTR | [5 empty] | 660 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 3DTR | #3DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0816 |  |  | 1-33-00 |  |  | Locate Empty | USE/LOCK | NO.3 D.TR. 387S |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#3DTR_87UL | #3DTR 87RY U/L | MTR | [5 empty] | 661 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS |  |  | 3DTR | #3DTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0817 |  |  | 1-33-01 |  |  | Locate Empty | 遙控/現場 | NO.3 D.TR. S/L (A) 343R1S3 |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#3DTR_S/L | #3DTR OLTC S/L | MTR | [5 empty] | 662 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D12 | 仁愛DS |  |  | 3DTR | #3DTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0818 |  | 0066 | 1-33-02 |  | 1-42 | Locate Empty | OLTC A/M | NO.3 D.TR. A/M (A) 3AX-S |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#3DTR_A/M | #3DTR OLTC A/M | MTR | [5 empty] | 663 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D12 | 仁愛DS |  |  | 3DTR | #3DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0819 |  |  | 1-33-03 |  |  | Locate Empty | A/N | NO.3 D.TR.撲氣電驛(1) 396B1 |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#3DTR_96B1 | #3DTR 96B1 RY | MTR | [5 empty] | 664 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 3DTR | #3DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0820 |  |  | 1-33-04 |  |  | Locate Empty | A/N | NO.3 D.TR.撲氣電驛(2) 396B2 |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#3DTR_96B2 | #3DTR 96B2 RY | MTR | [5 empty] | 665 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 3DTR | #3DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0821 |  |  | 1-33-05 |  |  | Locate Empty | A/N | NO.3 D.TR.放壓裝置 396D |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#3DTR_96D | #3DTR 96D RY | MTR | [5 empty] | 666 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 3DTR | #3DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0822 |  |  | 1-33-06 |  |  | Locate Empty | A/N | NO.3 D.TR.衝擊油壓 396P |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#3DTR_96P | #3DTR 96P RY | MTR | [5 empty] | 667 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 3DTR | #3DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0823 |  |  | 1-33-07 |  |  | Locate Empty | A/N | NO.3 D.TR. ULTC 363Q |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#3DTR_63Q | #3DTR 63Q RY | MTR | [5 empty] | 668 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 3DTR | #3DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0824 |  |  | 1-33-08 |  |  | Locate Empty | A/N | NO.3 D.TR.輕故障 3TRF |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#3DTR_TRF | #3DTR 輕故障 | MTR | [5 empty] | 669 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 3DTR | #3DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR |  |  |  |  | 0825 |  |  | 1-33-09 |  |  | Locate Empty | A/N | NO.3 D.TR.重故障 3TRA |  | a | B1/D12_A1 | [8 empty] | 仁愛DS.#3DTR_TRA | #3DTR 重故障 | MTR | [5 empty] | 670 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 4DTR | #4DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0826 |  |  | 1-33-10 |  |  | Locate Empty | USE/LOCK | NO.4 D.TR. 487S |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#4DTR_87UL | #4DTR 87RY U/L | MTR | [5 empty] | 671 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS |  |  | 4DTR | #4DTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0827 |  |  | 1-33-11 |  |  | Locate Empty | 遙控/現場 | NO.4 D.TR. S/L (A) 443R1S3 |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#4DTR_S/L | #4DTR OLTC S/L | MTR | [5 empty] | 672 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D12 | 仁愛DS |  |  | 4DTR | #4DTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0828 |  | 0068 | 1-33-12 |  | 1-44 | Locate Empty | OLTC A/M | NO.4 D.TR. A/M (A) 4AX-S |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#4DTR_A/M | #4DTR OLTC A/M | MTR | [5 empty] | 673 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D12 | 仁愛DS |  |  | 4DTR | #4DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0829 |  |  | 1-33-13 |  |  | Locate Empty | A/N | NO.4 D.TR.撲氣電驛(1) 496B1 |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#4DTR_96B1 | #4DTR 96B1 RY | MTR | [5 empty] | 674 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 4DTR | #4DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0830 |  |  | 1-33-14 |  |  | Locate Empty | A/N | NO.4 D.TR.撲氣電驛(2) 496B2 |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#4DTR_96B2 | #4DTR 96B2 RY | MTR | [5 empty] | 675 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 4DTR | #4DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0831 |  |  | 1-33-15 |  |  | Locate Empty | A/N | NO.4 D.TR.放壓裝置 496D |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#4DTR_96D | #4DTR 96D RY | MTR | [5 empty] | 676 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 4DTR | #4DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0832 |  |  | 1-34-00 |  |  | Locate Empty | A/N | NO.4 D.TR.衝擊油壓 496P |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#4DTR_96P | #4DTR 96P RY | MTR | [5 empty] | 677 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 4DTR | #4DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0833 |  |  | 1-34-01 |  |  | Locate Empty | A/N | NO.4 D.TR. ULTC 463Q |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#4DTR_63Q | #4DTR 63Q RY | MTR | [5 empty] | 678 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 4DTR | #4DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0834 |  |  | 1-34-02 |  |  | Locate Empty | A/N | NO.4 D.TR.輕故障 4TRF |  |  | B1/D12_A1 | [8 empty] | 仁愛DS.#4DTR_TRF | #4DTR 輕故障 | MTR | [5 empty] | 679 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D12 | 仁愛DS |  |  | 4DTR | #4DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR |  |  |  |  | 0835 |  |  | 1-34-03 |  |  | Locate Empty | A/N | NO.4 D.TR.重故障 4TRA |  | a | B1/D12_A1 | [8 empty] | 仁愛DS.#4DTR_TRA | #4DTR 重故障 | MTR | [5 empty] | 680 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | StaDev | 所內設施 |  | Fire1 | 受信總機 |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0836 |  |  | 1-34-04 |  |  | 火災警報(1 | A/N | 火災警報(1)受信總機 |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | [5 empty] | 681 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | StaDev | 所內設施 |  | Fire2 |  |  | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0837 |  |  | 1-34-05 |  |  | 火災警報(2) | A/N | 火災警報(2) |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.火災警報(2) | 火災警報(2) | OTHER | [5 empty] | 682 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | StaDev | 所內設施 |  | Fire3 |  |  | Status | 火災警報3 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0838 |  |  | 1-34-06 |  |  | 火災警報(3) | A/N | 火災警報(3) |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.火災警報(3) | 火災警報(3) | OTHER | [5 empty] | 683 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | StaDev | 所內設施 |  | Fire4 |  |  | Status | 火災警報4 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0839 |  |  | 1-34-07 |  |  | 火災警報(4) | A/N | 火災警報(4) |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.火災警報(4) | 火災警報(4) | OTHER | [5 empty] | 684 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | StaDev | 所內設施 |  | Fire5 |  |  | Status | 火災警報5 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0840 |  |  | 1-34-08 |  |  | 火災警報(5) | A/N | 火災警報(5) |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.火災警報(5) | 火災警報(5) | OTHER | [5 empty] | 685 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | StaDev | 所內設施 |  | Door1 | 1F大門門禁 |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0841 |  |  | 1-34-09 |  |  | Locate Empty | A/N | 無人化門禁(一)1F大門門禁警報 DOOR1 |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.無人化門禁(1) | 無人化門禁(1)建築物大門 | OTHER | [5 empty] | 686 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | StaDev | 所內設施 |  | Door2 | 控制室門禁 |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0842 |  |  | 1-34-10 |  |  | Locate Empty | A/N | 無人化門禁(二)控制室門禁警報 DOOR2 |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.無人化門禁(2) | 無人化門禁(2)控制室大門 | OTHER | [5 empty] | 687 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | StaDev | 所內設施 |  | Door3 | 保全警報 |  | Status | 無人化門禁3 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0843 |  |  | 1-34-11 |  |  | Locate Empty | A/N | 無人化門禁(三)保全警報 DOOR3 |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | [5 empty] | 688 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | StaDev | 所內設施 |  | Door4 |  |  | Status | 無人化門禁4 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0844 |  |  | 1-34-12 |  |  | Locate Empty | A/N | 無人化門禁(四) DOOR4 |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.無人化門禁(4) | 無人化門禁(4) | OTHER | [5 empty] | 689 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | StaDev | 所內設施 |  | Door5 |  | Element | Status | 無人化門禁5 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0845 |  |  | 1-34-13 |  |  | Locate Empty | A/N | 無人化門禁(五) DOOR5 |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.無人化門禁(5) | 無人化門禁(5) | OTHER | [5 empty] | 690 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | StaDev | 所內設施 |  | Lights1 |  |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0846 |  | 0124 | 1-34-14 |  | 1-7C | Locate Empty | ON/OFF | 無人化開關場照明(A) FLA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.開關場照明(A) | 開關場照明(A) | OTHER | [5 empty] | 691 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
D12 | 仁愛DS | 0 |  | StaDev | 所內設施 |  | Lights2 |  |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0847 |  | 0125 | 1-34-15 |  | 1-7D | Locate Empty | ON/OFF | 無人化開關場照明(B) FLB |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.開關場照明(B) | 開關場照明(B) | OTHER | [5 empty] | 692 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
D12 | 仁愛DS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0848 |  |  | 1-35-00 |  |  | Locate Empty | ON/OFF | 所內電源 ACB1 |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | [5 empty] | 693 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D12 | 仁愛DS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0849 |  |  | 1-35-01 |  |  | Locate Empty | ON/OFF | 所內電源 ACB2 |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | [5 empty] | 694 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D12 | 仁愛DS | 0 |  | ComPoint |  |  | OPA |  |  | Status | 充油電纜低壓警報 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0851 |  |  | 1-35-03 |  |  | Locate Empty | A/N | 充油電纜警報 OPA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | [5 empty] | 695 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0852 |  |  | 1-35-04 |  |  | Locate Empty | A/N | 所內欠壓警報 STUV |  |  | ELEM/D12_A1 | [8 empty] | 仁愛DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | [5 empty] | 696 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | StaDev | 所內設施 |  | AIRCON |  |  | Status | 冷氣跳脫 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0853 |  |  | 1-35-05 |  |  | Locate Empty | A/N | 冷氣機空調故障警報 |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.空調機故障 | 空調機故障或電源跳脫 | OTHER | [5 empty] | 697 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | StaDev | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0854 |  |  | 1-35-06 |  |  | Locate Empty | A/N | 電力量測器故障 PMA |  |  | ELEM/D12_A1 | [8 empty] | 仁愛DS.PMA | 電力量測表計故障 | OTHER | [5 empty] | 698 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0855 |  |  | 1-35-07 |  |  | Locate Empty | A/N | 161KV CB 重故障 CBA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.161KV_CBA | 161KV斷路器重故障 | OTHER | [5 empty] | 699 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0856 |  |  | 1-35-08 |  |  | Locate Empty | A/N | 161KV CB 輕故障 CBF |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | [5 empty] | 700 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0857 |  |  | 1-35-09 |  |  | Locate Empty | A/N | NFB跳脫警報 DCA |  |  | ELEM/D12_A1 | [8 empty] | 仁愛DS.直流電源DCA | 直流電源故障警報 | OTHER | [5 empty] | 701 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0858 |  |  | 1-35-10 |  |  | Locate Empty | A/N | ACB警報 ACBA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.所內電源ACBA | 所內電源故障警報 | OTHER | [5 empty] | 702 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0859 |  |  | 1-35-11 |  |  | Locate Empty | A/N | 161KV NO.1 BUS欠壓 VUA1 |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | [5 empty] | 703 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0860 |  |  | 1-35-12 |  |  | Locate Empty | A/N | 161KV NO.2 BUS欠壓 VUA2 |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | [5 empty] | 704 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0861 |  |  | 1-35-13 |  |  | Locate Empty | A/N | 充電機警報 CHG1 |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | [5 empty] | 705 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0862 |  |  | 1-35-14 |  |  | Locate Empty | A/N | DC接地警報 DCE |  |  | ELEM/D12_A1 | [8 empty] | 仁愛DS.直流電源DCE | 直流電源接地故障警報 | OTHER | [5 empty] | 706 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | StaDev | 所內設施 |  | Water1 |  |  | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0863 |  |  | 1-35-15 |  |  | Locate Empty | A/N | 地下室水位警報(1) UW1 |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.水位警報(1) | 地下室水位警報(1) | OTHER | [5 empty] | 707 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | StaDev | 所內設施 |  | Water2 |  |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0864 |  |  | 1-36-00 |  |  | Locate Empty | A/N | 地下室水位警報(2) UW2 |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.水位警報(2) | 地下室水位警報(2) | OTHER | [5 empty] | 708 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | ComPoint |  |  | COMT |  |  | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0865 |  |  | 1-36-01 |  |  | Locate Empty | A/N | 161KV CB空壓機超時運轉 COMT |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.161空壓機COMT | 161KV空壓機運轉超時警報 | OTHER | [5 empty] | 709 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | ComPoint |  |  | 60A |  |  | Status | 電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0866 |  |  | 1-36-02 |  |  | Locate Empty | A/N | 23KV SC 60-RY 警報 60A |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.23KV_SC_60A | 23/11KV SC 60A | OTHER | [5 empty] | 710 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0867 |  |  | 1-36-03 |  |  | Locate Empty | A/N | 23KV CB重故障 CBA |  |  | ELEM/D12_A1 | [8 empty] | 仁愛DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | [5 empty] | 711 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0868 |  |  | 1-36-04 |  |  | Locate Empty | A/N | 23KV CB輕故障 CBF |  |  | ELEM/D12_A1 | [8 empty] | 仁愛DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | [5 empty] | 712 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | ComPoint |  |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0869 |  |  | 1-36-05 |  |  | Locate Empty | A/N | 23KV FEEDER 79RY LOA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.FEEDER_RCA | 饋線復閉電驛動作 | OTHER | [5 empty] | 713 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | StaDev | 所內設施 |  | OilLeak1 |  |  | Status | 洩油池水位警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0870 |  |  | 1-36-06 |  |  | Locate Empty | A/N | OW1蓄油池水位警報1 WPF |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.洩油池警報(1) | 洩油池水位警報(1) | OTHER | [5 empty] | 714 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | StaDev | 所內設施 |  | OilLeak2 |  |  | Status | 洩油池水位警報2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0871 |  |  | 1-36-07 |  |  | Locate Empty | A/N | OW2蓄油池水位警報2 WPA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.洩油池警報(2) | 洩油池水位警報(2) | OTHER | [5 empty] | 715 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0873 |  | 0126 | 1-36-09 |  | 1-7E | Locate Empty | USE/LOCK | 161KV NO.1 BUS 87B1S |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | [5 empty] | 716 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 161 | 161kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0874 |  | 0127 | 1-36-10 |  | 1-7F | Locate Empty | USE/LOCK | 161KV NO.2 BUS 87B2S |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | [5 empty] | 717 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0875 |  |  | 1-36-11 |  |  | 1500 | 測試/正常 | 1500CB 測試/正常 1500SA |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | [5 empty] | 718 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Test | Test | 1 |  |  | TEST/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1520 | 嘉義～仁愛海線(1520) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0876 |  |  | 1-36-12 |  |  | Locate Empty | A/N | 嘉義仁愛海線1520 87L通訊故障 87CFA |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1520_87CFA | 嘉義仁愛海線(1520)87RY通訊故障 | OTHER | [5 empty] | 719 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1520 | 嘉義～仁愛海線(1520) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0877 |  |  | 1-36-13 |  |  | Locate Empty | A/N | 嘉義仁愛海線1520 電驛故障 RYFA |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1520_RYFA | 嘉義仁愛海線(1520)數位電驛故障 | OTHER | [5 empty] | 720 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1510 | 嘉義～仁愛山線(1510) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0878 |  |  | 1-36-14 |  |  | Locate Empty | A/N | 嘉義仁愛山線 1510 87L通訊故障 87CFA |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1510_87CFA | 嘉義仁愛山線(1510)87RY通訊故障 | OTHER | [5 empty] | 721 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1510 | 嘉義～仁愛山線(1510) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0879 |  |  | 1-36-15 |  |  | Locate Empty | A/N | 嘉義仁愛山線 1510 電驛故障 RYFA |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1510_RYFA | 嘉義仁愛山線(1510)數位電驛故障 | OTHER | [5 empty] | 722 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1540 | 仁愛～北回二路(1540) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0880 |  |  | 1-37-00 |  |  | Locate Empty |  | 仁愛北回二路 (1540 87L通訊故障) 87CFA |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1540_87CFA | 仁愛北回二路(1540)87RY通訊故障 | OTHER | [5 empty] | 723 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1540 | 仁愛～北回二路(1540) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0881 |  |  | 1-37-01 |  |  | Locate Empty |  | 仁愛北回二路 (1540 電驛故障) RYFA |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1540_RYFA | 仁愛北回二路(1540)數位電驛故障 | OTHER | [5 empty] | 724 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1530 | 仁愛～北回一路(1530) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0882 |  |  | 1-37-02 |  |  | Locate Empty |  | 仁愛北回一路(1530 87L通訊故障) 87CFA |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1530_87CFA | 仁愛北回一路(1530)87RY通訊故障 | OTHER | [5 empty] | 725 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1530 | 仁愛～北回一路(1530) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0883 |  |  | 1-37-03 |  |  | Locate Empty |  | 仁愛北回一路(1530 電驛故障) RYFA |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1530_RYFA | 仁愛北回一路(1530)數位電驛故障 | OTHER | [5 empty] | 726 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | StaDev | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0896 |  |  | 1-38-00 |  |  | Locate Empty | A/N | 其他輕故障 PSF |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.其他輕故障 | 變電所內其他輕故障 | OTHER | [5 empty] | 727 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | StaDev | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0897 |  |  | 1-38-01 |  |  | Locate Empty | A/N | 其他重故障 PSA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.其他重故障 | 變電所內其他重故障 | OTHER | [5 empty] | 728 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0898 |  |  | 1-38-02 |  |  | Locate Empty | A/N | 通訊用充電機故障 CHG2 |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | [5 empty] | 729 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0899 |  |  | 1-38-03 |  |  | Locate Empty | A/N | 通訊設備AC故障 ACFA |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | [5 empty] | 730 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | StaDev | 所內設施 |  | R_Temp |  |  | Status | 溫度警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0902 |  |  | 1-38-06 |  |  | Locate Empty | A/N | 通信室溫控警報 |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.通信機房溫度 | 通信機房溫度警報 | OTHER | [5 empty] | 731 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | StaDev | 所內設施 |  | Lights3 | 嘉義區處路燈控制 |  | Status | 照明3 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0903 |  | 0001 | 1-38-07 |  | 1-01 | Locate Empty | CLOSE/OPEN | 嘉義區處路燈控制 |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.路燈照明 | 路燈控制 | OTHER | [5 empty] | 732 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
D12 | 仁愛DS | 0 |  | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0904 |  |  | 1-38-08 |  |  | OSCF | A/N | 161KV示波器缺紙或故障警報OSCF |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | [5 empty] | 733 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | ComPoint |  |  | GRZ100 |  |  | Status | 電驛GRZ100閉鎖 | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0905 |  |  | 1-38-09 |  |  | BVS盤 | LOCK/USE | 本所各GRZ100 Ry U/L |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.BVS_RY | BVS GRZ100 RY U/L | OTHER | [5 empty] | 734 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | LOCK/USE | USE
D12 | 仁愛DS | 161 | 161kV | ComPoint | BUS |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0910 |  |  | 1-38-14 |  |  | BUS | A/N | 161KV BUS數位電驛故障 |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | [5 empty] | 735 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | ComPoint | BUS |  | 87CTFA |  |  | Status | 87RY CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0911 |  |  | 1-38-15 |  |  | BUS | A/N | 161KV BUS 87RY CT 迴路故障 |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.161KV_BUS_CTFA | 161KV BUS 87RY CT回路故障 | OTHER | [5 empty] | 736 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1520 | 嘉義～仁愛海線(1520) |  | DS1 | 1521 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0912 | 913 | 0070 | 1-39-00 | 1-39-01 | 1-46 | 1521 | ON | 嘉義仁愛海線 (1521) DS-AS |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1521_DS | 1521(嘉義仁愛海線) DS | LINE161 | [5 empty] | 737 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D12 | 仁愛DS | 161 | 161kV | 1520 | 嘉義～仁愛海線(1520) |  | DS2 | 1522 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0914 | 915 | 0071 | 1-39-02 | 1-39-03 | 1-47 | 1522 | ON | 嘉義仁愛海線 (1522) DS-AS |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1522_DS | 1522(嘉義仁愛海線) DS | LINE161 | [5 empty] | 738 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1520 | 嘉義～仁愛海線(1520) |  | DS3 | 1523 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0916 | 917 | 0072 | 1-39-04 | 1-39-05 | 1-48 | 1523 | ON | 嘉義仁愛海線 (1523) DS-AS |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1523_DS | 1523(嘉義仁愛海線) DS | LINE161 | [5 empty] | 739 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1520 | 嘉義～仁愛海線(1520) |  | ES3 | 1523E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0918 | 919 | 0073 | 1-39-06 | 1-39-07 | 1-49 | 1523E | ON | 嘉義仁愛海線 (1523E) ES-AS |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1523E_ES | 1523E(嘉義仁愛海線) ES | LINE161 | [5 empty] | 740 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D12 | 仁愛DS | 161 | 161kV | 1510 | 嘉義～仁愛山線(1510) |  | DS1 | 1511 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0920 | 921 | 0074 | 1-39-08 | 1-39-09 | 1-4A | 1511 | ON | 嘉義仁愛山線 (1511) DS-AS |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1511_DS | 1511(嘉義仁愛山線) DS | LINE161 | [5 empty] | 741 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1510 | 嘉義～仁愛山線(1510) |  | DS2 | 1512 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0922 | 923 | 0075 | 1-39-10 | 1-39-11 | 1-4B | 1512 | ON | 嘉義仁愛山線 (1512) DS-AS |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1512_DS | 1512(嘉義仁愛山線) DS | LINE161 | [5 empty] | 742 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D12 | 仁愛DS | 161 | 161kV | 1510 | 嘉義～仁愛山線(1510) |  | DS3 | 1513 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0924 | 925 | 0076 | 1-39-12 | 1-39-13 | 1-4C | 1513 | ON | 嘉義仁愛山線 (1513) DS-AS |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1513_DS | 1513(嘉義仁愛山線) DS | LINE161 | [5 empty] | 743 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1510 | 嘉義～仁愛山線(1510) |  | ES3 | 1513E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0926 | 927 | 0077 | 1-39-14 | 1-39-15 | 1-4D | 1513E | ON | 嘉義仁愛山線 (1513E) ES-AS |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1513E_ES | 1513E(嘉義仁愛山線) ES | LINE161 | [5 empty] | 744 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D12 | 仁愛DS | 161 | 161kV | 1540 | 仁愛～北回二路(1540) |  | DS1 | 1541 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0928 | 929 | 0078 | 1-3A-00 | 1-3A-01 | 1-4E | 1541 | ON | 仁愛北回二路 (1541) DS-AS |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1541_DS | 1541(仁愛北回二路) DS | LINE161 | [5 empty] | 745 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D12 | 仁愛DS | 161 | 161kV | 1540 | 仁愛～北回二路(1540) |  | DS2 | 1542 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0930 | 931 | 0079 | 1-3A-02 | 1-3A-03 | 1-4F | 1542 | ON | 仁愛北回二路 (1542) DS-AS |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1542_DS | 1542(仁愛北回二路) DS | LINE161 | [5 empty] | 746 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1540 | 仁愛～北回二路(1540) |  | DS3 | 1543 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0932 | 933 | 0080 | 1-3A-04 | 1-3A-05 | 1-50 | 1543 | ON | 仁愛北回二路 (1543) DS-AS |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1543_DS | 1543(仁愛北回二路) DS | LINE161 | [5 empty] | 747 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1540 | 仁愛～北回二路(1540) |  | ES3 | 1543E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0934 | 935 | 0081 | 1-3A-06 | 1-3A-07 | 1-51 | 1543E | ON | 仁愛北回二路 (1543E) ES-AS |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1543E_ES | 1543E(仁愛北回二路) ES | LINE161 | [5 empty] | 748 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D12 | 仁愛DS | 161 | 161kV | 1530 | 仁愛～北回一路(1530) |  | DS1 | 1531 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0936 | 937 | 0082 | 1-3A-08 | 1-3A-09 | 1-52 | 1531 | ON | 仁愛北回一路(1531) DS-AS |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1531_DS | 1531(仁愛北回一路) DS | LINE161 | [5 empty] | 749 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1530 | 仁愛～北回一路(1530) |  | DS2 | 1532 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0938 | 939 | 0083 | 1-3A-10 | 1-3A-11 | 1-53 | 1532 | ON | 仁愛北回一路(1532) DS-AS |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1532_DS | 1532(仁愛北回一路) DS | LINE161 | [5 empty] | 750 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D12 | 仁愛DS | 161 | 161kV | 1530 | 仁愛～北回一路(1530) |  | DS3 | 1533 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0940 | 941 | 0084 | 1-3A-12 | 1-3A-13 | 1-54 | 1533 | ON | 仁愛北回一路(1533) DS-AS |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1533_DS | 1533(仁愛北回一路) DS | LINE161 | [5 empty] | 751 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1530 | 仁愛～北回一路(1530) |  | ES3 | 1533E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0942 | 943 | 0085 | 1-3A-14 | 1-3A-15 | 1-55 | 1533E | ON | 仁愛北回一路(1533E) ES-AS |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1533E_ES | 1533E(仁愛北回一路) ES | LINE161 | [5 empty] | 752 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D12 | 仁愛DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0992 | 993 | 0110 | 1-3E-00 | 1-3E-01 | 1-6E | 1501 | ON | 161KV TIE (1501) DS-AS |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1501_DS | 1501(TIE) DS | TIE | [5 empty] | 753 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0994 | 995 | 0111 | 1-3E-02 | 1-3E-03 | 1-6F | 1502 | ON | 161KV TIE (1502) DS-AS |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1502_DS | 1502(TIE) DS | TIE | [5 empty] | 754 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0996 | 997 | 0112 | 1-3E-04 | 1-3E-05 | 1-70 | Locate Empty | ON | NO.1 DTR(1751) DS-AS |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1751_DS | 1751(#1DTR) DS | MTR | [5 empty] | 755 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0998 | 999 | 0113 | 1-3E-06 | 1-3E-07 | 1-71 | Locate Empty | ON | NO.1 DTR(1752) DS-AS |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1752_DS | 1752(#1DTR) DS | MTR | [5 empty] | 756 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D12 | 仁愛DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1000 | 1001 | 0114 | 1-3E-08 | 1-3E-09 | 1-72 | Locate Empty | ON | NO.2 DTR(1761) DS-AS |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1761_DS | 1761(#2DTR) DS | MTR | [5 empty] | 757 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D12 | 仁愛DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1002 | 1003 | 0115 | 1-3E-10 | 1-3E-11 | 1-73 | Locate Empty | ON | NO.2 DTR(1762) DS-AS |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1762_DS | 1762(#2DTR) DS | MTR | [5 empty] | 758 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1004 | 1005 | 0116 | 1-3E-12 | 1-3E-13 | 1-74 | Locate Empty | ON | NO.3 DTR(1771) DS-AS |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1771_DS | 1771(#3DTR) DS | MTR | [5 empty] | 759 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1006 | 1007 | 0117 | 1-3E-14 | 1-3E-15 | 1-75 | Locate Empty | ON | NO.3 DTR(1772) DS-AS |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1772_DS | 1772(#3DTR) DS | MTR | [5 empty] | 760 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D12 | 仁愛DS | 161 | 161kV | 1780 | #4DTR(1780) |  | DS1 | 1781 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1008 | 1009 | 0118 | 1-3F-00 | 1-3F-01 | 1-76 | Locate Empty | ON | NO.4 DTR(1781) DS-AS |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1781_DS | 1781(#4DTR) DS | MTR | [5 empty] | 761 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D12 | 仁愛DS | 161 | 161kV | 1780 | #4DTR(1780) |  | DS2 | 1782 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1010 | 1011 | 0119 | 1-3F-02 | 1-3F-03 | 1-77 | Locate Empty | ON | NO.4 DTR(1782) DS-AS |  |  | B2/D12_A1 | [8 empty] | 仁愛DS.1782_DS | 1782(#4DTR) DS | MTR | [5 empty] | 762 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 11 | 11kV | B1SC | #1DTR(1A)(1SC) |  | LBS |  | Element | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/210 | C/1SC(B) |  |  | 1012 | 1013 | 0120 | 1-3F-04 | 1-3F-05 | 1-78 | Locate Empty | ON | SC1A LBS LBS-AS |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.210_LBS | 210(11KV #1SC) LBS | SC | [5 empty] | 763 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 11 | 11kV | B2SC | #1DTR(1B)(2SC) |  | LBS |  | Element | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/220 | C/2SC(B) |  |  | 1014 | 1015 | 0121 | 1-3F-06 | 1-3F-07 | 1-79 | Locate Empty | ON | SC1B LBS LBS-AS |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.220_LBS | 220(11KV #2SC) LBS | SC | [5 empty] | 764 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 11 | 11kV | B3SC | #2DTR(2A)(3SC) |  | LBS |  | Element | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/230 | C/3SC(B) |  |  | 1016 | 1017 | 0122 | 1-3F-08 | 1-3F-09 | 1-7A | Locate Empty | ON | SC2A LBS LBS-AS |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.230_LBS | 230(11KV #3SC) LBS | SC | [5 empty] | 765 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 11 | 11kV | B4SC | #2DTR(2B)(4SC) |  | LBS |  | Element | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/240 | C/4SC(B) |  |  | 1018 | 1019 | 0123 | 1-3F-10 | 1-3F-11 | 1-7B | Locate Empty | ON | SC2B LBS LBS-AS |  |  | B3/D12_A1 | [8 empty] | 仁愛DS.240_LBS | 240(11KV #4SC) LBS | SC | [5 empty] | 766 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA21 | 愛21線(JA21) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1152 |  | 0174 | 2-38-00 |  | 2-2E | F1 | USE/LOCK | 愛21線 JA21 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA21_79UL | 11KV愛21線(JA21) 79RY U/L | FEEDER | [5 empty] | 767 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA21 | 愛21線(JA21) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1153 |  | 0175 | 2-38-01 |  | 2-2F | F1 | USE/LOCK | 愛21線 JA21 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA21_LCO_TAP | 11KV愛21線(JA21) LCO TAP | FEEDER | [5 empty] | 768 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA22 | 愛22線(JA22) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1154 |  | 0176 | 2-38-02 |  | 2-30 | F2 | USE/LOCK | 愛22線 JA22 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA22_79UL | 11KV愛22線(JA22) 79RY U/L | FEEDER | [5 empty] | 769 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA22 | 愛22線(JA22) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1155 |  | 0177 | 2-38-03 |  | 2-31 | F2 | USE/LOCK | 愛22線 JA22 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA22_LCO_TAP | 11KV愛22線(JA22) LCO TAP | FEEDER | [5 empty] | 770 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA23 | 愛23線(JA23) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1156 |  | 0178 | 2-38-04 |  | 2-32 | F3 | USE/LOCK | 愛23線 JA23 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA23_79UL | 11KV愛23線(JA23) 79RY U/L | FEEDER | [5 empty] | 771 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA23 | 愛23線(JA23) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1157 |  | 0179 | 2-38-05 |  | 2-33 | F3 | USE/LOCK | 愛23線 JA23 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA23_LCO_TAP | 11KV愛23線(JA23) LCO TAP | FEEDER | [5 empty] | 772 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA24 | 愛24線(JA24) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1158 |  | 0180 | 2-38-06 |  | 2-34 | F4 | USE/LOCK | 愛24線 JA24 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA24_79UL | 11KV愛24線(JA24) 79RY U/L | FEEDER | [5 empty] | 773 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA24 | 愛24線(JA24) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1159 |  | 0181 | 2-38-07 |  | 2-35 | F4 | USE/LOCK | 愛24線 JA24 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA24_LCO_TAP | 11KV愛24線(JA24) LCO TAP | FEEDER | [5 empty] | 774 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA25 | 愛25線(JA25) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1160 |  | 0182 | 2-38-08 |  | 2-36 | F5 | USE/LOCK | 愛25線 JA25 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA25_79UL | 11KV愛25線(JA25) 79RY U/L | FEEDER | [5 empty] | 775 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA25 | 愛25線(JA25) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1161 |  | 0183 | 2-38-09 |  | 2-37 | F5 | USE/LOCK | 愛25線 JA25 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA25_LCO_TAP | 11KV愛25線(JA25) LCO TAP | FEEDER | [5 empty] | 776 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA26 | 愛26線(JA26) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1162 |  | 0184 | 2-38-10 |  | 2-38 | F6 | USE/LOCK | 愛26線 JA26 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA26_79UL | 11KV愛26線(JA26) 79RY U/L | FEEDER | [5 empty] | 777 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA26 | 愛26線(JA26) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1163 |  | 0185 | 2-38-11 |  | 2-39 | F6 | USE/LOCK | 愛26線 JA26 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA26_LCO_TAP | 11KV愛26線(JA26) LCO TAP | FEEDER | [5 empty] | 778 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA27 | 愛27線(JA27) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1164 |  | 0186 | 2-38-12 |  | 2-3A | F7 | USE/LOCK | 愛27線 JA27 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA27_79UL | 11KV愛27線(JA27) 79RY U/L | FEEDER | [5 empty] | 779 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA27 | 愛27線(JA27) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1165 |  | 0187 | 2-38-13 |  | 2-3B | F7 | USE/LOCK | 愛27線 JA27 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA27_LCO_TAP | 11KV愛27線(JA27) LCO TAP | FEEDER | [5 empty] | 780 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA28 | 愛28線(JA28) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1166 |  | 0188 | 2-38-14 |  | 2-3C | F8 | USE/LOCK | 愛28線 JA28 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA28_79UL | 11KV愛28線(JA28) 79RY U/L | FEEDER | [5 empty] | 781 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA28 | 愛28線(JA28) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1167 |  | 0189 | 2-38-15 |  | 2-3D | F8 | USE/LOCK | 愛28線 JA28 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA28_LCO_TAP | 11KV愛28線(JA28) LCO TAP | FEEDER | [5 empty] | 782 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA29 | 愛29線(JA29) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1168 |  | 0190 | 2-39-00 |  | 2-3E | F9 | USE/LOCK | 愛29線 JA29 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA29_79UL | 11KV愛29線(JA29) 79RY U/L | FEEDER | [5 empty] | 783 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA29 | 愛29線(JA29) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1169 |  | 0191 | 2-39-01 |  | 2-3F | F9 | USE/LOCK | 愛29線 JA29 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA29_LCO_TAP | 11KV愛29線(JA29) LCO TAP | FEEDER | [5 empty] | 784 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA30 | 愛30線(JA30) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1170 |  | 0192 | 2-39-02 |  | 2-40 | F10 | USE/LOCK | 愛30線 JA30 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA30_79UL | 11KV愛30線(JA30) 79RY U/L | FEEDER | [5 empty] | 785 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA30 | 愛30線(JA30) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1171 |  | 0193 | 2-39-03 |  | 2-41 | F10 | USE/LOCK | 愛30線 JA30 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA30_LCO_TAP | 11KV愛30線(JA30) LCO TAP | FEEDER | [5 empty] | 786 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA31 | 愛31線(JA31) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1172 |  | 0194 | 2-39-04 |  | 2-42 | F11 | USE/LOCK | 愛31線 JA31 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA31_79UL | 11KV愛31線(JA31) 79RY U/L | FEEDER | [5 empty] | 787 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA31 | 愛31線(JA31) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1173 |  | 0195 | 2-39-05 |  | 2-43 | F11 | USE/LOCK | 愛31線 JA31 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA31_LCO_TAP | 11KV愛31線(JA31) LCO TAP | FEEDER | [5 empty] | 788 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA32 | 愛32線(JA32) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1174 |  | 0196 | 2-39-06 |  | 2-44 | F12 | USE/LOCK | 愛32線 JA32 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA32_79UL | 11KV愛32線(JA32) 79RY U/L | FEEDER | [5 empty] | 789 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA32 | 愛32線(JA32) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1175 |  | 0197 | 2-39-07 |  | 2-45 | F12 | USE/LOCK | 愛32線 JA32 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA32_LCO_TAP | 11KV愛32線(JA32) LCO TAP | FEEDER | [5 empty] | 790 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA33 | 愛33線(JA33) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1176 |  | 0198 | 2-39-08 |  | 2-46 | F13 | USE/LOCK | 愛33線 JA33 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA33_79UL | 11KV愛33線(JA33) 79RY U/L | FEEDER | [5 empty] | 791 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA33 | 愛33線(JA33) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1177 |  | 0199 | 2-39-09 |  | 2-47 | F13 | USE/LOCK | 愛33線 JA33 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA33_LCO_TAP | 11KV愛33線(JA33) LCO TAP | FEEDER | [5 empty] | 792 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA34 | 愛34線(JA34) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1178 |  | 0200 | 2-39-10 |  | 2-48 | F14 | USE/LOCK | 愛34線 JA34 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA34_79UL | 11KV愛34線(JA34) 79RY U/L | FEEDER | [5 empty] | 793 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA34 | 愛34線(JA34) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1179 |  | 0201 | 2-39-11 |  | 2-49 | F14 | USE/LOCK | 愛34線 JA34 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA34_LCO_TAP | 11KV愛34線(JA34) LCO TAP | FEEDER | [5 empty] | 794 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA35 | 愛35線(JA35) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1180 |  | 0202 | 2-39-12 |  | 2-4A | F15 | USE/LOCK | 愛35線 JA35 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA35_79UL | 11KV愛35線(JA35) 79RY U/L | FEEDER | [5 empty] | 795 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA35 | 愛35線(JA35) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1181 |  | 0203 | 2-39-13 |  | 2-4B | F15 | USE/LOCK | 愛35線 JA35 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA35_LCO_TAP | 11KV愛35線(JA35) LCO TAP | FEEDER | [5 empty] | 796 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA36 | 愛36線(JA36) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1182 |  | 0204 | 2-39-14 |  | 2-4C | F16 | USE/LOCK | 愛36線 JA36 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA36_79UL | 11KV愛36線(JA36) 79RY U/L | FEEDER | [5 empty] | 797 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA36 | 愛36線(JA36) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1183 |  | 0205 | 2-39-15 |  | 2-4D | F16 | USE/LOCK | 愛36線 JA36 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA36_LCO_TAP | 11KV愛36線(JA36) LCO TAP | FEEDER | [5 empty] | 798 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA37 | 愛37線(JA37) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1184 |  | 0206 | 2-3A-00 |  | 2-4E | F17 | USE/LOCK | 愛37線 JA37 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA37_79UL | 11KV愛37線(JA37) 79RY U/L | FEEDER | [5 empty] | 799 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA37 | 愛37線(JA37) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1185 |  | 0207 | 2-3A-01 |  | 2-4F | F17 | USE/LOCK | 愛37線 JA37 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA37_LCO_TAP | 11KV愛37線(JA37) LCO TAP | FEEDER | [5 empty] | 800 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA38 | 愛38線(JA38) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1186 |  | 0208 | 2-3A-02 |  | 2-50 | F18 | USE/LOCK | 愛38線 JA38 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA38_79UL | 11KV愛38線(JA38) 79RY U/L | FEEDER | [5 empty] | 801 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA38 | 愛38線(JA38) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1187 |  | 0209 | 2-3A-03 |  | 2-51 | F18 | USE/LOCK | 愛38線 JA38 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA38_LCO_TAP | 11KV愛38線(JA38) LCO TAP | FEEDER | [5 empty] | 802 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA39 | 愛39線(JA39) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1188 |  | 0210 | 2-3A-04 |  | 2-52 | F19 | USE/LOCK | 愛39線 JA39 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA39_79UL | 11KV愛39線(JA39) 79RY U/L | FEEDER | [5 empty] | 803 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA39 | 愛39線(JA39) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1189 |  | 0211 | 2-3A-05 |  | 2-53 | F19 | USE/LOCK | 愛39線 JA39 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA39_LCO_TAP | 11KV愛39線(JA39) LCO TAP | FEEDER | [5 empty] | 804 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA40 | 愛40線(JA40) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1190 |  | 0212 | 2-3A-06 |  | 2-54 | F20 | USE/LOCK | 愛40線 JA40 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA40_79UL | 11KV愛40線(JA40) 79RY U/L | FEEDER | [5 empty] | 805 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA40 | 愛40線(JA40) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1191 |  | 0213 | 2-3A-07 |  | 2-55 | F20 | USE/LOCK | 愛40線 JA40 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA40_LCO_TAP | 11KV愛40線(JA40) LCO TAP | FEEDER | [5 empty] | 806 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 22 | 22kV | JA71 | 愛71線(JA71) |  | FDR_RCA |  | B2 | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1192 |  | 0214 | 2-3A-08 |  | 2-56 | F21 | USE/LOCK | 愛71線 JA71 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA71_79UL | 23KV愛71線(JA71) 79RY U/L | FEEDER | [5 empty] | 807 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 22 | 22kV | JA71 | 愛71線(JA71) |  | 51NA |  | B2 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1193 |  | 0215 | 2-3A-09 |  | 2-57 | F21 | USE/LOCK | 愛71線 JA71 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA71_LCO_TAP | 23KV愛71線(JA71) LCO TAP | FEEDER | [5 empty] | 808 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 22 | 22kV | JA72 | 愛72線(JA72) |  | FDR_RCA |  | B2 | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1194 |  | 0216 | 2-3A-10 |  | 2-58 | F22 | USE/LOCK | 愛72線 JA72 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA72_79UL | 23KV愛72線(JA72) 79RY U/L | FEEDER | [5 empty] | 809 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 22 | 22kV | JA72 | 愛72線(JA72) |  | 51NA |  | B2 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1195 |  | 0217 | 2-3A-11 |  | 2-59 | F22 | USE/LOCK | 愛72線 JA72 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA72_LCO_TAP | 23KV愛72線(JA72) LCO TAP | FEEDER | [5 empty] | 810 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 22 | 22kV | JA73 | 愛73線(JA73) |  | FDR_RCA |  | B2 | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1196 |  | 0218 | 2-3A-12 |  | 2-5A | F23 | USE/LOCK | 愛73線 JA73 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA73_79UL | 23KV愛73線(JA73) 79RY U/L | FEEDER | [5 empty] | 811 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 22 | 22kV | JA73 | 愛73線(JA73) |  | 51NA |  | B2 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1197 |  | 0219 | 2-3A-13 |  | 2-5B | F23 | USE/LOCK | 愛73線 JA73 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA73_LCO_TAP | 23KV愛73線(JA73) LCO TAP | FEEDER | [5 empty] | 812 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 22 | 22kV | JA74 | 愛74線(JA74) |  | FDR_RCA |  | B2 | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1198 |  | 0220 | 2-3A-14 |  | 2-5C | F24 | USE/LOCK | 愛74線 JA74 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA74_79UL | 23KV愛74線(JA74) 79RY U/L | FEEDER | [5 empty] | 813 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 22 | 22kV | JA74 | 愛74線(JA74) |  | 51NA |  | B2 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1199 |  | 0221 | 2-3A-15 |  | 2-5D | F24 | USE/LOCK | 愛74線 JA74 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA74_LCO_TAP | 23KV愛74線(JA74) LCO TAP | FEEDER | [5 empty] | 814 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 22 | 22kV | JA75 | 愛75線(JA75) |  | FDR_RCA |  | B2 | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1200 |  | 0222 | 2-3B-00 |  | 2-5E | F25 | USE/LOCK | 愛75線 JA75 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA75_79UL | 23KV愛75線(JA75) 79RY U/L | FEEDER | [5 empty] | 815 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 22 | 22kV | JA75 | 愛75線(JA75) |  | 51NA |  | B2 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1201 |  | 0223 | 2-3B-01 |  | 2-5F | F25 | USE/LOCK | 愛75線 JA75 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA75_LCO_TAP | 23KV愛75線(JA75) LCO TAP | FEEDER | [5 empty] | 816 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 22 | 22kV | JA76 | 愛76線(JA76) |  | FDR_RCA |  | B2 | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1202 |  | 0224 | 2-3B-02 |  | 2-60 | F26 | USE/LOCK | 愛76線 JA76 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA76_79UL | 23KV愛76線(JA76) 79RY U/L | FEEDER | [5 empty] | 817 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 22 | 22kV | JA76 | 愛76線(JA76) |  | 51NA |  | B2 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1203 |  | 0225 | 2-3B-03 |  | 2-61 | F26 | USE/LOCK | 愛76線 JA76 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA76_LCO_TAP | 23KV愛76線(JA76) LCO TAP | FEEDER | [5 empty] | 818 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 22 | 22kV | JA77 | 愛77線(JA77) |  | FDR_RCA |  | B2 | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1204 |  | 0226 | 2-3B-04 |  | 2-62 | F27 | USE/LOCK | 愛77線 JA77 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA77_79UL | 23KV愛77線(JA77) 79RY U/L | FEEDER | [5 empty] | 819 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 22 | 22kV | JA77 | 愛77線(JA77) |  | 51NA |  | B2 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1205 |  | 0227 | 2-3B-05 |  | 2-63 | F27 | USE/LOCK | 愛77線 JA77 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA77_LCO_TAP | 23KV愛77線(JA77) LCO TAP | FEEDER | [5 empty] | 820 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 22 | 22kV | JA78 | 愛78線(JA78) |  | FDR_RCA |  | B2 | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1206 |  | 0228 | 2-3B-06 |  | 2-64 | F28 | USE/LOCK | 愛78線 JA78 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA78_79UL | 23KV愛78線(JA78) 79RY U/L | FEEDER | [5 empty] | 821 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 22 | 22kV | JA78 | 愛78線(JA78) |  | 51NA |  | B2 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1207 |  | 0229 | 2-3B-07 |  | 2-65 | F28 | USE/LOCK | 愛78線 JA78 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA78_LCO_TAP | 23KV愛78線(JA78) LCO TAP | FEEDER | [5 empty] | 822 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 22 | 22kV | JA5A | 愛5A線(JA5A) |  | FDR_RCA |  | B2 | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1208 |  | 0230 | 2-3B-08 |  | 2-66 | F29 | USE/LOCK | 愛5A線 JA5A 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA5A_79UL | 23KV愛5A線(JA5A) 79RY U/L | FEEDER | [5 empty] | 823 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 22 | 22kV | JA5A | 愛5A線(JA5A) |  | 51NA |  | B2 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1209 |  | 0231 | 2-3B-09 |  | 2-67 | F29 | USE/LOCK | 愛5A線 JA5A 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA5A_LCO_TAP | 23KV愛5A線(JA5A) LCO TAP | FEEDER | [5 empty] | 824 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 22 | 22kV | JA5B | 愛5B線(JA5B) |  | FDR_RCA |  | B2 | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1210 |  | 0232 | 2-3B-10 |  | 2-68 | F30 | USE/LOCK | 愛5B線 JA5B 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA5B_79UL | 23KV愛5B線(JA5B) 79RY U/L | FEEDER | [5 empty] | 825 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 22 | 22kV | JA5B | 愛5B線(JA5B) |  | 51NA |  | B2 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1211 |  | 0233 | 2-3B-11 |  | 2-69 | F30 | USE/LOCK | 愛5B線 JA5B 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA5B_LCO_TAP | 23KV愛5B線(JA5B) LCO TAP | FEEDER | [5 empty] | 826 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 22 | 22kV | JA5C | 愛5C線(JA5C) |  | FDR_RCA |  | B2 | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1212 |  | 0234 | 2-3B-12 |  | 2-6A | F31 | USE/LOCK | 愛5C線 JA5C 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA5C_79UL | 23KV愛5C線(JA5C) 79RY U/L | FEEDER | [5 empty] | 827 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 22 | 22kV | JA5C | 愛5C線(JA5C) |  | 51NA |  | B2 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1213 |  | 0235 | 2-3B-13 |  | 2-6B | F31 | USE/LOCK | 愛5C線 JA5C 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA5C_LCO_TAP | 23KV愛5C線(JA5C) LCO TAP | FEEDER | [5 empty] | 828 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 22 | 22kV | JA5D | 愛5D線(JA5D) |  | FDR_RCA |  | B2 | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1214 |  | 0236 | 2-3B-14 |  | 2-6C | F32 | USE/LOCK | 愛5D線 JA5D 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA5D_79UL | 23KV愛5D線(JA5D) 79RY U/L | FEEDER | [5 empty] | 829 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 22 | 22kV | JA5D | 愛5D線(JA5D) |  | 51NA |  | B2 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1215 |  | 0237 | 2-3B-15 |  | 2-6D | F32 | USE/LOCK | 愛5D線 JA5D 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA5D_LCO_TAP | 23KV愛5D線(JA5D) LCO TAP | FEEDER | [5 empty] | 830 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 22 | 22kV | JA5F | 愛5F線(JA5F) |  | FDR_RCA |  | B2 | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1216 |  | 0238 | 2-3C-00 |  | 2-6E | F33 | USE/LOCK | 愛5F線 JA5F 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA5F_79UL | 23KV愛5F線(JA5F) 79RY U/L | FEEDER | [5 empty] | 831 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 22 | 22kV | JA5F | 愛5F線(JA5F) |  | 51NA |  | B2 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1217 |  | 0239 | 2-3C-01 |  | 2-6F | F33 | USE/LOCK | 愛5F線 JA5F 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA5F_LCO_TAP | 23KV愛5F線(JA5F) LCO TAP | FEEDER | [5 empty] | 832 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 22 | 22kV | JA5G | 愛5G線(JA5G) |  | FDR_RCA |  | B2 | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1218 |  | 0240 | 2-3C-02 |  | 2-70 | F34 | USE/LOCK | 愛5G線 JA5G 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA5G_79UL | 23KV愛5G線(JA5G) 79RY U/L | FEEDER | [5 empty] | 833 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 22 | 22kV | JA5G | 愛5G線(JA5G) |  | 51NA |  | B2 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1219 |  | 0241 | 2-3C-03 |  | 2-71 | F34 | USE/LOCK | 愛5G線 JA5G 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA5G_LCO_TAP | 23KV愛5G線(JA5G) LCO TAP | FEEDER | [5 empty] | 834 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 22 | 22kV | JA5H | 愛5H線(JA5H) |  | FDR_RCA |  | B2 | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1220 |  | 0242 | 2-3C-04 |  | 2-72 | F35 | USE/LOCK | 愛5H線 JA5H 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA5H_79UL | 23KV愛5H線(JA5H) 79RY U/L | FEEDER | [5 empty] | 835 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 22 | 22kV | JA5H | 愛5H線(JA5H) |  | 51NA |  | B2 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1221 |  | 0243 | 2-3C-05 |  | 2-73 | F35 | USE/LOCK | 愛5H線 JA5H 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA5H_LCO_TAP | 23KV愛5H線(JA5H) LCO TAP | FEEDER | [5 empty] | 836 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D12 | 仁愛DS | 22 | 22kV | JA5K | 愛5K線(JA5K) |  | FDR_RCA |  | B2 | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1222 |  | 0244 | 2-3C-06 |  | 2-74 | F36 | USE/LOCK | 愛5K線 JA5K 79 RY 79S |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA5K_79UL | 23KV愛5K線(JA5K) 79RY U/L | FEEDER | [5 empty] | 837 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D12 | 仁愛DS | 22 | 22kV | JA5K | 愛5K線(JA5K) |  | 51NA |  | B2 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1223 |  | 0245 | 2-3C-07 |  | 2-75 | F36 | USE/LOCK | 愛5K線 JA5K 51N TAP 51NS |  |  | B2/D12_D1 | [8 empty] | 仁愛DS.JA5K_LCO_TAP | 23KV愛5K線(JA5K) LCO TAP | FEEDER | [5 empty] | 838 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
D12 | 仁愛DS | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/D12_A1 | [12 empty] | 仁愛DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: D12/161/1BUS/V; OPRD2: D12/161/2BUS/V
D12 | 仁愛DS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/D12_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: D12/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
D12 | 仁愛DS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/D12_A1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_4 | OPRD1: D12/161/1510/MW; OPRD2: D12/161/1520/MW; OPRD3: D12/161/1530/MW; OPRD4: D12/161/1540/MW
D12 | 仁愛DS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/D12_A1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: D12/0/CalcPoint/OPRN2_MW
D12 | 仁愛DS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/D12_A1 | [17 empty] | none
D12 | 仁愛DS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/D12_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: D12/0/CalcPoint/OPRN1; OPRD2: D12/0/CalcPoint/OPRN2; OPRD3: D12/0/CalcPoint/PRFL_UL
D12 | 仁愛DS |  |  | 1DTR | 1DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D12_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D12/11/310/I_R; OPRD2: D12/11/320/I_R
D12 | 仁愛DS |  |  | 1DTR | 1DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D12_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D12/11/310/I_S; OPRD2: D12/11/320/I_S
D12 | 仁愛DS |  |  | 1DTR | 1DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D12_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D12/11/310/I_T; OPRD2: D12/11/320/I_T
D12 | 仁愛DS |  |  | 2DTR | 2DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D12_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D12/11/330/I_R; OPRD2: D12/11/340/I_R
D12 | 仁愛DS |  |  | 2DTR | 2DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D12_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D12/11/330/I_S; OPRD2: D12/11/340/I_S
D12 | 仁愛DS |  |  | 2DTR | 2DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D12_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D12/11/330/I_T; OPRD2: D12/11/340/I_T
D12 | 仁愛DS | 161 | 161kV | 1510 | 嘉義～仁愛山線(1510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D12_A1 | [12 empty] | 仁愛DS.1510_AMP | 嘉義仁愛山線 AMP | LINE161 | AMP_CAL | C20R1790 | amp_cal | OPRD1: D12/161/1510/MW; OPRD2: D12/161/1510/MVAR; OPRD3: D12/0/CalcPoint/Vbs4
D12 | 仁愛DS | 161 | 161kV | 1520 | 嘉義～仁愛海線(1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D12_A1 | [12 empty] | 仁愛DS.1520_AMP | 嘉義仁愛海線 AMP | LINE161 | AMP_CAL | C20R1790 | amp_cal | OPRD1: D12/161/1520/MW; OPRD2: D12/161/1520/MVAR; OPRD3: D12/0/CalcPoint/Vbs4
D12 | 仁愛DS | 161 | 161kV | 1530 | 仁愛～北回一路(1530) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D12_A1 | [12 empty] | 仁愛DS.1530_AMP | 仁愛北回一路 AMP | LINE161 | AMP_CAL | C20R1930 | amp_cal | OPRD1: D12/161/1530/MW; OPRD2: D12/161/1530/MVAR; OPRD3: D12/0/CalcPoint/Vbs4
D12 | 仁愛DS | 161 | 161kV | 1540 | 仁愛～北回二路(1540) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D12_A1 | [12 empty] | 仁愛DS.1540_AMP | 仁愛北回二路 AMP | LINE161 | AMP_CAL | C20R1930 | amp_cal | OPRD1: D12/161/1540/MW; OPRD2: D12/161/1540/MVAR; OPRD3: D12/0/CalcPoint/Vbs4
D12 | 仁愛DS | 11 | 11kV | 1ABUS | #1ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D12_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D12/11/1ABUS/V
D12 | 仁愛DS | 11 | 11kV | 1BBUS | #1BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D12_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D12/11/1BBUS/V
D12 | 仁愛DS | 11 | 11kV | 2ABUS | #2ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D12_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D12/11/2ABUS/V
D12 | 仁愛DS | 11 | 11kV | 2BBUS | #2BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D12_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D12/11/2BBUS/V
D12 | 仁愛DS | 11 | 11kV | 3BUS | #3BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D12_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D12/11/3BUS/V
D12 | 仁愛DS | 11 | 11kV | 4BUS | #4BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D12_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D12/11/4BUS/V
D12 | 仁愛DS |  |  | 1DTR(A) | #1DTR(A) |  | TR_PERM | [9 empty] | B1/D12_A1 | [12 empty] | 仁愛DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D12//1DTR(A)/SupLocal; OPRD2: D12//1DTR(A)/Tap Chan
D12 | 仁愛DS |  |  | 1DTR(B) | #1DTR(B) |  | TR_PERM | [9 empty] | B1/D12_A1 | [12 empty] | 仁愛DS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D12//1DTR(B)/SupLocal; OPRD2: D12//1DTR(B)/Tap Chan
D12 | 仁愛DS |  |  | 2DTR(A) | #2DTR(A) |  | TR_PERM | [9 empty] | B1/D12_A1 | [12 empty] | 仁愛DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D12//2DTR(A)/SupLocal; OPRD2: D12//2DTR(A)/Tap Chan
D12 | 仁愛DS |  |  | 2DTR(B) | #2DTR(B) |  | TR_PERM | [9 empty] | B1/D12_A1 | [12 empty] | 仁愛DS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D12//2DTR(B)/SupLocal; OPRD2: D12//2DTR(B)/Tap Chan
D12 | 仁愛DS |  |  | 3DTR | #3DTR |  | TR_PERM | [9 empty] | B1/D12_A1 | [12 empty] | 仁愛DS.#3DTR_PERM | #3DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D12//3DTR/SupLocal; OPRD2: D12//3DTR/Tap Chan
D12 | 仁愛DS |  |  | 4DTR | #4DTR |  | TR_PERM | [9 empty] | B1/D12_A1 | [12 empty] | 仁愛DS.#4DTR_PERM | #4DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D12//4DTR/SupLocal; OPRD2: D12//4DTR/Tap Chan
D12 | 仁愛DS | 11 | 11kV | JA21 | 愛21線(JA21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D12/11/1ABUS/V; OPRD2: D12/11/JA21/I_R; OPRD3: D12/11/JA21/I_S; OPRD4: D12/11/JA21/I_T
D12 | 仁愛DS | 11 | 11kV | JA22 | 愛22線(JA22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D12/11/1ABUS/V; OPRD2: D12/11/JA22/I_R; OPRD3: D12/11/JA22/I_S; OPRD4: D12/11/JA22/I_T
D12 | 仁愛DS | 11 | 11kV | JA23 | 愛23線(JA23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D12/11/1ABUS/V; OPRD2: D12/11/JA23/I_R; OPRD3: D12/11/JA23/I_S; OPRD4: D12/11/JA23/I_T
D12 | 仁愛DS | 11 | 11kV | JA24 | 愛24線(JA24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D12/11/1ABUS/V; OPRD2: D12/11/JA24/I_R; OPRD3: D12/11/JA24/I_S; OPRD4: D12/11/JA24/I_T
D12 | 仁愛DS | 11 | 11kV | JA25 | 愛25線(JA25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D12/11/1ABUS/V; OPRD2: D12/11/JA25/I_R; OPRD3: D12/11/JA25/I_S; OPRD4: D12/11/JA25/I_T
D12 | 仁愛DS | 11 | 11kV | JA26 | 愛26線(JA26) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D12/11/1BBUS/V; OPRD2: D12/11/JA26/I_R; OPRD3: D12/11/JA26/I_S; OPRD4: D12/11/JA26/I_T
D12 | 仁愛DS | 11 | 11kV | JA27 | 愛27線(JA27) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D12/11/1BBUS/V; OPRD2: D12/11/JA27/I_R; OPRD3: D12/11/JA27/I_S; OPRD4: D12/11/JA27/I_T
D12 | 仁愛DS | 11 | 11kV | JA28 | 愛28線(JA28) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D12/11/1BBUS/V; OPRD2: D12/11/JA28/I_R; OPRD3: D12/11/JA28/I_S; OPRD4: D12/11/JA28/I_T
D12 | 仁愛DS | 11 | 11kV | JA29 | 愛29線(JA29) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D12/11/1BBUS/V; OPRD2: D12/11/JA29/I_R; OPRD3: D12/11/JA29/I_S; OPRD4: D12/11/JA29/I_T
D12 | 仁愛DS | 11 | 11kV | JA30 | 愛30線(JA30) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D12/11/1BBUS/V; OPRD2: D12/11/JA30/I_R; OPRD3: D12/11/JA30/I_S; OPRD4: D12/11/JA30/I_T
D12 | 仁愛DS | 11 | 11kV | JA31 | 愛31線(JA31) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D12/11/2ABUS/V; OPRD2: D12/11/JA31/I_R; OPRD3: D12/11/JA31/I_S; OPRD4: D12/11/JA31/I_T
D12 | 仁愛DS | 11 | 11kV | JA32 | 愛32線(JA32) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D12/11/2ABUS/V; OPRD2: D12/11/JA32/I_R; OPRD3: D12/11/JA32/I_S; OPRD4: D12/11/JA32/I_T
D12 | 仁愛DS | 11 | 11kV | JA33 | 愛33線(JA33) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D12/11/2ABUS/V; OPRD2: D12/11/JA33/I_R; OPRD3: D12/11/JA33/I_S; OPRD4: D12/11/JA33/I_T
D12 | 仁愛DS | 11 | 11kV | JA34 | 愛34線(JA34) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D12/11/2ABUS/V; OPRD2: D12/11/JA34/I_R; OPRD3: D12/11/JA34/I_S; OPRD4: D12/11/JA34/I_T
D12 | 仁愛DS | 11 | 11kV | JA35 | 愛35線(JA35) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D12/11/2ABUS/V; OPRD2: D12/11/JA35/I_R; OPRD3: D12/11/JA35/I_S; OPRD4: D12/11/JA35/I_T
D12 | 仁愛DS | 11 | 11kV | JA36 | 愛36線(JA36) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D12/11/2BBUS/V; OPRD2: D12/11/JA36/I_R; OPRD3: D12/11/JA36/I_S; OPRD4: D12/11/JA36/I_T
D12 | 仁愛DS | 11 | 11kV | JA37 | 愛37線(JA37) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D12/11/2BBUS/V; OPRD2: D12/11/JA37/I_R; OPRD3: D12/11/JA37/I_S; OPRD4: D12/11/JA37/I_T
D12 | 仁愛DS | 11 | 11kV | JA38 | 愛38線(JA38) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D12/11/2BBUS/V; OPRD2: D12/11/JA38/I_R; OPRD3: D12/11/JA38/I_S; OPRD4: D12/11/JA38/I_T
D12 | 仁愛DS | 11 | 11kV | JA39 | 愛39線(JA39) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D12/11/2BBUS/V; OPRD2: D12/11/JA39/I_R; OPRD3: D12/11/JA39/I_S; OPRD4: D12/11/JA39/I_T
D12 | 仁愛DS | 11 | 11kV | JA40 | 愛40線(JA40) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D12/11/2BBUS/V; OPRD2: D12/11/JA40/I_R; OPRD3: D12/11/JA40/I_S; OPRD4: D12/11/JA40/I_T
D12 | 仁愛DS | 22 | 22kV | JA5A | 愛5A線(JA5A) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D12/22/JA5A/I_R; OPRD3: D12/22/JA5A/I_S; OPRD4: D12/22/JA5A/I_T
D12 | 仁愛DS | 22 | 22kV | JA5B | 愛5B線(JA5B) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D12/22/JA5B/I_R; OPRD3: D12/22/JA5B/I_S; OPRD4: D12/22/JA5B/I_T
D12 | 仁愛DS | 22 | 22kV | JA5C | 愛5C線(JA5C) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D12/22/JA5C/I_R; OPRD3: D12/22/JA5C/I_S; OPRD4: D12/22/JA5C/I_T
D12 | 仁愛DS | 22 | 22kV | JA5D | 愛5D線(JA5D) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D12/22/JA5D/I_R; OPRD3: D12/22/JA5D/I_S; OPRD4: D12/22/JA5D/I_T
D12 | 仁愛DS | 22 | 22kV | JA5F | 愛5F線(JA5F) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D12/22/JA5F/I_R; OPRD3: D12/22/JA5F/I_S; OPRD4: D12/22/JA5F/I_T
D12 | 仁愛DS | 22 | 22kV | JA5G | 愛5G線(JA5G) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D12/22/JA5G/I_R; OPRD3: D12/22/JA5G/I_S; OPRD4: D12/22/JA5G/I_T
D12 | 仁愛DS | 22 | 22kV | JA5H | 愛5H線(JA5H) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D12/22/JA5H/I_R; OPRD3: D12/22/JA5H/I_S; OPRD4: D12/22/JA5H/I_T
D12 | 仁愛DS | 22 | 22kV | JA5K | 愛5K線(JA5K) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D12/22/JA5K/I_R; OPRD3: D12/22/JA5K/I_S; OPRD4: D12/22/JA5K/I_T
D12 | 仁愛DS | 22 | 22kV | JA71 | 愛71線(JA71) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D12/22/JA71/I_R; OPRD3: D12/22/JA71/I_S; OPRD4: D12/22/JA71/I_T
D12 | 仁愛DS | 22 | 22kV | JA72 | 愛72線(JA72) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D12/22/JA72/I_R; OPRD3: D12/22/JA72/I_S; OPRD4: D12/22/JA72/I_T
D12 | 仁愛DS | 22 | 22kV | JA73 | 愛73線(JA73) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D12/22/JA73/I_R; OPRD3: D12/22/JA73/I_S; OPRD4: D12/22/JA73/I_T
D12 | 仁愛DS | 22 | 22kV | JA74 | 愛74線(JA74) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D12/22/JA74/I_R; OPRD3: D12/22/JA74/I_S; OPRD4: D12/22/JA74/I_T
D12 | 仁愛DS | 22 | 22kV | JA75 | 愛75線(JA75) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D12/22/JA75/I_R; OPRD3: D12/22/JA75/I_S; OPRD4: D12/22/JA75/I_T
D12 | 仁愛DS | 22 | 22kV | JA76 | 愛76線(JA76) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D12/22/JA76/I_R; OPRD3: D12/22/JA76/I_S; OPRD4: D12/22/JA76/I_T
D12 | 仁愛DS | 22 | 22kV | JA77 | 愛77線(JA77) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D12/22/JA77/I_R; OPRD3: D12/22/JA77/I_S; OPRD4: D12/22/JA77/I_T
D12 | 仁愛DS | 22 | 22kV | JA78 | 愛78線(JA78) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D12/22/JA78/I_R; OPRD3: D12/22/JA78/I_S; OPRD4: D12/22/JA78/I_T
D12 | 仁愛DS | 11 | 11kV | JA21 | 愛21線(JA21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/11/JA21/kVA; OPRD2: D12/11/JA21/KVAR
D12 | 仁愛DS | 11 | 11kV | JA22 | 愛22線(JA22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/11/JA22/kVA; OPRD2: D12/11/JA22/KVAR
D12 | 仁愛DS | 11 | 11kV | JA23 | 愛23線(JA23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/11/JA23/kVA; OPRD2: D12/11/JA23/KVAR
D12 | 仁愛DS | 11 | 11kV | JA24 | 愛24線(JA24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/11/JA24/kVA; OPRD2: D12/11/JA24/KVAR
D12 | 仁愛DS | 11 | 11kV | JA25 | 愛25線(JA25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/11/JA25/kVA; OPRD2: D12/11/JA25/KVAR
D12 | 仁愛DS | 11 | 11kV | JA26 | 愛26線(JA26) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/11/JA26/kVA; OPRD2: D12/11/JA26/KVAR
D12 | 仁愛DS | 11 | 11kV | JA27 | 愛27線(JA27) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/11/JA27/kVA; OPRD2: D12/11/JA27/KVAR
D12 | 仁愛DS | 11 | 11kV | JA28 | 愛28線(JA28) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/11/JA28/kVA; OPRD2: D12/11/JA28/KVAR
D12 | 仁愛DS | 11 | 11kV | JA29 | 愛29線(JA29) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/11/JA29/kVA; OPRD2: D12/11/JA29/KVAR
D12 | 仁愛DS | 11 | 11kV | JA30 | 愛30線(JA30) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/11/JA30/kVA; OPRD2: D12/11/JA30/KVAR
D12 | 仁愛DS | 11 | 11kV | JA31 | 愛31線(JA31) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/11/JA31/kVA; OPRD2: D12/11/JA31/KVAR
D12 | 仁愛DS | 11 | 11kV | JA32 | 愛32線(JA32) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/11/JA32/kVA; OPRD2: D12/11/JA32/KVAR
D12 | 仁愛DS | 11 | 11kV | JA33 | 愛33線(JA33) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/11/JA33/kVA; OPRD2: D12/11/JA33/KVAR
D12 | 仁愛DS | 11 | 11kV | JA34 | 愛34線(JA34) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/11/JA34/kVA; OPRD2: D12/11/JA34/KVAR
D12 | 仁愛DS | 11 | 11kV | JA35 | 愛35線(JA35) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/11/JA35/kVA; OPRD2: D12/11/JA35/KVAR
D12 | 仁愛DS | 11 | 11kV | JA36 | 愛36線(JA36) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/11/JA36/kVA; OPRD2: D12/11/JA36/KVAR
D12 | 仁愛DS | 11 | 11kV | JA37 | 愛37線(JA37) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/11/JA37/kVA; OPRD2: D12/11/JA37/KVAR
D12 | 仁愛DS | 11 | 11kV | JA38 | 愛38線(JA38) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/11/JA38/kVA; OPRD2: D12/11/JA38/KVAR
D12 | 仁愛DS | 11 | 11kV | JA39 | 愛39線(JA39) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/11/JA39/kVA; OPRD2: D12/11/JA39/KVAR
D12 | 仁愛DS | 11 | 11kV | JA40 | 愛40線(JA40) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/11/JA40/kVA; OPRD2: D12/11/JA40/KVAR
D12 | 仁愛DS | 22 | 22kV | JA5A | 愛5A線(JA5A) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/22/JA5A/kVA; OPRD2: D12/22/JA5A/KVAR
D12 | 仁愛DS | 22 | 22kV | JA5B | 愛5B線(JA5B) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/22/JA5B/kVA; OPRD2: D12/22/JA5B/KVAR
D12 | 仁愛DS | 22 | 22kV | JA5C | 愛5C線(JA5C) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/22/JA5C/kVA; OPRD2: D12/22/JA5C/KVAR
D12 | 仁愛DS | 22 | 22kV | JA5D | 愛5D線(JA5D) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/22/JA5D/kVA; OPRD2: D12/22/JA5D/KVAR
D12 | 仁愛DS | 22 | 22kV | JA5F | 愛5F線(JA5F) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/22/JA5F/kVA; OPRD2: D12/22/JA5F/KVAR
D12 | 仁愛DS | 22 | 22kV | JA5G | 愛5G線(JA5G) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/22/JA5G/kVA; OPRD2: D12/22/JA5G/KVAR
D12 | 仁愛DS | 22 | 22kV | JA5H | 愛5H線(JA5H) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/22/JA5H/kVA; OPRD2: D12/22/JA5H/KVAR
D12 | 仁愛DS | 22 | 22kV | JA5K | 愛5K線(JA5K) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/22/JA5K/kVA; OPRD2: D12/22/JA5K/KVAR
D12 | 仁愛DS | 22 | 22kV | JA71 | 愛71線(JA71) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/22/JA71/kVA; OPRD2: D12/22/JA71/KVAR
D12 | 仁愛DS | 22 | 22kV | JA72 | 愛72線(JA72) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/22/JA72/kVA; OPRD2: D12/22/JA72/KVAR
D12 | 仁愛DS | 22 | 22kV | JA73 | 愛73線(JA73) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/22/JA73/kVA; OPRD2: D12/22/JA73/KVAR
D12 | 仁愛DS | 22 | 22kV | JA74 | 愛74線(JA74) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/22/JA74/kVA; OPRD2: D12/22/JA74/KVAR
D12 | 仁愛DS | 22 | 22kV | JA75 | 愛75線(JA75) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/22/JA75/kVA; OPRD2: D12/22/JA75/KVAR
D12 | 仁愛DS | 22 | 22kV | JA76 | 愛76線(JA76) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/22/JA76/kVA; OPRD2: D12/22/JA76/KVAR
D12 | 仁愛DS | 22 | 22kV | JA77 | 愛77線(JA77) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/22/JA77/kVA; OPRD2: D12/22/JA77/KVAR
D12 | 仁愛DS | 22 | 22kV | JA78 | 愛78線(JA78) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D12_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D12/22/JA78/kVA; OPRD2: D12/22/JA78/KVAR
D12 | 仁愛DS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D12_A1 | [12 empty] | 仁愛DS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D12/11/210/CB; OPRD2: 6.9; OPRD3: 0
D12 | 仁愛DS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D12_A1 | [12 empty] | 仁愛DS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D12/11/220/CB; OPRD2: 6.9; OPRD3: 0
D12 | 仁愛DS | 11 | 11kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D12_A1 | [12 empty] | 仁愛DS.230_SC_MVAR | 11KV#3SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D12/11/230/CB; OPRD2: 6.9; OPRD3: 0
D12 | 仁愛DS | 11 | 11kV | 240 | #4SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D12_A1 | [12 empty] | 仁愛DS.240_SC_MVAR | 11KV#4SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D12/11/240/CB; OPRD2: 6.9; OPRD3: 0
D12 | 仁愛DS | 22 | 22kV | 250 | #5SC(250) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D12_A1 | [12 empty] | 仁愛DS.250_SC_MVAR | 23KV#5SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D12/22/250/CB; OPRD2: 13.8; OPRD3: 0
D12 | 仁愛DS | 22 | 22kV | 260 | #6SC(260) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D12_A1 | [12 empty] | 仁愛DS.260_SC_MVAR | 23KV#6SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D12/22/260/CB; OPRD2: 13.8; OPRD3: 0
D12 | 仁愛DS | 22 | 22kV | 270 | #7SC(270) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D12_A1 | [12 empty] | 仁愛DS.270_SC_MVAR | 23KV#7SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D12/22/270/CB; OPRD2: 13.8; OPRD3: 0
D12 | 仁愛DS | 22 | 22kV | 280 | #8SC(280) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D12_A1 | [12 empty] | 仁愛DS.280_SC_MVAR | 23KV#8SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D12/22/280/CB; OPRD2: 13.8; OPRD3: 0
D12 | 仁愛DS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/D12_A1 | [12 empty] | 仁愛DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_18 |  | com_alarm_54 | D12//1DTR/GDA | D12//1DTR/PHA | D12//1DTR/96D | D12//1DTR/TRA | D12//1DTR/63Q | D12//1DTR/96B2 | D12//1DTR/96B1 | D12//1DTR/87A | D12//1DTR/51ZA | D12//1DTR/96PA | D12//2DTR/63Q | D12//2DTR/GDA | D12//2DTR/96D | D12//2DTR/96B1 | D12//2DTR/96B2 | D12//2DTR/87A | D12//2DTR/TRA | D12//2DTR/96PA | D12//2DTR/PHA | D12//2DTR/51ZA | D12//3DTR/63Q | D12//3DTR/TRA | D12//3DTR/96D | D12//3DTR/96B1 | D12//3DTR/96B2 | D12//3DTR/PHA | D12//3DTR/GDA | D12//3DTR/51ZA | D12//3DTR/87A | D12//3DTR/96PA | D12//4DTR/87A | D12//4DTR/96PA | D12//4DTR/63Q | D12//4DTR/96B1 | D12//4DTR/TRA | D12//4DTR/GDA | D12//4DTR/PHA | D12//4DTR/96D | D12//4DTR/51ZA | D12//4DTR/96B2 | D12/11/310/GDA | D12/11/310/PHA | D12/11/320/PHA | D12/11/320/GDA | D12/11/330/GDA | D12/11/330/PHA | D12/11/340/GDA | D12/11/340/PHA | D12/161/1BUS/87A | D12/161/2BUS/87A
D12 | 仁愛DS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/D12_A1 | [12 empty] | 仁愛DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | STATION_FAULT_4 |  | com_alarm_4 | OPRD1: D12//1DTR/TRF; OPRD2: D12//2DTR/TRF; OPRD3: D12//3DTR/TRF; OPRD4: D12//4DTR/TRF
D12 | 仁愛DS | 161 | 161kV | 1750_D1 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D12_D1 | [17 empty] | lamp2CC | OPRD1: D12/161/1750/CB
D12 | 仁愛DS | 11 | 11kV | 310_D1 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D12_D1 | [17 empty] | lamp2CC | OPRD1: D12/11/310/CB
D12 | 仁愛DS | 11 | 11kV | 320_D1 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D12_D1 | [17 empty] | lamp2CC | OPRD1: D12/11/320/CB
D12 | 仁愛DS | 161 | 161kV | 1760_D1 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D12_D1 | [17 empty] | lamp2CC | OPRD1: D12/161/1760/CB
D12 | 仁愛DS | 11 | 11kV | 330_D1 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D12_D1 | [17 empty] | lamp2CC | OPRD1: D12/11/330/CB
D12 | 仁愛DS | 11 | 11kV | 340_D1 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D12_D1 | [17 empty] | lamp2CC | OPRD1: D12/11/340/CB
D12 | 仁愛DS | 161 | 161kV | 1770_D1 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D12_D1 | [17 empty] | lamp2CC | OPRD1: D12/161/1770/CB
D12 | 仁愛DS | 22 | 22kV | 350_D1 | #3DTR(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D12_D1 | [17 empty] | lamp2CC | OPRD1: D12/22/350/CB
D12 | 仁愛DS | 161 | 161kV | 1780_D1 | #4DTR(1780) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D12_D1 | [17 empty] | lamp2CC | OPRD1: D12/161/1780/CB
D12 | 仁愛DS | 22 | 22kV | 370_D1 | #4DTR(370) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D12_D1 | [17 empty] | lamp2CC | OPRD1: D12/22/370/CB
D12 | 仁愛DS | 11 | 11kV | 310_D1 | #1DTR(A)(310) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/D12_D1 | [17 empty] | lamp2CC | OPRD1: D12/11/310/81A
D12 | 仁愛DS | 0 |  | RTU_D1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/D12_D1 | [17 empty] | lamp2CC | OPRD1: D12/0/RTU/RTU_R_L
D12 | 仁愛DS | 0 |  | StaDev_D1 | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/D12_D1 | [17 empty] | lamp2CC | OPRD1: D12/0/StaDev/STUV
D12 | 仁愛DS | 0 |  | StaDev_D1 | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D12_D1 | [17 empty] | lamp2CC | OPRD1: D12/0/StaDev/PMA
D12 | 仁愛DS | 0 |  | StaDev_D1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D12_D1 | [17 empty] | lamp2CC | OPRD1: D12/0/StaDev/DCA
D12 | 仁愛DS | 0 |  | StaDev_D1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D12_D1 | [17 empty] | lamp2CC | OPRD1: D12/0/StaDev/DCE
D12 | 仁愛DS | 22 | 22kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D12_D1 | [17 empty] | lamp2CC | OPRD1: D12/22/ComPoint/CBA
D12 | 仁愛DS | 22 | 22kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | ELEM/D12_D1 | [17 empty] | lamp2CC | OPRD1: D12/22/ComPoint/CBF

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D12 | 仁愛DS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | D12/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
D12 | 仁愛DS | 161 | 161kV | 1510 | 嘉義仁愛山線(1510) |  | I | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.1510_AMP | 嘉義仁愛山線 AMP | LINE161 | D12/161/1510/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D12 | 仁愛DS | 161 | 161kV | 1520 | 嘉義仁愛海線(1520) |  | I | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.1520_AMP | 嘉義仁愛海線 AMP | LINE161 | D12/161/1520/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D12 | 仁愛DS | 161 | 161kV | 1530 | 仁愛北回一路(1530) |  | I | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.1530_AMP | 仁愛北回一路 AMP | LINE161 | D12/161/1530/I |  | AMP_CAL |  |  | 5 | CalcAIPoint | [21 empty] | C20R1930 | 1737.800049 | 1737.800049 | 1930.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D12 | 仁愛DS | 161 | 161kV | 1540 | 仁愛北回二路(1540) |  | I | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.1540_AMP | 仁愛北回二路 AMP | LINE161 | D12/161/1540/I |  | AMP_CAL |  |  | 6 | CalcAIPoint | [21 empty] | C20R1930 | 1737.800049 | 1737.800049 | 1930.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛21線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛21線KVA | 11KV愛21線KVA | FEEDER |  |  | KVA_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛21線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛21線KW | 11KV愛21線KW | FEEDER |  |  | KW_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛22線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛22線KVA | 11KV愛22線KVA | FEEDER |  |  | KVA_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛22線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛22線KW | 11KV愛22線KW | FEEDER |  |  | KW_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛23線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛23線KVA | 11KV愛23線KVA | FEEDER |  |  | KVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛23線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛23線KW | 11KV愛23線KW | FEEDER |  |  | KW_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛24線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛24線KVA | 11KV愛24線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛24線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛24線KW | 11KV愛24線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛25線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛25線KVA | 11KV愛25線KVA | FEEDER |  |  | KVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛25線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛25線KW | 11KV愛25線KW | FEEDER |  |  | KW_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛26線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛26線KVA | 11KV愛26線KVA | FEEDER |  |  | KVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛26線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛26線KW | 11KV愛26線KW | FEEDER |  |  | KW_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛27線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛27線KVA | 11KV愛27線KVA | FEEDER |  |  | KVA_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛27線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛27線KW | 11KV愛27線KW | FEEDER |  |  | KW_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛28線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛28線KVA | 11KV愛28線KVA | FEEDER |  |  | KVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛28線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛28線KW | 11KV愛28線KW | FEEDER |  |  | KW_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛29線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛29線KVA | 11KV愛29線KVA | FEEDER |  |  | KVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛29線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛29線KW | 11KV愛29線KW | FEEDER |  |  | KW_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛30線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛30線KVA | 11KV愛30線KVA | FEEDER |  |  | KVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛30線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛30線KW | 11KV愛30線KW | FEEDER |  |  | KW_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛31線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛31線KVA | 11KV愛31線KVA | FEEDER |  |  | KVA_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛31線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛31線KW | 11KV愛31線KW | FEEDER |  |  | KW_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛32線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛32線KVA | 11KV愛32線KVA | FEEDER |  |  | KVA_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛32線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛32線KW | 11KV愛32線KW | FEEDER |  |  | KW_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛33線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛33線KVA | 11KV愛33線KVA | FEEDER |  |  | KVA_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛33線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛33線KW | 11KV愛33線KW | FEEDER |  |  | KW_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛34線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛34線KVA | 11KV愛34線KVA | FEEDER |  |  | KVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛34線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛34線KW | 11KV愛34線KW | FEEDER |  |  | KW_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛35線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛35線KVA | 11KV愛35線KVA | FEEDER |  |  | KVA_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛35線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛35線KW | 11KV愛35線KW | FEEDER |  |  | KW_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛36線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛36線KVA | 11KV愛36線KVA | FEEDER |  |  | KVA_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛36線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛36線KW | 11KV愛36線KW | FEEDER |  |  | KW_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛37線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛37線KVA | 11KV愛37線KVA | FEEDER |  |  | KVA_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛37線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛37線KW | 11KV愛37線KW | FEEDER |  |  | KW_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛38線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛38線KVA | 11KV愛38線KVA | FEEDER |  |  | KVA_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛38線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛38線KW | 11KV愛38線KW | FEEDER |  |  | KW_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛39線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛39線KVA | 11KV愛39線KVA | FEEDER |  |  | KVA_CAL |  |  | 43 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛39線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛39線KW | 11KV愛39線KW | FEEDER |  |  | KW_CAL |  |  | 44 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛40線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛40線KVA | 11KV愛40線KVA | FEEDER |  |  | KVA_CAL |  |  | 45 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛40線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛40線KW | 11KV愛40線KW | FEEDER |  |  | KW_CAL |  |  | 46 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛5A線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛5A線KVA | 23KV愛5A線KVA | FEEDER |  |  | KVA_CAL |  |  | 47 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛5A線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛5A線KW | 23KV愛5A線KW | FEEDER |  |  | KW_CAL |  |  | 48 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛5B線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛5B線KVA | 23KV愛5B線KVA | FEEDER |  |  | KVA_CAL |  |  | 49 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛5B線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛5B線KW | 23KV愛5B線KW | FEEDER |  |  | KW_CAL |  |  | 50 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛5C線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛5C線KVA | 23KV愛5C線KVA | FEEDER |  |  | KVA_CAL |  |  | 51 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛5C線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛5C線KW | 23KV愛5C線KW | FEEDER |  |  | KW_CAL |  |  | 52 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛5D線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛5D線KVA | 23KV愛5D線KVA | FEEDER |  |  | KVA_CAL |  |  | 53 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛5D線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛5D線KW | 23KV愛5D線KW | FEEDER |  |  | KW_CAL |  |  | 54 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛5F線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛5F線KVA | 23KV愛5F線KVA | FEEDER |  |  | KVA_CAL |  |  | 55 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛5F線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛5F線KW | 23KV愛5F線KW | FEEDER |  |  | KW_CAL |  |  | 56 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛5G線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛5G線KVA | 23KV愛5G線KVA | FEEDER |  |  | KVA_CAL |  |  | 57 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛5G線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛5G線KW | 23KV愛5G線KW | FEEDER |  |  | KW_CAL |  |  | 58 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛5H線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛5H線KVA | 23KV愛5H線KVA | FEEDER |  |  | KVA_CAL |  |  | 59 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛5H線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛5H線KW | 23KV愛5H線KW | FEEDER |  |  | KW_CAL |  |  | 60 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛5K線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛5K線KVA | 23KV愛5K線KVA | FEEDER |  |  | KVA_CAL |  |  | 61 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛5K線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛5K線KW | 23KV愛5K線KW | FEEDER |  |  | KW_CAL |  |  | 62 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛71線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛71線KVA | 23KV愛71線KVA | FEEDER |  |  | KVA_CAL |  |  | 63 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛71線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛71線KW | 23KV愛71線KW | FEEDER |  |  | KW_CAL |  |  | 64 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛72線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛72線KVA | 23KV愛72線KVA | FEEDER |  |  | KVA_CAL |  |  | 65 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛72線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛72線KW | 23KV愛72線KW | FEEDER |  |  | KW_CAL |  |  | 66 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛73線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛73線KVA | 23KV愛73線KVA | FEEDER |  |  | KVA_CAL |  |  | 67 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛73線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛73線KW | 23KV愛73線KW | FEEDER |  |  | KW_CAL |  |  | 68 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛74線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛74線KVA | 23KV愛74線KVA | FEEDER |  |  | KVA_CAL |  |  | 69 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛74線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛74線KW | 23KV愛74線KW | FEEDER |  |  | KW_CAL |  |  | 70 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛75線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛75線KVA | 23KV愛75線KVA | FEEDER |  |  | KVA_CAL |  |  | 71 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛75線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛75線KW | 23KV愛75線KW | FEEDER |  |  | KW_CAL |  |  | 72 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛76線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛76線KVA | 23KV愛76線KVA | FEEDER |  |  | KVA_CAL |  |  | 73 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛76線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛76線KW | 23KV愛76線KW | FEEDER |  |  | KW_CAL |  |  | 74 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛77線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛77線KVA | 23KV愛77線KVA | FEEDER |  |  | KVA_CAL |  |  | 75 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛77線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛77線KW | 23KV愛77線KW | FEEDER |  |  | KW_CAL |  |  | 76 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛78線KVA | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛78線KVA | 23KV愛78線KVA | FEEDER |  |  | KVA_CAL |  |  | 77 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  |  |  |  | 愛78線KW | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.愛78線KW | 23KV愛78線KW | FEEDER |  |  | KW_CAL |  |  | 78 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.#1DTR(A)_MVA | #1DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 79 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D12 | 仁愛DS | 0 |  | 1DTR(A) | #1DTR(A) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.#1DTR(A)_LOAD | #1DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 80 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D12 | 仁愛DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PF | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.#1DTR(A)_PF | #1DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 81 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D12 | 仁愛DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.#1DTR(B)_MVA | #1DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 82 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D12 | 仁愛DS | 0 |  | 1DTR(B) | #1DTR(B) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.#1DTR(B)_LOAD | #1DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 83 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D12 | 仁愛DS | 0 |  | 1DTR(B) | #1DTR(B) |  | PF | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.#1DTR(B)_PF | #1DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 84 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D12 | 仁愛DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.#2DTR(A)_MVA | #2DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 85 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D12 | 仁愛DS | 0 |  | 2DTR(A) | #2DTR(A) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.#2DTR(A)_LOAD | #2DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 86 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D12 | 仁愛DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PF | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.#2DTR(A)_PF | #2DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 87 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D12 | 仁愛DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.#2DTR(B)_MVA | #2DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 88 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D12 | 仁愛DS | 0 |  | 2DTR(B) | #2DTR(B) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.#2DTR(B)_LOAD | #2DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 89 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D12 | 仁愛DS | 0 |  | 2DTR(B) | #2DTR(B) |  | PF | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.#2DTR(B)_PF | #2DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 90 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D12 | 仁愛DS | 0 |  | 3DTR | #3DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.#3DTR_MVA | #3DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 91 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D12 | 仁愛DS | 0 |  | 3DTR | #3DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.#3DTR_LOAD | #3DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 92 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D12 | 仁愛DS | 0 |  | 3DTR | #3DTR |  | PF | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.#3DTR_PF | #3DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 93 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D12 | 仁愛DS | 0 |  | 4DTR | #4DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.#4DTR_MVA | #4DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 94 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D12 | 仁愛DS | 0 |  | 4DTR | #4DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.#4DTR_LOAD | #4DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 95 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D12 | 仁愛DS | 0 |  | 4DTR | #4DTR |  | PF | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.#4DTR_PF | #4DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 96 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D12 | 仁愛DS | 0 |  | 1DTR | #1DTR |  | MW | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.#1DTR_MW | #1DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 97 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  | 1DTR | #1DTR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.#1DTR_MVAR | #1DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 98 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  | 1DTR | #1DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.#1DTR_MVA | #1DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 99 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D12 | 仁愛DS | 0 |  | 1DTR | #1DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.#1DTR_LOAD | #1DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 100 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D12 | 仁愛DS | 0 |  | 2DTR | #2DTR |  | MW | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.#2DTR_MW | #2DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 101 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  | 2DTR | #2DTR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.#2DTR_MVAR | #2DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 102 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  | 2DTR | #2DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.#2DTR_MVA | #2DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 103 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D12 | 仁愛DS | 0 |  | 2DTR | #2DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.#2DTR_LOAD | #2DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 104 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D12 | 仁愛DS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.210_SC_MVAR | 11KV#1SC MVAR | SC | D12/11/210/MVAR |  | SC_LBS_11 |  |  | 105 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 11 | 11kV | 220_SC | #2SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.220_SC_MVAR | 11KV#2SC MVAR | SC | D12/11/220/MVAR |  | SC_LBS_11 |  |  | 106 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 11 | 11kV | 230_SC | #3SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.230_SC_MVAR | 11KV#3SC MVAR | SC | D12/11/230/MVAR |  | SC_LBS_11 |  |  | 107 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 11 | 11kV | 240_SC | #4SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.240_SC_MVAR | 11KV#4SC MVAR | SC | D12/11/240/MVAR |  | SC_LBS_11 |  |  | 108 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 22 | 22kV | 250_SC | #5SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.250_SC_MVAR | 23KV#5SC MVAR | SC | D12/22/250/MVAR |  | SC_CAL_23 |  |  | 109 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 22 | 22kV | 260_SC | #6SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.260_SC_MVAR | 23KV#6SC MVAR | SC | D12/22/260/MVAR |  | SC_CAL_23 |  |  | 110 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 22 | 22kV | 270_SC | #7SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.270_SC_MVAR | 23KV#7SC MVAR | SC | D12/22/270/MVAR |  | SC_CAL_23 |  |  | 111 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 22 | 22kV | 280_SC | #8SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.280_SC_MVAR | 23KV#8SC MVAR | SC | D12/22/280/MVAR |  | SC_CAL_23 |  |  | 112 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  | TRTOT | 仁愛主變瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 仁愛DS.TRTOT_MW | 仁愛主變瞬時供電量 MW |  |  |  | TOTAL_PQ_CAL_4 |  |  | 113 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  | TRTOT | 仁愛主變瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 仁愛DS.TRTOT_MVAR | 仁愛主變瞬時供電量 MVAR |  |  |  | TOTAL_PQ_CAL_4 |  |  | 114 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 0 |  | 100_CB | 100(100_CB) | [27 empty] | DDCS2_2 | [8 empty] | 仁愛DS.100_CB_2 | 100 CB (D2) | TIE |  |  | AD_LAMP_DD_1 |  |  | 115 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | 200_CB | 200(200_CB) | [27 empty] | DDCS2_2 | [8 empty] | 仁愛DS.200_CB_2 | 200 CB (D2) | TIE |  |  | AD_LAMP_DD_1 |  |  | 116 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | 400_CB | 400(400_CB) | [27 empty] | DDCS2_2 | [8 empty] | 仁愛DS.400_CB_2 | 400 CB (D2) | TIE |  |  | AD_LAMP_DD_1 |  |  | 117 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | 1750_CB | #1DTR(1750_CB) | [27 empty] | DDCS2_2 | [8 empty] | 仁愛DS.1750_CB_2 | 1750(#1DTR) CB (D2) | MTR |  |  | AD_LAMP_DD_1 |  |  | 118 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 310_CB | #1DTR(310_CB) | [27 empty] | DDCS2_2 | [8 empty] | 仁愛DS.310_CB_2 | 310(#1DTR) CB (D2) | MTR |  |  | AD_LAMP_DD_1 |  |  | 119 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 320_CB | #1DTR(320_CB) | [27 empty] | DDCS2_2 | [8 empty] | 仁愛DS.320_CB_2 | 320(#1DTR) CB (D2) | MTR |  |  | AD_LAMP_DD_1 |  |  | 120 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 1760_CB | #2DTR(1760_CB) | [27 empty] | DDCS2_2 | [8 empty] | 仁愛DS.1760_CB_2 | 1760(#2DTR) CB (D2) | MTR |  |  | AD_LAMP_DD_1 |  |  | 121 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 330_CB | #2DTR(330_CB) | [27 empty] | DDCS2_2 | [8 empty] | 仁愛DS.330_CB_2 | 330(#2DTR) CB (D2) | MTR |  |  | AD_LAMP_DD_1 |  |  | 122 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 340_CB | #2DTR(340_CB) | [27 empty] | DDCS2_2 | [8 empty] | 仁愛DS.340_CB_2 | 340(#2DTR) CB (D2) | MTR |  |  | AD_LAMP_DD_1 |  |  | 123 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 1770_CB | #3DTR(1770_CB) | [27 empty] | DDCS2_2 | [8 empty] | 仁愛DS.1770_CB_2 | 1770(#3DTR) CB (D2) | MTR |  |  | AD_LAMP_DD_1 |  |  | 124 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 350_CB | #3DTR(350_CB) | [27 empty] | DDCS2_2 | [8 empty] | 仁愛DS.350_CB_2 | 350(#3DTR) CB (D2) | MTR |  |  | AD_LAMP_DD_1 |  |  | 125 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 1780_CB | #4DTR(1780_CB) | [27 empty] | DDCS2_2 | [8 empty] | 仁愛DS.1780_CB_2 | 1780(#4DTR) CB (D2) | MTR |  |  | AD_LAMP_DD_1 |  |  | 126 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 370_CB | #4DTR(370_CB) | [27 empty] | DDCS2_2 | [8 empty] | 仁愛DS.370_CB_2 | 370(#4DTR) CB (D2) | MTR |  |  | AD_LAMP_DD_1 |  |  | 127 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | 210_CB | #1SC(210_CB) | [27 empty] | DDCS2_2 | [8 empty] | 仁愛DS.210_CB_2 | 210(11KV #1SC) CB (D2) | SC |  |  | AD_LAMP_DD_1 |  |  | 128 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | 220_CB | #2SC(220_CB) | [27 empty] | DDCS2_2 | [8 empty] | 仁愛DS.220_CB_2 | 220(11KV #2SC) CB (D2) | SC |  |  | AD_LAMP_DD_1 |  |  | 129 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | 230_CB | #3SC(230_CB) | [27 empty] | DDCS2_2 | [8 empty] | 仁愛DS.230_CB_2 | 230(11KV #3SC) CB (D2) | SC |  |  | AD_LAMP_DD_1 |  |  | 130 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | 240_CB | #4SC(240_CB) | [27 empty] | DDCS2_2 | [8 empty] | 仁愛DS.240_CB_2 | 240(11KV #4SC) CB (D2) | SC |  |  | AD_LAMP_DD_1 |  |  | 131 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | 250_CB | #5SC(250_CB) | [27 empty] | DDCS2_2 | [8 empty] | 仁愛DS.250_CB_2 | 250(23KV #5SC) CB (D2) | SC |  |  | AD_LAMP_DD_1 |  |  | 132 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | 260_CB | #6SC(260_CB) | [27 empty] | DDCS2_2 | [8 empty] | 仁愛DS.260_CB_2 | 260(23KV #6SC) CB (D2) | SC |  |  | AD_LAMP_DD_1 |  |  | 133 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | 270_CB | #7SC(270_CB) | [27 empty] | DDCS2_2 | [8 empty] | 仁愛DS.270_CB_2 | 270(23KV #7SC) CB (D2) | SC |  |  | AD_LAMP_DD_1 |  |  | 134 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | 280_CB | #8SC(280_CB) | [27 empty] | DDCS2_2 | [8 empty] | 仁愛DS.280_CB_2 | 280(23KV #8SC) CB (D2) | SC |  |  | AD_LAMP_DD_1 |  |  | 135 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | 11__CBA | 11/斷路器重故障(11__CBA) | [27 empty] | DDCS2_2 | [8 empty] | 仁愛DS.11/23KV_CBA_2 | 11/23KV斷路器重故障 (D2) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 136 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | 11__CBF | 11/斷路器輕故障(11__CBF) | [27 empty] | DDCS2_2 | [8 empty] | 仁愛DS.11/23KV_CBF_2 | 11/23KV斷路器輕故障 (D2) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 137 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | D12/0/CalcPoint/SUBA |  | STATION_FAULT_18 |  |  | 138 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 變電所輕故障點燈 | 變電所輕故障點燈 |  | SUBF | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | D12/0/CalcPoint/SUBF |  | STATION_FAULT_4 |  |  | 139 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 變電所重故障 | 變電所重故障點燈 | [27 empty] | DDCS2_2 | [8 empty] | 仁愛DS.變電所重故障_2 | 變電所重故障點燈 (D2) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 140 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 | [27 empty] | DDCS2_2 | [8 empty] | 仁愛DS.變電所輕故障_2 | 變電所輕故障點燈 (D2) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 141 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1510_AMP | 嘉義仁愛山線 | [27 empty] | ADCS_N | [8 empty] | 仁愛DS.1510_AMP_A | 嘉義仁愛山線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 142 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1520_AMP | 嘉義仁愛海線 | [27 empty] | ADCS_N | [8 empty] | 仁愛DS.1520_AMP_A | 嘉義仁愛海線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 143 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1530_AMP | 仁愛北回一路 | [27 empty] | ADCS_N | [8 empty] | 仁愛DS.1530_AMP_A | 仁愛北回一路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 144 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1540_AMP | 仁愛北回二路 | [27 empty] | ADCS_N | [8 empty] | 仁愛DS.1540_AMP_A | 仁愛北回二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 145 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D12 | 仁愛DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PERM | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | D12//1DTR(A)/TR_PERM |  | DTR_PERM |  |  | 146 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D12 | 仁愛DS | 0 |  | 1DTR(B) | #1DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | D12//1DTR(B)/TR_PERM |  | DTR_PERM |  |  | 147 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D12 | 仁愛DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PERM | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | D12//2DTR(A)/TR_PERM |  | DTR_PERM |  |  | 148 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D12 | 仁愛DS | 0 |  | 2DTR(B) | #2DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | D12//2DTR(B)/TR_PERM |  | DTR_PERM |  |  | 149 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D12 | 仁愛DS | 0 |  | 3DTR | #3DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.#3DTR_PERM | #3DTR TAP PERMISSION POINT | MTR | D12//3DTR/TR_PERM |  | DTR_PERM |  |  | 150 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D12 | 仁愛DS | 0 |  | 4DTR | #4DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.#4DTR_PERM | #4DTR TAP PERMISSION POINT | MTR | D12//4DTR/TR_PERM |  | DTR_PERM |  |  | 151 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D12 | 仁愛DS | 0 |  | 1DTR_MVA | #1DTR | [27 empty] | ADCS_N | [8 empty] | 仁愛DS.#1DTR_MVA_A | #1DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 152 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D12 | 仁愛DS | 0 |  | 1DTR_MVA | #1DTR(A) | [27 empty] | DDCS2_2 | [8 empty] | 仁愛DS.#1DTR_MVA_2 | #1DTR(A) MVA 點燈 (D2) | MTR |  |  | MAP_SET |  |  | 153 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
D12 | 仁愛DS | 0 |  | 1DTR_MVA | #1DTR(B) |  | 3 | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.#1DTR_MVA_3 | #1DTR(B) MVA 點燈 (D2) | MTR |  |  | MAP_SET |  |  | 154 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D12 | 仁愛DS | 0 |  | 2DTR_MVA | #2DTR | [27 empty] | ADCS_N | [8 empty] | 仁愛DS.#2DTR_MVA_A | #2DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 155 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D12 | 仁愛DS | 0 |  | 2DTR_MVA | #2DTR(A) | [27 empty] | DDCS2_2 | [8 empty] | 仁愛DS.#2DTR_MVA_2 | #2DTR(A) MVA 點燈 (D2) | MTR |  |  | MAP_SET |  |  | 156 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
D12 | 仁愛DS | 0 |  | 2DTR_MVA | #2DTR(B) |  | 3 | [25 empty] | DDCS2_2 | [8 empty] | 仁愛DS.#2DTR_MVA_3 | #2DTR(B) MVA 點燈 (D2) | MTR |  |  | MAP_SET |  |  | 157 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D12 | 仁愛DS | 0 |  | 3DTR_MVA | #3DTR | [27 empty] | ADCS_N | [8 empty] | 仁愛DS.#3DTR_MVA_A | #3DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 158 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D12 | 仁愛DS | 0 |  | 3DTR_MVA | #3DTR | [27 empty] | DDCS2_2 | [8 empty] | 仁愛DS.#3DTR_MVA_2 | #3DTR MVA 點燈 (D2) | MTR |  |  | AD_LAMP_DD_2 |  |  | 159 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
D12 | 仁愛DS | 0 |  | 4DTR_MVA | #4DTR | [27 empty] | ADCS_N | [8 empty] | 仁愛DS.#4DTR_MVA_A | #4DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 160 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D12 | 仁愛DS | 0 |  | 4DTR_MVA | #4DTR | [27 empty] | DDCS2_2 | [8 empty] | 仁愛DS.#4DTR_MVA_2 | #4DTR MVA 點燈 (D2) | MTR |  |  | AD_LAMP_DD_2 |  |  | 161 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
D12 | 仁愛DS | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_DS |  |  | 162 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | PMA | 電力量測表計故障 | [27 empty] | DDCS2_2 | [8 empty] | 仁愛DS.PMA_2 | 電力量測表計故障 (D2) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 163 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 1ABUS | #1ABUS |  | 11KV#1ABUSC | [25 empty] | CDCS | [8 empty] | 仁愛DS.11KV#1ABUSC | #1ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 164 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D12 | 仁愛DS | 0 |  | 1BBUS | #1BBUS |  | 11KV#1BBUSC | [25 empty] | CDCS | [8 empty] | 仁愛DS.11KV#1BBUSC | #1BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 165 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D12 | 仁愛DS | 0 |  | 2ABUS | #2ABUS |  | 11KV#2ABUSC | [25 empty] | CDCS | [8 empty] | 仁愛DS.11KV#2ABUSC | #2ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 166 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D12 | 仁愛DS | 0 |  | 2BBUS | #2BBUS |  | 11KV#2BBUSC | [25 empty] | CDCS | [8 empty] | 仁愛DS.11KV#2BBUSC | #2BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 167 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D12 | 仁愛DS | 0 |  | 3BUS | #3BUS |  | 23KV#3BUSC | [25 empty] | CDCS | [8 empty] | 仁愛DS.23KV#3BUSC | #3BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 168 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D12 | 仁愛DS | 0 |  | 4BUS | #4BUS |  | 23KV#4BUSC | [25 empty] | CDCS | [8 empty] | 仁愛DS.23KV#4BUSC | #4BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 169 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D12 | 仁愛DS | 0 |  | TAP_OVER | TAP |  | SET | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.TAP_OVER_SET | TAP OVER HI/LO ALARM | MTR |  |  | 5000_CB_T6 |  |  | 170 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D12 | 仁愛DS | 0 |  | BUS_OVER | BUS |  | SET | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.BUS_OVER_SET | BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B6 |  |  | 171 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D12 | 仁愛DS | 0 |  | 5000 | 虛擬5000 |  | CB動作 | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.5000_CB動作 | 虛擬5000 CB動作,請查明原因處理 | MTR |  |  | 5000_CB_M |  |  | 172 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 注意OLTC | 注意OLTC |  | BUS電壓異常 | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.BUS電壓異常 | 注意OLTC Tap位置,並將RPDC閉鎖 | OTHER |  |  | STATION_FAULT_3 |  |  | 173 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | D12/161/1BUS/V |  |  |  | CDC | 174 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D12 | 仁愛DS | 161 | 161kV | 2BUS | #2BUS |  | V | [17 empty] | 1-83 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | D12/161/2BUS/V |  |  |  | CDC | 175 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D12 | 仁愛DS | 11 | 11kV | 1ABUS | #1ABUS |  | V | [17 empty] | 1-AF | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.11KV#1ABUS_KV | 11KV #1ABUS KV | BUS | D12/11/1ABUS/V |  |  |  | CDC | 176 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D12 | 仁愛DS | 11 | 11kV | 1BBUS | #1BBUS |  | V | [17 empty] | 1-D3 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.11KV#1BBUS_KV | 11KV #1BBUS KV | BUS | D12/11/1BBUS/V |  |  |  | CDC | 177 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D12 | 仁愛DS | 11 | 11kV | 2ABUS | #2ABUS |  | V | [17 empty] | 1-F2 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS | D12/11/2ABUS/V |  |  |  | CDC | 178 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D12 | 仁愛DS | 11 | 11kV | 2BBUS | #2BBUS |  | V | [17 empty] | 2-93 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.11KV#2BBUS_KV | 11KV #2BBUS KV | BUS | D12/11/2BBUS/V |  |  |  | CDC | 179 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D12 | 仁愛DS | 22 | 22kV | 3BUS | #3BUS |  | V | [17 empty] | 2-B5 | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.23KV#3BUS_KV | 23KV #3BUS KV | BUS | D12/11/3BUS/V |  |  |  | CDC | 180 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D12 | 仁愛DS | 22 | 22kV | 4BUS | #4BUS |  | V | [17 empty] | 2-E5 | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.23KV#4BUS_KV | 23KV #4BUS KV | BUS | D12/11/4BUS/V |  |  |  | CDC | 181 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D12 | 仁愛DS | 161 | 161kV | 1510 | 嘉義仁愛山線(1510) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.1510_MW | 嘉義仁愛山線 MW | LINE161 | D12/161/1510/MW |  |  |  | CDC | 182 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D12 | 仁愛DS | 161 | 161kV | 1510 | 嘉義仁愛山線(1510) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.1510_MVAR | 嘉義仁愛山線 MVAR | LINE161 | D12/161/1510/MVAR |  |  |  | CDC | 183 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D12 | 仁愛DS | 161 | 161kV | 1520 | 嘉義仁愛海線(1520) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.1520_MW | 嘉義仁愛海線 MW | LINE161 | D12/161/1520/MW |  |  |  | CDC | 184 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D12 | 仁愛DS | 161 | 161kV | 1520 | 嘉義仁愛海線(1520) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.1520_MVAR | 嘉義仁愛海線 MVAR | LINE161 | D12/161/1520/MVAR |  |  |  | CDC | 185 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D12 | 仁愛DS | 161 | 161kV | 1530 | 仁愛北回一路(1530) |  | MW | [17 empty] | 1-8A | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.1530_MW | 仁愛北回一路 MW | LINE161 | D12/161/1530/MW |  |  |  | CDC | 186 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D12 | 仁愛DS | 161 | 161kV | 1530 | 仁愛北回一路(1530) |  | MVAR | [17 empty] | 1-8B | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.1530_MVAR | 仁愛北回一路 MVAR | LINE161 | D12/161/1530/MVAR |  |  |  | CDC | 187 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D12 | 仁愛DS | 161 | 161kV | 1540 | 仁愛北回二路(1540) |  | MW | [17 empty] | 1-88 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.1540_MW | 仁愛北回二路 MW | LINE161 | D12/161/1540/MW |  |  |  | CDC | 188 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D12 | 仁愛DS | 161 | 161kV | 1540 | 仁愛北回二路(1540) |  | MVAR | [17 empty] | 1-89 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.1540_MVAR | 仁愛北回二路 MVAR | LINE161 | D12/161/1540/MVAR |  |  |  | CDC | 189 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛21線 | 愛21線 |  | 愛21線KVAR | [17 empty] | 1-B0 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛21線KVAR | 11KV愛21線 KVAR | FEEDER | D12/11/JA21/KVAR |  |  |  | CDC | 190 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛21線 | 愛21線 |  | 愛21線A1 | [17 empty] | 1-B1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛21線A1 | 11KV愛21線 R相AMP | FEEDER | D12/11/JA21/I_R |  |  |  | CDC | 191 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛21線 | 愛21線 |  | 愛21線A2 | [17 empty] | 1-B2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛21線A2 | 11KV愛21線 S相AMP | FEEDER | D12/11/JA21/I_S |  |  |  | CDC | 192 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛21線 | 愛21線 |  | 愛21線A3 | [17 empty] | 1-B3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛21線A3 | 11KV愛21線 T相AMP | FEEDER | D12/11/JA21/I_T |  |  |  | CDC | 193 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛21線 | 愛21線 |  | 愛21線A0 | [17 empty] | 1-B4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛21線A0 | 11KV愛21線 N相AMP | FEEDER | D12/11/JA21/I_N |  |  |  | CDC | 194 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛22線 | 愛22線 |  | 愛22線KVAR | [17 empty] | 1-B5 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛22線KVAR | 11KV愛22線 KVAR | FEEDER | D12/11/JA22/KVAR |  |  |  | CDC | 195 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛22線 | 愛22線 |  | 愛22線A1 | [17 empty] | 1-B6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛22線A1 | 11KV愛22線 R相AMP | FEEDER | D12/11/JA22/I_R |  |  |  | CDC | 196 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛22線 | 愛22線 |  | 愛22線A2 | [17 empty] | 1-B7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛22線A2 | 11KV愛22線 S相AMP | FEEDER | D12/11/JA22/I_S |  |  |  | CDC | 197 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛22線 | 愛22線 |  | 愛22線A3 | [17 empty] | 1-B8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛22線A3 | 11KV愛22線 T相AMP | FEEDER | D12/11/JA22/I_T |  |  |  | CDC | 198 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛22線 | 愛22線 |  | 愛22線A0 | [17 empty] | 1-B9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛22線A0 | 11KV愛22線 N相AMP | FEEDER | D12/11/JA22/I_N |  |  |  | CDC | 199 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛23線 | 愛23線 |  | 愛23線KVAR | [17 empty] | 1-BA | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛23線KVAR | 11KV愛23線 KVAR | FEEDER | D12/11/JA23/KVAR |  |  |  | CDC | 200 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛23線 | 愛23線 |  | 愛23線A1 | [17 empty] | 1-BB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛23線A1 | 11KV愛23線 R相AMP | FEEDER | D12/11/JA23/I_R |  |  |  | CDC | 201 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛23線 | 愛23線 |  | 愛23線A2 | [17 empty] | 1-BC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛23線A2 | 11KV愛23線 S相AMP | FEEDER | D12/11/JA23/I_S |  |  |  | CDC | 202 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛23線 | 愛23線 |  | 愛23線A3 | [17 empty] | 1-BD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛23線A3 | 11KV愛23線 T相AMP | FEEDER | D12/11/JA23/I_T |  |  |  | CDC | 203 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛23線 | 愛23線 |  | 愛23線A0 | [17 empty] | 1-BE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛23線A0 | 11KV愛23線 N相AMP | FEEDER | D12/11/JA23/I_N |  |  |  | CDC | 204 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛24線 | 愛24線 |  | 愛24線KVAR | [17 empty] | 1-BF | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛24線KVAR | 11KV愛24線 KVAR | FEEDER | D12/11/JA24/KVAR |  |  |  | CDC | 205 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛24線 | 愛24線 |  | 愛24線A1 | [17 empty] | 1-C2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛24線A1 | 11KV愛24線 R相AMP | FEEDER | D12/11/JA24/I_R |  |  |  | CDC | 206 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛24線 | 愛24線 |  | 愛24線A2 | [17 empty] | 1-C3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛24線A2 | 11KV愛24線 S相AMP | FEEDER | D12/11/JA24/I_S |  |  |  | CDC | 207 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛24線 | 愛24線 |  | 愛24線A3 | [17 empty] | 1-C4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛24線A3 | 11KV愛24線 T相AMP | FEEDER | D12/11/JA24/I_T |  |  |  | CDC | 208 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛24線 | 愛24線 |  | 愛24線A0 | [17 empty] | 1-C5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛24線A0 | 11KV愛24線 N相AMP | FEEDER | D12/11/JA24/I_N |  |  |  | CDC | 209 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛25線 | 愛25線 |  | 愛25線KVAR | [17 empty] | 1-C6 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛25線KVAR | 11KV愛25線 KVAR | FEEDER | D12/11/JA25/KVAR |  |  |  | CDC | 210 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛25線 | 愛25線 |  | 愛25線A1 | [17 empty] | 1-C7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛25線A1 | 11KV愛25線 R相AMP | FEEDER | D12/11/JA25/I_R |  |  |  | CDC | 211 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛25線 | 愛25線 |  | 愛25線A2 | [17 empty] | 1-C8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛25線A2 | 11KV愛25線 S相AMP | FEEDER | D12/11/JA25/I_S |  |  |  | CDC | 212 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛25線 | 愛25線 |  | 愛25線A3 | [17 empty] | 1-C9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛25線A3 | 11KV愛25線 T相AMP | FEEDER | D12/11/JA25/I_T |  |  |  | CDC | 213 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛25線 | 愛25線 |  | 愛25線A0 | [17 empty] | 1-CA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛25線A0 | 11KV愛25線 N相AMP | FEEDER | D12/11/JA25/I_N |  |  |  | CDC | 214 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛26線 | 愛26線 |  | 愛26線KVAR | [17 empty] | 1-D4 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛26線KVAR | 11KV愛26線 KVAR | FEEDER | D12/11/JA26/KVAR |  |  |  | CDC | 215 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛26線 | 愛26線 |  | 愛26線A1 | [17 empty] | 1-D5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛26線A1 | 11KV愛26線 R相AMP | FEEDER | D12/11/JA26/I_R |  |  |  | CDC | 216 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛26線 | 愛26線 |  | 愛26線A2 | [17 empty] | 1-D6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛26線A2 | 11KV愛26線 S相AMP | FEEDER | D12/11/JA26/I_S |  |  |  | CDC | 217 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛26線 | 愛26線 |  | 愛26線A3 | [17 empty] | 1-D7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛26線A3 | 11KV愛26線 T相AMP | FEEDER | D12/11/JA26/I_T |  |  |  | CDC | 218 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛26線 | 愛26線 |  | 愛26線A0 | [17 empty] | 1-D8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛26線A0 | 11KV愛26線 N相AMP | FEEDER | D12/11/JA26/I_N |  |  |  | CDC | 219 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛27線 | 愛27線 |  | 愛27線KVAR | [17 empty] | 1-D9 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛27線KVAR | 11KV愛27線 KVAR | FEEDER | D12/11/JA27/KVAR |  |  |  | CDC | 220 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛27線 | 愛27線 |  | 愛27線A1 | [17 empty] | 1-DA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛27線A1 | 11KV愛27線 R相AMP | FEEDER | D12/11/JA27/I_R |  |  |  | CDC | 221 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛27線 | 愛27線 |  | 愛27線A2 | [17 empty] | 1-DB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛27線A2 | 11KV愛27線 S相AMP | FEEDER | D12/11/JA27/I_S |  |  |  | CDC | 222 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛27線 | 愛27線 |  | 愛27線A3 | [17 empty] | 1-DC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛27線A3 | 11KV愛27線 T相AMP | FEEDER | D12/11/JA27/I_T |  |  |  | CDC | 223 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛27線 | 愛27線 |  | 愛27線A0 | [17 empty] | 1-DD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛27線A0 | 11KV愛27線 N相AMP | FEEDER | D12/11/JA27/I_N |  |  |  | CDC | 224 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛28線 | 愛28線 |  | 愛28線KVAR | [17 empty] | 1-DE | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛28線KVAR | 11KV愛28線 KVAR | FEEDER | D12/11/JA28/KVAR |  |  |  | CDC | 225 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛28線 | 愛28線 |  | 愛28線A1 | [17 empty] | 1-DF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛28線A1 | 11KV愛28線 R相AMP | FEEDER | D12/11/JA28/I_R |  |  |  | CDC | 226 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛28線 | 愛28線 |  | 愛28線A2 | [17 empty] | 1-E0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛28線A2 | 11KV愛28線 S相AMP | FEEDER | D12/11/JA28/I_S |  |  |  | CDC | 227 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛28線 | 愛28線 |  | 愛28線A3 | [17 empty] | 1-E1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛28線A3 | 11KV愛28線 T相AMP | FEEDER | D12/11/JA28/I_T |  |  |  | CDC | 228 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛28線 | 愛28線 |  | 愛28線A0 | [17 empty] | 1-E2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛28線A0 | 11KV愛28線 N相AMP | FEEDER | D12/11/JA28/I_N |  |  |  | CDC | 229 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛29線 | 愛29線 |  | 愛29線KVAR | [17 empty] | 1-E3 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛29線KVAR | 11KV愛29線 KVAR | FEEDER | D12/11/JA29/KVAR |  |  |  | CDC | 230 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛29線 | 愛29線 |  | 愛29線A1 | [17 empty] | 1-E4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛29線A1 | 11KV愛29線 R相AMP | FEEDER | D12/11/JA29/I_R |  |  |  | CDC | 231 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛29線 | 愛29線 |  | 愛29線A2 | [17 empty] | 1-E5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛29線A2 | 11KV愛29線 S相AMP | FEEDER | D12/11/JA29/I_S |  |  |  | CDC | 232 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛29線 | 愛29線 |  | 愛29線A3 | [17 empty] | 1-E6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛29線A3 | 11KV愛29線 T相AMP | FEEDER | D12/11/JA29/I_T |  |  |  | CDC | 233 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛29線 | 愛29線 |  | 愛29線A0 | [17 empty] | 1-E7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛29線A0 | 11KV愛29線 N相AMP | FEEDER | D12/11/JA29/I_N |  |  |  | CDC | 234 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛30線 | 愛30線 |  | 愛30線KVAR | [17 empty] | 1-E8 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛30線KVAR | 11KV愛30線 KVAR | FEEDER | D12/11/JA30/KVAR |  |  |  | CDC | 235 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛30線 | 愛30線 |  | 愛30線A1 | [17 empty] | 1-E9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛30線A1 | 11KV愛30線 R相AMP | FEEDER | D12/11/JA30/I_R |  |  |  | CDC | 236 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛30線 | 愛30線 |  | 愛30線A2 | [17 empty] | 1-EA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛30線A2 | 11KV愛30線 S相AMP | FEEDER | D12/11/JA30/I_S |  |  |  | CDC | 237 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛30線 | 愛30線 |  | 愛30線A3 | [17 empty] | 1-EB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛30線A3 | 11KV愛30線 T相AMP | FEEDER | D12/11/JA30/I_T |  |  |  | CDC | 238 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛30線 | 愛30線 |  | 愛30線A0 | [17 empty] | 1-EC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛30線A0 | 11KV愛30線 N相AMP | FEEDER | D12/11/JA30/I_N |  |  |  | CDC | 239 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛31線 | 愛31線 |  | 愛31線KVAR | [17 empty] | 1-F3 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛31線KVAR | 11KV愛31線 KVAR | FEEDER | D12/11/JA31/KVAR |  |  |  | CDC | 240 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛31線 | 愛31線 |  | 愛31線A1 | [17 empty] | 1-F4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛31線A1 | 11KV愛31線 R相AMP | FEEDER | D12/11/JA31/I_R |  |  |  | CDC | 241 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛31線 | 愛31線 |  | 愛31線A2 | [17 empty] | 1-F5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛31線A2 | 11KV愛31線 S相AMP | FEEDER | D12/11/JA31/I_S |  |  |  | CDC | 242 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛31線 | 愛31線 |  | 愛31線A3 | [17 empty] | 1-F6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛31線A3 | 11KV愛31線 T相AMP | FEEDER | D12/11/JA31/I_T |  |  |  | CDC | 243 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛31線 | 愛31線 |  | 愛31線A0 | [17 empty] | 1-F7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛31線A0 | 11KV愛31線 N相AMP | FEEDER | D12/11/JA31/I_N |  |  |  | CDC | 244 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛32線 | 愛32線 |  | 愛32線KVAR | [17 empty] | 1-F8 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛32線KVAR | 11KV愛32線 KVAR | FEEDER | D12/11/JA32/KVAR |  |  |  | CDC | 245 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛32線 | 愛32線 |  | 愛32線A1 | [17 empty] | 1-F9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛32線A1 | 11KV愛32線 R相AMP | FEEDER | D12/11/JA32/I_R |  |  |  | CDC | 246 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛32線 | 愛32線 |  | 愛32線A2 | [17 empty] | 1-FA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛32線A2 | 11KV愛32線 S相AMP | FEEDER | D12/11/JA32/I_S |  |  |  | CDC | 247 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛32線 | 愛32線 |  | 愛32線A3 | [17 empty] | 1-FB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛32線A3 | 11KV愛32線 T相AMP | FEEDER | D12/11/JA32/I_T |  |  |  | CDC | 248 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛32線 | 愛32線 |  | 愛32線A0 | [17 empty] | 1-FC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛32線A0 | 11KV愛32線 N相AMP | FEEDER | D12/11/JA32/I_N |  |  |  | CDC | 249 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛33線 | 愛33線 |  | 愛33線KVAR | [17 empty] | 1-FD | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛33線KVAR | 11KV愛33線 KVAR | FEEDER | D12/11/JA33/KVAR |  |  |  | CDC | 250 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛33線 | 愛33線 |  | 愛33線A1 | [17 empty] | 1-FE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛33線A1 | 11KV愛33線 R相AMP | FEEDER | D12/11/JA33/I_R |  |  |  | CDC | 251 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛33線 | 愛33線 |  | 愛33線A2 | [17 empty] | 1-FF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛33線A2 | 11KV愛33線 S相AMP | FEEDER | D12/11/JA33/I_S |  |  |  | CDC | 252 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛33線 | 愛33線 |  | 愛33線A3 | [17 empty] | 2-82 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛33線A3 | 11KV愛33線 T相AMP | FEEDER | D12/11/JA33/I_T |  |  |  | CDC | 253 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛33線 | 愛33線 |  | 愛33線A0 | [17 empty] | 2-83 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛33線A0 | 11KV愛33線 N相AMP | FEEDER | D12/11/JA33/I_N |  |  |  | CDC | 254 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛34線 | 愛34線 |  | 愛34線KVAR | [17 empty] | 2-84 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛34線KVAR | 11KV愛34線 KVAR | FEEDER | D12/11/JA34/KVAR |  |  |  | CDC | 255 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛34線 | 愛34線 |  | 愛34線A1 | [17 empty] | 2-85 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛34線A1 | 11KV愛34線 R相AMP | FEEDER | D12/11/JA34/I_R |  |  |  | CDC | 256 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛34線 | 愛34線 |  | 愛34線A2 | [17 empty] | 2-86 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛34線A2 | 11KV愛34線 S相AMP | FEEDER | D12/11/JA34/I_S |  |  |  | CDC | 257 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛34線 | 愛34線 |  | 愛34線A3 | [17 empty] | 2-87 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛34線A3 | 11KV愛34線 T相AMP | FEEDER | D12/11/JA34/I_T |  |  |  | CDC | 258 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛34線 | 愛34線 |  | 愛34線A0 | [17 empty] | 2-88 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛34線A0 | 11KV愛34線 N相AMP | FEEDER | D12/11/JA34/I_N |  |  |  | CDC | 259 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛35線 | 愛35線 |  | 愛35線KVAR | [17 empty] | 2-89 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛35線KVAR | 11KV愛35線 KVAR | FEEDER | D12/11/JA35/KVAR |  |  |  | CDC | 260 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛35線 | 愛35線 |  | 愛35線A1 | [17 empty] | 2-8A | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛35線A1 | 11KV愛35線 R相AMP | FEEDER | D12/11/JA35/I_R |  |  |  | CDC | 261 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛35線 | 愛35線 |  | 愛35線A2 | [17 empty] | 2-8B | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛35線A2 | 11KV愛35線 S相AMP | FEEDER | D12/11/JA35/I_S |  |  |  | CDC | 262 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛35線 | 愛35線 |  | 愛35線A3 | [17 empty] | 2-8C | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛35線A3 | 11KV愛35線 T相AMP | FEEDER | D12/11/JA35/I_T |  |  |  | CDC | 263 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛35線 | 愛35線 |  | 愛35線A0 | [17 empty] | 2-8D | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛35線A0 | 11KV愛35線 N相AMP | FEEDER | D12/11/JA35/I_N |  |  |  | CDC | 264 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛36線 | 愛36線 |  | 愛36線KVAR | [17 empty] | 2-94 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛36線KVAR | 11KV愛36線 KVAR | FEEDER | D12/11/JA36/KVAR |  |  |  | CDC | 265 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛36線 | 愛36線 |  | 愛36線A1 | [17 empty] | 2-95 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛36線A1 | 11KV愛36線 R相AMP | FEEDER | D12/11/JA36/I_R |  |  |  | CDC | 266 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛36線 | 愛36線 |  | 愛36線A2 | [17 empty] | 2-96 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛36線A2 | 11KV愛36線 S相AMP | FEEDER | D12/11/JA36/I_S |  |  |  | CDC | 267 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛36線 | 愛36線 |  | 愛36線A3 | [17 empty] | 2-97 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛36線A3 | 11KV愛36線 T相AMP | FEEDER | D12/11/JA36/I_T |  |  |  | CDC | 268 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛36線 | 愛36線 |  | 愛36線A0 | [17 empty] | 2-98 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛36線A0 | 11KV愛36線 N相AMP | FEEDER | D12/11/JA36/I_N |  |  |  | CDC | 269 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛37線 | 愛37線 |  | 愛37線KVAR | [17 empty] | 2-99 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛37線KVAR | 11KV愛37線 KVAR | FEEDER | D12/11/JA37/KVAR |  |  |  | CDC | 270 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛37線 | 愛37線 |  | 愛37線A1 | [17 empty] | 2-9A | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛37線A1 | 11KV愛37線 R相AMP | FEEDER | D12/11/JA37/I_R |  |  |  | CDC | 271 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛37線 | 愛37線 |  | 愛37線A2 | [17 empty] | 2-9B | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛37線A2 | 11KV愛37線 S相AMP | FEEDER | D12/11/JA37/I_S |  |  |  | CDC | 272 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛37線 | 愛37線 |  | 愛37線A3 | [17 empty] | 2-9C | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛37線A3 | 11KV愛37線 T相AMP | FEEDER | D12/11/JA37/I_T |  |  |  | CDC | 273 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛37線 | 愛37線 |  | 愛37線A0 | [17 empty] | 2-9D | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛37線A0 | 11KV愛37線 N相AMP | FEEDER | D12/11/JA37/I_N |  |  |  | CDC | 274 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛38線 | 愛38線 |  | 愛38線KVAR | [17 empty] | 2-9E | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛38線KVAR | 11KV愛38線 KVAR | FEEDER | D12/11/JA38/KVAR |  |  |  | CDC | 275 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛38線 | 愛38線 |  | 愛38線A1 | [17 empty] | 2-9F | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛38線A1 | 11KV愛38線 R相AMP | FEEDER | D12/11/JA38/I_R |  |  |  | CDC | 276 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛38線 | 愛38線 |  | 愛38線A2 | [17 empty] | 2-A0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛38線A2 | 11KV愛38線 S相AMP | FEEDER | D12/11/JA38/I_S |  |  |  | CDC | 277 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛38線 | 愛38線 |  | 愛38線A3 | [17 empty] | 2-A1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛38線A3 | 11KV愛38線 T相AMP | FEEDER | D12/11/JA38/I_T |  |  |  | CDC | 278 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛38線 | 愛38線 |  | 愛38線A0 | [17 empty] | 2-A2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛38線A0 | 11KV愛38線 N相AMP | FEEDER | D12/11/JA38/I_N |  |  |  | CDC | 279 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛39線 | 愛39線 |  | 愛39線KVAR | [17 empty] | 2-A3 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛39線KVAR | 11KV愛39線 KVAR | FEEDER | D12/11/JA39/KVAR |  |  |  | CDC | 280 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛39線 | 愛39線 |  | 愛39線A1 | [17 empty] | 2-A4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛39線A1 | 11KV愛39線 R相AMP | FEEDER | D12/11/JA39/I_R |  |  |  | CDC | 281 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛39線 | 愛39線 |  | 愛39線A2 | [17 empty] | 2-A5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛39線A2 | 11KV愛39線 S相AMP | FEEDER | D12/11/JA39/I_S |  |  |  | CDC | 282 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛39線 | 愛39線 |  | 愛39線A3 | [17 empty] | 2-A6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛39線A3 | 11KV愛39線 T相AMP | FEEDER | D12/11/JA39/I_T |  |  |  | CDC | 283 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛39線 | 愛39線 |  | 愛39線A0 | [17 empty] | 2-A7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛39線A0 | 11KV愛39線 N相AMP | FEEDER | D12/11/JA39/I_N |  |  |  | CDC | 284 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛40線 | 愛40線 |  | 愛40線KVAR | [17 empty] | 2-A8 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛40線KVAR | 11KV愛40線 KVAR | FEEDER | D12/11/JA40/KVAR |  |  |  | CDC | 285 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛40線 | 愛40線 |  | 愛40線A1 | [17 empty] | 2-A9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛40線A1 | 11KV愛40線 R相AMP | FEEDER | D12/11/JA40/I_R |  |  |  | CDC | 286 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛40線 | 愛40線 |  | 愛40線A2 | [17 empty] | 2-AA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛40線A2 | 11KV愛40線 S相AMP | FEEDER | D12/11/JA40/I_S |  |  |  | CDC | 287 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛40線 | 愛40線 |  | 愛40線A3 | [17 empty] | 2-AB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛40線A3 | 11KV愛40線 T相AMP | FEEDER | D12/11/JA40/I_T |  |  |  | CDC | 288 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | 愛40線 | 愛40線 |  | 愛40線A0 | [17 empty] | 2-AC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛40線A0 | 11KV愛40線 N相AMP | FEEDER | D12/11/JA40/I_N |  |  |  | CDC | 289 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5A線 | 愛5A線 |  | 愛5A線KVAR | [17 empty] | 2-E6 | [5 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5A線KVAR | 23KV愛5A線 KVAR | FEEDER | D12/22/JA5A/KVAR |  |  |  | CDC | 290 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5A線 | 愛5A線 |  | 愛5A線A1 | [17 empty] | 2-E7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5A線A1 | 23KV愛5A線 R相AMP | FEEDER | D12/22/JA5A/I_R |  |  |  | CDC | 291 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5A線 | 愛5A線 |  | 愛5A線A2 | [17 empty] | 2-E8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5A線A2 | 23KV愛5A線 S相AMP | FEEDER | D12/22/JA5A/I_S |  |  |  | CDC | 292 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5A線 | 愛5A線 |  | 愛5A線A3 | [17 empty] | 2-E9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5A線A3 | 23KV愛5A線 T相AMP | FEEDER | D12/22/JA5A/I_T |  |  |  | CDC | 293 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5A線 | 愛5A線 |  | 愛5A線A0 | [17 empty] | 2-EA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5A線A0 | 23KV愛5A線 N相AMP | FEEDER | D12/22/JA5A/I_N |  |  |  | CDC | 294 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5B線 | 愛5B線 |  | 愛5B線KVAR | [17 empty] | 2-EB | [5 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5B線KVAR | 23KV愛5B線 KVAR | FEEDER | D12/22/JA5B/KVAR |  |  |  | CDC | 295 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5B線 | 愛5B線 |  | 愛5B線A1 | [17 empty] | 2-EC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5B線A1 | 23KV愛5B線 R相AMP | FEEDER | D12/22/JA5B/I_R |  |  |  | CDC | 296 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5B線 | 愛5B線 |  | 愛5B線A2 | [17 empty] | 2-ED | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5B線A2 | 23KV愛5B線 S相AMP | FEEDER | D12/22/JA5B/I_S |  |  |  | CDC | 297 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5B線 | 愛5B線 |  | 愛5B線A3 | [17 empty] | 2-EE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5B線A3 | 23KV愛5B線 T相AMP | FEEDER | D12/22/JA5B/I_T |  |  |  | CDC | 298 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5B線 | 愛5B線 |  | 愛5B線A0 | [17 empty] | 2-EF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5B線A0 | 23KV愛5B線 N相AMP | FEEDER | D12/22/JA5B/I_N |  |  |  | CDC | 299 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5C線 | 愛5C線 |  | 愛5C線KVAR | [17 empty] | 2-F0 | [5 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5C線KVAR | 23KV愛5C線 KVAR | FEEDER | D12/22/JA5C/KVAR |  |  |  | CDC | 300 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5C線 | 愛5C線 |  | 愛5C線A1 | [17 empty] | 2-F1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5C線A1 | 23KV愛5C線 R相AMP | FEEDER | D12/22/JA5C/I_R |  |  |  | CDC | 301 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5C線 | 愛5C線 |  | 愛5C線A2 | [17 empty] | 2-F2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5C線A2 | 23KV愛5C線 S相AMP | FEEDER | D12/22/JA5C/I_S |  |  |  | CDC | 302 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5C線 | 愛5C線 |  | 愛5C線A3 | [17 empty] | 2-F3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5C線A3 | 23KV愛5C線 T相AMP | FEEDER | D12/22/JA5C/I_T |  |  |  | CDC | 303 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5C線 | 愛5C線 |  | 愛5C線A0 | [17 empty] | 2-F4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5C線A0 | 23KV愛5C線 N相AMP | FEEDER | D12/22/JA5C/I_N |  |  |  | CDC | 304 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5D線 | 愛5D線 |  | 愛5D線KVAR | [17 empty] | 2-F5 | [5 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5D線KVAR | 23KV愛5D線 KVAR | FEEDER | D12/22/JA5D/KVAR |  |  |  | CDC | 305 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5D線 | 愛5D線 |  | 愛5D線A1 | [17 empty] | 2-F6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5D線A1 | 23KV愛5D線 R相AMP | FEEDER | D12/22/JA5D/I_R |  |  |  | CDC | 306 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5D線 | 愛5D線 |  | 愛5D線A2 | [17 empty] | 2-F7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5D線A2 | 23KV愛5D線 S相AMP | FEEDER | D12/22/JA5D/I_S |  |  |  | CDC | 307 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5D線 | 愛5D線 |  | 愛5D線A3 | [17 empty] | 2-F8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5D線A3 | 23KV愛5D線 T相AMP | FEEDER | D12/22/JA5D/I_T |  |  |  | CDC | 308 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5D線 | 愛5D線 |  | 愛5D線A0 | [17 empty] | 2-F9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5D線A0 | 23KV愛5D線 N相AMP | FEEDER | D12/22/JA5D/I_N |  |  |  | CDC | 309 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5F線 | 愛5F線 |  | 愛5F線KVAR | [17 empty] | 2-FA | [5 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5F線KVAR | 23KV愛5F線 KVAR | FEEDER | D12/22/JA5F/KVAR |  |  |  | CDC | 310 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5F線 | 愛5F線 |  | 愛5F線A1 | [17 empty] | 2-FB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5F線A1 | 23KV愛5F線 R相AMP | FEEDER | D12/22/JA5F/I_R |  |  |  | CDC | 311 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5F線 | 愛5F線 |  | 愛5F線A2 | [17 empty] | 2-FC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5F線A2 | 23KV愛5F線 S相AMP | FEEDER | D12/22/JA5F/I_S |  |  |  | CDC | 312 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5F線 | 愛5F線 |  | 愛5F線A3 | [17 empty] | 2-FD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5F線A3 | 23KV愛5F線 T相AMP | FEEDER | D12/22/JA5F/I_T |  |  |  | CDC | 313 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5F線 | 愛5F線 |  | 愛5F線A0 | [17 empty] | 2-FE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5F線A0 | 23KV愛5F線 N相AMP | FEEDER | D12/22/JA5F/I_N |  |  |  | CDC | 314 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5G線 | 愛5G線 |  | 愛5G線KVAR | [17 empty] | 3-82 | [5 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5G線KVAR | 23KV愛5G線 KVAR | FEEDER | D12/22/JA5G/KVAR |  |  |  | CDC | 315 | GENERICAIPoint | DS042_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5G線 | 愛5G線 |  | 愛5G線A1 | [17 empty] | 3-83 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5G線A1 | 23KV愛5G線 R相AMP | FEEDER | D12/22/JA5G/I_R |  |  |  | CDC | 316 | GENERICAIPoint | DS042_L3 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5G線 | 愛5G線 |  | 愛5G線A2 | [17 empty] | 3-84 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5G線A2 | 23KV愛5G線 S相AMP | FEEDER | D12/22/JA5G/I_S |  |  |  | CDC | 317 | GENERICAIPoint | DS042_L3 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5G線 | 愛5G線 |  | 愛5G線A3 | [17 empty] | 3-85 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5G線A3 | 23KV愛5G線 T相AMP | FEEDER | D12/22/JA5G/I_T |  |  |  | CDC | 318 | GENERICAIPoint | DS042_L3 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5G線 | 愛5G線 |  | 愛5G線A0 | [17 empty] | 3-86 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5G線A0 | 23KV愛5G線 N相AMP | FEEDER | D12/22/JA5G/I_N |  |  |  | CDC | 319 | GENERICAIPoint | DS042_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5H線 | 愛5H線 |  | 愛5H線KVAR | [17 empty] | 3-87 | [5 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5H線KVAR | 23KV愛5H線 KVAR | FEEDER | D12/22/JA5H/KVAR |  |  |  | CDC | 320 | GENERICAIPoint | DS042_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5H線 | 愛5H線 |  | 愛5H線A1 | [17 empty] | 3-88 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5H線A1 | 23KV愛5H線 R相AMP | FEEDER | D12/22/JA5H/I_R |  |  |  | CDC | 321 | GENERICAIPoint | DS042_L3 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5H線 | 愛5H線 |  | 愛5H線A2 | [17 empty] | 3-89 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5H線A2 | 23KV愛5H線 S相AMP | FEEDER | D12/22/JA5H/I_S |  |  |  | CDC | 322 | GENERICAIPoint | DS042_L3 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5H線 | 愛5H線 |  | 愛5H線A3 | [17 empty] | 3-8A | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5H線A3 | 23KV愛5H線 T相AMP | FEEDER | D12/22/JA5H/I_T |  |  |  | CDC | 323 | GENERICAIPoint | DS042_L3 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5H線 | 愛5H線 |  | 愛5H線A0 | [17 empty] | 3-8B | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5H線A0 | 23KV愛5H線 N相AMP | FEEDER | D12/22/JA5H/I_N |  |  |  | CDC | 324 | GENERICAIPoint | DS042_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5K線 | 愛5K線 |  | 愛5K線KVAR | [17 empty] | 3-8C | [5 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5K線KVAR | 23KV愛5K線 KVAR | FEEDER | D12/22/JA5K/KVAR |  |  |  | CDC | 325 | GENERICAIPoint | DS042_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5K線 | 愛5K線 |  | 愛5K線A1 | [17 empty] | 3-8D | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5K線A1 | 23KV愛5K線 R相AMP | FEEDER | D12/22/JA5K/I_R |  |  |  | CDC | 326 | GENERICAIPoint | DS042_L3 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5K線 | 愛5K線 |  | 愛5K線A2 | [17 empty] | 3-8E | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5K線A2 | 23KV愛5K線 S相AMP | FEEDER | D12/22/JA5K/I_S |  |  |  | CDC | 327 | GENERICAIPoint | DS042_L3 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5K線 | 愛5K線 |  | 愛5K線A3 | [17 empty] | 3-8F | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5K線A3 | 23KV愛5K線 T相AMP | FEEDER | D12/22/JA5K/I_T |  |  |  | CDC | 328 | GENERICAIPoint | DS042_L3 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛5K線 | 愛5K線 |  | 愛5K線A0 | [17 empty] | 3-90 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛5K線A0 | 23KV愛5K線 N相AMP | FEEDER | D12/22/JA5K/I_N |  |  |  | CDC | 329 | GENERICAIPoint | DS042_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛71線 | 愛71線 |  | 愛71線KVAR | [17 empty] | 2-B6 | [5 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛71線KVAR | 23KV愛71線 KVAR | FEEDER | D12/22/JA71/KVAR |  |  |  | CDC | 330 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛71線 | 愛71線 |  | 愛71線A1 | [17 empty] | 2-B7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛71線A1 | 23KV愛71線 R相AMP | FEEDER | D12/22/JA71/I_R |  |  |  | CDC | 331 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛71線 | 愛71線 |  | 愛71線A2 | [17 empty] | 2-B8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛71線A2 | 23KV愛71線 S相AMP | FEEDER | D12/22/JA71/I_S |  |  |  | CDC | 332 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛71線 | 愛71線 |  | 愛71線A3 | [17 empty] | 2-B9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛71線A3 | 23KV愛71線 T相AMP | FEEDER | D12/22/JA71/I_T |  |  |  | CDC | 333 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛71線 | 愛71線 |  | 愛71線A0 | [17 empty] | 2-BA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛71線A0 | 23KV愛71線 N相AMP | FEEDER | D12/22/JA71/I_N |  |  |  | CDC | 334 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛72線 | 愛72線 |  | 愛72線KVAR | [17 empty] | 2-BB | [5 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛72線KVAR | 23KV愛72線 KVAR | FEEDER | D12/22/JA72/KVAR |  |  |  | CDC | 335 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛72線 | 愛72線 |  | 愛72線A1 | [17 empty] | 2-BC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛72線A1 | 23KV愛72線 R相AMP | FEEDER | D12/22/JA72/I_R |  |  |  | CDC | 336 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛72線 | 愛72線 |  | 愛72線A2 | [17 empty] | 2-BD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛72線A2 | 23KV愛72線 S相AMP | FEEDER | D12/22/JA72/I_S |  |  |  | CDC | 337 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛72線 | 愛72線 |  | 愛72線A3 | [17 empty] | 2-BE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛72線A3 | 23KV愛72線 T相AMP | FEEDER | D12/22/JA72/I_T |  |  |  | CDC | 338 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛72線 | 愛72線 |  | 愛72線A0 | [17 empty] | 2-BF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛72線A0 | 23KV愛72線 N相AMP | FEEDER | D12/22/JA72/I_N |  |  |  | CDC | 339 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛73線 | 愛73線 |  | 愛73線KVAR | [17 empty] | 2-C2 | [5 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛73線KVAR | 23KV愛73線 KVAR | FEEDER | D12/22/JA73/KVAR |  |  |  | CDC | 340 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛73線 | 愛73線 |  | 愛73線A1 | [17 empty] | 2-C3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛73線A1 | 23KV愛73線 R相AMP | FEEDER | D12/22/JA73/I_R |  |  |  | CDC | 341 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛73線 | 愛73線 |  | 愛73線A2 | [17 empty] | 2-C4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛73線A2 | 23KV愛73線 S相AMP | FEEDER | D12/22/JA73/I_S |  |  |  | CDC | 342 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛73線 | 愛73線 |  | 愛73線A3 | [17 empty] | 2-C5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛73線A3 | 23KV愛73線 T相AMP | FEEDER | D12/22/JA73/I_T |  |  |  | CDC | 343 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛73線 | 愛73線 |  | 愛73線A0 | [17 empty] | 2-C6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛73線A0 | 23KV愛73線 N相AMP | FEEDER | D12/22/JA73/I_N |  |  |  | CDC | 344 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛74線 | 愛74線 |  | 愛74線KVAR | [17 empty] | 2-C7 | [5 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛74線KVAR | 23KV愛74線 KVAR | FEEDER | D12/22/JA74/KVAR |  |  |  | CDC | 345 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛74線 | 愛74線 |  | 愛74線A1 | [17 empty] | 2-C8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛74線A1 | 23KV愛74線 R相AMP | FEEDER | D12/22/JA74/I_R |  |  |  | CDC | 346 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛74線 | 愛74線 |  | 愛74線A2 | [17 empty] | 2-C9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛74線A2 | 23KV愛74線 S相AMP | FEEDER | D12/22/JA74/I_S |  |  |  | CDC | 347 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛74線 | 愛74線 |  | 愛74線A3 | [17 empty] | 2-CA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛74線A3 | 23KV愛74線 T相AMP | FEEDER | D12/22/JA74/I_T |  |  |  | CDC | 348 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛74線 | 愛74線 |  | 愛74線A0 | [17 empty] | 2-CB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛74線A0 | 23KV愛74線 N相AMP | FEEDER | D12/22/JA74/I_N |  |  |  | CDC | 349 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛75線 | 愛75線 |  | 愛75線KVAR | [17 empty] | 2-CC | [5 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛75線KVAR | 23KV愛75線 KVAR | FEEDER | D12/22/JA75/KVAR |  |  |  | CDC | 350 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛75線 | 愛75線 |  | 愛75線A1 | [17 empty] | 2-CD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛75線A1 | 23KV愛75線 R相AMP | FEEDER | D12/22/JA75/I_R |  |  |  | CDC | 351 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛75線 | 愛75線 |  | 愛75線A2 | [17 empty] | 2-CE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛75線A2 | 23KV愛75線 S相AMP | FEEDER | D12/22/JA75/I_S |  |  |  | CDC | 352 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛75線 | 愛75線 |  | 愛75線A3 | [17 empty] | 2-CF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛75線A3 | 23KV愛75線 T相AMP | FEEDER | D12/22/JA75/I_T |  |  |  | CDC | 353 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛75線 | 愛75線 |  | 愛75線A0 | [17 empty] | 2-D0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛75線A0 | 23KV愛75線 N相AMP | FEEDER | D12/22/JA75/I_N |  |  |  | CDC | 354 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛76線 | 愛76線 |  | 愛76線KVAR | [17 empty] | 2-D1 | [5 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛76線KVAR | 23KV愛76線 KVAR | FEEDER | D12/22/JA76/KVAR |  |  |  | CDC | 355 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛76線 | 愛76線 |  | 愛76線A1 | [17 empty] | 2-D2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛76線A1 | 23KV愛76線 R相AMP | FEEDER | D12/22/JA76/I_R |  |  |  | CDC | 356 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛76線 | 愛76線 |  | 愛76線A2 | [17 empty] | 2-D3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛76線A2 | 23KV愛76線 S相AMP | FEEDER | D12/22/JA76/I_S |  |  |  | CDC | 357 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛76線 | 愛76線 |  | 愛76線A3 | [17 empty] | 2-D4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛76線A3 | 23KV愛76線 T相AMP | FEEDER | D12/22/JA76/I_T |  |  |  | CDC | 358 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛76線 | 愛76線 |  | 愛76線A0 | [17 empty] | 2-D5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛76線A0 | 23KV愛76線 N相AMP | FEEDER | D12/22/JA76/I_N |  |  |  | CDC | 359 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛77線 | 愛77線 |  | 愛77線KVAR | [17 empty] | 2-D6 | [5 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛77線KVAR | 23KV愛77線 KVAR | FEEDER | D12/22/JA77/KVAR |  |  |  | CDC | 360 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛77線 | 愛77線 |  | 愛77線A1 | [17 empty] | 2-D7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛77線A1 | 23KV愛77線 R相AMP | FEEDER | D12/22/JA77/I_R |  |  |  | CDC | 361 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛77線 | 愛77線 |  | 愛77線A2 | [17 empty] | 2-D8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛77線A2 | 23KV愛77線 S相AMP | FEEDER | D12/22/JA77/I_S |  |  |  | CDC | 362 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛77線 | 愛77線 |  | 愛77線A3 | [17 empty] | 2-D9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛77線A3 | 23KV愛77線 T相AMP | FEEDER | D12/22/JA77/I_T |  |  |  | CDC | 363 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛77線 | 愛77線 |  | 愛77線A0 | [17 empty] | 2-DA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛77線A0 | 23KV愛77線 N相AMP | FEEDER | D12/22/JA77/I_N |  |  |  | CDC | 364 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛78線 | 愛78線 |  | 愛78線KVAR | [17 empty] | 2-DB | [5 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛78線KVAR | 23KV愛78線 KVAR | FEEDER | D12/22/JA78/KVAR |  |  |  | CDC | 365 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛78線 | 愛78線 |  | 愛78線A1 | [17 empty] | 2-DC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛78線A1 | 23KV愛78線 R相AMP | FEEDER | D12/22/JA78/I_R |  |  |  | CDC | 366 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R500R | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛78線 | 愛78線 |  | 愛78線A2 | [17 empty] | 2-DD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛78線A2 | 23KV愛78線 S相AMP | FEEDER | D12/22/JA78/I_S |  |  |  | CDC | 367 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛78線 | 愛78線 |  | 愛78線A3 | [17 empty] | 2-DE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛78線A3 | 23KV愛78線 T相AMP | FEEDER | D12/22/JA78/I_T |  |  |  | CDC | 368 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C05R0500 | 450.000000 | 450.000000 | 500.000000 | 500.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | 愛78線 | 愛78線 |  | 愛78線A0 | [17 empty] | 2-DF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_2 | [8 empty] | 仁愛DS.愛78線A0 | 23KV愛78線 N相AMP | FEEDER | D12/22/JA78/I_N |  |  |  | CDC | 369 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 0 |  | 1500TIE | 1500TIE |  | I | [17 empty] | 1-98 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.1500TIE_AMP | 1500TIE AMP | TIE | D12/161/1500/I_R |  |  |  | CDC | 370 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | _100 | 100 |  | I_R | [17 empty] | 1-CB | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.11KV_100_A1 | 11KV 100 R相AMP | TIE | D12/11/100/I_R |  |  |  | CDC | 371 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | _100 | 100 |  | I_S | [17 empty] | 1-CC | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.11KV_100_A2 | 11KV 100 S相AMP | TIE | D12/11/100/I_S |  |  |  | CDC | 372 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | _100 | 100 |  | I_T | [17 empty] | 1-CD | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.11KV_100_A3 | 11KV 100 T相AMP | TIE | D12/11/100/I_T |  |  |  | CDC | 373 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | _200 | 200 |  | I_R | [17 empty] | 2-AD | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.11KV_200_A1 | 11KV 200 R相AMP | TIE | D12/11/200/I_R |  |  |  | CDC | 374 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | _200 | 200 |  | I_S | [17 empty] | 2-AE | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.11KV_200_A2 | 11KV 200 S相AMP | TIE | D12/11/200/I_S |  |  |  | CDC | 375 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 11 | 11kV | _200 | 200 |  | I_T | [17 empty] | 2-AF | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.11KV_200_A3 | 11KV 200 T相AMP | TIE | D12/11/200/I_T |  |  |  | CDC | 376 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | _400 | 400 |  | I_R | [17 empty] | 3-91 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.23KV_400_A1 | 23KV 400 R相AMP | TIE | D12/22/400/I_R |  |  |  | CDC | 377 | GENERICAIPoint | DS042_L3 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | _400 | 400 |  | I_S | [17 empty] | 3-92 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.23KV_400_A2 | 23KV 400 S相AMP | TIE | D12/22/400/I_S |  |  |  | CDC | 378 | GENERICAIPoint | DS042_L3 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 22 | 22kV | _400 | 400 |  | I_T | [17 empty] | 3-93 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.23KV_400_A3 | 23KV 400 T相AMP | TIE | D12/22/400/I_T |  |  |  | CDC | 379 | GENERICAIPoint | DS042_L3 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MW | [17 empty] | 1-AA | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | D12/11/310/KW |  |  |  | CDC | 380 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D12 | 仁愛DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVAR | [17 empty] | 1-AB | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | D12/11/310/KVAR |  |  |  | CDC | 381 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D12 | 仁愛DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_R | [17 empty] | 1-AC | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | D12/11/310/I_R |  |  |  | CDC | 382 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_S | [17 empty] | 1-AD | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | D12/11/310/I_S |  |  |  | CDC | 383 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_T | [17 empty] | 1-AE | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | D12/11/310/I_T |  |  |  | CDC | 384 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 0 |  | 1DTR | #1DTR |  | OilTemp | [17 empty] | 1-99 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#1DTR_OIL | #1DTR 油溫 | MTR | D12//1DTR/OilTemp |  |  |  | CDC | 385 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D12 | 仁愛DS | 0 |  | 1DTR(A) | #1DTR(A) |  | CoilTemp | [17 empty] | 1-9A | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | D12//1DTR(A)/CoilTemp |  |  |  | CDC | 386 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D12 | 仁愛DS | 0 |  | 1DTR(A) | #1DTR(A) |  | TapPosMv | [17 empty] | 1-9C |  | 1-3B |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | D12//1DTR(A)/TapPosMv |  |  |  | CDC | 387 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D12 | 仁愛DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MW | [17 empty] | 1-CE | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | D12/11/320/KW |  |  |  | CDC | 388 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D12 | 仁愛DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVAR | [17 empty] | 1-CF | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | D12/11/320/KVAR |  |  |  | CDC | 389 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D12 | 仁愛DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_R | [17 empty] | 1-D0 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | D12/11/320/I_R |  |  |  | CDC | 390 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_S | [17 empty] | 1-D1 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | D12/11/320/I_S |  |  |  | CDC | 391 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_T | [17 empty] | 1-D2 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | D12/11/320/I_T |  |  |  | CDC | 392 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 0 |  | 1DTR(B) | #1DTR(B) |  | CoilTemp | [17 empty] | 1-9B | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | D12//1DTR(B)/CoilTemp |  |  |  | CDC | 393 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D12 | 仁愛DS | 0 |  | 1DTR(B) | #1DTR(B) |  | TapPosMv | [17 empty] | 1-9D |  | 1-3D |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | D12//1DTR(B)/TapPosMv |  |  |  | CDC | 394 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D12 | 仁愛DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MW | [17 empty] | 1-ED | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | D12/11/330/KW |  |  |  | CDC | 395 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D12 | 仁愛DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVAR | [17 empty] | 1-EE | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | D12/11/330/KVAR |  |  |  | CDC | 396 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D12 | 仁愛DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_R | [17 empty] | 1-EF | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | D12/11/330/I_R |  |  |  | CDC | 397 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_S | [17 empty] | 1-F0 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | D12/11/330/I_S |  |  |  | CDC | 398 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_T | [17 empty] | 1-F1 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | D12/11/330/I_T |  |  |  | CDC | 399 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 0 |  | 2DTR | #2DTR |  | OilTemp | [17 empty] | 1-9E | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#2DTR_OIL | #2DTR 油溫 | MTR | D12//2DTR/OilTemp |  |  |  | CDC | 400 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D12 | 仁愛DS | 0 |  | 2DTR(A) | #2DTR(A) |  | CoilTemp | [17 empty] | 1-9F | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | D12//2DTR(A)/CoilTemp |  |  |  | CDC | 401 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D12 | 仁愛DS | 0 |  | 2DTR(A) | #2DTR(A) |  | TapPosMv | [17 empty] | 1-A1 |  | 1-3F |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | D12//2DTR(A)/TapPosMv |  |  |  | CDC | 402 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D12 | 仁愛DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MW | [17 empty] | 2-8E | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | D12/11/340/KW |  |  |  | CDC | 403 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D12 | 仁愛DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVAR | [17 empty] | 2-8F | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | D12/11/340/KVAR |  |  |  | CDC | 404 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D12 | 仁愛DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_R | [17 empty] | 2-90 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | D12/11/340/I_R |  |  |  | CDC | 405 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_S | [17 empty] | 2-91 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | D12/11/340/I_S |  |  |  | CDC | 406 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_T | [17 empty] | 2-92 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | D12/11/340/I_T |  |  |  | CDC | 407 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 0 |  | 2DTR(B) | #2DTR(B) |  | CoilTemp | [17 empty] | 1-A0 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | D12//2DTR(B)/CoilTemp |  |  |  | CDC | 408 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D12 | 仁愛DS | 0 |  | 2DTR(B) | #2DTR(B) |  | TapPosMv | [17 empty] | 1-A2 |  | 1-41 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | D12//2DTR(B)/TapPosMv |  |  |  | CDC | 409 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D12 | 仁愛DS | 0 |  | 3DTR | #3DTR二次側 |  | MW | [17 empty] | 2-B0 | [5 empty] | MW_-108_108(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#3DTR_MW | #3DTR二次側 MW | MTR | D12/22/350/KW |  |  |  | CDC | 410 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D12 | 仁愛DS | 0 |  | 3DTR | #3DTR二次側 |  | MVAR | [17 empty] | 2-B1 | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#3DTR_MVAR | #3DTR二次側 MVAR | MTR | D12/22/350/KVAR |  |  |  | CDC | 411 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D12 | 仁愛DS | 0 |  | 3DTR | #3DTR二次側 |  | I_R | [17 empty] | 2-B2 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#3DTR_A1 | #3DTR二次側 R相AMP | MTR | D12/22/350/I_R |  |  |  | CDC | 412 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 0 |  | 3DTR | #3DTR二次側 |  | I_S | [17 empty] | 2-B3 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#3DTR_A2 | #3DTR二次側 S相AMP | MTR | D12/22/350/I_S |  |  |  | CDC | 413 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 0 |  | 3DTR | #3DTR二次側 |  | I_T | [17 empty] | 2-B4 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#3DTR_A3 | #3DTR二次側 T相AMP | MTR | D12/22/350/I_T |  |  |  | CDC | 414 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 0 |  | 3DTR | #3DTR |  | OilTemp | [17 empty] | 1-A3 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#3DTR_OIL | #3DTR 油溫 | MTR | D12//3DTR/OilTemp |  |  |  | CDC | 415 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D12 | 仁愛DS | 0 |  | 3DTR | #3DTR |  | CoilTemp | [17 empty] | 1-A4 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#3DTR_COIL | #3DTR 線溫 | MTR | D12//3DTR/CoilTemp |  |  |  | CDC | 416 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D12 | 仁愛DS | 0 |  | 3DTR | #3DTR |  | TapPosMv | [17 empty] | 1-A5 |  | 1-43 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#3DTR_TAP | #3DTR OLTC TAP | MTR | D12//3DTR/TapPosMv |  |  |  | CDC | 417 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D12 | 仁愛DS | 0 |  | 4DTR | #4DTR二次側 |  | MW | [17 empty] | 2-E0 | [5 empty] | MW_-108_108(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#4DTR_MW | #4DTR二次側 MW | MTR | D12/22/370/KW |  |  |  | CDC | 418 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D12 | 仁愛DS | 0 |  | 4DTR | #4DTR二次側 |  | MVAR | [17 empty] | 2-E1 | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#4DTR_MVAR | #4DTR二次側 MVAR | MTR | D12/22/370/KVAR |  |  |  | CDC | 419 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D12 | 仁愛DS | 0 |  | 4DTR | #4DTR二次側 |  | I_R | [17 empty] | 2-E2 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#4DTR_A1 | #4DTR二次側 R相AMP | MTR | D12/22/370/I_R |  |  |  | CDC | 420 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 0 |  | 4DTR | #4DTR二次側 |  | I_S | [17 empty] | 2-E3 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#4DTR_A2 | #4DTR二次側 S相AMP | MTR | D12/22/370/I_S |  |  |  | CDC | 421 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 0 |  | 4DTR | #4DTR二次側 |  | I_T | [17 empty] | 2-E4 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#4DTR_A3 | #4DTR二次側 T相AMP | MTR | D12/22/370/I_T |  |  |  | CDC | 422 | GENERICAIPoint | DS042_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D12 | 仁愛DS | 0 |  | 4DTR | #4DTR |  | OilTemp | [17 empty] | 1-A6 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#4DTR_OIL | #4DTR 油溫 | MTR | D12//4DTR/OilTemp |  |  |  | CDC | 423 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D12 | 仁愛DS | 0 |  | 4DTR | #4DTR |  | CoilTemp | [17 empty] | 1-A7 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#4DTR_COIL | #4DTR 線溫 | MTR | D12//4DTR/CoilTemp |  |  |  | CDC | 424 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D12 | 仁愛DS | 0 |  | 4DTR | #4DTR |  | TapPosMv | [17 empty] | 1-A8 |  | 1-45 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 仁愛DS.#4DTR_TAP | #4DTR OLTC TAP | MTR | D12//4DTR/TapPosMv |  |  |  | CDC | 425 | GENERICAIPoint | DS042_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D12 | 仁愛DS | 0 |  |  |  |  | DCV_N | [17 empty] | 3-95 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.直流N電源電壓 | 直流N電源電壓 | OTHER | D12/0/StaDev/DCV_N |  |  |  | CDC | 426 | GENERICAIPoint | DS042_L3 | CDC2_AI |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D12 | 仁愛DS | 0 |  |  |  |  | DCV_P | [17 empty] | 3-94 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 仁愛DS.直流P電源電壓 | 直流P電源電壓 | OTHER | D12/0/StaDev/DCV_P |  |  |  | CDC | 427 | GENERICAIPoint | DS042_L3 | CDC2_AI |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D12 | 仁愛DS | 161 | 161kV | 1510 | 嘉義仁愛山線(1510) |  | PHA | [17 empty] | 1-00-06 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.1510_PHA | 嘉義仁愛山線(1510) 相間RY | LINE161 | D12/161/1510/PHA |  |  |  | CDC | 428 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1510 | 嘉義仁愛山線(1510) |  | GDA | [17 empty] | 1-00-07 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.1510_GDA | 嘉義仁愛山線(1510) 接地RY | LINE161 | D12/161/1510/GDA |  |  |  | CDC | 429 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1510 | 嘉義仁愛山線(1510) |  | 87A | [17 empty] | 1-00-05 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.1510_87A | 嘉義仁愛山線(1510) 87RY | LINE161 | D12/161/1510/87A |  |  |  | CDC | 430 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1510 | 嘉義仁愛山線(1510) |  | 87UL | [17 empty] | 1-30-04 |  | 1-24 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.1510_87UL | 嘉義仁愛山線(1510) 87RY U/L | LINE161 | D12/161/1510/87UL |  |  |  | CDC | 431 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 161 | 161kV | 1510 | 嘉義仁愛山線(1510) |  | CB | [17 empty] | 1-00-04 |  | 1-03 | [5 empty] | 161KV_N | [8 empty] | 仁愛DS.1510_CB | 1510(嘉義仁愛山線) CB | LINE161 | D12/161/1510/CB |  |  |  | CDC | 432 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1510 | 嘉義仁愛山線(1510) |  | 79UL | [17 empty] | 1-30-05 |  | 1-25 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.1510_79UL | 嘉義仁愛山線(1510) 79RY U/L | LINE161 | D12/161/1510/79UL |  |  |  | CDC | 433 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 161 | 161kV | 1510 | 嘉義仁愛山線(1510) |  | DS1 | 1511 | [16 empty] | 1-39-08 | 1-39-09 | 1-4A | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.1511_DS | 1511(嘉義仁愛山線) DS | LINE161 | D12/161/1510/DS1 |  |  |  | CDC | 434 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1510 | 嘉義仁愛山線(1510) |  | DS2 | 1512 | [16 empty] | 1-39-10 | 1-39-11 | 1-4B | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.1512_DS | 1512(嘉義仁愛山線) DS | LINE161 | D12/161/1510/DS2 |  |  |  | CDC | 435 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D12 | 仁愛DS | 161 | 161kV | 1510 | 嘉義仁愛山線(1510) |  | DS3 | 1513 | [16 empty] | 1-39-12 | 1-39-13 | 1-4C | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.1513_DS | 1513(嘉義仁愛山線) DS | LINE161 | D12/161/1510/DS3 |  |  |  | CDC | 436 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1510 | 嘉義仁愛山線(1510) |  | E3 | 1513E | [16 empty] | 1-39-14 | 1-39-15 | 1-4D | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.1513E_ES | 1513E(嘉義仁愛山線) ES | LINE161 | D12/161/1510/ES3 |  |  |  | CDC | 437 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D12 | 仁愛DS | 161 | 161kV | 1520 | 嘉義仁愛海線(1520) |  | PHA | [17 empty] | 1-00-02 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.1520_PHA | 嘉義仁愛海線(1520) 相間RY | LINE161 | D12/161/1520/PHA |  |  |  | CDC | 438 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1520 | 嘉義仁愛海線(1520) |  | GDA | [17 empty] | 1-00-03 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.1520_GDA | 嘉義仁愛海線(1520) 接地RY | LINE161 | D12/161/1520/GDA |  |  |  | CDC | 439 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1520 | 嘉義仁愛海線(1520) |  | 87A | [17 empty] | 1-00-01 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.1520_87A | 嘉義仁愛海線(1520) 87RY | LINE161 | D12/161/1520/87A |  |  |  | CDC | 440 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1520 | 嘉義仁愛海線(1520) |  | 87UL | [17 empty] | 1-30-02 |  | 1-22 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.1520_87UL | 嘉義仁愛海線(1520) 87RY U/L | LINE161 | D12/161/1520/87UL |  |  |  | CDC | 441 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 161 | 161kV | 1520 | 嘉義仁愛海線(1520) |  | CB | [17 empty] | 1-00-00 |  | 1-02 | [5 empty] | 161KV_N | [8 empty] | 仁愛DS.1520_CB | 1520(嘉義仁愛海線) CB | LINE161 | D12/161/1520/CB |  |  |  | CDC | 442 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1520 | 嘉義仁愛海線(1520) |  | 79UL | [17 empty] | 1-30-03 |  | 1-23 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.1520_79UL | 嘉義仁愛海線(1520) 79RY U/L | LINE161 | D12/161/1520/79UL |  |  |  | CDC | 443 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 161 | 161kV | 1520 | 嘉義仁愛海線(1520) |  | DS1 | 1521 | [16 empty] | 1-39-00 | 1-39-01 | 1-46 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.1521_DS | 1521(嘉義仁愛海線) DS | LINE161 | D12/161/1520/DS1 |  |  |  | CDC | 444 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D12 | 仁愛DS | 161 | 161kV | 1520 | 嘉義仁愛海線(1520) |  | DS2 | 1522 | [16 empty] | 1-39-02 | 1-39-03 | 1-47 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.1522_DS | 1522(嘉義仁愛海線) DS | LINE161 | D12/161/1520/DS2 |  |  |  | CDC | 445 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1520 | 嘉義仁愛海線(1520) |  | DS3 | 1523 | [16 empty] | 1-39-04 | 1-39-05 | 1-48 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.1523_DS | 1523(嘉義仁愛海線) DS | LINE161 | D12/161/1520/DS3 |  |  |  | CDC | 446 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1520 | 嘉義仁愛海線(1520) |  | E3 | 1523E | [16 empty] | 1-39-06 | 1-39-07 | 1-49 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.1523E_ES | 1523E(嘉義仁愛海線) ES | LINE161 | D12/161/1520/ES3 |  |  |  | CDC | 447 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D12 | 仁愛DS | 161 | 161kV | 1530 | 仁愛北回一路(1530) |  | PHA | [17 empty] | 1-01-06 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.1530_PHA | 仁愛北回一路(1530) 相間RY | LINE161 | D12/161/1530/PHA |  |  |  | CDC | 448 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1530 | 仁愛北回一路(1530) |  | GDA | [17 empty] | 1-01-07 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.1530_GDA | 仁愛北回一路(1530) 接地RY | LINE161 | D12/161/1530/GDA |  |  |  | CDC | 449 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1530 | 仁愛北回一路(1530) |  | 87A | [17 empty] | 1-01-05 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.1530_87A | 仁愛北回一路(1530) 87RY | LINE161 | D12/161/1530/87A |  |  |  | CDC | 450 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1530 | 仁愛北回一路(1530) |  | 87UL | [17 empty] | 1-30-08 |  | 1-28 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.1530_87UL | 仁愛北回一路(1530) 87RY U/L | LINE161 | D12/161/1530/87UL |  |  |  | CDC | 451 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 161 | 161kV | 1530 | 仁愛北回一路(1530) |  | CB | [17 empty] | 1-01-04 |  | 1-05 | [5 empty] | 161KV_N | [8 empty] | 仁愛DS.1530_CB | 1530(仁愛北回一路) CB | LINE161 | D12/161/1530/CB |  |  |  | CDC | 452 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1530 | 仁愛北回一路(1530) |  | 79UL | [17 empty] | 1-30-09 |  | 1-29 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.1530_79UL | 仁愛北回一路(1530) 79RY U/L | LINE161 | D12/161/1530/79UL |  |  |  | CDC | 453 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 161 | 161kV | 1530 | 仁愛北回一路(1530) |  | DS1 | 1531 | [16 empty] | 1-3A-08 | 1-3A-09 | 1-52 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.1531_DS | 1531(仁愛北回一路) DS | LINE161 | D12/161/1530/DS1 |  |  |  | CDC | 454 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1530 | 仁愛北回一路(1530) |  | DS2 | 1532 | [16 empty] | 1-3A-10 | 1-3A-11 | 1-53 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.1532_DS | 1532(仁愛北回一路) DS | LINE161 | D12/161/1530/DS2 |  |  |  | CDC | 455 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D12 | 仁愛DS | 161 | 161kV | 1530 | 仁愛北回一路(1530) |  | DS3 | 1533 | [16 empty] | 1-3A-12 | 1-3A-13 | 1-54 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.1533_DS | 1533(仁愛北回一路) DS | LINE161 | D12/161/1530/DS3 |  |  |  | CDC | 456 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1530 | 仁愛北回一路(1530) |  | E3 | 1533E | [16 empty] | 1-3A-14 | 1-3A-15 | 1-55 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.1533E_ES | 1533E(仁愛北回一路) ES | LINE161 | D12/161/1530/ES3 |  |  |  | CDC | 457 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D12 | 仁愛DS | 161 | 161kV | 1540 | 仁愛北回二路(1540) |  | PHA | [17 empty] | 1-01-02 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.1540_PHA | 仁愛北回二路(1540) 相間RY | LINE161 | D12/161/1540/PHA |  |  |  | CDC | 458 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1540 | 仁愛北回二路(1540) |  | GDA | [17 empty] | 1-01-03 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.1540_GDA | 仁愛北回二路(1540) 接地RY | LINE161 | D12/161/1540/GDA |  |  |  | CDC | 459 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1540 | 仁愛北回二路(1540) |  | 87A | [17 empty] | 1-01-01 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.1540_87A | 仁愛北回二路(1540) 87RY | LINE161 | D12/161/1540/87A |  |  |  | CDC | 460 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1540 | 仁愛北回二路(1540) |  | 87UL | [17 empty] | 1-30-06 |  | 1-26 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.1540_87UL | 仁愛北回二路(1540) 87RY U/L | LINE161 | D12/161/1540/87UL |  |  |  | CDC | 461 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 161 | 161kV | 1540 | 仁愛北回二路(1540) |  | CB | [17 empty] | 1-01-00 |  | 1-04 | [5 empty] | 161KV_N | [8 empty] | 仁愛DS.1540_CB | 1540(仁愛北回二路) CB | LINE161 | D12/161/1540/CB |  |  |  | CDC | 462 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1540 | 仁愛北回二路(1540) |  | 79UL | [17 empty] | 1-30-07 |  | 1-27 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.1540_79UL | 仁愛北回二路(1540) 79RY U/L | LINE161 | D12/161/1540/79UL |  |  |  | CDC | 463 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 161 | 161kV | 1540 | 仁愛北回二路(1540) |  | DS1 | 1541 | [16 empty] | 1-3A-00 | 1-3A-01 | 1-4E | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.1541_DS | 1541(仁愛北回二路) DS | LINE161 | D12/161/1540/DS1 |  |  |  | CDC | 464 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D12 | 仁愛DS | 161 | 161kV | 1540 | 仁愛北回二路(1540) |  | DS2 | 1542 | [16 empty] | 1-3A-02 | 1-3A-03 | 1-4F | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.1542_DS | 1542(仁愛北回二路) DS | LINE161 | D12/161/1540/DS2 |  |  |  | CDC | 465 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1540 | 仁愛北回二路(1540) |  | DS3 | 1543 | [16 empty] | 1-3A-04 | 1-3A-05 | 1-50 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.1543_DS | 1543(仁愛北回二路) DS | LINE161 | D12/161/1540/DS3 |  |  |  | CDC | 466 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1540 | 仁愛北回二路(1540) |  | E3 | 1543E | [16 empty] | 1-3A-06 | 1-3A-07 | 1-51 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.1543E_ES | 1543E(仁愛北回二路) ES | LINE161 | D12/161/1540/ES3 |  |  |  | CDC | 467 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D12 | 仁愛DS | 11 | 11kV | JA21 | 愛21線(JA21) |  | PHA | [17 empty] | 1-10-01 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA21_PHA | 11KV愛21線(JA21) 相間RY | FEEDER | D12/11/JA21/PHA |  |  |  | CDC | 468 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA21 | 愛21線(JA21) |  | GDA | [17 empty] | 1-10-02 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA21_GDA | 11KV愛21線(JA21) 接地RY | FEEDER | D12/11/JA21/GDA |  |  |  | CDC | 469 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA21 | 愛21線(JA21) 79RY |  | 79UL | [17 empty] | 2-38-00 |  | 2-2E | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA21_79UL | 11KV愛21線(JA21) 79RY U/L | FEEDER | D12/11/JA21/FDR_RCA |  |  |  | CDC | 470 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA21_LCO | 愛21線(JA21) LCO |  | TapPosMv | [17 empty] | 2-38-01 |  | 2-2F | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA21_LCO_TAP | 11KV愛21線(JA21) LCO TAP | FEEDER | D12/11/JA21/51NA |  |  |  | CDC | 471 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA21 | JA21(11KV愛21線) |  | CB | [17 empty] | 1-10-00 |  | 1-13 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA21_CB | JA21(11KV愛21線) CB | FEEDER | D12/11/JA21/CB |  |  |  | CDC | 472 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA22 | 愛22線(JA22) |  | PHA | [17 empty] | 1-10-04 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA22_PHA | 11KV愛22線(JA22) 相間RY | FEEDER | D12/11/JA22/PHA |  |  |  | CDC | 473 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA22 | 愛22線(JA22) |  | GDA | [17 empty] | 1-10-05 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA22_GDA | 11KV愛22線(JA22) 接地RY | FEEDER | D12/11/JA22/GDA |  |  |  | CDC | 474 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA22 | 愛22線(JA22) 79RY |  | 79UL | [17 empty] | 2-38-02 |  | 2-30 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA22_79UL | 11KV愛22線(JA22) 79RY U/L | FEEDER | D12/11/JA22/FDR_RCA |  |  |  | CDC | 475 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA22_LCO | 愛22線(JA22) LCO |  | TapPosMv | [17 empty] | 2-38-03 |  | 2-31 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA22_LCO_TAP | 11KV愛22線(JA22) LCO TAP | FEEDER | D12/11/JA22/51NA |  |  |  | CDC | 476 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA22 | JA22(11KV愛22線) |  | CB | [17 empty] | 1-10-03 |  | 1-14 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA22_CB | JA22(11KV愛22線) CB | FEEDER | D12/11/JA22/CB |  |  |  | CDC | 477 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA23 | 愛23線(JA23) |  | PHA | [17 empty] | 1-10-07 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA23_PHA | 11KV愛23線(JA23) 相間RY | FEEDER | D12/11/JA23/PHA |  |  |  | CDC | 478 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA23 | 愛23線(JA23) |  | GDA | [17 empty] | 1-11-00 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA23_GDA | 11KV愛23線(JA23) 接地RY | FEEDER | D12/11/JA23/GDA |  |  |  | CDC | 479 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA23 | 愛23線(JA23) 79RY |  | 79UL | [17 empty] | 2-38-04 |  | 2-32 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA23_79UL | 11KV愛23線(JA23) 79RY U/L | FEEDER | D12/11/JA23/FDR_RCA |  |  |  | CDC | 480 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA23_LCO | 愛23線(JA23) LCO |  | TapPosMv | [17 empty] | 2-38-05 |  | 2-33 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA23_LCO_TAP | 11KV愛23線(JA23) LCO TAP | FEEDER | D12/11/JA23/51NA |  |  |  | CDC | 481 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA23 | JA23(11KV愛23線) |  | CB | [17 empty] | 1-10-06 |  | 1-15 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA23_CB | JA23(11KV愛23線) CB | FEEDER | D12/11/JA23/CB |  |  |  | CDC | 482 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA24 | 愛24線(JA24) |  | PHA | [17 empty] | 1-11-02 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA24_PHA | 11KV愛24線(JA24) 相間RY | FEEDER | D12/11/JA24/PHA |  |  |  | CDC | 483 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA24 | 愛24線(JA24) |  | GDA | [17 empty] | 1-11-03 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA24_GDA | 11KV愛24線(JA24) 接地RY | FEEDER | D12/11/JA24/GDA |  |  |  | CDC | 484 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA24 | 愛24線(JA24) 79RY |  | 79UL | [17 empty] | 2-38-06 |  | 2-34 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA24_79UL | 11KV愛24線(JA24) 79RY U/L | FEEDER | D12/11/JA24/FDR_RCA |  |  |  | CDC | 485 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA24_LCO | 愛24線(JA24) LCO |  | TapPosMv | [17 empty] | 2-38-07 |  | 2-35 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA24_LCO_TAP | 11KV愛24線(JA24) LCO TAP | FEEDER | D12/11/JA24/51NA |  |  |  | CDC | 486 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA24 | JA24(11KV愛24線) |  | CB | [17 empty] | 1-11-01 |  | 1-16 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA24_CB | JA24(11KV愛24線) CB | FEEDER | D12/11/JA24/CB |  |  |  | CDC | 487 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA25 | 愛25線(JA25) |  | PHA | [17 empty] | 1-11-05 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA25_PHA | 11KV愛25線(JA25) 相間RY | FEEDER | D12/11/JA25/PHA |  |  |  | CDC | 488 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA25 | 愛25線(JA25) |  | GDA | [17 empty] | 1-11-06 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA25_GDA | 11KV愛25線(JA25) 接地RY | FEEDER | D12/11/JA25/GDA |  |  |  | CDC | 489 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA25 | 愛25線(JA25) 79RY |  | 79UL | [17 empty] | 2-38-08 |  | 2-36 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA25_79UL | 11KV愛25線(JA25) 79RY U/L | FEEDER | D12/11/JA25/FDR_RCA |  |  |  | CDC | 490 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA25_LCO | 愛25線(JA25) LCO |  | TapPosMv | [17 empty] | 2-38-09 |  | 2-37 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA25_LCO_TAP | 11KV愛25線(JA25) LCO TAP | FEEDER | D12/11/JA25/51NA |  |  |  | CDC | 491 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA25 | JA25(11KV愛25線) |  | CB | [17 empty] | 1-11-04 |  | 1-17 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA25_CB | JA25(11KV愛25線) CB | FEEDER | D12/11/JA25/CB |  |  |  | CDC | 492 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA26 | 愛26線(JA26) |  | PHA | [17 empty] | 1-12-06 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA26_PHA | 11KV愛26線(JA26) 相間RY | FEEDER | D12/11/JA26/PHA |  |  |  | CDC | 493 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA26 | 愛26線(JA26) |  | GDA | [17 empty] | 1-12-07 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA26_GDA | 11KV愛26線(JA26) 接地RY | FEEDER | D12/11/JA26/GDA |  |  |  | CDC | 494 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA26 | 愛26線(JA26) 79RY |  | 79UL | [17 empty] | 2-38-10 |  | 2-38 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA26_79UL | 11KV愛26線(JA26) 79RY U/L | FEEDER | D12/11/JA26/FDR_RCA |  |  |  | CDC | 495 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA26_LCO | 愛26線(JA26) LCO |  | TapPosMv | [17 empty] | 2-38-11 |  | 2-39 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA26_LCO_TAP | 11KV愛26線(JA26) LCO TAP | FEEDER | D12/11/JA26/51NA |  |  |  | CDC | 496 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA26 | JA26(11KV愛26線) |  | CB | [17 empty] | 1-12-05 |  | 1-1C | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA26_CB | JA26(11KV愛26線) CB | FEEDER | D12/11/JA26/CB |  |  |  | CDC | 497 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA27 | 愛27線(JA27) |  | PHA | [17 empty] | 1-13-01 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA27_PHA | 11KV愛27線(JA27) 相間RY | FEEDER | D12/11/JA27/PHA |  |  |  | CDC | 498 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA27 | 愛27線(JA27) |  | GDA | [17 empty] | 1-13-02 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA27_GDA | 11KV愛27線(JA27) 接地RY | FEEDER | D12/11/JA27/GDA |  |  |  | CDC | 499 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA27 | 愛27線(JA27) 79RY |  | 79UL | [17 empty] | 2-38-12 |  | 2-3A | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA27_79UL | 11KV愛27線(JA27) 79RY U/L | FEEDER | D12/11/JA27/FDR_RCA |  |  |  | CDC | 500 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA27_LCO | 愛27線(JA27) LCO |  | TapPosMv | [17 empty] | 2-38-13 |  | 2-3B | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA27_LCO_TAP | 11KV愛27線(JA27) LCO TAP | FEEDER | D12/11/JA27/51NA |  |  |  | CDC | 501 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA27 | JA27(11KV愛27線) |  | CB | [17 empty] | 1-13-00 |  | 1-1D | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA27_CB | JA27(11KV愛27線) CB | FEEDER | D12/11/JA27/CB |  |  |  | CDC | 502 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA28 | 愛28線(JA28) |  | PHA | [17 empty] | 1-13-04 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA28_PHA | 11KV愛28線(JA28) 相間RY | FEEDER | D12/11/JA28/PHA |  |  |  | CDC | 503 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA28 | 愛28線(JA28) |  | GDA | [17 empty] | 1-13-05 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA28_GDA | 11KV愛28線(JA28) 接地RY | FEEDER | D12/11/JA28/GDA |  |  |  | CDC | 504 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA28 | 愛28線(JA28) 79RY |  | 79UL | [17 empty] | 2-38-14 |  | 2-3C | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA28_79UL | 11KV愛28線(JA28) 79RY U/L | FEEDER | D12/11/JA28/FDR_RCA |  |  |  | CDC | 505 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA28_LCO | 愛28線(JA28) LCO |  | TapPosMv | [17 empty] | 2-38-15 |  | 2-3D | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA28_LCO_TAP | 11KV愛28線(JA28) LCO TAP | FEEDER | D12/11/JA28/51NA |  |  |  | CDC | 506 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA28 | JA28(11KV愛28線) |  | CB | [17 empty] | 1-13-03 |  | 1-1E | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA28_CB | JA28(11KV愛28線) CB | FEEDER | D12/11/JA28/CB |  |  |  | CDC | 507 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA29 | 愛29線(JA29) |  | PHA | [17 empty] | 1-13-07 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA29_PHA | 11KV愛29線(JA29) 相間RY | FEEDER | D12/11/JA29/PHA |  |  |  | CDC | 508 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA29 | 愛29線(JA29) |  | GDA | [17 empty] | 1-14-00 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA29_GDA | 11KV愛29線(JA29) 接地RY | FEEDER | D12/11/JA29/GDA |  |  |  | CDC | 509 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA29 | 愛29線(JA29) 79RY |  | 79UL | [17 empty] | 2-39-00 |  | 2-3E | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA29_79UL | 11KV愛29線(JA29) 79RY U/L | FEEDER | D12/11/JA29/FDR_RCA |  |  |  | CDC | 510 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA29_LCO | 愛29線(JA29) LCO |  | TapPosMv | [17 empty] | 2-39-01 |  | 2-3F | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA29_LCO_TAP | 11KV愛29線(JA29) LCO TAP | FEEDER | D12/11/JA29/51NA |  |  |  | CDC | 511 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA29 | JA29(11KV愛29線) |  | CB | [17 empty] | 1-13-06 |  | 1-1F | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA29_CB | JA29(11KV愛29線) CB | FEEDER | D12/11/JA29/CB |  |  |  | CDC | 512 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA30 | 愛30線(JA30) |  | PHA | [17 empty] | 1-14-02 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA30_PHA | 11KV愛30線(JA30) 相間RY | FEEDER | D12/11/JA30/PHA |  |  |  | CDC | 513 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA30 | 愛30線(JA30) |  | GDA | [17 empty] | 1-14-03 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA30_GDA | 11KV愛30線(JA30) 接地RY | FEEDER | D12/11/JA30/GDA |  |  |  | CDC | 514 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA30 | 愛30線(JA30) 79RY |  | 79UL | [17 empty] | 2-39-02 |  | 2-40 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA30_79UL | 11KV愛30線(JA30) 79RY U/L | FEEDER | D12/11/JA30/FDR_RCA |  |  |  | CDC | 515 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA30_LCO | 愛30線(JA30) LCO |  | TapPosMv | [17 empty] | 2-39-03 |  | 2-41 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA30_LCO_TAP | 11KV愛30線(JA30) LCO TAP | FEEDER | D12/11/JA30/51NA |  |  |  | CDC | 516 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA30 | JA30(11KV愛30線) |  | CB | [17 empty] | 1-14-01 |  | 1-20 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA30_CB | JA30(11KV愛30線) CB | FEEDER | D12/11/JA30/CB |  |  |  | CDC | 517 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA31 | 愛31線(JA31) |  | PHA | [17 empty] | 2-00-01 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA31_PHA | 11KV愛31線(JA31) 相間RY | FEEDER | D12/11/JA31/PHA |  |  |  | CDC | 518 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA31 | 愛31線(JA31) |  | GDA | [17 empty] | 2-00-02 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA31_GDA | 11KV愛31線(JA31) 接地RY | FEEDER | D12/11/JA31/GDA |  |  |  | CDC | 519 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA31 | 愛31線(JA31) 79RY |  | 79UL | [17 empty] | 2-39-04 |  | 2-42 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA31_79UL | 11KV愛31線(JA31) 79RY U/L | FEEDER | D12/11/JA31/FDR_RCA |  |  |  | CDC | 520 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA31_LCO | 愛31線(JA31) LCO |  | TapPosMv | [17 empty] | 2-39-05 |  | 2-43 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA31_LCO_TAP | 11KV愛31線(JA31) LCO TAP | FEEDER | D12/11/JA31/51NA |  |  |  | CDC | 521 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA31 | JA31(11KV愛31線) |  | CB | [17 empty] | 2-00-00 |  | 2-07 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA31_CB | JA31(11KV愛31線) CB | FEEDER | D12/11/JA31/CB |  |  |  | CDC | 522 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA32 | 愛32線(JA32) |  | PHA | [17 empty] | 2-00-04 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA32_PHA | 11KV愛32線(JA32) 相間RY | FEEDER | D12/11/JA32/PHA |  |  |  | CDC | 523 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA32 | 愛32線(JA32) |  | GDA | [17 empty] | 2-00-05 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA32_GDA | 11KV愛32線(JA32) 接地RY | FEEDER | D12/11/JA32/GDA |  |  |  | CDC | 524 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA32 | 愛32線(JA32) 79RY |  | 79UL | [17 empty] | 2-39-06 |  | 2-44 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA32_79UL | 11KV愛32線(JA32) 79RY U/L | FEEDER | D12/11/JA32/FDR_RCA |  |  |  | CDC | 525 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA32_LCO | 愛32線(JA32) LCO |  | TapPosMv | [17 empty] | 2-39-07 |  | 2-45 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA32_LCO_TAP | 11KV愛32線(JA32) LCO TAP | FEEDER | D12/11/JA32/51NA |  |  |  | CDC | 526 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA32 | JA32(11KV愛32線) |  | CB | [17 empty] | 2-00-03 |  | 2-08 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA32_CB | JA32(11KV愛32線) CB | FEEDER | D12/11/JA32/CB |  |  |  | CDC | 527 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA33 | 愛33線(JA33) |  | PHA | [17 empty] | 2-00-07 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA33_PHA | 11KV愛33線(JA33) 相間RY | FEEDER | D12/11/JA33/PHA |  |  |  | CDC | 528 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA33 | 愛33線(JA33) |  | GDA | [17 empty] | 2-01-00 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA33_GDA | 11KV愛33線(JA33) 接地RY | FEEDER | D12/11/JA33/GDA |  |  |  | CDC | 529 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA33 | 愛33線(JA33) 79RY |  | 79UL | [17 empty] | 2-39-08 |  | 2-46 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA33_79UL | 11KV愛33線(JA33) 79RY U/L | FEEDER | D12/11/JA33/FDR_RCA |  |  |  | CDC | 530 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA33_LCO | 愛33線(JA33) LCO |  | TapPosMv | [17 empty] | 2-39-09 |  | 2-47 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA33_LCO_TAP | 11KV愛33線(JA33) LCO TAP | FEEDER | D12/11/JA33/51NA |  |  |  | CDC | 531 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA33 | JA33(11KV愛33線) |  | CB | [17 empty] | 2-00-06 |  | 2-09 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA33_CB | JA33(11KV愛33線) CB | FEEDER | D12/11/JA33/CB |  |  |  | CDC | 532 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA34 | 愛34線(JA34) |  | PHA | [17 empty] | 2-01-02 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA34_PHA | 11KV愛34線(JA34) 相間RY | FEEDER | D12/11/JA34/PHA |  |  |  | CDC | 533 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA34 | 愛34線(JA34) |  | GDA | [17 empty] | 2-01-03 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA34_GDA | 11KV愛34線(JA34) 接地RY | FEEDER | D12/11/JA34/GDA |  |  |  | CDC | 534 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA34 | 愛34線(JA34) 79RY |  | 79UL | [17 empty] | 2-39-10 |  | 2-48 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA34_79UL | 11KV愛34線(JA34) 79RY U/L | FEEDER | D12/11/JA34/FDR_RCA |  |  |  | CDC | 535 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA34_LCO | 愛34線(JA34) LCO |  | TapPosMv | [17 empty] | 2-39-11 |  | 2-49 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA34_LCO_TAP | 11KV愛34線(JA34) LCO TAP | FEEDER | D12/11/JA34/51NA |  |  |  | CDC | 536 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA34 | JA34(11KV愛34線) |  | CB | [17 empty] | 2-01-01 |  | 2-0A | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA34_CB | JA34(11KV愛34線) CB | FEEDER | D12/11/JA34/CB |  |  |  | CDC | 537 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA35 | 愛35線(JA35) |  | PHA | [17 empty] | 2-01-05 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA35_PHA | 11KV愛35線(JA35) 相間RY | FEEDER | D12/11/JA35/PHA |  |  |  | CDC | 538 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA35 | 愛35線(JA35) |  | GDA | [17 empty] | 2-01-06 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA35_GDA | 11KV愛35線(JA35) 接地RY | FEEDER | D12/11/JA35/GDA |  |  |  | CDC | 539 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA35 | 愛35線(JA35) 79RY |  | 79UL | [17 empty] | 2-39-12 |  | 2-4A | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA35_79UL | 11KV愛35線(JA35) 79RY U/L | FEEDER | D12/11/JA35/FDR_RCA |  |  |  | CDC | 540 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA35_LCO | 愛35線(JA35) LCO |  | TapPosMv | [17 empty] | 2-39-13 |  | 2-4B | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA35_LCO_TAP | 11KV愛35線(JA35) LCO TAP | FEEDER | D12/11/JA35/51NA |  |  |  | CDC | 541 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA35 | JA35(11KV愛35線) |  | CB | [17 empty] | 2-01-04 |  | 2-0B | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA35_CB | JA35(11KV愛35線) CB | FEEDER | D12/11/JA35/CB |  |  |  | CDC | 542 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA36 | 愛36線(JA36) |  | PHA | [17 empty] | 2-02-06 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA36_PHA | 11KV愛36線(JA36) 相間RY | FEEDER | D12/11/JA36/PHA |  |  |  | CDC | 543 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA36 | 愛36線(JA36) |  | GDA | [17 empty] | 2-02-07 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA36_GDA | 11KV愛36線(JA36) 接地RY | FEEDER | D12/11/JA36/GDA |  |  |  | CDC | 544 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA36 | 愛36線(JA36) 79RY |  | 79UL | [17 empty] | 2-39-14 |  | 2-4C | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA36_79UL | 11KV愛36線(JA36) 79RY U/L | FEEDER | D12/11/JA36/FDR_RCA |  |  |  | CDC | 545 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA36_LCO | 愛36線(JA36) LCO |  | TapPosMv | [17 empty] | 2-39-15 |  | 2-4D | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA36_LCO_TAP | 11KV愛36線(JA36) LCO TAP | FEEDER | D12/11/JA36/51NA |  |  |  | CDC | 546 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA36 | JA36(11KV愛36線) |  | CB | [17 empty] | 2-02-05 |  | 2-0F | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA36_CB | JA36(11KV愛36線) CB | FEEDER | D12/11/JA36/CB |  |  |  | CDC | 547 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA37 | 愛37線(JA37) |  | PHA | [17 empty] | 2-03-01 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA37_PHA | 11KV愛37線(JA37) 相間RY | FEEDER | D12/11/JA37/PHA |  |  |  | CDC | 548 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA37 | 愛37線(JA37) |  | GDA | [17 empty] | 2-03-02 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA37_GDA | 11KV愛37線(JA37) 接地RY | FEEDER | D12/11/JA37/GDA |  |  |  | CDC | 549 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA37 | 愛37線(JA37) 79RY |  | 79UL | [17 empty] | 2-3A-00 |  | 2-4E | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA37_79UL | 11KV愛37線(JA37) 79RY U/L | FEEDER | D12/11/JA37/FDR_RCA |  |  |  | CDC | 550 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA37_LCO | 愛37線(JA37) LCO |  | TapPosMv | [17 empty] | 2-3A-01 |  | 2-4F | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA37_LCO_TAP | 11KV愛37線(JA37) LCO TAP | FEEDER | D12/11/JA37/51NA |  |  |  | CDC | 551 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA37 | JA37(11KV愛37線) |  | CB | [17 empty] | 2-03-00 |  | 2-10 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA37_CB | JA37(11KV愛37線) CB | FEEDER | D12/11/JA37/CB |  |  |  | CDC | 552 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA38 | 愛38線(JA38) |  | PHA | [17 empty] | 2-03-04 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA38_PHA | 11KV愛38線(JA38) 相間RY | FEEDER | D12/11/JA38/PHA |  |  |  | CDC | 553 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA38 | 愛38線(JA38) |  | GDA | [17 empty] | 2-03-05 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA38_GDA | 11KV愛38線(JA38) 接地RY | FEEDER | D12/11/JA38/GDA |  |  |  | CDC | 554 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA38 | 愛38線(JA38) 79RY |  | 79UL | [17 empty] | 2-3A-02 |  | 2-50 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA38_79UL | 11KV愛38線(JA38) 79RY U/L | FEEDER | D12/11/JA38/FDR_RCA |  |  |  | CDC | 555 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA38_LCO | 愛38線(JA38) LCO |  | TapPosMv | [17 empty] | 2-3A-03 |  | 2-51 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA38_LCO_TAP | 11KV愛38線(JA38) LCO TAP | FEEDER | D12/11/JA38/51NA |  |  |  | CDC | 556 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA38 | JA38(11KV愛38線) |  | CB | [17 empty] | 2-03-03 |  | 2-11 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA38_CB | JA38(11KV愛38線) CB | FEEDER | D12/11/JA38/CB |  |  |  | CDC | 557 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA39 | 愛39線(JA39) |  | PHA | [17 empty] | 2-03-07 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA39_PHA | 11KV愛39線(JA39) 相間RY | FEEDER | D12/11/JA39/PHA |  |  |  | CDC | 558 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA39 | 愛39線(JA39) |  | GDA | [17 empty] | 2-04-00 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA39_GDA | 11KV愛39線(JA39) 接地RY | FEEDER | D12/11/JA39/GDA |  |  |  | CDC | 559 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA39 | 愛39線(JA39) 79RY |  | 79UL | [17 empty] | 2-3A-04 |  | 2-52 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA39_79UL | 11KV愛39線(JA39) 79RY U/L | FEEDER | D12/11/JA39/FDR_RCA |  |  |  | CDC | 560 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA39_LCO | 愛39線(JA39) LCO |  | TapPosMv | [17 empty] | 2-3A-05 |  | 2-53 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA39_LCO_TAP | 11KV愛39線(JA39) LCO TAP | FEEDER | D12/11/JA39/51NA |  |  |  | CDC | 561 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA39 | JA39(11KV愛39線) |  | CB | [17 empty] | 2-03-06 |  | 2-12 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA39_CB | JA39(11KV愛39線) CB | FEEDER | D12/11/JA39/CB |  |  |  | CDC | 562 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | JA40 | 愛40線(JA40) |  | PHA | [17 empty] | 2-04-02 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA40_PHA | 11KV愛40線(JA40) 相間RY | FEEDER | D12/11/JA40/PHA |  |  |  | CDC | 563 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA40 | 愛40線(JA40) |  | GDA | [17 empty] | 2-04-03 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA40_GDA | 11KV愛40線(JA40) 接地RY | FEEDER | D12/11/JA40/GDA |  |  |  | CDC | 564 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | JA40 | 愛40線(JA40) 79RY |  | 79UL | [17 empty] | 2-3A-06 |  | 2-54 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA40_79UL | 11KV愛40線(JA40) 79RY U/L | FEEDER | D12/11/JA40/FDR_RCA |  |  |  | CDC | 565 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 11 | 11kV | JA40_LCO | 愛40線(JA40) LCO |  | TapPosMv | [17 empty] | 2-3A-07 |  | 2-55 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA40_LCO_TAP | 11KV愛40線(JA40) LCO TAP | FEEDER | D12/11/JA40/51NA |  |  |  | CDC | 566 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 11 | 11kV | JA40 | JA40(11KV愛40線) |  | CB | [17 empty] | 2-04-01 |  | 2-13 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA40_CB | JA40(11KV愛40線) CB | FEEDER | D12/11/JA40/CB |  |  |  | CDC | 567 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA5A | 愛5A線(JA5A) |  | PHA | [17 empty] | 2-09-01 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5A_PHA | 23KV愛5A線(JA5A) 相間RY | FEEDER | D12/22/JA5A/PHA |  |  |  | CDC | 568 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA5A | 愛5A線(JA5A) |  | GDA | [17 empty] | 2-09-02 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5A_GDA | 23KV愛5A線(JA5A) 接地RY | FEEDER | D12/22/JA5A/GDA |  |  |  | CDC | 569 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA5A | 愛5A線(JA5A) 79RY |  | 79UL | [17 empty] | 2-3B-08 |  | 2-66 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5A_79UL | 23KV愛5A線(JA5A) 79RY U/L | FEEDER | D12/22/JA5A/FDR_RCA |  |  |  | CDC | 570 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 22 | 22kV | JA5A_LCO | 愛5A線(JA5A) LCO |  | TapPosMv | [17 empty] | 2-3B-09 |  | 2-67 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5A_LCO_TAP | 23KV愛5A線(JA5A) LCO TAP | FEEDER | D12/22/JA5A/51NA |  |  |  | CDC | 571 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 22 | 22kV | JA5A | JA5A(23KV愛5A線) |  | CB | [17 empty] | 2-09-00 |  | 2-20 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5A_CB | JA5A(23KV愛5A線) CB | FEEDER | D12/22/JA5A/CB |  |  |  | CDC | 572 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA5B | 愛5B線(JA5B) |  | PHA | [17 empty] | 2-09-04 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5B_PHA | 23KV愛5B線(JA5B) 相間RY | FEEDER | D12/22/JA5B/PHA |  |  |  | CDC | 573 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA5B | 愛5B線(JA5B) |  | GDA | [17 empty] | 2-09-05 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5B_GDA | 23KV愛5B線(JA5B) 接地RY | FEEDER | D12/22/JA5B/GDA |  |  |  | CDC | 574 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA5B | 愛5B線(JA5B) 79RY |  | 79UL | [17 empty] | 2-3B-10 |  | 2-68 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5B_79UL | 23KV愛5B線(JA5B) 79RY U/L | FEEDER | D12/22/JA5B/FDR_RCA |  |  |  | CDC | 575 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 22 | 22kV | JA5B_LCO | 愛5B線(JA5B) LCO |  | TapPosMv | [17 empty] | 2-3B-11 |  | 2-69 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5B_LCO_TAP | 23KV愛5B線(JA5B) LCO TAP | FEEDER | D12/22/JA5B/51NA |  |  |  | CDC | 576 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 22 | 22kV | JA5B | JA5B(23KV愛5B線) |  | CB | [17 empty] | 2-09-03 |  | 2-21 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5B_CB | JA5B(23KV愛5B線) CB | FEEDER | D12/22/JA5B/CB |  |  |  | CDC | 577 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA5C | 愛5C線(JA5C) |  | PHA | [17 empty] | 2-09-07 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5C_PHA | 23KV愛5C線(JA5C) 相間RY | FEEDER | D12/22/JA5C/PHA |  |  |  | CDC | 578 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA5C | 愛5C線(JA5C) |  | GDA | [17 empty] | 2-0A-00 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5C_GDA | 23KV愛5C線(JA5C) 接地RY | FEEDER | D12/22/JA5C/GDA |  |  |  | CDC | 579 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA5C | 愛5C線(JA5C) 79RY |  | 79UL | [17 empty] | 2-3B-12 |  | 2-6A | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5C_79UL | 23KV愛5C線(JA5C) 79RY U/L | FEEDER | D12/22/JA5C/FDR_RCA |  |  |  | CDC | 580 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 22 | 22kV | JA5C_LCO | 愛5C線(JA5C) LCO |  | TapPosMv | [17 empty] | 2-3B-13 |  | 2-6B | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5C_LCO_TAP | 23KV愛5C線(JA5C) LCO TAP | FEEDER | D12/22/JA5C/51NA |  |  |  | CDC | 581 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 22 | 22kV | JA5C | JA5C(23KV愛5C線) |  | CB | [17 empty] | 2-09-06 |  | 2-22 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5C_CB | JA5C(23KV愛5C線) CB | FEEDER | D12/22/JA5C/CB |  |  |  | CDC | 582 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA5D | 愛5D線(JA5D) |  | PHA | [17 empty] | 2-0A-02 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5D_PHA | 23KV愛5D線(JA5D) 相間RY | FEEDER | D12/22/JA5D/PHA |  |  |  | CDC | 583 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA5D | 愛5D線(JA5D) |  | GDA | [17 empty] | 2-0A-03 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5D_GDA | 23KV愛5D線(JA5D) 接地RY | FEEDER | D12/22/JA5D/GDA |  |  |  | CDC | 584 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA5D | 愛5D線(JA5D) 79RY |  | 79UL | [17 empty] | 2-3B-14 |  | 2-6C | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5D_79UL | 23KV愛5D線(JA5D) 79RY U/L | FEEDER | D12/22/JA5D/FDR_RCA |  |  |  | CDC | 585 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 22 | 22kV | JA5D_LCO | 愛5D線(JA5D) LCO |  | TapPosMv | [17 empty] | 2-3B-15 |  | 2-6D | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5D_LCO_TAP | 23KV愛5D線(JA5D) LCO TAP | FEEDER | D12/22/JA5D/51NA |  |  |  | CDC | 586 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 22 | 22kV | JA5D | JA5D(23KV愛5D線) |  | CB | [17 empty] | 2-0A-01 |  | 2-23 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5D_CB | JA5D(23KV愛5D線) CB | FEEDER | D12/22/JA5D/CB |  |  |  | CDC | 587 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA5F | 愛5F線(JA5F) |  | PHA | [17 empty] | 2-0B-00 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5F_PHA | 23KV愛5F線(JA5F) 相間RY | FEEDER | D12/22/JA5F/PHA |  |  |  | CDC | 588 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA5F | 愛5F線(JA5F) |  | GDA | [17 empty] | 2-0B-01 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5F_GDA | 23KV愛5F線(JA5F) 接地RY | FEEDER | D12/22/JA5F/GDA |  |  |  | CDC | 589 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA5F | 愛5F線(JA5F) 79RY |  | 79UL | [17 empty] | 2-3C-00 |  | 2-6E | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5F_79UL | 23KV愛5F線(JA5F) 79RY U/L | FEEDER | D12/22/JA5F/FDR_RCA |  |  |  | CDC | 590 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 22 | 22kV | JA5F_LCO | 愛5F線(JA5F) LCO |  | TapPosMv | [17 empty] | 2-3C-01 |  | 2-6F | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5F_LCO_TAP | 23KV愛5F線(JA5F) LCO TAP | FEEDER | D12/22/JA5F/51NA |  |  |  | CDC | 591 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 22 | 22kV | JA5F | JA5F(23KV愛5F線) |  | CB | [17 empty] | 2-0A-07 |  | 2-24 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5F_CB | JA5F(23KV愛5F線) CB | FEEDER | D12/22/JA5F/CB |  |  |  | CDC | 592 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA5G | 愛5G線(JA5G) |  | PHA | [17 empty] | 2-0B-03 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5G_PHA | 23KV愛5G線(JA5G) 相間RY | FEEDER | D12/22/JA5G/PHA |  |  |  | CDC | 593 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA5G | 愛5G線(JA5G) |  | GDA | [17 empty] | 2-0B-04 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5G_GDA | 23KV愛5G線(JA5G) 接地RY | FEEDER | D12/22/JA5G/GDA |  |  |  | CDC | 594 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA5G | 愛5G線(JA5G) 79RY |  | 79UL | [17 empty] | 2-3C-02 |  | 2-70 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5G_79UL | 23KV愛5G線(JA5G) 79RY U/L | FEEDER | D12/22/JA5G/FDR_RCA |  |  |  | CDC | 595 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 22 | 22kV | JA5G_LCO | 愛5G線(JA5G) LCO |  | TapPosMv | [17 empty] | 2-3C-03 |  | 2-71 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5G_LCO_TAP | 23KV愛5G線(JA5G) LCO TAP | FEEDER | D12/22/JA5G/51NA |  |  |  | CDC | 596 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 22 | 22kV | JA5G | JA5G(23KV愛5G線) |  | CB | [17 empty] | 2-0B-02 |  | 2-25 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5G_CB | JA5G(23KV愛5G線) CB | FEEDER | D12/22/JA5G/CB |  |  |  | CDC | 597 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA5H | 愛5H線(JA5H) |  | PHA | [17 empty] | 2-0B-06 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5H_PHA | 23KV愛5H線(JA5H) 相間RY | FEEDER | D12/22/JA5H/PHA |  |  |  | CDC | 598 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA5H | 愛5H線(JA5H) |  | GDA | [17 empty] | 2-0B-07 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5H_GDA | 23KV愛5H線(JA5H) 接地RY | FEEDER | D12/22/JA5H/GDA |  |  |  | CDC | 599 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA5H | 愛5H線(JA5H) 79RY |  | 79UL | [17 empty] | 2-3C-04 |  | 2-72 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5H_79UL | 23KV愛5H線(JA5H) 79RY U/L | FEEDER | D12/22/JA5H/FDR_RCA |  |  |  | CDC | 600 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 22 | 22kV | JA5H_LCO | 愛5H線(JA5H) LCO |  | TapPosMv | [17 empty] | 2-3C-05 |  | 2-73 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5H_LCO_TAP | 23KV愛5H線(JA5H) LCO TAP | FEEDER | D12/22/JA5H/51NA |  |  |  | CDC | 601 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 22 | 22kV | JA5H | JA5H(23KV愛5H線) |  | CB | [17 empty] | 2-0B-05 |  | 2-26 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5H_CB | JA5H(23KV愛5H線) CB | FEEDER | D12/22/JA5H/CB |  |  |  | CDC | 602 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA5K | 愛5K線(JA5K) |  | PHA | [17 empty] | 2-0C-01 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5K_PHA | 23KV愛5K線(JA5K) 相間RY | FEEDER | D12/22/JA5K/PHA |  |  |  | CDC | 603 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA5K | 愛5K線(JA5K) |  | GDA | [17 empty] | 2-0C-02 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5K_GDA | 23KV愛5K線(JA5K) 接地RY | FEEDER | D12/22/JA5K/GDA |  |  |  | CDC | 604 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA5K | 愛5K線(JA5K) 79RY |  | 79UL | [17 empty] | 2-3C-06 |  | 2-74 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5K_79UL | 23KV愛5K線(JA5K) 79RY U/L | FEEDER | D12/22/JA5K/FDR_RCA |  |  |  | CDC | 605 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 22 | 22kV | JA5K_LCO | 愛5K線(JA5K) LCO |  | TapPosMv | [17 empty] | 2-3C-07 |  | 2-75 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5K_LCO_TAP | 23KV愛5K線(JA5K) LCO TAP | FEEDER | D12/22/JA5K/51NA |  |  |  | CDC | 606 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 22 | 22kV | JA5K | JA5K(23KV愛5K線) |  | CB | [17 empty] | 2-0C-00 |  | 2-27 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5K_CB | JA5K(23KV愛5K線) CB | FEEDER | D12/22/JA5K/CB |  |  |  | CDC | 607 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA71 | 愛71線(JA71) |  | PHA | [17 empty] | 2-05-03 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA71_PHA | 23KV愛71線(JA71) 相間RY | FEEDER | D12/22/JA71/PHA |  |  |  | CDC | 608 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA71 | 愛71線(JA71) |  | GDA | [17 empty] | 2-05-04 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA71_GDA | 23KV愛71線(JA71) 接地RY | FEEDER | D12/22/JA71/GDA |  |  |  | CDC | 609 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA71 | 愛71線(JA71) 79RY |  | 79UL | [17 empty] | 2-3A-08 |  | 2-56 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA71_79UL | 23KV愛71線(JA71) 79RY U/L | FEEDER | D12/22/JA71/FDR_RCA |  |  |  | CDC | 610 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 22 | 22kV | JA71_LCO | 愛71線(JA71) LCO |  | TapPosMv | [17 empty] | 2-3A-09 |  | 2-57 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA71_LCO_TAP | 23KV愛71線(JA71) LCO TAP | FEEDER | D12/22/JA71/51NA |  |  |  | CDC | 611 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 22 | 22kV | JA71 | JA71(23KV愛71線) |  | CB | [17 empty] | 2-05-02 |  | 2-15 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA71_CB | JA71(23KV愛71線) CB | FEEDER | D12/22/JA71/CB |  |  |  | CDC | 612 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA72 | 愛72線(JA72) |  | PHA | [17 empty] | 2-05-06 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA72_PHA | 23KV愛72線(JA72) 相間RY | FEEDER | D12/22/JA72/PHA |  |  |  | CDC | 613 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA72 | 愛72線(JA72) |  | GDA | [17 empty] | 2-05-07 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA72_GDA | 23KV愛72線(JA72) 接地RY | FEEDER | D12/22/JA72/GDA |  |  |  | CDC | 614 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA72 | 愛72線(JA72) 79RY |  | 79UL | [17 empty] | 2-3A-10 |  | 2-58 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA72_79UL | 23KV愛72線(JA72) 79RY U/L | FEEDER | D12/22/JA72/FDR_RCA |  |  |  | CDC | 615 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 22 | 22kV | JA72_LCO | 愛72線(JA72) LCO |  | TapPosMv | [17 empty] | 2-3A-11 |  | 2-59 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA72_LCO_TAP | 23KV愛72線(JA72) LCO TAP | FEEDER | D12/22/JA72/51NA |  |  |  | CDC | 616 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 22 | 22kV | JA72 | JA72(23KV愛72線) |  | CB | [17 empty] | 2-05-05 |  | 2-16 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA72_CB | JA72(23KV愛72線) CB | FEEDER | D12/22/JA72/CB |  |  |  | CDC | 617 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA73 | 愛73線(JA73) |  | PHA | [17 empty] | 2-06-01 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA73_PHA | 23KV愛73線(JA73) 相間RY | FEEDER | D12/22/JA73/PHA |  |  |  | CDC | 618 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA73 | 愛73線(JA73) |  | GDA | [17 empty] | 2-06-02 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA73_GDA | 23KV愛73線(JA73) 接地RY | FEEDER | D12/22/JA73/GDA |  |  |  | CDC | 619 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA73 | 愛73線(JA73) 79RY |  | 79UL | [17 empty] | 2-3A-12 |  | 2-5A | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA73_79UL | 23KV愛73線(JA73) 79RY U/L | FEEDER | D12/22/JA73/FDR_RCA |  |  |  | CDC | 620 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 22 | 22kV | JA73_LCO | 愛73線(JA73) LCO |  | TapPosMv | [17 empty] | 2-3A-13 |  | 2-5B | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA73_LCO_TAP | 23KV愛73線(JA73) LCO TAP | FEEDER | D12/22/JA73/51NA |  |  |  | CDC | 621 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 22 | 22kV | JA73 | JA73(23KV愛73線) |  | CB | [17 empty] | 2-06-00 |  | 2-17 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA73_CB | JA73(23KV愛73線) CB | FEEDER | D12/22/JA73/CB |  |  |  | CDC | 622 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA74 | 愛74線(JA74) |  | PHA | [17 empty] | 2-06-04 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA74_PHA | 23KV愛74線(JA74) 相間RY | FEEDER | D12/22/JA74/PHA |  |  |  | CDC | 623 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA74 | 愛74線(JA74) |  | GDA | [17 empty] | 2-06-05 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA74_GDA | 23KV愛74線(JA74) 接地RY | FEEDER | D12/22/JA74/GDA |  |  |  | CDC | 624 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA74 | 愛74線(JA74) 79RY |  | 79UL | [17 empty] | 2-3A-14 |  | 2-5C | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA74_79UL | 23KV愛74線(JA74) 79RY U/L | FEEDER | D12/22/JA74/FDR_RCA |  |  |  | CDC | 625 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 22 | 22kV | JA74_LCO | 愛74線(JA74) LCO |  | TapPosMv | [17 empty] | 2-3A-15 |  | 2-5D | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA74_LCO_TAP | 23KV愛74線(JA74) LCO TAP | FEEDER | D12/22/JA74/51NA |  |  |  | CDC | 626 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 22 | 22kV | JA74 | JA74(23KV愛74線) |  | CB | [17 empty] | 2-06-03 |  | 2-18 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA74_CB | JA74(23KV愛74線) CB | FEEDER | D12/22/JA74/CB |  |  |  | CDC | 627 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA75 | 愛75線(JA75) |  | PHA | [17 empty] | 2-07-02 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA75_PHA | 23KV愛75線(JA75) 相間RY | FEEDER | D12/22/JA75/PHA |  |  |  | CDC | 628 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA75 | 愛75線(JA75) |  | GDA | [17 empty] | 2-07-03 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA75_GDA | 23KV愛75線(JA75) 接地RY | FEEDER | D12/22/JA75/GDA |  |  |  | CDC | 629 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA75 | 愛75線(JA75) 79RY |  | 79UL | [17 empty] | 2-3B-00 |  | 2-5E | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA75_79UL | 23KV愛75線(JA75) 79RY U/L | FEEDER | D12/22/JA75/FDR_RCA |  |  |  | CDC | 630 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 22 | 22kV | JA75_LCO | 愛75線(JA75) LCO |  | TapPosMv | [17 empty] | 2-3B-01 |  | 2-5F | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA75_LCO_TAP | 23KV愛75線(JA75) LCO TAP | FEEDER | D12/22/JA75/51NA |  |  |  | CDC | 631 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 22 | 22kV | JA75 | JA75(23KV愛75線) |  | CB | [17 empty] | 2-07-01 |  | 2-19 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA75_CB | JA75(23KV愛75線) CB | FEEDER | D12/22/JA75/CB |  |  |  | CDC | 632 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA76 | 愛76線(JA76) |  | PHA | [17 empty] | 2-07-05 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA76_PHA | 23KV愛76線(JA76) 相間RY | FEEDER | D12/22/JA76/PHA |  |  |  | CDC | 633 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA76 | 愛76線(JA76) |  | GDA | [17 empty] | 2-07-06 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA76_GDA | 23KV愛76線(JA76) 接地RY | FEEDER | D12/22/JA76/GDA |  |  |  | CDC | 634 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA76 | 愛76線(JA76) 79RY |  | 79UL | [17 empty] | 2-3B-02 |  | 2-60 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA76_79UL | 23KV愛76線(JA76) 79RY U/L | FEEDER | D12/22/JA76/FDR_RCA |  |  |  | CDC | 635 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 22 | 22kV | JA76_LCO | 愛76線(JA76) LCO |  | TapPosMv | [17 empty] | 2-3B-03 |  | 2-61 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA76_LCO_TAP | 23KV愛76線(JA76) LCO TAP | FEEDER | D12/22/JA76/51NA |  |  |  | CDC | 636 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 22 | 22kV | JA76 | JA76(23KV愛76線) |  | CB | [17 empty] | 2-07-04 |  | 2-1A | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA76_CB | JA76(23KV愛76線) CB | FEEDER | D12/22/JA76/CB |  |  |  | CDC | 637 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA77 | 愛77線(JA77) |  | PHA | [17 empty] | 2-08-00 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA77_PHA | 23KV愛77線(JA77) 相間RY | FEEDER | D12/22/JA77/PHA |  |  |  | CDC | 638 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA77 | 愛77線(JA77) |  | GDA | [17 empty] | 2-08-01 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA77_GDA | 23KV愛77線(JA77) 接地RY | FEEDER | D12/22/JA77/GDA |  |  |  | CDC | 639 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA77 | 愛77線(JA77) 79RY |  | 79UL | [17 empty] | 2-3B-04 |  | 2-62 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA77_79UL | 23KV愛77線(JA77) 79RY U/L | FEEDER | D12/22/JA77/FDR_RCA |  |  |  | CDC | 640 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 22 | 22kV | JA77_LCO | 愛77線(JA77) LCO |  | TapPosMv | [17 empty] | 2-3B-05 |  | 2-63 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA77_LCO_TAP | 23KV愛77線(JA77) LCO TAP | FEEDER | D12/22/JA77/51NA |  |  |  | CDC | 641 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 22 | 22kV | JA77 | JA77(23KV愛77線) |  | CB | [17 empty] | 2-07-07 |  | 2-1B | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA77_CB | JA77(23KV愛77線) CB | FEEDER | D12/22/JA77/CB |  |  |  | CDC | 642 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | JA78 | 愛78線(JA78) |  | PHA | [17 empty] | 2-08-03 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA78_PHA | 23KV愛78線(JA78) 相間RY | FEEDER | D12/22/JA78/PHA |  |  |  | CDC | 643 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA78 | 愛78線(JA78) |  | GDA | [17 empty] | 2-08-04 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA78_GDA | 23KV愛78線(JA78) 接地RY | FEEDER | D12/22/JA78/GDA |  |  |  | CDC | 644 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | JA78 | 愛78線(JA78) 79RY |  | 79UL | [17 empty] | 2-3B-06 |  | 2-64 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA78_79UL | 23KV愛78線(JA78) 79RY U/L | FEEDER | D12/22/JA78/FDR_RCA |  |  |  | CDC | 645 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 22 | 22kV | JA78_LCO | 愛78線(JA78) LCO |  | TapPosMv | [17 empty] | 2-3B-07 |  | 2-65 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA78_LCO_TAP | 23KV愛78線(JA78) LCO TAP | FEEDER | D12/22/JA78/51NA |  |  |  | CDC | 646 | GENERICDIPoint | DS042_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D12 | 仁愛DS | 22 | 22kV | JA78 | JA78(23KV愛78線) |  | CB | [17 empty] | 2-08-02 |  | 2-1C | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA78_CB | JA78(23KV愛78線) CB | FEEDER | D12/22/JA78/CB |  |  |  | CDC | 647 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 100 | TIE(100) |  | CB | [17 empty] | 1-12-02 |  | 1-18 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.100_CB | 100(TIE) CB | TIE | D12/11/100/CB |  |  |  | CDC | 648 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | 100 | TIE(100) |  | 51A | [17 empty] | 1-12-03 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.100_51A | 11KV TIE(100) 51RY | TIE | D12/11/100/PHA |  |  |  | CDC | 649 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 100 | TIE(100) |  | 51NA | [17 empty] | 1-12-04 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.100_51NA | 11KV TIE(100) 51N RY | TIE | D12/11/100/GDA |  |  |  | CDC | 650 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [17 empty] | 1-05-00 |  | 1-0C | [5 empty] | 161KV_N | [8 empty] | 仁愛DS.1500_CB | 1500(TIE) CB | TIE | D12/161/1500/CB |  |  |  | CDC | 651 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 1500 | TIE(1500) |  | 50A | [17 empty] | 1-05-01 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.1500_50A | 161KV TIE(1500) 50RY | TIE | D12/161/1500/50A |  |  |  | CDC | 652 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [16 empty] | 1-3E-00 | 1-3E-01 | 1-6E | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.1501_DS | 1501(TIE) DS | TIE | D12/161/1500/DS1 |  |  |  | CDC | 653 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [16 empty] | 1-3E-02 | 1-3E-03 | 1-6F | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.1502_DS | 1502(TIE) DS | TIE | D12/161/1500/DS2 |  |  |  | CDC | 654 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 0 |  | 200 | TIE(200) |  | CB | [17 empty] | 2-04-07 |  | 2-0D | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.200_CB | 200(TIE) CB | TIE | D12/11/200/CB |  |  |  | CDC | 655 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | 200 | TIE(200) |  | 51A | [17 empty] | 2-05-00 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.200_51A | 11KV TIE(200) 51RY | TIE | D12/11/200/PHA |  |  |  | CDC | 656 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 200 | TIE(200) |  | 51NA | [17 empty] | 2-05-01 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.200_51NA | 11KV TIE(200) 51N RY | TIE | D12/11/200/GDA |  |  |  | CDC | 657 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 400 | TIE(400) |  | CB | [17 empty] | 2-0C-06 |  | 2-1E | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.400_CB | 400(TIE) CB | TIE | D12/22/400/CB |  |  |  | CDC | 658 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | 400 | TIE(400) |  | 51A | [17 empty] | 2-0C-07 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.400_51A | 23KV TIE(400) 51RY | TIE | D12/22/400/PHA |  |  |  | CDC | 659 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 400 | TIE(400) |  | 51NA | [17 empty] | 2-0D-00 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.400_51NA | 23KV TIE(400) 51N RY | TIE | D12/22/400/GDA |  |  |  | CDC | 660 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 390 | #1SSTR(390) |  | CB | [17 empty] | 1-14-07 |  | 1-19 | [5 empty] | 161KV_N | [8 empty] | 仁愛DS.390_CB | 390(#1SSTR) CB | OTHER | D12/11/390/CB |  |  |  | CDC | 661 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 1SSTR | #1SSTR |  | 51A | [17 empty] | 1-15-00 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.#1SSTR_51A | #1SSTR 51RY | OTHER | D12/11/390/PHA |  |  |  | CDC | 662 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 1SSTR | #1SSTR |  | 51NA | [17 empty] | 1-15-01 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | D12/11/390/GDA |  |  |  | CDC | 663 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 490 | #2SSTR(490) |  | CB | [17 empty] | 2-02-02 |  | 2-0C | [5 empty] | 161KV_N | [8 empty] | 仁愛DS.490_CB | 490(#2SSTR) CB | OTHER | D12/11/490/CB |  |  |  | CDC | 664 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 2SSTR | #2SSTR |  | 51A | [17 empty] | 2-02-03 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.#2SSTR_51A | #2SSTR 51RY | OTHER | D12/11/490/PHA |  |  |  | CDC | 665 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 2SSTR | #2SSTR |  | 51NA | [17 empty] | 2-02-04 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | D12/11/490/GDA |  |  |  | CDC | 666 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB | [17 empty] | 1-06-00 |  | 1-0D | [5 empty] | 161KV_N | [8 empty] | 仁愛DS.1750_CB | 1750(#1DTR) CB | MTR | D12/161/1750/CB |  |  |  | CDC | 667 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 310 | #1DTR(310) |  | CB | [17 empty] | 1-07-00 |  | 1-11 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.310_CB | 310(#1DTR) CB | MTR | D12/11/310/CB |  |  |  | CDC | 668 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 320 | #1DTR(320) |  | CB | [17 empty] | 1-07-03 |  | 1-1A | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.320_CB | 320(#1DTR) CB | MTR | D12/11/320/CB |  |  |  | CDC | 669 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 1DTR | #1DTR |  | 51A | [17 empty] | 1-06-04 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.#1DTR_51A | #1DTR 51RY | MTR | D12//1DTR/PHA |  |  |  | CDC | 670 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 1DTR | #1DTR |  | 51NA | [17 empty] | 1-06-05 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.#1DTR_51NA | #1DTR 51N RY | MTR | D12//1DTR/GDA |  |  |  | CDC | 671 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 1DTR | #1DTR |  | 51ZA | [17 empty] | 1-06-03 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | D12//1DTR/51ZA |  |  |  | CDC | 672 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 1DTR | #1DTR |  | 87A | [17 empty] | 1-06-01 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.#1DTR_87A | #1DTR 87RY | MTR | D12//1DTR/87A |  |  |  | CDC | 673 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 1DTR | #1DTR |  | 87UL | [17 empty] | 1-31-08 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#1DTR_87UL | #1DTR 87RY U/L | MTR | D12//1DTR/87UL |  |  |  | CDC | 674 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 0 |  | 310 | #1DTR(310) |  | 51A | [17 empty] | 1-06-06 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.310_51A | #1DTR二次側(310) 51RY | MTR | D12/11/310/51A |  |  |  | CDC | 675 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 320 | #1DTR(320) |  | 51A | [17 empty] | 1-06-07 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.320_51A | #1DTR二次側(320) 51RY | MTR | D12/11/320/51A |  |  |  | CDC | 676 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 1DTR | #1DTR |  | 96PA | [17 empty] | 1-06-02 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | D12//1DTR/96PA |  |  |  | CDC | 677 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 1DTR | #1DTR |  | 96D | [17 empty] | 1-31-15 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#1DTR_96D | #1DTR 96D RY | MTR | D12//1DTR/96D |  |  |  | CDC | 678 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 1DTR | #1DTR |  | 96P | [17 empty] | 1-32-00 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#1DTR_96P | #1DTR 96P RY | MTR | D12//1DTR/96P |  |  |  | CDC | 679 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 1DTR | #1DTR |  | 63Q | [17 empty] | 1-32-01 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#1DTR_63Q | #1DTR 63Q RY | MTR | D12//1DTR/63Q |  |  |  | CDC | 680 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 1DTR | #1DTR |  | 96B1 | [17 empty] | 1-31-13 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | D12//1DTR/96B1 |  |  |  | CDC | 681 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 1DTR | #1DTR |  | 96B2 | [17 empty] | 1-31-14 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | D12//1DTR/96B2 |  |  |  | CDC | 682 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 1DTR | #1DTR |  | TRA | [17 empty] | 1-32-03 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#1DTR_TRA | #1DTR 重故障 | MTR | D12//1DTR/TRA |  |  |  | CDC | 683 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 1DTR | #1DTR |  | TRF | [17 empty] | 1-32-02 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#1DTR_TRF | #1DTR 輕故障 | MTR | D12//1DTR/TRF |  |  |  | CDC | 684 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 1DTR(A) | #1DTR(A) |  | SupLocal | [17 empty] | 1-31-09 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | D12//1DTR(A)/SupLocal |  |  |  | CDC | 685 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D12 | 仁愛DS | 0 |  | 1DTR(A) | #1DTR(A) |  | A_M | [17 empty] | 1-31-10 |  | 1-3A | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | D12//1DTR(A)/Tap Chan |  |  |  | CDC | 686 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D12 | 仁愛DS | 0 |  | 1DTR(B) | #1DTR(B) |  | SupLocal | [17 empty] | 1-31-11 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | D12//1DTR(B)/SupLocal |  |  |  | CDC | 687 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D12 | 仁愛DS | 0 |  | 1DTR(B) | #1DTR(B) |  | A_M | [17 empty] | 1-31-12 |  | 1-3C | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | D12//1DTR(B)/Tap Chan |  |  |  | CDC | 688 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D12 | 仁愛DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 | [16 empty] | 1-3E-04 | 1-3E-05 | 1-70 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.1751_DS | 1751(#1DTR) DS | MTR | D12/161/1750/DS1 |  |  |  | CDC | 689 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 | [16 empty] | 1-3E-06 | 1-3E-07 | 1-71 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.1752_DS | 1752(#1DTR) DS | MTR | D12/161/1750/DS2 |  |  |  | CDC | 690 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D12 | 仁愛DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB | [17 empty] | 1-07-06 |  | 1-0E | [5 empty] | 161KV_N | [8 empty] | 仁愛DS.1760_CB | 1760(#2DTR) CB | MTR | D12/161/1760/CB |  |  |  | CDC | 691 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 330 | #2DTR(330) |  | CB | [17 empty] | 1-08-06 |  | 1-36 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.330_CB | 330(#2DTR) CB | MTR | D12/11/330/CB |  |  |  | CDC | 692 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 340 | #2DTR(340) |  | CB | [17 empty] | 1-09-01 |  | 1-37 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.340_CB | 340(#2DTR) CB | MTR | D12/11/340/CB |  |  |  | CDC | 693 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 2DTR | #2DTR |  | 51A | [17 empty] | 1-08-02 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.#2DTR_51A | #2DTR 51RY | MTR | D12//2DTR/PHA |  |  |  | CDC | 694 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 2DTR | #2DTR |  | 51NA | [17 empty] | 1-08-03 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.#2DTR_51NA | #2DTR 51N RY | MTR | D12//2DTR/GDA |  |  |  | CDC | 695 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 2DTR | #2DTR |  | 51ZA | [17 empty] | 1-08-01 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | D12//2DTR/51ZA |  |  |  | CDC | 696 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 2DTR | #2DTR |  | 87A | [17 empty] | 1-07-07 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.#2DTR_87A | #2DTR 87RY | MTR | D12//2DTR/87A |  |  |  | CDC | 697 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 2DTR | #2DTR |  | 87UL | [17 empty] | 1-32-04 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#2DTR_87UL | #2DTR 87RY U/L | MTR | D12//2DTR/87UL |  |  |  | CDC | 698 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 0 |  | 330 | #2DTR(330) |  | 51A | [17 empty] | 1-08-04 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.330_51A | #2DTR二次側(330) 51RY | MTR | D12/11/330/51A |  |  |  | CDC | 699 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 340 | #2DTR(340) |  | 51A | [17 empty] | 1-08-05 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.340_51A | #2DTR二次側(340) 51RY | MTR | D12/11/340/51A |  |  |  | CDC | 700 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 2DTR | #2DTR |  | 96PA | [17 empty] | 1-08-00 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | D12//2DTR/96PA |  |  |  | CDC | 701 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 2DTR | #2DTR |  | 96D | [17 empty] | 1-32-11 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#2DTR_96D | #2DTR 96D RY | MTR | D12//2DTR/96D |  |  |  | CDC | 702 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 2DTR | #2DTR |  | 96P | [17 empty] | 1-32-12 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#2DTR_96P | #2DTR 96P RY | MTR | D12//2DTR/96P |  |  |  | CDC | 703 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 2DTR | #2DTR |  | 63Q | [17 empty] | 1-32-13 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#2DTR_63Q | #2DTR 63Q RY | MTR | D12//2DTR/63Q |  |  |  | CDC | 704 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 2DTR | #2DTR |  | 96B1 | [17 empty] | 1-32-09 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | D12//2DTR/96B1 |  |  |  | CDC | 705 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 2DTR | #2DTR |  | 96B2 | [17 empty] | 1-32-10 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | D12//2DTR/96B2 |  |  |  | CDC | 706 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 2DTR | #2DTR |  | TRA | [17 empty] | 1-32-15 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#2DTR_TRA | #2DTR 重故障 | MTR | D12//2DTR/TRA |  |  |  | CDC | 707 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 2DTR | #2DTR |  | TRF | [17 empty] | 1-32-14 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#2DTR_TRF | #2DTR 輕故障 | MTR | D12//2DTR/TRF |  |  |  | CDC | 708 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 2DTR(A) | #2DTR(A) |  | SupLocal | [17 empty] | 1-32-05 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | D12//2DTR(A)/SupLocal |  |  |  | CDC | 709 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D12 | 仁愛DS | 0 |  | 2DTR(A) | #2DTR(A) |  | A_M | [17 empty] | 1-32-06 |  | 1-3E | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | D12//2DTR(A)/Tap Chan |  |  |  | CDC | 710 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D12 | 仁愛DS | 0 |  | 2DTR(B) | #2DTR(B) |  | SupLocal | [17 empty] | 1-32-07 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | D12//2DTR(B)/SupLocal |  |  |  | CDC | 711 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D12 | 仁愛DS | 0 |  | 2DTR(B) | #2DTR(B) |  | A_M | [17 empty] | 1-32-08 |  | 1-40 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | D12//2DTR(B)/Tap Chan |  |  |  | CDC | 712 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D12 | 仁愛DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 | [16 empty] | 1-3E-08 | 1-3E-09 | 1-72 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.1761_DS | 1761(#2DTR) DS | MTR | D12/161/1760/DS1 |  |  |  | CDC | 713 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D12 | 仁愛DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 | [16 empty] | 1-3E-10 | 1-3E-11 | 1-73 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.1762_DS | 1762(#2DTR) DS | MTR | D12/161/1760/DS2 |  |  |  | CDC | 714 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB | [17 empty] | 1-09-04 |  | 1-0F | [5 empty] | 161KV_N | [8 empty] | 仁愛DS.1770_CB | 1770(#3DTR) CB | MTR | D12/161/1770/CB |  |  |  | CDC | 715 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 350 | #3DTR(350) |  | CB | [17 empty] | 1-0A-03 |  | 1-38 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.350_CB | 350(#3DTR) CB | MTR | D12/22/350/CB |  |  |  | CDC | 716 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 3DTR | #3DTR |  | 51A | [17 empty] | 1-0A-00 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.#3DTR_51A | #3DTR 51RY | MTR | D12//3DTR/PHA |  |  |  | CDC | 717 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 3DTR | #3DTR |  | 51NA | [17 empty] | 1-0A-01 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.#3DTR_51NA | #3DTR 51N RY | MTR | D12//3DTR/GDA |  |  |  | CDC | 718 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 3DTR | #3DTR |  | 51ZA | [17 empty] | 1-09-07 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.#3DTR_51ZA | #3DTR 51Z RY | MTR | D12//3DTR/51ZA |  |  |  | CDC | 719 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 3DTR | #3DTR |  | 87A | [17 empty] | 1-09-05 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.#3DTR_87A | #3DTR 87RY | MTR | D12//3DTR/87A |  |  |  | CDC | 720 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 3DTR | #3DTR |  | 87UL | [17 empty] | 1-33-00 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#3DTR_87UL | #3DTR 87RY U/L | MTR | D12//3DTR/87UL |  |  |  | CDC | 721 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 0 |  | 350 | #3DTR(350) |  | 51A | [17 empty] | 1-0A-02 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.350_51A | #3DTR二次側(350) 51RY | MTR | D12/22/350/51A |  |  |  | CDC | 722 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 3DTR | #3DTR |  | 96PA | [17 empty] | 1-09-06 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.#3DTR_96PA | #3DTR 機械保護動作 | MTR | D12//3DTR/96PA |  |  |  | CDC | 723 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 3DTR | #3DTR |  | 96D | [17 empty] | 1-33-05 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#3DTR_96D | #3DTR 96D RY | MTR | D12//3DTR/96D |  |  |  | CDC | 724 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 3DTR | #3DTR |  | 96P | [17 empty] | 1-33-06 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#3DTR_96P | #3DTR 96P RY | MTR | D12//3DTR/96P |  |  |  | CDC | 725 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 3DTR | #3DTR |  | 63Q | [17 empty] | 1-33-07 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#3DTR_63Q | #3DTR 63Q RY | MTR | D12//3DTR/63Q |  |  |  | CDC | 726 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 3DTR | #3DTR |  | 96B1 | [17 empty] | 1-33-03 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#3DTR_96B1 | #3DTR 96B1 RY | MTR | D12//3DTR/96B1 |  |  |  | CDC | 727 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 3DTR | #3DTR |  | 96B2 | [17 empty] | 1-33-04 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#3DTR_96B2 | #3DTR 96B2 RY | MTR | D12//3DTR/96B2 |  |  |  | CDC | 728 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 3DTR | #3DTR |  | TRA | [17 empty] | 1-33-09 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#3DTR_TRA | #3DTR 重故障 | MTR | D12//3DTR/TRA |  |  |  | CDC | 729 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 3DTR | #3DTR |  | TRF | [17 empty] | 1-33-08 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#3DTR_TRF | #3DTR 輕故障 | MTR | D12//3DTR/TRF |  |  |  | CDC | 730 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 3DTR | #3DTR |  | SupLocal | [17 empty] | 1-33-01 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#3DTR_S/L | #3DTR OLTC S/L | MTR | D12//3DTR/SupLocal |  |  |  | CDC | 731 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D12 | 仁愛DS | 0 |  | 3DTR | #3DTR |  | A_M | [17 empty] | 1-33-02 |  | 1-42 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.#3DTR_A/M | #3DTR OLTC A/M | MTR | D12//3DTR/Tap Chan |  |  |  | CDC | 732 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D12 | 仁愛DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 | [16 empty] | 1-3E-12 | 1-3E-13 | 1-74 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.1771_DS | 1771(#3DTR) DS | MTR | D12/161/1770/DS1 |  |  |  | CDC | 733 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 | [16 empty] | 1-3E-14 | 1-3E-15 | 1-75 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.1772_DS | 1772(#3DTR) DS | MTR | D12/161/1770/DS2 |  |  |  | CDC | 734 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D12 | 仁愛DS | 161 | 161kV | 1780 | #4DTR(1780) |  | CB | [17 empty] | 1-0A-06 |  | 1-10 | [5 empty] | 161KV_N | [8 empty] | 仁愛DS.1780_CB | 1780(#4DTR) CB | MTR | D12/161/1780/CB |  |  |  | CDC | 735 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 370 | #4DTR(370) |  | CB | [17 empty] | 1-0B-05 |  | 1-39 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.370_CB | 370(#4DTR) CB | MTR | D12/22/370/CB |  |  |  | CDC | 736 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 4DTR | #4DTR |  | 51A | [17 empty] | 1-0B-02 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.#4DTR_51A | #4DTR 51RY | MTR | D12//4DTR/PHA |  |  |  | CDC | 737 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 4DTR | #4DTR |  | 51NA | [17 empty] | 1-0B-03 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.#4DTR_51NA | #4DTR 51N RY | MTR | D12//4DTR/GDA |  |  |  | CDC | 738 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 4DTR | #4DTR |  | 51ZA | [17 empty] | 1-0B-01 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.#4DTR_51ZA | #4DTR 51Z RY | MTR | D12//4DTR/51ZA |  |  |  | CDC | 739 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 4DTR | #4DTR |  | 87A | [17 empty] | 1-0A-07 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.#4DTR_87A | #4DTR 87RY | MTR | D12//4DTR/87A |  |  |  | CDC | 740 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 4DTR | #4DTR |  | 87UL | [17 empty] | 1-33-10 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#4DTR_87UL | #4DTR 87RY U/L | MTR | D12//4DTR/87UL |  |  |  | CDC | 741 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 0 |  | 370 | #4DTR(370) |  | 51A | [17 empty] | 1-0B-04 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.370_51A | #4DTR二次側(370) 51RY | MTR | D12/22/370/51A |  |  |  | CDC | 742 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 4DTR | #4DTR |  | 96PA | [17 empty] | 1-0B-00 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.#4DTR_96PA | #4DTR 機械保護動作 | MTR | D12//4DTR/96PA |  |  |  | CDC | 743 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 4DTR | #4DTR |  | 96D | [17 empty] | 1-33-15 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#4DTR_96D | #4DTR 96D RY | MTR | D12//4DTR/96D |  |  |  | CDC | 744 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 4DTR | #4DTR |  | 96P | [17 empty] | 1-34-00 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#4DTR_96P | #4DTR 96P RY | MTR | D12//4DTR/96P |  |  |  | CDC | 745 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 4DTR | #4DTR |  | 63Q | [17 empty] | 1-34-01 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#4DTR_63Q | #4DTR 63Q RY | MTR | D12//4DTR/63Q |  |  |  | CDC | 746 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 4DTR | #4DTR |  | 96B1 | [17 empty] | 1-33-13 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#4DTR_96B1 | #4DTR 96B1 RY | MTR | D12//4DTR/96B1 |  |  |  | CDC | 747 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 4DTR | #4DTR |  | 96B2 | [17 empty] | 1-33-14 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#4DTR_96B2 | #4DTR 96B2 RY | MTR | D12//4DTR/96B2 |  |  |  | CDC | 748 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 4DTR | #4DTR |  | TRA | [17 empty] | 1-34-03 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#4DTR_TRA | #4DTR 重故障 | MTR | D12//4DTR/TRA |  |  |  | CDC | 749 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 4DTR | #4DTR |  | TRF | [17 empty] | 1-34-02 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#4DTR_TRF | #4DTR 輕故障 | MTR | D12//4DTR/TRF |  |  |  | CDC | 750 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 4DTR | #4DTR |  | SupLocal | [17 empty] | 1-33-11 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.#4DTR_S/L | #4DTR OLTC S/L | MTR | D12//4DTR/SupLocal |  |  |  | CDC | 751 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D12 | 仁愛DS | 0 |  | 4DTR | #4DTR |  | A_M | [17 empty] | 1-33-12 |  | 1-44 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.#4DTR_A/M | #4DTR OLTC A/M | MTR | D12//4DTR/Tap Chan |  |  |  | CDC | 752 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D12 | 仁愛DS | 161 | 161kV | 1780 | #4DTR(1780) |  | DS1 | 1781 | [16 empty] | 1-3F-00 | 1-3F-01 | 1-76 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.1781_DS | 1781(#4DTR) DS | MTR | D12/161/1780/DS1 |  |  |  | CDC | 753 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D12 | 仁愛DS | 161 | 161kV | 1780 | #4DTR(1780) |  | DS2 | 1782 | [16 empty] | 1-3F-02 | 1-3F-03 | 1-77 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.1782_DS | 1782(#4DTR) DS | MTR | D12/161/1780/DS2 |  |  |  | CDC | 754 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-11-07 |  | 1-12 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.210_CB | 210(11KV #1SC) CB | SC | D12/11/210/CB |  |  |  | CDC | 755 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-12-00 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.210_SCA | 11KV #1SC 51,51N RY | SC | D12/11/210/SCA |  |  |  | CDC | 756 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-12-01 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | D12/11/210/UVA |  |  |  | CDC | 757 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 210 | #1SC(210) |  | LBS | [17 empty] | 1-3F-04 | 1-3F-05 | 1-78 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.210_LBS | 210(11KV #1SC) LBS | SC | D12/11/1SC/LBS |  |  |  | CDC | 758 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 1-14-04 |  | 1-1B | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.220_CB | 220(11KV #2SC) CB | SC | D12/11/220/CB |  |  |  | CDC | 759 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 1-14-05 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.220_SCA | 11KV #2SC 51,51N RY | SC | D12/11/220/SCA |  |  |  | CDC | 760 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 1-14-06 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | D12/11/220/UVA |  |  |  | CDC | 761 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 220 | #2SC(220) |  | LBS | [17 empty] | 1-3F-06 | 1-3F-07 | 1-79 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.220_LBS | 220(11KV #2SC) LBS | SC | D12/11/2SC/LBS |  |  |  | CDC | 762 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 11 | 11kV | 230 | #3SC(230) |  | CB | [17 empty] | 2-01-07 |  | 2-06 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.230_CB | 230(11KV #3SC) CB | SC | D12/11/230/CB |  |  |  | CDC | 763 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | 230 | #3SC(230) |  | SCA | [17 empty] | 2-02-00 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.230_SCA | 11KV #3SC 51,51N RY | SC | D12/11/230/SCA |  |  |  | CDC | 764 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 230 | #3SC(230) |  | UVA | [17 empty] | 2-02-01 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | D12/11/230/UVA |  |  |  | CDC | 765 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 230 | #3SC(230) |  | LBS | [17 empty] | 1-3F-08 | 1-3F-09 | 1-7A | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.230_LBS | 230(11KV #3SC) LBS | SC | D12/11/3SC/LBS |  |  |  | CDC | 766 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 11 | 11kV | 240 | #4SC(240) |  | CB | [17 empty] | 2-04-04 |  | 2-0E | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.240_CB | 240(11KV #4SC) CB | SC | D12/11/240/CB |  |  |  | CDC | 767 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 11 | 11kV | 240 | #4SC(240) |  | SCA | [17 empty] | 2-04-05 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.240_SCA | 11KV #4SC 51,51N RY | SC | D12/11/240/SCA |  |  |  | CDC | 768 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 240 | #4SC(240) |  | UVA | [17 empty] | 2-04-06 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.240_UVA | 11KV #4SC 27RY(欠壓) | SC | D12/11/240/UVA |  |  |  | CDC | 769 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 240 | #4SC(240) |  | LBS | [17 empty] | 1-3F-10 | 1-3F-11 | 1-7B | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.240_LBS | 240(11KV #4SC) LBS | SC | D12/11/4SC/LBS |  |  |  | CDC | 770 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D12 | 仁愛DS | 22 | 22kV | 250 | #5SC(250) |  | CB | [17 empty] | 2-06-06 |  | 2-14 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.250_CB | 250(23KV #5SC) CB | SC | D12/22/250/CB |  |  |  | CDC | 771 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | 250 | #5SC(250) |  | SCA | [17 empty] | 2-06-07 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.250_SCA | 23KV #5SC 51,51N RY | SC | D12/22/250/SCA |  |  |  | CDC | 772 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | 250 | #5SC(250) |  | UVA | [17 empty] | 2-07-00 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.250_UVA | 23KV #5SC 27RY(欠壓) | SC | D12/22/250/UVA |  |  |  | CDC | 773 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | 260 | #6SC(260) |  | CB | [17 empty] | 2-08-05 |  | 2-1D | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.260_CB | 260(23KV #6SC) CB | SC | D12/22/260/CB |  |  |  | CDC | 774 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | 260 | #6SC(260) |  | SCA | [17 empty] | 2-08-06 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.260_SCA | 23KV #6SC 51,51N RY | SC | D12/22/260/SCA |  |  |  | CDC | 775 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | 260 | #6SC(260) |  | UVA | [17 empty] | 2-08-07 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.260_UVA | 23KV #6SC 27RY(欠壓) | SC | D12/22/260/UVA |  |  |  | CDC | 776 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | 270 | #7SC(270) |  | CB | [17 empty] | 2-0A-04 |  | 2-1F | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.270_CB | 270(23KV #7SC) CB | SC | D12/22/270/CB |  |  |  | CDC | 777 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | 270 | #7SC(270) |  | SCA | [17 empty] | 2-0A-05 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.270_SCA | 23KV #7SC 51,51N RY | SC | D12/22/270/SCA |  |  |  | CDC | 778 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | 270 | #7SC(270) |  | UVA | [17 empty] | 2-0A-06 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.270_UVA | 23KV #7SC 27RY(欠壓) | SC | D12/22/270/UVA |  |  |  | CDC | 779 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | 280 | #8SC(280) |  | CB | [17 empty] | 2-0C-03 |  | 2-28 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.280_CB | 280(23KV #8SC) CB | SC | D12/22/280/CB |  |  |  | CDC | 780 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 22 | 22kV | 280 | #8SC(280) |  | SCA | [17 empty] | 2-0C-04 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.280_SCA | 23KV #8SC 51,51N RY | SC | D12/22/280/SCA |  |  |  | CDC | 781 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | 280 | #8SC(280) |  | UVA | [17 empty] | 2-0C-05 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.280_UVA | 23KV #8SC 27RY(欠壓) | SC | D12/22/280/UVA |  |  |  | CDC | 782 | GENERICDIPoint | DS042_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1611BUS | #1BUS |  | VUA | [17 empty] | 1-35-11 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | D12/161/1BUS/BUS_VUA |  |  |  | CDC | 783 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1611BUS | #1BUS |  | 87A | [17 empty] | 1-05-02 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | D12/161/1BUS/87A |  |  |  | CDC | 784 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1611BUS | #1BUS |  | 87UL | [17 empty] | 1-36-09 |  | 1-7E | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | D12/161/1BUS/87UL |  |  |  | CDC | 785 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 161 | 161kV | 1612BUS | #2BUS |  | VUA | [17 empty] | 1-35-12 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | D12/161/2BUS/BUS_VUA |  |  |  | CDC | 786 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1612BUS | #2BUS |  | 87A | [17 empty] | 1-05-03 | [7 empty] | 161KV_N | [8 empty] | 仁愛DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | D12/161/2BUS/87A |  |  |  | CDC | 787 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | 1612BUS | #2BUS |  | 87UL | [17 empty] | 1-36-10 |  | 1-7F | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | D12/161/2BUS/87UL |  |  |  | CDC | 788 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D12 | 仁愛DS | 22 | 22kV | 11_ | 11/ |  | CBA | [17 empty] | 1-36-03 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | D12/22/ComPoint/CBA |  |  |  | CDC | 789 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | 11_ | 11/ |  | CBF | [17 empty] | 1-36-04 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | D12/22/ComPoint/CBF |  |  |  | CDC | 790 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV |  |  |  | CBA | [17 empty] | 1-35-07 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.161KV_CBA | 161KV斷路器重故障 | OTHER | D12/161/ComPoint/CBA |  |  |  | CDC | 791 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV |  |  |  | CBF | [17 empty] | 1-35-08 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | D12/161/ComPoint/CBF |  |  |  | CDC | 792 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | LINE | LINE |  | RCA | [17 empty] | 1-05-04 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | D12/161/ComPoint/RCA |  |  |  | CDC | 793 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV |  |  |  | COMT | [17 empty] | 1-36-01 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.161空壓機COMT | 161KV空壓機運轉超時警報 | OTHER | D12/0/ComPoint/COMT |  |  |  | CDC | 794 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 22 | 22kV | _SC | 23/ SC |  | 60A | [17 empty] | 1-36-02 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.23KV_SC_60A | 23/11KV SC 60A | OTHER | D12/22/ComPoint/60A |  |  |  | CDC | 795 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | FEEDER | FEEDER |  | RCA | [17 empty] | 1-36-05 | [7 empty] | DDCS2_2 | [8 empty] | 仁愛DS.FEEDER_RCA | 饋線復閉電驛動作 | OTHER | D12/22/ComPoint/LOA |  |  |  | CDC | 796 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.RTU_S/L | RTU SUPY/LOCAL | OTHER | D12/0/RTU/RTU_R_L |  |  |  | CDC | 797 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D12 | 仁愛DS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.TEST_CB | TEST CB | OTHER | D12/0/RTU/Test_CB |  |  |  | CDC | 798 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  |  |  |  | Fire1 | [17 empty] | 1-34-04 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | D12/0/StaDev/Fire1 |  |  |  | CDC | 799 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  |  |  |  | Fire2 | [17 empty] | 1-34-05 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.火災警報(2) | 火災警報(2) | OTHER | D12/0/StaDev/Fire2 |  |  |  | CDC | 800 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  |  |  |  | Fire3 | [17 empty] | 1-34-06 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.火災警報(3) | 火災警報(3) | OTHER | D12/0/StaDev/Fire3 |  |  |  | CDC | 801 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  |  |  |  | Fire4 | [17 empty] | 1-34-07 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.火災警報(4) | 火災警報(4) | OTHER | D12/0/StaDev/Fire4 |  |  |  | CDC | 802 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  |  |  |  | 火災警報(5) | [17 empty] | 1-34-08 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.火災警報(5) | 火災警報(5) | OTHER | D12/0/StaDev/Fire5 |  |  |  | CDC | 803 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  |  |  |  | OPA | [17 empty] | 1-35-03 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | D12/0/ComPoint/OPA |  |  |  | CDC | 804 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  |  |  |  | 25PFA | [17 empty] | 1-15-02 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER | D12/0/ComPoint/25PFA |  |  |  | CDC | 805 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  |  |  |  | 25TA | [17 empty] | 1-15-03 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | D12/0/ComPoint/25TA |  |  |  | CDC | 806 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  |  |  |  | SUBA | [17 empty] | 1-38-01 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.其他重故障 | 變電所內其他重故障 | OTHER | D12/0/StaDev/PSA |  |  |  | CDC | 807 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  |  |  |  | SUBF | [17 empty] | 1-38-00 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.其他輕故障 | 變電所內其他輕故障 | OTHER | D12/0/StaDev/PSF |  |  |  | CDC | 808 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  |  |  |  | ACB1 | [17 empty] | 1-35-00 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | D12/0/StaDev/ACB1 |  |  |  | CDC | 809 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
D12 | 仁愛DS | 0 |  |  |  |  | ACB2 | [17 empty] | 1-35-01 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | D12/0/StaDev/ACB2 |  |  |  | CDC | 810 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
D12 | 仁愛DS | 0 |  |  |  |  | ACBA | [17 empty] | 1-35-10 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.所內電源ACBA | 所內電源故障警報 | OTHER | D12/0/StaDev/ACBA |  |  |  | CDC | 811 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 所內電源開關ACB | 所內電源開關ACB |  | ACBT | [17 empty] | 1-35-02 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.所內電源ACBT | 所內電源開關ACB TIE | OTHER |  |  |  |  | CDC | 812 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D12 | 仁愛DS | 0 |  |  |  |  | STUV | [17 empty] | 1-35-04 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | D12/0/StaDev/STUV |  |  |  | CDC | 813 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-35-13 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | D12/0/StaDev/CHG1 |  |  |  | CDC | 814 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  |  |  |  | DCA | [17 empty] | 1-35-09 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.直流電源DCA | 直流電源故障警報 | OTHER | D12/0/StaDev/DCA |  |  |  | CDC | 815 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  |  |  |  | DCE | [17 empty] | 1-35-14 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.直流電源DCE | 直流電源接地故障警報 | OTHER | D12/0/StaDev/DCE |  |  |  | CDC | 816 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-38-02 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | D12/0/StaDev/CHG2 |  |  |  | CDC | 817 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  |  |  |  | CommACF | [17 empty] | 1-38-03 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | D12/0/StaDev/CommACF |  |  |  | CDC | 818 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  |  |  |  | Door1 | [17 empty] | 1-34-09 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.無人化門禁(1) | 無人化門禁(1)建築物大門 | OTHER | D12/0/StaDev/Door1 |  |  |  | CDC | 819 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  |  |  |  | Door2 | [17 empty] | 1-34-10 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.無人化門禁(2) | 無人化門禁(2)控制室大門 | OTHER | D12/0/StaDev/Door2 |  |  |  | CDC | 820 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  |  |  |  | Lights1 | [17 empty] | 1-34-14 |  | 1-7C | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.開關場照明(A) | 開關場照明(A) | OTHER | D12/0/StaDev/Lights1 |  |  |  | CDC | 821 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D12 | 仁愛DS | 0 |  |  |  |  | Lights2 | [17 empty] | 1-34-15 |  | 1-7D | [5 empty] | ADCS_N | [8 empty] | 仁愛DS.開關場照明(B) | 開關場照明(B) | OTHER | D12/0/StaDev/Lights2 |  |  |  | CDC | 822 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D12 | 仁愛DS | 0 |  | 1510 | 嘉義仁愛山線(1510) |  | 87CFA | [17 empty] | 1-36-14 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.1510_87CFA | 嘉義仁愛山線(1510)87RY通訊故障 | OTHER | D12/161/1510/87CFA |  |  |  | CDC | 823 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 1510 | 嘉義仁愛山線(1510) |  | RYFA | [17 empty] | 1-36-15 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.1510_RYFA | 嘉義仁愛山線(1510)數位電驛故障 | OTHER | D12/161/1510/RYFA |  |  |  | CDC | 824 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 1520 | 嘉義仁愛海線(1520) |  | 87CFA | [17 empty] | 1-36-12 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.1520_87CFA | 嘉義仁愛海線(1520)87RY通訊故障 | OTHER | D12/161/1520/87CFA |  |  |  | CDC | 825 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 1520 | 嘉義仁愛海線(1520) |  | RYFA | [17 empty] | 1-36-13 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.1520_RYFA | 嘉義仁愛海線(1520)數位電驛故障 | OTHER | D12/161/1520/RYFA |  |  |  | CDC | 826 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 1530 | 仁愛北回一路(1530) |  | 87CFA | [17 empty] | 1-37-02 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.1530_87CFA | 仁愛北回一路(1530)87RY通訊故障 | OTHER | D12/161/1530/87CFA |  |  |  | CDC | 827 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 1530 | 仁愛北回一路(1530) |  | RYFA | [17 empty] | 1-37-03 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.1530_RYFA | 仁愛北回一路(1530)數位電驛故障 | OTHER | D12/161/1530/RYFA |  |  |  | CDC | 828 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 1540 | 仁愛北回二路(1540) |  | 87CFA | [17 empty] | 1-37-00 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.1540_87CFA | 仁愛北回二路(1540)87RY通訊故障 | OTHER | D12/161/1540/87CFA |  |  |  | CDC | 829 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 1540 | 仁愛北回二路(1540) |  | RYFA | [17 empty] | 1-37-01 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.1540_RYFA | 仁愛北回二路(1540)數位電驛故障 | OTHER | D12/161/1540/RYFA |  |  |  | CDC | 830 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | _OSCA | _OSCA |  | 1 | [17 empty] | 1-05-05 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.161KV_OSCA_1 | 161KV示波器啟動警報(1) | OTHER | D12/161/ComPoint/OSCA |  |  |  | CDC | 831 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | _OSCA | _OSCA | [19 empty] | 1-05-06 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.161KV_OSCA_2 | 161KV示波器啟動警報(2) | OTHER | D12/161/ComPoint/OSCF |  |  |  | CDC | 832 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 310 | #1DTR(310) |  | GDA | [17 empty] | 1-07-02 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.310_GDA | 310開關箱IED RY GDA | OTHER | D12/11/310/GDA |  |  |  | CDC | 833 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 310 | #1DTR(310) |  | PHA2 | [17 empty] | 1-07-01 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.310_PHA2 | 310開關箱IED RY PHA | OTHER | D12/11/310/PHA |  |  |  | CDC | 834 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 320 | #1DTR(320) |  | GDA | [17 empty] | 1-07-05 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.320_GDA | 320開關箱IED RY GDA | OTHER | D12/11/320/GDA |  |  |  | CDC | 835 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 320 | #1DTR(320) |  | PHA2 | [17 empty] | 1-07-04 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.320_PHA2 | 320開關箱IED RY PHA | OTHER | D12/11/320/PHA |  |  |  | CDC | 836 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 330 | #2DTR(330) |  | GDA | [17 empty] | 1-09-00 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.330_GDA | 330開關箱IED RY GDA | OTHER | D12/11/330/GDA |  |  |  | CDC | 837 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 330 | #2DTR(330) |  | PHA2 | [17 empty] | 1-08-07 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.330_PHA2 | 330開關箱IED RY PHA | OTHER | D12/11/330/PHA |  |  |  | CDC | 838 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 340 | #2DTR(340) |  | GDA | [17 empty] | 1-09-03 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.340_GDA | 340開關箱IED RY GDA | OTHER | D12/11/340/GDA |  |  |  | CDC | 839 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 340 | #2DTR(340) |  | PHA2 | [17 empty] | 1-09-02 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.340_PHA2 | 340開關箱IED RY PHA | OTHER | D12/11/340/PHA |  |  |  | CDC | 840 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 350 | #3DTR(350) |  | GDA | [17 empty] | 1-0A-05 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.350_GDA | 350開關箱IED RY GDA | OTHER | D12/22/350/GDA |  |  |  | CDC | 841 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 350 | #3DTR(350) |  | PHA2 | [17 empty] | 1-0A-04 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.350_PHA2 | 350開關箱IED RY PHA | OTHER | D12/22/350/PHA |  |  |  | CDC | 842 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 370 | #4DTR(370) |  | GDA | [17 empty] | 1-0B-07 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.370_GDA | 370開關箱IED RY GDA | OTHER | D12/22/370/GDA |  |  |  | CDC | 843 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 370 | #4DTR(370) |  | PHA2 | [17 empty] | 1-0B-06 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.370_PHA2 | 370開關箱IED RY PHA | OTHER | D12/22/370/PHA |  |  |  | CDC | 844 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  |  |  |  | 水位警報(1) | [17 empty] | 1-35-15 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.水位警報(1) | 地下室水位警報(1) | OTHER | D12/0/StaDev/Water1 |  |  |  | CDC | 845 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  |  |  |  | 水位警報(2) | [17 empty] | 1-36-00 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.水位警報(2) | 地下室水位警報(2) | OTHER | D12/0/StaDev/Water2 |  |  |  | CDC | 846 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  |  |  |  | 空調機故障 | [17 empty] | 1-35-05 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.空調機故障 | 空調機故障或電源跳脫 | OTHER | D12/0/StaDev/AIRCON |  |  |  | CDC | 847 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  |  |  |  | OilLeak1 | [17 empty] | 1-36-06 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.洩油池警報(1) | 洩油池水位警報(1) | OTHER | D12/0/StaDev/OilLeak1 |  |  |  | CDC | 848 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  |  |  |  | OilLeak2 | [17 empty] | 1-36-07 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.洩油池警報(2) | 洩油池水位警報(2) | OTHER | D12/0/StaDev/OilLeak2 |  |  |  | CDC | 849 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  |  |  |  | 通信機房溫度 | [17 empty] | 1-38-06 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.通信機房溫度 | 通信機房溫度警報 | OTHER | D12/0/StaDev/R_Temp |  |  |  | CDC | 850 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  |  |  |  | 無人化門禁(4) | [17 empty] | 1-34-12 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.無人化門禁(4) | 無人化門禁(4) | OTHER | D12/0/StaDev/Door4 |  |  |  | CDC | 851 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  |  |  |  | 無人化門禁(5) | [17 empty] | 1-34-13 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.無人化門禁(5) | 無人化門禁(5) | OTHER | D12/0/StaDev/Door5 |  |  |  | CDC | 852 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  |  |  |  | 路燈照明 | [17 empty] | 1-38-07 |  | 1-01 | [5 empty] | DDCS2_2 | [8 empty] | 仁愛DS.路燈照明 | 路燈控制 | OTHER | D12/0/StaDev/Lights3 |  |  |  | CDC | 853 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D12 | 仁愛DS | 0 |  | 1500TIE | 1500 |  | 50SA | [17 empty] | 1-36-11 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | D12/161/1500/50SA |  |  |  | CDC | 854 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | TEST/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  |  |  |  | PMA | [17 empty] | 1-35-06 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.PMA | 電力量測表計故障 | OTHER | D12/0/StaDev/PMA |  |  |  | CDC | 855 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV |  |  |  | OSCF | [17 empty] | 1-38-08 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | D12/0/ComPoint/OSCF |  |  |  | CDC | 856 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  |  |  |  | Burglar1 | [17 empty] | 1-34-11 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | D12/0/StaDev/Door3 |  |  |  | CDC | 857 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | 81RY | 310 |  | A/S(1) | [17 empty] | 1-15-04 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.81RY_A/S(1) | 310 81RY A/S | OTHER | D12/11/310/81A |  |  |  | CDC | 858 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
D12 | 仁愛DS | 0 |  | BVS | BVS |  | RY | [17 empty] | 1-38-09 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.BVS_RY | BVS GRZ100 RY U/L | OTHER | D12/0/ComPoint/GRZ100 |  |  |  | CDC | 859 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | LOCK/USE | USE
D12 | 仁愛DS | 0 |  |  |  |  | GEN | [17 empty] | 1-31-07 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.GEN | 緊急發電機運轉 | OTHER | D12/0/ComPoint/1A5Other |  |  |  | CDC | 860 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D12 | 仁愛DS | 161 | 161kV | _BUS | BUS |  | 87CTFA | [17 empty] | 1-38-15 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.161KV_BUS_CTFA | 161KV BUS 87RY CT回路故障 | OTHER | D12/161/BUS/87CTFA |  |  |  | CDC | 861 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 161 | 161kV | _BUS | BUS |  | RYFA | [17 empty] | 1-38-14 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | D12/161/BUS/RYFA |  |  |  | CDC | 862 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  |  |  |  | RTUA | [17 empty] | 1-0C-01 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.RTUA | RTU發生異常 | OTHER | D12/0/RTU/RTUA |  |  |  | CDC | 863 | GENERICDIPoint | DS042_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 0 |  | OLTC | OLTC |  | OLTCA | [17 empty] | 1-31-06 | [7 empty] | ADCS_N | [8 empty] | 仁愛DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | D12/0/ComPoint/OLTC_A |  |  |  | CDC | 864 | GENERICDIPoint | DS042_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D12 | 仁愛DS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 865 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 11 | 11kV | 220_SC | #2SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 866 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 11 | 11kV | 230_SC | #3SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.230_SC_CAP | 11KV#3SC 容量 | SC | [5 empty] | 867 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 11 | 11kV | 240_SC | #4SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.240_SC_CAP | 11KV#4SC 容量 | SC | [5 empty] | 868 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 22 | 22kV | 250_SC | #5SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.250_SC_CAP | 23KV#5SC 容量 | SC | [5 empty] | 869 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 22 | 22kV | 260_SC | #6SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.260_SC_CAP | 23KV#6SC 容量 | SC | [5 empty] | 870 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 22 | 22kV | 270_SC | #7SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.270_SC_CAP | 23KV#7SC 容量 | SC | [5 empty] | 871 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 22 | 22kV | 280_SC | #8SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 仁愛DS.280_SC_CAP | 23KV#8SC 容量 | SC | [5 empty] | 872 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D12 | 仁愛DS | 161 | 161kV | 1510 | 嘉義仁愛山線(1510) |  | LE0 | 1510LE | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.1510LE | 1510LE (非取樣點) | LINE161 | D12/161/1510/LE0 |  |  |  |  | 873 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 1510 | 嘉義仁愛山線(1510) |  | BE0 | 1510BE | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.1510BE | 1510BE (非取樣點) | LINE161 | D12/161/1510/BE0 |  |  |  |  | 874 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 1520 | 嘉義仁愛海線(1520) |  | LE0 | 1520LE | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.1520LE | 1520LE (非取樣點) | LINE161 | D12/161/1520/LE0 |  |  |  |  | 875 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 1520 | 嘉義仁愛海線(1520) |  | BE0 | 1520BE | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.1520BE | 1520BE (非取樣點) | LINE161 | D12/161/1520/BE0 |  |  |  |  | 876 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 1530 | 仁愛北回一路(1530) |  | LE0 | 1530LE | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.1530LE | 1530LE (非取樣點) | LINE161 | D12/161/1530/LE0 |  |  |  |  | 877 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 1530 | 仁愛北回一路(1530) |  | BE0 | 1530BE | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.1530BE | 1530BE (非取樣點) | LINE161 | D12/161/1530/BE0 |  |  |  |  | 878 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 1540 | 仁愛北回二路(1540) |  | LE0 | 1540LE | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.1540LE | 1540LE (非取樣點) | LINE161 | D12/161/1540/LE0 |  |  |  |  | 879 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 1540 | 仁愛北回二路(1540) |  | BE0 | 1540BE | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.1540BE | 1540BE (非取樣點) | LINE161 | D12/161/1540/BE0 |  |  |  |  | 880 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA21 | JA21_DS |  | DS1 | JA21_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA21_DS | JA21_DS (非取樣點) | FEEDER | D12/11/JA21/DS |  |  |  |  | 881 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA21 | JA21_ES |  | LE0 | JA21_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA21_ES | JA21_ES (非取樣點) | FEEDER | D12/11/JA21/ES |  |  |  |  | 882 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA22 | JA22_DS |  | DS1 | JA22_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA22_DS | JA22_DS (非取樣點) | FEEDER | D12/11/JA22/DS |  |  |  |  | 883 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA22 | JA22_ES |  | LE0 | JA22_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA22_ES | JA22_ES (非取樣點) | FEEDER | D12/11/JA22/ES |  |  |  |  | 884 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA23 | JA23_DS |  | DS1 | JA23_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA23_DS | JA23_DS (非取樣點) | FEEDER | D12/11/JA23/DS |  |  |  |  | 885 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA23 | JA23_ES |  | LE0 | JA23_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA23_ES | JA23_ES (非取樣點) | FEEDER | D12/11/JA23/ES |  |  |  |  | 886 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA24 | JA24_DS |  | DS1 | JA24_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA24_DS | JA24_DS (非取樣點) | FEEDER | D12/11/JA24/DS |  |  |  |  | 887 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA24 | JA24_ES |  | LE0 | JA24_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA24_ES | JA24_ES (非取樣點) | FEEDER | D12/11/JA24/ES |  |  |  |  | 888 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA25 | JA25_DS |  | DS1 | JA25_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA25_DS | JA25_DS (非取樣點) | FEEDER | D12/11/JA25/DS |  |  |  |  | 889 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA25 | JA25_ES |  | LE0 | JA25_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA25_ES | JA25_ES (非取樣點) | FEEDER | D12/11/JA25/ES |  |  |  |  | 890 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA26 | JA26_DS |  | DS1 | JA26_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA26_DS | JA26_DS (非取樣點) | FEEDER | D12/11/JA26/DS |  |  |  |  | 891 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA26 | JA26_ES |  | LE0 | JA26_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA26_ES | JA26_ES (非取樣點) | FEEDER | D12/11/JA26/ES |  |  |  |  | 892 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA27 | JA27_DS |  | DS1 | JA27_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA27_DS | JA27_DS (非取樣點) | FEEDER | D12/11/JA27/DS |  |  |  |  | 893 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA27 | JA27_ES |  | LE0 | JA27_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA27_ES | JA27_ES (非取樣點) | FEEDER | D12/11/JA27/ES |  |  |  |  | 894 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA28 | JA28_DS |  | DS1 | JA28_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA28_DS | JA28_DS (非取樣點) | FEEDER | D12/11/JA28/DS |  |  |  |  | 895 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA28 | JA28_ES |  | LE0 | JA28_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA28_ES | JA28_ES (非取樣點) | FEEDER | D12/11/JA28/ES |  |  |  |  | 896 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA29 | JA29_DS |  | DS1 | JA29_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA29_DS | JA29_DS (非取樣點) | FEEDER | D12/11/JA29/DS |  |  |  |  | 897 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA29 | JA29_ES |  | LE0 | JA29_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA29_ES | JA29_ES (非取樣點) | FEEDER | D12/11/JA29/ES |  |  |  |  | 898 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA30 | JA30_DS |  | DS1 | JA30_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA30_DS | JA30_DS (非取樣點) | FEEDER | D12/11/JA30/DS |  |  |  |  | 899 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA30 | JA30_ES |  | LE0 | JA30_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA30_ES | JA30_ES (非取樣點) | FEEDER | D12/11/JA30/ES |  |  |  |  | 900 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA31 | JA31_DS |  | DS1 | JA31_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA31_DS | JA31_DS (非取樣點) | FEEDER | D12/11/JA31/DS |  |  |  |  | 901 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA31 | JA31_ES |  | LE0 | JA31_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA31_ES | JA31_ES (非取樣點) | FEEDER | D12/11/JA31/ES |  |  |  |  | 902 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA32 | JA32_DS |  | DS1 | JA32_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA32_DS | JA32_DS (非取樣點) | FEEDER | D12/11/JA32/DS |  |  |  |  | 903 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA32 | JA32_ES |  | LE0 | JA32_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA32_ES | JA32_ES (非取樣點) | FEEDER | D12/11/JA32/ES |  |  |  |  | 904 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA33 | JA33_DS |  | DS1 | JA33_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA33_DS | JA33_DS (非取樣點) | FEEDER | D12/11/JA33/DS |  |  |  |  | 905 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA33 | JA33_ES |  | LE0 | JA33_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA33_ES | JA33_ES (非取樣點) | FEEDER | D12/11/JA33/ES |  |  |  |  | 906 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA34 | JA34_DS |  | DS1 | JA34_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA34_DS | JA34_DS (非取樣點) | FEEDER | D12/11/JA34/DS |  |  |  |  | 907 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA34 | JA34_ES |  | LE0 | JA34_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA34_ES | JA34_ES (非取樣點) | FEEDER | D12/11/JA34/ES |  |  |  |  | 908 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA35 | JA35_DS |  | DS1 | JA35_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA35_DS | JA35_DS (非取樣點) | FEEDER | D12/11/JA35/DS |  |  |  |  | 909 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA35 | JA35_ES |  | LE0 | JA35_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA35_ES | JA35_ES (非取樣點) | FEEDER | D12/11/JA35/ES |  |  |  |  | 910 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA36 | JA36_DS |  | DS1 | JA36_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA36_DS | JA36_DS (非取樣點) | FEEDER | D12/11/JA36/DS |  |  |  |  | 911 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA36 | JA36_ES |  | LE0 | JA36_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA36_ES | JA36_ES (非取樣點) | FEEDER | D12/11/JA36/ES |  |  |  |  | 912 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA37 | JA37_DS |  | DS1 | JA37_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA37_DS | JA37_DS (非取樣點) | FEEDER | D12/11/JA37/DS |  |  |  |  | 913 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA37 | JA37_ES |  | LE0 | JA37_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA37_ES | JA37_ES (非取樣點) | FEEDER | D12/11/JA37/ES |  |  |  |  | 914 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA38 | JA38_DS |  | DS1 | JA38_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA38_DS | JA38_DS (非取樣點) | FEEDER | D12/11/JA38/DS |  |  |  |  | 915 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA38 | JA38_ES |  | LE0 | JA38_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA38_ES | JA38_ES (非取樣點) | FEEDER | D12/11/JA38/ES |  |  |  |  | 916 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA39 | JA39_DS |  | DS1 | JA39_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA39_DS | JA39_DS (非取樣點) | FEEDER | D12/11/JA39/DS |  |  |  |  | 917 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA39 | JA39_ES |  | LE0 | JA39_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA39_ES | JA39_ES (非取樣點) | FEEDER | D12/11/JA39/ES |  |  |  |  | 918 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA40 | JA40_DS |  | DS1 | JA40_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA40_DS | JA40_DS (非取樣點) | FEEDER | D12/11/JA40/DS |  |  |  |  | 919 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA40 | JA40_ES |  | LE0 | JA40_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA40_ES | JA40_ES (非取樣點) | FEEDER | D12/11/JA40/ES |  |  |  |  | 920 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA71 | JA71_DS |  | DS1 | JA71_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA71_DS | JA71_DS (非取樣點) | FEEDER | D12/22/JA71/DS |  |  |  |  | 921 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA71 | JA71_ES |  | LE0 | JA71_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA71_ES | JA71_ES (非取樣點) | FEEDER | D12/22/JA71/ES |  |  |  |  | 922 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA72 | JA72_DS |  | DS1 | JA72_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA72_DS | JA72_DS (非取樣點) | FEEDER | D12/22/JA72/DS |  |  |  |  | 923 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA72 | JA72_ES |  | LE0 | JA72_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA72_ES | JA72_ES (非取樣點) | FEEDER | D12/22/JA72/ES |  |  |  |  | 924 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA73 | JA73_DS |  | DS1 | JA73_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA73_DS | JA73_DS (非取樣點) | FEEDER | D12/22/JA73/DS |  |  |  |  | 925 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA73 | JA73_ES |  | LE0 | JA73_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA73_ES | JA73_ES (非取樣點) | FEEDER | D12/22/JA73/ES |  |  |  |  | 926 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA74 | JA74_DS |  | DS1 | JA74_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA74_DS | JA74_DS (非取樣點) | FEEDER | D12/22/JA74/DS |  |  |  |  | 927 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA74 | JA74_ES |  | LE0 | JA74_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA74_ES | JA74_ES (非取樣點) | FEEDER | D12/22/JA74/ES |  |  |  |  | 928 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA75 | JA75_DS |  | DS1 | JA75_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA75_DS | JA75_DS (非取樣點) | FEEDER | D12/22/JA75/DS |  |  |  |  | 929 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA75 | JA75_ES |  | LE0 | JA75_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA75_ES | JA75_ES (非取樣點) | FEEDER | D12/22/JA75/ES |  |  |  |  | 930 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA76 | JA76_DS |  | DS1 | JA76_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA76_DS | JA76_DS (非取樣點) | FEEDER | D12/22/JA76/DS |  |  |  |  | 931 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA76 | JA76_ES |  | LE0 | JA76_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA76_ES | JA76_ES (非取樣點) | FEEDER | D12/22/JA76/ES |  |  |  |  | 932 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA77 | JA77_DS |  | DS1 | JA77_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA77_DS | JA77_DS (非取樣點) | FEEDER | D12/22/JA77/DS |  |  |  |  | 933 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA77 | JA77_ES |  | LE0 | JA77_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA77_ES | JA77_ES (非取樣點) | FEEDER | D12/22/JA77/ES |  |  |  |  | 934 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA78 | JA78_DS |  | DS1 | JA78_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA78_DS | JA78_DS (非取樣點) | FEEDER | D12/22/JA78/DS |  |  |  |  | 935 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA78 | JA78_ES |  | LE0 | JA78_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA78_ES | JA78_ES (非取樣點) | FEEDER | D12/22/JA78/ES |  |  |  |  | 936 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | 101 | 101 |  | 101 | 101 | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.101 | 101 (非取樣點) | TIE | D12/11/100/D1 |  |  |  |  | 937 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 102 | 102 |  | 102 | 102 | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.102 | 102 (非取樣點) | TIE | D12/11/100/D2 |  |  |  |  | 938 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.1501E | 1501E (非取樣點) | TIE | D12/161/1500/E1 |  |  |  |  | 939 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.1502E | 1502E (非取樣點) | TIE | D12/161/1500/E2 |  |  |  |  | 940 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | 201 | 201 |  | 201 | 201 | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.201 | 201 (非取樣點) | TIE | D12/11/200/D1 |  |  |  |  | 941 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 202 | 202 |  | 202 | 202 | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.202 | 202 (非取樣點) | TIE | D12/11/200/D2 |  |  |  |  | 942 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 401 | 401 |  | 401 | 401 | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.401 | 401 (非取樣點) | TIE | D12/22/400/D1 |  |  |  |  | 943 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 402 | 402 |  | 402 | 402 | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.402 | 402 (非取樣點) | TIE | D12/22/400/D2 |  |  |  |  | 944 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 391 | 391 |  | 391 | 391 | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.391 | 391 (非取樣點) | OTHER | D12/11/390/D1 |  |  |  |  | 945 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 391E | 391E |  | 391E | 391E | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.391E | 391E (非取樣點) | OTHER | D12/11/390/E1 |  |  |  |  | 946 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | 491 | 491 |  | 491 | 491 | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.491 | 491 (非取樣點) | OTHER | D12/11/490/D1 |  |  |  |  | 947 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 491E | 491E |  | 491E | 491E | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.491E | 491E (非取樣點) | OTHER | D12/11/490/E1 |  |  |  |  | 948 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | 1750TE | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.1750TE | 1750TE (非取樣點) | MTR | D12/161/1750/TE0 |  |  |  |  | 949 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | 1750BE | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.1750BE | 1750BE (非取樣點) | MTR | D12/161/1750/BE0 |  |  |  |  | 950 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | 311 | 311 |  | 311 | 311 | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.311 | 311 (非取樣點) | MTR | D12/11/310/D1 |  |  |  |  | 951 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 310 | #1DTR(310) |  | E1 | 311E | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.311E | 311E (非取樣點) | MTR | D12/11/310/E1 |  |  |  |  | 952 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | 321 | 321 |  | 321 | 321 | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.321 | 321 (非取樣點) | MTR | D12/11/320/D1 |  |  |  |  | 953 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 320 | #1DTR(320) |  | E1 | 321E | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.321E | 321E (非取樣點) | MTR | D12/11/320/E1 |  |  |  |  | 954 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | 1760TE | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.1760TE | 1760TE (非取樣點) | MTR | D12/161/1760/TE0 |  |  |  |  | 955 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | 1760BE | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.1760BE | 1760BE (非取樣點) | MTR | D12/161/1760/BE0 |  |  |  |  | 956 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | 331 | 331 |  | 331 | 331 | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.331 | 331 (非取樣點) | MTR | D12/11/330/D1 |  |  |  |  | 957 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 330 | #2DTR(330) |  | E1 | 331E | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.331E | 331E (非取樣點) | MTR | D12/11/330/E1 |  |  |  |  | 958 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | 341 | 341 |  | 341 | 341 | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.341 | 341 (非取樣點) | MTR | D12/11/340/D1 |  |  |  |  | 959 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 340 | #2DTR(340) |  | E1 | 341E | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.341E | 341E (非取樣點) | MTR | D12/11/340/E1 |  |  |  |  | 960 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | 1770TE | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.1770TE | 1770TE (非取樣點) | MTR | D12/161/1770/TE0 |  |  |  |  | 961 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | 1770BE | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.1770BE | 1770BE (非取樣點) | MTR | D12/161/1770/BE0 |  |  |  |  | 962 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | 351 | 351 |  | 351 | 351 | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.351 | 351 (非取樣點) | MTR | D12/22/350/D1 |  |  |  |  | 963 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 350 | #3DTR(350) |  | E1 | 351E | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.351E | 351E (非取樣點) | MTR | D12/22/350/E1 |  |  |  |  | 964 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 1780 | #4DTR(1780) |  | TE0 | 1780TE | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.1780TE | 1780TE (非取樣點) | MTR | D12/161/1780/TE0 |  |  |  |  | 965 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 161 | 161kV | 1780 | #4DTR(1780) |  | BE0 | 1780BE | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.1780BE | 1780BE (非取樣點) | MTR | D12/161/1780/BE0 |  |  |  |  | 966 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | 371 | 371 |  | 371 | 371 | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.371 | 371 (非取樣點) | MTR | D12/22/370/D1 |  |  |  |  | 967 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 370 | #4DTR(370) |  | E1 | 371E | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.371E | 371E (非取樣點) | MTR | D12/22/370/E1 |  |  |  |  | 968 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | 211E | 211E |  | 211E | 211E | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.211E | 211E (非取樣點) | SC | D12/11/210/E1 |  |  |  |  | 969 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | 211 | 211 |  | 211 | 211 | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.211 | 211 (非取樣點) | SC | D12/11/210/D1 |  |  |  |  | 970 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 221E | 221E |  | 221E | 221E | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.221E | 221E (非取樣點) | SC | D12/11/220/E1 |  |  |  |  | 971 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | 221 | 221 |  | 221 | 221 | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.221 | 221 (非取樣點) | SC | D12/11/220/D1 |  |  |  |  | 972 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 231E | 231E |  | 231E | 231E | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.231E | 231E (非取樣點) | SC | D12/11/230/E1 |  |  |  |  | 973 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | 231 | 231 |  | 231 | 231 | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.231 | 231 (非取樣點) | SC | D12/11/230/D1 |  |  |  |  | 974 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 241E | 241E |  | 241E | 241E | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.241E | 241E (非取樣點) | SC | D12/11/240/E1 |  |  |  |  | 975 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | 241 | 241 |  | 241 | 241 | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.241 | 241 (非取樣點) | SC | D12/11/240/D1 |  |  |  |  | 976 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 251E | 251E |  | 251E | 251E | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.251E | 251E (非取樣點) | SC | D12/22/250/E1 |  |  |  |  | 977 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | 251 | 251 |  | 251 | 251 | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.251 | 251 (非取樣點) | SC | D12/22/250/D1 |  |  |  |  | 978 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 261E | 261E |  | 261E | 261E | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.261E | 261E (非取樣點) | SC | D12/22/260/E1 |  |  |  |  | 979 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | 261 | 261 |  | 261 | 261 | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.261 | 261 (非取樣點) | SC | D12/22/260/D1 |  |  |  |  | 980 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 271E | 271E |  | 271E | 271E | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.271E | 271E (非取樣點) | SC | D12/22/270/E1 |  |  |  |  | 981 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | 271 | 271 |  | 271 | 271 | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.271 | 271 (非取樣點) | SC | D12/22/270/D1 |  |  |  |  | 982 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 281E | 281E |  | 281E | 281E | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.281E | 281E (非取樣點) | SC | D12/22/280/E1 |  |  |  |  | 983 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | 281 | 281 |  | 281 | 281 | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.281 | 281 (非取樣點) | SC | D12/22/280/D1 |  |  |  |  | 984 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 15B1E | 15B1E |  | BE1 | 15B1E | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.15B1E | 15B1E (非取樣點) | BUS | D12/161/161B1E/BE1 |  |  |  |  | 985 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | 15B2E | 15B2E |  | BE2 | 15B2E | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.15B2E | 15B2E (非取樣點) | BUS | D12/161/161B2E/BE2 |  |  |  |  | 986 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 987 | NotelDIPoint | [38 empty] | START/STOP | STOP
D12 | 仁愛DS | 0 |  |  |  |  | 101E | 101E | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.101E | 101E(非取樣點) | OTHER | D12/11/100/E1 |  |  |  |  | 988 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  |  |  |  | 102E | 102E | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.102E | 102E(非取樣點) | OTHER | D12/11/100/E2 |  |  |  |  | 989 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  |  |  |  | 201E | 201E | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.201E | 201E(非取樣點) | OTHER | D12/11/200/E1 |  |  |  |  | 990 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  |  |  |  | 202E | 202E | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.202E | 202E(非取樣點) | OTHER | D12/11/200/E2 |  |  |  |  | 991 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  |  |  |  | 401E | 401E | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.401E | 401E(非取樣點) | OTHER | D12/22/400/E1 |  |  |  |  | 992 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  |  |  |  | 402E | 402E | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.402E | 402E(非取樣點) | OTHER | D12/22/400/E2 |  |  |  |  | 993 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA5A | JA5A_DS |  | DS1 | JA5A_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5A_DS | JA5A_DS (非取樣點) | FEEDER | D12/22/JA5A/DS |  |  |  |  | 994 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA5A | JA5A_ES |  | LE0 | JA5A_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5A_ES | JA5A_ES (非取樣點) | FEEDER | D12/22/JA5A/ES |  |  |  |  | 995 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA5B | JA5B_DS |  | DS1 | JA5B_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5B_DS | JA5B_DS (非取樣點) | FEEDER | D12/22/JA5B/DS |  |  |  |  | 996 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA5B | JA5B_ES |  | LE0 | JA5B_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5B_ES | JA5B_ES (非取樣點) | FEEDER | D12/22/JA5B/ES |  |  |  |  | 997 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA5C | JA5C_DS |  | DS1 | JA5C_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5C_DS | JA5C_DS (非取樣點) | FEEDER | D12/22/JA5C/DS |  |  |  |  | 998 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA5C | JA5C_ES |  | LE0 | JA5C_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5C_ES | JA5C_ES (非取樣點) | FEEDER | D12/22/JA5C/ES |  |  |  |  | 999 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA5D | JA5D_DS |  | DS1 | JA5D_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5D_DS | JA5D_DS (非取樣點) | FEEDER | D12/22/JA5D/DS |  |  |  |  | 1000 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA5D | JA5D_ES |  | LE0 | JA5D_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5D_ES | JA5D_ES (非取樣點) | FEEDER | D12/22/JA5D/ES |  |  |  |  | 1001 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA5F | JA5F_DS |  | DS1 | JA5F_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5F_DS | JA5F_DS (非取樣點) | FEEDER | D12/22/JA5F/DS |  |  |  |  | 1002 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA5F | JA5F_ES |  | LE0 | JA5F_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5F_ES | JA5F_ES (非取樣點) | FEEDER | D12/22/JA5F/ES |  |  |  |  | 1003 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA5G | JA5G_DS |  | DS1 | JA5G_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5G_DS | JA5G_DS (非取樣點) | FEEDER | D12/22/JA5G/DS |  |  |  |  | 1004 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA5G | JA5G_ES |  | LE0 | JA5G_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5G_ES | JA5G_ES (非取樣點) | FEEDER | D12/22/JA5G/ES |  |  |  |  | 1005 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA5H | JA5H_DS |  | DS1 | JA5H_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5H_DS | JA5H_DS (非取樣點) | FEEDER | D12/22/JA5H/DS |  |  |  |  | 1006 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA5H | JA5H_ES |  | LE0 | JA5H_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5H_ES | JA5H_ES (非取樣點) | FEEDER | D12/22/JA5H/ES |  |  |  |  | 1007 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | JA5K | JA5K_DS |  | DS1 | JA5K_DS | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5K_DS | JA5K_DS (非取樣點) | FEEDER | D12/22/JA5K/DS |  |  |  |  | 1008 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | JA5K | JA5K_ES |  | LE0 | JA5K_ES | [24 empty] | DDCS2_2 | [8 empty] | 仁愛DS.JA5K_ES | JA5K_ES (非取樣點) | FEEDER | D12/22/JA5K/ES |  |  |  |  | 1009 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | 1ABUS | 1ABUS |  | PTD | 1ABUS_PTD | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.1ABUS_PTD | #1ABUS_PTD(非取樣點) | OTHER | [5 empty] | 1010 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 1ABUS | 1ABUS |  | PTE | 1ABUS_PTE | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.1ABUS_PTE | #1ABUS_PTE(非取樣點) | OTHER | [5 empty] | 1011 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | 1BBUS | 1BBUS |  | PTD | 1BBUS_PTD | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.1BBUS_PTD | #1BBUS_PTD(非取樣點) | OTHER | [5 empty] | 1012 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 1BBUS | 1BBUS |  | PTE | 1BBUS_PTE | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.1BBUS_PTE | #1BBUS_PTE(非取樣點) | OTHER | [5 empty] | 1013 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | 2ABUS | 2ABUS |  | PTD | 2ABUS_PTD | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.2ABUS_PTD | #2ABUS_PTD(非取樣點) | OTHER | [5 empty] | 1014 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 2ABUS | 2ABUS |  | PTE | 2ABUS_PTE | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.2ABUS_PTE | #2ABUS_PTE(非取樣點) | OTHER | [5 empty] | 1015 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | 2BBUS | 2BBUS |  | PTD | 2BBUS_PTD | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.2BBUS_PTD | #2BBUS_PTD(非取樣點) | OTHER | [5 empty] | 1016 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 2BBUS | 2BBUS |  | PTE | 2BBUS_PTE | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.2BBUS_PTE | #2BBUS_PTE(非取樣點) | OTHER | [5 empty] | 1017 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | 3BUS | 3BUS |  | PTD | 3BUS_PTD | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.3BUS_PTD | #3BUS_PTD(非取樣點) | OTHER | [5 empty] | 1018 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 3BUS | 3BUS |  | PTE | 3BUS_PTE | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.3BUS_PTE | #3BUS_PTE(非取樣點) | OTHER | [5 empty] | 1019 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D12 | 仁愛DS | 0 |  | 4BUS | 4BUS |  | PTD | 4BUS_PTD | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.4BUS_PTD | #4BUS_PTD(非取樣點) | OTHER | [5 empty] | 1020 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D12 | 仁愛DS | 0 |  | 4BUS | 4BUS |  | PTE | 4BUS_PTE | [24 empty] | ADCS_N | [8 empty] | 仁愛DS.4BUS_PTE | #4BUS_PTE(非取樣點) | OTHER | [5 empty] | 1021 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo