## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D13 | 虎科DS | 161 | 161kV | 1960 | #2SHR(1960) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_A1 | [8 empty] | 虎科DS.1960BE | 1960BE(非取樣點) | OTHER | [5 empty] | 2 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1960 | #2SHR(1960) |  | RE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_A1 | [8 empty] | 虎科DS.1960RE | 1960RE(非取樣點) | OTHER | [5 empty] | 3 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1570 | 虎科～虎菁一路(1570) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_A1 | [8 empty] | 虎科DS.1570LE | 1570LE (非取樣點) | LINE161 | [5 empty] | 4 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1570 | 虎科～虎菁一路(1570) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_A1 | [8 empty] | 虎科DS.1570BE | 1570BE (非取樣點) | LINE161 | [5 empty] | 5 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1580 | 虎科～虎菁二路(1580) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_A1 | [8 empty] | 虎科DS.1580LE | 1580LE (非取樣點) | LINE161 | [5 empty] | 6 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1580 | 虎科～虎菁二路(1580) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_A1 | [8 empty] | 虎科DS.1580BE | 1580BE (非取樣點) | LINE161 | [5 empty] | 7 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_A1 | [8 empty] | 虎科DS.1610LE | 1610LE (非取樣點) | LINE161 | [5 empty] | 8 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_A1 | [8 empty] | 虎科DS.1610BE | 1610BE (非取樣點) | LINE161 | [5 empty] | 9 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_A1 | [8 empty] | 虎科DS.1620LE | 1620LE (非取樣點) | LINE161 | [5 empty] | 10 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_A1 | [8 empty] | 虎科DS.1620BE | 1620BE (非取樣點) | LINE161 | [5 empty] | 11 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1630 | 越港虎科紅線(1630) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_A1 | [8 empty] | 虎科DS.1630LE | 1630LE (非取樣點) | LINE161 | [5 empty] | 12 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1630 | 越港虎科紅線(1630) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_A1 | [8 empty] | 虎科DS.1630BE | 1630BE (非取樣點) | LINE161 | [5 empty] | 13 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1640 | 越港虎科白線(1640) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_A1 | [8 empty] | 虎科DS.1640LE | 1640LE (非取樣點) | LINE161 | [5 empty] | 14 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1640 | 越港虎科白線(1640) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_A1 | [8 empty] | 虎科DS.1640BE | 1640BE (非取樣點) | LINE161 | [5 empty] | 15 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_A1 | [8 empty] | 虎科DS.1760TE | 1760TE (非取樣點) | MTR | [5 empty] | 16 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_A1 | [8 empty] | 虎科DS.1760BE | 1760BE (非取樣點) | MTR | [5 empty] | 17 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_A1 | [8 empty] | 虎科DS.1770TE | 1770TE (非取樣點) | MTR | [5 empty] | 18 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_A1 | [8 empty] | 虎科DS.1770BE | 1770BE (非取樣點) | MTR | [5 empty] | 19 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1780 | #4DTR(1780) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_A1 | [8 empty] | 虎科DS.1780TE | 1780TE (非取樣點) | MTR | [5 empty] | 20 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1780 | #4DTR(1780) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_A1 | [8 empty] | 虎科DS.1780BE | 1780BE (非取樣點) | MTR | [5 empty] | 21 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_A1 | [8 empty] | 虎科DS.1501E | 1501E (非取樣點) | TIE | [5 empty] | 22 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_A1 | [8 empty] | 虎科DS.1502E | 1502E (非取樣點) | TIE | [5 empty] | 23 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | D1 | 331(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.331 | 331 (非取樣點) | MTR | [5 empty] | 24 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | E1 | 331E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.331E | 331E (非取樣點) | MTR | [5 empty] | 25 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | D1 | 341(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.341 | 341 (非取樣點) | MTR | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | E1 | 341E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.341E | 341E (非取樣點) | MTR | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | D1 | 351(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.351 | 351 (非取樣點) | MTR | [5 empty] | 28 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | E1 | 351E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.351E | 351E (非取樣點) | MTR | [5 empty] | 29 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | D1 | 361(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.361 | 361 (非取樣點) | MTR | [5 empty] | 30 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | E1 | 361E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.361E | 361E (非取樣點) | MTR | [5 empty] | 31 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 22 | 22kV | 370 | #4DTR(A)(370) |  | D1 | 371(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.371 | 371 (非取樣點) | MTR | [5 empty] | 32 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | 370 | #4DTR(A)(370) |  | E1 | 371E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.371E | 371E (非取樣點) | MTR | [5 empty] | 33 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 22 | 22kV | 380 | #4DTR(B)(380) |  | D1 | 381(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.381 | 381 (非取樣點) | MTR | [5 empty] | 34 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | 380 | #4DTR(B)(380) |  | E1 | 381E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.381E | 381E (非取樣點) | MTR | [5 empty] | 35 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 11 | 11kV | 100 | TIE(100) |  | E1 | 101E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.101E | 101E (非取樣點) | TIE | [5 empty] | 36 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 11 | 11kV | 100 | TIE(100) |  | E2 | 102E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.102E | 102E (非取樣點) | TIE | [5 empty] | 37 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 11 | 11kV | 100 | TIE(100) |  | D1 | 101(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.101 | 101 (非取樣點) | TIE | [5 empty] | 38 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | 100 | TIE(100) |  | D2 | 102(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.102 | 102 (非取樣點) | TIE | [5 empty] | 39 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | XO31 | 科十一線(XO31) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO31_DS | XO31_DS (非取樣點) | FEEDER | [5 empty] | 40 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | XO31 | 科十一線(XO31) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO31_ES | XO31_ES (非取樣點) | FEEDER | [5 empty] | 41 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 11 | 11kV | XO32 | 科十二線(XO32) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO32_DS | XO32_DS (非取樣點) | FEEDER | [5 empty] | 42 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | XO32 | 科十二線(XO32) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO32_ES | XO32_ES (非取樣點) | FEEDER | [5 empty] | 43 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 11 | 11kV | XO33 | 科十三線(XO33) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO33_DS | XO33_DS (非取樣點) | FEEDER | [5 empty] | 44 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | XO33 | 科十三線(XO33) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO33_ES | XO33_ES (非取樣點) | FEEDER | [5 empty] | 45 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 11 | 11kV | XO34 | 科十四線(XO34) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO34_DS | XO34_DS (非取樣點) | FEEDER | [5 empty] | 46 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | XO34 | 科十四線(XO34) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO34_ES | XO34_ES (非取樣點) | FEEDER | [5 empty] | 47 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 11 | 11kV | XO35 | 科十五線(XO35) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO35_DS | XO35_DS (非取樣點) | FEEDER | [5 empty] | 48 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | XO35 | 科十五線(XO35) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO35_ES | XO35_ES (非取樣點) | FEEDER | [5 empty] | 49 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 11 | 11kV | 230 | #3SC(230) |  | E1 | 231E(非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.231E | 231E (非取樣點) | SC | [5 empty] | 50 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 11 | 11kV | 230 | #3SC(230) |  | D1 | 231(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.231 | 231 (非取樣點) | SC | [5 empty] | 51 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | 200 | TIE(200) |  | E1 | 201E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.201E | 201E (非取樣點) | TIE | [5 empty] | 52 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 11 | 11kV | 200 | TIE(200) |  | E2 | 202E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.202E | 202E (非取樣點) | TIE | [5 empty] | 53 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 11 | 11kV | 200 | TIE(200) |  | D1 | 201(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.201 | 201 (非取樣點) | TIE | [5 empty] | 54 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | 200 | TIE(200) |  | D2 | 202(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.202 | 202 (非取樣點) | TIE | [5 empty] | 55 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | XO36 | 科十六線(XO36) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO36_DS | XO36_DS (非取樣點) | FEEDER | [5 empty] | 56 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | XO36 | 科十六線(XO36) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO36_ES | XO36_ES (非取樣點) | FEEDER | [5 empty] | 57 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 11 | 11kV | XO37 | 科十七線(XO37) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO37_DS | XO37_DS (非取樣點) | FEEDER | [5 empty] | 58 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | XO37 | 科十七線(XO37) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO37_ES | XO37_ES (非取樣點) | FEEDER | [5 empty] | 59 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 11 | 11kV | XO38 | 科十八線(XO38) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO38_DS | XO38_DS (非取樣點) | FEEDER | [5 empty] | 60 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | XO38 | 科十八線(XO38) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO38_ES | XO38_ES (非取樣點) | FEEDER | [5 empty] | 61 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 11 | 11kV | XO39 | 科十九線(XO39) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO39_DS | XO39_DS (非取樣點) | FEEDER | [5 empty] | 62 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | XO39 | 科十九線(XO39) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO39_ES | XO39_ES (非取樣點) | FEEDER | [5 empty] | 63 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 11 | 11kV | XO40 | 科二十線(XO40) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO40_DS | XO40_DS (非取樣點) | FEEDER | [5 empty] | 64 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | XO40 | 科二十線(XO40) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO40_ES | XO40_ES (非取樣點) | FEEDER | [5 empty] | 65 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 11 | 11kV | 240 | #4SC(240) |  | E1 | 241E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.241E | 241E (非取樣點) | SC | [5 empty] | 66 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 11 | 11kV | 240 | #4SC(240) |  | D1 | 241(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.241 | 241 (非取樣點) | SC | [5 empty] | 67 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | 250 | #5SC(250) |  | E1 | 251E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.251E | 251E (非取樣點) | SC | [5 empty] | 68 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 22 | 22kV | 250 | #5SC(250) |  | D1 | 251(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.251 | 251 (非取樣點) | SC | [5 empty] | 69 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO61 | 科六一線(XO61) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO61_DS | XO61_DS (非取樣點) | FEEDER | [5 empty] | 70 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO61 | 科六一線(XO61) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO61_ES | XO61_ES (非取樣點) | FEEDER | [5 empty] | 71 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 22 | 22kV | XO62 | 科六二線(XO62) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO62_DS | XO62_DS (非取樣點) | FEEDER | [5 empty] | 72 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO62 | 科六二線(XO62) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO62_ES | XO62_ES (非取樣點) | FEEDER | [5 empty] | 73 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 22 | 22kV | XO63 | 科六三線(XO63) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO63_DS | XO63_DS (非取樣點) | FEEDER | [5 empty] | 74 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO63 | 科六三線(XO63) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO63_ES | XO63_ES (非取樣點) | FEEDER | [5 empty] | 75 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 22 | 22kV | XO64 | 科六四線(XO64) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO64_DS | XO64_DS (非取樣點) | FEEDER | [5 empty] | 76 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO64 | 科六四線(XO64) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO64_ES | XO64_ES (非取樣點) | FEEDER | [5 empty] | 77 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 22 | 22kV | 260 | #6SC(260) |  | E1 | 261E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.261E | 261E (非取樣點) | SC | [5 empty] | 78 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 22 | 22kV | 260 | #6SC(260) |  | D1 | 261(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.261 | 261 (非取樣點) | SC | [5 empty] | 79 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO65 | 科六五線(XO65) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO65_DS | XO65_DS (非取樣點) | FEEDER | [5 empty] | 80 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO65 | 科六五線(XO65) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO65_ES | XO65_ES (非取樣點) | FEEDER | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 22 | 22kV | XO66 | 科六六線(XO66) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO66_DS | XO66_DS (非取樣點) | FEEDER | [5 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO66 | 科六六線(XO66) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO66_ES | XO66_ES (非取樣點) | FEEDER | [5 empty] | 83 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 22 | 22kV | XO67 | 科六七線(XO67) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO67_DS | XO67_DS (非取樣點) | FEEDER | [5 empty] | 84 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO67 | 科六七線(XO67) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO67_ES | XO67_ES (非取樣點) | FEEDER | [5 empty] | 85 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 22 | 22kV | XO68 | 科六八線(XO68) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO68_DS | XO68_DS (非取樣點) | FEEDER | [5 empty] | 86 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO68 | 科六八線(XO68) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO68_ES | XO68_ES (非取樣點) | FEEDER | [5 empty] | 87 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 22 | 22kV | 390 | #1SSTR(390) |  | D1 | 391(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.391 | 391 (非取樣點) | OTHER | [5 empty] | 88 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | 390 | #1SSTR(390) |  | E1 | 391E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.391E | 391E (非取樣點) | OTHER | [5 empty] | 89 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 22 | 22kV | 300 | TIE(300) |  | E1 | 301E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.301E | 301E (非取樣點) | TIE | [5 empty] | 90 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 22 | 22kV | 300 | TIE(300) |  | E2 | 302E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.302E | 302E (非取樣點) | TIE | [5 empty] | 91 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 22 | 22kV | 300 | TIE(300) |  | D1 | 301(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.301 | 301 (非取樣點) | TIE | [5 empty] | 92 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | 300 | TIE(300) |  | D2 | 302(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.302 | 302 (非取樣點) | TIE | [5 empty] | 93 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO71 | 科七一線(XO71) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO71_DS | XO71_DS (非取樣點) | FEEDER | [5 empty] | 94 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO71 | 科七一線(XO71) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO71_ES | XO71_ES (非取樣點) | FEEDER | [5 empty] | 95 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 22 | 22kV | XO72 | 科七二線(XO72) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO72_DS | XO72_DS (非取樣點) | FEEDER | [5 empty] | 96 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO72 | 科七二線(XO72) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO72_ES | XO72_ES (非取樣點) | FEEDER | [5 empty] | 97 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 22 | 22kV | XO73 | 科七三線(XO73) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO73_DS | XO73_DS (非取樣點) | FEEDER | [5 empty] | 98 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO73 | 科七三線(XO73) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO73_ES | XO73_ES (非取樣點) | FEEDER | [5 empty] | 99 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 22 | 22kV | XO74 | 科七四線(XO74) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO74_DS | XO74_DS (非取樣點) | FEEDER | [5 empty] | 100 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO74 | 科七四線(XO74) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO74_ES | XO74_ES (非取樣點) | FEEDER | [5 empty] | 101 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 22 | 22kV | 270 | #7SC(270) |  | E1 | 271E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.271E | 271E (非取樣點) | SC | [5 empty] | 102 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 22 | 22kV | 270 | #7SC(270) |  | D1 | 271(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.271 | 271 (非取樣點) | SC | [5 empty] | 103 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | 490 | #2SSTR(490) |  | D1 | 491(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.491 | 491 (非取樣點) | OTHER | [5 empty] | 104 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | 490 | #2SSTR(490) |  | E1 | 491E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.491E | 491E (非取樣點) | OTHER | [5 empty] | 105 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 22 | 22kV | 400 | TIE(400) |  | E1 | 401E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.401E | 401E (非取樣點) | TIE | [5 empty] | 106 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 22 | 22kV | 400 | TIE(400) |  | E2 | 402E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.402E | 402E (非取樣點) | TIE | [5 empty] | 107 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 22 | 22kV | 400 | TIE(400) |  | D1 | 401(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.401 | 401 (非取樣點) | TIE | [5 empty] | 108 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | 400 | TIE(400) |  | D2 | 402(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.402 | 402 (非取樣點) | TIE | [5 empty] | 109 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO75 | 科七五線(XO75) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO75_DS | XO75_DS (非取樣點) | FEEDER | [5 empty] | 110 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO75 | 科七五線(XO75) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO75_ES | XO75_ES (非取樣點) | FEEDER | [5 empty] | 111 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 22 | 22kV | XO76 | 科七六線(XO76) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO76_DS | XO76_DS (非取樣點) | FEEDER | [5 empty] | 112 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO76 | 科七六線(XO76) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO76_ES | XO76_ES (非取樣點) | FEEDER | [5 empty] | 113 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 22 | 22kV | XO77 | 科七七線(XO77) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO77_DS | XO77_DS (非取樣點) | FEEDER | [5 empty] | 114 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO77 | 科七七線(XO77) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO77_ES | XO77_ES (非取樣點) | FEEDER | [5 empty] | 115 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 22 | 22kV | XO78 | 科七八線(XO78) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO78_DS | XO78_DS (非取樣點) | FEEDER | [5 empty] | 116 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO78 | 科七八線(XO78) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D13_D1 | [8 empty] | 虎科DS.XO78_ES | XO78_ES (非取樣點) | FEEDER | [5 empty] | 117 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 22 | 22kV | 280 | #8SC(280) |  | E1 | 281E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.281E | 281E (非取樣點) | SC | [5 empty] | 118 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 22 | 22kV | 280 | #8SC(280) |  | D1 | 281(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D13_A1 | [8 empty] | 虎科DS.281 | 281 (非取樣點) | SC | [5 empty] | 119 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | 15B1E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aalz | B2/D13_A1 | [8 empty] | 虎科DS.15B1E | 15B1E (非取樣點) | BUS | [5 empty] | 120 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | 15B2E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/2Bus | [13 empty] | aalz | B2/D13_A1 | [8 empty] | 虎科DS.15B2E | 15B2E (非取樣點) | BUS | [5 empty] | 121 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D13 | 虎科DS |  |  | 2DTR(A) | #2DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0000 |  | 0002 | 1-80 |  | 1-02 | M2 | ------ | #2 DTR ULTC TAP-A指示量 t=-8~+8 | TAP_-8.5_8.5(0_2000) |  | B1/D13_A1 | [8 empty] | 虎科DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | [5 empty] | 122 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D13 | 虎科DS |  |  | 2DTR(B) | #2DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0001 |  | 0004 | 1-81 |  | 1-04 | M2 | ------ | #2 DTR ULTC TAP-B指示量 t=-8~+8 | TAP_-8.5_8.5(0_2000) |  | B1/D13_A1 | [8 empty] | 虎科DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | [5 empty] | 123 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D13 | 虎科DS |  |  | 2DTR(A) | #2DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0002 |  |  | 1-82 |  |  | M2 | ℃ | #2A DTR 線溫指示量 0~120℃ | COIL_-120_120(-2000_2000) |  | B1/D13_A1 | [8 empty] | 虎科DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | [5 empty] | 124 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D13 | 虎科DS |  |  | 2DTR(B) | #2DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0003 |  |  | 1-83 |  |  | M2 | ℃ | #2B DTR 線溫指示量 0~120℃ | COIL_-120_120(-2000_2000) |  | B1/D13_A1 | [8 empty] | 虎科DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | [5 empty] | 125 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D13 | 虎科DS |  |  | 2DTR | #2DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | M2 | ℃ | #2 DTR 油溫指示量 0~120℃ | OIL_-120_120(-2000_2000) |  | B1/D13_A1 | [8 empty] | 虎科DS.#2DTR_OIL | #2DTR 油溫 | MTR | [5 empty] | 126 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D13 | 虎科DS |  |  | 3DTR | #3DTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0005 |  | 0006 | 1-85 |  | 1-06 | M3 | ------ | #3 DTR ULTC TAP指示量 t=-8~+8 | TAP_-8.5_8.5(0_2000) |  | B1/D13_A1 | [8 empty] | 虎科DS.#3DTR_TAP | #3DTR OLTC TAP | MTR | [5 empty] | 127 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D13 | 虎科DS |  |  | 3DTR | #3DTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | M3 | ℃ | #3 DTR 線溫指示量 0~120℃ | COIL_-120_120(-2000_2000) |  | B1/D13_A1 | [8 empty] | 虎科DS.#3DTR_COIL | #3DTR 線溫 | MTR | [5 empty] | 128 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D13 | 虎科DS |  |  | 3DTR | #3DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | M3 | ℃ | #3 DTR 油溫指示量 0~120℃ | OIL_-120_120(-2000_2000) |  | B1/D13_A1 | [8 empty] | 虎科DS.#3DTR_OIL | #3DTR 油溫 | MTR | [5 empty] | 129 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D13 | 虎科DS |  |  | 4DTR | #4DTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0008 |  | 0008 | 1-88 |  | 1-08 | M4 | ------ | #4 DTR ULTC TAP指示量 t=-8~+8 | TAP_-8.5_8.5(0_2000) |  | B1/D13_A1 | [8 empty] | 虎科DS.#4DTR_TAP | #4DTR OLTC TAP | MTR | [5 empty] | 130 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D13 | 虎科DS |  |  | 4DTR | #4DTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | M4 | ℃ | #4 DTR 線溫指示量 0~120℃ | COIL_-120_120(-2000_2000) |  | B1/D13_A1 | [8 empty] | 虎科DS.#4DTR_COIL | #4DTR 線溫 | MTR | [5 empty] | 131 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D13 | 虎科DS |  |  | 4DTR | #4DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | M4 | ℃ | #4 DTR 油溫指示量 0~120℃ | OIL_-120_120(-2000_2000) |  | B1/D13_A1 | [8 empty] | 虎科DS.#4DTR_OIL | #4DTR 油溫 | MTR | [5 empty] | 132 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D13 | 虎科DS | 161 | 161kV | 1570 | 虎科～虎菁一路(1570) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | ------ | ------ | 1570 虎科虎菁一路瓦量 0~±2000MW | MW_-560_560(-2000_2000) |  | B2/D13_A1 | [8 empty] | 虎科DS.1570_MW | 虎科虎菁一路 MW | LINE161 | [5 empty] | 133 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D13 | 虎科DS | 161 | 161kV | 1570 | 虎科～虎菁一路(1570) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0012 |  |  | 1-8C |  |  | ------ | ------ | 1570 虎科虎菁一路乏量0~±2000MVAR | MVAR_-560_560(-2000_2000) |  | B2/D13_A1 | [8 empty] | 虎科DS.1570_MVAR | 虎科虎菁一路 MVAR | LINE161 | [5 empty] | 134 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D13 | 虎科DS | 161 | 161kV | 1580 | 虎科～虎菁二路(1580) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0013 |  |  | 1-8D |  |  | ------ | ------ | 1580 虎科虎菁二路瓦量 0~±2000MKW | MW_-560_560(-2000_2000) |  | B2/D13_A1 | [8 empty] | 虎科DS.1580_MW | 虎科虎菁二路 MW | LINE161 | [5 empty] | 135 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D13 | 虎科DS | 161 | 161kV | 1580 | 虎科～虎菁二路(1580) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0014 |  |  | 1-8E |  |  | ------ | ------ | 1580 虎科虎菁二路乏量 0~±2000MKVAR | MVAR_-560_560(-2000_2000) |  | B2/D13_A1 | [8 empty] | 虎科DS.1580_MVAR | 虎科虎菁二路 MVAR | LINE161 | [5 empty] | 136 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0015 |  |  | 1-8F |  |  | ------ | ------ | 1610 虎科和鑫一路瓦量 0~±2000MW | MW_-560_560(-2000_2000) |  | B2/D13_A1 | [8 empty] | 虎科DS.1610_MW | 虎科和鑫一路 MW | LINE161 | [5 empty] | 137 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0016 |  |  | 1-90 |  |  | ------ | ------ | 1610 虎科和鑫一路乏量0~±2000MVAR | MVAR_-560_560(-2000_2000) |  | B2/D13_A1 | [8 empty] | 虎科DS.1610_MVAR | 虎科和鑫一路 MVAR | LINE161 | [5 empty] | 138 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0017 |  |  | 1-91 |  |  | ------ | ------ | 1620 虎科和鑫二路瓦量 0~±2000MKW | MW_-560_560(-2000_2000) |  | B2/D13_A1 | [8 empty] | 虎科DS.1620_MW | 虎科和鑫二路 MW | LINE161 | [5 empty] | 139 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | ------ | ------ | 1620 虎科和鑫二路乏量 0~±2000MKVAR | MVAR_-560_560(-2000_2000) |  | B2/D13_A1 | [8 empty] | 虎科DS.1620_MVAR | 虎科和鑫二路 MVAR | LINE161 | [5 empty] | 140 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D13 | 虎科DS | 161 | 161kV | 1630 | 越港虎科紅線(1630) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | ------ | ------ | 1630 越港虎科紅線瓦量 0~±2000MW | MW_-560_560(-2000_2000) |  | B2/D13_A1 | [8 empty] | 虎科DS.1630_MW | 越港虎科紅線 MW | LINE161 | [5 empty] | 141 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D13 | 虎科DS | 161 | 161kV | 1630 | 越港虎科紅線(1630) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | ------ | ------ | 1630 越港虎科紅線乏量0~±2000MVAR | MVAR_-560_560(-2000_2000) |  | B2/D13_A1 | [8 empty] | 虎科DS.1630_MVAR | 越港虎科紅線 MVAR | LINE161 | [5 empty] | 142 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D13 | 虎科DS | 161 | 161kV | 1640 | 越港虎科白線(1640) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | ------ | ------ | 1640 越港虎科白線瓦量 0~±2000MKW | MW_-560_560(-2000_2000) |  | B2/D13_A1 | [8 empty] | 虎科DS.1640_MW | 越港虎科白線 MW | LINE161 | [5 empty] | 143 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D13 | 虎科DS | 161 | 161kV | 1640 | 越港虎科白線(1640) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | ------ | ------ | 1640 越港虎科白線乏量 0~±2000MKVAR | MVAR_-560_560(-2000_2000) |  | B2/D13_A1 | [8 empty] | 虎科DS.1640_MVAR | 越港虎科白線 MVAR | LINE161 | [5 empty] | 144 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D13 | 虎科DS | 161 | 161kV | 1570 | 虎科～虎菁一路(1570) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | ------ | ------ | 1570 虎科虎菁一路 線電壓 | kV_-210_210(-2000_2000) |  | B2/D13_A1 | [8 empty] | 虎科DS.1570LPD_KV | 虎科虎菁一路(1570) LPD KV | LINE161 | [5 empty] | 145 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D13 | 虎科DS | 161 | 161kV | 1580 | 虎科～虎菁二路(1580) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | ------ | ------ | 1580 虎科虎菁二路 線電壓 | kV_-210_210(-2000_2000) |  | B2/D13_A1 | [8 empty] | 虎科DS.1580LPD_KV | 虎科虎菁二路(1580) LPD KV | LINE161 | [5 empty] | 146 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | ------ | ------ | 1610 虎科和鑫一路 線電壓 | kV_-210_210(-2000_2000) |  | B2/D13_A1 | [8 empty] | 虎科DS.1610LPD_KV | 虎科和鑫一路(1610) LPD KV | LINE161 | [5 empty] | 147 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | ------ | ------ | 1620 虎科和鑫二路 線電壓 | kV_-210_210(-2000_2000) |  | B2/D13_A1 | [8 empty] | 虎科DS.1620LPD_KV | 虎科和鑫二路(1620) LPD KV | LINE161 | [5 empty] | 148 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D13 | 虎科DS | 161 | 161kV | 1630 | 越港虎科紅線(1630) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | ------ | ------ | 1630 越港虎科紅線 線電壓 | kV_-210_210(-2000_2000) |  | B2/D13_A1 | [8 empty] | 虎科DS.1630LPD_KV | 越港虎科紅線(1630) LPD KV | LINE161 | [5 empty] | 149 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D13 | 虎科DS | 161 | 161kV | 1640 | 越港虎科白線(1640) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | ------ | ------ | 1640 越港虎科白線 線電壓 | kV_-210_210(-2000_2000) |  | B2/D13_A1 | [8 empty] | 虎科DS.1640LPD_KV | 越港虎科白線(1640) LPD KV | LINE161 | [5 empty] | 150 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D13 | 虎科DS | 161 | 161kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0041 |  |  | 1-A9 |  |  | 161KV #1B BUS | KV | 161KV #1 BUS電壓量 | kV_-210_210(-2000_2000) | aaa | B2/D13_A1 | [8 empty] | 虎科DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | [5 empty] | 151 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D13 | 虎科DS | 161 | 161kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0042 |  |  | 1-AA |  |  | 161KV #2B BUS | KV | 161KV #2 BUS電壓量 | kV_-210_210(-2000_2000) | aab | B2/D13_A1 | [8 empty] | 虎科DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | [5 empty] | 152 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D13 | 虎科DS | 161 | 161kV | 1500 | TIE(1500) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | 1500 TIE | A | 1500 TIE R相電流量 | A_-2000_2000(-2000_2000) |  | B2/D13_A1 | [8 empty] | 虎科DS.1500TIE_AMP | 1500TIE AMP | TIE | [5 empty] | 153 |  |  |  |  | AI | [5 empty] | C20R1600 | 1520 | 1600 | 1760 | 1968 | 2.27 | -1520 | -1600 | -1760 | -1968 | 1 | 0.01 | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 2ABUS | #2ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0044 |  |  | 1-AC |  |  | 23KV #2A BUS | KV | 11KV #2A BUS電壓量 | kV_-9_9(-2000_2000) | aaa | B3/D13_A1 | [8 empty] | 虎科DS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS | [5 empty] | 154 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D13 | 虎科DS | 11 | 11kV | 2BBUS | #2BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0045 |  |  | 1-AD |  |  | 23KV #2B BUS | KV | 11KV #2B BUS電壓量 | kV_-9_9(-2000_2000) | baa | B3/D13_A1 | [8 empty] | 虎科DS.11KV#2BBUS_KV | 11KV #2BBUS KV | BUS | [5 empty] | 155 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D13 | 虎科DS | 22 | 22kV | 3ABUS | #3ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0046 |  |  | 1-AE |  |  | 23KV #3A BUS | KV | 23KV #3A BUS電壓量 | kV_-18_18(-2000_2000) | aba | B3/D13_A1 | [8 empty] | 虎科DS.23KV#3ABUS_KV | 23KV #3ABUS KV | BUS | [5 empty] | 156 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D13 | 虎科DS | 22 | 22kV | 3BBUS | #3BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0047 |  |  | 1-AF |  |  | 23KV #3B BUS | KV | 23KV #3B BUS電壓量 | kV_-18_18(-2000_2000) | aca | B3/D13_A1 | [8 empty] | 虎科DS.23KV#3BBUS_KV | 23KV #3BBUS KV | BUS | [5 empty] | 157 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D13 | 虎科DS | 22 | 22kV | 4ABUS | #4ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0048 |  |  | 1-B0 |  |  | 23KV #4A BUS | KV | 23KV #4A BUS電壓量 | kV_-18_18(-2000_2000) | bba | B3/D13_A1 | [8 empty] | 虎科DS.23KV#4ABUS_KV | 23KV #4ABUS KV | BUS | [5 empty] | 158 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D13 | 虎科DS | 22 | 22kV | 4BBUS | #4BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0049 |  |  | 1-B1 |  |  | 23KV #4B BUS | KV | 23KV #4B BUS電壓量 | kV_-18_18(-2000_2000) | bca | B3/D13_A1 | [8 empty] | 虎科DS.23KV#4BBUS_KV | 23KV #4BBUS KV | BUS | [5 empty] | 159 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D13 | 虎科DS | 161 | 161kV | 1960 | #2SHR(1960) |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | M6 | ℃ | 161kV #2 SHR 油溫 | OIL_-120_120(-2000_2000) | [10 empty] | 虎科DS.161#2SHR_OIL | 161KV #2SHR 油溫 | OTHER | [5 empty] | 160 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D13 | 虎科DS | 161 | 161kV | 1960 | #2SHR(1960) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | M6 | ℃ | 161kV #2 SHR 線溫 | COIL_-120_120(-2000_2000) | [10 empty] | 虎科DS.161#2SHR_COIL | 161KV #2SHR 線溫 | OTHER | [5 empty] | 161 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D13 | 虎科DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | 330 | KW | 330 瓦量 | MW_-36_36(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | [5 empty] | 162 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.036 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.036000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | 330 | KVAR | 330 乏量 | MVAR_-24_24(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | [5 empty] | 163 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.024 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.024000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | 330 | A | 330 R相電流量 | A_-2000_2000(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | [5 empty] | 164 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | 330 | A | 330 S相電流量 | A_-2000_2000(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | [5 empty] | 165 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | 330 | A | 330 T相電流量 | A_-2000_2000(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | [5 empty] | 166 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 100 | TIE(100) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | 100 | A | 100 R相電流量 | A_-2000_2000(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.11KV_100_A1 | 11KV 100 R相AMP | TIE | [5 empty] | 167 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 100 | TIE(100) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | 100 | A | 100 S相電流量 | A_-2000_2000(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.11KV_100_A2 | 11KV 100 S相AMP | TIE | [5 empty] | 168 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 100 | TIE(100) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | 100 | A | 100 T相電流量 | A_-2000_2000(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.11KV_100_A3 | 11KV 100 T相AMP | TIE | [5 empty] | 169 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO31 | 科十一線(XO31) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0060 |  |  | 1-BC |  |  | XO31 | KVAR | XO31 乏量 | KVAR_-9000_9000(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科11線KVAR | 11KV科11線 KVAR | FEEDER | [5 empty] | 170 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO31 | 科十一線(XO31) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | XO31 | A | XO31 R相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科11線A1 | 11KV科11線 R相AMP | FEEDER | [5 empty] | 171 |  |  |  |  | AI | [5 empty] | C05R450R | 405 | 406 | 450 | 500 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO31 | 科十一線(XO31) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | XO31 | A | XO31 S相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科11線A2 | 11KV科11線 S相AMP | FEEDER | [5 empty] | 172 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO31 | 科十一線(XO31) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0063 |  |  | 1-BF |  |  | XO31 | A | XO31 T相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科11線A3 | 11KV科11線 T相AMP | FEEDER | [5 empty] | 173 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO31 | 科十一線(XO31) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | XO31 | A | XO31 N相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科11線A0 | 11KV科11線 N相AMP | FEEDER | [5 empty] | 174 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO32 | 科十二線(XO32) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | XO32 | KVAR | XO32 乏量 | KVAR_-9000_9000(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科12線KVAR | 11KV科12線 KVAR | FEEDER | [5 empty] | 175 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO32 | 科十二線(XO32) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | XO32 | A | XO32 R相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科12線A1 | 11KV科12線 R相AMP | FEEDER | [5 empty] | 176 |  |  |  |  | AI | [5 empty] | C05R450R | 405 | 406 | 450 | 500 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO32 | 科十二線(XO32) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | XO32 | A | XO32 S相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科12線A2 | 11KV科12線 S相AMP | FEEDER | [5 empty] | 177 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO32 | 科十二線(XO32) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | XO32 | A | XO32 T相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科12線A3 | 11KV科12線 T相AMP | FEEDER | [5 empty] | 178 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO32 | 科十二線(XO32) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | XO32 | A | XO32 N相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科12線A0 | 11KV科12線 N相AMP | FEEDER | [5 empty] | 179 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO33 | 科十三線(XO33) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | XO33 | KVAR | XO33 乏量 | KVAR_-9000_9000(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科13線KVAR | 11KV科13線 KVAR | FEEDER | [5 empty] | 180 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO33 | 科十三線(XO33) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | XO33 | A | XO33 R相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科13線A1 | 11KV科13線 R相AMP | FEEDER | [5 empty] | 181 |  |  |  |  | AI | [5 empty] | C05R450R | 405 | 406 | 450 | 500 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO33 | 科十三線(XO33) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | XO33 | A | XO33 S相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科13線A2 | 11KV科13線 S相AMP | FEEDER | [5 empty] | 182 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO33 | 科十三線(XO33) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | XO33 | A | XO33 T相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科13線A3 | 11KV科13線 T相AMP | FEEDER | [5 empty] | 183 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO33 | 科十三線(XO33) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | XO33 | A | XO33 N相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科13線A0 | 11KV科13線 N相AMP | FEEDER | [5 empty] | 184 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO34 | 科十四線(XO34) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | XO34 | KVAR | XO34 乏量 | KVAR_-9000_9000(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科14線KVAR | 11KV科14線 KVAR | FEEDER | [5 empty] | 185 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO34 | 科十四線(XO34) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | XO34 | A | XO34 R相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科14線A1 | 11KV科14線 R相AMP | FEEDER | [5 empty] | 186 |  |  |  |  | AI | [5 empty] | C05R450R | 405 | 406 | 450 | 500 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO34 | 科十四線(XO34) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | XO34 | A | XO34 S相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科14線A2 | 11KV科14線 S相AMP | FEEDER | [5 empty] | 187 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO34 | 科十四線(XO34) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | XO34 | A | XO34 T相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科14線A3 | 11KV科14線 T相AMP | FEEDER | [5 empty] | 188 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO34 | 科十四線(XO34) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | XO34 | A | XO34 N相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科14線A0 | 11KV科14線 N相AMP | FEEDER | [5 empty] | 189 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO35 | 科十五線(XO35) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | XO35 | KVAR | XO35 乏量 | KVAR_-9000_9000(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科15線KVAR | 11KV科15線 KVAR | FEEDER | [5 empty] | 190 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO35 | 科十五線(XO35) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | XO35 | A | XO35 R相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科15線A1 | 11KV科15線 R相AMP | FEEDER | [5 empty] | 191 |  |  |  |  | AI | [5 empty] | C05R450R | 405 | 406 | 450 | 500 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO35 | 科十五線(XO35) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | XO35 | A | XO35 S相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科15線A2 | 11KV科15線 S相AMP | FEEDER | [5 empty] | 192 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO35 | 科十五線(XO35) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | XO35 | A | XO35 T相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科15線A3 | 11KV科15線 T相AMP | FEEDER | [5 empty] | 193 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO35 | 科十五線(XO35) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | XO35 | A | XO35 N相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科15線A0 | 11KV科15線 N相AMP | FEEDER | [5 empty] | 194 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | 340 | KW | 340 瓦量 | MW_-36_36(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | [5 empty] | 195 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.036 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.036000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | 340 | KVAR | 340 乏量 | MVAR_-24_24(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | [5 empty] | 196 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.024 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.024000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | 340 | A | 340 R相電流量 | A_-2000_2000(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | [5 empty] | 197 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | 340 | A | 340 S相電流量 | A_-2000_2000(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | [5 empty] | 198 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | 340 | A | 340 T相電流量 | A_-2000_2000(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | [5 empty] | 199 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 200 | TIE(200) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | 200 | A | 200 R相電流量 | A_-2000_2000(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.11KV_200_A1 | 11KV 200 R相AMP | TIE | [5 empty] | 200 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 200 | TIE(200) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | 200 | A | 200 S相電流量 | A_-2000_2000(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.11KV_200_A2 | 11KV 200 S相AMP | TIE | [5 empty] | 201 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 200 | TIE(200) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | 200 | A | 200 T相電流量 | A_-2000_2000(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.11KV_200_A3 | 11KV 200 T相AMP | TIE | [5 empty] | 202 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO36 | 科十六線(XO36) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | XO36 | KVAR | XO36 乏量 | KVAR_-9000_9000(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科16線KVAR | 11KV科16線 KVAR | FEEDER | [5 empty] | 203 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO36 | 科十六線(XO36) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | XO36 | A | XO36 R相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科16線A1 | 11KV科16線 R相AMP | FEEDER | [5 empty] | 204 |  |  |  |  | AI | [5 empty] | C05R450R | 405 | 406 | 450 | 500 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO36 | 科十六線(XO36) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | XO36 | A | XO36 S相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科16線A2 | 11KV科16線 S相AMP | FEEDER | [5 empty] | 205 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO36 | 科十六線(XO36) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | XO36 | A | XO36 T相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科16線A3 | 11KV科16線 T相AMP | FEEDER | [5 empty] | 206 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO36 | 科十六線(XO36) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | XO36 | A | XO36 N相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科16線A0 | 11KV科16線 N相AMP | FEEDER | [5 empty] | 207 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO37 | 科十七線(XO37) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0098 |  |  | 1-E2 |  |  | XO37 | KVAR | XO37 乏量 | KVAR_-9000_9000(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科17線KVAR | 11KV科17線 KVAR | FEEDER | [5 empty] | 208 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO37 | 科十七線(XO37) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | XO37 | A | XO37 R相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科17線A1 | 11KV科17線 R相AMP | FEEDER | [5 empty] | 209 |  |  |  |  | AI | [5 empty] | C05R450R | 405 | 406 | 450 | 500 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO37 | 科十七線(XO37) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | XO37 | A | XO37 S相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科17線A2 | 11KV科17線 S相AMP | FEEDER | [5 empty] | 210 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO37 | 科十七線(XO37) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0101 |  |  | 1-E5 |  |  | XO37 | A | XO37 T相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科17線A3 | 11KV科17線 T相AMP | FEEDER | [5 empty] | 211 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO37 | 科十七線(XO37) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | XO37 | A | XO37 N相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科17線A0 | 11KV科17線 N相AMP | FEEDER | [5 empty] | 212 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO38 | 科十八線(XO38) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | XO38 | KVAR | XO38 乏量 | KVAR_-9000_9000(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科18線KVAR | 11KV科18線 KVAR | FEEDER | [5 empty] | 213 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO38 | 科十八線(XO38) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | XO38 | A | XO38 R相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科18線A1 | 11KV科18線 R相AMP | FEEDER | [5 empty] | 214 |  |  |  |  | AI | [5 empty] | C05R450R | 405 | 406 | 450 | 500 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO38 | 科十八線(XO38) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | XO38 | A | XO38 S相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科18線A2 | 11KV科18線 S相AMP | FEEDER | [5 empty] | 215 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO38 | 科十八線(XO38) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | XO38 | A | XO38 T相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科18線A3 | 11KV科18線 T相AMP | FEEDER | [5 empty] | 216 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO38 | 科十八線(XO38) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | XO38 | A | XO38 N相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科18線A0 | 11KV科18線 N相AMP | FEEDER | [5 empty] | 217 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO39 | 科十九線(XO39) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | XO39 | KVAR | XO39 乏量 | KVAR_-9000_9000(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科19線KVAR | 11KV科19線 KVAR | FEEDER | [5 empty] | 218 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO39 | 科十九線(XO39) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | XO39 | A | XO39 R相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科19線A1 | 11KV科19線 R相AMP | FEEDER | [5 empty] | 219 |  |  |  |  | AI | [5 empty] | C05R450R | 405 | 406 | 450 | 500 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO39 | 科十九線(XO39) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | XO39 | A | XO39 S相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科19線A2 | 11KV科19線 S相AMP | FEEDER | [5 empty] | 220 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO39 | 科十九線(XO39) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | XO39 | A | XO39 T相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科19線A3 | 11KV科19線 T相AMP | FEEDER | [5 empty] | 221 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO39 | 科十九線(XO39) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | XO39 | A | XO39 N相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科19線A0 | 11KV科19線 N相AMP | FEEDER | [5 empty] | 222 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO40 | 科二十線(XO40) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | XO40 | KVAR | XO40 乏量 | KVAR_-9000_9000(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科20線KVAR | 11KV科20線 KVAR | FEEDER | [5 empty] | 223 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO40 | 科二十線(XO40) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | XO40 | A | XO40 R相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科20線A1 | 11KV科20線 R相AMP | FEEDER | [5 empty] | 224 |  |  |  |  | AI | [5 empty] | C05R450R | 405 | 406 | 450 | 500 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO40 | 科二十線(XO40) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | XO40 | A | XO40 S相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科20線A2 | 11KV科20線 S相AMP | FEEDER | [5 empty] | 225 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO40 | 科二十線(XO40) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | XO40 | A | XO40 T相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科20線A3 | 11KV科20線 T相AMP | FEEDER | [5 empty] | 226 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | XO40 | 科二十線(XO40) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | XO40 | A | XO40 N相電流量 | A_-500_500(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科20線A0 | 11KV科20線 N相AMP | FEEDER | [5 empty] | 227 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | 350 | KW | 350 瓦量 | MW_-72_72(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.#3DTR(A)_MW | #3DTR二次側(A) MW | MTR | [5 empty] | 228 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | 350 | KVAR | 350 乏量 | MVAR_-48_48(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.#3DTR(A)_MVAR | #3DTR二次側(A) MVAR | MTR | [5 empty] | 229 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.048 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.048000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | 350 | A | 350 R相電流量 | A_-2000_2000(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.#3DTR(A)_A1 | #3DTR二次側(A) R相AMP | MTR | [5 empty] | 230 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | 350 | A | 350 S相電流量 | A_-2000_2000(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.#3DTR(A)_A2 | #3DTR二次側(A) S相AMP | MTR | [5 empty] | 231 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | 350 | A | 350 T相電流量 | A_-2000_2000(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.#3DTR(A)_A3 | #3DTR二次側(A) T相AMP | MTR | [5 empty] | 232 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO61 | 科六一線(XO61) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | XO61 | KVAR | XO61 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科61線KVAR | 23KV科61線 KVAR | FEEDER | [5 empty] | 233 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO61 | 科六一線(XO61) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | XO61 | A | XO61 R相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科61線A1 | 23KV科61線 R相AMP | FEEDER | [5 empty] | 234 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO61 | 科六一線(XO61) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | XO61 | A | XO61 S相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科61線A2 | 23KV科61線 S相AMP | FEEDER | [5 empty] | 235 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO61 | 科六一線(XO61) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | XO61 | A | XO61 T相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科61線A3 | 23KV科61線 T相AMP | FEEDER | [5 empty] | 236 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO61 | 科六一線(XO61) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | XO61 | A | XO61 N相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科61線A0 | 23KV科61線 N相AMP | FEEDER | [5 empty] | 237 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO62 | 科六二線(XO62) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | XO62 | KVAR | XO62 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科62線KVAR | 23KV科62線 KVAR | FEEDER | [5 empty] | 238 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO62 | 科六二線(XO62) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | XO62 | A | XO62 R相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科62線A1 | 23KV科62線 R相AMP | FEEDER | [5 empty] | 239 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO62 | 科六二線(XO62) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | XO62 | A | XO62 S相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科62線A2 | 23KV科62線 S相AMP | FEEDER | [5 empty] | 240 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO62 | 科六二線(XO62) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | XO62 | A | XO62 T相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科62線A3 | 23KV科62線 T相AMP | FEEDER | [5 empty] | 241 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO62 | 科六二線(XO62) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | XO62 | A | XO62 N相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科62線A0 | 23KV科62線 N相AMP | FEEDER | [5 empty] | 242 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO63 | 科六三線(XO63) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0133 |  |  | 2-85 |  |  | XO63 | KVAR | XO63 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科63線KVAR | 23KV科63線 KVAR | FEEDER | [5 empty] | 243 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO63 | 科六三線(XO63) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | XO63 | A | XO63 R相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科63線A1 | 23KV科63線 R相AMP | FEEDER | [5 empty] | 244 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO63 | 科六三線(XO63) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0135 |  |  | 2-87 |  |  | XO63 | A | XO63 S相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科63線A2 | 23KV科63線 S相AMP | FEEDER | [5 empty] | 245 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO63 | 科六三線(XO63) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0136 |  |  | 2-88 |  |  | XO63 | A | XO63 T相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科63線A3 | 23KV科63線 T相AMP | FEEDER | [5 empty] | 246 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO63 | 科六三線(XO63) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0137 |  |  | 2-89 |  |  | XO63 | A | XO63 N相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科63線A0 | 23KV科63線 N相AMP | FEEDER | [5 empty] | 247 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO64 | 科六四線(XO64) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0138 |  |  | 2-8A |  |  | XO64 | KVAR | XO64 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科64線KVAR | 23KV科64線 KVAR | FEEDER | [5 empty] | 248 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO64 | 科六四線(XO64) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0139 |  |  | 2-8B |  |  | XO64 | A | XO64 R相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科64線A1 | 23KV科64線 R相AMP | FEEDER | [5 empty] | 249 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO64 | 科六四線(XO64) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0140 |  |  | 2-8C |  |  | XO64 | A | XO64 S相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科64線A2 | 23KV科64線 S相AMP | FEEDER | [5 empty] | 250 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO64 | 科六四線(XO64) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0141 |  |  | 2-8D |  |  | XO64 | A | XO64 T相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科64線A3 | 23KV科64線 T相AMP | FEEDER | [5 empty] | 251 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO64 | 科六四線(XO64) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0142 |  |  | 2-8E |  |  | XO64 | A | XO64 N相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科64線A0 | 23KV科64線 N相AMP | FEEDER | [5 empty] | 252 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0143 |  |  | 2-8F |  |  | 360 | KW | 360 瓦量 | MW_-72_72(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.#3DTR(B)_MW | #3DTR二次側(B) MW | MTR | [5 empty] | 253 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0144 |  |  | 2-90 |  |  | 360 | KVAR | 360 乏量 | MVAR_-48_48(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.#3DTR(B)_MVAR | #3DTR二次側(B) MVAR | MTR | [5 empty] | 254 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.048 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.048000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0145 |  |  | 2-91 |  |  | 360 | A | 360 R相電流量 | A_-2000_2000(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.#3DTR(B)_A1 | #3DTR二次側(B) R相AMP | MTR | [5 empty] | 255 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0146 |  |  | 2-92 |  |  | 360 | A | 360 S相電流量 | A_-2000_2000(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.#3DTR(B)_A2 | #3DTR二次側(B) S相AMP | MTR | [5 empty] | 256 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0147 |  |  | 2-93 |  |  | 360 | A | 360 T相電流量 | A_-2000_2000(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.#3DTR(B)_A3 | #3DTR二次側(B) T相AMP | MTR | [5 empty] | 257 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO65 | 科六五線(XO65) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0148 |  |  | 2-94 |  |  | XO65 | KVAR | XO65 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科65線KVAR | 23KV科65線 KVAR | FEEDER | [5 empty] | 258 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO65 | 科六五線(XO65) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0149 |  |  | 2-95 |  |  | XO65 | A | XO65 R相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科65線A1 | 23KV科65線 R相AMP | FEEDER | [5 empty] | 259 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO65 | 科六五線(XO65) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0150 |  |  | 2-96 |  |  | XO65 | A | XO65 S相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科65線A2 | 23KV科65線 S相AMP | FEEDER | [5 empty] | 260 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO65 | 科六五線(XO65) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0151 |  |  | 2-97 |  |  | XO65 | A | XO65 T相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科65線A3 | 23KV科65線 T相AMP | FEEDER | [5 empty] | 261 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO65 | 科六五線(XO65) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0152 |  |  | 2-98 |  |  | XO65 | A | XO65 N相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科65線A0 | 23KV科65線 N相AMP | FEEDER | [5 empty] | 262 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO66 | 科六六線(XO66) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0153 |  |  | 2-99 |  |  | XO66 | KVAR | XO66 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科66線KVAR | 23KV科66線 KVAR | FEEDER | [5 empty] | 263 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO66 | 科六六線(XO66) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0154 |  |  | 2-9A |  |  | XO66 | A | XO66 R相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科66線A1 | 23KV科66線 R相AMP | FEEDER | [5 empty] | 264 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO66 | 科六六線(XO66) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0155 |  |  | 2-9B |  |  | XO66 | A | XO66 S相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科66線A2 | 23KV科66線 S相AMP | FEEDER | [5 empty] | 265 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO66 | 科六六線(XO66) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0156 |  |  | 2-9C |  |  | XO66 | A | XO66 T相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科66線A3 | 23KV科66線 T相AMP | FEEDER | [5 empty] | 266 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO66 | 科六六線(XO66) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0157 |  |  | 2-9D |  |  | XO66 | A | XO66 N相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科66線A0 | 23KV科66線 N相AMP | FEEDER | [5 empty] | 267 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO67 | 科六七線(XO67) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0158 |  |  | 2-9E |  |  | XO67 | KVAR | XO67 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科67線KVAR | 23KV科67線 KVAR | FEEDER | [5 empty] | 268 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO67 | 科六七線(XO67) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0159 |  |  | 2-9F |  |  | XO67 | A | XO67 R相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科67線A1 | 23KV科67線 R相AMP | FEEDER | [5 empty] | 269 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO67 | 科六七線(XO67) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0160 |  |  | 2-A0 |  |  | XO67 | A | XO67 S相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科67線A2 | 23KV科67線 S相AMP | FEEDER | [5 empty] | 270 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO67 | 科六七線(XO67) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0161 |  |  | 2-A1 |  |  | XO67 | A | XO67 T相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科67線A3 | 23KV科67線 T相AMP | FEEDER | [5 empty] | 271 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO67 | 科六七線(XO67) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0162 |  |  | 2-A2 |  |  | XO67 | A | XO67 N相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科67線A0 | 23KV科67線 N相AMP | FEEDER | [5 empty] | 272 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO68 | 科六八線(XO68) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0163 |  |  | 2-A3 |  |  | XO68 | KVAR | XO68 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科68線KVAR | 23KV科68線 KVAR | FEEDER | [5 empty] | 273 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO68 | 科六八線(XO68) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0164 |  |  | 2-A4 |  |  | XO68 | A | XO68 R相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科68線A1 | 23KV科68線 R相AMP | FEEDER | [5 empty] | 274 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO68 | 科六八線(XO68) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0165 |  |  | 2-A5 |  |  | XO68 | A | XO68 S相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科68線A2 | 23KV科68線 S相AMP | FEEDER | [5 empty] | 275 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO68 | 科六八線(XO68) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0166 |  |  | 2-A6 |  |  | XO68 | A | XO68 T相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科68線A3 | 23KV科68線 T相AMP | FEEDER | [5 empty] | 276 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO68 | 科六八線(XO68) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0167 |  |  | 2-A7 |  |  | XO68 | A | XO68 N相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科68線A0 | 23KV科68線 N相AMP | FEEDER | [5 empty] | 277 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 370 | #4DTR(A)(370) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0168 |  |  | 2-A8 |  |  | 370 | KW | 370 瓦量 | MW_-72_72(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.#4DTR(A)_MW | #4DTR二次側(A) MW | MTR | [5 empty] | 278 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 370 | #4DTR(A)(370) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0169 |  |  | 2-A9 |  |  | 370 | KVAR | 370 乏量 | MVAR_-48_48(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.#4DTR(A)_MVAR | #4DTR二次側(A) MVAR | MTR | [5 empty] | 279 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.048 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.048000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 370 | #4DTR(A)(370) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0170 |  |  | 2-AA |  |  | 370 | A | 370 R相電流量 | A_-2000_2000(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.#4DTR(A)_A1 | #4DTR二次側(A) R相AMP | MTR | [5 empty] | 280 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 370 | #4DTR(A)(370) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0171 |  |  | 2-AB |  |  | 370 | A | 370 S相電流量 | A_-2000_2000(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.#4DTR(A)_A2 | #4DTR二次側(A) S相AMP | MTR | [5 empty] | 281 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 370 | #4DTR(A)(370) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0172 |  |  | 2-AC |  |  | 370 | A | 370 T相電流量 | A_-2000_2000(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.#4DTR(A)_A3 | #4DTR二次側(A) T相AMP | MTR | [5 empty] | 282 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO71 | 科七一線(XO71) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0173 |  |  | 2-AD |  |  | XO71 | KVAR | XO71 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科71線KVAR | 23KV科71線 KVAR | FEEDER | [5 empty] | 283 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO71 | 科七一線(XO71) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0174 |  |  | 2-AE |  |  | XO71 | A | XO71 R相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科71線A1 | 23KV科71線 R相AMP | FEEDER | [5 empty] | 284 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO71 | 科七一線(XO71) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0175 |  |  | 2-AF |  |  | XO71 | A | XO71 S相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科71線A2 | 23KV科71線 S相AMP | FEEDER | [5 empty] | 285 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO71 | 科七一線(XO71) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0176 |  |  | 2-B0 |  |  | XO71 | A | XO71 T相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科71線A3 | 23KV科71線 T相AMP | FEEDER | [5 empty] | 286 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO71 | 科七一線(XO71) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0177 |  |  | 2-B1 |  |  | XO71 | A | XO71 N相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科71線A0 | 23KV科71線 N相AMP | FEEDER | [5 empty] | 287 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO72 | 科七二線(XO72) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0178 |  |  | 2-B2 |  |  | XO72 | KVAR | XO72 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科72線KVAR | 23KV科72線 KVAR | FEEDER | [5 empty] | 288 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO72 | 科七二線(XO72) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0179 |  |  | 2-B3 |  |  | XO72 | A | XO72 R相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科72線A1 | 23KV科72線 R相AMP | FEEDER | [5 empty] | 289 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO72 | 科七二線(XO72) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0180 |  |  | 2-B4 |  |  | XO72 | A | XO72 S相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科72線A2 | 23KV科72線 S相AMP | FEEDER | [5 empty] | 290 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO72 | 科七二線(XO72) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0181 |  |  | 2-B5 |  |  | XO72 | A | XO72 T相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科72線A3 | 23KV科72線 T相AMP | FEEDER | [5 empty] | 291 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO72 | 科七二線(XO72) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0182 |  |  | 2-B6 |  |  | XO72 | A | XO72 N相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科72線A0 | 23KV科72線 N相AMP | FEEDER | [5 empty] | 292 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO73 | 科七三線(XO73) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0183 |  |  | 2-B7 |  |  | XO73 | KVAR | XO73 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科73線KVAR | 23KV科73線 KVAR | FEEDER | [5 empty] | 293 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO73 | 科七三線(XO73) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0184 |  |  | 2-B8 |  |  | XO73 | A | XO73 R相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科73線A1 | 23KV科73線 R相AMP | FEEDER | [5 empty] | 294 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO73 | 科七三線(XO73) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0185 |  |  | 2-B9 |  |  | XO73 | A | XO73 S相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科73線A2 | 23KV科73線 S相AMP | FEEDER | [5 empty] | 295 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO73 | 科七三線(XO73) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0186 |  |  | 2-BA |  |  | XO73 | A | XO73 T相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科73線A3 | 23KV科73線 T相AMP | FEEDER | [5 empty] | 296 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO73 | 科七三線(XO73) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0187 |  |  | 2-BB |  |  | XO73 | A | XO73 N相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科73線A0 | 23KV科73線 N相AMP | FEEDER | [5 empty] | 297 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO74 | 科七四線(XO74) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0188 |  |  | 2-BC |  |  | XO74 | KVAR | XO74 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科74線KVAR | 23KV科74線 KVAR | FEEDER | [5 empty] | 298 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO74 | 科七四線(XO74) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0189 |  |  | 2-BD |  |  | XO74 | A | XO74 R相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科74線A1 | 23KV科74線 R相AMP | FEEDER | [5 empty] | 299 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO74 | 科七四線(XO74) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0190 |  |  | 2-BE |  |  | XO74 | A | XO74 S相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科74線A2 | 23KV科74線 S相AMP | FEEDER | [5 empty] | 300 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO74 | 科七四線(XO74) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0191 |  |  | 2-BF |  |  | XO74 | A | XO74 T相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科74線A3 | 23KV科74線 T相AMP | FEEDER | [5 empty] | 301 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO74 | 科七四線(XO74) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0192 |  |  | 2-C0 |  |  | XO74 | A | XO74 N相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科74線A0 | 23KV科74線 N相AMP | FEEDER | [5 empty] | 302 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 380 | #4DTR(B)(380) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0193 |  |  | 2-C1 |  |  | 380 | KW | 380 瓦量 | MW_-72_72(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.#4DTR(B)_MW | #4DTR二次側(B) MW | MTR | [5 empty] | 303 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 380 | #4DTR(B)(380) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0194 |  |  | 2-C2 |  |  | 380 | KVAR | 380 乏量 | MVAR_-48_48(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.#4DTR(B)_MVAR | #4DTR二次側(B) MVAR | MTR | [5 empty] | 304 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.048 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.048000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 380 | #4DTR(B)(380) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0195 |  |  | 2-C3 |  |  | 380 | A | 380 R相電流量 | A_-2000_2000(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.#4DTR(B)_A1 | #4DTR二次側(B) R相AMP | MTR | [5 empty] | 305 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 380 | #4DTR(B)(380) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0196 |  |  | 2-C4 |  |  | 380 | A | 380 S相電流量 | A_-2000_2000(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.#4DTR(B)_A2 | #4DTR二次側(B) S相AMP | MTR | [5 empty] | 306 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 380 | #4DTR(B)(380) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0197 |  |  | 2-C5 |  |  | 380 | A | 380 T相電流量 | A_-2000_2000(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.#4DTR(B)_A3 | #4DTR二次側(B) T相AMP | MTR | [5 empty] | 307 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO75 | 科七五線(XO75) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0198 |  |  | 2-C6 |  |  | XO75 | KVAR | XO75 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科75線KVAR | 23KV科75線 KVAR | FEEDER | [5 empty] | 308 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO75 | 科七五線(XO75) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0199 |  |  | 2-C7 |  |  | XO75 | A | XO75 R相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科75線A1 | 23KV科75線 R相AMP | FEEDER | [5 empty] | 309 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO75 | 科七五線(XO75) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0200 |  |  | 2-C8 |  |  | XO75 | A | XO75 S相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科75線A2 | 23KV科75線 S相AMP | FEEDER | [5 empty] | 310 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO75 | 科七五線(XO75) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0201 |  |  | 2-C9 |  |  | XO75 | A | XO75 T相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科75線A3 | 23KV科75線 T相AMP | FEEDER | [5 empty] | 311 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO75 | 科七五線(XO75) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0202 |  |  | 2-CA |  |  | XO75 | A | XO75 N相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科75線A0 | 23KV科75線 N相AMP | FEEDER | [5 empty] | 312 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO76 | 科七六線(XO76) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0203 |  |  | 2-CB |  |  | XO76 | KVAR | XO76 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科76線KVAR | 23KV科76線 KVAR | FEEDER | [5 empty] | 313 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO76 | 科七六線(XO76) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0204 |  |  | 2-CC |  |  | XO72 | A | XO76 R相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科76線A1 | 23KV科76線 R相AMP | FEEDER | [5 empty] | 314 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO76 | 科七六線(XO76) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0205 |  |  | 2-CD |  |  | XO76 | A | XO76 S相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科76線A2 | 23KV科76線 S相AMP | FEEDER | [5 empty] | 315 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO76 | 科七六線(XO76) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0206 |  |  | 2-CE |  |  | XO76 | A | XO76 T相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科76線A3 | 23KV科76線 T相AMP | FEEDER | [5 empty] | 316 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO76 | 科七六線(XO76) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0207 |  |  | 2-CF |  |  | XO76 | A | XO76 N相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科76線A0 | 23KV科76線 N相AMP | FEEDER | [5 empty] | 317 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO77 | 科七七線(XO77) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0208 |  |  | 2-D0 |  |  | XO77 | KVAR | XO77 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科77線KVAR | 23KV科77線 KVAR | FEEDER | [5 empty] | 318 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO77 | 科七七線(XO77) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0209 |  |  | 2-D1 |  |  | XO77 | A | XO77 R相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科77線A1 | 23KV科77線 R相AMP | FEEDER | [5 empty] | 319 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO77 | 科七七線(XO77) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0210 |  |  | 2-D2 |  |  | XO77 | A | XO77 S相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科77線A2 | 23KV科77線 S相AMP | FEEDER | [5 empty] | 320 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO77 | 科七七線(XO77) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0211 |  |  | 2-D3 |  |  | XO77 | A | XO77 T相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科77線A3 | 23KV科77線 T相AMP | FEEDER | [5 empty] | 321 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO77 | 科七七線(XO77) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0212 |  |  | 2-D4 |  |  | XO77 | A | XO77 N相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科77線A0 | 23KV科77線 N相AMP | FEEDER | [5 empty] | 322 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO78 | 科七八線(XO78) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0213 |  |  | 2-D5 |  |  | XO78 | KVAR | XO78 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科78線KVAR | 23KV科78線 KVAR | FEEDER | [5 empty] | 323 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO78 | 科七八線(XO78) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0214 |  |  | 2-D6 |  |  | XO78 | A | XO78 R相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科78線A1 | 23KV科78線 R相AMP | FEEDER | [5 empty] | 324 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO78 | 科七八線(XO78) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0215 |  |  | 2-D7 |  |  | XO78 | A | XO78 S相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科78線A2 | 23KV科78線 S相AMP | FEEDER | [5 empty] | 325 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO78 | 科七八線(XO78) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0216 |  |  | 2-D8 |  |  | XO78 | A | XO78 T相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科78線A3 | 23KV科78線 T相AMP | FEEDER | [5 empty] | 326 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | XO78 | 科七八線(XO78) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0217 |  |  | 2-D9 |  |  | XO78 | A | XO78 N相電流量 | A_-600_600(-2000_2000) |  | B2/D13_D1 | [8 empty] | 虎科DS.科78線A0 | 23KV科78線 N相AMP | FEEDER | [5 empty] | 327 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 300 | TIE(300) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0218 |  |  | 2-DA |  |  | 300 | A | 300 R相電流量 | A_-2000_2000(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.23KV_300_A1 | 23KV 300 R相AMP | TIE | [5 empty] | 328 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 300 | TIE(300) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0219 |  |  | 2-DB |  |  | 300 | A | 300 S相電流量 | A_-2000_2000(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.23KV_300_A2 | 23KV 300 S相AMP | TIE | [5 empty] | 329 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 300 | TIE(300) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0220 |  |  | 2-DC |  |  | 300 | A | 300 T相電流量 | A_-2000_2000(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.23KV_300_A3 | 23KV 300 T相AMP | TIE | [5 empty] | 330 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 400 | TIE(400) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0221 |  |  | 2-DD |  |  | 400 | A | 400 R相電流量 | A_-2000_2000(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.23KV_400_A1 | 23KV 400 R相AMP | TIE | [5 empty] | 331 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 400 | TIE(400) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0222 |  |  | 2-DE |  |  | 400 | A | 400 S相電流量 | A_-2000_2000(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.23KV_400_A2 | 23KV 400 S相AMP | TIE | [5 empty] | 332 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 400 | TIE(400) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0223 |  |  | 2-DF |  |  | 400 | A | 400 T相電流量 | A_-2000_2000(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.23KV_400_A3 | 23KV 400 T相AMP | TIE | [5 empty] | 333 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 0 |  | StaDev | 所內設施 |  | DCV_P |  |  | MvMoment | 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0224 |  |  | 2-E0 |  |  | -------- | DCP | 直流P電源電壓 | kV_-150_150(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.直流P電源電壓 | 直流P電源電壓 | OTHER | [5 empty] | 334 |  |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 | 0.01 | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D13 | 虎科DS | 0 |  | StaDev | 所內設施 |  | DCV_N |  |  | MvMoment | 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0225 |  |  | 2-E1 |  |  | -------- | DCN | 直流N電源電壓 | kV_-150_150(-2000_2000) |  | B3/D13_A1 | [8 empty] | 虎科DS.直流N電源電壓 | 直流N電源電壓 | OTHER | [5 empty] | 335 |  |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 | 0.01 | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D13 | 虎科DS | 161 | 161kV | 1570 | 虎科～虎菁一路(1570) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0000 |  |  | 1-00-00 |  |  | R5 | L787A | 1570 虎科虎菁一路主保護(動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1570_87A | 虎科虎菁一路(1570) 87RY | LINE161 | [5 empty] | 336 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1570 | 虎科～虎菁一路(1570) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0001 |  |  | 1-00-01 |  |  | R5 | L7PHA | 1570 虎科虎菁一路相間電驛(動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1570_PHA | 虎科虎菁一路(1570) 相間RY | LINE161 | [5 empty] | 337 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1570 | 虎科～虎菁一路(1570) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0002 |  |  | 1-00-02 |  |  | R5 | L7GDA | 1570 虎科虎菁一路接地電驛(動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1570_GDA | 虎科虎菁一路(1570) 接地RY | LINE161 | [5 empty] | 338 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1580 | 虎科～虎菁二路(1580) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | R6 | L887A | 1580 虎科虎菁二路主保護(動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1580_87A | 虎科虎菁二路(1580) 87RY | LINE161 | [5 empty] | 339 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1580 | 虎科～虎菁二路(1580) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0004 |  |  | 1-00-04 |  |  | R6 | L8PHA | 1580 虎科虎菁二路相間電驛(動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1580_PHA | 虎科虎菁二路(1580) 相間RY | LINE161 | [5 empty] | 340 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1580 | 虎科～虎菁二路(1580) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0005 |  |  | 1-00-05 |  |  | R6 | L8GDA | 1580 虎科虎菁二路接地電驛(動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1580_GDA | 虎科虎菁二路(1580) 接地RY | LINE161 | [5 empty] | 341 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | R7 | L987A | 1610 虎科和鑫一路(第一套)主保護(動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1610_87A1 | 虎科和鑫一路(1610) #1 87RY | LINE161 | [5 empty] | 342 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-07 |  |  | R7 | L987A | 1610 虎科和鑫一路(第二套)主保護(動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1610_87A2 | 虎科和鑫一路(1610) #2 87RY | LINE161 | [5 empty] | 343 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-01-00 |  |  | R7 | L9PHA | 1610 虎科和鑫一路相間電驛(動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1610_PHA | 虎科和鑫一路(1610) 相間RY | LINE161 | [5 empty] | 344 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | R7 | L9GDA | 1610 虎科和鑫一路接地電驛(動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1610_GDA | 虎科和鑫一路(1610) 接地RY | LINE161 | [5 empty] | 345 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0010 |  |  | 1-01-02 |  |  | R8 | L1087A | 1620 虎科和鑫二路主保護(動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1620_87A1 | 虎科和鑫二路(1620) #1 87RY | LINE161 | [5 empty] | 346 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-03 |  |  | R8 | L1087A | 1620 虎科和鑫二路主保護(動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1620_87A2 | 虎科和鑫二路(1620) #2 87RY | LINE161 | [5 empty] | 347 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0012 |  |  | 1-01-04 |  |  | R8 | L10PHA | 1620 虎科和鑫二路相間電驛(動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1620_PHA | 虎科和鑫二路(1620) 相間RY | LINE161 | [5 empty] | 348 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0013 |  |  | 1-01-05 |  |  | R8 | L10GDA | 1620 虎科和鑫二路接地電驛(動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1620_GDA | 虎科和鑫二路(1620) 接地RY | LINE161 | [5 empty] | 349 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1630 | 越港虎科紅線(1630) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-06 |  |  | R9 | L1187A | 1630 越港虎科紅線主保護(動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1630_87A | 越港虎科紅線(1630) 87RY | LINE161 | [5 empty] | 350 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1630 | 越港虎科紅線(1630) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0015 |  |  | 1-01-07 |  |  | R9 | L11PHA | 1630 越港虎科紅線相間電驛(動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1630_PHA | 越港虎科紅線(1630) 相間RY | LINE161 | [5 empty] | 351 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1630 | 越港虎科紅線(1630) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-02-00 |  |  | R9 | L11GDA | 1630 越港虎科紅線接地電驛(動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1630_GDA | 越港虎科紅線(1630) 接地RY | LINE161 | [5 empty] | 352 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1640 | 越港虎科白線(1640) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0017 |  |  | 1-02-01 |  |  | R10 | L1287A | 1640 越港虎科白線主保護(動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1640_87A | 越港虎科白線(1640) 87RY | LINE161 | [5 empty] | 353 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1640 | 越港虎科白線(1640) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 |  |  | 1-02-02 |  |  | R10 | L12PHA | 1640 越港虎科白線相間電驛(動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1640_PHA | 越港虎科白線(1640) 相間RY | LINE161 | [5 empty] | 354 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1640 | 越港虎科白線(1640) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0019 |  |  | 1-02-03 |  |  | R10 | L12GDA | 1640 越港虎科白線接地電驛(動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1640_GDA | 越港虎科白線(1640) 接地RY | LINE161 | [5 empty] | 355 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS |  |  | 2DTR | #2DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | R1 | 287A | #2 DTR.差動電驛(動作/正常) |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#2DTR_87A | #2DTR 87RY | MTR | [5 empty] | 356 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS |  |  | 2DTR | #2DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0053 |  |  | 1-06-05 |  |  | R5 | 296PA | #2 DTR. 機械保護動作(動作/正常) |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | [5 empty] | 357 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS |  |  | 2DTR | #2DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0054 |  |  | 1-06-06 |  |  | R5 | 251ZA | #2 DTR.中性點接地電驛(動作/正常) |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | [5 empty] | 358 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS |  |  | 3DTR | #3DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0061 |  |  | 1-07-05 |  |  | R2 | 387A | #3 DTR.差動電驛(動作/正常) |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#3DTR_87A | #3DTR 87RY | MTR | [5 empty] | 359 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS |  |  | 3DTR | #3DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0062 |  |  | 1-07-06 |  |  | R6 | 396PA | #3 DTR. 機械保護動作(動作/正常) |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#3DTR_96PA | #3DTR 機械保護動作 | MTR | [5 empty] | 360 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS |  |  | 3DTR | #3DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0063 |  |  | 1-07-07 |  |  | R6 | 351ZA | #3 DTR.中性點接地電驛(動作/正常) |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#3DTR_51ZA | #3DTR 51Z RY | MTR | [5 empty] | 361 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS |  |  | 4DTR | #4DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0070 |  |  | 1-08-06 |  |  | R7 | 487A | #4 DTR.差動電驛(動作/正常) |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#4DTR_87A | #4DTR 87RY | MTR | [5 empty] | 362 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS |  |  | 4DTR | #4DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0071 |  |  | 1-08-07 |  |  | R7 | 496PA | #4 DTR. 機械保護動作(動作/正常) |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#4DTR_96PA | #4DTR 機械保護動作 | MTR | [5 empty] | 363 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS |  |  | 4DTR | #4DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0072 |  |  | 1-09-00 |  |  | R7 | 451ZA | #4 DTR.中性點接地電驛(動作/正常) |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#4DTR_51ZA | #4DTR 51Z RY | MTR | [5 empty] | 364 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0080 |  | 0029 | 1-0A-00 |  | 1-1D | R5 | 50A | 161KV TIE 瞬時電驛 (動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1500_50A | 161KV TIE(1500) 50RY | TIE | [5 empty] | 365 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0081 |  |  | 1-0A-01 |  |  | R5 | 87B1A | 161KV #1 BUS 電驛 (動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | [5 empty] | 366 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0082 |  |  | 1-0A-02 |  |  | R5 | 87B2A | 161KV #2 BUS 電驛 (動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | [5 empty] | 367 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0083 |  |  | 1-0A-03 |  |  | ------ | OSCA1 | OSC SYSTEM OPERATION ALARM |  |  | B3/D13_A1 | [8 empty] | 虎科DS.161KV_OSCA_1 | 161KV示波器啟動警報 | OTHER | [5 empty] | 368 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS |  |  | 2DTR | #2DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0084 |  |  | 1-0A-04 |  |  | ------ | 2PHA | #2 DTR PHA |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#2DTR_PHA | #2DTR 50/51 RY | OTHER | [5 empty] | 369 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS |  |  | 3DTR | #3DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0085 |  |  | 1-0A-05 |  |  | ------ | 3'PHA | #3 DTR PHA |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#3DTR_PHA | #3DTR 50/51 RY | OTHER | [5 empty] | 370 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS |  |  | 4DTR | #4DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0086 |  |  | 1-0A-06 |  |  | ------ | 4'PHA | #4 DTR PHA |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#4DTR_PHA | #4DTR 50/51 RY | OTHER | [5 empty] | 371 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS |  |  | 2DTR | #2DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0087 |  |  | 1-0A-07 |  |  | ------ | 2'GDA | #2 DTR GDA |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#2DTR_GDA | #2DTR 50N/51N RY | OTHER | [5 empty] | 372 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS |  |  | 3DTR | #3DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0088 |  |  | 1-0B-00 |  |  | ------ | 3'GDA | #3 DTR GDA |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#3DTR_GDA | #3DTR 50N/51N RY | OTHER | [5 empty] | 373 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS |  |  | 4DTR | #4DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0089 |  |  | 1-0B-01 |  |  | ------ | 4GDA | #4 DTR GDA |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#4DTR_GDA | #4DTR 50N/51N RY | OTHER | [5 empty] | 374 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1960 | #2SHR(1960) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | R/2SHR |  | 0090 |  | 0084 | 1-0B-02 |  | 1-54 | 1960 GIS LCC | 52AS | 1960 CB (ON/OFF) |  | aaab | B2/D13_A1 | [8 empty] | 虎科DS.1960_CB | 1960(161KV #2SHR) CB | OTHER | [5 empty] | 375 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1960 | #2SHR(1960) |  | 87A1 |  | B3 | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0091 |  |  | 1-0B-03 |  |  | R6 | 87R1A | 161kV #2 SH.R. 87R1A 第一套差動電驛 (動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.161#2SHR87A1 | 161KV #2SHR #1 87RY | OTHER | [5 empty] | 376 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1960 | #2SHR(1960) |  | 87A2 |  | B3 | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0092 |  |  | 1-0B-04 |  |  | R6 | 87R2A | 161kV #2 SH.R. 87R2A 第二套差動電驛 (動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.161#2SHR87A2 | 161KV #2SHR #2 87RY | OTHER | [5 empty] | 377 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1960 | #2SHR(1960) |  | 96PA |  | B3 | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0093 |  |  | 1-0B-05 |  |  | R6 | 96PA | 161kV #2 SH.R. 96PA 機械保護電驛 (動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.161#2SHR96PA | 161KV #2SHR 機械保護動作 | OTHER | [5 empty] | 378 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1960 | #2SHR(1960) |  | 86A |  | B3,Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0094 |  |  | 1-0B-06 |  |  | R6 | 86A | 161kV #2 SH.R. 86A 輔助閉鎖電驛 (動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.161#2SHR_86A | 161KV #2SHR 86RY | OTHER | [5 empty] | 379 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1960 | #2SHR(1960) |  | 51A |  | B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0095 |  |  | 1-0B-07 |  |  | R6 | 51A | 161kV #2 SH.R. 51A 延時過流警報 (動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.161#2SHR_51A | 161KV #2SHR 51RY | OTHER | [5 empty] | 380 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | ComPoint |  |  | 25TA |  |  | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0107 |  |  | 1-0D-03 |  |  | ------ | 25TA | 161KV GIS 25電驛超時警報 (COMMON) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | [5 empty] | 381 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0108 |  |  | 1-0D-04 |  |  | ------ | RCA | 161KV 復閉電驛(動作/正常)(COMMON) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | [5 empty] | 382 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1570 | 虎科～虎菁一路(1570) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D13D241/T1 |  | 0109 |  | 0054 | 1-0D-05 |  | 1-36 | GL7 | 52AS | 1570 CB (ON/OFF) |  | aaca | B2/D13_A1 | [8 empty] | 虎科DS.1570_CB | 1570(虎科虎菁一路) CB | LINE161 | [5 empty] | 383 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 161 | 161kV | 1580 | 虎科～虎菁二路(1580) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D13D242/T1 |  | 0110 |  | 0059 | 1-0D-06 |  | 1-3B | GL8 | 52AS | 1580 CB (ON/OFF) |  | aada | B2/D13_A1 | [8 empty] | 虎科DS.1580_CB | 1580(虎科虎菁二路) CB | LINE161 | [5 empty] | 384 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/備用線/T1 |  | 0111 |  | 0064 | 1-0D-07 |  | 1-40 | GT1 | 52AS | 1610 CB (ON/OFF) |  | aaga | B2/D13_A1 | [8 empty] | 虎科DS.1610_CB | 1610(虎科和鑫一路) CB | LINE161 | [5 empty] | 385 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/備用線/T1 |  | 0112 |  | 0069 | 1-0E-00 |  | 1-45 | GT2 | 52AS | 1620 CB (ON/OFF) |  | aaha | B2/D13_A1 | [8 empty] | 虎科DS.1620_CB | 1620(虎科和鑫二路) CB | LINE161 | [5 empty] | 386 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 161 | 161kV | 1630 | 越港虎科紅線(1630) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/備用線/T2 |  | 0113 |  | 0074 | 1-0E-01 |  | 1-4A | GB1 | 52AS | 1630 CB (ON/OFF) |  | aaja | B2/D13_A1 | [8 empty] | 虎科DS.1630_CB | 1630(越港虎科紅線) CB | LINE161 | [5 empty] | 387 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 161 | 161kV | 1640 | 越港虎科白線(1640) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/備用線/T2 |  | 0114 |  | 0079 | 1-0E-02 |  | 1-4F | 310 | 52AS | 1640 CB (ON/OFF) |  | aaka | B2/D13_A1 | [8 empty] | 虎科DS.1640_CB | 1640(越港虎科白線) CB | LINE161 | [5 empty] | 388 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2DTR |  | 0115 |  | 0114 | 1-0E-03 |  | 1-72 | 310 | 52AS | 1760CB (ON/OFF) |  | aabb | ELEM/D13_A1 | [8 empty] | 虎科DS.1760_CB | 1760(#2DTR) CB | MTR | [5 empty] | 389 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/3DTR |  | 0116 |  | 0117 | 1-0E-04 |  | 1-75 | 310 | 52AS | 1770 CB (ON/OFF) |  | aafb | ELEM/D13_A1 | [8 empty] | 虎科DS.1770_CB | 1770(#3DTR) CB | MTR | [5 empty] | 390 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 161 | 161kV | 1780 | #4DTR(1780) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/4DTR |  | 0117 |  | 0120 | 1-0E-05 |  | 1-78 | 320 | 52AS | 1780 CB (ON/OFF) |  | aaib | ELEM/D13_A1 | [8 empty] | 虎科DS.1780_CB | 1780(#4DTR) CB | MTR | [5 empty] | 391 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0118 |  | 0051 | 1-0E-06 |  | 1-33 | 320 | 52AS | 1500 CB (ON/OFF) |  | aaez | B2/D13_A1 | [8 empty] | 虎科DS.1500_CB | 1500(TIE) CB | TIE | [5 empty] | 392 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | T/2DTR(A) |  |  | 0119 |  | 0128 | 1-0E-07 |  | 2-00 | 330 | 52AS | 330 CB (ON/OFF) |  | aaia | ELEM/D13_A1 | [8 empty] | 虎科DS.330_CB | 330(#2DTR) CB | MTR | [5 empty] | 393 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0120 |  |  | 1-0F-00 |  |  | 330 | PHA | 330 相間電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.330_PHA2 | 330開關箱IED RY PHA | OTHER | [5 empty] | 394 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0121 |  |  | 1-0F-01 |  |  | 330 | GDA | 330 接地電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.330_GDA | 330開關箱IED RY GDA | OTHER | [5 empty] | 395 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | T/2DTR(B) |  |  | 0122 |  | 0146 | 1-0F-02 |  | 2-12 | 340 | 52AS | 340 CB (ON/OFF) |  | baia | ELEM/D13_A1 | [8 empty] | 虎科DS.340_CB | 340(#2DTR) CB | MTR | [5 empty] | 396 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0123 |  |  | 1-0F-03 |  |  | 340 | PHA | 340 相間電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.340_PHA2 | 340開關箱IED RY PHA | OTHER | [5 empty] | 397 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0124 |  |  | 1-0F-04 |  |  | 340 | GDA | 340 接地電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.340_GDA | 340開關箱IED RY GDA | OTHER | [5 empty] | 398 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3ABus | A/360^T/3DTR(A) |  |  | 0125 |  | 0163 | 1-0F-05 |  | 2-23 | 350 | 52AS | 350 CB (ON/OFF) |  | abaa | ELEM/D13_A1 | [8 empty] | 虎科DS.350_CB | 350(#3DTR) CB | MTR | [5 empty] | 399 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0126 |  |  | 1-0F-06 |  |  | 350 | PHA | 350 相間電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.350_PHA2 | 350開關箱IED RY PHA | OTHER | [5 empty] | 400 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0127 |  |  | 1-0F-07 |  |  | 350 | GDA | 350 接地電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.350_GDA | 350開關箱IED RY GDA | OTHER | [5 empty] | 401 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3BBus | A/350^T/3DTR(B) |  |  | 0128 |  | 0177 | 1-10-00 |  | 2-31 | 360 | 52AS | 360 CB (ON/OFF) |  | acaa | ELEM/D13_A1 | [8 empty] | 虎科DS.360_CB | 360(#3DTR) CB | MTR | [5 empty] | 402 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0129 |  |  | 1-10-01 |  |  | 360 | PHA | 360 相間電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.360_PHA2 | 360開關箱IED RY PHA | OTHER | [5 empty] | 403 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-10-02 |  |  | 360 | GDA | 360 接地電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.360_GDA | 360開關箱IED RY GDA | OTHER | [5 empty] | 404 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 370 | #4DTR(A)(370) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4ABus | A/380^T/4DTR(A) |  |  | 0131 |  | 0192 | 1-10-03 |  | 2-40 | 370 | 52AS | 370 CB (ON/OFF) |  | bbaa | ELEM/D13_A1 | [8 empty] | 虎科DS.370_CB | 370(#4DTR) CB | MTR | [5 empty] | 405 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | 370 | #4DTR(A)(370) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0132 |  |  | 1-10-04 |  |  | 370 | PHA | 370 相間電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.370_PHA2 | 370開關箱IED RY PHA | OTHER | [5 empty] | 406 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 370 | #4DTR(A)(370) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0133 |  |  | 1-10-05 |  |  | 370 | GDA | 370 接地電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.370_GDA | 370開關箱IED RY GDA | OTHER | [5 empty] | 407 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 380 | #4DTR(B)(380) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4BBus | A/370^T/4DTR(B) |  |  | 0134 |  | 0208 | 1-10-06 |  | 2-50 | 380 | 52AS | 380 CB (ON/OFF) |  | bcaa | ELEM/D13_A1 | [8 empty] | 虎科DS.380_CB | 380(#4DTR) CB | MTR | [5 empty] | 408 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | 380 | #4DTR(B)(380) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0135 |  |  | 1-10-07 |  |  | 380 | PHA | 380 相間電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.380_PHA2 | 380開關箱IED RY PHA | OTHER | [5 empty] | 409 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 380 | #4DTR(B)(380) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0136 |  |  | 1-11-00 |  |  | 380 | GDA | 380 接地電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.380_GDA | 380開關箱IED RY GDA | OTHER | [5 empty] | 410 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | 100 | TIE(100) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0256 |  |  | 2-00-00 |  |  | 100 | PHA | 100 相間電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.100_51A | 11KV TIE(100) 51RY | TIE | [5 empty] | 411 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | 100 | TIE(100) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0257 |  |  | 2-00-01 |  |  | 100 | GDA | 100 接地電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.100_51NA | 11KV TIE(100) 51N RY | TIE | [5 empty] | 412 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | 100 | TIE(100) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/2ABus | B/2BBus |  |  | 0258 |  | 0224 | 2-00-02 |  | 2-60 | 100 | 52AS | 100 CB (ON/OFF) |  | aaab | B3/D13_A1 | [8 empty] | 虎科DS.100_CB | 100(TIE) CB | TIE | [5 empty] | 413 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 11 | 11kV | XO31 | 科十一線(XO31) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0259 |  |  | 2-00-03 |  |  | XO31 | PHA | XO31 相間電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO31_PHA | 11KV科11線(XO31) 相間RY | FEEDER | [5 empty] | 414 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO31 | 科十一線(XO31) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0260 |  |  | 2-00-04 |  |  | XO31 | GDA | XO31 接地電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO31_GDA | 11KV科11線(XO31) 接地RY | FEEDER | [5 empty] | 415 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO31 | 科十一線(XO31) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/XO31/T1 |  |  | 0261 |  | 0129 | 2-00-05 |  | 2-01 | XO31 | 52AS | XO31 CB (ON/OFF) |  | aabb | B2/D13_D1 | [8 empty] | 虎科DS.XO31_CB | XO31(11KV科11線) CB | FEEDER | [5 empty] | 416 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | XO32 | 科十二線(XO32) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0262 |  |  | 2-00-06 |  |  | XO32 | PHA | XO32 相間電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO32_PHA | 11KV科12線(XO32) 相間RY | FEEDER | [5 empty] | 417 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO32 | 科十二線(XO32) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0263 |  |  | 2-00-07 |  |  | XO32 | GDA | XO32 接地電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO32_GDA | 11KV科12線(XO32) 接地RY | FEEDER | [5 empty] | 418 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO32 | 科十二線(XO32) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/XO32/T1 |  |  | 0264 |  | 0132 | 2-01-00 |  | 2-04 | XO32 | 52AS | XO32 CB (ON/OFF) |  | aacb | B2/D13_D1 | [8 empty] | 虎科DS.XO32_CB | XO32(11KV科12線) CB | FEEDER | [5 empty] | 419 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | XO33 | 科十三線(XO33) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0265 |  |  | 2-01-01 |  |  | XO33 | PHA | XO33 相間電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO33_PHA | 11KV科13線(XO33) 相間RY | FEEDER | [5 empty] | 420 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO33 | 科十三線(XO33) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0266 |  |  | 2-01-02 |  |  | XO33 | GDA | XO33 接地電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO33_GDA | 11KV科13線(XO33) 接地RY | FEEDER | [5 empty] | 421 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO33 | 科十三線(XO33) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/XO33/T1 |  |  | 0267 |  | 0135 | 2-01-03 |  | 2-07 | XO33 | 52AS | XO33 CB (ON/OFF) |  | aadb | B2/D13_D1 | [8 empty] | 虎科DS.XO33_CB | XO33(11KV科13線) CB | FEEDER | [5 empty] | 422 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | XO34 | 科十四線(XO34) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0268 |  |  | 2-01-04 |  |  | XO34 | PHA | XO34 相間電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO34_PHA | 11KV科14線(XO34) 相間RY | FEEDER | [5 empty] | 423 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO34 | 科十四線(XO34) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0269 |  |  | 2-01-05 |  |  | XO34 | GDA | XO34 接地電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO34_GDA | 11KV科14線(XO34) 接地RY | FEEDER | [5 empty] | 424 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO34 | 科十四線(XO34) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/XO34/T1 |  |  | 0270 |  | 0138 | 2-01-06 |  | 2-0A | XO34 | 52AS | XO34 CB (ON/OFF) |  | aaeb | B2/D13_D1 | [8 empty] | 虎科DS.XO34_CB | XO34(11KV科14線) CB | FEEDER | [5 empty] | 425 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | XO35 | 科十五線(XO35) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0271 |  |  | 2-01-07 |  |  | XO35 | PHA | XO35 相間電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO35_PHA | 11KV科15線(XO35) 相間RY | FEEDER | [5 empty] | 426 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO35 | 科十五線(XO35) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0272 |  |  | 2-02-00 |  |  | XO35 | GDA | XO35 接地電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO35_GDA | 11KV科15線(XO35) 接地RY | FEEDER | [5 empty] | 427 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO35 | 科十五線(XO35) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/XO35/T1 |  |  | 0273 |  | 0141 | 2-02-01 |  | 2-0D | XO35 | 52AS | XO35 CB (ON/OFF) |  | aafb | B2/D13_D1 | [8 empty] | 虎科DS.XO35_CB | XO35(11KV科15線) CB | FEEDER | [5 empty] | 428 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | 230 | #3SC(230) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0274 |  |  | 2-02-02 |  |  | 230 | SCA | 230 相間及接地電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.230_SCA | 11KV #3SC 51,51N RY | SC | [5 empty] | 429 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | 230 | #3SC(230) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0275 |  |  | 2-02-03 |  |  | 230 | 2AUVA | 230 欠壓電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.230_OUVA | 11KV #3SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 430 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | 230 | #3SC(230) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | C/3SC |  |  | 0276 |  | 0144 | 2-02-04 |  | 2-10 | 230 | 52AS | 230 CB (ON/OFF) |  | aagb | B3/D13_A1 | [8 empty] | 虎科DS.230_CB | 230(11KV #3SC) CB | SC | [5 empty] | 431 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | 200 | TIE(200) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0277 |  |  | 2-02-05 |  |  | 200 | PHA | 200 相間電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.200_51A | 23KV TIE(200) 51RY | TIE | [5 empty] | 432 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | 200 | TIE(200) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0278 |  |  | 2-02-06 |  |  | 200 | GDA | 200 接地電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.200_51NA | 23KV TIE(200) 51N RY | TIE | [5 empty] | 433 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | 200 | TIE(200) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/2BBus | B/2ABus |  |  | 0279 |  | 0145 | 2-02-07 |  | 2-11 | 200 | 52AS | 200 CB (ON/OFF) |  | baab | B3/D13_A1 | [8 empty] | 虎科DS.200_CB | 200(TIE) CB | TIE | [5 empty] | 434 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 11 | 11kV | XO36 | 科十六線(XO36) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0280 |  |  | 2-03-00 |  |  | XO36 | PHA | XO36 相間電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO36_PHA | 11KV科16線(XO36) 相間RY | FEEDER | [5 empty] | 435 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO36 | 科十六線(XO36) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0281 |  |  | 2-03-01 |  |  | XO36 | GDA | XO36 接地電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO36_GDA | 11KV科16線(XO36) 接地RY | FEEDER | [5 empty] | 436 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO36 | 科十六線(XO36) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/XO36/T1 |  |  | 0282 |  | 0147 | 2-03-02 |  | 2-13 | XO36 | 52AS | XO36 CB (ON/OFF) |  | babb | B2/D13_D1 | [8 empty] | 虎科DS.XO36_CB | XO36(11KV科16線) CB | FEEDER | [5 empty] | 437 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | XO37 | 科十七線(XO37) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0283 |  |  | 2-03-03 |  |  | XO37 | PHA | XO37 相間電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO37_PHA | 11KV科17線(XO37) 相間RY | FEEDER | [5 empty] | 438 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO37 | 科十七線(XO37) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0284 |  |  | 2-03-04 |  |  | XO37 | GDA | XO37 接地電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO37_GDA | 11KV科17線(XO37) 接地RY | FEEDER | [5 empty] | 439 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO37 | 科十七線(XO37) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/XO37/T1 |  |  | 0285 |  | 0150 | 2-03-05 |  | 2-16 | XO37 | 52AS | XO37 CB (ON/OFF) |  | bacb | B2/D13_D1 | [8 empty] | 虎科DS.XO37_CB | XO37(11KV科17線) CB | FEEDER | [5 empty] | 440 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | XO38 | 科十八線(XO38) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0286 |  |  | 2-03-06 |  |  | XO38 | PHA | XO38 相間電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO38_PHA | 11KV科18線(XO38) 相間RY | FEEDER | [5 empty] | 441 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO38 | 科十八線(XO38) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0287 |  |  | 2-03-07 |  |  | XO38 | GDA | XO38 接地電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO38_GDA | 11KV科18線(XO38) 接地RY | FEEDER | [5 empty] | 442 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO38 | 科十八線(XO38) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/XO38/T1 |  |  | 0288 |  | 0153 | 2-04-00 |  | 2-19 | XO38 | 52AS | XO38 CB (ON/OFF) |  | badb | B2/D13_D1 | [8 empty] | 虎科DS.XO38_CB | XO38(11KV科18線) CB | FEEDER | [5 empty] | 443 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | XO39 | 科十九線(XO39) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0289 |  |  | 2-04-01 |  |  | XO39 | PHA | XO39 相間電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO39_PHA | 11KV科19線(XO39) 相間RY | FEEDER | [5 empty] | 444 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO39 | 科十九線(XO39) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0290 |  |  | 2-04-02 |  |  | XO39 | GDA | XO39 接地電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO39_GDA | 11KV科19線(XO39) 接地RY | FEEDER | [5 empty] | 445 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO39 | 科十九線(XO39) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/XO39/T1 |  |  | 0291 |  | 0156 | 2-04-03 |  | 2-1C | XO39 | 52AS | XO39 CB (ON/OFF) |  | baeb | B2/D13_D1 | [8 empty] | 虎科DS.XO39_CB | XO39(11KV科19線) CB | FEEDER | [5 empty] | 446 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | XO40 | 科二十線(XO40) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0292 |  |  | 2-04-04 |  |  | XO40 | PHA | XO40 相間電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO40_PHA | 11KV科20線(XO40) 相間RY | FEEDER | [5 empty] | 447 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO40 | 科二十線(XO40) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0293 |  |  | 2-04-05 |  |  | XO40 | GDA | XO40 接地電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO40_GDA | 11KV科20線(XO40) 接地RY | FEEDER | [5 empty] | 448 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO40 | 科二十線(XO40) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/XO40/T1 |  |  | 0294 |  | 0159 | 2-04-06 |  | 2-1F | XO40 | 52AS | XO40 CB (ON/OFF) |  | bafb | B2/D13_D1 | [8 empty] | 虎科DS.XO40_CB | XO40(11KV科20線) CB | FEEDER | [5 empty] | 449 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | 240 | #4SC(240) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0295 |  |  | 2-04-07 |  |  | 240 | SCA | 240 相間及接地電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.240_SCA | 11KV #4SC 51,51N RY | SC | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | 240 | #4SC(240) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0296 |  |  | 2-05-00 |  |  | 240 | 2BUVA | 240 欠壓電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.240_OUVA | 11KV #4SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 451 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | 240 | #4SC(240) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | C/4SC |  |  | 0297 |  | 0162 | 2-05-01 |  | 2-22 | 240 | 52AS | 240 CB (ON/OFF) |  | bagb | B3/D13_A1 | [8 empty] | 虎科DS.240_CB | 240(11KV #4SC) CB | SC | [5 empty] | 452 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | 250 | #5SC(250) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0298 |  |  | 2-05-02 |  |  | 250 | SCA | 250 相間及接地電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.250_SCA | 23KV #5SC 51,51N RY | SC | [5 empty] | 453 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 250 | #5SC(250) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0299 |  |  | 2-05-03 |  |  | 250 | 2BUVA | 250 欠壓電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.250_OUVA | 23KV #5SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 454 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 250 | #5SC(250) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3ABus | C/5SC |  |  | 0300 |  | 0164 | 2-05-04 |  | 2-24 | 250 | 52AS | 250 CB (ON/OFF) |  | abbb | B3/D13_A1 | [8 empty] | 虎科DS.250_CB | 250(23KV #5SC) CB | SC | [5 empty] | 455 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO61 | 科六一線(XO61) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0301 |  |  | 2-05-05 |  |  | XO61 | PHA | XO61 相間電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO61_PHA | 23KV科61線(XO61) 相間RY | FEEDER | [5 empty] | 456 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO61 | 科六一線(XO61) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0302 |  |  | 2-05-06 |  |  | XO61 | GDA | XO61 接地電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO61_GDA | 23KV科61線(XO61) 接地RY | FEEDER | [5 empty] | 457 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO61 | 科六一線(XO61) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3ABus | L/XO61/T1 |  |  | 0303 |  | 0165 | 2-05-07 |  | 2-25 | XO61 | 52AS | XO61 CB (ON/OFF) |  | abcb | B2/D13_D1 | [8 empty] | 虎科DS.XO61_CB | XO61(23KV科61線) CB | FEEDER | [5 empty] | 458 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO62 | 科六二線(XO62) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0304 |  |  | 2-06-00 |  |  | XO62 | PHA | XO62 相間電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO62_PHA | 23KV科62線(XO62) 相間RY | FEEDER | [5 empty] | 459 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO62 | 科六二線(XO62) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0305 |  |  | 2-06-01 |  |  | XO62 | GDA | XO62 接地電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO62_GDA | 23KV科62線(XO62) 接地RY | FEEDER | [5 empty] | 460 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO62 | 科六二線(XO62) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3ABus | L/XO62/T1 |  |  | 0306 |  | 0168 | 2-06-02 |  | 2-28 | XO62 | 52AS | XO62 CB (ON/OFF) |  | abdb | B2/D13_D1 | [8 empty] | 虎科DS.XO62_CB | XO62(23KV科62線) CB | FEEDER | [5 empty] | 461 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO63 | 科六三線(XO63) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0307 |  |  | 2-06-03 |  |  | XO63 | PHA | XO63 相間電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO63_PHA | 23KV科63線(XO63) 相間RY | FEEDER | [5 empty] | 462 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO63 | 科六三線(XO63) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0308 |  |  | 2-06-04 |  |  | XO63 | GDA | XO63 接地電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO63_GDA | 23KV科63線(XO63) 接地RY | FEEDER | [5 empty] | 463 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO63 | 科六三線(XO63) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3ABus | L/XO63/T1 |  |  | 0309 |  | 0171 | 2-06-05 |  | 2-2B | XO63 | 52AS | XO63 CB (ON/OFF) |  | abfb | B2/D13_D1 | [8 empty] | 虎科DS.XO63_CB | XO63(23KV科63線) CB | FEEDER | [5 empty] | 464 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO64 | 科六四線(XO64) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0310 |  |  | 2-06-06 |  |  | XO64 | PHA | XO64 相間電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO64_PHA | 23KV科64線(XO64) 相間RY | FEEDER | [5 empty] | 465 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO64 | 科六四線(XO64) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0311 |  |  | 2-06-07 |  |  | XO64 | GDA | XO64 接地電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO64_GDA | 23KV科64線(XO64) 接地RY | FEEDER | [5 empty] | 466 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO64 | 科六四線(XO64) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3ABus | L/XO64/T1 |  |  | 0312 |  | 0174 | 2-07-00 |  | 2-2E | XO64 | 52AS | XO64 CB (ON/OFF) |  | abgb | B2/D13_D1 | [8 empty] | 虎科DS.XO64_CB | XO64(23KV科64線) CB | FEEDER | [5 empty] | 467 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | 260 | #6SC(260) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0313 |  |  | 2-07-01 |  |  | 260 | SCA | 260 相間及接地電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.260_SCA | 23KV #6SC 51,51N RY | SC | [5 empty] | 468 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 260 | #6SC(260) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0314 |  |  | 2-07-02 |  |  | 260 | 2BUVA | 260 欠壓電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.260_OUVA | 23KV #6SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 469 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 260 | #6SC(260) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3BBus | C/6SC |  |  | 0315 |  | 0178 | 2-07-03 |  | 2-32 | 260 | 52AS | 260 CB (ON/OFF) |  | acbb | B3/D13_A1 | [8 empty] | 虎科DS.260_CB | 260(23KV #6SC) CB | SC | [5 empty] | 470 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO65 | 科六五線(XO65) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0316 |  |  | 2-07-04 |  |  | XO65 | PHA | XO65 相間電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO65_PHA | 23KV科65線(XO65) 相間RY | FEEDER | [5 empty] | 471 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO65 | 科六五線(XO65) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0317 |  |  | 2-07-05 |  |  | XO65 | GDA | XO65 接地電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO65_GDA | 23KV科65線(XO65) 接地RY | FEEDER | [5 empty] | 472 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO65 | 科六五線(XO65) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BBus | L/XO65/T1 |  |  | 0318 |  | 0179 | 2-07-06 |  | 2-33 | XO65 | 52AS | XO65 CB (ON/OFF) |  | accb | B2/D13_D1 | [8 empty] | 虎科DS.XO65_CB | XO65(23KV科65線) CB | FEEDER | [5 empty] | 473 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO66 | 科六六線(XO66) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0319 |  |  | 2-07-07 |  |  | XO66 | PHA | XO66 相間電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO66_PHA | 23KV科66線(XO66) 相間RY | FEEDER | [5 empty] | 474 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO66 | 科六六線(XO66) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0320 |  |  | 2-08-00 |  |  | XO66 | GDA | XO66 接地電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO66_GDA | 23KV科66線(XO66) 接地RY | FEEDER | [5 empty] | 475 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO66 | 科六六線(XO66) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BBus | L/XO66/T1 |  |  | 0321 |  | 0182 | 2-08-01 |  | 2-36 | XO66 | 52AS | XO66 CB (ON/OFF) |  | acdb | B2/D13_D1 | [8 empty] | 虎科DS.XO66_CB | XO66(23KV科66線) CB | FEEDER | [5 empty] | 476 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO67 | 科六七線(XO67) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0322 |  |  | 2-08-02 |  |  | XO67 | PHA | XO67 相間電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO67_PHA | 23KV科67線(XO67) 相間RY | FEEDER | [5 empty] | 477 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO67 | 科六七線(XO67) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0323 |  |  | 2-08-03 |  |  | XO67 | GDA | XO67 接地電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO67_GDA | 23KV科67線(XO67) 接地RY | FEEDER | [5 empty] | 478 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO67 | 科六七線(XO67) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BBus | L/XO67/T1 |  |  | 0324 |  | 0185 | 2-08-04 |  | 2-39 | XO67 | 52AS | XO67 CB (ON/OFF) |  | acfb | B2/D13_D1 | [8 empty] | 虎科DS.XO67_CB | XO67(23KV科67線) CB | FEEDER | [5 empty] | 479 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO68 | 科六八線(XO68) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0325 |  |  | 2-08-05 |  |  | XO68 | PHA | XO68 相間電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO68_PHA | 23KV科68線(XO68) 相間RY | FEEDER | [5 empty] | 480 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO68 | 科六八線(XO68) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0326 |  |  | 2-08-06 |  |  | XO68 | GDA | XO68 接地電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO68_GDA | 23KV科68線(XO68) 接地RY | FEEDER | [5 empty] | 481 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO68 | 科六八線(XO68) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BBus | L/XO68/T1 |  |  | 0327 |  | 0188 | 2-08-07 |  | 2-3C | XO68 | 52AS | XO68 CB (ON/OFF) |  | acgb | B2/D13_D1 | [8 empty] | 虎科DS.XO68_CB | XO68(23KV科68線) CB | FEEDER | [5 empty] | 482 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | 390 | #1SSTR(390) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0328 |  |  | 2-09-00 |  |  | 390 | PHA | 390 相間電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.#1SSTR_51A | #1SSTR 51RY | OTHER | [5 empty] | 483 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 390 | #1SSTR(390) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0329 |  |  | 2-09-01 |  |  | 390 | GDA | 390 接地電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | [5 empty] | 484 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 390 | #1SSTR(390) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3BBus | T/1SSTR |  |  | 0330 |  | 0191 | 2-09-02 |  | 2-3F | 390 | 52AS | 390 CB (ON/OFF) |  | achb | B3/D13_A1 | [8 empty] | 虎科DS.390_CB | 390(#1SSTR) CB | OTHER | [5 empty] | 485 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | 300 | TIE(300) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0331 |  |  | 2-09-03 |  |  | 300 | PHA | 300 相間電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.300_51A | 23KV TIE(300) 51RY | TIE | [5 empty] | 486 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 300 | TIE(300) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0332 |  |  | 2-09-04 |  |  | 300 | GDA | 300 接地電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.300_51NA | 23KV TIE(300) 51N RY | TIE | [5 empty] | 487 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 300 | TIE(300) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/4ABus | B/3ABus |  |  | 0333 |  | 0193 | 2-09-05 |  | 2-41 | 300 | 52AS | 300 CB (ON/OFF) |  | bbib | B3/D13_A1 | [8 empty] | 虎科DS.300_CB | 300(TIE) CB | TIE | [5 empty] | 488 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 22 | 22kV | XO71 | 科七一線(XO71) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0334 |  |  | 2-09-06 |  |  | XO71 | PHA | XO71 相間電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO71_PHA | 23KV科71線(XO71) 相間RY | FEEDER | [5 empty] | 489 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO71 | 科七一線(XO71) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0335 |  |  | 2-09-07 |  |  | XO71 | GDA | XO71 接地電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO71_GDA | 23KV科71線(XO71) 接地RY | FEEDER | [5 empty] | 490 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO71 | 科七一線(XO71) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4ABus | L/XO71/T1 |  |  | 0336 |  | 0194 | 2-0A-00 |  | 2-42 | XO71 | 52AS | XO71 CB (ON/OFF) |  | bbhb | B2/D13_D1 | [8 empty] | 虎科DS.XO71_CB | XO71(23KV科71線) CB | FEEDER | [5 empty] | 491 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO72 | 科七二線(XO72) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0337 |  |  | 2-0A-01 |  |  | XO72 | PHA | XO72 相間電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO72_PHA | 23KV科72線(XO72) 相間RY | FEEDER | [5 empty] | 492 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO72 | 科七二線(XO72) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0338 |  |  | 2-0A-02 |  |  | XO72 | GDA | XO72 接地電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO72_GDA | 23KV科72線(XO72) 接地RY | FEEDER | [5 empty] | 493 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO72 | 科七二線(XO72) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4ABus | L/XO72/T1 |  |  | 0339 |  | 0197 | 2-0A-03 |  | 2-45 | XO72 | 52AS | XO72 CB (ON/OFF) |  | bbgb | B2/D13_D1 | [8 empty] | 虎科DS.XO72_CB | XO72(23KV科72線) CB | FEEDER | [5 empty] | 494 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO73 | 科七三線(XO73) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0340 |  |  | 2-0A-04 |  |  | XO73 | PHA | XO73 相間電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO73_PHA | 23KV科73線(XO73) 相間RY | FEEDER | [5 empty] | 495 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO73 | 科七三線(XO73) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0341 |  |  | 2-0A-05 |  |  | XO73 | GDA | XO73 接地電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO73_GDA | 23KV科73線(XO73) 接地RY | FEEDER | [5 empty] | 496 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO73 | 科七三線(XO73) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4ABus | L/XO73/T1 |  |  | 0342 |  | 0200 | 2-0A-06 |  | 2-48 | XO73 | 52AS | XO73 CB (ON/OFF) |  | bbfb | B2/D13_D1 | [8 empty] | 虎科DS.XO73_CB | XO73(23KV科73線) CB | FEEDER | [5 empty] | 497 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO74 | 科七四線(XO74) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0343 |  |  | 2-0A-07 |  |  | XO74 | PHA | XO74 相間電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO74_PHA | 23KV科74線(XO74) 相間RY | FEEDER | [5 empty] | 498 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO74 | 科七四線(XO74) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0344 |  |  | 2-0B-00 |  |  | XO74 | GDA | XO74 接地電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO74_GDA | 23KV科74線(XO74) 接地RY | FEEDER | [5 empty] | 499 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO74 | 科七四線(XO74) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4ABus | L/XO74/T1 |  |  | 0345 |  | 0203 | 2-0B-01 |  | 2-4B | XO74 | 52AS | XO74 CB (ON/OFF) |  | bbeb | B2/D13_D1 | [8 empty] | 虎科DS.XO74_CB | XO74(23KV科74線) CB | FEEDER | [5 empty] | 500 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | 270 | #7SC(270) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0346 |  |  | 2-0B-02 |  |  | 270 | SCA | 270 相間及接地電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.270_SCA | 23KV #7SC 51,51N RY | SC | [5 empty] | 501 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 270 | #7SC(270) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0347 |  |  | 2-0B-03 |  |  | 270 | 2BUVA | 270 欠壓電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.270_OUVA | 23KV #7SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 502 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 270 | #7SC(270) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4ABus | C/7SC |  |  | 0348 |  | 0206 | 2-0B-04 |  | 2-4E | 270 | 52AS | 270 CB (ON/OFF) |  | bbcb | B3/D13_A1 | [8 empty] | 虎科DS.270_CB | 270(23KV #7SC) CB | SC | [5 empty] | 503 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | 490 | #2SSTR(490) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0349 |  |  | 2-0B-05 |  |  | 490 | PHA | 490 相間電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.#2SSTR_51A | #2SSTR 51RY | OTHER | [5 empty] | 504 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 490 | #2SSTR(490) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0350 |  |  | 2-0B-06 |  |  | 490 | GDA | 490 接地電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | [5 empty] | 505 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 490 | #2SSTR(490) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4ABus | T/2SSTR |  |  | 0351 |  | 0207 | 2-0B-07 |  | 2-4F | 490 | 52AS | 490 CB (ON/OFF) |  | bbbb | B3/D13_A1 | [8 empty] | 虎科DS.490_CB | 490(#2SSTR) CB | OTHER | [5 empty] | 506 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | 400 | TIE(400) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0352 |  |  | 2-0C-00 |  |  | 400 | PHA | 400 相間電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.400_51A | 23KV TIE(400) 51RY | TIE | [5 empty] | 507 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 400 | TIE(400) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0353 |  |  | 2-0C-01 |  |  | 400 | GDA | 400 接地電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.400_51NA | 23KV TIE(400) 51N RY | TIE | [5 empty] | 508 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 400 | TIE(400) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/4BBus | B/3BBus |  |  | 0354 |  | 0209 | 2-0C-02 |  | 2-51 | 400 | 52AS | 400 CB (ON/OFF) |  | bchb | B3/D13_A1 | [8 empty] | 虎科DS.400_CB | 400(TIE) CB | TIE | [5 empty] | 509 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D13 | 虎科DS | 22 | 22kV | XO75 | 科七五線(XO75) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0355 |  |  | 2-0C-03 |  |  | XO75 | PHA | XO75 相間電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO75_PHA | 23KV科75線(XO75) 相間RY | FEEDER | [5 empty] | 510 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO75 | 科七五線(XO75) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0356 |  |  | 2-0C-04 |  |  | XO75 | GDA | XO75 接地電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO75_GDA | 23KV科75線(XO75) 接地RY | FEEDER | [5 empty] | 511 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO75 | 科七五線(XO75) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4BBus | L/XO75/T1 |  |  | 0357 |  | 0210 | 2-0C-05 |  | 2-52 | XO75 | 52AS | XO75 CB (ON/OFF) |  | bcgb | B2/D13_D1 | [8 empty] | 虎科DS.XO75_CB | XO75(23KV科75線) CB | FEEDER | [5 empty] | 512 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO76 | 科七六線(XO76) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0358 |  |  | 2-0C-06 |  |  | XO76 | PHA | XO76 相間電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO76_PHA | 23KV科76線(XO76) 相間RY | FEEDER | [5 empty] | 513 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO76 | 科七六線(XO76) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0359 |  |  | 2-0C-07 |  |  | XO76 | GDA | XO76 接地電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO76_GDA | 23KV科76線(XO76) 接地RY | FEEDER | [5 empty] | 514 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO76 | 科七六線(XO76) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4BBus | L/XO76/T1 |  |  | 0360 |  | 0213 | 2-0D-00 |  | 2-55 | XO76 | 52AS | XO76 CB (ON/OFF) |  | bcfb | B2/D13_D1 | [8 empty] | 虎科DS.XO76_CB | XO76(23KV科76線) CB | FEEDER | [5 empty] | 515 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO77 | 科七七線(XO77) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0361 |  |  | 2-0D-01 |  |  | XO77 | PHA | XO77 相間電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO77_PHA | 23KV科77線(XO77) 相間RY | FEEDER | [5 empty] | 516 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO77 | 科七七線(XO77) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0362 |  |  | 2-0D-02 |  |  | XO77 | GDA | XO77 接地電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO77_GDA | 23KV科77線(XO77) 接地RY | FEEDER | [5 empty] | 517 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO77 | 科七七線(XO77) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4BBus | L/XO77/T1 |  |  | 0363 |  | 0216 | 2-0D-03 |  | 2-58 | XO77 | 52AS | XO77 CB (ON/OFF) |  | bceb | B2/D13_D1 | [8 empty] | 虎科DS.XO77_CB | XO77(23KV科77線) CB | FEEDER | [5 empty] | 518 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO78 | 科七八線(XO78) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0364 |  |  | 2-0D-04 |  |  | XO78 | PHA | XO78 相間電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO78_PHA | 23KV科78線(XO78) 相間RY | FEEDER | [5 empty] | 519 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO78 | 科七八線(XO78) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0365 |  |  | 2-0D-05 |  |  | XO78 | GDA | XO78 接地電驛(動作/正常) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO78_GDA | 23KV科78線(XO78) 接地RY | FEEDER | [5 empty] | 520 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO78 | 科七八線(XO78) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4BBus | L/XO78/T1 |  |  | 0366 |  | 0219 | 2-0D-06 |  | 2-5B | XO78 | 52AS | XO78 CB (ON/OFF) |  | bcdb | B2/D13_D1 | [8 empty] | 虎科DS.XO78_CB | XO78(23KV科78線) CB | FEEDER | [5 empty] | 521 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | 280 | #8SC(280) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0367 |  |  | 2-0D-07 |  |  | 280 | SCA | 280 相間及接地電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.280_SCA | 23KV #8SC 51,51N RY | SC | [5 empty] | 522 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 280 | #8SC(280) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0368 |  |  | 2-0E-00 |  |  | 280 | 2BUVA | 280 欠壓電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.280_OUVA | 23KV #8SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 523 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 280 | #8SC(280) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4BBus | C/8SC |  |  | 0369 |  | 0222 | 2-0E-01 |  | 2-5E | 280 | 52AS | 280 CB (ON/OFF) |  | bcbb | B3/D13_A1 | [8 empty] | 虎科DS.280_CB | 280(23KV #8SC) CB | SC | [5 empty] | 524 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0512 |  | 0000 | 1-30-00 |  | 1-00 | MCC-1 | TEST | TEST CB (開啟/ 閉合) |  |  | ELEM/ALL | [8 empty] | 虎科DS.TEST_CB | TEST CB | OTHER | [5 empty] | 525 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS |  |  | 2DTR | #2DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0513 |  |  | 1-30-01 |  |  | M2 | 2TRA | #2 DTR 重故障警報(動作/正常) |  | a | B1/D13_A1 | [8 empty] | 虎科DS.#2DTR_TRA | #2DTR 重故障 | MTR | [5 empty] | 526 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS |  |  | 2DTR | #2DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0514 |  |  | 1-30-02 |  |  | M2 | 2TRF | #2 DTR 輕故障警報(動作/正常) |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#2DTR_TRF | #2DTR 輕故障 | MTR | [5 empty] | 527 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS |  |  | 2DTR(A) | #2DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0515 |  | 0001 | 1-30-03 |  | 1-01 | M2 | 243AS1 | #2 DTR WIND-A ULTC(自動/手動) |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | [5 empty] | 528 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D13 | 虎科DS |  |  | 2DTR(B) | #2DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0516 |  | 0003 | 1-30-04 |  | 1-03 | M2 | 243AS2 | #2 DTR WIND-B ULTC(自動/手動) |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | [5 empty] | 529 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D13 | 虎科DS |  |  | 2DTR | #2DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0517 |  |  | 1-30-05 |  |  | M2 | 263Q | #2 DTR ULTC 保護電驛警報 |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#2DTR_63Q | #2DTR 63Q RY | MTR | [5 empty] | 530 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS |  |  | 2DTR | #2DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0518 |  |  | 1-30-06 |  |  | M2 | 296D | #2 DTR 放壓電驛警報(動作/正常) |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#2DTR_96D | #2DTR 96D RY | MTR | [5 empty] | 531 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS |  |  | 2DTR | #2DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0519 |  |  | 1-30-07 |  |  | M2 | 296B2 | #2 DTR 撲氣電驛第二段警報(動作/正常) |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | [5 empty] | 532 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS |  |  | 2DTR | #2DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0520 |  |  | 1-30-08 |  |  | M2 | 296B1 | #2 DTR 撲氣電驛第一段警報(動作/正常) |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | [5 empty] | 533 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS |  |  | 2DTR(A) | #2DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0521 |  |  | 1-30-09 |  |  | M2 | 243RS1 | #2 DTR WIND-A位置(SUP/LOC) |  | c | B1/D13_A1 | [8 empty] | 虎科DS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | [5 empty] | 534 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D13 | 虎科DS |  |  | 2DTR(B) | #2DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0522 |  |  | 1-30-10 |  |  | M2 | 243RS2 | #2 DTR WIND-B位置(SUP/LOC) |  | b | B1/D13_A1 | [8 empty] | 虎科DS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | [5 empty] | 535 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D13 | 虎科DS |  |  | 2DTR | #2DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0523 |  |  | 1-30-11 |  |  | M2 | 296P | #2 DTR 衝擊油壓電驛警報(動作/正常) |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#2DTR_96P | #2DTR 96P RY | MTR | [5 empty] | 536 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS |  |  | 3DTR | #3DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR |  |  |  |  | 0524 |  |  | 1-30-12 |  |  | M3 | 3TRA | #3 DTR 重故障警報(動作/正常) |  | a | B1/D13_A1 | [8 empty] | 虎科DS.#3DTR_TRA | #3DTR 重故障 | MTR | [5 empty] | 537 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS |  |  | 3DTR | #3DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0525 |  |  | 1-30-13 |  |  | M3 | 3TRF | #3 DTR 輕故障警報(動作/正常) |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#3DTR_TRF | #3DTR 輕故障 | MTR | [5 empty] | 538 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS |  |  | 3DTR | #3DTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0526 |  | 0005 | 1-30-14 |  | 1-05 | M3 | 343AS1 | #3 DTR WIND-AULTC(自動/手動) |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#3DTR_A/M | #3DTR OLTC A/M | MTR | [5 empty] | 539 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D13 | 虎科DS |  |  | 3DTR | #3DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0527 |  |  | 1-30-15 |  |  | M3 | 363Q | #3 DTR ULTC 保護電驛警報 |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#3DTR_63Q | #3DTR 63Q RY | MTR | [5 empty] | 540 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS |  |  | 3DTR | #3DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0528 |  |  | 1-31-00 |  |  | M3 | 396D | #3 DTR 放壓電驛警報(動作/正常) |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#3DTR_96D | #3DTR 96D RY | MTR | [5 empty] | 541 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS |  |  | 3DTR | #3DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0529 |  |  | 1-31-01 |  |  | M3 | 396B2 | #3 DTR 撲氣電驛第二段警報(動作/正常) |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#3DTR_96B2 | #3DTR 96B2 RY | MTR | [5 empty] | 542 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS |  |  | 3DTR | #3DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0530 |  |  | 1-31-02 |  |  | M3 | 396B1 | #3 DTR 撲氣電驛第一段警報(動作/正常) |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#3DTR_96B1 | #3DTR 96B1 RY | MTR | [5 empty] | 543 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS |  |  | 3DTR | #3DTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0531 |  |  | 1-31-03 |  |  | M3 | 343RS1 | #3 DTR WIND-A 位置(SUP/LOC) |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#3DTR_S/L | #3DTR OLTC S/L | MTR | [5 empty] | 544 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D13 | 虎科DS |  |  | 3DTR | #3DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0532 |  |  | 1-31-04 |  |  | M3 | 396P | #3 DTR 衝擊油壓電驛警報(動作/正常) |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#3DTR_96P | #3DTR 96P RY | MTR | [5 empty] | 545 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS |  |  | 4DTR | #4DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR |  |  |  |  | 0533 |  |  | 1-31-05 |  |  | M4 | 4TRA | #4 DTR 重故障警報(動作/正常) |  | a | B1/D13_A1 | [8 empty] | 虎科DS.#4DTR_TRA | #4DTR 重故障 | MTR | [5 empty] | 546 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS |  |  | 4DTR | #4DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0534 |  |  | 1-31-06 |  |  | M4 | 4TRF | #4 DTR 輕故障警報(動作/正常) |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#4DTR_TRF | #4DTR 輕故障 | MTR | [5 empty] | 547 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS |  |  | 4DTR | #4DTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0535 |  | 0007 | 1-31-07 |  | 1-07 | M4 | 443AS1 | #4 DTR WIND-AULTC(自動/手動) |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#4DTR_A/M | #4DTR OLTC A/M | MTR | [5 empty] | 548 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D13 | 虎科DS |  |  | 4DTR | #4DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0536 |  |  | 1-31-08 |  |  | M4 | 463Q | #4 DTR ULTC 保護電驛警報 |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#4DTR_63Q | #4DTR 63Q RY | MTR | [5 empty] | 549 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS |  |  | 4DTR | #4DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0537 |  |  | 1-31-09 |  |  | M4 | 496D | #4 DTR 放壓電驛警報(動作/正常) |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#4DTR_96D | #4DTR 96D RY | MTR | [5 empty] | 550 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS |  |  | 4DTR | #4DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0538 |  |  | 1-31-10 |  |  | M4 | 496B2 | #4 DTR 撲氣電驛第二段警報(動作/正常) |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#4DTR_96B2 | #4DTR 96B2 RY | MTR | [5 empty] | 551 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS |  |  | 4DTR | #4DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0539 |  |  | 1-31-11 |  |  | M4 | 496B1 | #4 DTR 撲氣電驛第一段警報(動作/正常) |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#4DTR_96B1 | #4DTR 96B1 RY | MTR | [5 empty] | 552 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS |  |  | 4DTR | #4DTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0540 |  |  | 1-31-12 |  |  | M4 | 443RS1 | #4 DTR WIND-A 位置(SUP/LOC) |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#4DTR_S/L | #4DTR OLTC S/L | MTR | [5 empty] | 553 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D13 | 虎科DS |  |  | 4DTR | #4DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0541 |  |  | 1-31-13 |  |  | M4 | 496P | #4 DTR 衝擊油壓電驛警報(動作/正常) |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#4DTR_96P | #4DTR 96P RY | MTR | [5 empty] | 554 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS |  |  | 4DTR | #4DTR |  | OLTC_A |  |  | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0542 |  |  | 1-31-14 |  |  | ------ | OLTCA | OLTC 15分鐘內連動3次警報 |  |  | B1/D13_A1 | [8 empty] | 虎科DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | [5 empty] | 555 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1570 | 虎科～虎菁一路(1570) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0549 |  | 0013 | 1-32-05 |  | 1-0D | R1 | L787S | 1570 虎科虎菁一路主保護電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1570_87UL | 虎科虎菁一路(1570) 87RY U/L | LINE161 | [5 empty] | 556 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | 1580 | 虎科～虎菁二路(1580) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0550 |  | 0015 | 1-32-06 |  | 1-0F | R2 | L887S | 1580 虎科虎菁二路主保護電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1580_87UL | 虎科虎菁二路(1580) 87RY U/L | LINE161 | [5 empty] | 557 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0551 |  | 0017 | 1-32-07 |  | 1-11 | R3 | L987S1 | 1610 虎科和鑫一路(第一套)主保護電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1610_87UL1 | 虎科和鑫一路(1610) #1 87RY U/L | LINE161 | [5 empty] | 558 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0552 |  | 0019 | 1-32-08 |  | 1-13 | R3 | L987S2 | 1610 虎科和鑫一路(第二套)主保護電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1610_87UL2 | 虎科和鑫一路(1610) #2 87RY U/L | LINE161 | [5 empty] | 559 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0553 |  | 0020 | 1-32-09 |  | 1-14 | R4 | L1087S | 1620 虎科和鑫二路(第一套)主保護電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1620_87UL1 | 虎科和鑫二路(1620) #1 87RY U/L | LINE161 | [5 empty] | 560 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0554 |  | 0022 | 1-32-10 |  | 1-16 | R4 | L1087S | 1620 虎科和鑫二路(第二套)主保護電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1620_87UL2 | 虎科和鑫二路(1620) #2 87RY U/L | LINE161 | [5 empty] | 561 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | 1630 | 越港虎科紅線(1630) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0555 |  | 0023 | 1-32-11 |  | 1-17 | R5 | L1187S | 1630 越港虎科紅線主保護電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1630_87UL | 越港虎科紅線(1630) 87RY U/L | LINE161 | [5 empty] | 562 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | 1640 | 越港虎科白線(1640) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0556 |  | 0025 | 1-32-12 |  | 1-19 | R6 | L1287S | 1640 越港虎科白線主保護電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1640_87UL | 越港虎科白線(1640) 87RY U/L | LINE161 | [5 empty] | 563 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | 1570 | 虎科～虎菁一路(1570) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0557 |  | 0014 | 1-32-13 |  | 1-0E | R1 | L779S | 1570 虎科虎菁一路復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1570_79UL | 虎科虎菁一路(1570) 79RY U/L | LINE161 | [5 empty] | 564 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | 1580 | 虎科～虎菁二路(1580) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0558 |  | 0016 | 1-32-14 |  | 1-10 | R2 | L879S | 1580 虎科虎菁二路復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1580_79UL | 虎科虎菁二路(1580) 79RY U/L | LINE161 | [5 empty] | 565 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0559 |  | 0018 | 1-32-15 |  | 1-12 | R1 | L979S | 1610 虎科和鑫一路復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1610_79UL | 虎科和鑫一路(1610) 79RY U/L | LINE161 | [5 empty] | 566 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0560 |  | 0021 | 1-33-00 |  | 1-15 | R2 | L1079S | 1620 虎科和鑫二路復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1620_79UL | 虎科和鑫二路(1620) 79RY U/L | LINE161 | [5 empty] | 567 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | 1630 | 越港虎科紅線(1630) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0561 |  | 0024 | 1-33-01 |  | 1-18 | R1 | L1179S | 1630 越港虎科紅線復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1630_79UL | 越港虎科紅線(1630) 79RY U/L | LINE161 | [5 empty] | 568 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | 1640 | 越港虎科白線(1640) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0562 |  | 0026 | 1-33-02 |  | 1-1A | R2 | L1279S | 1640 越港虎科白線復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1640_79UL | 越港虎科白線(1640) 79RY U/L | LINE161 | [5 empty] | 569 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | ComPoint |  |  | 2A5Other | OSCF1_示波器故障 | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0563 |  |  | 1-33-03 |  |  | M5 | OSCA2 | OSC SYSTEM OFF LINE ALARM |  |  | B3/D13_A1 | [8 empty] | 虎科DS.161KV_OSCA_2 | 161KV示波器故障 | OTHER | [5 empty] | 570 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | ComPoint |  |  | 3A5Other | OSCF2_DC電源故障 | Element | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0564 |  |  | 1-33-04 |  |  | M5 | OSCA3 | OSC DC FAIL ALARM |  |  | B3/D13_A1 | [8 empty] | 虎科DS.161KV_OSCA_3 | 161KV示波器電源故障 | OTHER | [5 empty] | 571 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1570 | 虎科～虎菁一路(1570) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0565 |  |  | 1-33-05 |  |  | M5 | 1RYFA | 1570 RYFA |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1570_RYFA | 虎科虎菁一路(1570)數位電驛故障 | OTHER | [5 empty] | 572 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1580 | 虎科～虎菁二路(1580) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0566 |  |  | 1-33-06 |  |  | M6 | 2RYFA | 1580 RYFA |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1580_RYFA | 虎科虎菁二路(1580)數位電驛故障 | OTHER | [5 empty] | 573 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0567 |  |  | 1-33-07 |  |  | M5 | 3RYFA | 1610 RYFA |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1610_RYFA | 虎科和鑫一路(1610)數位電驛故障 | OTHER | [5 empty] | 574 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0568 |  |  | 1-33-08 |  |  | M6 | 4RYFA | 1620 RYFA |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1620_RYFA | 虎科和鑫二路(1620)數位電驛故障 | OTHER | [5 empty] | 575 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1630 | 越港虎科紅線(1630) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0569 |  |  | 1-33-09 |  |  | M5 | 5RYFA | 1630 RYFA |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1630_RYFA | 越港虎科紅線(1630)數位電驛故障 | OTHER | [5 empty] | 576 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1640 | 越港虎科白線(1640) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0570 |  |  | 1-33-10 |  |  | M6 | 6RYFA | 1640 RYFA |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1640_RYFA | 越港虎科白線(1640)數位電驛故障 | OTHER | [5 empty] | 577 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS |  |  | 2DTR | #2DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0571 |  |  | 1-33-11 |  |  | ------ | ------ | #2 DTR 86A |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#2DTR_86A | #2DTR 86(50/50N/51Z/87/96)RY | OTHER | [5 empty] | 578 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS |  |  | 2DTR | #2DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0572 |  |  | 1-33-12 |  |  | ------ | ------ | #2 DTR RYFA |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#2DTR_RYFA | #2DTR 數位電驛故障 | OTHER | [5 empty] | 579 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS |  |  | 2DTR | #2DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0573 |  |  | 1-33-13 |  |  | ------ | ------ | #2 DTR 51ZUL |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#2DTR_51ZUL | #2DTR 51Z RY U/L | OTHER | [5 empty] | 580 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS |  |  | 2DTR | #2DTR |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0574 |  |  | 1-33-14 |  |  | ------ | ------ | #2 DTR 50/51NUL |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#2DTR_50/51NUL | #2DTR 50/50N/51/51N RY U/L | OTHER | [5 empty] | 581 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS |  |  | 3DTR | #3DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0575 |  |  | 1-33-15 |  |  | ------ | ------ | #3 DTR 86A |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#3DTR_86A | #3DTR 86(50/50N/51Z/87/96)RY | OTHER | [5 empty] | 582 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS |  |  | 3DTR | #3DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0576 |  |  | 1-34-00 |  |  | ------ | ------ | #3 DTR RYFA |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#3DTR_RYFA | #3DTR 數位電驛故障 | OTHER | [5 empty] | 583 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS |  |  | 3DTR | #3DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0577 |  |  | 1-34-01 |  |  | ------ | ------ | #3 DTR 51ZUL |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#3DTR_51ZUL | #3DTR 51Z RY U/L | OTHER | [5 empty] | 584 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS |  |  | 3DTR | #3DTR |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0578 |  |  | 1-34-02 |  |  | ------ | ------ | #3 DTR 50/51NUL |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#3DTR_50/51NUL | #3DTR 50/50N/51/51N RY U/L | OTHER | [5 empty] | 585 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS |  |  | 4DTR | #4DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0579 |  |  | 1-34-03 |  |  | ------ | ------ | #4 DTR 86A |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#4DTR_86A | #4DTR 86(50/50N/51Z/87/96)RY | OTHER | [5 empty] | 586 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS |  |  | 4DTR | #4DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0580 |  |  | 1-34-04 |  |  | ------ | ------ | #4 DTR RYFA |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#4DTR_RYFA | #4DTR 數位電驛故障 | OTHER | [5 empty] | 587 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS |  |  | 4DTR | #4DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0581 |  |  | 1-34-05 |  |  | ------ | ------ | #4 DTR 51ZUL |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#4DTR_51ZUL | #4DTR 51Z RY U/L | OTHER | [5 empty] | 588 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS |  |  | 4DTR | #4DTR |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0582 |  |  | 1-34-06 |  |  | ------ | ------ | #4 DTR 50/51NUL |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#4DTR_50/51NUL | #4DTR 50/50N/51/51N RY U/L | OTHER | [5 empty] | 589 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS |  |  | 2DTR | #2DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0590 |  |  | 1-34-14 |  |  | R2 | 287S | #2 DTR 差動電驛鎖開關(使用/閉鎖) |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#2DTR_87UL | #2DTR 87RY U/L | MTR | [5 empty] | 590 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS |  |  | 3DTR | #3DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0591 |  |  | 1-34-15 |  |  | R2 | 387S | #3 DTR 差動電驛鎖開關(使用/閉鎖) |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#3DTR_87UL | #3DTR 87RY U/L | MTR | [5 empty] | 591 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS |  |  | 4DTR | #4DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0592 |  |  | 1-35-00 |  |  | R2 | 487S | #4 DTR 差動電驛鎖開關(使用/閉鎖) |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#4DTR_87UL | #4DTR 87RY U/L | MTR | [5 empty] | 592 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0593 |  | 0027 | 1-35-01 |  | 1-1B | R5 | 87B1S | 161KV #1 BUS 電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | [5 empty] | 593 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0594 |  | 0028 | 1-35-02 |  | 1-1C | R5 | 87B2S | 161KV #2 BUS 電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | [5 empty] | 594 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 0 |  | ComPoint |  |  | FDR_60A |  |  | Status | 11/22kV電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0595 |  |  | 1-35-03 |  |  | M5 | 60A | 11/23KV SC 60電驛(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.23KV_SC_60A | 11/23KV SC 60A | OTHER | [5 empty] | 595 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0596 |  |  | 1-35-04 |  |  | M6 | CBA | 161KV GIS 重故障 |  |  | B3/D13_A1 | [8 empty] | 虎科DS.161KV_CBA | 161KV斷路器重故障 | OTHER | [5 empty] | 596 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0597 |  |  | 1-35-05 |  |  | M6 | CBF | 161KV GIS 輕故障 |  |  | B3/D13_A1 | [8 empty] | 虎科DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | [5 empty] | 597 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1570 | 虎科～虎菁一路(1570) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0598 |  |  | 1-35-06 |  |  | M5 | 187CFA | 1570 虎科虎菁一路通訊頻道故障(動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1570_87CFA | 虎科虎菁一路(1570)87RY通訊故障 | OTHER | [5 empty] | 598 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1580 | 虎科～虎菁二路(1580) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0599 |  |  | 1-35-07 |  |  | M5 | 287CFA | 1580 虎科虎菁二路通訊頻道故障(動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1580_87CFA | 虎科虎菁二路(1580)87RY通訊故障 | OTHER | [5 empty] | 599 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0600 |  |  | 1-35-08 |  |  | M5 | 387CFA | 1610 虎科和鑫一路通訊頻道故障(動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1610_87CFA | 虎科和鑫一路(1610)87RY通訊故障 | OTHER | [5 empty] | 600 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0601 |  |  | 1-35-09 |  |  | M5 | 487CFA | 1620 虎科和鑫二路通訊頻道故障(動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1620_87CFA | 虎科和鑫二路(1620)87RY通訊故障 | OTHER | [5 empty] | 601 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1630 | 越港虎科紅線(1630) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0602 |  |  | 1-35-10 |  |  | M5 | 587CFA | 1630 越港虎科紅線通訊頻道故障(動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1630_87CFA | 越港虎科紅線(1630)87RY通訊故障 | OTHER | [5 empty] | 602 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1640 | 越港虎科白線(1640) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0603 |  |  | 1-35-11 |  |  | M5 | 687CFA | 1640 越港虎科白線通訊頻道故障(動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1640_87CFA | 越港虎科白線(1640)87RY通訊故障 | OTHER | [5 empty] | 603 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0610 |  |  | 1-36-02 |  |  | R5 | 50SA | 161 TIE 瞬時電驛警報 |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1500_50SA | 161KV TIE(1500) 50RY 測試/正常 | TIE | [5 empty] | 604 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Test | Test | 1 |  |  | TEST/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0613 |  |  | 1-36-05 |  |  | M5 | DCE | D.C接地警報 |  |  | ELEM/D13_A1 | [8 empty] | 虎科DS.直流電源DCE | 直流電源接地故障警報 | OTHER | [5 empty] | 605 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | ComPoint |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0614 |  |  | 1-36-06 |  |  | 直流電源盤 | DCA | 直流NFB跳脫警報 |  |  | ELEM/D13_A1 | [8 empty] | 虎科DS.直流電源DCA | 直流電源故障警報 | OTHER | [5 empty] | 606 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | StaDev | 所內設施 |  | Door1 | 電動大,小門 |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0615 |  |  | 1-36-07 |  |  | 保全控制盤 | DOR | 門禁1 (電動大,小門) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.無人化門禁(1) | 無人化門禁(1)控制室及大門 | OTHER | [5 empty] | 607 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | StaDev | 所內設施 |  | Fire1 | 受信總機 |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0616 |  |  | 1-36-08 |  |  | 火災警報(1) | FIR | 火災警報(1)受信總機 |  |  | B3/D13_A1 | [8 empty] | 虎科DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | [5 empty] | 608 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0617 |  |  | 1-36-09 |  |  | 390&490盤 | STUV | 所內變壓器欠壓警報 |  |  | ELEM/D13_A1 | [8 empty] | 虎科DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | [5 empty] | 609 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | StaDev | 所內設施 |  | Lights1 |  |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0618 |  | 0223 | 1-36-10 |  | 2-5F | 照明控制箱 | FLA | 景觀照明動作 |  |  | B3/D13_A1 | [8 empty] | 虎科DS.開關場照明(A) | 景觀照明 | OTHER | [5 empty] | 610 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
D13 | 虎科DS | 0 |  | StaDev | 所內設施 |  | MCC |  |  | Status | MCC電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0619 |  |  | 1-36-11 |  |  | ------ | MCCA | MCC IED ALARM(COMMON) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.MCCA | MCC電驛故障 | OTHER | [5 empty] | 611 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | StaDev | 所內設施 |  | PMCC |  |  | Status | PMCC電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0620 |  |  | 1-36-12 |  |  | ------ | PMCCA | PMCC IED ALARM(COMMON) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.PMCCA | PMCC電驛故障 | OTHER | [5 empty] | 612 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0621 |  |  | 1-36-13 |  |  | 通訊盤 | ACF | 通訊設備AC故障 |  |  | B3/D13_A1 | [8 empty] | 虎科DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | [5 empty] | 613 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | StaDev | 所內設施 |  | R_Temp | 通訊室或控制室 |  | Status | 溫度警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0622 |  |  | 1-36-14 |  |  | 通訊盤 | ------ | 通訊室或控制室溫控警報 |  |  | B3/D13_A1 | [8 empty] | 虎科DS.通信機房溫度 | 通信室或控制室溫度警報 | OTHER | [5 empty] | 614 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0625 |  |  | 1-37-01 |  |  | M5 | UVA1 | 一號匯流排欠壓電驛(動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | [5 empty] | 615 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0626 |  |  | 1-37-02 |  |  | M5 | UVA2 | 二號匯流排欠壓電驛(動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | [5 empty] | 616 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | StaDev | 所內設施 |  | Water1 |  |  | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0627 |  |  | 1-37-03 |  |  | M5 | WP-1 | 地下室淹水警報(第一段) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.水位警報(1) | 地下室水位警報(1) | OTHER | [5 empty] | 617 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | StaDev | 所內設施 |  | Water2 |  |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0628 |  |  | 1-37-04 |  |  | M5 | WP-2 | 地下室淹水警報(第二段) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.水位警報(2) | 地下室水位警報(2) | OTHER | [5 empty] | 618 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0629 |  | 0228 | 1-37-05 |  | 2-64 | ACBS1 | ACB1 | 所內電源ACB1 |  |  | B3/D13_A1 | [8 empty] | 虎科DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | [5 empty] | 619 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D13 | 虎科DS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0630 |  | 0229 | 1-37-06 |  | 2-65 | ACBS2 | ACB2 | 所內電源ACB2 |  |  | B3/D13_A1 | [8 empty] | 虎科DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | [5 empty] | 620 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D13 | 虎科DS | 0 |  | StaDev | 所內設施 |  | ACBT |  |  | Status | 所內電源ACB TIE | Close/Open | Y | 3 | DI-SP | [6 empty] | 0631 |  | 0230 | 1-37-07 |  | 2-66 | ACBS3 | ACB TIE | 所內電源ACB TIE |  |  | B3/D13_A1 | [8 empty] | 虎科DS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | [5 empty] | 621 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ON/OFF | OFF
D13 | 虎科DS | 0 |  | StaDev | 所內設施 |  | SCADAA |  |  | Status | LocalSCADA故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0632 |  |  | 1-37-08 |  |  | 監控主機 | SUPA | 所內SCADA故障 |  |  | B3/D13_A1 | [8 empty] | 虎科DS.SCADA故障 | 變電所SCADA故障 | OTHER | [5 empty] | 622 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | StaDev | 所內設施 |  | Comm_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0633 |  |  | 1-37-09 |  |  | 通訊處理單元 | COMMRL | 通訊處理單元LOCAL/REMOTE |  |  | B3/D13_A1 | [8 empty] | 虎科DS.COMM_S/L | 通訊處理單元 SUPY/LOCAL | OTHER | [5 empty] | 623 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
D13 | 虎科DS | 0 |  | ComPoint |  |  | PMCC_R_L | MCC_R_L | Element | Status | PMCC Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0634 |  |  | 1-37-10 |  |  | ------ | MCCRL | MCC IED LOCAL/REMOTE |  |  | B3/D13_A1 | [8 empty] | 虎科DS.MCC_IED_S/L | 161KV IED SUPY/LOCAL | OTHER | [5 empty] | 624 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
D13 | 虎科DS | 0 |  | StaDev | 所內設施 |  | PMCC_R_L |  |  | Status | PMCC Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0635 |  |  | 1-37-11 |  |  | ------ | PMCCRL | PMCC IED LOCAL/REMOTE |  |  | B3/D13_A1 | [8 empty] | 虎科DS.PMCC_IED_S/L | 11/23KV IED SUPY/LOCAL | OTHER | [5 empty] | 625 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
D13 | 虎科DS | 0 |  | ComPoint |  |  | FDR_CBA |  |  | Status | 11/22kV斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0636 |  |  | 1-37-12 |  |  | ------ | 22 CBA | 11 & 23KV GIS 重故障 |  |  | ELEM/D13_D1 | [8 empty] | 虎科DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | [5 empty] | 626 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | ComPoint |  |  | FDR_CBF |  |  | Status | 11/22kV斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0637 |  |  | 1-37-13 |  |  | ------ | 22 CBF | 11 & 23KV GIS 輕故障 |  |  | ELEM/D13_D1 | [8 empty] | 虎科DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | [5 empty] | 627 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | ComPoint |  |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0638 |  |  | 1-37-14 |  |  | ------ | LOA | 11 & 23KV饋線復閉失敗閉鎖警報(動作/正常) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.11/23KV_LOA | 11/23KV饋線復閉失敗閉鎖 | OTHER | [5 empty] | 628 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0639 |  |  | 1-37-15 |  |  | ------ | ACBA | 所內AC電源用ACB(故障警報) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.所內電源ACBA | 所內電源故障警報 | OTHER | [5 empty] | 629 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | StaDev | 所內設施 |  | OilLeak1 |  |  | Status | 洩油池水位警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0640 |  |  | 1-38-00 |  |  | M5 | OW-1 | 集油池警報(第一段) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.集油池警報(1) | 集油池水位警報(1) | OTHER | [5 empty] | 630 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | StaDev | 所內設施 |  | OilLeak2 |  |  | Status | 洩油池水位警報2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0641 |  |  | 1-38-01 |  |  | M5 | OW-2 | 集油池警報(第二段) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.集油池警報(2) | 集油池水位警報(2) | OTHER | [5 empty] | 631 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | StaDev | 所內設施 |  | 4A5Other | 專線數據機電源故障 | Element | Status | 警報等級5動作4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0642 |  |  | 1-38-02 |  |  | MCC-1A | RX/TX | 專線數據機電源故障警報點 |  |  | B3/D13_A1 | [8 empty] | 虎科DS.MODEMA | MODEM POWER FAIL故障 | OTHER | [5 empty] | 632 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | StaDev | 所內設施 |  | Lights2 |  |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0643 |  | 0227 | 1-38-03 |  | 2-63 | 照明控制箱 | FLB | 路燈照明動作 |  |  | B3/D13_A1 | [8 empty] | 虎科DS.開關場照明(B) | 路燈照明 | OTHER | [5 empty] | 633 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
D13 | 虎科DS | 0 |  | StaDev | 所內設施 |  | Door2 | 變電所門禁 |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0644 |  |  | 1-38-04 |  |  | ------ | ------ | 門禁2 (變電所門禁) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.無人化門禁(2) | 無人化門禁(2)建築物大小門 | OTHER | [5 empty] | 634 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | StaDev | 所內設施 |  | Door3 | 保全系統 |  | Status | 無人化門禁3 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0645 |  |  | 1-38-05 |  |  | ------ | ------ | 門禁3 (保全系統) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | [5 empty] | 635 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | ComPoint |  |  | 12B_CTFA | BUS_87CTFA | Element | Status | #1#2 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0646 |  |  | 1-38-06 |  |  | M7 | CTFA | 161kV 匯流排差流電驛CT迴路故障警報 |  |  | B3/D13_A1 | [8 empty] | 虎科DS.161KV_BUS_CTFA | 161KV BUS CT 回路故障 | OTHER | [5 empty] | 636 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | ComPoint |  |  | BUS_RYFA |  |  | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0647 |  |  | 1-38-07 |  |  | M7 | RYFA | 161kV 匯流排數位電驛故障警報 |  |  | B3/D13_A1 | [8 empty] | 虎科DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | [5 empty] | 637 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | StaDev | 所內設施 |  | GEN | 緊急發電機運轉 | Element | Status | 警報等級5動作5 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0648 |  |  | 1-38-08 |  |  | ------ | ------ | 緊急發電機運轉 |  |  | B3/D13_A1 | [8 empty] | 虎科DS.GEN | 緊急發電機運轉 | OTHER | [5 empty] | 638 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | OFF/ON | OFF
D13 | 虎科DS | 11 | 11kV | XO31 | 科十一線(XO31) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0653 |  | 0130 | 1-38-13 |  | 2-02 | XO31 | 79S | XO31復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO31_79UL | 11KV科11線(XO31) 79RY U/L | FEEDER | [5 empty] | 639 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 11 | 11kV | XO31 | 科十一線(XO31) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0654 |  | 0131 | 1-38-14 |  | 2-03 | XO31 | TAPS | XO31 LCO TAP (使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO31_LCO_TAP | 11KV科11線(XO31) LCO TAP | FEEDER | [5 empty] | 640 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D13 | 虎科DS | 11 | 11kV | XO32 | 科十二線(XO32) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0655 |  | 0133 | 1-38-15 |  | 2-05 | XO32 | 79S | XO32復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO32_79UL | 11KV科12線(XO32) 79RY U/L | FEEDER | [5 empty] | 641 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 11 | 11kV | XO32 | 科十二線(XO32) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0656 |  | 0134 | 1-39-00 |  | 2-06 | XO32 | TAPS | XO32 LCO TAP (使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO32_LCO_TAP | 11KV科12線(XO32) LCO TAP | FEEDER | [5 empty] | 642 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D13 | 虎科DS | 11 | 11kV | XO33 | 科十三線(XO33) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0657 |  | 0136 | 1-39-01 |  | 2-08 | XO33 | 79S | XO33復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO33_79UL | 11KV科13線(XO33) 79RY U/L | FEEDER | [5 empty] | 643 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 11 | 11kV | XO33 | 科十三線(XO33) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0658 |  | 0137 | 1-39-02 |  | 2-09 | XO33 | TAPS | XO33 LCO TAP (使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO33_LCO_TAP | 11KV科13線(XO33) LCO TAP | FEEDER | [5 empty] | 644 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D13 | 虎科DS | 11 | 11kV | XO34 | 科十四線(XO34) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0659 |  | 0139 | 1-39-03 |  | 2-0B | XO34 | 79S | XO34復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO34_79UL | 11KV科14線(XO34) 79RY U/L | FEEDER | [5 empty] | 645 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 11 | 11kV | XO34 | 科十四線(XO34) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0660 |  | 0140 | 1-39-04 |  | 2-0C | XO34 | TAPS | XO34 LCO TAP (使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO34_LCO_TAP | 11KV科14線(XO34) LCO TAP | FEEDER | [5 empty] | 646 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D13 | 虎科DS | 11 | 11kV | XO35 | 科十五線(XO35) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0661 |  | 0142 | 1-39-05 |  | 2-0E | XO35 | 79S | XO35復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO35_79UL | 11KV科15線(XO35) 79RY U/L | FEEDER | [5 empty] | 647 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 11 | 11kV | XO35 | 科十五線(XO35) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0662 |  | 0143 | 1-39-06 |  | 2-0F | XO35 | TAPS | XO35 LCO TAP (使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO35_LCO_TAP | 11KV科15線(XO35) LCO TAP | FEEDER | [5 empty] | 648 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D13 | 虎科DS | 11 | 11kV | XO36 | 科十六線(XO36) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0663 |  | 0148 | 1-39-07 |  | 2-14 | XO31 | 79S | XO36復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO36_79UL | 11KV科16線(XO36) 79RY U/L | FEEDER | [5 empty] | 649 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 11 | 11kV | XO36 | 科十六線(XO36) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0664 |  | 0149 | 1-39-08 |  | 2-15 | XO36 | TAPS | XO36 LCO TAP (使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO36_LCO_TAP | 11KV科16線(XO36) LCO TAP | FEEDER | [5 empty] | 650 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D13 | 虎科DS | 11 | 11kV | XO37 | 科十七線(XO37) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0665 |  | 0151 | 1-39-09 |  | 2-17 | XO37 | 79S | XO37復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO37_79UL | 11KV科17線(XO37) 79RY U/L | FEEDER | [5 empty] | 651 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 11 | 11kV | XO37 | 科十七線(XO37) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0666 |  | 0152 | 1-39-10 |  | 2-18 | XO37 | TAPS | XO37 LCO TAP (使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO37_LCO_TAP | 11KV科17線(XO37) LCO TAP | FEEDER | [5 empty] | 652 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D13 | 虎科DS | 11 | 11kV | XO38 | 科十八線(XO38) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0667 |  | 0154 | 1-39-11 |  | 2-1A | XO38 | 79S | XO38復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO38_79UL | 11KV科18線(XO38) 79RY U/L | FEEDER | [5 empty] | 653 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 11 | 11kV | XO38 | 科十八線(XO38) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0668 |  | 0155 | 1-39-12 |  | 2-1B | XO38 | TAPS | XO38 LCO TAP (使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO38_LCO_TAP | 11KV科18線(XO38) LCO TAP | FEEDER | [5 empty] | 654 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D13 | 虎科DS | 11 | 11kV | XO39 | 科十九線(XO39) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0669 |  | 0157 | 1-39-13 |  | 2-1D | XO39 | 79S | XO39復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO39_79UL | 11KV科19線(XO39) 79RY U/L | FEEDER | [5 empty] | 655 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 11 | 11kV | XO39 | 科十九線(XO39) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0670 |  | 0158 | 1-39-14 |  | 2-1E | XO39 | TAPS | XO39 LCO TAP (使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO39_LCO_TAP | 11KV科19線(XO39) LCO TAP | FEEDER | [5 empty] | 656 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D13 | 虎科DS | 11 | 11kV | XO40 | 科二十線(XO40) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0671 |  | 0160 | 1-39-15 |  | 2-20 | XO40 | 79S | XO40復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO40_79UL | 11KV科20線(XO40) 79RY U/L | FEEDER | [5 empty] | 657 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 11 | 11kV | XO40 | 科二十線(XO40) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0672 |  | 0161 | 1-3A-00 |  | 2-21 | XO40 | TAPS | XO40 LCO TAP (使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO40_LCO_TAP | 11KV科20線(XO40) LCO TAP | FEEDER | [5 empty] | 658 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D13 | 虎科DS | 22 | 22kV | XO61 | 科六一線(XO61) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0673 |  | 0166 | 1-3A-01 |  | 2-26 | XO61 | 79S | XO61復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO61_79UL | 23KV科61線(XO61) 79RY U/L | FEEDER | [5 empty] | 659 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 22 | 22kV | XO61 | 科六一線(XO61) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0674 |  | 0167 | 1-3A-02 |  | 2-27 | XO61 | TAPS | XO61 LCO TAP (使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO61_LCO_TAP | 23KV科61線(XO61) LCO TAP | FEEDER | [5 empty] | 660 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D13 | 虎科DS | 22 | 22kV | XO62 | 科六二線(XO62) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0675 |  | 0169 | 1-3A-03 |  | 2-29 | XO62 | 79S | XO62復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO62_79UL | 23KV科62線(XO62) 79RY U/L | FEEDER | [5 empty] | 661 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 22 | 22kV | XO62 | 科六二線(XO62) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0676 |  | 0170 | 1-3A-04 |  | 2-2A | XO62 | TAPS | XO62 LCO TAP (使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO62_LCO_TAP | 23KV科62線(XO62) LCO TAP | FEEDER | [5 empty] | 662 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D13 | 虎科DS | 22 | 22kV | XO63 | 科六三線(XO63) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0677 |  | 0172 | 1-3A-05 |  | 2-2C | XO63 | 79S | XO63復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO63_79UL | 23KV科63線(XO63) 79RY U/L | FEEDER | [5 empty] | 663 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 22 | 22kV | XO63 | 科六三線(XO63) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0678 |  | 0173 | 1-3A-06 |  | 2-2D | XO63 | TAPS | XO63 LCO TAP (使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO63_LCO_TAP | 23KV科63線(XO63) LCO TAP | FEEDER | [5 empty] | 664 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D13 | 虎科DS | 22 | 22kV | XO64 | 科六四線(XO64) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0679 |  | 0175 | 1-3A-07 |  | 2-2F | XO64 | 79S | XO64復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO64_79UL | 23KV科64線(XO64) 79RY U/L | FEEDER | [5 empty] | 665 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 22 | 22kV | XO64 | 科六四線(XO64) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0680 |  | 0176 | 1-3A-08 |  | 2-30 | XO64 | TAPS | XO64 LCO TAP (使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO64_LCO_TAP | 23KV科64線(XO64) LCO TAP | FEEDER | [5 empty] | 666 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D13 | 虎科DS | 22 | 22kV | XO65 | 科六五線(XO65) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0681 |  | 0180 | 1-3A-09 |  | 2-34 | XO65 | 79S | XO65復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO65_79UL | 23KV科65線(XO65) 79RY U/L | FEEDER | [5 empty] | 667 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 22 | 22kV | XO65 | 科六五線(XO65) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0682 |  | 0181 | 1-3A-10 |  | 2-35 | XO65 | TAPS | XO65 LCO TAP (使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO65_LCO_TAP | 23KV科65線(XO65) LCO TAP | FEEDER | [5 empty] | 668 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D13 | 虎科DS | 22 | 22kV | XO66 | 科六六線(XO66) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0683 |  | 0183 | 1-3A-11 |  | 2-37 | XO66 | 79S | XO66復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO66_79UL | 23KV科66線(XO66) 79RY U/L | FEEDER | [5 empty] | 669 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 22 | 22kV | XO66 | 科六六線(XO66) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0684 |  | 0184 | 1-3A-12 |  | 2-38 | XO66 | TAPS | XO66 LCO TAP (使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO66_LCO_TAP | 23KV科66線(XO66) LCO TAP | FEEDER | [5 empty] | 670 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D13 | 虎科DS | 22 | 22kV | XO67 | 科六七線(XO67) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0685 |  | 0186 | 1-3A-13 |  | 2-3A | XO67 | 79S | XO67復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO67_79UL | 23KV科67線(XO67) 79RY U/L | FEEDER | [5 empty] | 671 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 22 | 22kV | XO67 | 科六七線(XO67) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0686 |  | 0187 | 1-3A-14 |  | 2-3B | XO67 | TAPS | XO67 LCO TAP (使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO67_LCO_TAP | 23KV科67線(XO67) LCO TAP | FEEDER | [5 empty] | 672 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D13 | 虎科DS | 22 | 22kV | XO68 | 科六八線(XO68) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0687 |  | 0189 | 1-3A-15 |  | 2-3D | XO68 | 79S | XO68復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO68_79UL | 23KV科68線(XO68) 79RY U/L | FEEDER | [5 empty] | 673 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 22 | 22kV | XO68 | 科六八線(XO68) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0688 |  | 0190 | 1-3B-00 |  | 2-3E | XO68 | TAPS | XO68 LCO TAP (使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO68_LCO_TAP | 23KV科68線(XO68) LCO TAP | FEEDER | [5 empty] | 674 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D13 | 虎科DS | 22 | 22kV | XO71 | 科七一線(XO71) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0689 |  | 0195 | 1-3B-01 |  | 2-43 | XO71 | 79S | XO71復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO71_79UL | 23KV科71線(XO71) 79RY U/L | FEEDER | [5 empty] | 675 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 22 | 22kV | XO71 | 科七一線(XO71) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0690 |  | 0196 | 1-3B-02 |  | 2-44 | XO71 | TAPS | XO71 LCO TAP (使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO71_LCO_TAP | 23KV科71線(XO71) LCO TAP | FEEDER | [5 empty] | 676 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D13 | 虎科DS | 22 | 22kV | XO72 | 科七二線(XO72) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0691 |  | 0198 | 1-3B-03 |  | 2-46 | XO72 | 79S | XO72復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO72_79UL | 23KV科72線(XO72) 79RY U/L | FEEDER | [5 empty] | 677 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 22 | 22kV | XO72 | 科七二線(XO72) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0692 |  | 0199 | 1-3B-04 |  | 2-47 | XO72 | TAPS | XO72 LCO TAP (使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO72_LCO_TAP | 23KV科72線(XO72) LCO TAP | FEEDER | [5 empty] | 678 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D13 | 虎科DS | 22 | 22kV | XO73 | 科七三線(XO73) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0693 |  | 0201 | 1-3B-05 |  | 2-49 | XO73 | 79S | XO73復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO73_79UL | 23KV科73線(XO73) 79RY U/L | FEEDER | [5 empty] | 679 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 22 | 22kV | XO73 | 科七三線(XO73) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0694 |  | 0202 | 1-3B-06 |  | 2-4A | XO73 | TAPS | XO73 LCO TAP (使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO73_LCO_TAP | 23KV科73線(XO73) LCO TAP | FEEDER | [5 empty] | 680 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D13 | 虎科DS | 22 | 22kV | XO74 | 科七四線(XO74) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0695 |  | 0204 | 1-3B-07 |  | 2-4C | XO74 | 79S | XO74復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO74_79UL | 23KV科74線(XO74) 79RY U/L | FEEDER | [5 empty] | 681 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 22 | 22kV | XO74 | 科七四線(XO74) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0696 |  | 0205 | 1-3B-08 |  | 2-4D | XO74 | TAPS | XO74 LCO TAP (使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO74_LCO_TAP | 23KV科74線(XO74) LCO TAP | FEEDER | [5 empty] | 682 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D13 | 虎科DS | 22 | 22kV | XO75 | 科七五線(XO75) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0697 |  | 0211 | 1-3B-09 |  | 2-53 | XO75 | 79S | XO75復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO75_79UL | 23KV科75線(XO75) 79RY U/L | FEEDER | [5 empty] | 683 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 22 | 22kV | XO75 | 科七五線(XO75) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0698 |  | 0212 | 1-3B-10 |  | 2-54 | XO75 | TAPS | XO75 LCO TAP (使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO75_LCO_TAP | 23KV科75線(XO75) LCO TAP | FEEDER | [5 empty] | 684 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D13 | 虎科DS | 22 | 22kV | XO76 | 科七六線(XO76) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0699 |  | 0214 | 1-3B-11 |  | 2-56 | XO76 | 79S | XO76復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO76_79UL | 23KV科76線(XO76) 79RY U/L | FEEDER | [5 empty] | 685 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 22 | 22kV | XO76 | 科七六線(XO76) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0700 |  | 0215 | 1-3B-12 |  | 2-57 | XO76 | TAPS | XO76 LCO TAP (使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO76_LCO_TAP | 23KV科76線(XO76) LCO TAP | FEEDER | [5 empty] | 686 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D13 | 虎科DS | 22 | 22kV | XO77 | 科七七線(XO77) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0701 |  | 0217 | 1-3B-13 |  | 2-59 | XO77 | 79S | XO77復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO77_79UL | 23KV科77線(XO77) 79RY U/L | FEEDER | [5 empty] | 687 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 22 | 22kV | XO77 | 科七七線(XO77) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0702 |  | 0218 | 1-3B-14 |  | 2-5A | XO77 | TAPS | XO77 LCO TAP (使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO77_LCO_TAP | 23KV科77線(XO77) LCO TAP | FEEDER | [5 empty] | 688 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D13 | 虎科DS | 22 | 22kV | XO78 | 科七八線(XO78) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0703 |  | 0220 | 1-3B-15 |  | 2-5C | XO78 | 79S | XO78復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO78_79UL | 23KV科78線(XO78) 79RY U/L | FEEDER | [5 empty] | 689 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 22 | 22kV | XO78 | 科七八線(XO78) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0704 |  | 0221 | 1-3C-00 |  | 2-5D | XO78 | TAPS | XO78 LCO TAP (使用/閉鎖) |  |  | B2/D13_D1 | [8 empty] | 虎科DS.XO78_LCO_TAP | 23KV科78線(XO78) LCO TAP | FEEDER | [5 empty] | 690 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D13 | 虎科DS | 0 |  | StaDev | 所內設施 |  | TCA | 斷路器跳脫迴路故障 | Element | Status | 警報等級5動作6 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0705 |  |  | 1-3C-01 |  |  | ------ | TCSA | 161/23/11 TCSA(動作/正常)(COMMON) |  |  | B3/D13_A1 | [8 empty] | 虎科DS.TCA | 斷路器跳脫回路故障 | OTHER | [5 empty] | 691 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1960 | #2SHR(1960) |  | 96B1 |  | B3 | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0706 |  |  | 1-3C-02 |  |  | M6 | 96B1 | 161kV #2SH.R. 96B1撲氣電驛第一段警報 (動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.161#2SHR_96B1 | 161KV #2SHR 96B1 RY | OTHER | [5 empty] | 692 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1960 | #2SHR(1960) |  | 96B2 |  | B3 | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0707 |  |  | 1-3C-03 |  |  | M6 | 96B2 | 161kV #2SH.R. 96B2 撲氣電驛第二段警報 (動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.161#2SHR_96B2 | 161KV #2SHR 96B2 RY | OTHER | [5 empty] | 693 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1960 | #2SHR(1960) |  | 96D |  | B3 | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0708 |  |  | 1-3C-04 |  |  | M6 | 96D | 161kV #2SH.R. 96D 放壓電驛警報 (動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.161#2SHR_96D | 161KV #2SHR 96D RY | OTHER | [5 empty] | 694 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1960 | #2SHR(1960) |  | 96P |  | B3 | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0709 |  |  | 1-3C-05 |  |  | M6 | 96P | 161kV #2SH.R. 96P 衝擊油壓電驛警報 (動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.161#2SHR_96P | 161KV #2SHR 96P RY | OTHER | [5 empty] | 695 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1960 | #2SHR(1960) |  | SHRF |  | B3 | Status | 電抗器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0710 |  |  | 1-3C-06 |  |  | M6 | SRF | 161kV #2SH.R. 輕故障警報 (動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.161#2SHR_SRF | 161KV #2SHR 輕故障 | OTHER | [5 empty] | 696 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1960 | #2SHR(1960) |  | SHRA |  | B3 | Status | 電抗器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0711 |  |  | 1-3C-07 |  |  | M6 | SRA | 161kV #2SH.R. 重故障警報 (動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.161#2SHR_SRA | 161KV #2SHR 重故障 | OTHER | [5 empty] | 697 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1960 | #2SHR(1960) |  | 1_87UL1 |  | B3 | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0712 |  | 0030 | 1-3C-08 |  | 1-1E | R6 | 87R1S | 161kV #2 SH.R. 第一套差動電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.161#2SHR_87UL1 | 161KV #2SHR #1 87RY U/L | OTHER | [5 empty] | 698 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | 1960 | #2SHR(1960) |  | 1_87UL2 |  | B3 | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0713 |  | 0031 | 1-3C-09 |  | 1-1F | R6 | 87R2S | 161kV #2 SH.R. 第二套差動電驛閉鎖開關(使用/閉鎖) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.161#2SHR_87UL2 | 161KV #2SHR #2 87RY U/L | OTHER | [5 empty] | 699 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | 1960 | #2SHR(1960) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0714 |  |  | 1-3C-10 |  |  | M8 | RYFA | 161kV #2 SH.R. 差動電驛故障 (動作/正常) |  |  | B2/D13_A1 | [8 empty] | 虎科DS.161#2SHR_RYFA | 161KV 2SHR(1960)數位電驛故障 | OTHER | [5 empty] | 700 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0768 | 769 | 0052 | 2-30-00 | 2-30-01 | 1-34 | GB1 | DS (ON) | 1501 DS ON |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1501_DS | 1501(TIE) DS | TIE | [5 empty] | 701 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0770 | 771 | 0053 | 2-30-02 | 2-30-03 | 1-35 | GB1 | DS (ON) | 1502 DS ON |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1502_DS | 1502(TIE) DS | TIE | [5 empty] | 702 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 161 | 161kV | 1570 | 虎科～虎菁一路(1570) |  | DS1 | 1571 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0772 | 773 | 0055 | 2-30-04 | 2-30-05 | 1-37 | GL7 | DS (ON) | 1571 DS ON |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1571_DS | 1571(虎科虎菁一路) DS | LINE161 | [5 empty] | 703 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 161 | 161kV | 1570 | 虎科～虎菁一路(1570) |  | DS2 | 1572 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0774 | 775 | 0056 | 2-30-06 | 2-30-07 | 1-38 | GL7 | DS (ON) | 1572 DS ON |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1572_DS | 1572(虎科虎菁一路) DS | LINE161 | [5 empty] | 704 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D13 | 虎科DS | 161 | 161kV | 1570 | 虎科～虎菁一路(1570) |  | DS3 | 1573 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0776 | 777 | 0057 | 2-30-08 | 2-30-09 | 1-39 | GL7 | DS (ON) | 1573 DS ON |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1573_DS | 1573(虎科虎菁一路) DS | LINE161 | [5 empty] | 705 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 161 | 161kV | 1570 | 虎科～虎菁一路(1570) |  | ES3 | 1573E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0778 | 779 | 0058 | 2-30-10 | 2-30-11 | 1-3A | GL7 | ES (ON) | 1573E ES ON |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1573E_ES | 1573E(虎科虎菁一路) ES | LINE161 | [5 empty] | 706 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D13 | 虎科DS | 161 | 161kV | 1580 | 虎科～虎菁二路(1580) |  | DS1 | 1581 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0780 | 781 | 0060 | 2-30-12 | 2-30-13 | 1-3C | GL8 | DS (ON) | 1581 DS ON |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1581_DS | 1581(虎科虎菁二路) DS | LINE161 | [5 empty] | 707 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D13 | 虎科DS | 161 | 161kV | 1580 | 虎科～虎菁二路(1580) |  | DS2 | 1582 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0782 | 783 | 0061 | 2-30-14 | 2-30-15 | 1-3D | GL8 | DS (ON) | 1582 DS ON |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1582_DS | 1582(虎科虎菁二路) DS | LINE161 | [5 empty] | 708 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 161 | 161kV | 1580 | 虎科～虎菁二路(1580) |  | DS3 | 1583 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0784 | 785 | 0062 | 2-31-00 | 2-31-01 | 1-3E | GL8 | DS (ON) | 1583 DS ON |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1583_DS | 1583(虎科虎菁二路) DS | LINE161 | [5 empty] | 709 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 161 | 161kV | 1580 | 虎科～虎菁二路(1580) |  | ES3 | 1583E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0786 | 787 | 0063 | 2-31-02 | 2-31-03 | 1-3F | GL8 | ES (ON) | 1583E ES ON |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1583E_ES | 1583E(虎科虎菁二路) ES | LINE161 | [5 empty] | 710 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | DS1 | 1611 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0788 | 789 | 0065 | 2-31-04 | 2-31-05 | 1-41 | GL9 | DS (ON) | 1611 DS ON |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1611_DS | 1611(虎科和鑫一路) DS | LINE161 | [5 empty] | 711 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | DS2 | 1612 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0790 | 791 | 0066 | 2-31-06 | 2-31-07 | 1-42 | GL9 | DS (ON) | 1612 DS ON |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1612_DS | 1612(虎科和鑫一路) DS | LINE161 | [5 empty] | 712 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | DS3 | 1613 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0792 | 793 | 0067 | 2-31-08 | 2-31-09 | 1-43 | GL9 | DS (ON) | 1613 DS ON |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1613_DS | 1613(虎科和鑫一路) DS | LINE161 | [5 empty] | 713 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | ES3 | 1613E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0794 | 795 | 0068 | 2-31-10 | 2-31-11 | 1-44 | GL9 | ES (ON) | 1613E ES ON |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1613E_ES | 1613E(虎科和鑫一路) ES | LINE161 | [5 empty] | 714 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | DS1 | 1621 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0796 | 797 | 0070 | 2-31-12 | 2-31-13 | 1-46 | GL10 | DS (ON) | 1621 DS ON |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1621_DS | 1621(虎科和鑫二路) DS | LINE161 | [5 empty] | 715 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | DS2 | 1622 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0798 | 799 | 0071 | 2-31-14 | 2-31-15 | 1-47 | GL10 | DS (ON) | 1622 DS ON |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1622_DS | 1622(虎科和鑫二路) DS | LINE161 | [5 empty] | 716 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | DS3 | 1623 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0800 | 801 | 0072 | 2-32-00 | 2-32-01 | 1-48 | GL10 | DS (ON) | 1623 DS ON |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1623_DS | 1623(虎科和鑫二路) DS | LINE161 | [5 empty] | 717 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | ES3 | 1623E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0802 | 803 | 0073 | 2-32-02 | 2-32-03 | 1-49 | GL10 | ES (ON) | 1623E ES ON |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1623E_ES | 1623E(虎科和鑫二路) ES | LINE161 | [5 empty] | 718 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D13 | 虎科DS | 161 | 161kV | 1630 | 越港虎科紅線(1630) |  | DS1 | 1631 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0804 | 805 | 0075 | 2-32-04 | 2-32-05 | 1-4B | GL11 | DS (ON) | 1631 DS ON |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1631_DS | 1631(越港虎科紅線) DS | LINE161 | [5 empty] | 719 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 161 | 161kV | 1630 | 越港虎科紅線(1630) |  | DS2 | 1632 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0806 | 807 | 0076 | 2-32-06 | 2-32-07 | 1-4C | GL11 | DS (ON) | 1632 DS ON |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1632_DS | 1632(越港虎科紅線) DS | LINE161 | [5 empty] | 720 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D13 | 虎科DS | 161 | 161kV | 1630 | 越港虎科紅線(1630) |  | DS3 | 1633 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0808 | 809 | 0077 | 2-32-08 | 2-32-09 | 1-4D | GL11 | DS (ON) | 1633 DS ON |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1633_DS | 1633(越港虎科紅線) DS | LINE161 | [5 empty] | 721 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 161 | 161kV | 1630 | 越港虎科紅線(1630) |  | ES3 | 1633E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0810 | 811 | 0078 | 2-32-10 | 2-32-11 | 1-4E | GL11 | ES (ON) | 1633E ES ON |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1633E_ES | 1633E(越港虎科紅線) ES | LINE161 | [5 empty] | 722 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D13 | 虎科DS | 161 | 161kV | 1640 | 越港虎科白線(1640) |  | DS1 | 1641 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0812 | 813 | 0080 | 2-32-12 | 2-32-13 | 1-50 | GL12 | DS (ON) | 1641 DS ON |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1641_DS | 1641(越港虎科白線) DS | LINE161 | [5 empty] | 723 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D13 | 虎科DS | 161 | 161kV | 1640 | 越港虎科白線(1640) |  | DS2 | 1642 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0814 | 815 | 0081 | 2-32-14 | 2-32-15 | 1-51 | GL12 | DS (ON) | 1642 DS ON |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1642_DS | 1642(越港虎科白線) DS | LINE161 | [5 empty] | 724 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 161 | 161kV | 1640 | 越港虎科白線(1640) |  | DS3 | 1643 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0816 | 817 | 0082 | 2-33-00 | 2-33-01 | 1-52 | GL12 | DS (ON) | 1643 DS ON |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1643_DS | 1643(越港虎科白線) DS | LINE161 | [5 empty] | 725 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 161 | 161kV | 1640 | 越港虎科白線(1640) |  | ES3 | 1643E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0818 | 819 | 0083 | 2-33-02 | 2-33-03 | 1-53 | GL12 | ES (ON) | 1643E ES ON |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1643E_ES | 1643E(越港虎科白線) ES | LINE161 | [5 empty] | 726 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D13 | 虎科DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0868 | 869 | 0115 | 2-36-04 | 2-36-05 | 1-73 | GT2 | DS (ON) | 1761 DS ON |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1761_DS | 1761(#2DTR) DS | MTR | [5 empty] | 727 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D13 | 虎科DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0870 | 871 | 0116 | 2-36-06 | 2-36-07 | 1-74 | GT2 | DS (ON) | 1762 DS ON |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1762_DS | 1762(#2DTR) DS | MTR | [5 empty] | 728 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0872 | 873 | 0118 | 2-36-08 | 2-36-09 | 1-76 | GT3 | DS (ON) | 1771 DS ON |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1771_DS | 1771(#3DTR) DS | MTR | [5 empty] | 729 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0874 | 875 | 0119 | 2-36-10 | 2-36-11 | 1-77 | GT3 | DS (ON) | 1772 DS ON |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1772_DS | 1772(#3DTR) DS | MTR | [5 empty] | 730 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D13 | 虎科DS | 161 | 161kV | 1780 | #4DTR(1780) |  | DS1 | 1781 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0876 | 877 | 0121 | 2-36-12 | 2-36-13 | 1-79 | GT4 | DS (ON) | 1781 DS ON |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1781_DS | 1781(#4DTR) DS | MTR | [5 empty] | 731 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D13 | 虎科DS | 161 | 161kV | 1780 | #4DTR(1780) |  | DS2 | 1782 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0878 | 879 | 0122 | 2-36-14 | 2-36-15 | 1-7A | GT4 | DS (ON) | 1782 DS ON |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1782_DS | 1782(#4DTR) DS | MTR | [5 empty] | 732 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 11 | 11kV | LBS230 | #3SC(230) |  | LBS |  | Element | Status | 警報等級5動作9 | Normal/Alarm | Y | 5 | DI-SP |  | Bay1BbLBS | A/230 | C/3SC(B) |  |  | 0880 | 881 | 0225 | 2-37-00 | 2-37-01 | 2-61 | 230 | LBS(ON) | 230 LBS ON |  |  | B3/D13_A1 | [8 empty] | 虎科DS.230_LBS | 230(11KV #3SC) LBS | SC | [5 empty] | 733 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm |  | 2 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 11 | 11kV | LBS240 | #4SC(240) |  | LBS |  | Element | [7 empty] | Bay1BbLBS | A/240 | C/4SC(B) |  |  | 0882 | 883 | 0226 | 2-37-02 | 2-37-03 | 2-62 | 240 | LBS(ON) | 240 LBS ON |  |  | B3/D13_A1 | [8 empty] | 虎科DS.240_LBS | 240(11KV #4SC) LBS | SC | [5 empty] | 734 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 161 | 161kV | 1960 | #2SHR(1960) |  | DS1 | 1961 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0884 | 885 | 0085 | 2-37-04 | 2-37-05 | 1-55 | 1960 GIS LCC | DS (ON) | 1961 DS ON |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1961_DS | 1961(161KV #2SHR) DS | OTHER | [5 empty] | 735 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 161 | 161kV | 1960 | #2SHR(1960) |  | DS2 | 1962 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0886 | 887 | 0086 | 2-37-06 | 2-37-07 | 1-56 | 1960 GIS LCC | DS (ON) | 1962 DS ON |  |  | B2/D13_A1 | [8 empty] | 虎科DS.1962_DS | 1962(161KV #2SHR) DS | OTHER | [5 empty] | 736 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS |  |  | 2DTR | #2DTR |  | 51A |  | INSERT | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0055 |  |  | 1-06-07 |  |  | ------ | ------ | SPARE |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#2DTR_51A | #2DTR 51RY | MTR | [5 empty] | 737 | DNPDIPoint | DS054 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS |  |  | 2DTR | #2DTR |  | 51NA |  | INSERT | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0056 |  |  | 1-07-00 |  |  | ------ | ------ | SPARE |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#2DTR_51NA | #2DTR 51N RY | MTR | [5 empty] | 738 | DNPDIPoint | DS054 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | 330 | #2DTR(330) |  | 51A |  | INSERT | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0050 |  |  | 1-06-02 |  |  | ------ | ------ | SPARE |  |  | B3/D13_A1 | [8 empty] | 虎科DS.330_51A | #2DTR二次側(330) 51RY | MTR | [5 empty] | 739 | DNPDIPoint | DS054 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | 340 | #2DTR(340) |  | 51A |  | INSERT | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0051 |  |  | 1-06-03 |  |  | ------ | ------ | SPARE |  |  | B3/D13_A1 | [8 empty] | 虎科DS.340_51A | #2DTR二次側(340) 51RY | MTR | [5 empty] | 740 | DNPDIPoint | DS054 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS |  |  | 3DTR | #3DTR |  | 51A |  | INSERT | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0064 |  |  | 1-08-00 |  |  | ------ | ------ | SPARE |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#3DTR_51A | #3DTR 51RY | MTR | [5 empty] | 741 | DNPDIPoint | DS054 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS |  |  | 3DTR | #3DTR |  | 51NA |  | INSERT | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0065 |  |  | 1-08-01 |  |  | ------ | ------ | SPARE |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#3DTR_51NA | #3DTR 51N RY | MTR | [5 empty] | 742 | DNPDIPoint | DS054 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 350 | #3DTR(350) |  | 51A |  | INSERT | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0059 |  |  | 1-07-03 |  |  | ------ | ------ | SPARE |  |  | B3/D13_A1 | [8 empty] | 虎科DS.350_51A | #3DTR二次側(350) 51RY | MTR | [5 empty] | 743 | DNPDIPoint | DS054 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 360 | #3DTR(360) |  | 51A |  | INSERT | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0060 |  |  | 1-07-04 |  |  | ------ | ------ | SPARE |  |  | B3/D13_A1 | [8 empty] | 虎科DS.360_51A | #3DTR二次側(360) 51RY | MTR | [5 empty] | 744 | DNPDIPoint | DS054 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS |  |  | 4DTR | #4DTR |  | 51A |  | INSERT | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0073 |  |  | 1-09-01 |  |  | ------ | ------ | SPARE |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#4DTR_51A | #4DTR 51RY | MTR | [5 empty] | 745 | DNPDIPoint | DS054 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS |  |  | 4DTR | #4DTR |  | 51NA |  | INSERT | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-09-02 |  |  | ------ | ------ | SPARE |  |  | B1/D13_A1 | [8 empty] | 虎科DS.#4DTR_51NA | #4DTR 51N RY | MTR | [5 empty] | 746 | DNPDIPoint | DS054 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 370 | #4DTR(370) |  | 51A |  | INSERT | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 |  |  | 1-08-04 |  |  | ------ | ------ | SPARE |  |  | B3/D13_A1 | [8 empty] | 虎科DS.370_51A | #4DTR二次側(370) 51RY | MTR | [5 empty] | 747 | DNPDIPoint | DS054 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 380 | #4DTR(380) |  | 51A |  | INSERT | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 |  |  | 1-08-05 |  |  | ------ | ------ | SPARE |  |  | B3/D13_A1 | [8 empty] | 虎科DS.380_51A | #4DTR二次側(380) 51RY | MTR | [5 empty] | 748 | DNPDIPoint | DS054 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | StaDev | 所內設施 |  | CHG1 |  | INSERT | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0611 |  |  | 1-36-03 |  |  | M5 | CHG1 | 充電機設備用警報 |  |  | B3/D13_A1 | [8 empty] | 虎科DS.直流充電機故障 | 直流充電機故障 | OTHER | [5 empty] | 749 | DNPDIPoint | DS054 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | StaDev | 所內設施 |  | CHG2 |  | INSERT | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0612 |  |  | 1-36-04 |  |  | M5 | CHG2 | 充電機通訊用警報 |  |  | B3/D13_A1 | [8 empty] | 虎科DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | [5 empty] | 750 | DNPDIPoint | DS054 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
D13 | 虎科DS | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/D13_A1 | [12 empty] | 虎科DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: D13/161/1BUS/V; OPRD2: D13/161/2BUS/V
D13 | 虎科DS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/D13_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: D13/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
D13 | 虎科DS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/D13_A1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_6 | OPRD1: D13/161/1570/MW; OPRD2: D13/161/1580/MW; OPRD3: D13/161/1610/MW; OPRD4: D13/161/1620/MW; OPRD5: D13/161/1630/MW; OPRD6: D13/161/1640/MW
D13 | 虎科DS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/D13_A1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: D13/0/CalcPoint/OPRN2_MW
D13 | 虎科DS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/D13_A1 | [17 empty] | none
D13 | 虎科DS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/D13_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: D13/0/CalcPoint/OPRN1; OPRD2: D13/0/CalcPoint/OPRN2; OPRD3: D13/0/CalcPoint/PRFL_UL
D13 | 虎科DS |  |  | 2DTR | 2DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D13_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D13/11/330/I_R; OPRD2: D13/11/340/I_R
D13 | 虎科DS |  |  | 2DTR | 2DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D13_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D13/11/330/I_S; OPRD2: D13/11/340/I_S
D13 | 虎科DS |  |  | 2DTR | 2DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D13_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D13/11/330/I_T; OPRD2: D13/11/340/I_T
D13 | 虎科DS |  |  | 3DTR | 3DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D13_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D13/22/350/I_R; OPRD2: D13/22/360/I_R
D13 | 虎科DS |  |  | 3DTR | 3DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D13_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D13/22/350/I_S; OPRD2: D13/22/360/I_S
D13 | 虎科DS |  |  | 3DTR | 3DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D13_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D13/22/350/I_T; OPRD2: D13/22/360/I_T
D13 | 虎科DS |  |  | 4DTR | 4DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D13_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D13/22/370/I_R; OPRD2: D13/22/380/I_R
D13 | 虎科DS |  |  | 4DTR | 4DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D13_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D13/22/370/I_S; OPRD2: D13/22/380/I_S
D13 | 虎科DS |  |  | 4DTR | 4DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D13_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D13/22/370/I_T; OPRD2: D13/22/380/I_T
D13 | 虎科DS | 161 | 161kV | 1570 | 虎科～虎菁一路(1570) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D13_A1 | [12 empty] | 虎科DS.1570_AMP | 虎科虎菁一路 AMP | LINE161 | AMP_CAL | C20R2000 | amp_cal | OPRD1: D13/161/1570/MW; OPRD2: D13/161/1570/MVAR; OPRD3: D13/0/CalcPoint/Vbs4
D13 | 虎科DS | 161 | 161kV | 1580 | 虎科～虎菁二路(1580) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D13_A1 | [12 empty] | 虎科DS.1580_AMP | 虎科虎菁二路 AMP | LINE161 | AMP_CAL | C20R2000 | amp_cal | OPRD1: D13/161/1580/MW; OPRD2: D13/161/1580/MVAR; OPRD3: D13/0/CalcPoint/Vbs4
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D13_A1 | [12 empty] | 虎科DS.1610_AMP | 虎科和鑫一路 AMP | LINE161 | AMP_CAL | C20R1000 | amp_cal | OPRD1: D13/161/1610/MW; OPRD2: D13/161/1610/MVAR; OPRD3: D13/0/CalcPoint/Vbs4
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D13_A1 | [12 empty] | 虎科DS.1620_AMP | 虎科和鑫二路 AMP | LINE161 | AMP_CAL | C20R1000 | amp_cal | OPRD1: D13/161/1620/MW; OPRD2: D13/161/1620/MVAR; OPRD3: D13/0/CalcPoint/Vbs4
D13 | 虎科DS | 161 | 161kV | 1630 | 越港虎科紅線(1630) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D13_A1 | [12 empty] | 虎科DS.1630_AMP | 越港虎科紅線 AMP | LINE161 | AMP_CAL | C20R1000 | amp_cal | OPRD1: D13/161/1630/MW; OPRD2: D13/161/1630/MVAR; OPRD3: D13/0/CalcPoint/Vbs4
D13 | 虎科DS | 161 | 161kV | 1640 | 越港虎科白線(1640) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D13_A1 | [12 empty] | 虎科DS.1640_AMP | 越港虎科白線 AMP | LINE161 | AMP_CAL | C20R1000 | amp_cal | OPRD1: D13/161/1640/MW; OPRD2: D13/161/1640/MVAR; OPRD3: D13/0/CalcPoint/Vbs4
D13 | 虎科DS | 11 | 11kV | 2ABUS | #2ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D13_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D13/11/2ABUS/V
D13 | 虎科DS | 11 | 11kV | 2BBUS | #2BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D13_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D13/11/2BBUS/V
D13 | 虎科DS | 22 | 22kV | 3ABUS | #3ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D13_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D13/22/3ABUS/V
D13 | 虎科DS | 22 | 22kV | 3BBUS | #3BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D13_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D13/22/3BBUS/V
D13 | 虎科DS | 22 | 22kV | 4ABUS | #4ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D13_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D13/22/4ABUS/V
D13 | 虎科DS | 22 | 22kV | 4BBUS | #4BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D13_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D13/22/4BBUS/V
D13 | 虎科DS |  |  | 2DTR(A) | #2DTR(A) |  | TR_PERM | [9 empty] | B1/D13_A1 | [12 empty] | 虎科DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D13//2DTR(A)/SupLocal; OPRD2: D13//2DTR(A)/Tap Chan
D13 | 虎科DS |  |  | 2DTR(B) | #2DTR(B) |  | TR_PERM | [9 empty] | B1/D13_A1 | [12 empty] | 虎科DS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D13//2DTR(B)/SupLocal; OPRD2: D13//2DTR(B)/Tap Chan
D13 | 虎科DS |  |  | 3DTR | #3DTR |  | TR_PERM | [9 empty] | B1/D13_A1 | [12 empty] | 虎科DS.#3DTR_PERM | #3DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D13//3DTR/SupLocal; OPRD2: D13//3DTR/Tap Chan
D13 | 虎科DS |  |  | 4DTR | #4DTR |  | TR_PERM | [9 empty] | B1/D13_A1 | [12 empty] | 虎科DS.#4DTR_PERM | #4DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D13//4DTR/SupLocal; OPRD2: D13//4DTR/Tap Chan
D13 | 虎科DS | 11 | 11kV | XO31 | 科十一線(XO31) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D13/11/2ABUS/V; OPRD2: D13/11/XO31/I_R; OPRD3: D13/11/XO31/I_S; OPRD4: D13/11/XO31/I_T
D13 | 虎科DS | 11 | 11kV | XO32 | 科十二線(XO32) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D13/11/2ABUS/V; OPRD2: D13/11/XO32/I_R; OPRD3: D13/11/XO32/I_S; OPRD4: D13/11/XO32/I_T
D13 | 虎科DS | 11 | 11kV | XO33 | 科十三線(XO33) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D13/11/2ABUS/V; OPRD2: D13/11/XO33/I_R; OPRD3: D13/11/XO33/I_S; OPRD4: D13/11/XO33/I_T
D13 | 虎科DS | 11 | 11kV | XO34 | 科十四線(XO34) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D13/11/2ABUS/V; OPRD2: D13/11/XO34/I_R; OPRD3: D13/11/XO34/I_S; OPRD4: D13/11/XO34/I_T
D13 | 虎科DS | 11 | 11kV | XO35 | 科十五線(XO35) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D13/11/2ABUS/V; OPRD2: D13/11/XO35/I_R; OPRD3: D13/11/XO35/I_S; OPRD4: D13/11/XO35/I_T
D13 | 虎科DS | 11 | 11kV | XO36 | 科十六線(XO36) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D13/11/2BBUS/V; OPRD2: D13/11/XO36/I_R; OPRD3: D13/11/XO36/I_S; OPRD4: D13/11/XO36/I_T
D13 | 虎科DS | 11 | 11kV | XO37 | 科十七線(XO37) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D13/11/2BBUS/V; OPRD2: D13/11/XO37/I_R; OPRD3: D13/11/XO37/I_S; OPRD4: D13/11/XO37/I_T
D13 | 虎科DS | 11 | 11kV | XO38 | 科十八線(XO38) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D13/11/2BBUS/V; OPRD2: D13/11/XO38/I_R; OPRD3: D13/11/XO38/I_S; OPRD4: D13/11/XO38/I_T
D13 | 虎科DS | 11 | 11kV | XO39 | 科十九線(XO39) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D13/11/2BBUS/V; OPRD2: D13/11/XO39/I_R; OPRD3: D13/11/XO39/I_S; OPRD4: D13/11/XO39/I_T
D13 | 虎科DS | 11 | 11kV | XO40 | 科二十線(XO40) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D13/11/2BBUS/V; OPRD2: D13/11/XO40/I_R; OPRD3: D13/11/XO40/I_S; OPRD4: D13/11/XO40/I_T
D13 | 虎科DS | 22 | 22kV | XO61 | 科六一線(XO61) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D13/22/3ABUS/V; OPRD2: D13/22/XO61/I_R; OPRD3: D13/22/XO61/I_S; OPRD4: D13/22/XO61/I_T
D13 | 虎科DS | 22 | 22kV | XO62 | 科六二線(XO62) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D13/22/3ABUS/V; OPRD2: D13/22/XO62/I_R; OPRD3: D13/22/XO62/I_S; OPRD4: D13/22/XO62/I_T
D13 | 虎科DS | 22 | 22kV | XO63 | 科六三線(XO63) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D13/22/3ABUS/V; OPRD2: D13/22/XO63/I_R; OPRD3: D13/22/XO63/I_S; OPRD4: D13/22/XO63/I_T
D13 | 虎科DS | 22 | 22kV | XO64 | 科六四線(XO64) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D13/22/3ABUS/V; OPRD2: D13/22/XO64/I_R; OPRD3: D13/22/XO64/I_S; OPRD4: D13/22/XO64/I_T
D13 | 虎科DS | 22 | 22kV | XO65 | 科六五線(XO65) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D13/22/3BBUS/V; OPRD2: D13/22/XO65/I_R; OPRD3: D13/22/XO65/I_S; OPRD4: D13/22/XO65/I_T
D13 | 虎科DS | 22 | 22kV | XO66 | 科六六線(XO66) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D13/22/3BBUS/V; OPRD2: D13/22/XO66/I_R; OPRD3: D13/22/XO66/I_S; OPRD4: D13/22/XO66/I_T
D13 | 虎科DS | 22 | 22kV | XO67 | 科六七線(XO67) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D13/22/3BBUS/V; OPRD2: D13/22/XO67/I_R; OPRD3: D13/22/XO67/I_S; OPRD4: D13/22/XO67/I_T
D13 | 虎科DS | 22 | 22kV | XO68 | 科六八線(XO68) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D13/22/3BBUS/V; OPRD2: D13/22/XO68/I_R; OPRD3: D13/22/XO68/I_S; OPRD4: D13/22/XO68/I_T
D13 | 虎科DS | 22 | 22kV | XO71 | 科七一線(XO71) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D13/22/4ABUS/V; OPRD2: D13/22/XO71/I_R; OPRD3: D13/22/XO71/I_S; OPRD4: D13/22/XO71/I_T
D13 | 虎科DS | 22 | 22kV | XO72 | 科七二線(XO72) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D13/22/4ABUS/V; OPRD2: D13/22/XO72/I_R; OPRD3: D13/22/XO72/I_S; OPRD4: D13/22/XO72/I_T
D13 | 虎科DS | 22 | 22kV | XO73 | 科七三線(XO73) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D13/22/4ABUS/V; OPRD2: D13/22/XO73/I_R; OPRD3: D13/22/XO73/I_S; OPRD4: D13/22/XO73/I_T
D13 | 虎科DS | 22 | 22kV | XO74 | 科七四線(XO74) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D13/22/4ABUS/V; OPRD2: D13/22/XO74/I_R; OPRD3: D13/22/XO74/I_S; OPRD4: D13/22/XO74/I_T
D13 | 虎科DS | 22 | 22kV | XO75 | 科七五線(XO75) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D13/22/4BBUS/V; OPRD2: D13/22/XO75/I_R; OPRD3: D13/22/XO75/I_S; OPRD4: D13/22/XO75/I_T
D13 | 虎科DS | 22 | 22kV | XO76 | 科七六線(XO76) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D13/22/4BBUS/V; OPRD2: D13/22/XO76/I_R; OPRD3: D13/22/XO76/I_S; OPRD4: D13/22/XO76/I_T
D13 | 虎科DS | 22 | 22kV | XO77 | 科七七線(XO77) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D13/22/4BBUS/V; OPRD2: D13/22/XO77/I_R; OPRD3: D13/22/XO77/I_S; OPRD4: D13/22/XO77/I_T
D13 | 虎科DS | 22 | 22kV | XO78 | 科七八線(XO78) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D13/22/4BBUS/V; OPRD2: D13/22/XO78/I_R; OPRD3: D13/22/XO78/I_S; OPRD4: D13/22/XO78/I_T
D13 | 虎科DS | 11 | 11kV | XO31 | 科十一線(XO31) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D13/11/XO31/kVA; OPRD2: D13/11/XO31/KVAR
D13 | 虎科DS | 11 | 11kV | XO32 | 科十二線(XO32) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D13/11/XO32/kVA; OPRD2: D13/11/XO32/KVAR
D13 | 虎科DS | 11 | 11kV | XO33 | 科十三線(XO33) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D13/11/XO33/kVA; OPRD2: D13/11/XO33/KVAR
D13 | 虎科DS | 11 | 11kV | XO34 | 科十四線(XO34) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D13/11/XO34/kVA; OPRD2: D13/11/XO34/KVAR
D13 | 虎科DS | 11 | 11kV | XO35 | 科十五線(XO35) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D13/11/XO35/kVA; OPRD2: D13/11/XO35/KVAR
D13 | 虎科DS | 11 | 11kV | XO36 | 科十六線(XO36) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D13/11/XO36/kVA; OPRD2: D13/11/XO36/KVAR
D13 | 虎科DS | 11 | 11kV | XO37 | 科十七線(XO37) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D13/11/XO37/kVA; OPRD2: D13/11/XO37/KVAR
D13 | 虎科DS | 11 | 11kV | XO38 | 科十八線(XO38) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D13/11/XO38/kVA; OPRD2: D13/11/XO38/KVAR
D13 | 虎科DS | 11 | 11kV | XO39 | 科十九線(XO39) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D13/11/XO39/kVA; OPRD2: D13/11/XO39/KVAR
D13 | 虎科DS | 11 | 11kV | XO40 | 科二十線(XO40) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D13/11/XO40/kVA; OPRD2: D13/11/XO40/KVAR
D13 | 虎科DS | 22 | 22kV | XO61 | 科六一線(XO61) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D13/22/XO61/kVA; OPRD2: D13/22/XO61/KVAR
D13 | 虎科DS | 22 | 22kV | XO62 | 科六二線(XO62) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D13/22/XO62/kVA; OPRD2: D13/22/XO62/KVAR
D13 | 虎科DS | 22 | 22kV | XO63 | 科六三線(XO63) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D13/22/XO63/kVA; OPRD2: D13/22/XO63/KVAR
D13 | 虎科DS | 22 | 22kV | XO64 | 科六四線(XO64) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D13/22/XO64/kVA; OPRD2: D13/22/XO64/KVAR
D13 | 虎科DS | 22 | 22kV | XO65 | 科六五線(XO65) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D13/22/XO65/kVA; OPRD2: D13/22/XO65/KVAR
D13 | 虎科DS | 22 | 22kV | XO66 | 科六六線(XO66) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D13/22/XO66/kVA; OPRD2: D13/22/XO66/KVAR
D13 | 虎科DS | 22 | 22kV | XO67 | 科六七線(XO67) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D13/22/XO67/kVA; OPRD2: D13/22/XO67/KVAR
D13 | 虎科DS | 22 | 22kV | XO68 | 科六八線(XO68) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D13/22/XO68/kVA; OPRD2: D13/22/XO68/KVAR
D13 | 虎科DS | 22 | 22kV | XO71 | 科七一線(XO71) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D13/22/XO71/kVA; OPRD2: D13/22/XO71/KVAR
D13 | 虎科DS | 22 | 22kV | XO72 | 科七二線(XO72) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D13/22/XO72/kVA; OPRD2: D13/22/XO72/KVAR
D13 | 虎科DS | 22 | 22kV | XO73 | 科七三線(XO73) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D13/22/XO73/kVA; OPRD2: D13/22/XO73/KVAR
D13 | 虎科DS | 22 | 22kV | XO74 | 科七四線(XO74) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D13/22/XO74/kVA; OPRD2: D13/22/XO74/KVAR
D13 | 虎科DS | 22 | 22kV | XO75 | 科七五線(XO75) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D13/22/XO75/kVA; OPRD2: D13/22/XO75/KVAR
D13 | 虎科DS | 22 | 22kV | XO76 | 科七六線(XO76) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D13/22/XO76/kVA; OPRD2: D13/22/XO76/KVAR
D13 | 虎科DS | 22 | 22kV | XO77 | 科七七線(XO77) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D13/22/XO77/kVA; OPRD2: D13/22/XO77/KVAR
D13 | 虎科DS | 22 | 22kV | XO78 | 科七八線(XO78) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D13_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D13/22/XO78/kVA; OPRD2: D13/22/XO78/KVAR
D13 | 虎科DS | 11 | 11kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D13_A1 | [12 empty] | 虎科DS.230_SC_MVAR | 11KV#3SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D13/11/230/CB; OPRD2: 6.9; OPRD3: 0
D13 | 虎科DS | 11 | 11kV | 240 | #4SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D13_A1 | [12 empty] | 虎科DS.240_SC_MVAR | 11KV#4SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D13/11/240/CB; OPRD2: 6.9; OPRD3: 0
D13 | 虎科DS | 22 | 22kV | 250 | #5SC(250) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D13_A1 | [12 empty] | 虎科DS.250_SC_MVAR | 23KV#5SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D13/22/250/CB; OPRD2: 13.8; OPRD3: 0
D13 | 虎科DS | 22 | 22kV | 260 | #6SC(260) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D13_A1 | [12 empty] | 虎科DS.260_SC_MVAR | 23KV#6SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D13/22/260/CB; OPRD2: 13.8; OPRD3: 0
D13 | 虎科DS | 22 | 22kV | 270 | #7SC(270) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D13_A1 | [12 empty] | 虎科DS.270_SC_MVAR | 23KV#7SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D13/22/270/CB; OPRD2: 13.8; OPRD3: 0
D13 | 虎科DS | 22 | 22kV | 280 | #8SC(280) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D13_A1 | [12 empty] | 虎科DS.280_SC_MVAR | 23KV#8SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D13/22/280/CB; OPRD2: 13.8; OPRD3: 0
D13 | 虎科DS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/D13_A1 | [12 empty] | 虎科DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_14 |  | com_alarm_44 | D13//2DTR/96B1 | D13//2DTR/GDA | D13//2DTR/PHA | D13//2DTR/96B2 | D13//2DTR/TRA | D13//2DTR/63Q | D13//2DTR/96D | D13//2DTR/51ZA | D13//2DTR/96PA | D13//2DTR/87A | D13//3DTR/96PA | D13//3DTR/87A | D13//3DTR/96D | D13//3DTR/96B2 | D13//3DTR/96B1 | D13//3DTR/GDA | D13//3DTR/PHA | D13//3DTR/63Q | D13//3DTR/TRA | D13//3DTR/51ZA | D13//4DTR/TRA | D13//4DTR/63Q | D13//4DTR/51ZA | D13//4DTR/96PA | D13//4DTR/87A | D13//4DTR/PHA | D13//4DTR/GDA | D13//4DTR/96D | D13//4DTR/96B2 | D13//4DTR/96B1 | D13/11/330/GDA | D13/11/330/PHA | D13/11/340/GDA | D13/11/340/PHA | D13/161/1BUS/87A | D13/161/2BUS/87A | D13/22/350/GDA | D13/22/350/PHA | D13/22/360/GDA | D13/22/360/PHA | D13/22/370/GDA | D13/22/370/PHA | D13/22/380/GDA | D13/22/380/PHA
D13 | 虎科DS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/D13_A1 | [12 empty] | 虎科DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | STATION_FAULT_3 |  | com_alarm_3 | OPRD1: D13//2DTR/TRF; OPRD2: D13//3DTR/TRF; OPRD3: D13//4DTR/TRF
D13 | 虎科DS | 161 | 161kV | 1760_D1 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D13_D1 | [17 empty] | lamp2CC | OPRD1: D13/161/1760/CB
D13 | 虎科DS | 161 | 161kV | 1770_D1 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D13_D1 | [17 empty] | lamp2CC | OPRD1: D13/161/1770/CB
D13 | 虎科DS | 161 | 161kV | 1780_D1 | #4DTR(1780) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D13_D1 | [17 empty] | lamp2CC | OPRD1: D13/161/1780/CB
D13 | 虎科DS | 11 | 11kV | 330_D1 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D13_D1 | [17 empty] | lamp2CC | OPRD1: D13/11/330/CB
D13 | 虎科DS | 11 | 11kV | 340_D1 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D13_D1 | [17 empty] | lamp2CC | OPRD1: D13/11/340/CB
D13 | 虎科DS | 22 | 22kV | 350_D1 | #3DTR(A)(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D13_D1 | [17 empty] | lamp2CC | OPRD1: D13/22/350/CB
D13 | 虎科DS | 22 | 22kV | 360_D1 | #3DTR(B)(360) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D13_D1 | [17 empty] | lamp2CC | OPRD1: D13/22/360/CB
D13 | 虎科DS | 22 | 22kV | 370_D1 | #4DTR(A)(370) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D13_D1 | [17 empty] | lamp2CC | OPRD1: D13/22/370/CB
D13 | 虎科DS | 22 | 22kV | 380_D1 | #4DTR(B)(380) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D13_D1 | [17 empty] | lamp2CC | OPRD1: D13/22/380/CB
D13 | 虎科DS | 0 |  | StaDev_D1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D13_D1 | [17 empty] | lamp2CC | OPRD1: D13/0/StaDev/DCE
D13 | 虎科DS | 0 |  | ComPoint_D1 |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/D13_D1 | [17 empty] | lamp2CC | OPRD1: D13/0/ComPoint/ABS_89A
D13 | 虎科DS | 0 |  | StaDev_D1 | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/D13_D1 | [17 empty] | lamp2CC | OPRD1: D13/0/StaDev/STUV

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | I | [25 empty] | ADCS_N | [8 empty] | 虎科DS.1610_AMP | 虎科和鑫一路 AMP | LINE161 | D13/161/1610/I |  | AMP_CAL |  |  | 2 | CalcAIPoint | [21 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D13 | 虎科DS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 虎科DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | D13/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 3 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
D13 | 虎科DS | 161 | 161kV | 1570 | 虎科虎菁一路(1570) |  | I | [25 empty] | ADCS_N | [8 empty] | 虎科DS.1570_AMP | 虎科虎菁一路 AMP | LINE161 | D13/161/1570/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000
D13 | 虎科DS | 161 | 161kV | 1580 | 虎科虎菁二路(1580) |  | I | [25 empty] | ADCS_N | [8 empty] | 虎科DS.1580_AMP | 虎科虎菁二路 AMP | LINE161 | D13/161/1580/I |  | AMP_CAL |  |  | 5 | CalcAIPoint | [21 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | I | [25 empty] | ADCS_N | [8 empty] | 虎科DS.1620_AMP | 虎科和鑫二路 AMP | LINE161 | D13/161/1620/I |  | AMP_CAL |  |  | 6 | CalcAIPoint | [21 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D13 | 虎科DS | 161 | 161kV | 1630 | 越港虎科紅線(1630) |  | I | [25 empty] | ADCS_N | [8 empty] | 虎科DS.1630_AMP | 越港虎科紅線 AMP | LINE161 | D13/161/1630/I |  | AMP_CAL |  |  | 7 | CalcAIPoint | [21 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D13 | 虎科DS | 161 | 161kV | 1640 | 越港虎科白線(1640) |  | I | [25 empty] | ADCS_N | [8 empty] | 虎科DS.1640_AMP | 越港虎科白線 AMP | LINE161 | D13/161/1640/I |  | AMP_CAL |  |  | 8 | CalcAIPoint | [21 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D13 | 虎科DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#2DTR(A)_MVA | #2DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D13 | 虎科DS | 0 |  | 2DTR(A) | #2DTR(A) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#2DTR(A)_LOAD | #2DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 10 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D13 | 虎科DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PF | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#2DTR(A)_PF | #2DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D13 | 虎科DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#2DTR(B)_MVA | #2DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D13 | 虎科DS | 0 |  | 2DTR(B) | #2DTR(B) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#2DTR(B)_LOAD | #2DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 13 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D13 | 虎科DS | 0 |  | 2DTR(B) | #2DTR(B) |  | PF | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#2DTR(B)_PF | #2DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D13 | 虎科DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#3DTR(A)_MVA | #3DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D13 | 虎科DS | 0 |  | 3DTR(A) | #3DTR(A) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#3DTR(A)_LOAD | #3DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 16 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D13 | 虎科DS | 0 |  | 3DTR(A) | #3DTR(A) |  | PF | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#3DTR(A)_PF | #3DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D13 | 虎科DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#3DTR(B)_MVA | #3DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D13 | 虎科DS | 0 |  | 3DTR(B) | #3DTR(B) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#3DTR(B)_LOAD | #3DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 19 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D13 | 虎科DS | 0 |  | 3DTR(B) | #3DTR(B) |  | PF | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#3DTR(B)_PF | #3DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D13 | 虎科DS | 0 |  | 4DTR(A) | #4DTR二次側(A) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#4DTR(A)_MVA | #4DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D13 | 虎科DS | 0 |  | 4DTR(A) | #4DTR(A) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#4DTR(A)_LOAD | #4DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 22 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D13 | 虎科DS | 0 |  | 4DTR(A) | #4DTR(A) |  | PF | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#4DTR(A)_PF | #4DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D13 | 虎科DS | 0 |  | 4DTR(B) | #4DTR二次側(B) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#4DTR(B)_MVA | #4DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D13 | 虎科DS | 0 |  | 4DTR(B) | #4DTR(B) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#4DTR(B)_LOAD | #4DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 25 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D13 | 虎科DS | 0 |  | 4DTR(B) | #4DTR(B) |  | PF | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#4DTR(B)_PF | #4DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D13 | 虎科DS | 0 |  | 2DTR | #2DTR |  | MW | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#2DTR_MW | #2DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  | 2DTR | #2DTR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#2DTR_MVAR | #2DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  | 2DTR | #2DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#2DTR_MVA | #2DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D13 | 虎科DS | 0 |  | 2DTR | #2DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#2DTR_LOAD | #2DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 30 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D13 | 虎科DS | 0 |  | 2DTR | #2DTR |  | PF | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#2DTR_PF | #2DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D13 | 虎科DS | 0 |  | 3DTR | #3DTR |  | MW | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#3DTR_MW | #3DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  | 3DTR | #3DTR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#3DTR_MVAR | #3DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  | 3DTR | #3DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#3DTR_MVA | #3DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D13 | 虎科DS | 0 |  | 3DTR | #3DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#3DTR_LOAD | #3DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 35 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D13 | 虎科DS | 0 |  | 3DTR | #3DTR |  | PF | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#3DTR_PF | #3DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D13 | 虎科DS | 0 |  | 4DTR | #4DTR |  | MW | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#4DTR_MW | #4DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  | 4DTR | #4DTR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#4DTR_MVAR | #4DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  | 4DTR | #4DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#4DTR_MVA | #4DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D13 | 虎科DS | 0 |  | 4DTR | #4DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#4DTR_LOAD | #4DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 40 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D13 | 虎科DS | 0 |  | 4DTR | #4DTR |  | PF | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#4DTR_PF | #4DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D13 | 虎科DS | 11 | 11kV | 230_SC | #3SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 虎科DS.230_SC_MVAR | 11KV#3SC MVAR | SC | D13/11/230/MVAR |  | SC_LBS_11 |  |  | 42 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 11 | 11kV | 240_SC | #4SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 虎科DS.240_SC_MVAR | 11KV#4SC MVAR | SC | D13/11/240/MVAR |  | SC_LBS_11 |  |  | 43 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 22 | 22kV | 250_SC | #5SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 虎科DS.250_SC_MVAR | 23KV#5SC MVAR | SC | D13/22/250/MVAR |  | SC_CAL_23 |  |  | 44 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 22 | 22kV | 260_SC | #6SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 虎科DS.260_SC_MVAR | 23KV#6SC MVAR | SC | D13/22/260/MVAR |  | SC_CAL_23 |  |  | 45 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 22 | 22kV | 270_SC | #7SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 虎科DS.270_SC_MVAR | 23KV#7SC MVAR | SC | D13/22/270/MVAR |  | SC_CAL_23 |  |  | 46 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 22 | 22kV | 280_SC | #8SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 虎科DS.280_SC_MVAR | 23KV#8SC MVAR | SC | D13/22/280/MVAR |  | SC_CAL_23 |  |  | 47 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  | TRTOT | 虎科主變瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 虎科DS.TRTOT_MW | 虎科主變瞬時供電量 MW |  |  |  | TOTAL_PQ_CAL_3 |  |  | 48 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  | TRTOT | 虎科主變瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 虎科DS.TRTOT_MVAR | 虎科主變瞬時供電量 MVAR |  |  |  | TOTAL_PQ_CAL_3 |  |  | 49 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 22 | 22kV | 3BUS | #3BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 虎科DS.23KV#3BUS_KV | 23KV #3BUS BEST SOURCE | BUS |  |  | BEST_1W2CB |  |  | 50 | CalcAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D13 | 虎科DS | 22 | 22kV | 4BUS | #4BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 虎科DS.23KV#4BUS_KV | 23KV #4BUS BEST SOURCE | BUS |  |  | BEST_1W2CB |  |  | 51 | CalcAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D13 | 虎科DS | 0 |  |  |  |  | 科11線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科11線KVA | 11KV科11線KVA | FEEDER |  |  | KVA_CAL |  |  | 52 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科11線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科11線KW | 11KV科11線KW | FEEDER |  |  | KW_CAL |  |  | 53 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科12線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科12線KVA | 11KV科12線KVA | FEEDER |  |  | KVA_CAL |  |  | 54 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科12線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科12線KW | 11KV科12線KW | FEEDER |  |  | KW_CAL |  |  | 55 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科13線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科13線KVA | 11KV科13線KVA | FEEDER |  |  | KVA_CAL |  |  | 56 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科13線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科13線KW | 11KV科13線KW | FEEDER |  |  | KW_CAL |  |  | 57 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科14線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科14線KVA | 11KV科14線KVA | FEEDER |  |  | KVA_CAL |  |  | 58 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科14線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科14線KW | 11KV科14線KW | FEEDER |  |  | KW_CAL |  |  | 59 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科15線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科15線KVA | 11KV科15線KVA | FEEDER |  |  | KVA_CAL |  |  | 60 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科15線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科15線KW | 11KV科15線KW | FEEDER |  |  | KW_CAL |  |  | 61 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科16線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科16線KVA | 11KV科16線KVA | FEEDER |  |  | KVA_CAL |  |  | 62 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科16線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科16線KW | 11KV科16線KW | FEEDER |  |  | KW_CAL |  |  | 63 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科17線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科17線KVA | 11KV科17線KVA | FEEDER |  |  | KVA_CAL |  |  | 64 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科17線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科17線KW | 11KV科17線KW | FEEDER |  |  | KW_CAL |  |  | 65 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科18線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科18線KVA | 11KV科18線KVA | FEEDER |  |  | KVA_CAL |  |  | 66 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科18線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科18線KW | 11KV科18線KW | FEEDER |  |  | KW_CAL |  |  | 67 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科19線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科19線KVA | 11KV科19線KVA | FEEDER |  |  | KVA_CAL |  |  | 68 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科19線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科19線KW | 11KV科19線KW | FEEDER |  |  | KW_CAL |  |  | 69 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科20線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科20線KVA | 11KV科20線KVA | FEEDER |  |  | KVA_CAL |  |  | 70 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科20線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科20線KW | 11KV科20線KW | FEEDER |  |  | KW_CAL |  |  | 71 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科61線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科61線KVA | 23KV科61線KVA | FEEDER |  |  | KVA_CAL |  |  | 72 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科61線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科61線KW | 23KV科61線KW | FEEDER |  |  | KW_CAL |  |  | 73 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科62線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科62線KVA | 23KV科62線KVA | FEEDER |  |  | KVA_CAL |  |  | 74 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科62線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科62線KW | 23KV科62線KW | FEEDER |  |  | KW_CAL |  |  | 75 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科63線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科63線KVA | 23KV科63線KVA | FEEDER |  |  | KVA_CAL |  |  | 76 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科63線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科63線KW | 23KV科63線KW | FEEDER |  |  | KW_CAL |  |  | 77 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科64線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科64線KVA | 23KV科64線KVA | FEEDER |  |  | KVA_CAL |  |  | 78 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科64線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科64線KW | 23KV科64線KW | FEEDER |  |  | KW_CAL |  |  | 79 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科65線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科65線KVA | 23KV科65線KVA | FEEDER |  |  | KVA_CAL |  |  | 80 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科65線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科65線KW | 23KV科65線KW | FEEDER |  |  | KW_CAL |  |  | 81 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科66線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科66線KVA | 23KV科66線KVA | FEEDER |  |  | KVA_CAL |  |  | 82 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科66線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科66線KW | 23KV科66線KW | FEEDER |  |  | KW_CAL |  |  | 83 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科67線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科67線KVA | 23KV科67線KVA | FEEDER |  |  | KVA_CAL |  |  | 84 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科67線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科67線KW | 23KV科67線KW | FEEDER |  |  | KW_CAL |  |  | 85 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科68線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科68線KVA | 23KV科68線KVA | FEEDER |  |  | KVA_CAL |  |  | 86 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科68線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科68線KW | 23KV科68線KW | FEEDER |  |  | KW_CAL |  |  | 87 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科71線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科71線KVA | 23KV科71線KVA | FEEDER |  |  | KVA_CAL |  |  | 88 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科71線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科71線KW | 23KV科71線KW | FEEDER |  |  | KW_CAL |  |  | 89 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科72線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科72線KVA | 23KV科72線KVA | FEEDER |  |  | KVA_CAL |  |  | 90 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科72線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科72線KW | 23KV科72線KW | FEEDER |  |  | KW_CAL |  |  | 91 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科73線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科73線KVA | 23KV科73線KVA | FEEDER |  |  | KVA_CAL |  |  | 92 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科73線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科73線KW | 23KV科73線KW | FEEDER |  |  | KW_CAL |  |  | 93 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科74線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科74線KVA | 23KV科74線KVA | FEEDER |  |  | KVA_CAL |  |  | 94 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科74線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科74線KW | 23KV科74線KW | FEEDER |  |  | KW_CAL |  |  | 95 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科75線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科75線KVA | 23KV科75線KVA | FEEDER |  |  | KVA_CAL |  |  | 96 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科75線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科75線KW | 23KV科75線KW | FEEDER |  |  | KW_CAL |  |  | 97 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科76線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科76線KVA | 23KV科76線KVA | FEEDER |  |  | KVA_CAL |  |  | 98 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科76線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科76線KW | 23KV科76線KW | FEEDER |  |  | KW_CAL |  |  | 99 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科77線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科77線KVA | 23KV科77線KVA | FEEDER |  |  | KVA_CAL |  |  | 100 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科77線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科77線KW | 23KV科77線KW | FEEDER |  |  | KW_CAL |  |  | 101 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科78線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科78線KVA | 23KV科78線KVA | FEEDER |  |  | KVA_CAL |  |  | 102 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 0 |  |  |  |  | 科78線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.科78線KW | 23KV科78線KW | FEEDER |  |  | KW_CAL |  |  | 103 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 161 | 161kV | 1960_SHR | #2SHR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 虎科DS.1960_SHR_MVAR | 161KV#2SHR MVAR | SC |  |  | SHR_CAL_MVAR |  |  | 104 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 161 | 161kV | 1610_AMP | 虎科和鑫一路 | [27 empty] | ADCS_N | [8 empty] | 虎科DS.1610_AMP_A | 虎科和鑫一路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 105 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D13 | 虎科DS | 0 |  | 100_CB | 100(100_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.100_CB_1 | 100 CB (D1) | TIE |  |  | AD_LAMP_DD_1 |  |  | 106 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 200_CB | 200(200_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.200_CB_1 | 200 CB (D1) | TIE |  |  | AD_LAMP_DD_1 |  |  | 107 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 300_CB | 300(300_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.300_CB_1 | 300 CB (D1) | TIE |  |  | AD_LAMP_DD_1 |  |  | 108 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 400_CB | 400(400_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.400_CB_1 | 400 CB (D1) | TIE |  |  | AD_LAMP_DD_1 |  |  | 109 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 1760_CB | #2DTR(1760_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.1760_CB_1 | 1760(#2DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 110 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 330_CB | #2DTR(330_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.330_CB_1 | 330(#2DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 111 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 340_CB | #2DTR(340_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.340_CB_1 | 340(#2DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 112 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 1770_CB | #3DTR(1770_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.1770_CB_1 | 1770(#3DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 113 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 350_CB | #3DTR(350_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.350_CB_1 | 350(#3DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 114 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 360_CB | #3DTR(360_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.360_CB_1 | 360(#3DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 115 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 1780_CB | #4DTR(1780_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.1780_CB_1 | 1780(#4DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 116 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 370_CB | #4DTR(370_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.370_CB_1 | 370(#4DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 117 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 380_CB | #4DTR(380_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.380_CB_1 | 380(#4DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 118 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | 230_CB | #3SC(230_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.230_CB_1 | 230(11KV #3SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 119 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | 240_CB | #4SC(240_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.240_CB_1 | 240(11KV #4SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 120 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | 250_CB | #5SC(250_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.250_CB_1 | 250(23KV #5SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 121 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | 260_CB | #6SC(260_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.260_CB_1 | 260(23KV #6SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 122 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | 270_CB | #7SC(270_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.270_CB_1 | 270(23KV #7SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 123 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | 280_CB | #8SC(280_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.280_CB_1 | 280(23KV #8SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 124 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | 11__CBA | 11/斷路器重故障(11__CBA) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.11/23KV_CBA_1 | 11/23KV斷路器重故障 (D1) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 125 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 11__CBF | 11/斷路器輕故障(11__CBF) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.11/23KV_CBF_1 | 11/23KV斷路器輕故障 (D1) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 126 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | COMM_S_L | 通訊處理單元 |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.COMM_S/L_1 | 通訊處理單元 SUPY/LOCAL (D1) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 127 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D13 | 虎科DS | 0 |  | PMCCA | PMCC電驛故障 |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.PMCCA_1 | PMCC電驛故障 (D1) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 128 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | PMCC_IED_S_L | 11/ IED |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.PMCC_IED_S/L_1 | 11/23KV IED SUPY/LOCAL (D1) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 129 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D13 | 虎科DS | 0 |  | TCA | 斷路器跳脫回路故障 |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.TCA_1 | 斷路器跳脫回路故障 (D1) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 130 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_N | [8 empty] | 虎科DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | D13/0/CalcPoint/SUBA |  | STATION_FAULT_14 |  |  | 131 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 變電所輕故障點燈 | 變電所輕故障點燈 |  | SUBF | [25 empty] | ADCS_N | [8 empty] | 虎科DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | D13/0/CalcPoint/SUBF |  | STATION_FAULT_3 |  |  | 132 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.變電所重故障_1 | 變電所重故障點燈 (D1) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 133 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.變電所輕故障_1 | 變電所輕故障點燈 (D1) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 134 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1570_AMP | 虎科虎菁一路 | [27 empty] | ADCS_N | [8 empty] | 虎科DS.1570_AMP_A | 虎科虎菁一路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 135 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D13 | 虎科DS | 161 | 161kV | 1580_AMP | 虎科虎菁二路 | [27 empty] | ADCS_N | [8 empty] | 虎科DS.1580_AMP_A | 虎科虎菁二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 136 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D13 | 虎科DS | 161 | 161kV | 1620_AMP | 虎科和鑫二路 | [27 empty] | ADCS_N | [8 empty] | 虎科DS.1620_AMP_A | 虎科和鑫二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 137 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D13 | 虎科DS | 161 | 161kV | 1630_AMP | 越港虎科紅線 | [27 empty] | ADCS_N | [8 empty] | 虎科DS.1630_AMP_A | 越港虎科紅線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 138 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D13 | 虎科DS | 161 | 161kV | 1640_AMP | 越港虎科白線 | [27 empty] | ADCS_N | [8 empty] | 虎科DS.1640_AMP_A | 越港虎科白線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 139 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D13 | 虎科DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PERM | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | D13//2DTR(A)/TR_PERM |  | DTR_PERM |  |  | 140 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D13 | 虎科DS | 0 |  | 2DTR(B) | #2DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | D13//2DTR(B)/TR_PERM |  | DTR_PERM |  |  | 141 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D13 | 虎科DS | 0 |  | 3DTR | #3DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#3DTR_PERM | #3DTR TAP PERMISSION POINT | MTR | D13//3DTR/TR_PERM |  | DTR_PERM |  |  | 142 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D13 | 虎科DS | 0 |  | 4DTR | #4DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 虎科DS.#4DTR_PERM | #4DTR TAP PERMISSION POINT | MTR | D13//4DTR/TR_PERM |  | DTR_PERM |  |  | 143 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D13 | 虎科DS | 0 |  | 2DTR_MVA | #2DTR | [27 empty] | ADCS_N | [8 empty] | 虎科DS.#2DTR_MVA_A | #2DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 144 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D13 | 虎科DS | 0 |  | 2DTR_MVA | #2DTR(A) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.#2DTR_MVA_1 | #2DTR(A) MVA 點燈 (D1) | MTR |  |  | MAP_SET |  |  | 145 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D13 | 虎科DS | 0 |  | 2DTR_MVA | #2DTR(B) | [27 empty] | DDCS1_1 | [8 empty] | 虎科DS.#2DTR_MVA_2 | #2DTR(B) MVA 點燈 (D1) | MTR |  |  | MAP_SET |  |  | 146 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
D13 | 虎科DS | 0 |  | 3DTR_MVA | #3DTR | [27 empty] | ADCS_N | [8 empty] | 虎科DS.#3DTR_MVA_A | #3DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 147 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D13 | 虎科DS | 0 |  | 3DTR_MVA | #3DTR(A) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.#3DTR_MVA_1 | #3DTR(A) MVA 點燈 (D1) | MTR |  |  | MAP_SET |  |  | 148 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D13 | 虎科DS | 0 |  | 3DTR_MVA | #3DTR(B) | [27 empty] | DDCS1_1 | [8 empty] | 虎科DS.#3DTR_MVA_2 | #3DTR(B) MVA 點燈 (D1) | MTR |  |  | MAP_SET |  |  | 149 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
D13 | 虎科DS | 0 |  | 4DTR_MVA | #4DTR | [27 empty] | ADCS_N | [8 empty] | 虎科DS.#4DTR_MVA_A | #4DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 150 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D13 | 虎科DS | 0 |  | 4DTR_MVA | #4DTR(A) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎科DS.#4DTR_MVA_1 | #4DTR(A) MVA 點燈 (D1) | MTR |  |  | MAP_SET |  |  | 151 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D13 | 虎科DS | 0 |  | 4DTR_MVA | #4DTR(B) | [27 empty] | DDCS1_1 | [8 empty] | 虎科DS.#4DTR_MVA_2 | #4DTR(B) MVA 點燈 (D1) | MTR |  |  | MAP_SET |  |  | 152 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
D13 | 虎科DS | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_N | [8 empty] | 虎科DS.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_DS |  |  | 153 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 2ABUS | #2ABUS |  | 11KV#2ABUSC | [25 empty] | CDCS | [8 empty] | 虎科DS.11KV#2ABUSC | #2ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 154 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D13 | 虎科DS | 0 |  | 2BBUS | #2BBUS |  | 11KV#2BBUSC | [25 empty] | CDCS | [8 empty] | 虎科DS.11KV#2BBUSC | #2BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 155 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D13 | 虎科DS | 0 |  | 3ABUS | #3ABUS |  | 23KV#3ABUSC | [25 empty] | CDCS | [8 empty] | 虎科DS.23KV#3ABUSC | #3ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 156 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D13 | 虎科DS | 0 |  | 3BBUS | #3BBUS |  | 23KV#3BBUSC | [25 empty] | CDCS | [8 empty] | 虎科DS.23KV#3BBUSC | #3BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 157 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D13 | 虎科DS | 0 |  | 4ABUS | #4ABUS |  | 23KV#4ABUSC | [25 empty] | CDCS | [8 empty] | 虎科DS.23KV#4ABUSC | #4ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 158 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D13 | 虎科DS | 0 |  | 4BBUS | #4BBUS |  | 23KV#4BBUSC | [25 empty] | CDCS | [8 empty] | 虎科DS.23KV#4BBUSC | #4BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 159 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D13 | 虎科DS | 0 |  | TAP_OVER | TAP |  | SET | [25 empty] | ADCS_N | [8 empty] | 虎科DS.TAP_OVER_SET | TAP OVER HI/LO ALARM | MTR |  |  | 5000_CB_T4 |  |  | 160 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D13 | 虎科DS | 0 |  | BUS_OVER | BUS |  | SET | [25 empty] | ADCS_N | [8 empty] | 虎科DS.BUS_OVER_SET | BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B6 |  |  | 161 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D13 | 虎科DS | 0 |  | 5000 | 虛擬5000 |  | CB動作 | [25 empty] | ADCS_N | [8 empty] | 虎科DS.5000_CB動作 | 虛擬5000 CB動作,請查明原因處理 | MTR |  |  | 5000_CB_M |  |  | 162 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 注意OLTC | 注意OLTC |  | BUS電壓異常 | [25 empty] | ADCS_N | [8 empty] | 虎科DS.BUS電壓異常 | 注意OLTC Tap位置,並將RPDC閉鎖 | OTHER |  |  | STATION_FAULT_2 |  |  | 163 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | MW | [14 empty] | 0015 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.1610_MW | 虎科和鑫一路 MW | LINE161 | D13/161/1610/MW |  |  |  | DNP | 164 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | MVAR | [14 empty] | 0016 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.1610_MVAR | 虎科和鑫一路 MVAR | LINE161 | D13/161/1610/MVAR |  |  |  | DNP | 165 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D13 | 虎科DS | 161 | 161kV | 1610LPD | 虎科和鑫一路(1610) |  | V | [14 empty] | 0033 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.1610LPD_KV | 虎科和鑫一路(1610) LPD KV | LINE161 | D13/161/1610/V |  |  |  | DNP | 166 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D13 | 虎科DS | 11 | 11kV | 2ABUS | #2ABUS |  | V | [14 empty] | 0044 | [8 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS | D13/11/2ABUS/V |  |  |  | DNP | 167 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D13 | 虎科DS | 161 | 161kV | 1BUS | #1BUS |  | V | [14 empty] | 0041 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | D13/161/1BUS/V |  |  |  | DNP | 168 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D13 | 虎科DS | 161 | 161kV | 2BUS | #2BUS |  | V | [14 empty] | 0042 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | D13/161/2BUS/V |  |  |  | DNP | 169 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D13 | 虎科DS | 11 | 11kV | 2BBUS | #2BBUS |  | V | [14 empty] | 0045 | [8 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.11KV#2BBUS_KV | 11KV #2BBUS KV | BUS | D13/11/2BBUS/V |  |  |  | DNP | 170 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D13 | 虎科DS | 22 | 22kV | 3ABUS | #3ABUS |  | V | [14 empty] | 0046 | [8 empty] | kV_-18_18(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.23KV#3ABUS_KV | 23KV #3ABUS KV | BUS | D13/22/3ABUS/V |  |  |  | DNP | 171 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D13 | 虎科DS | 22 | 22kV | 3BBUS | #3BBUS |  | V | [14 empty] | 0047 | [8 empty] | kV_-18_18(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.23KV#3BBUS_KV | 23KV #3BBUS KV | BUS | D13/22/3BBUS/V |  |  |  | DNP | 172 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D13 | 虎科DS | 22 | 22kV | 4ABUS | #4ABUS |  | V | [14 empty] | 0048 | [8 empty] | kV_-18_18(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.23KV#4ABUS_KV | 23KV #4ABUS KV | BUS | D13/22/4ABUS/V |  |  |  | DNP | 173 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D13 | 虎科DS | 22 | 22kV | 4BBUS | #4BBUS |  | V | [14 empty] | 0049 | [8 empty] | kV_-18_18(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.23KV#4BBUS_KV | 23KV #4BBUS KV | BUS | D13/22/4BBUS/V |  |  |  | DNP | 174 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D13 | 虎科DS | 161 | 161kV | 1570 | 虎科虎菁一路(1570) |  | MW | [14 empty] | 0011 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.1570_MW | 虎科虎菁一路 MW | LINE161 | D13/161/1570/MW |  |  |  | DNP | 175 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D13 | 虎科DS | 161 | 161kV | 1570 | 虎科虎菁一路(1570) |  | MVAR | [14 empty] | 0012 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.1570_MVAR | 虎科虎菁一路 MVAR | LINE161 | D13/161/1570/MVAR |  |  |  | DNP | 176 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D13 | 虎科DS | 161 | 161kV | 1570LPD | 虎科虎菁一路(1570) |  | V | [14 empty] | 0031 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.1570LPD_KV | 虎科虎菁一路(1570) LPD KV | LINE161 | D13/161/1570/V |  |  |  | DNP | 177 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D13 | 虎科DS | 161 | 161kV | 1580 | 虎科虎菁二路(1580) |  | MW | [14 empty] | 0013 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.1580_MW | 虎科虎菁二路 MW | LINE161 | D13/161/1580/MW |  |  |  | DNP | 178 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D13 | 虎科DS | 161 | 161kV | 1580 | 虎科虎菁二路(1580) |  | MVAR | [14 empty] | 0014 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.1580_MVAR | 虎科虎菁二路 MVAR | LINE161 | D13/161/1580/MVAR |  |  |  | DNP | 179 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D13 | 虎科DS | 161 | 161kV | 1580LPD | 虎科虎菁二路(1580) |  | V | [14 empty] | 0032 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.1580LPD_KV | 虎科虎菁二路(1580) LPD KV | LINE161 | D13/161/1580/V |  |  |  | DNP | 180 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | MW | [14 empty] | 0017 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.1620_MW | 虎科和鑫二路 MW | LINE161 | D13/161/1620/MW |  |  |  | DNP | 181 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | MVAR | [14 empty] | 0018 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.1620_MVAR | 虎科和鑫二路 MVAR | LINE161 | D13/161/1620/MVAR |  |  |  | DNP | 182 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D13 | 虎科DS | 161 | 161kV | 1620LPD | 虎科和鑫二路(1620) |  | V | [14 empty] | 0034 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.1620LPD_KV | 虎科和鑫二路(1620) LPD KV | LINE161 | D13/161/1620/V |  |  |  | DNP | 183 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D13 | 虎科DS | 161 | 161kV | 1630 | 越港虎科紅線(1630) |  | MW | [14 empty] | 0019 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.1630_MW | 越港虎科紅線 MW | LINE161 | D13/161/1630/MW |  |  |  | DNP | 184 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D13 | 虎科DS | 161 | 161kV | 1630 | 越港虎科紅線(1630) |  | MVAR | [14 empty] | 0020 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.1630_MVAR | 越港虎科紅線 MVAR | LINE161 | D13/161/1630/MVAR |  |  |  | DNP | 185 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D13 | 虎科DS | 161 | 161kV | 1630LPD | 越港虎科紅線(1630) |  | V | [14 empty] | 0035 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.1630LPD_KV | 越港虎科紅線(1630) LPD KV | LINE161 | D13/161/1630/V |  |  |  | DNP | 186 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D13 | 虎科DS | 161 | 161kV | 1640 | 越港虎科白線(1640) |  | MW | [14 empty] | 0021 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.1640_MW | 越港虎科白線 MW | LINE161 | D13/161/1640/MW |  |  |  | DNP | 187 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D13 | 虎科DS | 161 | 161kV | 1640 | 越港虎科白線(1640) |  | MVAR | [14 empty] | 0022 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.1640_MVAR | 越港虎科白線 MVAR | LINE161 | D13/161/1640/MVAR |  |  |  | DNP | 188 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D13 | 虎科DS | 161 | 161kV | 1640LPD | 越港虎科白線(1640) |  | V | [14 empty] | 0036 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.1640LPD_KV | 越港虎科白線(1640) LPD KV | LINE161 | D13/161/1640/V |  |  |  | DNP | 189 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D13 | 虎科DS | 0 |  | 1500TIE | 1500TIE |  | I | [14 empty] | 0043 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.1500TIE_AMP | 1500TIE AMP | TIE | D13/161/1500/I_R |  |  |  | DNP | 190 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | _100 | 100 |  | I_R | [14 empty] | 0057 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.11KV_100_A1 | 11KV 100 R相AMP | TIE | D13/11/100/I_R |  |  |  | DNP | 191 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | _100 | 100 |  | I_S | [14 empty] | 0058 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.11KV_100_A2 | 11KV 100 S相AMP | TIE | D13/11/100/I_S |  |  |  | DNP | 192 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | _100 | 100 |  | I_T | [14 empty] | 0059 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.11KV_100_A3 | 11KV 100 T相AMP | TIE | D13/11/100/I_T |  |  |  | DNP | 193 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | _200 | 200 |  | I_R | [14 empty] | 0090 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.11KV_200_A1 | 11KV 200 R相AMP | TIE | D13/11/200/I_R |  |  |  | DNP | 194 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | _200 | 200 |  | I_S | [14 empty] | 0091 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.11KV_200_A2 | 11KV 200 S相AMP | TIE | D13/11/200/I_S |  |  |  | DNP | 195 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | _200 | 200 |  | I_T | [14 empty] | 0092 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.11KV_200_A3 | 11KV 200 T相AMP | TIE | D13/11/200/I_T |  |  |  | DNP | 196 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | _300 | 300 |  | I_R | [14 empty] | 0218 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.23KV_300_A1 | 23KV 300 R相AMP | TIE | D13/22/300/I_R |  |  |  | DNP | 197 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | _300 | 300 |  | I_S | [14 empty] | 0219 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.23KV_300_A2 | 23KV 300 S相AMP | TIE | D13/22/300/I_S |  |  |  | DNP | 198 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | _300 | 300 |  | I_T | [14 empty] | 0220 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.23KV_300_A3 | 23KV 300 T相AMP | TIE | D13/22/300/I_T |  |  |  | DNP | 199 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | _400 | 400 |  | I_R | [14 empty] | 0221 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.23KV_400_A1 | 23KV 400 R相AMP | TIE | D13/22/400/I_R |  |  |  | DNP | 200 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | _400 | 400 |  | I_S | [14 empty] | 0222 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.23KV_400_A2 | 23KV 400 S相AMP | TIE | D13/22/400/I_S |  |  |  | DNP | 201 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | _400 | 400 |  | I_T | [14 empty] | 0223 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.23KV_400_A3 | 23KV 400 T相AMP | TIE | D13/22/400/I_T |  |  |  | DNP | 202 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MW | [14 empty] | 0052 | [8 empty] | MW_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | D13/11/330/KW |  |  |  | DNP | 203 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.036000 | 0.010000
D13 | 虎科DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVAR | [14 empty] | 0053 | [8 empty] | MVAR_-24_24(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | D13/11/330/KVAR |  |  |  | DNP | 204 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.024000 | 0.010000
D13 | 虎科DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_R | [14 empty] | 0054 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | D13/11/330/I_R |  |  |  | DNP | 205 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_S | [14 empty] | 0055 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | D13/11/330/I_S |  |  |  | DNP | 206 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_T | [14 empty] | 0056 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | D13/11/330/I_T |  |  |  | DNP | 207 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 0 |  | 2DTR | #2DTR |  | OilTemp | [14 empty] | 0004 | [8 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#2DTR_OIL | #2DTR 油溫 | MTR | D13//2DTR/OilTemp |  |  |  | DNP | 208 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D13 | 虎科DS | 0 |  | 2DTR(A) | #2DTR(A) |  | CoilTemp | [14 empty] | 0002 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | D13//2DTR(A)/CoilTemp |  |  |  | DNP | 209 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D13 | 虎科DS | 0 |  | 2DTR(A) | #2DTR(A) |  | TapPosMv | [14 empty] | 0000 |  | 0002 | [6 empty] | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 虎科DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | D13//2DTR(A)/TapPosMv |  |  |  | DNP | 210 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D13 | 虎科DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MW | [14 empty] | 0085 | [8 empty] | MW_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | D13/11/340/KW |  |  |  | DNP | 211 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.036000 | 0.010000
D13 | 虎科DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVAR | [14 empty] | 0086 | [8 empty] | MVAR_-24_24(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | D13/11/340/KVAR |  |  |  | DNP | 212 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.024000 | 0.010000
D13 | 虎科DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_R | [14 empty] | 0087 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | D13/11/340/I_R |  |  |  | DNP | 213 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_S | [14 empty] | 0088 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | D13/11/340/I_S |  |  |  | DNP | 214 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_T | [14 empty] | 0089 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | D13/11/340/I_T |  |  |  | DNP | 215 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 0 |  | 2DTR(B) | #2DTR(B) |  | CoilTemp | [14 empty] | 0003 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | D13//2DTR(B)/CoilTemp |  |  |  | DNP | 216 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D13 | 虎科DS | 0 |  | 2DTR(B) | #2DTR(B) |  | TapPosMv | [14 empty] | 0001 |  | 0004 | [6 empty] | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 虎科DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | D13//2DTR(B)/TapPosMv |  |  |  | DNP | 217 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D13 | 虎科DS | 0 |  | 3DTR | #3DTR |  | OilTemp | [14 empty] | 0007 | [8 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#3DTR_OIL | #3DTR 油溫 | MTR | D13//3DTR/OilTemp |  |  |  | DNP | 218 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D13 | 虎科DS | 0 |  | 3DTR | #3DTR |  | CoilTemp | [14 empty] | 0006 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#3DTR_COIL | #3DTR 線溫 | MTR | D13//3DTR/CoilTemp |  |  |  | DNP | 219 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D13 | 虎科DS | 0 |  | 3DTR | #3DTR |  | TapPosMv | [14 empty] | 0005 |  | 0006 | [6 empty] | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 虎科DS.#3DTR_TAP | #3DTR OLTC TAP | MTR | D13//3DTR/TapPosMv |  |  |  | DNP | 220 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D13 | 虎科DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | MW | [14 empty] | 0118 | [8 empty] | MW_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#3DTR(A)_MW | #3DTR二次側(A) MW | MTR | D13/22/350/KW |  |  |  | DNP | 221 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D13 | 虎科DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | MVAR | [14 empty] | 0119 | [8 empty] | MVAR_-48_48(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#3DTR(A)_MVAR | #3DTR二次側(A) MVAR | MTR | D13/22/350/KVAR |  |  |  | DNP | 222 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.048000 | 0.010000
D13 | 虎科DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | I_R | [14 empty] | 0120 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#3DTR(A)_A1 | #3DTR二次側(A) R相AMP | MTR | D13/22/350/I_R |  |  |  | DNP | 223 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | I_S | [14 empty] | 0121 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#3DTR(A)_A2 | #3DTR二次側(A) S相AMP | MTR | D13/22/350/I_S |  |  |  | DNP | 224 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | I_T | [14 empty] | 0122 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#3DTR(A)_A3 | #3DTR二次側(A) T相AMP | MTR | D13/22/350/I_T |  |  |  | DNP | 225 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | MW | [14 empty] | 0143 | [8 empty] | MW_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#3DTR(B)_MW | #3DTR二次側(B) MW | MTR | D13/22/360/KW |  |  |  | DNP | 226 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D13 | 虎科DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | MVAR | [14 empty] | 0144 | [8 empty] | MVAR_-48_48(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#3DTR(B)_MVAR | #3DTR二次側(B) MVAR | MTR | D13/22/360/KVAR |  |  |  | DNP | 227 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.048000 | 0.010000
D13 | 虎科DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | I_R | [14 empty] | 0145 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#3DTR(B)_A1 | #3DTR二次側(B) R相AMP | MTR | D13/22/360/I_R |  |  |  | DNP | 228 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | I_S | [14 empty] | 0146 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#3DTR(B)_A2 | #3DTR二次側(B) S相AMP | MTR | D13/22/360/I_S |  |  |  | DNP | 229 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | I_T | [14 empty] | 0147 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#3DTR(B)_A3 | #3DTR二次側(B) T相AMP | MTR | D13/22/360/I_T |  |  |  | DNP | 230 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 0 |  | 4DTR | #4DTR |  | OilTemp | [14 empty] | 0010 | [8 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#4DTR_OIL | #4DTR 油溫 | MTR | D13//4DTR/OilTemp |  |  |  | DNP | 231 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D13 | 虎科DS | 0 |  | 4DTR | #4DTR |  | CoilTemp | [14 empty] | 0009 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#4DTR_COIL | #4DTR 線溫 | MTR | D13//4DTR/CoilTemp |  |  |  | DNP | 232 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D13 | 虎科DS | 0 |  | 4DTR | #4DTR |  | TapPosMv | [14 empty] | 0008 |  | 0008 | [6 empty] | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 虎科DS.#4DTR_TAP | #4DTR OLTC TAP | MTR | D13//4DTR/TapPosMv |  |  |  | DNP | 233 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D13 | 虎科DS | 0 |  | 4DTR(A) | #4DTR二次側(A) |  | MW | [14 empty] | 0168 | [8 empty] | MW_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#4DTR(A)_MW | #4DTR二次側(A) MW | MTR | D13/22/370/KW |  |  |  | DNP | 234 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D13 | 虎科DS | 0 |  | 4DTR(A) | #4DTR二次側(A) |  | MVAR | [14 empty] | 0169 | [8 empty] | MVAR_-48_48(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#4DTR(A)_MVAR | #4DTR二次側(A) MVAR | MTR | D13/22/370/KVAR |  |  |  | DNP | 235 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.048000 | 0.010000
D13 | 虎科DS | 0 |  | 4DTR(A) | #4DTR二次側(A) |  | I_R | [14 empty] | 0170 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#4DTR(A)_A1 | #4DTR二次側(A) R相AMP | MTR | D13/22/370/I_R |  |  |  | DNP | 236 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 0 |  | 4DTR(A) | #4DTR二次側(A) |  | I_S | [14 empty] | 0171 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#4DTR(A)_A2 | #4DTR二次側(A) S相AMP | MTR | D13/22/370/I_S |  |  |  | DNP | 237 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 0 |  | 4DTR(A) | #4DTR二次側(A) |  | I_T | [14 empty] | 0172 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#4DTR(A)_A3 | #4DTR二次側(A) T相AMP | MTR | D13/22/370/I_T |  |  |  | DNP | 238 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 0 |  | 4DTR(B) | #4DTR二次側(B) |  | MW | [14 empty] | 0193 | [8 empty] | MW_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#4DTR(B)_MW | #4DTR二次側(B) MW | MTR | D13/22/380/KW |  |  |  | DNP | 239 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D13 | 虎科DS | 0 |  | 4DTR(B) | #4DTR二次側(B) |  | MVAR | [14 empty] | 0194 | [8 empty] | MVAR_-48_48(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#4DTR(B)_MVAR | #4DTR二次側(B) MVAR | MTR | D13/22/380/KVAR |  |  |  | DNP | 240 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.048000 | 0.010000
D13 | 虎科DS | 0 |  | 4DTR(B) | #4DTR二次側(B) |  | I_R | [14 empty] | 0195 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#4DTR(B)_A1 | #4DTR二次側(B) R相AMP | MTR | D13/22/380/I_R |  |  |  | DNP | 241 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 0 |  | 4DTR(B) | #4DTR二次側(B) |  | I_S | [14 empty] | 0196 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#4DTR(B)_A2 | #4DTR二次側(B) S相AMP | MTR | D13/22/380/I_S |  |  |  | DNP | 242 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 0 |  | 4DTR(B) | #4DTR二次側(B) |  | I_T | [14 empty] | 0197 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.#4DTR(B)_A3 | #4DTR二次側(B) T相AMP | MTR | D13/22/380/I_T |  |  |  | DNP | 243 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科11線 | 科11線 |  | 科11線KVAR | [14 empty] | 0060 | [8 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科11線KVAR | 11KV科11線 KVAR | FEEDER | D13/11/XO31/KVAR |  |  |  | DNP | 244 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科11線 | 科11線 |  | 科11線A1 | [14 empty] | 0061 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科11線A1 | 11KV科11線 R相AMP | FEEDER | D13/11/XO31/I_R |  |  |  | DNP | 245 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科11線 | 科11線 |  | 科11線A2 | [14 empty] | 0062 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科11線A2 | 11KV科11線 S相AMP | FEEDER | D13/11/XO31/I_S |  |  |  | DNP | 246 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科11線 | 科11線 |  | 科11線A3 | [14 empty] | 0063 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科11線A3 | 11KV科11線 T相AMP | FEEDER | D13/11/XO31/I_T |  |  |  | DNP | 247 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科11線 | 科11線 |  | 科11線A0 | [14 empty] | 0064 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科11線A0 | 11KV科11線 N相AMP | FEEDER | D13/11/XO31/I_N |  |  |  | DNP | 248 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科12線 | 科12線 |  | 科12線KVAR | [14 empty] | 0065 | [8 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科12線KVAR | 11KV科12線 KVAR | FEEDER | D13/11/XO32/KVAR |  |  |  | DNP | 249 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科12線 | 科12線 |  | 科12線A1 | [14 empty] | 0066 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科12線A1 | 11KV科12線 R相AMP | FEEDER | D13/11/XO32/I_R |  |  |  | DNP | 250 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科12線 | 科12線 |  | 科12線A2 | [14 empty] | 0067 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科12線A2 | 11KV科12線 S相AMP | FEEDER | D13/11/XO32/I_S |  |  |  | DNP | 251 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科12線 | 科12線 |  | 科12線A3 | [14 empty] | 0068 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科12線A3 | 11KV科12線 T相AMP | FEEDER | D13/11/XO32/I_T |  |  |  | DNP | 252 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科12線 | 科12線 |  | 科12線A0 | [14 empty] | 0069 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科12線A0 | 11KV科12線 N相AMP | FEEDER | D13/11/XO32/I_N |  |  |  | DNP | 253 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科13線 | 科13線 |  | 科13線KVAR | [14 empty] | 0070 | [8 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科13線KVAR | 11KV科13線 KVAR | FEEDER | D13/11/XO33/KVAR |  |  |  | DNP | 254 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科13線 | 科13線 |  | 科13線A1 | [14 empty] | 0071 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科13線A1 | 11KV科13線 R相AMP | FEEDER | D13/11/XO33/I_R |  |  |  | DNP | 255 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科13線 | 科13線 |  | 科13線A2 | [14 empty] | 0072 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科13線A2 | 11KV科13線 S相AMP | FEEDER | D13/11/XO33/I_S |  |  |  | DNP | 256 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科13線 | 科13線 |  | 科13線A3 | [14 empty] | 0073 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科13線A3 | 11KV科13線 T相AMP | FEEDER | D13/11/XO33/I_T |  |  |  | DNP | 257 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科13線 | 科13線 |  | 科13線A0 | [14 empty] | 0074 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科13線A0 | 11KV科13線 N相AMP | FEEDER | D13/11/XO33/I_N |  |  |  | DNP | 258 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科14線 | 科14線 |  | 科14線KVAR | [14 empty] | 0075 | [8 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科14線KVAR | 11KV科14線 KVAR | FEEDER | D13/11/XO34/KVAR |  |  |  | DNP | 259 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科14線 | 科14線 |  | 科14線A1 | [14 empty] | 0076 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科14線A1 | 11KV科14線 R相AMP | FEEDER | D13/11/XO34/I_R |  |  |  | DNP | 260 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科14線 | 科14線 |  | 科14線A2 | [14 empty] | 0077 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科14線A2 | 11KV科14線 S相AMP | FEEDER | D13/11/XO34/I_S |  |  |  | DNP | 261 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科14線 | 科14線 |  | 科14線A3 | [14 empty] | 0078 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科14線A3 | 11KV科14線 T相AMP | FEEDER | D13/11/XO34/I_T |  |  |  | DNP | 262 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科14線 | 科14線 |  | 科14線A0 | [14 empty] | 0079 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科14線A0 | 11KV科14線 N相AMP | FEEDER | D13/11/XO34/I_N |  |  |  | DNP | 263 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科15線 | 科15線 |  | 科15線KVAR | [14 empty] | 0080 | [8 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科15線KVAR | 11KV科15線 KVAR | FEEDER | D13/11/XO35/KVAR |  |  |  | DNP | 264 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科15線 | 科15線 |  | 科15線A1 | [14 empty] | 0081 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科15線A1 | 11KV科15線 R相AMP | FEEDER | D13/11/XO35/I_R |  |  |  | DNP | 265 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科15線 | 科15線 |  | 科15線A2 | [14 empty] | 0082 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科15線A2 | 11KV科15線 S相AMP | FEEDER | D13/11/XO35/I_S |  |  |  | DNP | 266 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科15線 | 科15線 |  | 科15線A3 | [14 empty] | 0083 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科15線A3 | 11KV科15線 T相AMP | FEEDER | D13/11/XO35/I_T |  |  |  | DNP | 267 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科15線 | 科15線 |  | 科15線A0 | [14 empty] | 0084 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科15線A0 | 11KV科15線 N相AMP | FEEDER | D13/11/XO35/I_N |  |  |  | DNP | 268 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科16線 | 科16線 |  | 科16線KVAR | [14 empty] | 0093 | [8 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科16線KVAR | 11KV科16線 KVAR | FEEDER | D13/11/XO36/KVAR |  |  |  | DNP | 269 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科16線 | 科16線 |  | 科16線A1 | [14 empty] | 0094 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科16線A1 | 11KV科16線 R相AMP | FEEDER | D13/11/XO36/I_R |  |  |  | DNP | 270 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科16線 | 科16線 |  | 科16線A2 | [14 empty] | 0095 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科16線A2 | 11KV科16線 S相AMP | FEEDER | D13/11/XO36/I_S |  |  |  | DNP | 271 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科16線 | 科16線 |  | 科16線A3 | [14 empty] | 0096 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科16線A3 | 11KV科16線 T相AMP | FEEDER | D13/11/XO36/I_T |  |  |  | DNP | 272 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科16線 | 科16線 |  | 科16線A0 | [14 empty] | 0097 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科16線A0 | 11KV科16線 N相AMP | FEEDER | D13/11/XO36/I_N |  |  |  | DNP | 273 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科17線 | 科17線 |  | 科17線KVAR | [14 empty] | 0098 | [8 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科17線KVAR | 11KV科17線 KVAR | FEEDER | D13/11/XO37/KVAR |  |  |  | DNP | 274 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科17線 | 科17線 |  | 科17線A1 | [14 empty] | 0099 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科17線A1 | 11KV科17線 R相AMP | FEEDER | D13/11/XO37/I_R |  |  |  | DNP | 275 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科17線 | 科17線 |  | 科17線A2 | [14 empty] | 0100 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科17線A2 | 11KV科17線 S相AMP | FEEDER | D13/11/XO37/I_S |  |  |  | DNP | 276 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科17線 | 科17線 |  | 科17線A3 | [14 empty] | 0101 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科17線A3 | 11KV科17線 T相AMP | FEEDER | D13/11/XO37/I_T |  |  |  | DNP | 277 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科17線 | 科17線 |  | 科17線A0 | [14 empty] | 0102 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科17線A0 | 11KV科17線 N相AMP | FEEDER | D13/11/XO37/I_N |  |  |  | DNP | 278 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科18線 | 科18線 |  | 科18線KVAR | [14 empty] | 0103 | [8 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科18線KVAR | 11KV科18線 KVAR | FEEDER | D13/11/XO38/KVAR |  |  |  | DNP | 279 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科18線 | 科18線 |  | 科18線A1 | [14 empty] | 0104 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科18線A1 | 11KV科18線 R相AMP | FEEDER | D13/11/XO38/I_R |  |  |  | DNP | 280 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科18線 | 科18線 |  | 科18線A2 | [14 empty] | 0105 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科18線A2 | 11KV科18線 S相AMP | FEEDER | D13/11/XO38/I_S |  |  |  | DNP | 281 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科18線 | 科18線 |  | 科18線A3 | [14 empty] | 0106 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科18線A3 | 11KV科18線 T相AMP | FEEDER | D13/11/XO38/I_T |  |  |  | DNP | 282 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科18線 | 科18線 |  | 科18線A0 | [14 empty] | 0107 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科18線A0 | 11KV科18線 N相AMP | FEEDER | D13/11/XO38/I_N |  |  |  | DNP | 283 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科19線 | 科19線 |  | 科19線KVAR | [14 empty] | 0108 | [8 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科19線KVAR | 11KV科19線 KVAR | FEEDER | D13/11/XO39/KVAR |  |  |  | DNP | 284 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科19線 | 科19線 |  | 科19線A1 | [14 empty] | 0109 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科19線A1 | 11KV科19線 R相AMP | FEEDER | D13/11/XO39/I_R |  |  |  | DNP | 285 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科19線 | 科19線 |  | 科19線A2 | [14 empty] | 0110 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科19線A2 | 11KV科19線 S相AMP | FEEDER | D13/11/XO39/I_S |  |  |  | DNP | 286 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科19線 | 科19線 |  | 科19線A3 | [14 empty] | 0111 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科19線A3 | 11KV科19線 T相AMP | FEEDER | D13/11/XO39/I_T |  |  |  | DNP | 287 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科19線 | 科19線 |  | 科19線A0 | [14 empty] | 0112 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科19線A0 | 11KV科19線 N相AMP | FEEDER | D13/11/XO39/I_N |  |  |  | DNP | 288 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科20線 | 科20線 |  | 科20線KVAR | [14 empty] | 0113 | [8 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科20線KVAR | 11KV科20線 KVAR | FEEDER | D13/11/XO40/KVAR |  |  |  | DNP | 289 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科20線 | 科20線 |  | 科20線A1 | [14 empty] | 0114 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科20線A1 | 11KV科20線 R相AMP | FEEDER | D13/11/XO40/I_R |  |  |  | DNP | 290 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科20線 | 科20線 |  | 科20線A2 | [14 empty] | 0115 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科20線A2 | 11KV科20線 S相AMP | FEEDER | D13/11/XO40/I_S |  |  |  | DNP | 291 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科20線 | 科20線 |  | 科20線A3 | [14 empty] | 0116 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科20線A3 | 11KV科20線 T相AMP | FEEDER | D13/11/XO40/I_T |  |  |  | DNP | 292 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 11 | 11kV | 科20線 | 科20線 |  | 科20線A0 | [14 empty] | 0117 | [8 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科20線A0 | 11KV科20線 N相AMP | FEEDER | D13/11/XO40/I_N |  |  |  | DNP | 293 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科61線 | 科61線 |  | 科61線KVAR | [14 empty] | 0123 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科61線KVAR | 23KV科61線 KVAR | FEEDER | D13/22/XO61/KVAR |  |  |  | DNP | 294 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科61線 | 科61線 |  | 科61線A1 | [14 empty] | 0124 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科61線A1 | 23KV科61線 R相AMP | FEEDER | D13/22/XO61/I_R |  |  |  | DNP | 295 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科61線 | 科61線 |  | 科61線A2 | [14 empty] | 0125 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科61線A2 | 23KV科61線 S相AMP | FEEDER | D13/22/XO61/I_S |  |  |  | DNP | 296 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科61線 | 科61線 |  | 科61線A3 | [14 empty] | 0126 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科61線A3 | 23KV科61線 T相AMP | FEEDER | D13/22/XO61/I_T |  |  |  | DNP | 297 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科61線 | 科61線 |  | 科61線A0 | [14 empty] | 0127 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科61線A0 | 23KV科61線 N相AMP | FEEDER | D13/22/XO61/I_N |  |  |  | DNP | 298 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科62線 | 科62線 |  | 科62線KVAR | [14 empty] | 0128 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科62線KVAR | 23KV科62線 KVAR | FEEDER | D13/22/XO62/KVAR |  |  |  | DNP | 299 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科62線 | 科62線 |  | 科62線A1 | [14 empty] | 0129 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科62線A1 | 23KV科62線 R相AMP | FEEDER | D13/22/XO62/I_R |  |  |  | DNP | 300 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科62線 | 科62線 |  | 科62線A2 | [14 empty] | 0130 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科62線A2 | 23KV科62線 S相AMP | FEEDER | D13/22/XO62/I_S |  |  |  | DNP | 301 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科62線 | 科62線 |  | 科62線A3 | [14 empty] | 0131 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科62線A3 | 23KV科62線 T相AMP | FEEDER | D13/22/XO62/I_T |  |  |  | DNP | 302 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科62線 | 科62線 |  | 科62線A0 | [14 empty] | 0132 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科62線A0 | 23KV科62線 N相AMP | FEEDER | D13/22/XO62/I_N |  |  |  | DNP | 303 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科63線 | 科63線 |  | 科63線KVAR | [14 empty] | 0133 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科63線KVAR | 23KV科63線 KVAR | FEEDER | D13/22/XO63/KVAR |  |  |  | DNP | 304 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科63線 | 科63線 |  | 科63線A1 | [14 empty] | 0134 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科63線A1 | 23KV科63線 R相AMP | FEEDER | D13/22/XO63/I_R |  |  |  | DNP | 305 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科63線 | 科63線 |  | 科63線A2 | [14 empty] | 0135 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科63線A2 | 23KV科63線 S相AMP | FEEDER | D13/22/XO63/I_S |  |  |  | DNP | 306 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科63線 | 科63線 |  | 科63線A3 | [14 empty] | 0136 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科63線A3 | 23KV科63線 T相AMP | FEEDER | D13/22/XO63/I_T |  |  |  | DNP | 307 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科63線 | 科63線 |  | 科63線A0 | [14 empty] | 0137 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科63線A0 | 23KV科63線 N相AMP | FEEDER | D13/22/XO63/I_N |  |  |  | DNP | 308 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科64線 | 科64線 |  | 科64線KVAR | [14 empty] | 0138 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科64線KVAR | 23KV科64線 KVAR | FEEDER | D13/22/XO64/KVAR |  |  |  | DNP | 309 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科64線 | 科64線 |  | 科64線A1 | [14 empty] | 0139 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科64線A1 | 23KV科64線 R相AMP | FEEDER | D13/22/XO64/I_R |  |  |  | DNP | 310 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科64線 | 科64線 |  | 科64線A2 | [14 empty] | 0140 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科64線A2 | 23KV科64線 S相AMP | FEEDER | D13/22/XO64/I_S |  |  |  | DNP | 311 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科64線 | 科64線 |  | 科64線A3 | [14 empty] | 0141 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科64線A3 | 23KV科64線 T相AMP | FEEDER | D13/22/XO64/I_T |  |  |  | DNP | 312 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科64線 | 科64線 |  | 科64線A0 | [14 empty] | 0142 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科64線A0 | 23KV科64線 N相AMP | FEEDER | D13/22/XO64/I_N |  |  |  | DNP | 313 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科65線 | 科65線 |  | 科65線KVAR | [14 empty] | 0148 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科65線KVAR | 23KV科65線 KVAR | FEEDER | D13/22/XO65/KVAR |  |  |  | DNP | 314 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科65線 | 科65線 |  | 科65線A1 | [14 empty] | 0149 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科65線A1 | 23KV科65線 R相AMP | FEEDER | D13/22/XO65/I_R |  |  |  | DNP | 315 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科65線 | 科65線 |  | 科65線A2 | [14 empty] | 0150 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科65線A2 | 23KV科65線 S相AMP | FEEDER | D13/22/XO65/I_S |  |  |  | DNP | 316 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科65線 | 科65線 |  | 科65線A3 | [14 empty] | 0151 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科65線A3 | 23KV科65線 T相AMP | FEEDER | D13/22/XO65/I_T |  |  |  | DNP | 317 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科65線 | 科65線 |  | 科65線A0 | [14 empty] | 0152 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科65線A0 | 23KV科65線 N相AMP | FEEDER | D13/22/XO65/I_N |  |  |  | DNP | 318 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科66線 | 科66線 |  | 科66線KVAR | [14 empty] | 0153 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科66線KVAR | 23KV科66線 KVAR | FEEDER | D13/22/XO66/KVAR |  |  |  | DNP | 319 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科66線 | 科66線 |  | 科66線A1 | [14 empty] | 0154 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科66線A1 | 23KV科66線 R相AMP | FEEDER | D13/22/XO66/I_R |  |  |  | DNP | 320 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科66線 | 科66線 |  | 科66線A2 | [14 empty] | 0155 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科66線A2 | 23KV科66線 S相AMP | FEEDER | D13/22/XO66/I_S |  |  |  | DNP | 321 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科66線 | 科66線 |  | 科66線A3 | [14 empty] | 0156 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科66線A3 | 23KV科66線 T相AMP | FEEDER | D13/22/XO66/I_T |  |  |  | DNP | 322 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科66線 | 科66線 |  | 科66線A0 | [14 empty] | 0157 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科66線A0 | 23KV科66線 N相AMP | FEEDER | D13/22/XO66/I_N |  |  |  | DNP | 323 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科67線 | 科67線 |  | 科67線KVAR | [14 empty] | 0158 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科67線KVAR | 23KV科67線 KVAR | FEEDER | D13/22/XO67/KVAR |  |  |  | DNP | 324 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科67線 | 科67線 |  | 科67線A1 | [14 empty] | 0159 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科67線A1 | 23KV科67線 R相AMP | FEEDER | D13/22/XO67/I_R |  |  |  | DNP | 325 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科67線 | 科67線 |  | 科67線A2 | [14 empty] | 0160 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科67線A2 | 23KV科67線 S相AMP | FEEDER | D13/22/XO67/I_S |  |  |  | DNP | 326 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科67線 | 科67線 |  | 科67線A3 | [14 empty] | 0161 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科67線A3 | 23KV科67線 T相AMP | FEEDER | D13/22/XO67/I_T |  |  |  | DNP | 327 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科67線 | 科67線 |  | 科67線A0 | [14 empty] | 0162 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科67線A0 | 23KV科67線 N相AMP | FEEDER | D13/22/XO67/I_N |  |  |  | DNP | 328 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科68線 | 科68線 |  | 科68線KVAR | [14 empty] | 0163 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科68線KVAR | 23KV科68線 KVAR | FEEDER | D13/22/XO68/KVAR |  |  |  | DNP | 329 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科68線 | 科68線 |  | 科68線A1 | [14 empty] | 0164 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科68線A1 | 23KV科68線 R相AMP | FEEDER | D13/22/XO68/I_R |  |  |  | DNP | 330 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科68線 | 科68線 |  | 科68線A2 | [14 empty] | 0165 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科68線A2 | 23KV科68線 S相AMP | FEEDER | D13/22/XO68/I_S |  |  |  | DNP | 331 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科68線 | 科68線 |  | 科68線A3 | [14 empty] | 0166 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科68線A3 | 23KV科68線 T相AMP | FEEDER | D13/22/XO68/I_T |  |  |  | DNP | 332 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科68線 | 科68線 |  | 科68線A0 | [14 empty] | 0167 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科68線A0 | 23KV科68線 N相AMP | FEEDER | D13/22/XO68/I_N |  |  |  | DNP | 333 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科71線 | 科71線 |  | 科71線KVAR | [14 empty] | 0173 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科71線KVAR | 23KV科71線 KVAR | FEEDER | D13/22/XO71/KVAR |  |  |  | DNP | 334 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科71線 | 科71線 |  | 科71線A1 | [14 empty] | 0174 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科71線A1 | 23KV科71線 R相AMP | FEEDER | D13/22/XO71/I_R |  |  |  | DNP | 335 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科71線 | 科71線 |  | 科71線A2 | [14 empty] | 0175 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科71線A2 | 23KV科71線 S相AMP | FEEDER | D13/22/XO71/I_S |  |  |  | DNP | 336 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科71線 | 科71線 |  | 科71線A3 | [14 empty] | 0176 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科71線A3 | 23KV科71線 T相AMP | FEEDER | D13/22/XO71/I_T |  |  |  | DNP | 337 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科71線 | 科71線 |  | 科71線A0 | [14 empty] | 0177 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科71線A0 | 23KV科71線 N相AMP | FEEDER | D13/22/XO71/I_N |  |  |  | DNP | 338 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科72線 | 科72線 |  | 科72線KVAR | [14 empty] | 0178 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科72線KVAR | 23KV科72線 KVAR | FEEDER | D13/22/XO72/KVAR |  |  |  | DNP | 339 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科72線 | 科72線 |  | 科72線A1 | [14 empty] | 0179 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科72線A1 | 23KV科72線 R相AMP | FEEDER | D13/22/XO72/I_R |  |  |  | DNP | 340 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科72線 | 科72線 |  | 科72線A2 | [14 empty] | 0180 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科72線A2 | 23KV科72線 S相AMP | FEEDER | D13/22/XO72/I_S |  |  |  | DNP | 341 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科72線 | 科72線 |  | 科72線A3 | [14 empty] | 0181 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科72線A3 | 23KV科72線 T相AMP | FEEDER | D13/22/XO72/I_T |  |  |  | DNP | 342 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科72線 | 科72線 |  | 科72線A0 | [14 empty] | 0182 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科72線A0 | 23KV科72線 N相AMP | FEEDER | D13/22/XO72/I_N |  |  |  | DNP | 343 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科73線 | 科73線 |  | 科73線KVAR | [14 empty] | 0183 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科73線KVAR | 23KV科73線 KVAR | FEEDER | D13/22/XO73/KVAR |  |  |  | DNP | 344 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科73線 | 科73線 |  | 科73線A1 | [14 empty] | 0184 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科73線A1 | 23KV科73線 R相AMP | FEEDER | D13/22/XO73/I_R |  |  |  | DNP | 345 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科73線 | 科73線 |  | 科73線A2 | [14 empty] | 0185 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科73線A2 | 23KV科73線 S相AMP | FEEDER | D13/22/XO73/I_S |  |  |  | DNP | 346 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科73線 | 科73線 |  | 科73線A3 | [14 empty] | 0186 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科73線A3 | 23KV科73線 T相AMP | FEEDER | D13/22/XO73/I_T |  |  |  | DNP | 347 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科73線 | 科73線 |  | 科73線A0 | [14 empty] | 0187 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科73線A0 | 23KV科73線 N相AMP | FEEDER | D13/22/XO73/I_N |  |  |  | DNP | 348 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科74線 | 科74線 |  | 科74線KVAR | [14 empty] | 0188 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科74線KVAR | 23KV科74線 KVAR | FEEDER | D13/22/XO74/KVAR |  |  |  | DNP | 349 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科74線 | 科74線 |  | 科74線A1 | [14 empty] | 0189 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科74線A1 | 23KV科74線 R相AMP | FEEDER | D13/22/XO74/I_R |  |  |  | DNP | 350 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科74線 | 科74線 |  | 科74線A2 | [14 empty] | 0190 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科74線A2 | 23KV科74線 S相AMP | FEEDER | D13/22/XO74/I_S |  |  |  | DNP | 351 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科74線 | 科74線 |  | 科74線A3 | [14 empty] | 0191 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科74線A3 | 23KV科74線 T相AMP | FEEDER | D13/22/XO74/I_T |  |  |  | DNP | 352 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科74線 | 科74線 |  | 科74線A0 | [14 empty] | 0192 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科74線A0 | 23KV科74線 N相AMP | FEEDER | D13/22/XO74/I_N |  |  |  | DNP | 353 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科75線 | 科75線 |  | 科75線KVAR | [14 empty] | 0198 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科75線KVAR | 23KV科75線 KVAR | FEEDER | D13/22/XO75/KVAR |  |  |  | DNP | 354 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科75線 | 科75線 |  | 科75線A1 | [14 empty] | 0199 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科75線A1 | 23KV科75線 R相AMP | FEEDER | D13/22/XO75/I_R |  |  |  | DNP | 355 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科75線 | 科75線 |  | 科75線A2 | [14 empty] | 0200 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科75線A2 | 23KV科75線 S相AMP | FEEDER | D13/22/XO75/I_S |  |  |  | DNP | 356 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科75線 | 科75線 |  | 科75線A3 | [14 empty] | 0201 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科75線A3 | 23KV科75線 T相AMP | FEEDER | D13/22/XO75/I_T |  |  |  | DNP | 357 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科75線 | 科75線 |  | 科75線A0 | [14 empty] | 0202 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科75線A0 | 23KV科75線 N相AMP | FEEDER | D13/22/XO75/I_N |  |  |  | DNP | 358 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科76線 | 科76線 |  | 科76線KVAR | [14 empty] | 0203 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科76線KVAR | 23KV科76線 KVAR | FEEDER | D13/22/XO76/KVAR |  |  |  | DNP | 359 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科76線 | 科76線 |  | 科76線A1 | [14 empty] | 0204 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科76線A1 | 23KV科76線 R相AMP | FEEDER | D13/22/XO76/I_R |  |  |  | DNP | 360 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科76線 | 科76線 |  | 科76線A2 | [14 empty] | 0205 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科76線A2 | 23KV科76線 S相AMP | FEEDER | D13/22/XO76/I_S |  |  |  | DNP | 361 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科76線 | 科76線 |  | 科76線A3 | [14 empty] | 0206 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科76線A3 | 23KV科76線 T相AMP | FEEDER | D13/22/XO76/I_T |  |  |  | DNP | 362 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科76線 | 科76線 |  | 科76線A0 | [14 empty] | 0207 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科76線A0 | 23KV科76線 N相AMP | FEEDER | D13/22/XO76/I_N |  |  |  | DNP | 363 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科77線 | 科77線 |  | 科77線KVAR | [14 empty] | 0208 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科77線KVAR | 23KV科77線 KVAR | FEEDER | D13/22/XO77/KVAR |  |  |  | DNP | 364 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科77線 | 科77線 |  | 科77線A1 | [14 empty] | 0209 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科77線A1 | 23KV科77線 R相AMP | FEEDER | D13/22/XO77/I_R |  |  |  | DNP | 365 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科77線 | 科77線 |  | 科77線A2 | [14 empty] | 0210 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科77線A2 | 23KV科77線 S相AMP | FEEDER | D13/22/XO77/I_S |  |  |  | DNP | 366 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科77線 | 科77線 |  | 科77線A3 | [14 empty] | 0211 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科77線A3 | 23KV科77線 T相AMP | FEEDER | D13/22/XO77/I_T |  |  |  | DNP | 367 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科77線 | 科77線 |  | 科77線A0 | [14 empty] | 0212 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科77線A0 | 23KV科77線 N相AMP | FEEDER | D13/22/XO77/I_N |  |  |  | DNP | 368 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科78線 | 科78線 |  | 科78線KVAR | [14 empty] | 0213 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科78線KVAR | 23KV科78線 KVAR | FEEDER | D13/22/XO78/KVAR |  |  |  | DNP | 369 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科78線 | 科78線 |  | 科78線A1 | [14 empty] | 0214 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科78線A1 | 23KV科78線 R相AMP | FEEDER | D13/22/XO78/I_R |  |  |  | DNP | 370 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科78線 | 科78線 |  | 科78線A2 | [14 empty] | 0215 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科78線A2 | 23KV科78線 S相AMP | FEEDER | D13/22/XO78/I_S |  |  |  | DNP | 371 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科78線 | 科78線 |  | 科78線A3 | [14 empty] | 0216 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科78線A3 | 23KV科78線 T相AMP | FEEDER | D13/22/XO78/I_T |  |  |  | DNP | 372 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 22 | 22kV | 科78線 | 科78線 |  | 科78線A0 | [14 empty] | 0217 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎科DS.科78線A0 | 23KV科78線 N相AMP | FEEDER | D13/22/XO78/I_N |  |  |  | DNP | 373 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D13 | 虎科DS | 0 |  |  |  |  | DCV_N | [14 empty] | 0225 | [8 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.直流N電源電壓 | 直流N電源電壓 | OTHER | D13/0/StaDev/DCV_N |  |  |  | DNP | 374 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D13 | 虎科DS | 0 |  |  |  |  | DCV_P | [14 empty] | 0224 | [8 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.直流P電源電壓 | 直流P電源電壓 | OTHER | D13/0/StaDev/DCV_P |  |  |  | DNP | 375 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D13 | 虎科DS | 161 | 161kV | 1612SHR | #2SHR |  | CoilTemp | [14 empty] | 0051 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.161#2SHR_COIL | 161KV #2SHR 線溫 | OTHER | D13//2SHR/CoilTemp |  |  |  | DNP | 376 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D13 | 虎科DS | 161 | 161kV | 1612SHR | #2SHR |  | OilTemp | [14 empty] | 0050 | [8 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 虎科DS.161#2SHR_OIL | 161KV #2SHR 油溫 | OTHER | D13//2SHR/OilTemp |  |  |  | DNP | 377 | DNPAIPoint | DS054 |  |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | PHA | [14 empty] | 0008 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.1610_PHA | 虎科和鑫一路(1610) 相間RY | LINE161 | D13/161/1610/PHA |  |  |  | DNP | 378 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | GDA | [14 empty] | 0009 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.1610_GDA | 虎科和鑫一路(1610) 接地RY | LINE161 | D13/161/1610/GDA |  |  |  | DNP | 379 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | 87A2 | [14 empty] | 0007 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.1610_87A2 | 虎科和鑫一路(1610) #2 87RY | LINE161 | D13/161/1610/87A2 |  |  |  | DNP | 380 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | 87A1 | [14 empty] | 0006 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.1610_87A1 | 虎科和鑫一路(1610) #1 87RY | LINE161 | D13/161/1610/87A1 |  |  |  | DNP | 381 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | 1_87UL2 | [14 empty] | 0552 |  | 0019 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1610_87UL2 | 虎科和鑫一路(1610) #2 87RY U/L | LINE161 | D13/161/1610/1_87UL2 |  |  |  | DNP | 382 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | 1_87UL1 | [14 empty] | 0551 |  | 0017 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1610_87UL1 | 虎科和鑫一路(1610) #1 87RY U/L | LINE161 | D13/161/1610/1_87UL1 |  |  |  | DNP | 383 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | CB | [14 empty] | 0111 |  | 0064 | [8 empty] | 161KV_N | [8 empty] | 虎科DS.1610_CB | 1610(虎科和鑫一路) CB | LINE161 | D13/161/1610/CB |  |  |  | DNP | 384 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | 79UL | [14 empty] | 0559 |  | 0018 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1610_79UL | 虎科和鑫一路(1610) 79RY U/L | LINE161 | D13/161/1610/79UL |  |  |  | DNP | 385 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | DS1 | 1611 | [13 empty] | 0788 | 789 | 0065 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1611_DS | 1611(虎科和鑫一路) DS | LINE161 | D13/161/1610/DS1 |  |  |  | DNP | 386 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | DS2 | 1612 | [13 empty] | 0790 | 791 | 0066 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1612_DS | 1612(虎科和鑫一路) DS | LINE161 | D13/161/1610/DS2 |  |  |  | DNP | 387 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | DS3 | 1613 | [13 empty] | 0792 | 793 | 0067 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1613_DS | 1613(虎科和鑫一路) DS | LINE161 | D13/161/1610/DS3 |  |  |  | DNP | 388 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | E3 | 1613E | [13 empty] | 0794 | 795 | 0068 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1613E_ES | 1613E(虎科和鑫一路) ES | LINE161 | D13/161/1610/ES3 |  |  |  | DNP | 389 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D13 | 虎科DS | 0 |  | 1610 | 虎科和鑫一路(1610) |  | 87CFA | [14 empty] | 0600 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.1610_87CFA | 虎科和鑫一路(1610)87RY通訊故障 | OTHER | D13/161/1610/87CFA |  |  |  | DNP | 390 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 1610 | 虎科和鑫一路(1610) |  | RYFA | [14 empty] | 0567 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.1610_RYFA | 虎科和鑫一路(1610)數位電驛故障 | OTHER | D13/161/1610/RYFA |  |  |  | DNP | 391 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO31 | 科11線(XO31) |  | PHA | [14 empty] | 0259 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO31_PHA | 11KV科11線(XO31) 相間RY | FEEDER | D13/11/XO31/PHA |  |  |  | DNP | 392 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO31 | 科11線(XO31) |  | GDA | [14 empty] | 0260 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO31_GDA | 11KV科11線(XO31) 接地RY | FEEDER | D13/11/XO31/GDA |  |  |  | DNP | 393 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO31 | 科11線(XO31) 79RY |  | 79UL | [14 empty] | 0653 |  | 0130 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO31_79UL | 11KV科11線(XO31) 79RY U/L | FEEDER | D13/11/XO31/79UL |  |  |  | DNP | 394 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 11 | 11kV | XO31_LCO | 科11線(XO31) LCO |  | TapPosMv | [14 empty] | 0654 |  | 0131 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO31_LCO_TAP | 11KV科11線(XO31) LCO TAP | FEEDER | D13/11/XO31/ADJ |  |  |  | DNP | 395 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D13 | 虎科DS | 11 | 11kV | XO31 | XO31(11KV科11線) |  | CB | [14 empty] | 0261 |  | 0129 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO31_CB | XO31(11KV科11線) CB | FEEDER | D13/11/XO31/CB |  |  |  | DNP | 396 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 161 | 161kV | 1570 | 虎科虎菁一路(1570) |  | PHA | [14 empty] | 0001 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.1570_PHA | 虎科虎菁一路(1570) 相間RY | LINE161 | D13/161/1570/PHA |  |  |  | DNP | 397 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1570 | 虎科虎菁一路(1570) |  | GDA | [14 empty] | 0002 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.1570_GDA | 虎科虎菁一路(1570) 接地RY | LINE161 | D13/161/1570/GDA |  |  |  | DNP | 398 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1570 | 虎科虎菁一路(1570) |  | 87A | [14 empty] | 0000 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.1570_87A | 虎科虎菁一路(1570) 87RY | LINE161 | D13/161/1570/87A |  |  |  | DNP | 399 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1570 | 虎科虎菁一路(1570) |  | 87UL | [14 empty] | 0549 |  | 0013 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1570_87UL | 虎科虎菁一路(1570) 87RY U/L | LINE161 | D13/161/1570/87UL |  |  |  | DNP | 400 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | 1570 | 虎科虎菁一路(1570) |  | CB | [14 empty] | 0109 |  | 0054 | [8 empty] | 161KV_N | [8 empty] | 虎科DS.1570_CB | 1570(虎科虎菁一路) CB | LINE161 | D13/161/1570/CB |  |  |  | DNP | 401 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 161 | 161kV | 1570 | 虎科虎菁一路(1570) |  | 79UL | [14 empty] | 0557 |  | 0014 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1570_79UL | 虎科虎菁一路(1570) 79RY U/L | LINE161 | D13/161/1570/79UL |  |  |  | DNP | 402 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | 1570 | 虎科虎菁一路(1570) |  | DS1 | 1571 | [13 empty] | 0772 | 773 | 0055 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1571_DS | 1571(虎科虎菁一路) DS | LINE161 | D13/161/1570/DS1 |  |  |  | DNP | 403 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 161 | 161kV | 1570 | 虎科虎菁一路(1570) |  | DS2 | 1572 | [13 empty] | 0774 | 775 | 0056 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1572_DS | 1572(虎科虎菁一路) DS | LINE161 | D13/161/1570/DS2 |  |  |  | DNP | 404 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D13 | 虎科DS | 161 | 161kV | 1570 | 虎科虎菁一路(1570) |  | DS3 | 1573 | [13 empty] | 0776 | 777 | 0057 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1573_DS | 1573(虎科虎菁一路) DS | LINE161 | D13/161/1570/DS3 |  |  |  | DNP | 405 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 161 | 161kV | 1570 | 虎科虎菁一路(1570) |  | E3 | 1573E | [13 empty] | 0778 | 779 | 0058 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1573E_ES | 1573E(虎科虎菁一路) ES | LINE161 | D13/161/1570/ES3 |  |  |  | DNP | 406 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D13 | 虎科DS | 161 | 161kV | 1580 | 虎科虎菁二路(1580) |  | PHA | [14 empty] | 0004 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.1580_PHA | 虎科虎菁二路(1580) 相間RY | LINE161 | D13/161/1580/PHA |  |  |  | DNP | 407 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1580 | 虎科虎菁二路(1580) |  | GDA | [14 empty] | 0005 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.1580_GDA | 虎科虎菁二路(1580) 接地RY | LINE161 | D13/161/1580/GDA |  |  |  | DNP | 408 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1580 | 虎科虎菁二路(1580) |  | 87A | [14 empty] | 0003 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.1580_87A | 虎科虎菁二路(1580) 87RY | LINE161 | D13/161/1580/87A |  |  |  | DNP | 409 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1580 | 虎科虎菁二路(1580) |  | 87UL | [14 empty] | 0550 |  | 0015 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1580_87UL | 虎科虎菁二路(1580) 87RY U/L | LINE161 | D13/161/1580/87UL |  |  |  | DNP | 410 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | 1580 | 虎科虎菁二路(1580) |  | CB | [14 empty] | 0110 |  | 0059 | [8 empty] | 161KV_N | [8 empty] | 虎科DS.1580_CB | 1580(虎科虎菁二路) CB | LINE161 | D13/161/1580/CB |  |  |  | DNP | 411 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 161 | 161kV | 1580 | 虎科虎菁二路(1580) |  | 79UL | [14 empty] | 0558 |  | 0016 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1580_79UL | 虎科虎菁二路(1580) 79RY U/L | LINE161 | D13/161/1580/79UL |  |  |  | DNP | 412 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | 1580 | 虎科虎菁二路(1580) |  | DS1 | 1581 | [13 empty] | 0780 | 781 | 0060 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1581_DS | 1581(虎科虎菁二路) DS | LINE161 | D13/161/1580/DS1 |  |  |  | DNP | 413 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D13 | 虎科DS | 161 | 161kV | 1580 | 虎科虎菁二路(1580) |  | DS2 | 1582 | [13 empty] | 0782 | 783 | 0061 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1582_DS | 1582(虎科虎菁二路) DS | LINE161 | D13/161/1580/DS2 |  |  |  | DNP | 414 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 161 | 161kV | 1580 | 虎科虎菁二路(1580) |  | DS3 | 1583 | [13 empty] | 0784 | 785 | 0062 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1583_DS | 1583(虎科虎菁二路) DS | LINE161 | D13/161/1580/DS3 |  |  |  | DNP | 415 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 161 | 161kV | 1580 | 虎科虎菁二路(1580) |  | E3 | 1583E | [13 empty] | 0786 | 787 | 0063 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1583E_ES | 1583E(虎科虎菁二路) ES | LINE161 | D13/161/1580/ES3 |  |  |  | DNP | 416 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | PHA | [14 empty] | 0012 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.1620_PHA | 虎科和鑫二路(1620) 相間RY | LINE161 | D13/161/1620/PHA |  |  |  | DNP | 417 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | GDA | [14 empty] | 0013 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.1620_GDA | 虎科和鑫二路(1620) 接地RY | LINE161 | D13/161/1620/GDA |  |  |  | DNP | 418 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | 87A2 | [14 empty] | 0011 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.1620_87A2 | 虎科和鑫二路(1620) #2 87RY | LINE161 | D13/161/1620/87A2 |  |  |  | DNP | 419 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | 87A1 | [14 empty] | 0010 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.1620_87A1 | 虎科和鑫二路(1620) #1 87RY | LINE161 | D13/161/1620/87A1 |  |  |  | DNP | 420 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | 1_87UL2 | [14 empty] | 0554 |  | 0022 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1620_87UL2 | 虎科和鑫二路(1620) #2 87RY U/L | LINE161 | D13/161/1620/1_87UL2 |  |  |  | DNP | 421 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | 1_87UL1 | [14 empty] | 0553 |  | 0020 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1620_87UL1 | 虎科和鑫二路(1620) #1 87RY U/L | LINE161 | D13/161/1620/1_87UL1 |  |  |  | DNP | 422 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | CB | [14 empty] | 0112 |  | 0069 | [8 empty] | 161KV_N | [8 empty] | 虎科DS.1620_CB | 1620(虎科和鑫二路) CB | LINE161 | D13/161/1620/CB |  |  |  | DNP | 423 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | 79UL | [14 empty] | 0560 |  | 0021 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1620_79UL | 虎科和鑫二路(1620) 79RY U/L | LINE161 | D13/161/1620/79UL |  |  |  | DNP | 424 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | DS1 | 1621 | [13 empty] | 0796 | 797 | 0070 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1621_DS | 1621(虎科和鑫二路) DS | LINE161 | D13/161/1620/DS1 |  |  |  | DNP | 425 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | DS2 | 1622 | [13 empty] | 0798 | 799 | 0071 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1622_DS | 1622(虎科和鑫二路) DS | LINE161 | D13/161/1620/DS2 |  |  |  | DNP | 426 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | DS3 | 1623 | [13 empty] | 0800 | 801 | 0072 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1623_DS | 1623(虎科和鑫二路) DS | LINE161 | D13/161/1620/DS3 |  |  |  | DNP | 427 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | E3 | 1623E | [13 empty] | 0802 | 803 | 0073 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1623E_ES | 1623E(虎科和鑫二路) ES | LINE161 | D13/161/1620/ES3 |  |  |  | DNP | 428 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D13 | 虎科DS | 161 | 161kV | 1630 | 越港虎科紅線(1630) |  | PHA | [14 empty] | 0015 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.1630_PHA | 越港虎科紅線(1630) 相間RY | LINE161 | D13/161/1630/PHA |  |  |  | DNP | 429 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1630 | 越港虎科紅線(1630) |  | GDA | [14 empty] | 0016 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.1630_GDA | 越港虎科紅線(1630) 接地RY | LINE161 | D13/161/1630/GDA |  |  |  | DNP | 430 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1630 | 越港虎科紅線(1630) |  | 87A | [14 empty] | 0014 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.1630_87A | 越港虎科紅線(1630) 87RY | LINE161 | D13/161/1630/87A |  |  |  | DNP | 431 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1630 | 越港虎科紅線(1630) |  | 87UL | [14 empty] | 0555 |  | 0023 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1630_87UL | 越港虎科紅線(1630) 87RY U/L | LINE161 | D13/161/1630/87UL |  |  |  | DNP | 432 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | 1630 | 越港虎科紅線(1630) |  | CB | [14 empty] | 0113 |  | 0074 | [8 empty] | 161KV_N | [8 empty] | 虎科DS.1630_CB | 1630(越港虎科紅線) CB | LINE161 | D13/161/1630/CB |  |  |  | DNP | 433 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 161 | 161kV | 1630 | 越港虎科紅線(1630) |  | 79UL | [14 empty] | 0561 |  | 0024 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1630_79UL | 越港虎科紅線(1630) 79RY U/L | LINE161 | D13/161/1630/79UL |  |  |  | DNP | 434 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | 1630 | 越港虎科紅線(1630) |  | DS1 | 1631 | [13 empty] | 0804 | 805 | 0075 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1631_DS | 1631(越港虎科紅線) DS | LINE161 | D13/161/1630/DS1 |  |  |  | DNP | 435 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 161 | 161kV | 1630 | 越港虎科紅線(1630) |  | DS2 | 1632 | [13 empty] | 0806 | 807 | 0076 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1632_DS | 1632(越港虎科紅線) DS | LINE161 | D13/161/1630/DS2 |  |  |  | DNP | 436 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D13 | 虎科DS | 161 | 161kV | 1630 | 越港虎科紅線(1630) |  | DS3 | 1633 | [13 empty] | 0808 | 809 | 0077 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1633_DS | 1633(越港虎科紅線) DS | LINE161 | D13/161/1630/DS3 |  |  |  | DNP | 437 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 161 | 161kV | 1630 | 越港虎科紅線(1630) |  | E3 | 1633E | [13 empty] | 0810 | 811 | 0078 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1633E_ES | 1633E(越港虎科紅線) ES | LINE161 | D13/161/1630/ES3 |  |  |  | DNP | 438 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D13 | 虎科DS | 161 | 161kV | 1640 | 越港虎科白線(1640) |  | PHA | [14 empty] | 0018 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.1640_PHA | 越港虎科白線(1640) 相間RY | LINE161 | D13/161/1640/PHA |  |  |  | DNP | 439 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1640 | 越港虎科白線(1640) |  | GDA | [14 empty] | 0019 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.1640_GDA | 越港虎科白線(1640) 接地RY | LINE161 | D13/161/1640/GDA |  |  |  | DNP | 440 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1640 | 越港虎科白線(1640) |  | 87A | [14 empty] | 0017 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.1640_87A | 越港虎科白線(1640) 87RY | LINE161 | D13/161/1640/87A |  |  |  | DNP | 441 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1640 | 越港虎科白線(1640) |  | 87UL | [14 empty] | 0556 |  | 0025 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1640_87UL | 越港虎科白線(1640) 87RY U/L | LINE161 | D13/161/1640/87UL |  |  |  | DNP | 442 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | 1640 | 越港虎科白線(1640) |  | CB | [14 empty] | 0114 |  | 0079 | [8 empty] | 161KV_N | [8 empty] | 虎科DS.1640_CB | 1640(越港虎科白線) CB | LINE161 | D13/161/1640/CB |  |  |  | DNP | 443 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 161 | 161kV | 1640 | 越港虎科白線(1640) |  | 79UL | [14 empty] | 0562 |  | 0026 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1640_79UL | 越港虎科白線(1640) 79RY U/L | LINE161 | D13/161/1640/79UL |  |  |  | DNP | 444 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | 1640 | 越港虎科白線(1640) |  | DS1 | 1641 | [13 empty] | 0812 | 813 | 0080 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1641_DS | 1641(越港虎科白線) DS | LINE161 | D13/161/1640/DS1 |  |  |  | DNP | 445 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D13 | 虎科DS | 161 | 161kV | 1640 | 越港虎科白線(1640) |  | DS2 | 1642 | [13 empty] | 0814 | 815 | 0081 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1642_DS | 1642(越港虎科白線) DS | LINE161 | D13/161/1640/DS2 |  |  |  | DNP | 446 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 161 | 161kV | 1640 | 越港虎科白線(1640) |  | DS3 | 1643 | [13 empty] | 0816 | 817 | 0082 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1643_DS | 1643(越港虎科白線) DS | LINE161 | D13/161/1640/DS3 |  |  |  | DNP | 447 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 161 | 161kV | 1640 | 越港虎科白線(1640) |  | E3 | 1643E | [13 empty] | 0818 | 819 | 0083 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1643E_ES | 1643E(越港虎科白線) ES | LINE161 | D13/161/1640/ES3 |  |  |  | DNP | 448 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D13 | 虎科DS | 11 | 11kV | XO32 | 科12線(XO32) |  | PHA | [14 empty] | 0262 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO32_PHA | 11KV科12線(XO32) 相間RY | FEEDER | D13/11/XO32/PHA |  |  |  | DNP | 449 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO32 | 科12線(XO32) |  | GDA | [14 empty] | 0263 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO32_GDA | 11KV科12線(XO32) 接地RY | FEEDER | D13/11/XO32/GDA |  |  |  | DNP | 450 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO32 | 科12線(XO32) 79RY |  | 79UL | [14 empty] | 0655 |  | 0133 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO32_79UL | 11KV科12線(XO32) 79RY U/L | FEEDER | D13/11/XO32/79UL |  |  |  | DNP | 451 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 11 | 11kV | XO32_LCO | 科12線(XO32) LCO |  | TapPosMv | [14 empty] | 0656 |  | 0134 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO32_LCO_TAP | 11KV科12線(XO32) LCO TAP | FEEDER | D13/11/XO32/ADJ |  |  |  | DNP | 452 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D13 | 虎科DS | 11 | 11kV | XO32 | XO32(11KV科12線) |  | CB | [14 empty] | 0264 |  | 0132 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO32_CB | XO32(11KV科12線) CB | FEEDER | D13/11/XO32/CB |  |  |  | DNP | 453 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | XO33 | 科13線(XO33) |  | PHA | [14 empty] | 0265 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO33_PHA | 11KV科13線(XO33) 相間RY | FEEDER | D13/11/XO33/PHA |  |  |  | DNP | 454 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO33 | 科13線(XO33) |  | GDA | [14 empty] | 0266 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO33_GDA | 11KV科13線(XO33) 接地RY | FEEDER | D13/11/XO33/GDA |  |  |  | DNP | 455 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO33 | 科13線(XO33) 79RY |  | 79UL | [14 empty] | 0657 |  | 0136 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO33_79UL | 11KV科13線(XO33) 79RY U/L | FEEDER | D13/11/XO33/79UL |  |  |  | DNP | 456 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 11 | 11kV | XO33_LCO | 科13線(XO33) LCO |  | TapPosMv | [14 empty] | 0658 |  | 0137 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO33_LCO_TAP | 11KV科13線(XO33) LCO TAP | FEEDER | D13/11/XO33/ADJ |  |  |  | DNP | 457 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D13 | 虎科DS | 11 | 11kV | XO33 | XO33(11KV科13線) |  | CB | [14 empty] | 0267 |  | 0135 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO33_CB | XO33(11KV科13線) CB | FEEDER | D13/11/XO33/CB |  |  |  | DNP | 458 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | XO34 | 科14線(XO34) |  | PHA | [14 empty] | 0268 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO34_PHA | 11KV科14線(XO34) 相間RY | FEEDER | D13/11/XO34/PHA |  |  |  | DNP | 459 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO34 | 科14線(XO34) |  | GDA | [14 empty] | 0269 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO34_GDA | 11KV科14線(XO34) 接地RY | FEEDER | D13/11/XO34/GDA |  |  |  | DNP | 460 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO34 | 科14線(XO34) 79RY |  | 79UL | [14 empty] | 0659 |  | 0139 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO34_79UL | 11KV科14線(XO34) 79RY U/L | FEEDER | D13/11/XO34/79UL |  |  |  | DNP | 461 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 11 | 11kV | XO34_LCO | 科14線(XO34) LCO |  | TapPosMv | [14 empty] | 0660 |  | 0140 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO34_LCO_TAP | 11KV科14線(XO34) LCO TAP | FEEDER | D13/11/XO34/ADJ |  |  |  | DNP | 462 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D13 | 虎科DS | 11 | 11kV | XO34 | XO34(11KV科14線) |  | CB | [14 empty] | 0270 |  | 0138 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO34_CB | XO34(11KV科14線) CB | FEEDER | D13/11/XO34/CB |  |  |  | DNP | 463 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | XO35 | 科15線(XO35) |  | PHA | [14 empty] | 0271 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO35_PHA | 11KV科15線(XO35) 相間RY | FEEDER | D13/11/XO35/PHA |  |  |  | DNP | 464 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO35 | 科15線(XO35) |  | GDA | [14 empty] | 0272 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO35_GDA | 11KV科15線(XO35) 接地RY | FEEDER | D13/11/XO35/GDA |  |  |  | DNP | 465 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO35 | 科15線(XO35) 79RY |  | 79UL | [14 empty] | 0661 |  | 0142 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO35_79UL | 11KV科15線(XO35) 79RY U/L | FEEDER | D13/11/XO35/79UL |  |  |  | DNP | 466 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 11 | 11kV | XO35_LCO | 科15線(XO35) LCO |  | TapPosMv | [14 empty] | 0662 |  | 0143 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO35_LCO_TAP | 11KV科15線(XO35) LCO TAP | FEEDER | D13/11/XO35/ADJ |  |  |  | DNP | 467 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D13 | 虎科DS | 11 | 11kV | XO35 | XO35(11KV科15線) |  | CB | [14 empty] | 0273 |  | 0141 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO35_CB | XO35(11KV科15線) CB | FEEDER | D13/11/XO35/CB |  |  |  | DNP | 468 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | XO36 | 科16線(XO36) |  | PHA | [14 empty] | 0280 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO36_PHA | 11KV科16線(XO36) 相間RY | FEEDER | D13/11/XO36/PHA |  |  |  | DNP | 469 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO36 | 科16線(XO36) |  | GDA | [14 empty] | 0281 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO36_GDA | 11KV科16線(XO36) 接地RY | FEEDER | D13/11/XO36/GDA |  |  |  | DNP | 470 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO36 | 科16線(XO36) 79RY |  | 79UL | [14 empty] | 0663 |  | 0148 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO36_79UL | 11KV科16線(XO36) 79RY U/L | FEEDER | D13/11/XO36/79UL |  |  |  | DNP | 471 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 11 | 11kV | XO36_LCO | 科16線(XO36) LCO |  | TapPosMv | [14 empty] | 0664 |  | 0149 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO36_LCO_TAP | 11KV科16線(XO36) LCO TAP | FEEDER | D13/11/XO36/ADJ |  |  |  | DNP | 472 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D13 | 虎科DS | 11 | 11kV | XO36 | XO36(11KV科16線) |  | CB | [14 empty] | 0282 |  | 0147 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO36_CB | XO36(11KV科16線) CB | FEEDER | D13/11/XO36/CB |  |  |  | DNP | 473 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | XO37 | 科17線(XO37) |  | PHA | [14 empty] | 0283 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO37_PHA | 11KV科17線(XO37) 相間RY | FEEDER | D13/11/XO37/PHA |  |  |  | DNP | 474 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO37 | 科17線(XO37) |  | GDA | [14 empty] | 0284 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO37_GDA | 11KV科17線(XO37) 接地RY | FEEDER | D13/11/XO37/GDA |  |  |  | DNP | 475 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO37 | 科17線(XO37) 79RY |  | 79UL | [14 empty] | 0665 |  | 0151 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO37_79UL | 11KV科17線(XO37) 79RY U/L | FEEDER | D13/11/XO37/79UL |  |  |  | DNP | 476 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 11 | 11kV | XO37_LCO | 科17線(XO37) LCO |  | TapPosMv | [14 empty] | 0666 |  | 0152 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO37_LCO_TAP | 11KV科17線(XO37) LCO TAP | FEEDER | D13/11/XO37/ADJ |  |  |  | DNP | 477 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D13 | 虎科DS | 11 | 11kV | XO37 | XO37(11KV科17線) |  | CB | [14 empty] | 0285 |  | 0150 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO37_CB | XO37(11KV科17線) CB | FEEDER | D13/11/XO37/CB |  |  |  | DNP | 478 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | XO38 | 科18線(XO38) |  | PHA | [14 empty] | 0286 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO38_PHA | 11KV科18線(XO38) 相間RY | FEEDER | D13/11/XO38/PHA |  |  |  | DNP | 479 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO38 | 科18線(XO38) |  | GDA | [14 empty] | 0287 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO38_GDA | 11KV科18線(XO38) 接地RY | FEEDER | D13/11/XO38/GDA |  |  |  | DNP | 480 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO38 | 科18線(XO38) 79RY |  | 79UL | [14 empty] | 0667 |  | 0154 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO38_79UL | 11KV科18線(XO38) 79RY U/L | FEEDER | D13/11/XO38/79UL |  |  |  | DNP | 481 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 11 | 11kV | XO38_LCO | 科18線(XO38) LCO |  | TapPosMv | [14 empty] | 0668 |  | 0155 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO38_LCO_TAP | 11KV科18線(XO38) LCO TAP | FEEDER | D13/11/XO38/ADJ |  |  |  | DNP | 482 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D13 | 虎科DS | 11 | 11kV | XO38 | XO38(11KV科18線) |  | CB | [14 empty] | 0288 |  | 0153 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO38_CB | XO38(11KV科18線) CB | FEEDER | D13/11/XO38/CB |  |  |  | DNP | 483 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | XO39 | 科19線(XO39) |  | PHA | [14 empty] | 0289 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO39_PHA | 11KV科19線(XO39) 相間RY | FEEDER | D13/11/XO39/PHA |  |  |  | DNP | 484 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO39 | 科19線(XO39) |  | GDA | [14 empty] | 0290 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO39_GDA | 11KV科19線(XO39) 接地RY | FEEDER | D13/11/XO39/GDA |  |  |  | DNP | 485 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO39 | 科19線(XO39) 79RY |  | 79UL | [14 empty] | 0669 |  | 0157 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO39_79UL | 11KV科19線(XO39) 79RY U/L | FEEDER | D13/11/XO39/79UL |  |  |  | DNP | 486 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 11 | 11kV | XO39_LCO | 科19線(XO39) LCO |  | TapPosMv | [14 empty] | 0670 |  | 0158 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO39_LCO_TAP | 11KV科19線(XO39) LCO TAP | FEEDER | D13/11/XO39/ADJ |  |  |  | DNP | 487 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D13 | 虎科DS | 11 | 11kV | XO39 | XO39(11KV科19線) |  | CB | [14 empty] | 0291 |  | 0156 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO39_CB | XO39(11KV科19線) CB | FEEDER | D13/11/XO39/CB |  |  |  | DNP | 488 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | XO40 | 科20線(XO40) |  | PHA | [14 empty] | 0292 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO40_PHA | 11KV科20線(XO40) 相間RY | FEEDER | D13/11/XO40/PHA |  |  |  | DNP | 489 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO40 | 科20線(XO40) |  | GDA | [14 empty] | 0293 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO40_GDA | 11KV科20線(XO40) 接地RY | FEEDER | D13/11/XO40/GDA |  |  |  | DNP | 490 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | XO40 | 科20線(XO40) 79RY |  | 79UL | [14 empty] | 0671 |  | 0160 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO40_79UL | 11KV科20線(XO40) 79RY U/L | FEEDER | D13/11/XO40/79UL |  |  |  | DNP | 491 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 11 | 11kV | XO40_LCO | 科20線(XO40) LCO |  | TapPosMv | [14 empty] | 0672 |  | 0161 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO40_LCO_TAP | 11KV科20線(XO40) LCO TAP | FEEDER | D13/11/XO40/ADJ |  |  |  | DNP | 492 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D13 | 虎科DS | 11 | 11kV | XO40 | XO40(11KV科20線) |  | CB | [14 empty] | 0294 |  | 0159 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO40_CB | XO40(11KV科20線) CB | FEEDER | D13/11/XO40/CB |  |  |  | DNP | 493 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO61 | 科61線(XO61) |  | PHA | [14 empty] | 0301 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO61_PHA | 23KV科61線(XO61) 相間RY | FEEDER | D13/22/XO61/PHA |  |  |  | DNP | 494 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO61 | 科61線(XO61) |  | GDA | [14 empty] | 0302 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO61_GDA | 23KV科61線(XO61) 接地RY | FEEDER | D13/22/XO61/GDA |  |  |  | DNP | 495 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO61 | 科61線(XO61) 79RY |  | 79UL | [14 empty] | 0673 |  | 0166 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO61_79UL | 23KV科61線(XO61) 79RY U/L | FEEDER | D13/22/XO61/79UL |  |  |  | DNP | 496 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 22 | 22kV | XO61_LCO | 科61線(XO61) LCO |  | TapPosMv | [14 empty] | 0674 |  | 0167 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO61_LCO_TAP | 23KV科61線(XO61) LCO TAP | FEEDER | D13/22/XO61/ADJ |  |  |  | DNP | 497 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D13 | 虎科DS | 22 | 22kV | XO61 | XO61(23KV科61線) |  | CB | [14 empty] | 0303 |  | 0165 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO61_CB | XO61(23KV科61線) CB | FEEDER | D13/22/XO61/CB |  |  |  | DNP | 498 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO62 | 科62線(XO62) |  | PHA | [14 empty] | 0304 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO62_PHA | 23KV科62線(XO62) 相間RY | FEEDER | D13/22/XO62/PHA |  |  |  | DNP | 499 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO62 | 科62線(XO62) |  | GDA | [14 empty] | 0305 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO62_GDA | 23KV科62線(XO62) 接地RY | FEEDER | D13/22/XO62/GDA |  |  |  | DNP | 500 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO62 | 科62線(XO62) 79RY |  | 79UL | [14 empty] | 0675 |  | 0169 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO62_79UL | 23KV科62線(XO62) 79RY U/L | FEEDER | D13/22/XO62/79UL |  |  |  | DNP | 501 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 22 | 22kV | XO62_LCO | 科62線(XO62) LCO |  | TapPosMv | [14 empty] | 0676 |  | 0170 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO62_LCO_TAP | 23KV科62線(XO62) LCO TAP | FEEDER | D13/22/XO62/ADJ |  |  |  | DNP | 502 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D13 | 虎科DS | 22 | 22kV | XO62 | XO62(23KV科62線) |  | CB | [14 empty] | 0306 |  | 0168 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO62_CB | XO62(23KV科62線) CB | FEEDER | D13/22/XO62/CB |  |  |  | DNP | 503 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO63 | 科63線(XO63) |  | PHA | [14 empty] | 0307 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO63_PHA | 23KV科63線(XO63) 相間RY | FEEDER | D13/22/XO63/PHA |  |  |  | DNP | 504 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO63 | 科63線(XO63) |  | GDA | [14 empty] | 0308 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO63_GDA | 23KV科63線(XO63) 接地RY | FEEDER | D13/22/XO63/GDA |  |  |  | DNP | 505 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO63 | 科63線(XO63) 79RY |  | 79UL | [14 empty] | 0677 |  | 0172 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO63_79UL | 23KV科63線(XO63) 79RY U/L | FEEDER | D13/22/XO63/79UL |  |  |  | DNP | 506 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 22 | 22kV | XO63_LCO | 科63線(XO63) LCO |  | TapPosMv | [14 empty] | 0678 |  | 0173 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO63_LCO_TAP | 23KV科63線(XO63) LCO TAP | FEEDER | D13/22/XO63/ADJ |  |  |  | DNP | 507 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D13 | 虎科DS | 22 | 22kV | XO63 | XO63(23KV科63線) |  | CB | [14 empty] | 0309 |  | 0171 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO63_CB | XO63(23KV科63線) CB | FEEDER | D13/22/XO63/CB |  |  |  | DNP | 508 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO64 | 科64線(XO64) |  | PHA | [14 empty] | 0310 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO64_PHA | 23KV科64線(XO64) 相間RY | FEEDER | D13/22/XO64/PHA |  |  |  | DNP | 509 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO64 | 科64線(XO64) |  | GDA | [14 empty] | 0311 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO64_GDA | 23KV科64線(XO64) 接地RY | FEEDER | D13/22/XO64/GDA |  |  |  | DNP | 510 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO64 | 科64線(XO64) 79RY |  | 79UL | [14 empty] | 0679 |  | 0175 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO64_79UL | 23KV科64線(XO64) 79RY U/L | FEEDER | D13/22/XO64/79UL |  |  |  | DNP | 511 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 22 | 22kV | XO64_LCO | 科64線(XO64) LCO |  | TapPosMv | [14 empty] | 0680 |  | 0176 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO64_LCO_TAP | 23KV科64線(XO64) LCO TAP | FEEDER | D13/22/XO64/ADJ |  |  |  | DNP | 512 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D13 | 虎科DS | 22 | 22kV | XO64 | XO64(23KV科64線) |  | CB | [14 empty] | 0312 |  | 0174 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO64_CB | XO64(23KV科64線) CB | FEEDER | D13/22/XO64/CB |  |  |  | DNP | 513 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO65 | 科65線(XO65) |  | PHA | [14 empty] | 0316 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO65_PHA | 23KV科65線(XO65) 相間RY | FEEDER | D13/22/XO65/PHA |  |  |  | DNP | 514 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO65 | 科65線(XO65) |  | GDA | [14 empty] | 0317 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO65_GDA | 23KV科65線(XO65) 接地RY | FEEDER | D13/22/XO65/GDA |  |  |  | DNP | 515 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO65 | 科65線(XO65) 79RY |  | 79UL | [14 empty] | 0681 |  | 0180 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO65_79UL | 23KV科65線(XO65) 79RY U/L | FEEDER | D13/22/XO65/79UL |  |  |  | DNP | 516 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 22 | 22kV | XO65_LCO | 科65線(XO65) LCO |  | TapPosMv | [14 empty] | 0682 |  | 0181 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO65_LCO_TAP | 23KV科65線(XO65) LCO TAP | FEEDER | D13/22/XO65/ADJ |  |  |  | DNP | 517 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D13 | 虎科DS | 22 | 22kV | XO65 | XO65(23KV科65線) |  | CB | [14 empty] | 0318 |  | 0179 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO65_CB | XO65(23KV科65線) CB | FEEDER | D13/22/XO65/CB |  |  |  | DNP | 518 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO66 | 科66線(XO66) |  | PHA | [14 empty] | 0319 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO66_PHA | 23KV科66線(XO66) 相間RY | FEEDER | D13/22/XO66/PHA |  |  |  | DNP | 519 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO66 | 科66線(XO66) |  | GDA | [14 empty] | 0320 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO66_GDA | 23KV科66線(XO66) 接地RY | FEEDER | D13/22/XO66/GDA |  |  |  | DNP | 520 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO66 | 科66線(XO66) 79RY |  | 79UL | [14 empty] | 0683 |  | 0183 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO66_79UL | 23KV科66線(XO66) 79RY U/L | FEEDER | D13/22/XO66/79UL |  |  |  | DNP | 521 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 22 | 22kV | XO66_LCO | 科66線(XO66) LCO |  | TapPosMv | [14 empty] | 0684 |  | 0184 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO66_LCO_TAP | 23KV科66線(XO66) LCO TAP | FEEDER | D13/22/XO66/ADJ |  |  |  | DNP | 522 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D13 | 虎科DS | 22 | 22kV | XO66 | XO66(23KV科66線) |  | CB | [14 empty] | 0321 |  | 0182 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO66_CB | XO66(23KV科66線) CB | FEEDER | D13/22/XO66/CB |  |  |  | DNP | 523 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO67 | 科67線(XO67) |  | PHA | [14 empty] | 0322 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO67_PHA | 23KV科67線(XO67) 相間RY | FEEDER | D13/22/XO67/PHA |  |  |  | DNP | 524 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO67 | 科67線(XO67) |  | GDA | [14 empty] | 0323 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO67_GDA | 23KV科67線(XO67) 接地RY | FEEDER | D13/22/XO67/GDA |  |  |  | DNP | 525 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO67 | 科67線(XO67) 79RY |  | 79UL | [14 empty] | 0685 |  | 0186 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO67_79UL | 23KV科67線(XO67) 79RY U/L | FEEDER | D13/22/XO67/79UL |  |  |  | DNP | 526 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 22 | 22kV | XO67_LCO | 科67線(XO67) LCO |  | TapPosMv | [14 empty] | 0686 |  | 0187 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO67_LCO_TAP | 23KV科67線(XO67) LCO TAP | FEEDER | D13/22/XO67/ADJ |  |  |  | DNP | 527 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D13 | 虎科DS | 22 | 22kV | XO67 | XO67(23KV科67線) |  | CB | [14 empty] | 0324 |  | 0185 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO67_CB | XO67(23KV科67線) CB | FEEDER | D13/22/XO67/CB |  |  |  | DNP | 528 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO68 | 科68線(XO68) |  | PHA | [14 empty] | 0325 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO68_PHA | 23KV科68線(XO68) 相間RY | FEEDER | D13/22/XO68/PHA |  |  |  | DNP | 529 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO68 | 科68線(XO68) |  | GDA | [14 empty] | 0326 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO68_GDA | 23KV科68線(XO68) 接地RY | FEEDER | D13/22/XO68/GDA |  |  |  | DNP | 530 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO68 | 科68線(XO68) 79RY |  | 79UL | [14 empty] | 0687 |  | 0189 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO68_79UL | 23KV科68線(XO68) 79RY U/L | FEEDER | D13/22/XO68/79UL |  |  |  | DNP | 531 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 22 | 22kV | XO68_LCO | 科68線(XO68) LCO |  | TapPosMv | [14 empty] | 0688 |  | 0190 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO68_LCO_TAP | 23KV科68線(XO68) LCO TAP | FEEDER | D13/22/XO68/ADJ |  |  |  | DNP | 532 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D13 | 虎科DS | 22 | 22kV | XO68 | XO68(23KV科68線) |  | CB | [14 empty] | 0327 |  | 0188 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO68_CB | XO68(23KV科68線) CB | FEEDER | D13/22/XO68/CB |  |  |  | DNP | 533 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO71 | 科71線(XO71) |  | PHA | [14 empty] | 0334 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO71_PHA | 23KV科71線(XO71) 相間RY | FEEDER | D13/22/XO71/PHA |  |  |  | DNP | 534 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO71 | 科71線(XO71) |  | GDA | [14 empty] | 0335 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO71_GDA | 23KV科71線(XO71) 接地RY | FEEDER | D13/22/XO71/GDA |  |  |  | DNP | 535 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO71 | 科71線(XO71) 79RY |  | 79UL | [14 empty] | 0689 |  | 0195 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO71_79UL | 23KV科71線(XO71) 79RY U/L | FEEDER | D13/22/XO71/79UL |  |  |  | DNP | 536 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 22 | 22kV | XO71_LCO | 科71線(XO71) LCO |  | TapPosMv | [14 empty] | 0690 |  | 0196 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO71_LCO_TAP | 23KV科71線(XO71) LCO TAP | FEEDER | D13/22/XO71/ADJ |  |  |  | DNP | 537 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D13 | 虎科DS | 22 | 22kV | XO71 | XO71(23KV科71線) |  | CB | [14 empty] | 0336 |  | 0194 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO71_CB | XO71(23KV科71線) CB | FEEDER | D13/22/XO71/CB |  |  |  | DNP | 538 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO72 | 科72線(XO72) |  | PHA | [14 empty] | 0337 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO72_PHA | 23KV科72線(XO72) 相間RY | FEEDER | D13/22/XO72/PHA |  |  |  | DNP | 539 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO72 | 科72線(XO72) |  | GDA | [14 empty] | 0338 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO72_GDA | 23KV科72線(XO72) 接地RY | FEEDER | D13/22/XO72/GDA |  |  |  | DNP | 540 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO72 | 科72線(XO72) 79RY |  | 79UL | [14 empty] | 0691 |  | 0198 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO72_79UL | 23KV科72線(XO72) 79RY U/L | FEEDER | D13/22/XO72/79UL |  |  |  | DNP | 541 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 22 | 22kV | XO72_LCO | 科72線(XO72) LCO |  | TapPosMv | [14 empty] | 0692 |  | 0199 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO72_LCO_TAP | 23KV科72線(XO72) LCO TAP | FEEDER | D13/22/XO72/ADJ |  |  |  | DNP | 542 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D13 | 虎科DS | 22 | 22kV | XO72 | XO72(23KV科72線) |  | CB | [14 empty] | 0339 |  | 0197 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO72_CB | XO72(23KV科72線) CB | FEEDER | D13/22/XO72/CB |  |  |  | DNP | 543 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO73 | 科73線(XO73) |  | PHA | [14 empty] | 0340 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO73_PHA | 23KV科73線(XO73) 相間RY | FEEDER | D13/22/XO73/PHA |  |  |  | DNP | 544 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO73 | 科73線(XO73) |  | GDA | [14 empty] | 0341 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO73_GDA | 23KV科73線(XO73) 接地RY | FEEDER | D13/22/XO73/GDA |  |  |  | DNP | 545 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO73 | 科73線(XO73) 79RY |  | 79UL | [14 empty] | 0693 |  | 0201 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO73_79UL | 23KV科73線(XO73) 79RY U/L | FEEDER | D13/22/XO73/79UL |  |  |  | DNP | 546 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 22 | 22kV | XO73_LCO | 科73線(XO73) LCO |  | TapPosMv | [14 empty] | 0694 |  | 0202 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO73_LCO_TAP | 23KV科73線(XO73) LCO TAP | FEEDER | D13/22/XO73/ADJ |  |  |  | DNP | 547 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D13 | 虎科DS | 22 | 22kV | XO73 | XO73(23KV科73線) |  | CB | [14 empty] | 0342 |  | 0200 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO73_CB | XO73(23KV科73線) CB | FEEDER | D13/22/XO73/CB |  |  |  | DNP | 548 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO74 | 科74線(XO74) |  | PHA | [14 empty] | 0343 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO74_PHA | 23KV科74線(XO74) 相間RY | FEEDER | D13/22/XO74/PHA |  |  |  | DNP | 549 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO74 | 科74線(XO74) |  | GDA | [14 empty] | 0344 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO74_GDA | 23KV科74線(XO74) 接地RY | FEEDER | D13/22/XO74/GDA |  |  |  | DNP | 550 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO74 | 科74線(XO74) 79RY |  | 79UL | [14 empty] | 0695 |  | 0204 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO74_79UL | 23KV科74線(XO74) 79RY U/L | FEEDER | D13/22/XO74/79UL |  |  |  | DNP | 551 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 22 | 22kV | XO74_LCO | 科74線(XO74) LCO |  | TapPosMv | [14 empty] | 0696 |  | 0205 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO74_LCO_TAP | 23KV科74線(XO74) LCO TAP | FEEDER | D13/22/XO74/ADJ |  |  |  | DNP | 552 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D13 | 虎科DS | 22 | 22kV | XO74 | XO74(23KV科74線) |  | CB | [14 empty] | 0345 |  | 0203 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO74_CB | XO74(23KV科74線) CB | FEEDER | D13/22/XO74/CB |  |  |  | DNP | 553 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO75 | 科75線(XO75) |  | PHA | [14 empty] | 0355 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO75_PHA | 23KV科75線(XO75) 相間RY | FEEDER | D13/22/XO75/PHA |  |  |  | DNP | 554 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO75 | 科75線(XO75) |  | GDA | [14 empty] | 0356 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO75_GDA | 23KV科75線(XO75) 接地RY | FEEDER | D13/22/XO75/GDA |  |  |  | DNP | 555 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO75 | 科75線(XO75) 79RY |  | 79UL | [14 empty] | 0697 |  | 0211 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO75_79UL | 23KV科75線(XO75) 79RY U/L | FEEDER | D13/22/XO75/79UL |  |  |  | DNP | 556 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 22 | 22kV | XO75_LCO | 科75線(XO75) LCO |  | TapPosMv | [14 empty] | 0698 |  | 0212 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO75_LCO_TAP | 23KV科75線(XO75) LCO TAP | FEEDER | D13/22/XO75/ADJ |  |  |  | DNP | 557 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D13 | 虎科DS | 22 | 22kV | XO75 | XO75(23KV科75線) |  | CB | [14 empty] | 0357 |  | 0210 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO75_CB | XO75(23KV科75線) CB | FEEDER | D13/22/XO75/CB |  |  |  | DNP | 558 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO76 | 科76線(XO76) |  | PHA | [14 empty] | 0358 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO76_PHA | 23KV科76線(XO76) 相間RY | FEEDER | D13/22/XO76/PHA |  |  |  | DNP | 559 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO76 | 科76線(XO76) |  | GDA | [14 empty] | 0359 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO76_GDA | 23KV科76線(XO76) 接地RY | FEEDER | D13/22/XO76/GDA |  |  |  | DNP | 560 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO76 | 科76線(XO76) 79RY |  | 79UL | [14 empty] | 0699 |  | 0214 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO76_79UL | 23KV科76線(XO76) 79RY U/L | FEEDER | D13/22/XO76/79UL |  |  |  | DNP | 561 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 22 | 22kV | XO76_LCO | 科76線(XO76) LCO |  | TapPosMv | [14 empty] | 0700 |  | 0215 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO76_LCO_TAP | 23KV科76線(XO76) LCO TAP | FEEDER | D13/22/XO76/ADJ |  |  |  | DNP | 562 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D13 | 虎科DS | 22 | 22kV | XO76 | XO76(23KV科76線) |  | CB | [14 empty] | 0360 |  | 0213 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO76_CB | XO76(23KV科76線) CB | FEEDER | D13/22/XO76/CB |  |  |  | DNP | 563 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO77 | 科77線(XO77) |  | PHA | [14 empty] | 0361 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO77_PHA | 23KV科77線(XO77) 相間RY | FEEDER | D13/22/XO77/PHA |  |  |  | DNP | 564 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO77 | 科77線(XO77) |  | GDA | [14 empty] | 0362 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO77_GDA | 23KV科77線(XO77) 接地RY | FEEDER | D13/22/XO77/GDA |  |  |  | DNP | 565 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO77 | 科77線(XO77) 79RY |  | 79UL | [14 empty] | 0701 |  | 0217 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO77_79UL | 23KV科77線(XO77) 79RY U/L | FEEDER | D13/22/XO77/79UL |  |  |  | DNP | 566 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 22 | 22kV | XO77_LCO | 科77線(XO77) LCO |  | TapPosMv | [14 empty] | 0702 |  | 0218 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO77_LCO_TAP | 23KV科77線(XO77) LCO TAP | FEEDER | D13/22/XO77/ADJ |  |  |  | DNP | 567 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D13 | 虎科DS | 22 | 22kV | XO77 | XO77(23KV科77線) |  | CB | [14 empty] | 0363 |  | 0216 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO77_CB | XO77(23KV科77線) CB | FEEDER | D13/22/XO77/CB |  |  |  | DNP | 568 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | XO78 | 科78線(XO78) |  | PHA | [14 empty] | 0364 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO78_PHA | 23KV科78線(XO78) 相間RY | FEEDER | D13/22/XO78/PHA |  |  |  | DNP | 569 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO78 | 科78線(XO78) |  | GDA | [14 empty] | 0365 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO78_GDA | 23KV科78線(XO78) 接地RY | FEEDER | D13/22/XO78/GDA |  |  |  | DNP | 570 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | XO78 | 科78線(XO78) 79RY |  | 79UL | [14 empty] | 0703 |  | 0220 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO78_79UL | 23KV科78線(XO78) 79RY U/L | FEEDER | D13/22/XO78/79UL |  |  |  | DNP | 571 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 22 | 22kV | XO78_LCO | 科78線(XO78) LCO |  | TapPosMv | [14 empty] | 0704 |  | 0221 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO78_LCO_TAP | 23KV科78線(XO78) LCO TAP | FEEDER | D13/22/XO78/ADJ |  |  |  | DNP | 572 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D13 | 虎科DS | 22 | 22kV | XO78 | XO78(23KV科78線) |  | CB | [14 empty] | 0366 |  | 0219 | [8 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO78_CB | XO78(23KV科78線) CB | FEEDER | D13/22/XO78/CB |  |  |  | DNP | 573 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 100 | TIE(100) |  | CB | [14 empty] | 0258 |  | 0224 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.100_CB | 100(TIE) CB | TIE | D13/11/100/CB |  |  |  | DNP | 574 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 100 | TIE(100) |  | 51A | [14 empty] | 0256 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.100_51A | 11KV TIE(100) 51RY | TIE | D13/11/100/PHA |  |  |  | DNP | 575 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 100 | TIE(100) |  | 51NA | [14 empty] | 0257 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.100_51NA | 11KV TIE(100) 51N RY | TIE | D13/11/100/GDA |  |  |  | DNP | 576 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [14 empty] | 0118 |  | 0051 | [8 empty] | 161KV_N | [8 empty] | 虎科DS.1500_CB | 1500(TIE) CB | TIE | D13/161/1500/CB |  |  |  | DNP | 577 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 1500 | TIE(1500) |  | 50A | [14 empty] | 0080 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.1500_50A | 161KV TIE(1500) 50RY | TIE | D13/161/1500/50A |  |  |  | DNP | 578 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [13 empty] | 0768 | 769 | 0052 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1501_DS | 1501(TIE) DS | TIE | D13/161/1500/DS1 |  |  |  | DNP | 579 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [13 empty] | 0770 | 771 | 0053 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1502_DS | 1502(TIE) DS | TIE | D13/161/1500/DS2 |  |  |  | DNP | 580 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 0 |  | 1500 | TIE(1500) |  | 50SA | [14 empty] | 0610 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.1500_50SA | 161KV TIE(1500) 50RY 測試/正常 | TIE | D13/161/1500/50SA |  |  |  | DNP | 581 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TEST/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 200 | TIE(200) |  | CB | [14 empty] | 0279 |  | 0145 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.200_CB | 200(TIE) CB | TIE | D13/11/200/CB |  |  |  | DNP | 582 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 200 | TIE(200) |  | 51A | [14 empty] | 0277 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.200_51A | 23KV TIE(200) 51RY | TIE | D13/11/200/PHA |  |  |  | DNP | 583 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 200 | TIE(200) |  | 51NA | [14 empty] | 0278 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.200_51NA | 23KV TIE(200) 51N RY | TIE | D13/11/200/GDA |  |  |  | DNP | 584 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 300 | TIE(300) |  | CB | [14 empty] | 0333 |  | 0193 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.300_CB | 300(TIE) CB | TIE | D13/22/300/CB |  |  |  | DNP | 585 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 300 | TIE(300) |  | 51A | [14 empty] | 0331 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.300_51A | 23KV TIE(300) 51RY | TIE | D13/22/300/PHA |  |  |  | DNP | 586 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 300 | TIE(300) |  | 51NA | [14 empty] | 0332 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.300_51NA | 23KV TIE(300) 51N RY | TIE | D13/22/300/GDA |  |  |  | DNP | 587 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 400 | TIE(400) |  | CB | [14 empty] | 0354 |  | 0209 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.400_CB | 400(TIE) CB | TIE | D13/22/400/CB |  |  |  | DNP | 588 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 400 | TIE(400) |  | 51A | [14 empty] | 0352 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.400_51A | 23KV TIE(400) 51RY | TIE | D13/22/400/PHA |  |  |  | DNP | 589 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 400 | TIE(400) |  | 51NA | [14 empty] | 0353 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.400_51NA | 23KV TIE(400) 51N RY | TIE | D13/22/400/GDA |  |  |  | DNP | 590 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 390 | #1SSTR(390) |  | CB | [14 empty] | 0330 |  | 0191 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.390_CB | 390(#1SSTR) CB | OTHER | D13/22/390/CB |  |  |  | DNP | 591 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 1SSTR | #1SSTR |  | 51A | [14 empty] | 0328 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#1SSTR_51A | #1SSTR 51RY | OTHER | D13/22/390/PHA |  |  |  | DNP | 592 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 1SSTR | #1SSTR |  | 51NA | [14 empty] | 0329 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | D13/22/390/GDA |  |  |  | DNP | 593 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 490 | #2SSTR(490) |  | CB | [14 empty] | 0351 |  | 0207 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.490_CB | 490(#2SSTR) CB | OTHER | D13/22/490/CB |  |  |  | DNP | 594 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 2SSTR | #2SSTR |  | 51A | [14 empty] | 0349 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#2SSTR_51A | #2SSTR 51RY | OTHER | D13/22/490/PHA |  |  |  | DNP | 595 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 2SSTR | #2SSTR |  | 51NA | [14 empty] | 0350 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | D13/22/490/GDA |  |  |  | DNP | 596 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB | [14 empty] | 0115 |  | 0114 | [8 empty] | 161KV_N | [8 empty] | 虎科DS.1760_CB | 1760(#2DTR) CB | MTR | D13/161/1760/CB |  |  |  | DNP | 597 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 330 | #2DTR(330) |  | CB | [14 empty] | 0119 |  | 0128 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.330_CB | 330(#2DTR) CB | MTR | D13/11/330/CB |  |  |  | DNP | 598 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 340 | #2DTR(340) |  | CB | [14 empty] | 0122 |  | 0146 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.340_CB | 340(#2DTR) CB | MTR | D13/11/340/CB |  |  |  | DNP | 599 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 2DTR | #2DTR |  | 51A | [14 empty] | 0055 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.#2DTR_51A | #2DTR 51RY | MTR | D13//2DTR/51A |  |  |  | DNP | 600 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 2DTR | #2DTR |  | 51NA | [14 empty] | 0056 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.#2DTR_51NA | #2DTR 51N RY | MTR | D13//2DTR/51NA |  |  |  | DNP | 601 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 2DTR | #2DTR |  | 51ZA | [14 empty] | 0054 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | D13//2DTR/51ZA |  |  |  | DNP | 602 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 2DTR | #2DTR |  | 87A | [14 empty] | 0052 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.#2DTR_87A | #2DTR 87RY | MTR | D13//2DTR/87A |  |  |  | DNP | 603 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 2DTR | #2DTR |  | 87UL | [14 empty] | 0590 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#2DTR_87UL | #2DTR 87RY U/L | MTR | D13//2DTR/87UL |  |  |  | DNP | 604 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 0 |  | 330 | #2DTR(330) |  | 51A | [14 empty] | 0050 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.330_51A | #2DTR二次側(330) 51RY | MTR | D13/11/330/51A |  |  |  | DNP | 605 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 340 | #2DTR(340) |  | 51A | [14 empty] | 0051 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.340_51A | #2DTR二次側(340) 51RY | MTR | D13/11/340/51A |  |  |  | DNP | 606 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 2DTR | #2DTR |  | 96PA | [14 empty] | 0053 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | D13//2DTR/96PA |  |  |  | DNP | 607 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 2DTR | #2DTR |  | 96D | [14 empty] | 0518 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#2DTR_96D | #2DTR 96D RY | MTR | D13//2DTR/96D |  |  |  | DNP | 608 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 2DTR | #2DTR |  | 96P | [14 empty] | 0523 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#2DTR_96P | #2DTR 96P RY | MTR | D13//2DTR/96P |  |  |  | DNP | 609 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 2DTR | #2DTR |  | 63Q | [14 empty] | 0517 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#2DTR_63Q | #2DTR 63Q RY | MTR | D13//2DTR/63Q |  |  |  | DNP | 610 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 2DTR | #2DTR |  | 96B1 | [14 empty] | 0520 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | D13//2DTR/96B1 |  |  |  | DNP | 611 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 2DTR | #2DTR |  | 96B2 | [14 empty] | 0519 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | D13//2DTR/96B2 |  |  |  | DNP | 612 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 2DTR | #2DTR |  | TRA | [14 empty] | 0513 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#2DTR_TRA | #2DTR 重故障 | MTR | D13//2DTR/TRA |  |  |  | DNP | 613 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 2DTR | #2DTR |  | TRF | [14 empty] | 0514 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#2DTR_TRF | #2DTR 輕故障 | MTR | D13//2DTR/TRF |  |  |  | DNP | 614 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 2DTR(A) | #2DTR(A) |  | SupLocal | [14 empty] | 0521 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | D13//2DTR(A)/SupLocal |  |  |  | DNP | 615 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D13 | 虎科DS | 0 |  | 2DTR(A) | #2DTR(A) |  | A_M | [14 empty] | 0515 |  | 0001 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | D13//2DTR(A)/Tap Chan |  |  |  | DNP | 616 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D13 | 虎科DS | 0 |  | 2DTR(B) | #2DTR(B) |  | SupLocal | [14 empty] | 0522 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | D13//2DTR(B)/SupLocal |  |  |  | DNP | 617 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D13 | 虎科DS | 0 |  | 2DTR(B) | #2DTR(B) |  | A_M | [14 empty] | 0516 |  | 0003 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | D13//2DTR(B)/Tap Chan |  |  |  | DNP | 618 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D13 | 虎科DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 | [13 empty] | 0868 | 869 | 0115 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1761_DS | 1761(#2DTR) DS | MTR | D13/161/1760/DS1 |  |  |  | DNP | 619 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D13 | 虎科DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 | [13 empty] | 0870 | 871 | 0116 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1762_DS | 1762(#2DTR) DS | MTR | D13/161/1760/DS2 |  |  |  | DNP | 620 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB | [14 empty] | 0116 |  | 0117 | [8 empty] | 161KV_N | [8 empty] | 虎科DS.1770_CB | 1770(#3DTR) CB | MTR | D13/161/1770/CB |  |  |  | DNP | 621 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 350 | #3DTR(350) |  | CB | [14 empty] | 0125 |  | 0163 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.350_CB | 350(#3DTR) CB | MTR | D13/22/350/CB |  |  |  | DNP | 622 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 360 | #3DTR(360) |  | CB | [14 empty] | 0128 |  | 0177 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.360_CB | 360(#3DTR) CB | MTR | D13/22/360/CB |  |  |  | DNP | 623 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 3DTR | #3DTR |  | 51A | [14 empty] | 0064 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.#3DTR_51A | #3DTR 51RY | MTR | D13//3DTR/51A |  |  |  | DNP | 624 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 3DTR | #3DTR |  | 51NA | [14 empty] | 0065 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.#3DTR_51NA | #3DTR 51N RY | MTR | D13//3DTR/51NA |  |  |  | DNP | 625 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 3DTR | #3DTR |  | 51ZA | [14 empty] | 0063 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.#3DTR_51ZA | #3DTR 51Z RY | MTR | D13//3DTR/51ZA |  |  |  | DNP | 626 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 3DTR | #3DTR |  | 87A | [14 empty] | 0061 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.#3DTR_87A | #3DTR 87RY | MTR | D13//3DTR/87A |  |  |  | DNP | 627 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 3DTR | #3DTR |  | 87UL | [14 empty] | 0591 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#3DTR_87UL | #3DTR 87RY U/L | MTR | D13//3DTR/87UL |  |  |  | DNP | 628 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 0 |  | 350 | #3DTR(350) |  | 51A | [14 empty] | 0059 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.350_51A | #3DTR二次側(350) 51RY | MTR | D13/22/350/51A |  |  |  | DNP | 629 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 360 | #3DTR(360) |  | 51A | [14 empty] | 0060 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.360_51A | #3DTR二次側(360) 51RY | MTR | D13/22/360/51A |  |  |  | DNP | 630 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 3DTR | #3DTR |  | 96PA | [14 empty] | 0062 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.#3DTR_96PA | #3DTR 機械保護動作 | MTR | D13//3DTR/96PA |  |  |  | DNP | 631 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 3DTR | #3DTR |  | 96D | [14 empty] | 0528 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#3DTR_96D | #3DTR 96D RY | MTR | D13//3DTR/96D |  |  |  | DNP | 632 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 3DTR | #3DTR |  | 96P | [14 empty] | 0532 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#3DTR_96P | #3DTR 96P RY | MTR | D13//3DTR/96P |  |  |  | DNP | 633 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 3DTR | #3DTR |  | 63Q | [14 empty] | 0527 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#3DTR_63Q | #3DTR 63Q RY | MTR | D13//3DTR/63Q |  |  |  | DNP | 634 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 3DTR | #3DTR |  | 96B1 | [14 empty] | 0530 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#3DTR_96B1 | #3DTR 96B1 RY | MTR | D13//3DTR/96B1 |  |  |  | DNP | 635 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 3DTR | #3DTR |  | 96B2 | [14 empty] | 0529 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#3DTR_96B2 | #3DTR 96B2 RY | MTR | D13//3DTR/96B2 |  |  |  | DNP | 636 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 3DTR | #3DTR |  | TRA | [14 empty] | 0524 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#3DTR_TRA | #3DTR 重故障 | MTR | D13//3DTR/TRA |  |  |  | DNP | 637 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 3DTR | #3DTR |  | TRF | [14 empty] | 0525 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#3DTR_TRF | #3DTR 輕故障 | MTR | D13//3DTR/TRF |  |  |  | DNP | 638 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 3DTR | #3DTR |  | SupLocal | [14 empty] | 0531 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#3DTR_S/L | #3DTR OLTC S/L | MTR | D13//3DTR/SupLocal |  |  |  | DNP | 639 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D13 | 虎科DS | 0 |  | 3DTR | #3DTR |  | A_M | [14 empty] | 0526 |  | 0005 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.#3DTR_A/M | #3DTR OLTC A/M | MTR | D13//3DTR/Tap Chan |  |  |  | DNP | 640 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D13 | 虎科DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 | [13 empty] | 0872 | 873 | 0118 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1771_DS | 1771(#3DTR) DS | MTR | D13/161/1770/DS1 |  |  |  | DNP | 641 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 | [13 empty] | 0874 | 875 | 0119 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1772_DS | 1772(#3DTR) DS | MTR | D13/161/1770/DS2 |  |  |  | DNP | 642 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D13 | 虎科DS | 161 | 161kV | 1780 | #4DTR(1780) |  | CB | [14 empty] | 0117 |  | 0120 | [8 empty] | 161KV_N | [8 empty] | 虎科DS.1780_CB | 1780(#4DTR) CB | MTR | D13/161/1780/CB |  |  |  | DNP | 643 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 370 | #4DTR(370) |  | CB | [14 empty] | 0131 |  | 0192 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.370_CB | 370(#4DTR) CB | MTR | D13/22/370/CB |  |  |  | DNP | 644 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 380 | #4DTR(380) |  | CB | [14 empty] | 0134 |  | 0208 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.380_CB | 380(#4DTR) CB | MTR | D13/22/380/CB |  |  |  | DNP | 645 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 4DTR | #4DTR |  | 51A | [14 empty] | 0073 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.#4DTR_51A | #4DTR 51RY | MTR | D13//4DTR/51A |  |  |  | DNP | 646 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 4DTR | #4DTR |  | 51NA | [14 empty] | 0074 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.#4DTR_51NA | #4DTR 51N RY | MTR | D13//4DTR/51NA |  |  |  | DNP | 647 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 4DTR | #4DTR |  | 51ZA | [14 empty] | 0072 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.#4DTR_51ZA | #4DTR 51Z RY | MTR | D13//4DTR/51ZA |  |  |  | DNP | 648 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 4DTR | #4DTR |  | 87A | [14 empty] | 0070 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.#4DTR_87A | #4DTR 87RY | MTR | D13//4DTR/87A |  |  |  | DNP | 649 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 4DTR | #4DTR |  | 87UL | [14 empty] | 0592 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#4DTR_87UL | #4DTR 87RY U/L | MTR | D13//4DTR/87UL |  |  |  | DNP | 650 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 0 |  | 370 | #4DTR(370) |  | 51A | [14 empty] | 0068 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.370_51A | #4DTR二次側(370) 51RY | MTR | D13/22/370/51A |  |  |  | DNP | 651 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 380 | #4DTR(380) |  | 51A | [14 empty] | 0069 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.380_51A | #4DTR二次側(380) 51RY | MTR | D13/22/380/51A |  |  |  | DNP | 652 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 4DTR | #4DTR |  | 96PA | [14 empty] | 0071 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.#4DTR_96PA | #4DTR 機械保護動作 | MTR | D13//4DTR/96PA |  |  |  | DNP | 653 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 4DTR | #4DTR |  | 96D | [14 empty] | 0537 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#4DTR_96D | #4DTR 96D RY | MTR | D13//4DTR/96D |  |  |  | DNP | 654 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 4DTR | #4DTR |  | 96P | [14 empty] | 0541 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#4DTR_96P | #4DTR 96P RY | MTR | D13//4DTR/96P |  |  |  | DNP | 655 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 4DTR | #4DTR |  | 63Q | [14 empty] | 0536 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#4DTR_63Q | #4DTR 63Q RY | MTR | D13//4DTR/63Q |  |  |  | DNP | 656 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 4DTR | #4DTR |  | 96B1 | [14 empty] | 0539 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#4DTR_96B1 | #4DTR 96B1 RY | MTR | D13//4DTR/96B1 |  |  |  | DNP | 657 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 4DTR | #4DTR |  | 96B2 | [14 empty] | 0538 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#4DTR_96B2 | #4DTR 96B2 RY | MTR | D13//4DTR/96B2 |  |  |  | DNP | 658 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 4DTR | #4DTR |  | TRA | [14 empty] | 0533 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#4DTR_TRA | #4DTR 重故障 | MTR | D13//4DTR/TRA |  |  |  | DNP | 659 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 4DTR | #4DTR |  | TRF | [14 empty] | 0534 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#4DTR_TRF | #4DTR 輕故障 | MTR | D13//4DTR/TRF |  |  |  | DNP | 660 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 4DTR | #4DTR |  | SupLocal | [14 empty] | 0540 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#4DTR_S/L | #4DTR OLTC S/L | MTR | D13//4DTR/SupLocal |  |  |  | DNP | 661 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D13 | 虎科DS | 0 |  | 4DTR | #4DTR |  | A_M | [14 empty] | 0535 |  | 0007 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.#4DTR_A/M | #4DTR OLTC A/M | MTR | D13//4DTR/Tap Chan |  |  |  | DNP | 662 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D13 | 虎科DS | 161 | 161kV | 1780 | #4DTR(1780) |  | DS1 | 1781 | [13 empty] | 0876 | 877 | 0121 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1781_DS | 1781(#4DTR) DS | MTR | D13/161/1780/DS1 |  |  |  | DNP | 663 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D13 | 虎科DS | 161 | 161kV | 1780 | #4DTR(1780) |  | DS2 | 1782 | [13 empty] | 0878 | 879 | 0122 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1782_DS | 1782(#4DTR) DS | MTR | D13/161/1780/DS2 |  |  |  | DNP | 664 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 11 | 11kV | 230 | #3SC(230) |  | CB | [14 empty] | 0276 |  | 0144 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.230_CB | 230(11KV #3SC) CB | SC | D13/11/230/CB |  |  |  | DNP | 665 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | 230 | #3SC(230) |  | SCA | [14 empty] | 0274 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.230_SCA | 11KV #3SC 51,51N RY | SC | D13/11/230/SCA |  |  |  | DNP | 666 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | 230 | #3SC(230) |  | UVA | [14 empty] | 0275 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.230_OUVA | 11KV #3SC 27,59RY(欠壓或過壓) | SC | D13/11/230/UVA |  |  |  | DNP | 667 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | 230 | #3SC(230) |  | LBS | [14 empty] | 0880 | 881 | 0225 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.230_LBS | 230(11KV #3SC) LBS | SC | D13/11/230/9A5Other |  |  |  | DNP | 668 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 11 | 11kV | 240 | #4SC(240) |  | CB | [14 empty] | 0297 |  | 0162 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.240_CB | 240(11KV #4SC) CB | SC | D13/11/240/CB |  |  |  | DNP | 669 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 11 | 11kV | 240 | #4SC(240) |  | SCA | [14 empty] | 0295 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.240_SCA | 11KV #4SC 51,51N RY | SC | D13/11/240/SCA |  |  |  | DNP | 670 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | 240 | #4SC(240) |  | UVA | [14 empty] | 0296 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.240_OUVA | 11KV #4SC 27,59RY(欠壓或過壓) | SC | D13/11/240/UVA |  |  |  | DNP | 671 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | 240 | #4SC(240) |  | LBS | [14 empty] | 0882 | 883 | 0226 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.240_LBS | 240(11KV #4SC) LBS | SC | D13/11/240/10A5Other |  |  |  | DNP | 672 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 22 | 22kV | 250 | #5SC(250) |  | CB | [14 empty] | 0300 |  | 0164 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.250_CB | 250(23KV #5SC) CB | SC | D13/22/250/CB |  |  |  | DNP | 673 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | 250 | #5SC(250) |  | SCA | [14 empty] | 0298 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.250_SCA | 23KV #5SC 51,51N RY | SC | D13/22/250/SCA |  |  |  | DNP | 674 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 250 | #5SC(250) |  | UVA | [14 empty] | 0299 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.250_OUVA | 23KV #5SC 27,59RY(欠壓或過壓) | SC | D13/22/250/UVA |  |  |  | DNP | 675 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 260 | #6SC(260) |  | CB | [14 empty] | 0315 |  | 0178 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.260_CB | 260(23KV #6SC) CB | SC | D13/22/260/CB |  |  |  | DNP | 676 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | 260 | #6SC(260) |  | SCA | [14 empty] | 0313 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.260_SCA | 23KV #6SC 51,51N RY | SC | D13/22/260/SCA |  |  |  | DNP | 677 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 260 | #6SC(260) |  | UVA | [14 empty] | 0314 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.260_OUVA | 23KV #6SC 27,59RY(欠壓或過壓) | SC | D13/22/260/UVA |  |  |  | DNP | 678 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 270 | #7SC(270) |  | CB | [14 empty] | 0348 |  | 0206 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.270_CB | 270(23KV #7SC) CB | SC | D13/22/270/CB |  |  |  | DNP | 679 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | 270 | #7SC(270) |  | SCA | [14 empty] | 0346 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.270_SCA | 23KV #7SC 51,51N RY | SC | D13/22/270/SCA |  |  |  | DNP | 680 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 270 | #7SC(270) |  | UVA | [14 empty] | 0347 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.270_OUVA | 23KV #7SC 27,59RY(欠壓或過壓) | SC | D13/22/270/UVA |  |  |  | DNP | 681 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 280 | #8SC(280) |  | CB | [14 empty] | 0369 |  | 0222 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.280_CB | 280(23KV #8SC) CB | SC | D13/22/280/CB |  |  |  | DNP | 682 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 22 | 22kV | 280 | #8SC(280) |  | SCA | [14 empty] | 0367 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.280_SCA | 23KV #8SC 51,51N RY | SC | D13/22/280/SCA |  |  |  | DNP | 683 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 280 | #8SC(280) |  | UVA | [14 empty] | 0368 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.280_OUVA | 23KV #8SC 27,59RY(欠壓或過壓) | SC | D13/22/280/UVA |  |  |  | DNP | 684 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1611BUS | #1BUS |  | VUA | [14 empty] | 0625 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | D13/161/1BUS/BUS_VUA |  |  |  | DNP | 685 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1611BUS | #1BUS |  | 87A | [14 empty] | 0081 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | D13/161/1BUS/87A |  |  |  | DNP | 686 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1611BUS | #1BUS |  | 87UL | [14 empty] | 0593 |  | 0027 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | D13/161/1BUS/87UL |  |  |  | DNP | 687 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | 1612BUS | #2BUS |  | VUA | [14 empty] | 0626 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | D13/161/2BUS/BUS_VUA |  |  |  | DNP | 688 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1612BUS | #2BUS |  | 87A | [14 empty] | 0082 | [10 empty] | 161KV_N | [8 empty] | 虎科DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | D13/161/2BUS/87A |  |  |  | DNP | 689 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1612BUS | #2BUS |  | 87UL | [14 empty] | 0594 |  | 0028 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | D13/161/2BUS/87UL |  |  |  | DNP | 690 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 22 | 22kV | 11_ | 11/ |  | CBA | [14 empty] | 0636 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | D13/0/ComPoint/FDR_CBA |  |  |  | DNP | 691 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | 11_ | 11/ |  | CBF | [14 empty] | 0637 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | D13/0/ComPoint/FDR_CBF |  |  |  | DNP | 692 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV |  |  |  | CBA | [14 empty] | 0596 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.161KV_CBA | 161KV斷路器重故障 | OTHER | D13/161/ComPoint/CBA |  |  |  | DNP | 693 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV |  |  |  | CBF | [14 empty] | 0597 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | D13/161/ComPoint/CBF |  |  |  | DNP | 694 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | LINE | LINE |  | RCA | [14 empty] | 0108 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | D13/161/ComPoint/RCA |  |  |  | DNP | 695 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | _SC | 11/ SC |  | 60A | [14 empty] | 0595 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.23KV_SC_60A | 11/23KV SC 60A | OTHER | D13/0/ComPoint/FDR_60A |  |  |  | DNP | 696 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | TEST | TEST |  | CB | [14 empty] | 0512 |  | 0000 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.TEST_CB | TEST CB | OTHER | D13/0/RTU/Test_CB |  |  |  | DNP | 697 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  |  |  |  | Fire1 | [14 empty] | 0616 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | D13/0/StaDev/Fire1 |  |  |  | DNP | 698 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  |  |  |  | 25TA | [14 empty] | 0107 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | D13/161/ComPoint/25TA |  |  |  | DNP | 699 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  |  |  |  | ACB1 | [14 empty] | 0629 |  | 0228 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | D13/0/StaDev/ACB1 |  |  |  | DNP | 700 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ON/OFF | ON
D13 | 虎科DS | 0 |  |  |  |  | ACB2 | [14 empty] | 0630 |  | 0229 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | D13/0/StaDev/ACB2 |  |  |  | DNP | 701 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ON/OFF | ON
D13 | 虎科DS | 0 |  |  |  |  | ACBA | [14 empty] | 0639 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.所內電源ACBA | 所內電源故障警報 | OTHER | D13/0/StaDev/ACBA |  |  |  | DNP | 702 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 所內電源開關ACB | 所內電源開關ACB |  | ACBT | [14 empty] | 0631 |  | 0230 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | D13/0/StaDev/ACBT |  |  |  | DNP | 703 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ON/OFF | OFF
D13 | 虎科DS | 0 |  |  |  |  | STUV | [14 empty] | 0617 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | D13/0/StaDev/STUV |  |  |  | DNP | 704 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  |  |  |  | CHG1 | [14 empty] | 0611 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.直流充電機故障 | 直流充電機故障 | OTHER | D13/0/StaDev/CHG1 |  |  |  | DNP | 705 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  |  |  |  | DCA | [14 empty] | 0614 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.直流電源DCA | 直流電源故障警報 | OTHER | D13/0/ComPoint/ABS_89A |  |  |  | DNP | 706 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  |  |  |  | DCE | [14 empty] | 0613 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.直流電源DCE | 直流電源接地故障警報 | OTHER | D13/0/StaDev/DCE |  |  |  | DNP | 707 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  |  |  |  | CHG2 | [14 empty] | 0612 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | D13/0/StaDev/CHG2 |  |  |  | DNP | 708 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  |  |  |  | CommACF | [14 empty] | 0621 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | D13/0/StaDev/CommACF |  |  |  | DNP | 709 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  |  |  |  | Burglar1 | [14 empty] | 0645 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | D13/0/StaDev/Door3 |  |  |  | DNP | 710 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  |  |  |  | Door1 | [14 empty] | 0615 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.無人化門禁(1) | 無人化門禁(1)控制室及大門 | OTHER | D13/0/StaDev/Door1 |  |  |  | DNP | 711 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  |  |  |  | Lights1 | [14 empty] | 0618 |  | 0223 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.開關場照明(A) | 景觀照明 | OTHER | D13/0/StaDev/Lights1 |  |  |  | DNP | 712 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ON/OFF | OFF
D13 | 虎科DS | 0 |  |  |  |  | Lights2 | [14 empty] | 0643 |  | 0227 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.開關場照明(B) | 路燈照明 | OTHER | D13/0/StaDev/Lights2 |  |  |  | DNP | 713 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ON/OFF | OFF
D13 | 虎科DS | 22 | 22kV | 11_ | 11/ |  | LOA | [14 empty] | 0638 | [10 empty] | DDCS1_1 | [8 empty] | 虎科DS.11/23KV_LOA | 11/23KV饋線復閉失敗閉鎖 | OTHER | D13/0/ComPoint/LOA |  |  |  | DNP | 714 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 1570 | 虎科虎菁一路(1570) |  | 87CFA | [14 empty] | 0598 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.1570_87CFA | 虎科虎菁一路(1570)87RY通訊故障 | OTHER | D13/161/1570/87CFA |  |  |  | DNP | 715 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 1570 | 虎科虎菁一路(1570) |  | RYFA | [14 empty] | 0565 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.1570_RYFA | 虎科虎菁一路(1570)數位電驛故障 | OTHER | D13/161/1570/RYFA |  |  |  | DNP | 716 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 1580 | 虎科虎菁二路(1580) |  | 87CFA | [14 empty] | 0599 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.1580_87CFA | 虎科虎菁二路(1580)87RY通訊故障 | OTHER | D13/161/1580/87CFA |  |  |  | DNP | 717 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 1580 | 虎科虎菁二路(1580) |  | RYFA | [14 empty] | 0566 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.1580_RYFA | 虎科虎菁二路(1580)數位電驛故障 | OTHER | D13/161/1580/RYFA |  |  |  | DNP | 718 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | _OSCA | _OSCA |  | 1 | [14 empty] | 0083 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.161KV_OSCA_1 | 161KV示波器啟動警報 | OTHER | D13/161/ComPoint/OSCA |  |  |  | DNP | 719 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | _OSCA | _OSCA | [16 empty] | 0563 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.161KV_OSCA_2 | 161KV示波器故障 | OTHER | D13/161/ComPoint/2A5Other |  |  |  | DNP | 720 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | _OSCA | _OSCA |  | 3 | [14 empty] | 0564 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.161KV_OSCA_3 | 161KV示波器電源故障 | OTHER | D13/161/ComPoint/3A5Other |  |  |  | DNP | 721 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 1620 | 虎科和鑫二路(1620) |  | 87CFA | [14 empty] | 0601 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.1620_87CFA | 虎科和鑫二路(1620)87RY通訊故障 | OTHER | D13/161/1620/87CFA |  |  |  | DNP | 722 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 1620 | 虎科和鑫二路(1620) |  | RYFA | [14 empty] | 0568 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.1620_RYFA | 虎科和鑫二路(1620)數位電驛故障 | OTHER | D13/161/1620/RYFA |  |  |  | DNP | 723 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 1630 | 越港虎科紅線(1630) |  | 87CFA | [14 empty] | 0602 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.1630_87CFA | 越港虎科紅線(1630)87RY通訊故障 | OTHER | D13/161/1630/87CFA |  |  |  | DNP | 724 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 1630 | 越港虎科紅線(1630) |  | RYFA | [14 empty] | 0569 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.1630_RYFA | 越港虎科紅線(1630)數位電驛故障 | OTHER | D13/161/1630/RYFA |  |  |  | DNP | 725 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 1640 | 越港虎科白線(1640) |  | 87CFA | [14 empty] | 0603 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.1640_87CFA | 越港虎科白線(1640)87RY通訊故障 | OTHER | D13/161/1640/87CFA |  |  |  | DNP | 726 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 1640 | 越港虎科白線(1640) |  | RYFA | [14 empty] | 0570 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.1640_RYFA | 越港虎科白線(1640)數位電驛故障 | OTHER | D13/161/1640/RYFA |  |  |  | DNP | 727 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 330 | #2DTR(330) |  | GDA | [14 empty] | 0121 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.330_GDA | 330開關箱IED RY GDA | OTHER | D13/11/330/GDA |  |  |  | DNP | 728 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 330 | #2DTR(330) |  | PHA2 | [14 empty] | 0120 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.330_PHA2 | 330開關箱IED RY PHA | OTHER | D13/11/330/PHA |  |  |  | DNP | 729 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 340 | #2DTR(340) |  | GDA | [14 empty] | 0124 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.340_GDA | 340開關箱IED RY GDA | OTHER | D13/11/340/GDA |  |  |  | DNP | 730 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 340 | #2DTR(340) |  | PHA2 | [14 empty] | 0123 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.340_PHA2 | 340開關箱IED RY PHA | OTHER | D13/11/340/PHA |  |  |  | DNP | 731 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 350 | #3DTR(350) |  | GDA | [14 empty] | 0127 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.350_GDA | 350開關箱IED RY GDA | OTHER | D13/22/350/GDA |  |  |  | DNP | 732 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 350 | #3DTR(350) |  | PHA2 | [14 empty] | 0126 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.350_PHA2 | 350開關箱IED RY PHA | OTHER | D13/22/350/PHA |  |  |  | DNP | 733 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 360 | #3DTR(360) |  | GDA | [14 empty] | 0130 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.360_GDA | 360開關箱IED RY GDA | OTHER | D13/22/360/GDA |  |  |  | DNP | 734 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 360 | #3DTR(360) |  | PHA2 | [14 empty] | 0129 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.360_PHA2 | 360開關箱IED RY PHA | OTHER | D13/22/360/PHA |  |  |  | DNP | 735 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 370 | #4DTR(370) |  | GDA | [14 empty] | 0133 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.370_GDA | 370開關箱IED RY GDA | OTHER | D13/22/370/GDA |  |  |  | DNP | 736 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 370 | #4DTR(370) |  | PHA2 | [14 empty] | 0132 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.370_PHA2 | 370開關箱IED RY PHA | OTHER | D13/22/370/PHA |  |  |  | DNP | 737 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 380 | #4DTR(380) |  | GDA | [14 empty] | 0136 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.380_GDA | 380開關箱IED RY GDA | OTHER | D13/22/380/GDA |  |  |  | DNP | 738 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 380 | #4DTR(380) |  | PHA2 | [14 empty] | 0135 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.380_PHA2 | 380開關箱IED RY PHA | OTHER | D13/22/380/PHA |  |  |  | DNP | 739 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | COMM | 通訊處理單元 |  | SupLocal | [14 empty] | 0633 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.COMM_S/L | 通訊處理單元 SUPY/LOCAL | OTHER | D13/0/StaDev/Comm_R_L |  |  |  | DNP | 740 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D13 | 虎科DS | 0 |  |  |  |  | MCCA | [14 empty] | 0619 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.MCCA | MCC電驛故障 | OTHER | D13/0/StaDev/MCC |  |  |  | DNP | 741 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | MCC_IED | IED |  | SupLocal | [14 empty] | 0634 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.MCC_IED_S/L | 161KV IED SUPY/LOCAL | OTHER | D13/0/ComPoint/PMCC_R_L |  |  |  | DNP | 742 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D13 | 虎科DS | 0 |  | MODEM | MODEM |  | MODEMA | [14 empty] | 0642 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.MODEMA | MODEM POWER FAIL故障 | OTHER | D13/0/StaDev/4A5Other |  |  |  | DNP | 743 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  |  |  |  | PMCCA | [14 empty] | 0620 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.PMCCA | PMCC電驛故障 | OTHER | D13/0/StaDev/PMCC |  |  |  | DNP | 744 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 22 | 22kV | PMCC_IED | 11/ IED |  | SupLocal | [14 empty] | 0635 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.PMCC_IED_S/L | 11/23KV IED SUPY/LOCAL | OTHER | D13/0/StaDev/PMCC_R_L |  |  |  | DNP | 745 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D13 | 虎科DS | 0 |  |  |  |  | SCADAA | [14 empty] | 0632 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.SCADA故障 | 變電所SCADA故障 | OTHER | D13/0/StaDev/SCADAA |  |  |  | DNP | 746 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  |  |  |  | TCA | [14 empty] | 0705 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.TCA | 斷路器跳脫回路故障 | OTHER | D13/0/StaDev/6A5Other |  |  |  | DNP | 747 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  |  |  |  | 水位警報(1) | [14 empty] | 0627 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.水位警報(1) | 地下室水位警報(1) | OTHER | D13/0/StaDev/Water1 |  |  |  | DNP | 748 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  |  |  |  | 水位警報(2) | [14 empty] | 0628 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.水位警報(2) | 地下室水位警報(2) | OTHER | D13/0/StaDev/Water2 |  |  |  | DNP | 749 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  |  |  |  | 通信機房溫度 | [14 empty] | 0622 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.通信機房溫度 | 通信室或控制室溫度警報 | OTHER | D13/0/StaDev/R_Temp |  |  |  | DNP | 750 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 0 |  |  |  |  | 集油池警報(1) | [14 empty] | 0640 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.集油池警報(1) | 集油池水位警報(1) | OTHER | D13/0/StaDev/OilLeak1 |  |  |  | DNP | 751 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  |  |  |  | 集油池警報(2) | [14 empty] | 0641 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.集油池警報(2) | 集油池水位警報(2) | OTHER | D13/0/StaDev/OilLeak2 |  |  |  | DNP | 752 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  |  |  |  | Door2 | [14 empty] | 0644 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.無人化門禁(2) | 無人化門禁(2)建築物大小門 | OTHER | D13/0/StaDev/Door2 |  |  |  | DNP | 753 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 2DTR | #2DTR |  | 50_51NUL | [14 empty] | 0574 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#2DTR_50/51NUL | #2DTR 50/50N/51/51N RY U/L | OTHER | D13//2DTR/50_51NUL |  |  |  | DNP | 754 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 0 |  | 2DTR | #2DTR |  | 51Z_UL | [14 empty] | 0573 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#2DTR_51ZUL | #2DTR 51Z RY U/L | OTHER | D13//2DTR/51Z_UL |  |  |  | DNP | 755 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 0 |  | 2DTR | #2DTR |  | DTR_86A | [14 empty] | 0571 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#2DTR_86A | #2DTR 86(50/50N/51Z/87/96)RY | OTHER | D13//2DTR/DTR_86A |  |  |  | DNP | 756 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 2DTR | #2DTR |  | RYFA | [14 empty] | 0572 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#2DTR_RYFA | #2DTR 數位電驛故障 | OTHER | D13//2DTR/RYFA |  |  |  | DNP | 757 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 3DTR | #3DTR |  | 50_51NUL | [14 empty] | 0578 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#3DTR_50/51NUL | #3DTR 50/50N/51/51N RY U/L | OTHER | D13//3DTR/50_51NUL |  |  |  | DNP | 758 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 0 |  | 3DTR | #3DTR |  | 51Z_UL | [14 empty] | 0577 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#3DTR_51ZUL | #3DTR 51Z RY U/L | OTHER | D13//3DTR/51Z_UL |  |  |  | DNP | 759 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 0 |  | 3DTR | #3DTR |  | DTR_86A | [14 empty] | 0575 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#3DTR_86A | #3DTR 86(50/50N/51Z/87/96)RY | OTHER | D13//3DTR/DTR_86A |  |  |  | DNP | 760 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 3DTR | #3DTR |  | RYFA | [14 empty] | 0576 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#3DTR_RYFA | #3DTR 數位電驛故障 | OTHER | D13//3DTR/RYFA |  |  |  | DNP | 761 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 4DTR | #4DTR |  | 50_51NUL | [14 empty] | 0582 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#4DTR_50/51NUL | #4DTR 50/50N/51/51N RY U/L | OTHER | D13//4DTR/50_51NUL |  |  |  | DNP | 762 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 0 |  | 4DTR | #4DTR |  | 51Z_UL | [14 empty] | 0581 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#4DTR_51ZUL | #4DTR 51Z RY U/L | OTHER | D13//4DTR/51Z_UL |  |  |  | DNP | 763 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 0 |  | 4DTR | #4DTR |  | DTR_86A | [14 empty] | 0579 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#4DTR_86A | #4DTR 86(50/50N/51Z/87/96)RY | OTHER | D13//4DTR/DTR_86A |  |  |  | DNP | 764 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 4DTR | #4DTR |  | RYFA | [14 empty] | 0580 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#4DTR_RYFA | #4DTR 數位電驛故障 | OTHER | D13//4DTR/RYFA |  |  |  | DNP | 765 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | _BUS | BUS |  | 87CTFA | [14 empty] | 0646 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.161KV_BUS_CTFA | 161KV BUS CT 回路故障 | OTHER | D13/161/ComPoint/12B_CTFA |  |  |  | DNP | 766 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | _BUS | BUS |  | RYFA | [14 empty] | 0647 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | D13/161/ComPoint/BUS_RYFA |  |  |  | DNP | 767 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 0 |  |  |  |  | GEN | [14 empty] | 0648 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.GEN | 緊急發電機運轉 | OTHER | D13/0/StaDev/5A5Other |  |  |  | DNP | 768 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | OFF/ON | OFF
D13 | 虎科DS | 0 |  | 2DTR | #2DTR |  | GDA | [14 empty] | 0087 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#2DTR_GDA | #2DTR 50N/51N RY | OTHER | D13//2DTR/GDA |  |  |  | DNP | 769 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 2DTR | #2DTR |  | PHA | [14 empty] | 0084 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#2DTR_PHA | #2DTR 50/51 RY | OTHER | D13//2DTR/PHA |  |  |  | DNP | 770 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 3DTR | #3DTR |  | GDA | [14 empty] | 0088 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#3DTR_GDA | #3DTR 50N/51N RY | OTHER | D13//3DTR/GDA |  |  |  | DNP | 771 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 3DTR | #3DTR |  | PHA | [14 empty] | 0085 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#3DTR_PHA | #3DTR 50/51 RY | OTHER | D13//3DTR/PHA |  |  |  | DNP | 772 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 4DTR | #4DTR |  | GDA | [14 empty] | 0089 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#4DTR_GDA | #4DTR 50N/51N RY | OTHER | D13//4DTR/GDA |  |  |  | DNP | 773 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 0 |  | 4DTR | #4DTR |  | PHA | [14 empty] | 0086 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.#4DTR_PHA | #4DTR 50/51 RY | OTHER | D13//4DTR/PHA |  |  |  | DNP | 774 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 2SHR | #2SHR |  | 161#2SHR87A1 | [14 empty] | 0091 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.161#2SHR87A1 | 161KV #2SHR #1 87RY | OTHER | D13/161/1960/87A1 |  |  |  | DNP | 775 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 2SHR | #2SHR |  | 161#2SHR87A2 | [14 empty] | 0092 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.161#2SHR87A2 | 161KV #2SHR #2 87RY | OTHER | D13/161/1960/87A2 |  |  |  | DNP | 776 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 2SHR | #2SHR |  | 161#2SHR96PA | [14 empty] | 0093 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.161#2SHR96PA | 161KV #2SHR 機械保護動作 | OTHER | D13/161/1960/96PA |  |  |  | DNP | 777 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1612SHR | #2SHR |  | 51A | [14 empty] | 0095 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.161#2SHR_51A | 161KV #2SHR 51RY | OTHER | D13/161/1960/51A |  |  |  | DNP | 778 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1612SHR | #2SHR |  | 86A | [14 empty] | 0094 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.161#2SHR_86A | 161KV #2SHR 86RY | OTHER | D13/161/1960/1A5Other |  |  |  | DNP | 779 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1612SHR | #2SHR |  | 1_87UL1 | [14 empty] | 0712 |  | 0030 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.161#2SHR_87UL1 | 161KV #2SHR #1 87RY U/L | OTHER | D13/161/1960/1_87UL1 |  |  |  | DNP | 780 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | 1612SHR | #2SHR |  | 1_87UL2 | [14 empty] | 0713 |  | 0031 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.161#2SHR_87UL2 | 161KV #2SHR #2 87RY U/L | OTHER | D13/161/1960/1_87UL2 |  |  |  | DNP | 781 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | USE/LOCK | USE
D13 | 虎科DS | 161 | 161kV | 1612SHR | #2SHR |  | 96B1 | [14 empty] | 0706 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.161#2SHR_96B1 | 161KV #2SHR 96B1 RY | OTHER | D13/161/1960/96B1 |  |  |  | DNP | 782 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1612SHR | #2SHR |  | 96B2 | [14 empty] | 0707 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.161#2SHR_96B2 | 161KV #2SHR 96B2 RY | OTHER | D13/161/1960/96B2 |  |  |  | DNP | 783 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1612SHR | #2SHR |  | 96D | [14 empty] | 0708 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.161#2SHR_96D | 161KV #2SHR 96D RY | OTHER | D13/161/1960/96D |  |  |  | DNP | 784 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1612SHR | #2SHR |  | 96P | [14 empty] | 0709 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.161#2SHR_96P | 161KV #2SHR 96P RY | OTHER | D13/161/1960/96P |  |  |  | DNP | 785 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1612SHR | 161#2SHR |  | RYFA | [14 empty] | 0714 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.161#2SHR_RYFA | 161KV 2SHR(1960)數位電驛故障 | OTHER | D13/161/1960/RYFA |  |  |  | DNP | 786 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1612SHR | #2SHR |  | SHRA | [14 empty] | 0711 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.161#2SHR_SRA | 161KV #2SHR 重故障 | OTHER | D13/161/1960/SHRA |  |  |  | DNP | 787 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1612SHR | #2SHR |  | SRF | [14 empty] | 0710 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.161#2SHR_SRF | 161KV #2SHR 輕故障 | OTHER | D13/161/1960/SHRF |  |  |  | DNP | 788 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D13 | 虎科DS | 161 | 161kV | 1960 | #2SHR(1960) |  | CB | [14 empty] | 0090 |  | 0084 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1960_CB | 1960(161KV #2SHR) CB | OTHER | D13/161/1960/CB |  |  |  | DNP | 789 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1960 | #2SHR(1960) |  | DS1 | 1961 | [13 empty] | 0884 | 885 | 0085 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1961_DS | 1961(161KV #2SHR) DS | OTHER | D13/161/1960/DS1 |  |  |  | DNP | 790 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 161 | 161kV | 1960 | #2SHR(1960) |  | DS2 | 1962 | [13 empty] | 0886 | 887 | 0086 | [8 empty] | ADCS_N | [8 empty] | 虎科DS.1962_DS | 1962(161KV #2SHR) DS | OTHER | D13/161/1960/DS2 |  |  |  | DNP | 791 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D13 | 虎科DS | 0 |  | OLTC | OLTC |  | OLTCA | [14 empty] | 0542 | [10 empty] | ADCS_N | [8 empty] | 虎科DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | D13//4DTR/OLTC_A |  |  |  | DNP | 792 | DNPDIPoint | DS054 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D13 | 虎科DS | 11 | 11kV | 230_SC | #3SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 虎科DS.230_SC_CAP | 11KV#3SC 容量 | SC | [5 empty] | 793 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 11 | 11kV | 240_SC | #4SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 虎科DS.240_SC_CAP | 11KV#4SC 容量 | SC | [5 empty] | 794 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 22 | 22kV | 250_SC | #5SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 虎科DS.250_SC_CAP | 23KV#5SC 容量 | SC | [5 empty] | 795 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 22 | 22kV | 260_SC | #6SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 虎科DS.260_SC_CAP | 23KV#6SC 容量 | SC | [5 empty] | 796 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 22 | 22kV | 270_SC | #7SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 虎科DS.270_SC_CAP | 23KV#7SC 容量 | SC | [5 empty] | 797 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 22 | 22kV | 280_SC | #8SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 虎科DS.280_SC_CAP | 23KV#8SC 容量 | SC | [5 empty] | 798 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 161 | 161kV | 1960_SHR | #2SHR |  | XL | [25 empty] | ADCS_N | [8 empty] | 虎科DS.1960_SHR_XL | 161KV#2SHR 感抗值 | SC | [5 empty] | 799 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | LE0 | 1610LE | [24 empty] | ADCS_N | [8 empty] | 虎科DS.1610LE | 1610LE (非取樣點) | LINE161 | D13/161/1610/LE0 |  |  |  |  | 800 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1610 | 虎科和鑫一路(1610) |  | BE0 | 1610BE | [24 empty] | ADCS_N | [8 empty] | 虎科DS.1610BE | 1610BE (非取樣點) | LINE161 | D13/161/1610/BE0 |  |  |  |  | 801 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | XO31 | XO31_DS |  | DS1 | XO31_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO31_DS | XO31_DS (非取樣點) | FEEDER | D13/11/XO31/DS |  |  |  |  | 802 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | XO31 | XO31_ES |  | LE0 | XO31_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO31_ES | XO31_ES (非取樣點) | FEEDER | D13/11/XO31/ES |  |  |  |  | 803 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1570 | 虎科虎菁一路(1570) |  | LE0 | 1570LE | [24 empty] | ADCS_N | [8 empty] | 虎科DS.1570LE | 1570LE (非取樣點) | LINE161 | D13/161/1570/LE0 |  |  |  |  | 804 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1570 | 虎科虎菁一路(1570) |  | BE0 | 1570BE | [24 empty] | ADCS_N | [8 empty] | 虎科DS.1570BE | 1570BE (非取樣點) | LINE161 | D13/161/1570/BE0 |  |  |  |  | 805 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1580 | 虎科虎菁二路(1580) |  | LE0 | 1580LE | [24 empty] | ADCS_N | [8 empty] | 虎科DS.1580LE | 1580LE (非取樣點) | LINE161 | D13/161/1580/LE0 |  |  |  |  | 806 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1580 | 虎科虎菁二路(1580) |  | BE0 | 1580BE | [24 empty] | ADCS_N | [8 empty] | 虎科DS.1580BE | 1580BE (非取樣點) | LINE161 | D13/161/1580/BE0 |  |  |  |  | 807 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | LE0 | 1620LE | [24 empty] | ADCS_N | [8 empty] | 虎科DS.1620LE | 1620LE (非取樣點) | LINE161 | D13/161/1620/LE0 |  |  |  |  | 808 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1620 | 虎科和鑫二路(1620) |  | BE0 | 1620BE | [24 empty] | ADCS_N | [8 empty] | 虎科DS.1620BE | 1620BE (非取樣點) | LINE161 | D13/161/1620/BE0 |  |  |  |  | 809 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1630 | 越港虎科紅線(1630) |  | LE0 | 1630LE | [24 empty] | ADCS_N | [8 empty] | 虎科DS.1630LE | 1630LE (非取樣點) | LINE161 | D13/161/1630/LE0 |  |  |  |  | 810 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1630 | 越港虎科紅線(1630) |  | BE0 | 1630BE | [24 empty] | ADCS_N | [8 empty] | 虎科DS.1630BE | 1630BE (非取樣點) | LINE161 | D13/161/1630/BE0 |  |  |  |  | 811 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1640 | 越港虎科白線(1640) |  | LE0 | 1640LE | [24 empty] | ADCS_N | [8 empty] | 虎科DS.1640LE | 1640LE (非取樣點) | LINE161 | D13/161/1640/LE0 |  |  |  |  | 812 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1640 | 越港虎科白線(1640) |  | BE0 | 1640BE | [24 empty] | ADCS_N | [8 empty] | 虎科DS.1640BE | 1640BE (非取樣點) | LINE161 | D13/161/1640/BE0 |  |  |  |  | 813 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | XO32 | XO32_DS |  | DS1 | XO32_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO32_DS | XO32_DS (非取樣點) | FEEDER | D13/11/XO32/DS |  |  |  |  | 814 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | XO32 | XO32_ES |  | LE0 | XO32_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO32_ES | XO32_ES (非取樣點) | FEEDER | D13/11/XO32/ES |  |  |  |  | 815 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | XO33 | XO33_DS |  | DS1 | XO33_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO33_DS | XO33_DS (非取樣點) | FEEDER | D13/11/XO33/DS |  |  |  |  | 816 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | XO33 | XO33_ES |  | LE0 | XO33_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO33_ES | XO33_ES (非取樣點) | FEEDER | D13/11/XO33/ES |  |  |  |  | 817 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | XO34 | XO34_DS |  | DS1 | XO34_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO34_DS | XO34_DS (非取樣點) | FEEDER | D13/11/XO34/DS |  |  |  |  | 818 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | XO34 | XO34_ES |  | LE0 | XO34_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO34_ES | XO34_ES (非取樣點) | FEEDER | D13/11/XO34/ES |  |  |  |  | 819 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | XO35 | XO35_DS |  | DS1 | XO35_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO35_DS | XO35_DS (非取樣點) | FEEDER | D13/11/XO35/DS |  |  |  |  | 820 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | XO35 | XO35_ES |  | LE0 | XO35_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO35_ES | XO35_ES (非取樣點) | FEEDER | D13/11/XO35/ES |  |  |  |  | 821 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | XO36 | XO36_DS |  | DS1 | XO36_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO36_DS | XO36_DS (非取樣點) | FEEDER | D13/11/XO36/DS |  |  |  |  | 822 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | XO36 | XO36_ES |  | LE0 | XO36_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO36_ES | XO36_ES (非取樣點) | FEEDER | D13/11/XO36/ES |  |  |  |  | 823 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | XO37 | XO37_DS |  | DS1 | XO37_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO37_DS | XO37_DS (非取樣點) | FEEDER | D13/11/XO37/DS |  |  |  |  | 824 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | XO37 | XO37_ES |  | LE0 | XO37_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO37_ES | XO37_ES (非取樣點) | FEEDER | D13/11/XO37/ES |  |  |  |  | 825 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | XO38 | XO38_DS |  | DS1 | XO38_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO38_DS | XO38_DS (非取樣點) | FEEDER | D13/11/XO38/DS |  |  |  |  | 826 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | XO38 | XO38_ES |  | LE0 | XO38_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO38_ES | XO38_ES (非取樣點) | FEEDER | D13/11/XO38/ES |  |  |  |  | 827 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | XO39 | XO39_DS |  | DS1 | XO39_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO39_DS | XO39_DS (非取樣點) | FEEDER | D13/11/XO39/DS |  |  |  |  | 828 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | XO39 | XO39_ES |  | LE0 | XO39_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO39_ES | XO39_ES (非取樣點) | FEEDER | D13/11/XO39/ES |  |  |  |  | 829 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | XO40 | XO40_DS |  | DS1 | XO40_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO40_DS | XO40_DS (非取樣點) | FEEDER | D13/11/XO40/DS |  |  |  |  | 830 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | XO40 | XO40_ES |  | LE0 | XO40_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO40_ES | XO40_ES (非取樣點) | FEEDER | D13/11/XO40/ES |  |  |  |  | 831 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | XO61 | XO61_DS |  | DS1 | XO61_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO61_DS | XO61_DS (非取樣點) | FEEDER | D13/22/XO61/DS |  |  |  |  | 832 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | XO61 | XO61_ES |  | LE0 | XO61_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO61_ES | XO61_ES (非取樣點) | FEEDER | D13/22/XO61/ES |  |  |  |  | 833 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | XO62 | XO62_DS |  | DS1 | XO62_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO62_DS | XO62_DS (非取樣點) | FEEDER | D13/22/XO62/DS |  |  |  |  | 834 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | XO62 | XO62_ES |  | LE0 | XO62_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO62_ES | XO62_ES (非取樣點) | FEEDER | D13/22/XO62/ES |  |  |  |  | 835 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | XO63 | XO63_DS |  | DS1 | XO63_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO63_DS | XO63_DS (非取樣點) | FEEDER | D13/22/XO63/DS |  |  |  |  | 836 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | XO63 | XO63_ES |  | LE0 | XO63_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO63_ES | XO63_ES (非取樣點) | FEEDER | D13/22/XO63/ES |  |  |  |  | 837 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | XO64 | XO64_DS |  | DS1 | XO64_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO64_DS | XO64_DS (非取樣點) | FEEDER | D13/22/XO64/DS |  |  |  |  | 838 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | XO64 | XO64_ES |  | LE0 | XO64_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO64_ES | XO64_ES (非取樣點) | FEEDER | D13/22/XO64/ES |  |  |  |  | 839 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | XO65 | XO65_DS |  | DS1 | XO65_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO65_DS | XO65_DS (非取樣點) | FEEDER | D13/22/XO65/DS |  |  |  |  | 840 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | XO65 | XO65_ES |  | LE0 | XO65_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO65_ES | XO65_ES (非取樣點) | FEEDER | D13/22/XO65/ES |  |  |  |  | 841 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | XO66 | XO66_DS |  | DS1 | XO66_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO66_DS | XO66_DS (非取樣點) | FEEDER | D13/22/XO66/DS |  |  |  |  | 842 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | XO66 | XO66_ES |  | LE0 | XO66_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO66_ES | XO66_ES (非取樣點) | FEEDER | D13/22/XO66/ES |  |  |  |  | 843 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | XO67 | XO67_DS |  | DS1 | XO67_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO67_DS | XO67_DS (非取樣點) | FEEDER | D13/22/XO67/DS |  |  |  |  | 844 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | XO67 | XO67_ES |  | LE0 | XO67_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO67_ES | XO67_ES (非取樣點) | FEEDER | D13/22/XO67/ES |  |  |  |  | 845 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | XO68 | XO68_DS |  | DS1 | XO68_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO68_DS | XO68_DS (非取樣點) | FEEDER | D13/22/XO68/DS |  |  |  |  | 846 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | XO68 | XO68_ES |  | LE0 | XO68_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO68_ES | XO68_ES (非取樣點) | FEEDER | D13/22/XO68/ES |  |  |  |  | 847 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | XO71 | XO71_DS |  | DS1 | XO71_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO71_DS | XO71_DS (非取樣點) | FEEDER | D13/22/XO71/DS |  |  |  |  | 848 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | XO71 | XO71_ES |  | LE0 | XO71_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO71_ES | XO71_ES (非取樣點) | FEEDER | D13/22/XO71/ES |  |  |  |  | 849 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | XO72 | XO72_DS |  | DS1 | XO72_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO72_DS | XO72_DS (非取樣點) | FEEDER | D13/22/XO72/DS |  |  |  |  | 850 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | XO72 | XO72_ES |  | LE0 | XO72_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO72_ES | XO72_ES (非取樣點) | FEEDER | D13/22/XO72/ES |  |  |  |  | 851 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | XO73 | XO73_DS |  | DS1 | XO73_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO73_DS | XO73_DS (非取樣點) | FEEDER | D13/22/XO73/DS |  |  |  |  | 852 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | XO73 | XO73_ES |  | LE0 | XO73_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO73_ES | XO73_ES (非取樣點) | FEEDER | D13/22/XO73/ES |  |  |  |  | 853 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | XO74 | XO74_DS |  | DS1 | XO74_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO74_DS | XO74_DS (非取樣點) | FEEDER | D13/22/XO74/DS |  |  |  |  | 854 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | XO74 | XO74_ES |  | LE0 | XO74_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO74_ES | XO74_ES (非取樣點) | FEEDER | D13/22/XO74/ES |  |  |  |  | 855 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | XO75 | XO75_DS |  | DS1 | XO75_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO75_DS | XO75_DS (非取樣點) | FEEDER | D13/22/XO75/DS |  |  |  |  | 856 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | XO75 | XO75_ES |  | LE0 | XO75_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO75_ES | XO75_ES (非取樣點) | FEEDER | D13/22/XO75/ES |  |  |  |  | 857 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | XO76 | XO76_DS |  | DS1 | XO76_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO76_DS | XO76_DS (非取樣點) | FEEDER | D13/22/XO76/DS |  |  |  |  | 858 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | XO76 | XO76_ES |  | LE0 | XO76_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO76_ES | XO76_ES (非取樣點) | FEEDER | D13/22/XO76/ES |  |  |  |  | 859 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | XO77 | XO77_DS |  | DS1 | XO77_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO77_DS | XO77_DS (非取樣點) | FEEDER | D13/22/XO77/DS |  |  |  |  | 860 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | XO77 | XO77_ES |  | LE0 | XO77_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO77_ES | XO77_ES (非取樣點) | FEEDER | D13/22/XO77/ES |  |  |  |  | 861 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | XO78 | XO78_DS |  | DS1 | XO78_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO78_DS | XO78_DS (非取樣點) | FEEDER | D13/22/XO78/DS |  |  |  |  | 862 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | XO78 | XO78_ES |  | LE0 | XO78_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎科DS.XO78_ES | XO78_ES (非取樣點) | FEEDER | D13/22/XO78/ES |  |  |  |  | 863 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 100 | TIE(100) |  | E1 | 101E | [24 empty] | ADCS_N | [8 empty] | 虎科DS.101E | 101E (非取樣點) | TIE | D13/11/100/E1 |  |  |  |  | 864 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 100 | TIE(100) |  | E2 | 102E | [24 empty] | ADCS_N | [8 empty] | 虎科DS.102E | 102E (非取樣點) | TIE | D13/11/100/E2 |  |  |  |  | 865 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 101 | 101 |  | 101 | 101 | [24 empty] | ADCS_N | [8 empty] | 虎科DS.101 | 101 (非取樣點) | TIE | D13/11/100/D1 |  |  |  |  | 866 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 102 | 102 |  | 102 | 102 | [24 empty] | ADCS_N | [8 empty] | 虎科DS.102 | 102 (非取樣點) | TIE | D13/11/100/D2 |  |  |  |  | 867 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [24 empty] | ADCS_N | [8 empty] | 虎科DS.1501E | 1501E (非取樣點) | TIE | D13/161/1500/E1 |  |  |  |  | 868 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [24 empty] | ADCS_N | [8 empty] | 虎科DS.1502E | 1502E (非取樣點) | TIE | D13/161/1500/E2 |  |  |  |  | 869 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 200 | TIE(200) |  | E1 | 201E | [24 empty] | ADCS_N | [8 empty] | 虎科DS.201E | 201E (非取樣點) | TIE | D13/11/200/E1 |  |  |  |  | 870 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 200 | TIE(200) |  | E2 | 202E | [24 empty] | ADCS_N | [8 empty] | 虎科DS.202E | 202E (非取樣點) | TIE | D13/11/200/E2 |  |  |  |  | 871 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 201 | 201 |  | 201 | 201 | [24 empty] | ADCS_N | [8 empty] | 虎科DS.201 | 201 (非取樣點) | TIE | D13/11/200/D1 |  |  |  |  | 872 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 202 | 202 |  | 202 | 202 | [24 empty] | ADCS_N | [8 empty] | 虎科DS.202 | 202 (非取樣點) | TIE | D13/11/200/D2 |  |  |  |  | 873 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 300 | TIE(300) |  | E1 | 301E | [24 empty] | ADCS_N | [8 empty] | 虎科DS.301E | 301E (非取樣點) | TIE | D13/22/300/E1 |  |  |  |  | 874 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 300 | TIE(300) |  | E2 | 302E | [24 empty] | ADCS_N | [8 empty] | 虎科DS.302E | 302E (非取樣點) | TIE | D13/22/300/E2 |  |  |  |  | 875 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 301 | 301 |  | 301 | 301 | [24 empty] | ADCS_N | [8 empty] | 虎科DS.301 | 301 (非取樣點) | TIE | D13/22/300/D1 |  |  |  |  | 876 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 302 | 302 |  | 302 | 302 | [24 empty] | ADCS_N | [8 empty] | 虎科DS.302 | 302 (非取樣點) | TIE | D13/22/300/D2 |  |  |  |  | 877 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 400 | TIE(400) |  | E1 | 401E | [24 empty] | ADCS_N | [8 empty] | 虎科DS.401E | 401E (非取樣點) | TIE | D13/22/400/E1 |  |  |  |  | 878 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 400 | TIE(400) |  | E2 | 402E | [24 empty] | ADCS_N | [8 empty] | 虎科DS.402E | 402E (非取樣點) | TIE | D13/22/400/E2 |  |  |  |  | 879 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 401 | 401 |  | 401 | 401 | [24 empty] | ADCS_N | [8 empty] | 虎科DS.401 | 401 (非取樣點) | TIE | D13/22/400/D1 |  |  |  |  | 880 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 402 | 402 |  | 402 | 402 | [24 empty] | ADCS_N | [8 empty] | 虎科DS.402 | 402 (非取樣點) | TIE | D13/22/400/D2 |  |  |  |  | 881 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 391 | 391 |  | 391 | 391 | [24 empty] | ADCS_N | [8 empty] | 虎科DS.391 | 391 (非取樣點) | OTHER | D13/22/390/D1 |  |  |  |  | 882 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 391E | 391E |  | 391E | 391E | [24 empty] | ADCS_N | [8 empty] | 虎科DS.391E | 391E (非取樣點) | OTHER | D13/22/390/E1 |  |  |  |  | 883 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 491 | 491 |  | 491 | 491 | [24 empty] | ADCS_N | [8 empty] | 虎科DS.491 | 491 (非取樣點) | OTHER | D13/22/490/D1 |  |  |  |  | 884 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 491E | 491E |  | 491E | 491E | [24 empty] | ADCS_N | [8 empty] | 虎科DS.491E | 491E (非取樣點) | OTHER | D13/22/490/E1 |  |  |  |  | 885 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | 1760TE | [24 empty] | ADCS_N | [8 empty] | 虎科DS.1760TE | 1760TE (非取樣點) | MTR | D13/161/1760/TE0 |  |  |  |  | 886 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | 1760BE | [24 empty] | ADCS_N | [8 empty] | 虎科DS.1760BE | 1760BE (非取樣點) | MTR | D13/161/1760/BE0 |  |  |  |  | 887 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 331 | 331 |  | 331 | 331 | [24 empty] | ADCS_N | [8 empty] | 虎科DS.331 | 331 (非取樣點) | MTR | D13/11/330/D1 |  |  |  |  | 888 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 330 | #2DTR(330) |  | E1 | 331E | [24 empty] | ADCS_N | [8 empty] | 虎科DS.331E | 331E (非取樣點) | MTR | D13/11/330/E1 |  |  |  |  | 889 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 341 | 341 |  | 341 | 341 | [24 empty] | ADCS_N | [8 empty] | 虎科DS.341 | 341 (非取樣點) | MTR | D13/11/340/D1 |  |  |  |  | 890 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 340 | #2DTR(340) |  | E1 | 341E | [24 empty] | ADCS_N | [8 empty] | 虎科DS.341E | 341E (非取樣點) | MTR | D13/11/340/E1 |  |  |  |  | 891 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | 1770TE | [24 empty] | ADCS_N | [8 empty] | 虎科DS.1770TE | 1770TE (非取樣點) | MTR | D13/161/1770/TE0 |  |  |  |  | 892 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | 1770BE | [24 empty] | ADCS_N | [8 empty] | 虎科DS.1770BE | 1770BE (非取樣點) | MTR | D13/161/1770/BE0 |  |  |  |  | 893 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 351 | 351 |  | 351 | 351 | [24 empty] | ADCS_N | [8 empty] | 虎科DS.351 | 351 (非取樣點) | MTR | D13/22/350/D1 |  |  |  |  | 894 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 350 | #3DTR(350) |  | E1 | 351E | [24 empty] | ADCS_N | [8 empty] | 虎科DS.351E | 351E (非取樣點) | MTR | D13/22/350/E1 |  |  |  |  | 895 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 361 | 361 |  | 361 | 361 | [24 empty] | ADCS_N | [8 empty] | 虎科DS.361 | 361 (非取樣點) | MTR | D13/22/360/D1 |  |  |  |  | 896 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 360 | #3DTR(360) |  | E1 | 361E | [24 empty] | ADCS_N | [8 empty] | 虎科DS.361E | 361E (非取樣點) | MTR | D13/22/360/E1 |  |  |  |  | 897 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1780 | #4DTR(1780) |  | TE0 | 1780TE | [24 empty] | ADCS_N | [8 empty] | 虎科DS.1780TE | 1780TE (非取樣點) | MTR | D13/161/1780/TE0 |  |  |  |  | 898 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 161 | 161kV | 1780 | #4DTR(1780) |  | BE0 | 1780BE | [24 empty] | ADCS_N | [8 empty] | 虎科DS.1780BE | 1780BE (非取樣點) | MTR | D13/161/1780/BE0 |  |  |  |  | 899 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 371 | 371 |  | 371 | 371 | [24 empty] | ADCS_N | [8 empty] | 虎科DS.371 | 371 (非取樣點) | MTR | D13/22/370/D1 |  |  |  |  | 900 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 370 | #4DTR(370) |  | E1 | 371E | [24 empty] | ADCS_N | [8 empty] | 虎科DS.371E | 371E (非取樣點) | MTR | D13/22/370/E1 |  |  |  |  | 901 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 381 | 381 |  | 381 | 381 | [24 empty] | ADCS_N | [8 empty] | 虎科DS.381 | 381 (非取樣點) | MTR | D13/22/380/D1 |  |  |  |  | 902 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 380 | #4DTR(380) |  | E1 | 381E | [24 empty] | ADCS_N | [8 empty] | 虎科DS.381E | 381E (非取樣點) | MTR | D13/22/380/E1 |  |  |  |  | 903 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 231E | 231E |  | 231E | 231E | [24 empty] | ADCS_N | [8 empty] | 虎科DS.231E | 231E (非取樣點) | SC | D13/11/230/ES |  |  |  |  | 904 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 231 | 231 |  | 231 | 231 | [24 empty] | ADCS_N | [8 empty] | 虎科DS.231 | 231 (非取樣點) | SC | D13/11/230/D1 |  |  |  |  | 905 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 241E | 241E |  | 241E | 241E | [24 empty] | ADCS_N | [8 empty] | 虎科DS.241E | 241E (非取樣點) | SC | D13/11/240/E1 |  |  |  |  | 906 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 241 | 241 |  | 241 | 241 | [24 empty] | ADCS_N | [8 empty] | 虎科DS.241 | 241 (非取樣點) | SC | D13/11/240/D1 |  |  |  |  | 907 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 251E | 251E |  | 251E | 251E | [24 empty] | ADCS_N | [8 empty] | 虎科DS.251E | 251E (非取樣點) | SC | D13/22/250/E1 |  |  |  |  | 908 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 251 | 251 |  | 251 | 251 | [24 empty] | ADCS_N | [8 empty] | 虎科DS.251 | 251 (非取樣點) | SC | D13/22/250/D1 |  |  |  |  | 909 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 261E | 261E |  | 261E | 261E | [24 empty] | ADCS_N | [8 empty] | 虎科DS.261E | 261E (非取樣點) | SC | D13/22/260/E1 |  |  |  |  | 910 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 261 | 261 |  | 261 | 261 | [24 empty] | ADCS_N | [8 empty] | 虎科DS.261 | 261 (非取樣點) | SC | D13/22/260/D1 |  |  |  |  | 911 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 271E | 271E |  | 271E | 271E | [24 empty] | ADCS_N | [8 empty] | 虎科DS.271E | 271E (非取樣點) | SC | D13/22/270/E1 |  |  |  |  | 912 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 271 | 271 |  | 271 | 271 | [24 empty] | ADCS_N | [8 empty] | 虎科DS.271 | 271 (非取樣點) | SC | D13/22/270/D1 |  |  |  |  | 913 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 281E | 281E |  | 281E | 281E | [24 empty] | ADCS_N | [8 empty] | 虎科DS.281E | 281E (非取樣點) | SC | D13/22/280/E1 |  |  |  |  | 914 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 281 | 281 |  | 281 | 281 | [24 empty] | ADCS_N | [8 empty] | 虎科DS.281 | 281 (非取樣點) | SC | D13/22/280/D1 |  |  |  |  | 915 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 15B1E | 15B1E |  | BE1 | 15B1E | [24 empty] | ADCS_N | [8 empty] | 虎科DS.15B1E | 15B1E (非取樣點) | BUS | D13/161/161B1E/BE1 |  |  |  |  | 916 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 15B2E | 15B2E |  | BE2 | 15B2E | [24 empty] | ADCS_N | [8 empty] | 虎科DS.15B2E | 15B2E (非取樣點) | BUS | D13/161/161B2E/BE2 |  |  |  |  | 917 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | ADCS_N | [8 empty] | 虎科DS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 918 | NotelDIPoint | [38 empty] | START/STOP | STOP
D13 | 虎科DS | 0 |  | 3A | #3A |  | BE | #3A_BE | [24 empty] | ADCS_N | [8 empty] | 虎科DS.#3A_BE | #3A BE(非取樣點) | OTHER | [5 empty] | 919 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 3B | #3B |  | BE | #3B_BE | [24 empty] | ADCS_N | [8 empty] | 虎科DS.#3B_BE | #3B BE(非取樣點) | OTHER | [5 empty] | 920 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 4A | #4A |  | BE | #4A_BE | [24 empty] | ADCS_N | [8 empty] | 虎科DS.#4A_BE | #4A BE(非取樣點) | OTHER | [5 empty] | 921 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 4B | #4B |  | BE | #4B_BE | [24 empty] | ADCS_N | [8 empty] | 虎科DS.#4B_BE | #4B BE(非取樣點) | OTHER | [5 empty] | 922 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 2A | #2A |  | BE | #2A_BE | [24 empty] | ADCS_N | [8 empty] | 虎科DS.#2A_BE | #2A BE(非取樣點) | OTHER | [5 empty] | 923 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 2B | #2B |  | BE | #2B_BE | [24 empty] | ADCS_N | [8 empty] | 虎科DS.#2B_BE | #2B BE(非取樣點) | OTHER | [5 empty] | 924 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  |  |  |  | 1960BE | 1960BE | [24 empty] | ADCS_N | [8 empty] | 虎科DS.1960BE | 1960BE(非取樣點) | OTHER | D13/161/1960/BE0 |  |  |  |  | 925 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  |  |  |  | 1960RE | 1960RE | [24 empty] | ADCS_N | [8 empty] | 虎科DS.1960RE | 1960RE(非取樣點) | OTHER | D13/161/1960/RE0 |  |  |  |  | 926 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 2ABUS | 2ABUS |  | PTD | 2ABUS_PTD | [24 empty] | ADCS_N | [8 empty] | 虎科DS.2ABUS_PTD | #2ABUS_PTD(非取樣點) | OTHER | [5 empty] | 927 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 2ABUS | 2ABUS |  | PTE | 2ABUS_PTE | [24 empty] | ADCS_N | [8 empty] | 虎科DS.2ABUS_PTE | #2ABUS_PTE(非取樣點) | OTHER | [5 empty] | 928 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 2BBUS | 2BBUS |  | PTD | 2BBUS_PTD | [24 empty] | ADCS_N | [8 empty] | 虎科DS.2BBUS_PTD | #2BBUS_PTD(非取樣點) | OTHER | [5 empty] | 929 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 2BBUS | 2BBUS |  | PTE | 2BBUS_PTE | [24 empty] | ADCS_N | [8 empty] | 虎科DS.2BBUS_PTE | #2BBUS_PTE(非取樣點) | OTHER | [5 empty] | 930 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 3ABUS | 3ABUS |  | PTD | 3ABUS_PTD | [24 empty] | ADCS_N | [8 empty] | 虎科DS.3ABUS_PTD | #3ABUS_PTD(非取樣點) | OTHER | [5 empty] | 931 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 3ABUS | 3ABUS |  | PTE | 3ABUS_PTE | [24 empty] | ADCS_N | [8 empty] | 虎科DS.3ABUS_PTE | #3ABUS_PTE(非取樣點) | OTHER | [5 empty] | 932 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 3BBUS | 3BBUS |  | PTD | 3BBUS_PTD | [24 empty] | ADCS_N | [8 empty] | 虎科DS.3BBUS_PTD | #3BBUS_PTD(非取樣點) | OTHER | [5 empty] | 933 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 3BBUS | 3BBUS |  | PTE | 3BBUS_PTE | [24 empty] | ADCS_N | [8 empty] | 虎科DS.3BBUS_PTE | #3BBUS_PTE(非取樣點) | OTHER | [5 empty] | 934 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 4ABUS | 4ABUS |  | PTD | 4ABUS_PTD | [24 empty] | ADCS_N | [8 empty] | 虎科DS.4ABUS_PTD | #4ABUS_PTD(非取樣點) | OTHER | [5 empty] | 935 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 4ABUS | 4ABUS |  | PTE | 4ABUS_PTE | [24 empty] | ADCS_N | [8 empty] | 虎科DS.4ABUS_PTE | #4ABUS_PTE(非取樣點) | OTHER | [5 empty] | 936 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D13 | 虎科DS | 0 |  | 4BBUS | 4BBUS |  | PTD | 4BBUS_PTD | [24 empty] | ADCS_N | [8 empty] | 虎科DS.4BBUS_PTD | #4BBUS_PTD(非取樣點) | OTHER | [5 empty] | 937 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D13 | 虎科DS | 0 |  | 4BBUS | 4BBUS |  | PTE | 4BBUS_PTE | [24 empty] | ADCS_N | [8 empty] | 虎科DS.4BBUS_PTE | #4BBUS_PTE(非取樣點) | OTHER | [5 empty] | 938 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo