## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛～北回一路(1510) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D14_A1 | [8 empty] | 北回DS.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 2 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛～北回一路(1510) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D14_A1 | [8 empty] | 北回DS.1510BE | 1510BE (非取樣點) | LINE161 | [5 empty] | 3 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛～北回二路(1520) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D14_A1 | [8 empty] | 北回DS.1520LE | 1520LE (非取樣點) | LINE161 | [5 empty] | 4 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛～北回二路(1520) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D14_A1 | [8 empty] | 北回DS.1520BE | 1520BE (非取樣點) | LINE161 | [5 empty] | 5 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D14_A1 | [8 empty] | 北回DS.1530LE | 1530LE (非取樣點) | LINE161 | [5 empty] | 6 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D14_A1 | [8 empty] | 北回DS.1530BE | 1530BE (非取樣點) | LINE161 | [5 empty] | 7 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D14_A1 | [8 empty] | 北回DS.1540LE | 1540LE (非取樣點) | LINE161 | [5 empty] | 8 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D14_A1 | [8 empty] | 北回DS.1540BE | 1540BE (非取樣點) | LINE161 | [5 empty] | 9 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D14_A1 | [8 empty] | 北回DS.1501E | 1501E (非取樣點) | TIE | [5 empty] | 10 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D14_A1 | [8 empty] | 北回DS.1502E | 1502E (非取樣點) | TIE | [5 empty] | 11 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D14_A1 | [8 empty] | 北回DS.1750TE | 1750TE (非取樣點) | MTR | [5 empty] | 12 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D14_A1 | [8 empty] | 北回DS.1750BE | 1750BE (非取樣點) | MTR | [5 empty] | 13 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | D1 | 311(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D14_A1 | [8 empty] | 北回DS.311 | 311 (非取樣點) | MTR | [5 empty] | 14 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | E1 | 311E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D14_A1 | [8 empty] | 北回DS.311E | 311E (非取樣點) | MTR | [5 empty] | 15 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | D1 | 321(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D14_A1 | [8 empty] | 北回DS.321 | 321 (非取樣點) | MTR | [5 empty] | 16 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | E1 | 321E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D14_A1 | [8 empty] | 北回DS.321E | 321E (非取樣點) | MTR | [5 empty] | 17 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D14_A1 | [8 empty] | 北回DS.1760TE | 1760TE (非取樣點) | MTR | [5 empty] | 18 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D14_A1 | [8 empty] | 北回DS.1760BE | 1760BE (非取樣點) | MTR | [5 empty] | 19 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | D1 | 331(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D14_A1 | [8 empty] | 北回DS.331 | 331 (非取樣點) | MTR | [5 empty] | 20 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | E1 | 331E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D14_A1 | [8 empty] | 北回DS.331E | 331E (非取樣點) | MTR | [5 empty] | 21 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | D1 | 341(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D14_A1 | [8 empty] | 北回DS.341 | 341 (非取樣點) | MTR | [5 empty] | 22 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | E1 | 341E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D14_A1 | [8 empty] | 北回DS.341E | 341E (非取樣點) | MTR | [5 empty] | 23 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 11 | 11kV | 210 | #1SC(210) |  | E1 | 211E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D14_A1 | [8 empty] | 北回DS.211E | 211E (非取樣點) | SC | [5 empty] | 24 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 11 | 11kV | 210 | #1SC(210) |  | DS1 | 211(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D14_A1 | [8 empty] | 北回DS.211 | 211 (非取樣點) | SC | [5 empty] | 25 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | 390 | #1SSTR(390) |  | D1 | 391(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D14_A1 | [8 empty] | 北回DS.391 | 391 (非取樣點) | OTHER | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | 390 | #1SSTR(390) |  | E1 | 391E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D14_A1 | [8 empty] | 北回DS.391E | 391E (非取樣點) | OTHER | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 11 | 11kV | JJ21 | 回21線(JJ21) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ21_DS | JJ21_DS (非取樣點) | FEEDER | [5 empty] | 28 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | JJ21 | 回21線(JJ21) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ21_ES | JJ21_ES (非取樣點) | FEEDER | [5 empty] | 29 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 11 | 11kV | JJ22 | 回22線(JJ22) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ22_DS | JJ22_DS (非取樣點) | FEEDER | [5 empty] | 30 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | JJ22 | 回22線(JJ22) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ22_ES | JJ22_ES (非取樣點) | FEEDER | [5 empty] | 31 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 11 | 11kV | JJ23 | 回23線(JJ23) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ23_DS | JJ23_DS (非取樣點) | FEEDER | [5 empty] | 32 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | JJ23 | 回23線(JJ23) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ23_ES | JJ23_ES (非取樣點) | FEEDER | [5 empty] | 33 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 11 | 11kV | JJ24 | 回24線(JJ24) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ24_DS | JJ24_DS (非取樣點) | FEEDER | [5 empty] | 34 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | JJ24 | 回24線(JJ24) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ24_ES | JJ24_ES (非取樣點) | FEEDER | [5 empty] | 35 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 11 | 11kV | JJ25 | 回25線(JJ25) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ25_DS | JJ25_DS (非取樣點) | FEEDER | [5 empty] | 36 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | JJ25 | 回25線(JJ25) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ25_ES | JJ25_ES (非取樣點) | FEEDER | [5 empty] | 37 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 11 | 11kV | 100 | TIE(100) |  | D1 | 101(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D14_A1 | [8 empty] | 北回DS.101 | 101 (非取樣點) | TIE | [5 empty] | 38 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | 100 | TIE(100) |  | D2 | 102(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D14_A1 | [8 empty] | 北回DS.102 | 102 (非取樣點) | TIE | [5 empty] | 39 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | 100 | TIE(100) |  | E1 | 101E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D14_A1 | [8 empty] | 北回DS.101E | 101E(非取樣點) | OTHER | [5 empty] | 40 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 11 | 11kV | 100 | TIE(100) |  | E2 | 102E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D14_A1 | [8 empty] | 北回DS.102E | 102E(非取樣點) | OTHER | [5 empty] | 41 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 22 | 22kV | 220 | #2SC(220) |  | E1 | 221E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D14_A1 | [8 empty] | 北回DS.221E | 221E (非取樣點) | SC | [5 empty] | 42 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 22 | 22kV | 220 | #2SC(220) |  | D1 | 221(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D14_A1 | [8 empty] | 北回DS.221 | 221 (非取樣點) | SC | [5 empty] | 43 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | JJ56 | 回56線(JJ56) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ56_DS | JJ56_DS (非取樣點) | FEEDER | [5 empty] | 44 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | JJ56 | 回56線(JJ56) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ56_ES | JJ56_ES (非取樣點) | FEEDER | [5 empty] | 45 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 22 | 22kV | JJ57 | 回57線(JJ57) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ57_DS | JJ57_DS (非取樣點) | FEEDER | [5 empty] | 46 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | JJ57 | 回57線(JJ57) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ57_ES | JJ57_ES (非取樣點) | FEEDER | [5 empty] | 47 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 22 | 22kV | JJ58 | 回58線(JJ58) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ58_DS | JJ58_DS (非取樣點) | FEEDER | [5 empty] | 48 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | JJ58 | 回58線(JJ58) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ58_ES | JJ58_ES (非取樣點) | FEEDER | [5 empty] | 49 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 22 | 22kV | JJ59 | 回59線(JJ59) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ59_DS | JJ59_DS (非取樣點) | FEEDER | [5 empty] | 50 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | JJ59 | 回59線(JJ59) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ59_ES | JJ59_ES (非取樣點) | FEEDER | [5 empty] | 51 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 22 | 22kV | JJ60 | 回60線(JJ60) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ60_DS | JJ60_DS (非取樣點) | FEEDER | [5 empty] | 52 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | JJ60 | 回60線(JJ60) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ60_ES | JJ60_ES (非取樣點) | FEEDER | [5 empty] | 53 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 22 | 22kV | 200 | TIE(200) |  | D1 | 201(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D14_A1 | [8 empty] | 北回DS.201 | 201 (非取樣點) | TIE | [5 empty] | 54 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | 200 | TIE(200) |  | D2 | 202(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D14_A1 | [8 empty] | 北回DS.202 | 202 (非取樣點) | TIE | [5 empty] | 55 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | 200 | TIE(200) |  | E1 | 201E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D14_A1 | [8 empty] | 北回DS.201E | 201E(非取樣點) | OTHER | [5 empty] | 56 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 22 | 22kV | 200 | TIE(200) |  | E2 | 202E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D14_A1 | [8 empty] | 北回DS.202E | 202E(非取樣點) | OTHER | [5 empty] | 57 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 11 | 11kV | 230 | #3SC(230) |  | E1 | 231E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D14_A1 | [8 empty] | 北回DS.231E | 231E (非取樣點) | SC | [5 empty] | 58 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 11 | 11kV | 230 | #3SC(230) |  | DS1 | 231(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D14_A1 | [8 empty] | 北回DS.231 | 231 (非取樣點) | SC | [5 empty] | 59 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | JJ31 | 回31線(JJ31) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ31_DS | JJ31_DS (非取樣點) | FEEDER | [5 empty] | 60 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | JJ31 | 回31線(JJ31) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ31_ES | JJ31_ES (非取樣點) | FEEDER | [5 empty] | 61 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 11 | 11kV | JJ32 | 回32線(JJ32) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ32_DS | JJ32_DS (非取樣點) | FEEDER | [5 empty] | 62 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | JJ32 | 回32線(JJ32) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ32_ES | JJ32_ES (非取樣點) | FEEDER | [5 empty] | 63 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 11 | 11kV | JJ33 | 回33線(JJ33) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ33_DS | JJ33_DS (非取樣點) | FEEDER | [5 empty] | 64 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | JJ33 | 回33線(JJ33) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ33_ES | JJ33_ES (非取樣點) | FEEDER | [5 empty] | 65 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 11 | 11kV | JJ34 | 回34線(JJ34) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ34_DS | JJ34_DS (非取樣點) | FEEDER | [5 empty] | 66 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | JJ34 | 回34線(JJ34) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ34_ES | JJ34_ES (非取樣點) | FEEDER | [5 empty] | 67 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 11 | 11kV | JJ35 | 回35線(JJ35) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ35_DS | JJ35_DS (非取樣點) | FEEDER | [5 empty] | 68 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | JJ35 | 回35線(JJ35) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ35_ES | JJ35_ES (非取樣點) | FEEDER | [5 empty] | 69 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 22 | 22kV | 240 | #4SC(240) |  | E1 | 241E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D14_A1 | [8 empty] | 北回DS.241E | 241E (非取樣點) | SC | [5 empty] | 70 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 22 | 22kV | 240 | #4SC(240) |  | D1 | 241(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D14_A1 | [8 empty] | 北回DS.241 | 241 (非取樣點) | SC | [5 empty] | 71 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | 490 | #2SSTR(490) |  | D1 | 491(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D14_A1 | [8 empty] | 北回DS.491 | 491 (非取樣點) | OTHER | [5 empty] | 72 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | 490 | #2SSTR(490) |  | E1 | 491E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D14_A1 | [8 empty] | 北回DS.491E | 491E (非取樣點) | OTHER | [5 empty] | 73 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 22 | 22kV | JJ66 | 回66線(JJ66) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ66_DS | JJ66_DS (非取樣點) | FEEDER | [5 empty] | 74 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | JJ66 | 回66線(JJ66) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ66_ES | JJ66_ES (非取樣點) | FEEDER | [5 empty] | 75 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 22 | 22kV | JJ67 | 回67線(JJ67) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ67_DS | JJ67_DS (非取樣點) | FEEDER | [5 empty] | 76 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | JJ67 | 回67線(JJ67) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ67_ES | JJ67_ES (非取樣點) | FEEDER | [5 empty] | 77 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 22 | 22kV | JJ68 | 回68線(JJ68) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ68_DS | JJ68_DS (非取樣點) | FEEDER | [5 empty] | 78 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | JJ68 | 回68線(JJ68) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ68_ES | JJ68_ES (非取樣點) | FEEDER | [5 empty] | 79 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 22 | 22kV | JJ69 | 回69線(JJ69) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ69_DS | JJ69_DS (非取樣點) | FEEDER | [5 empty] | 80 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | JJ69 | 回69線(JJ69) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ69_ES | JJ69_ES (非取樣點) | FEEDER | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 22 | 22kV | JJ70 | 回70線(JJ70) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ70_DS | JJ70_DS (非取樣點) | FEEDER | [5 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | JJ70 | 回70線(JJ70) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D14_D1 | [8 empty] | 北回DS.JJ70_ES | JJ70_ES (非取樣點) | FEEDER | [5 empty] | 83 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | 15B1E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aaaz | B2/D14_A1 | [8 empty] | 北回DS.15B1E | 15B1E (非取樣點) | BUS | [5 empty] | 84 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | 15B2E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/2Bus | [13 empty] | aaaz | B2/D14_A1 | [8 empty] | 北回DS.15B2E | 15B2E (非取樣點) | BUS | [5 empty] | 85 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | RTU | RTU |  | ADCL1 |  |  | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | Locate Empty |  | TEST #1 10% | ADCL_-2000_2000(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.AI_ADCL1 | AI10%參考點 ADCL1 | OTHER | [5 empty] | 86 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D14 | 北回DS | 0 |  | RTU | RTU |  | ADCH1 |  |  | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | Locate Empty |  | TEST #1 90% | ADCH_-2000_2000(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.AI_ADCH1 | AI90%參考點 ADCH1 | OTHER | [5 empty] | 87 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D14 | 北回DS | 161 | 161kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | MCC_2B | KV | 161KV #1BUS 電壓 | kV_-210_210(-2000_2000) | aaa | B2/D14_A1 | [8 empty] | 北回DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | [5 empty] | 88 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D14 | 北回DS | 161 | 161kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0003 |  |  | 1-83 |  |  | MCC_2B | KV | 161KV #2BUS 電壓 | kV_-210_210(-2000_2000) | aab | B2/D14_A1 | [8 empty] | 北回DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | [5 empty] | 89 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛～北回一路(1510) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | MCC_2A | MW | 1510 仁愛北回一路 MW | MW_-560_560(-2000_2000) |  | B2/D14_A1 | [8 empty] | 北回DS.1510_MW | 仁愛北回一路 MW | LINE161 | [5 empty] | 90 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛～北回一路(1510) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | MCC_2A | MVAR | 1510 仁愛北回一路 MVAR | MVAR_-560_560(-2000_2000) |  | B2/D14_A1 | [8 empty] | 北回DS.1510_MVAR | 仁愛北回一路 MVAR | LINE161 | [5 empty] | 91 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛～北回二路(1520) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | MCC_2A | MW | 1520 仁愛北回二路 MW | MW_-560_560(-2000_2000) |  | B2/D14_A1 | [8 empty] | 北回DS.1520_MW | 仁愛北回二路 MW | LINE161 | [5 empty] | 92 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛～北回二路(1520) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | MCC_2A | MVAR | 1520 仁愛北回二路 MVAR | MVAR_-560_560(-2000_2000) |  | B2/D14_A1 | [8 empty] | 北回DS.1520_MVAR | 仁愛北回二路 MVAR | LINE161 | [5 empty] | 93 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D14 | 北回DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | MCC_2A | MW | 1530 北回太鐵紅線 MW | MW_-560_560(-2000_2000) |  | B2/D14_A1 | [8 empty] | 北回DS.1530_MW | 北回太鐵紅線 MW | LINE161 | [5 empty] | 94 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D14 | 北回DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | MCC_2A | MVAR | 1530 北回太鐵紅線 MVAR | MVAR_-560_560(-2000_2000) |  | B2/D14_A1 | [8 empty] | 北回DS.1530_MVAR | 北回太鐵紅線 MVAR | LINE161 | [5 empty] | 95 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D14 | 北回DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | MCC_2A | MW | 1540 北回太鐵白線 MW | MW_-560_560(-2000_2000) |  | B2/D14_A1 | [8 empty] | 北回DS.1540_MW | 北回太鐵白線 MW | LINE161 | [5 empty] | 96 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D14 | 北回DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | MCC_2A | MVAR | 1540 北回太鐵白線 MVAR | MVAR_-560_560(-2000_2000) |  | B2/D14_A1 | [8 empty] | 北回DS.1540_MVAR | 北回太鐵白線 MVAR | LINE161 | [5 empty] | 97 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛～北回一路(1510) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | Locate Empty | KV | 1510 仁愛北回一路 LPT | kV_-210_210(-2000_2000) |  | B2/D14_A1 | [8 empty] | 北回DS.1510LPD_KV | 仁愛北回一路(1510) LPD KV | LINE161 | [5 empty] | 98 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛～北回二路(1520) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | Locate Empty | KV | 1520 仁愛北回二路 LPT | kV_-210_210(-2000_2000) |  | B2/D14_A1 | [8 empty] | 北回DS.1520LPD_KV | 仁愛北回二路(1520) LPD KV | LINE161 | [5 empty] | 99 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D14 | 北回DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | Locate Empty | KV | 1530 北回太鐵紅線 LPT | kV_-210_210(-2000_2000) |  | B2/D14_A1 | [8 empty] | 北回DS.1530LPD_KV | 北回太鐵紅線(1530) LPD KV | LINE161 | [5 empty] | 100 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D14 | 北回DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | Locate Empty | KV | 1540 北回太鐵白線 LPT | kV_-210_210(-2000_2000) |  | B2/D14_A1 | [8 empty] | 北回DS.1540LPD_KV | 北回太鐵白線(1540) LPD KV | LINE161 | [5 empty] | 101 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D14 | 北回DS | 161 | 161kV | 1500 | TIE(1500) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0024 |  |  | 1-98 |  |  | MCC2B | A | 1500 TIE R相電流 | A_-2000_2000(-2000_2000) |  | B2/D14_A1 | [8 empty] | 北回DS.1500TIE_AMP | 1500TIE AMP | TIE | [5 empty] | 102 |  |  |  |  | AI | [5 empty] | C20R1600 | 1520 | 1600 | 1760 | 1968 | 2.27 | -1520 | -1600 | -1760 | -1968 | 1 | 0.01 | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0768 |  | 0000 | 2-38-00 |  | 1-00 | 100 | DS(ON) | TIE-1A(100) DS-AS |  |  | ELEM/ALL | [16 empty] | 103 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛～北回一路(1510) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D12D141/T2 |  | 0000 |  | 0001 | 1-00-00 |  | 1-01 | MCC2A | 52AS | 1510 仁愛北回一路 CB |  | aaca | B2/D14_A1 | [8 empty] | 北回DS.1510_CB | 1510(仁愛北回一路) CB | LINE161 | [5 empty] | 104 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS |  |  | 1DTR | #1DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0027 |  |  | 1-9B |  |  | MCC1B | ℃ | 1750 #1DTR 油溫指示量 | OIL_-120_120(-2000_2000) |  | B1/D14_A1 | [8 empty] | 北回DS.#1DTR_OIL | #1DTR 油溫 | MTR | [5 empty] | 105 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D14 | 北回DS |  |  | 1DTR(A) | #1DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | MCC1B | ℃ | 1750 #1DTR 線溫指示量1A | COIL_-120_120(-2000_2000) |  | B1/D14_A1 | [8 empty] | 北回DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | [5 empty] | 106 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D14 | 北回DS |  |  | 1DTR(B) | #1DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | MCC1B | ℃ | 1750 #1DTR 線溫指示量1B | COIL_-120_120(-2000_2000) |  | B1/D14_A1 | [8 empty] | 北回DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | [5 empty] | 107 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛～北回二路(1520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D12D142/T2 |  | 0005 |  | 0002 | 1-00-05 |  | 1-02 | MCC2A | 52AS | 1520 仁愛北回二路 CB |  | aada | B2/D14_A1 | [8 empty] | 北回DS.1520_CB | 1520(仁愛北回二路) CB | LINE161 | [5 empty] | 108 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D14D07R/T1 |  | 0010 |  | 0003 | 1-01-02 |  | 1-03 | MCC2A | 52AS | 1530 北回太鐵紅線 CB |  | aaga | B2/D14_A1 | [8 empty] | 北回DS.1530_CB | 1530(北回太鐵紅線) CB | LINE161 | [5 empty] | 109 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS |  |  | 2DTR | #2DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | MCC1B | ℃ | 1760 #2DTR 油溫指示量 | OIL_-120_120(-2000_2000) |  | B1/D14_A1 | [8 empty] | 北回DS.#2DTR_OIL | #2DTR 油溫 | MTR | [5 empty] | 110 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D14 | 北回DS |  |  | 2DTR(A) | #2DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | MCC1B | ℃ | 1760 #2DTR 線溫指示量1A | COIL_-120_120(-2000_2000) |  | B1/D14_A1 | [8 empty] | 北回DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | [5 empty] | 111 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D14 | 北回DS |  |  | 2DTR(B) | #2DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | MCC1B | ℃ | 1760 #2DTR 線溫指示量1B | COIL_-120_120(-2000_2000) |  | B1/D14_A1 | [8 empty] | 北回DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | [5 empty] | 112 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D14 | 北回DS | 11 | 11kV | 1ABUS | #1ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0045 |  |  | 1-AD |  |  | 310 | KV | #1A BUS PT-1A | kV_-9_9(-2000_2000) | aaa | B3/D14_A1 | [8 empty] | 北回DS.11KV#1ABUS_KV | 11KV #1ABUS KV | BUS | [5 empty] | 113 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D14 | 北回DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | 310 | MW | M-1A(310) MW | MW_-36_36(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | [5 empty] | 114 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D14 | 北回DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | 310 | MVAR | M-1A(310) MVAR | MVAR_-36_36(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | [5 empty] | 115 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D14 | 北回DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | 310 | A | M-1A(310) R相電流 | A_-2000_2000(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | [5 empty] | 116 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | 310 | A | M-1A(310) S相電流量 | A_-2000_2000(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | [5 empty] | 117 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | 310 | A | M-1A(310) T相電流量 | A_-2000_2000(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | [5 empty] | 118 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ21 | 回21線(JJ21) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | JJ21 | KVAR | F-1(JJ21)回21線 KVAR | KVAR_-9000_9000(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回21線KVAR | 11KV回21線 KVAR | FEEDER | [5 empty] | 119 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ21 | 回21線(JJ21) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | JJ21 | A | F-1(JJ21)回21線 R相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回21線A1 | 11KV回21線 R相AMP | FEEDER | [5 empty] | 120 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ21 | 回21線(JJ21) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | JJ21 | A | F-1(JJ21)回21線 S相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回21線A2 | 11KV回21線 S相AMP | FEEDER | [5 empty] | 121 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ21 | 回21線(JJ21) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | JJ21 | A | F-1(JJ21)回21線 T相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回21線A3 | 11KV回21線 T相AMP | FEEDER | [5 empty] | 122 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ21 | 回21線(JJ21) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | JJ21 | A | F-1(JJ21)回21線 N相電流量 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回21線A0 | 11KV回21線 N相AMP | FEEDER | [5 empty] | 123 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ22 | 回22線(JJ22) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | JJ22 | KVAR | F-2(JJ22)回22線 KVAR | KVAR_-9000_9000(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回22線KVAR | 11KV回22線 KVAR | FEEDER | [5 empty] | 124 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ22 | 回22線(JJ22) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | JJ22 | A | F-2(JJ22)回22線 R相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回22線A1 | 11KV回22線 R相AMP | FEEDER | [5 empty] | 125 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ22 | 回22線(JJ22) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0060 |  |  | 1-BC |  |  | JJ22 | A | F-2(JJ22)回22線 S相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回22線A2 | 11KV回22線 S相AMP | FEEDER | [5 empty] | 126 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ22 | 回22線(JJ22) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | JJ22 | A | F-2(JJ22)回22線 T相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回22線A3 | 11KV回22線 T相AMP | FEEDER | [5 empty] | 127 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ22 | 回22線(JJ22) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | JJ22 | A | F-2(JJ22)回22線 N相電流量 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回22線A0 | 11KV回22線 N相AMP | FEEDER | [5 empty] | 128 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 0 |  | RTU | RTU |  | ADCL2 |  |  | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | Locate Empty |  | TEST #2 10% | ADCL_-2000_2000(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.AI_ADCL2 | AI10%參考點 ADCL2 | OTHER | [5 empty] | 129 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D14 | 北回DS | 0 |  | RTU | RTU |  | ADCH2 |  |  | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | Locate Empty |  | TEST #2 90% | ADCH_-2000_2000(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.AI_ADCH2 | AI90%參考點 ADCH2 | OTHER | [5 empty] | 130 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ23 | 回23線(JJ23) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | JJ23 | KVAR | F-3(JJ23)回23線 KVAR | KVAR_-9000_9000(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回23線KVAR | 11KV回23線 KVAR | FEEDER | [5 empty] | 131 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ23 | 回23線(JJ23) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | JJ23 | A | F-3(JJ23)回23線 R相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回23線A1 | 11KV回23線 R相AMP | FEEDER | [5 empty] | 132 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ23 | 回23線(JJ23) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | JJ23 | A | F-3(JJ23)回23線 S相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回23線A2 | 11KV回23線 S相AMP | FEEDER | [5 empty] | 133 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ23 | 回23線(JJ23) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | JJ23 | A | F-3(JJ23)回23線 T相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回23線A3 | 11KV回23線 T相AMP | FEEDER | [5 empty] | 134 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ23 | 回23線(JJ23) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | JJ23 | A | F-3(JJ23)回23線 N相電流量 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回23線A0 | 11KV回23線 N相AMP | FEEDER | [5 empty] | 135 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ24 | 回24線(JJ24) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | JJ24 | KVAR | F-4(JJ24)回24線 KVAR | KVAR_-9000_9000(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回24線KVAR | 11KV回24線 KVAR | FEEDER | [5 empty] | 136 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ24 | 回24線(JJ24) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | JJ24 | A | F-4(JJ24)回24線 R相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回24線A1 | 11KV回24線 R相AMP | FEEDER | [5 empty] | 137 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ24 | 回24線(JJ24) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | JJ24 | A | F-4(JJ24)回24線 S相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回24線A2 | 11KV回24線 S相AMP | FEEDER | [5 empty] | 138 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ24 | 回24線(JJ24) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | JJ24 | A | F-4(JJ24)回24線 T相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回24線A3 | 11KV回24線 T相AMP | FEEDER | [5 empty] | 139 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ24 | 回24線(JJ24) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | JJ24 | A | F-4(JJ24)回24線 N相電流量 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回24線A0 | 11KV回24線 N相AMP | FEEDER | [5 empty] | 140 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ25 | 回25線(JJ25) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | JJ25 | KVAR | F-5(JJ25)回25線 KVAR | KVAR_-9000_9000(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回25線KVAR | 11KV回25線 KVAR | FEEDER | [5 empty] | 141 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ25 | 回25線(JJ25) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | JJ25 | A | F-5(JJ25)回25線 R相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回25線A1 | 11KV回25線 R相AMP | FEEDER | [5 empty] | 142 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ25 | 回25線(JJ25) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | JJ25 | A | F-5(JJ25)回25線 S相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回25線A2 | 11KV回25線 S相AMP | FEEDER | [5 empty] | 143 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ25 | 回25線(JJ25) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | JJ25 | A | F-5(JJ25)回25線 T相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回25線A3 | 11KV回25線 T相AMP | FEEDER | [5 empty] | 144 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ25 | 回25線(JJ25) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | JJ25 | A | F-5(JJ25)回25線 N相電流量 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回25線A0 | 11KV回25線 N相AMP | FEEDER | [5 empty] | 145 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 100 | TIE(100) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | 100 | A | TIE-1A(100) R相電流量 | A_-2000_2000(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.11KV_100_A1 | 11KV 100 R相AMP | TIE | [5 empty] | 146 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 100 | TIE(100) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | 100 | A | TIE-1A(100) S相電流量 | A_-2000_2000(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.11KV_100_A2 | 11KV 100 S相AMP | TIE | [5 empty] | 147 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 100 | TIE(100) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | 100 | A | TIE-1A(100) T相電流量 | A_-2000_2000(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.11KV_100_A3 | 11KV 100 T相AMP | TIE | [5 empty] | 148 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 1BBUS | #1BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0086 |  |  | 1-D6 |  |  | 320 | KV | #1B BUS PT-1B | kV_-18_18(-2000_2000) | baa | B3/D14_A1 | [8 empty] | 北回DS.23KV#1BBUS_KV | 23KV #1BBUS KV | BUS | [5 empty] | 149 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D14 | 北回DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | 320 | MW | M-1B(320) MW | MW_-72_72(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | [5 empty] | 150 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D14 | 北回DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | 320 | MVAR | M-1B(320) MVAR | MVAR_-72_72(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | [5 empty] | 151 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D14 | 北回DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | 320 | A | M-1B(320) R相電流 | A_-2000_2000(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | [5 empty] | 152 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | 320 | A | M-1B(320) S相電流量 | A_-2000_2000(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | [5 empty] | 153 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | 320 | A | M-1B(320) T相電流量 | A_-2000_2000(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | [5 empty] | 154 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ56 | 回56線(JJ56) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | JJ56 | KVAR | F-6(JJ56)回56線 KVAR | KVAR_-18000_18000(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回56線KVAR | 23KV回56線 KVAR | FEEDER | [5 empty] | 155 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ56 | 回56線(JJ56) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | JJ56 | A | F-6(JJ56)回56線 R相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回56線A1 | 23KV回56線 R相AMP | FEEDER | [5 empty] | 156 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ56 | 回56線(JJ56) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | JJ56 | A | F-6(JJ56)回56線 S相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回56線A2 | 23KV回56線 S相AMP | FEEDER | [5 empty] | 157 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ56 | 回56線(JJ56) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | JJ56 | A | F-6(JJ56)回56線 T相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回56線A3 | 23KV回56線 T相AMP | FEEDER | [5 empty] | 158 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ56 | 回56線(JJ56) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | JJ56 | A | F-6(JJ56)回56線 N相電流量 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回56線A0 | 23KV回56線 N相AMP | FEEDER | [5 empty] | 159 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ57 | 回57線(JJ57) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | JJ57 | KVAR | F-7(JJ57)回57線 KVAR | KVAR_-18000_18000(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回57線KVAR | 23KV回57線 KVAR | FEEDER | [5 empty] | 160 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ57 | 回57線(JJ57) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | JJ57 | A | F-7(JJ57)回57線 R相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回57線A1 | 23KV回57線 R相AMP | FEEDER | [5 empty] | 161 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ57 | 回57線(JJ57) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0101 |  |  | 1-E5 |  |  | JJ57 | A | F-7(JJ57)回57線 S相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回57線A2 | 23KV回57線 S相AMP | FEEDER | [5 empty] | 162 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ57 | 回57線(JJ57) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | JJ57 | A | F-7(JJ57)回57線 T相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回57線A3 | 23KV回57線 T相AMP | FEEDER | [5 empty] | 163 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ57 | 回57線(JJ57) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | JJ57 | A | F-7(JJ57)回57線 N相電流量 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回57線A0 | 23KV回57線 N相AMP | FEEDER | [5 empty] | 164 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ58 | 回58線(JJ58) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | JJ58 | KVAR | F-8(JJ58)回58線 KVAR | KVAR_-18000_18000(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回58線KVAR | 23KV回58線 KVAR | FEEDER | [5 empty] | 165 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ58 | 回58線(JJ58) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | JJ58 | A | F-8(JJ58)回58線 R相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回58線A1 | 23KV回58線 R相AMP | FEEDER | [5 empty] | 166 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ58 | 回58線(JJ58) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | JJ58 | A | F-8(JJ58)回58線 S相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回58線A2 | 23KV回58線 S相AMP | FEEDER | [5 empty] | 167 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ58 | 回58線(JJ58) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | JJ58 | A | F-8(JJ58)回58線 T相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回58線A3 | 23KV回58線 T相AMP | FEEDER | [5 empty] | 168 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ58 | 回58線(JJ58) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | JJ58 | A | F-8(JJ58)回58線 N相電流量 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回58線A0 | 23KV回58線 N相AMP | FEEDER | [5 empty] | 169 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ59 | 回59線(JJ59) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | JJ59 | KVAR | F-9(JJ59)回59線 KVAR | KVAR_-18000_18000(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回59線KVAR | 23KV回59線 KVAR | FEEDER | [5 empty] | 170 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ59 | 回59線(JJ59) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | JJ59 | A | F-9(JJ59)回59線 R相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回59線A1 | 23KV回59線 R相AMP | FEEDER | [5 empty] | 171 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ59 | 回59線(JJ59) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | JJ59 | A | F-9(JJ59)回59線 S相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回59線A2 | 23KV回59線 S相AMP | FEEDER | [5 empty] | 172 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ59 | 回59線(JJ59) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | JJ59 | A | F-9(JJ59)回59線 T相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回59線A3 | 23KV回59線 T相AMP | FEEDER | [5 empty] | 173 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ59 | 回59線(JJ59) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | JJ59 | A | F-9(JJ59)回59線 N相電流量 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回59線A0 | 23KV回59線 N相AMP | FEEDER | [5 empty] | 174 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ60 | 回60線(JJ60) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | JJ60 | KVAR | F-10(JJ60)回60線 KVAR | KVAR_-18000_18000(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回60線KVAR | 23KV回60線 KVAR | FEEDER | [5 empty] | 175 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ60 | 回60線(JJ60) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | JJ60 | A | F-10(JJ60)回60線 R相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回60線A1 | 23KV回60線 R相AMP | FEEDER | [5 empty] | 176 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ60 | 回60線(JJ60) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | JJ60 | A | F-10(JJ60)回60線 S相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回60線A2 | 23KV回60線 S相AMP | FEEDER | [5 empty] | 177 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ60 | 回60線(JJ60) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | JJ60 | A | F-10(JJ60)回60線 T相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回60線A3 | 23KV回60線 T相AMP | FEEDER | [5 empty] | 178 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ60 | 回60線(JJ60) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | JJ60 | A | F-10(JJ60)回60線 N相電流量 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回60線A0 | 23KV回60線 N相AMP | FEEDER | [5 empty] | 179 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 200 | TIE(200) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | 200 | A | TIE-1B(200) R相電流量 | A_-2000_2000(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.23KV_200_A1 | 23KV 200 R相AMP | TIE | [5 empty] | 180 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 200 | TIE(200) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | 200 | A | TIE-1B(200) S相電流量 | A_-2000_2000(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.23KV_200_A2 | 23KV 200 S相AMP | TIE | [5 empty] | 181 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 200 | TIE(200) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | 200 | A | TIE-1B(200) T相電流量 | A_-2000_2000(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.23KV_200_A3 | 23KV 200 T相AMP | TIE | [5 empty] | 182 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 2ABUS | #2ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0125 |  |  | 1-FD |  |  | 330 | KV | #2A BUS PT-2A | kV_-9_9(-2000_2000) | aba | B3/D14_A1 | [8 empty] | 北回DS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS | [5 empty] | 183 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D14 | 北回DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | 330 | MW | M-2A(330) MW | MW_-36_36(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | [5 empty] | 184 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D14 | 北回DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | 330 | MVAR | M-2A(330) MVAR | MVAR_-36_36(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | [5 empty] | 185 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D14 | 北回DS | 0 |  | RTU | RTU |  | ADCL3 |  |  | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | Locate Empty |  | TEST #3 10% | ADCL_-2000_2000(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.AI_ADCL3 | AI10%參考點 ADCL3 | OTHER | [5 empty] | 186 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D14 | 北回DS | 0 |  | RTU | RTU |  | ADCH3 |  |  | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | Locate Empty |  | TEST #3 90% | ADCH_-2000_2000(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.AI_ADCH3 | AI90%參考點 ADCH3 | OTHER | [5 empty] | 187 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | 330 | A | M-2A(330) R相電流 | A_-2000_2000(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | [5 empty] | 188 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | 330 | A | M-2A(330) S相電流量 | A_-2000_2000(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | [5 empty] | 189 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | 330 | A | M-2A(330) T相電流量 | A_-2000_2000(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | [5 empty] | 190 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ31 | 回31線(JJ31) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | JJ31 | KVAR | F11-(JJ31)回31線 KVAR | KVAR_-9000_9000(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回31線KVAR | 11KV回31線 KVAR | FEEDER | [5 empty] | 191 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ31 | 回31線(JJ31) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0135 |  |  | 2-87 |  |  | JJ31 | A | F11-(JJ31)回31線 R相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回31線A1 | 11KV回31線 R相AMP | FEEDER | [5 empty] | 192 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ31 | 回31線(JJ31) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0136 |  |  | 2-88 |  |  | JJ31 | A | F11-(JJ31)回31線 S相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回31線A2 | 11KV回31線 S相AMP | FEEDER | [5 empty] | 193 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ31 | 回31線(JJ31) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0137 |  |  | 2-89 |  |  | JJ31 | A | F11-(JJ31)回31線 T相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回31線A3 | 11KV回31線 T相AMP | FEEDER | [5 empty] | 194 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ31 | 回31線(JJ31) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0138 |  |  | 2-8A |  |  | JJ31 | A | F11-(JJ31)回31線 N相電流量 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回31線A0 | 11KV回31線 N相AMP | FEEDER | [5 empty] | 195 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ32 | 回32線(JJ32) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0140 |  |  | 2-8C |  |  | JJ32 | KVAR | F12-(JJ32)回32線 KVAR | KVAR_-9000_9000(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回32線KVAR | 11KV回32線 KVAR | FEEDER | [5 empty] | 196 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ32 | 回32線(JJ32) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0141 |  |  | 2-8D |  |  | JJ32 | A | F12-(JJ32)回32線 R相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回32線A1 | 11KV回32線 R相AMP | FEEDER | [5 empty] | 197 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ32 | 回32線(JJ32) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0142 |  |  | 2-8E |  |  | JJ32 | A | F12-(JJ32)回32線 S相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回32線A2 | 11KV回32線 S相AMP | FEEDER | [5 empty] | 198 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ32 | 回32線(JJ32) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0143 |  |  | 2-8F |  |  | JJ32 | A | F12-(JJ32)回32線 T相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回32線A3 | 11KV回32線 T相AMP | FEEDER | [5 empty] | 199 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ32 | 回32線(JJ32) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0144 |  |  | 2-90 |  |  | JJ32 | A | F12-(JJ32)回32線 N相電流量 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回32線A0 | 11KV回32線 N相AMP | FEEDER | [5 empty] | 200 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ33 | 回33線(JJ33) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0146 |  |  | 2-92 |  |  | JJ33 | KVAR | F13-(JJ33)回33線 KVAR | KVAR_-9000_9000(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回33線KVAR | 11KV回33線 KVAR | FEEDER | [5 empty] | 201 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ33 | 回33線(JJ33) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0147 |  |  | 2-93 |  |  | JJ33 | A | F13-(JJ33)回33線 R相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回33線A1 | 11KV回33線 R相AMP | FEEDER | [5 empty] | 202 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ33 | 回33線(JJ33) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0148 |  |  | 2-94 |  |  | JJ33 | A | F13-(JJ33)回33線 S相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回33線A2 | 11KV回33線 S相AMP | FEEDER | [5 empty] | 203 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ33 | 回33線(JJ33) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0149 |  |  | 2-95 |  |  | JJ33 | A | F13-(JJ33)回33線 T相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回33線A3 | 11KV回33線 T相AMP | FEEDER | [5 empty] | 204 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ33 | 回33線(JJ33) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0150 |  |  | 2-96 |  |  | JJ33 | A | F13-(JJ33)回33線 N相電流量 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回33線A0 | 11KV回33線 N相AMP | FEEDER | [5 empty] | 205 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ34 | 回34線(JJ34) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0152 |  |  | 2-98 |  |  | JJ34 | KVAR | F14-(JJ34)回34線 KVAR | KVAR_-9000_9000(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回34線KVAR | 11KV回34線 KVAR | FEEDER | [5 empty] | 206 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ34 | 回34線(JJ34) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0153 |  |  | 2-99 |  |  | JJ34 | A | F14-(JJ34)回34線 R相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回34線A1 | 11KV回34線 R相AMP | FEEDER | [5 empty] | 207 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ34 | 回34線(JJ34) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0154 |  |  | 2-9A |  |  | JJ34 | A | F14-(JJ34)回34線 S相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回34線A2 | 11KV回34線 S相AMP | FEEDER | [5 empty] | 208 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ34 | 回34線(JJ34) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0155 |  |  | 2-9B |  |  | JJ34 | A | F14-(JJ34)回34線 T相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回34線A3 | 11KV回34線 T相AMP | FEEDER | [5 empty] | 209 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ34 | 回34線(JJ34) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0156 |  |  | 2-9C |  |  | JJ34 | A | F14-(JJ34)回34線 N相電流量 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回34線A0 | 11KV回34線 N相AMP | FEEDER | [5 empty] | 210 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ35 | 回35線(JJ35) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0158 |  |  | 2-9E |  |  | JJ35 | KVAR | F15-(JJ35)回35線 KVAR | KVAR_-9000_9000(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回35線KVAR | 11KV回35線 KVAR | FEEDER | [5 empty] | 211 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ35 | 回35線(JJ35) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0159 |  |  | 2-9F |  |  | JJ35 | A | F15-(JJ35)回35線 R相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回35線A1 | 11KV回35線 R相AMP | FEEDER | [5 empty] | 212 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ35 | 回35線(JJ35) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0160 |  |  | 2-A0 |  |  | JJ35 | A | F15-(JJ35)回35線 S相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回35線A2 | 11KV回35線 S相AMP | FEEDER | [5 empty] | 213 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ35 | 回35線(JJ35) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0161 |  |  | 2-A1 |  |  | JJ35 | A | F15-(JJ35)回35線 T相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回35線A3 | 11KV回35線 T相AMP | FEEDER | [5 empty] | 214 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | JJ35 | 回35線(JJ35) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0162 |  |  | 2-A2 |  |  | JJ35 | A | F15-(JJ35)回35線 N相電流量 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回35線A0 | 11KV回35線 N相AMP | FEEDER | [5 empty] | 215 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 2BBUS | #2BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0163 |  |  | 2-A3 |  |  | 340 | KV | #2B BUS PT-2B | kV_-18_18(-2000_2000) | bba | B3/D14_A1 | [8 empty] | 北回DS.23KV#2BBUS_KV | 23KV #2BBUS KV | BUS | [5 empty] | 216 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D14 | 北回DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0164 |  |  | 2-A4 |  |  | 340 | MW | M-2B(340) MW | MW_-72_72(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | [5 empty] | 217 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D14 | 北回DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0165 |  |  | 2-A5 |  |  | 340 | MVAR | M-2B(340) MVAR | MVAR_-72_72(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | [5 empty] | 218 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D14 | 北回DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0166 |  |  | 2-A6 |  |  | 340 | A | M-2B(340) R相電流 | A_-2000_2000(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | [5 empty] | 219 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0167 |  |  | 2-A7 |  |  | 340 | A | M-2B(340) S相電流量 | A_-2000_2000(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | [5 empty] | 220 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0168 |  |  | 2-A8 |  |  | 340 | A | M-2B(340) T相電流量 | A_-2000_2000(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | [5 empty] | 221 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ66 | 回66線(JJ66) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0170 |  |  | 2-AA |  |  | JJ66 | KVAR | F-16(JJ66)回66線 KVAR | KVAR_-18000_18000(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回66線KVAR | 23KV回66線 KVAR | FEEDER | [5 empty] | 222 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ66 | 回66線(JJ66) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0171 |  |  | 2-AB |  |  | JJ66 | A | F-16(JJ66)回66線 R相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回66線A1 | 23KV回66線 R相AMP | FEEDER | [5 empty] | 223 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ66 | 回66線(JJ66) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0172 |  |  | 2-AC |  |  | JJ66 | A | F-16(JJ66)回66線 S相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回66線A2 | 23KV回66線 S相AMP | FEEDER | [5 empty] | 224 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ66 | 回66線(JJ66) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0173 |  |  | 2-AD |  |  | JJ66 | A | F-16(JJ66)回66線 T相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回66線A3 | 23KV回66線 T相AMP | FEEDER | [5 empty] | 225 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ66 | 回66線(JJ66) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0174 |  |  | 2-AE |  |  | JJ66 | A | F-16(JJ66)回66線 N相電流量 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回66線A0 | 23KV回66線 N相AMP | FEEDER | [5 empty] | 226 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ67 | 回67線(JJ67) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0176 |  |  | 2-B0 |  |  | JJ67 | KVAR | F-17(JJ22)回22線8 KVAR | KVAR_-18000_18000(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回67線KVAR | 23KV回67線 KVAR | FEEDER | [5 empty] | 227 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ67 | 回67線(JJ67) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0177 |  |  | 2-B1 |  |  | JJ67 | A | F-17(JJ67)回67線 R相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回67線A1 | 23KV回67線 R相AMP | FEEDER | [5 empty] | 228 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ67 | 回67線(JJ67) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0178 |  |  | 2-B2 |  |  | JJ67 | A | F-17(JJ67)回67線 S相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回67線A2 | 23KV回67線 S相AMP | FEEDER | [5 empty] | 229 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ67 | 回67線(JJ67) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0179 |  |  | 2-B3 |  |  | JJ67 | A | F-17(JJ67)回67線 T相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回67線A3 | 23KV回67線 T相AMP | FEEDER | [5 empty] | 230 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ67 | 回67線(JJ67) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0180 |  |  | 2-B4 |  |  | JJ67 | A | F-17(JJ67)回67線 N相電流量 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回67線A0 | 23KV回67線 N相AMP | FEEDER | [5 empty] | 231 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ68 | 回68線(JJ68) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0182 |  |  | 2-B6 |  |  | JJ68 | KVAR | F-18(JJ68)回68線 KVAR | KVAR_-18000_18000(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回68線KVAR | 23KV回68線 KVAR | FEEDER | [5 empty] | 232 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ68 | 回68線(JJ68) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0183 |  |  | 2-B7 |  |  | JJ68 | A | F-18(JJ68)回68線 R相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回68線A1 | 23KV回68線 R相AMP | FEEDER | [5 empty] | 233 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ68 | 回68線(JJ68) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0184 |  |  | 2-B8 |  |  | JJ68 | A | F-18(JJ68)回68線 S相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回68線A2 | 23KV回68線 S相AMP | FEEDER | [5 empty] | 234 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ68 | 回68線(JJ68) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0185 |  |  | 2-B9 |  |  | JJ68 | A | F-18(JJ68)回68線 T相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回68線A3 | 23KV回68線 T相AMP | FEEDER | [5 empty] | 235 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ68 | 回68線(JJ68) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0186 |  |  | 2-BA |  |  | JJ68 | A | F-18(JJ68)回68線 N相電流量 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回68線A0 | 23KV回68線 N相AMP | FEEDER | [5 empty] | 236 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ69 | 回69線(JJ69) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0188 |  |  | 2-BC |  |  | JJ69 | KVAR | F-19(JJ69)回69線 KVAR | KVAR_-18000_18000(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回69線KVAR | 23KV回69線 KVAR | FEEDER | [5 empty] | 237 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ69 | 回69線(JJ69) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0189 |  |  | 2-BD |  |  | JJ69 | A | F-19(JJ69)回69線 R相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回69線A1 | 23KV回69線 R相AMP | FEEDER | [5 empty] | 238 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ69 | 回69線(JJ69) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0190 |  |  | 2-BE |  |  | JJ69 | A | F-19(JJ69)回69線 S相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回69線A2 | 23KV回69線 S相AMP | FEEDER | [5 empty] | 239 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ69 | 回69線(JJ69) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0191 |  |  | 2-BF |  |  | JJ69 | A | F-19(JJ69)回69線 T相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回69線A3 | 23KV回69線 T相AMP | FEEDER | [5 empty] | 240 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 0 |  | RTU | RTU |  | ADCL4 |  |  | MvMoment | No4 AI參考點 10% |  | Y |  | AI | [6 empty] | 0192 |  |  | 2-C0 |  |  | Locate Empty |  | TEST #4 10% | ADCL_-2000_2000(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.AI_ADCL4 | AI10%參考點 ADCL4 | OTHER | [5 empty] | 241 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D14 | 北回DS | 0 |  | RTU | RTU |  | ADCH4 |  |  | MvMoment | No4 AI參考點 90% |  | Y |  | AI | [6 empty] | 0193 |  |  | 2-C1 |  |  | Locate Empty |  | TEST #4 90% | ADCH_-2000_2000(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.AI_ADCH4 | AI90%參考點 ADCH4 | OTHER | [5 empty] | 242 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ69 | 回69線(JJ69) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0194 |  |  | 2-C2 |  |  | JJ69 | A | F-19(JJ69)回69線 N相電流量 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回69線A0 | 23KV回69線 N相AMP | FEEDER | [5 empty] | 243 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ70 | 回70線(JJ70) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0196 |  |  | 2-C4 |  |  | JJ26 | KVAR | F-20(JJ70)回70線 KVAR | KVAR_-18000_18000(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回70線KVAR | 23KV回70線 KVAR | FEEDER | [5 empty] | 244 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 18 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ70 | 回70線(JJ70) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0197 |  |  | 2-C5 |  |  | JJ26 | A | F-20(JJ70)回70線 R相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回70線A1 | 23KV回70線 R相AMP | FEEDER | [5 empty] | 245 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ70 | 回70線(JJ70) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0198 |  |  | 2-C6 |  |  | JJ26 | A | F-20(JJ70)回70線 S相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回70線A2 | 23KV回70線 S相AMP | FEEDER | [5 empty] | 246 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ70 | 回70線(JJ70) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0199 |  |  | 2-C7 |  |  | JJ26 | A | F-20(JJ70)回70線 T相電流 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回70線A3 | 23KV回70線 T相AMP | FEEDER | [5 empty] | 247 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | JJ70 | 回70線(JJ70) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0200 |  |  | 2-C8 |  |  | JJ26 | A | F-20(JJ70)回70線 N相電流量 | A_-500_500(-2000_2000) |  | B2/D14_D1 | [8 empty] | 北回DS.回70線A0 | 23KV回70線 N相AMP | FEEDER | [5 empty] | 248 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 0 |  | StaDev | 所內設施 |  | DCV_P |  |  | MvMoment | 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0328 |  |  | 3-C8 |  |  | Locate Empty | V | 直流P電源電壓 | kV_-150_150(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.直流P電源電壓 | 直流P電源電壓 | OTHER | [5 empty] | 249 |  |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 | 0.01 | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D14 | 北回DS | 0 |  | StaDev | 所內設施 |  | DCV_N |  |  | MvMoment | 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0329 |  |  | 3-C9 |  |  | Locate Empty | V | 直流N電源電壓 | kV_-150_150(-2000_2000) |  | B3/D14_A1 | [8 empty] | 北回DS.直流N電源電壓 | 直流N電源電壓 | OTHER | [5 empty] | 250 |  |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 | 0.01 | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D14 | 北回DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D14D07W/T1 |  | 0015 |  | 0004 | 1-01-07 |  | 1-04 | MCC2A | 52AS | 1540 北回太鐵白線 CB |  | aaha | B2/D14_A1 | [8 empty] | 北回DS.1540_CB | 1540(北回太鐵白線) CB | LINE161 | [5 empty] | 251 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛～北回一路(1510) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0001 |  |  | 1-00-01 |  |  | MCC1A | 87LA | 1510 仁愛北回一路 87A |  |  | B2/D14_A1 | [8 empty] | 北回DS.1510_87A | 仁愛北回一路(1510) 87RY | LINE161 | [5 empty] | 252 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛～北回一路(1510) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | MCC1A | PHA | 1510 仁愛北回一路 相間電驛PHA |  |  | B2/D14_A1 | [8 empty] | 北回DS.1510_PHA | 仁愛北回一路(1510) 相間RY | LINE161 | [5 empty] | 253 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛～北回一路(1510) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0004 |  |  | 1-00-04 |  |  | MCC1A | GDA | 1510 仁愛北回一路 接地電驛GDA |  |  | B2/D14_A1 | [8 empty] | 北回DS.1510_GDA | 仁愛北回一路(1510) 接地RY | LINE161 | [5 empty] | 254 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0050 |  | 0011 | 1-06-02 |  | 1-0B | MCC2B | 52AS | 1500 CB |  | aaez | B2/D14_A1 | [8 empty] | 北回DS.1500_CB | 1500(TIE) CB | TIE | [5 empty] | 255 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛～北回二路(1520) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | MCC1A | 87LA | 1520 仁愛北回二路 87A |  |  | B2/D14_A1 | [8 empty] | 北回DS.1520_87A | 仁愛北回二路(1520) 87RY | LINE161 | [5 empty] | 256 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛～北回二路(1520) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-01-00 |  |  | MCC1A | PHA | 1520 仁愛北回二路 相間電驛PHA |  |  | B2/D14_A1 | [8 empty] | 北回DS.1520_PHA | 仁愛北回二路(1520) 相間RY | LINE161 | [5 empty] | 257 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛～北回二路(1520) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | MCC1A | GDA | 1520 仁愛北回二路 接地電驛GDA |  |  | B2/D14_A1 | [8 empty] | 北回DS.1520_GDA | 仁愛北回二路(1520) 接地RY | LINE161 | [5 empty] | 258 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/1DTR |  | 0059 |  | 0012 | 1-07-03 |  | 1-0C | MCC2B | 52AS | 1750 CB |  | aabb | ELEM/D14_A1 | [8 empty] | 北回DS.1750_CB | 1750(#1DTR) CB | MTR | [5 empty] | 259 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-03 |  |  | MCC1A | 87LA | 1530 北回太鐵紅線 87A |  |  | B2/D14_A1 | [8 empty] | 北回DS.1530_87A | 北回太鐵紅線(1530) 87RY | LINE161 | [5 empty] | 260 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0013 |  |  | 1-01-05 |  |  | MCC1A | PHA | 1530 北回太鐵紅線 相間電驛PHA |  |  | B2/D14_A1 | [8 empty] | 北回DS.1530_PHA | 北回太鐵紅線(1530) 相間RY | LINE161 | [5 empty] | 261 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-06 |  |  | MCC1A | GDA | 1530 北回太鐵紅線 接地電驛GDA |  |  | B2/D14_A1 | [8 empty] | 北回DS.1530_GDA | 北回太鐵紅線(1530) 接地RY | LINE161 | [5 empty] | 262 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2DTR |  | 0072 |  | 0013 | 1-09-00 |  | 1-0D | MCC2B | 52AS | 1760 CB |  | aafb | ELEM/D14_A1 | [8 empty] | 北回DS.1760_CB | 1760(#2DTR) CB | MTR | [5 empty] | 263 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-02-00 |  |  | MCC1A | 87LA | 1540 北回太鐵白線 87A |  |  | B2/D14_A1 | [8 empty] | 北回DS.1540_87A | 北回太鐵白線(1540) 87RY | LINE161 | [5 empty] | 264 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 |  |  | 1-02-02 |  |  | MCC1A | PHA | 1540 北回太鐵白線 相間電驛PHA |  |  | B2/D14_A1 | [8 empty] | 北回DS.1540_PHA | 北回太鐵白線(1540) 相間RY | LINE161 | [5 empty] | 265 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0019 |  |  | 1-02-03 |  |  | MCC1A | GDA | 1540 北回太鐵白線 接地電驛GDA |  |  | B2/D14_A1 | [8 empty] | 北回DS.1540_GDA | 北回太鐵白線(1540) 接地RY | LINE161 | [5 empty] | 266 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | T/1DTR(A) |  |  | 0066 |  | 0016 | 1-08-02 |  | 1-10 | 310 | 52AS | M-1A(310) CB |  | aada | ELEM/D14_A1 | [8 empty] | 北回DS.310_CB | 310(#1DTR) CB | MTR | [5 empty] | 267 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0051 |  |  | 1-06-03 |  |  | MCC1B | 50A | 1500 瞬時電驛50A |  |  | B2/D14_A1 | [8 empty] | 北回DS.1500_50A | 161KV TIE(1500) 50RY | TIE | [5 empty] | 268 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | MCC1B | 87B1A | 161KV BUS#1差動電驛(87B1A) |  |  | B2/D14_A1 | [8 empty] | 北回DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | [5 empty] | 269 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0053 |  |  | 1-06-05 |  |  | MCC1B | 87B2A | 161KV BUS#2差動電驛(87B2A) |  |  | B2/D14_A1 | [8 empty] | 北回DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | [5 empty] | 270 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0055 |  |  | 1-06-07 |  |  | MCC2B | 1 RCA | 161KV 系統79電驛動作(RCA) |  |  | B3/D14_A1 | [8 empty] | 北回DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | [5 empty] | 271 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | ComPoint |  |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0056 |  |  | 1-07-00 |  |  | MCC2B | LOA | 23KV 系統79電驛動作(LOA) |  |  | B3/D14_A1 | [8 empty] | 北回DS.11/23KV_LOA | 11/23KV 饋線復閉失敗 | OTHER | [5 empty] | 272 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0057 |  |  | 1-07-01 |  |  | MCC1A | 1 OSCA | 161KV 系統示波器啟動警報(OSCA) |  |  | B3/D14_A1 | [8 empty] | 北回DS.161KV_OSCA | 161KV示波器啟動警報 | OTHER | [5 empty] | 273 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | 210 | #1SC(210) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | A/LBS210^C/1SC(A) |  |  | 0160 |  | 0017 | 1-14-00 |  | 1-11 | 210 | 52AS | #1SC(210) CB |  | aajb | B3/D14_A1 | [8 empty] | 北回DS.210_CB | 210(11KV #1SC) CB | SC | [5 empty] | 274 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS |  |  | 1DTR | #1DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0060 |  |  | 1-07-04 |  |  | MCC1B | 87TA | #1DTR 差動電驛警報(87TA) |  |  | B1/D14_A1 | [8 empty] | 北回DS.#1DTR_87A | #1DTR 87RY | MTR | [5 empty] | 275 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS |  |  | 1DTR | #1DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0061 |  |  | 1-07-05 |  |  | MCC1B | 96PA | #1DTR 機械保護動作(96PA) |  |  | B1/D14_A1 | [8 empty] | 北回DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | [5 empty] | 276 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS |  |  | 1DTR | #1DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0062 |  |  | 1-07-06 |  |  | MCC1B | 1 51ZA | #1DTR 中性點接地電驛(#1 & #2 51Z1A) |  |  | B1/D14_A1 | [8 empty] | 北回DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | [5 empty] | 277 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS |  |  | 1DTR | #1DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0064 |  |  | 1-08-00 |  |  | MCC1B | PHA | #1DTR 相間電驛PHA |  |  | B1/D14_A1 | [8 empty] | 北回DS.#1DTR_51A | #1DTR 51RY | MTR | [5 empty] | 278 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS |  |  | 1DTR | #1DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0065 |  |  | 1-08-01 |  |  | MCC1B | GDA | #1DTR 接地電驛GDA |  |  | B1/D14_A1 | [8 empty] | 北回DS.#1DTR_51NA | #1DTR 51N RY | MTR | [5 empty] | 279 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | 390 | #1SSTR(390) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | T/1SSTR |  |  | 0163 |  | 0018 | 1-14-03 |  | 1-12 | 390 | 52AS | #1SSTR(390) CB |  | aacb | B3/D14_A1 | [8 empty] | 北回DS.390_CB | 390(#1SSTR) CB | OTHER | [5 empty] | 280 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | PHA1 |  |  | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0067 |  |  | 1-08-03 |  |  | 310 | PHA | M-1A(310) 相間電驛PHA |  |  | B3/D14_A1 | [8 empty] | 北回DS.310_PHA | 310開關箱IED RY PHA | OTHER | [5 empty] | 281 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 |  |  | 1-08-04 |  |  | 310 | GDA | M-1A(310) 接地電驛GDA |  |  | B3/D14_A1 | [8 empty] | 北回DS.310_GDA | 310開關箱IED RY GDA | OTHER | [5 empty] | 282 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ21 | 回21線(JJ21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/JJ21/T1 |  |  | 0166 |  | 0019 | 1-14-06 |  | 1-13 | JJ21 | 52AS | F-1(JJ21)回21線 CB |  | aaeb | B2/D14_D1 | [8 empty] | 北回DS.JJ21_CB | JJ21(11KV回21線) CB | FEEDER | [5 empty] | 283 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | PHA1 |  |  | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0070 |  |  | 1-08-06 |  |  | 320 | PHA | M-1B(320) 相間電驛PHA |  |  | B3/D14_A1 | [8 empty] | 北回DS.320_PHA | 320開關箱IED RY PHA | OTHER | [5 empty] | 284 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0071 |  |  | 1-08-07 |  |  | 320 | GDA | M-1B(320) 接地電驛GDA |  |  | B3/D14_A1 | [8 empty] | 北回DS.320_GDA | 320開關箱IED RY GDA | OTHER | [5 empty] | 285 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ22 | 回22線(JJ22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/JJ22/T1 |  |  | 0169 |  | 0020 | 1-15-01 |  | 1-14 | JJ22 | 52AS | F-2(JJ22)回22線 CB |  | aafb | B2/D14_D1 | [8 empty] | 北回DS.JJ22_CB | JJ22(11KV回22線) CB | FEEDER | [5 empty] | 286 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS |  |  | 2DTR | #2DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0073 |  |  | 1-09-01 |  |  | MCC1B | 87A | #2DTR 差動電驛警報(87TA) |  |  | B1/D14_A1 | [8 empty] | 北回DS.#2DTR_87A | #2DTR 87RY | MTR | [5 empty] | 287 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS |  |  | 2DTR | #2DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-09-02 |  |  | MCC1B | 96PA | #2DTR 機械保護動作(96PA) |  |  | B1/D14_A1 | [8 empty] | 北回DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | [5 empty] | 288 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS |  |  | 2DTR | #2DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0075 |  |  | 1-09-03 |  |  | MCC1B | 1 51ZA | #2DTR 中性點接地電驛(#1 & #2 51Z1) |  |  | B1/D14_A1 | [8 empty] | 北回DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | [5 empty] | 289 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS |  |  | 2DTR | #2DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0077 |  |  | 1-09-05 |  |  | MCC1B | PHA | #2DTR 相間電驛PHA |  |  | B1/D14_A1 | [8 empty] | 北回DS.#2DTR_51A | #2DTR 51RY | MTR | [5 empty] | 290 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS |  |  | 2DTR | #2DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0078 |  |  | 1-09-06 |  |  | MCC1B | GDA | #2DTR 接地電驛GDA |  |  | B1/D14_A1 | [8 empty] | 北回DS.#2DTR_51NA | #2DTR 51N RY | MTR | [5 empty] | 291 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ23 | 回23線(JJ23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/JJ23/T1 |  |  | 0172 |  | 0021 | 1-15-04 |  | 1-15 | JJ23 | 52AS | F-3(JJ23)回23線 CB |  | aagb | B2/D14_D1 | [8 empty] | 北回DS.JJ23_CB | JJ23(11KV回23線) CB | FEEDER | [5 empty] | 292 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | PHA1 |  |  | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0080 |  |  | 1-0A-00 |  |  | 330 | PHA | M-2A(330) 相間電驛PHA |  |  | B3/D14_A1 | [8 empty] | 北回DS.330_PHA | 330開關箱IED RY PHA | OTHER | [5 empty] | 293 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0081 |  |  | 1-0A-01 |  |  | 330 | GDA | M-2A(330) 接地電驛GDA |  |  | B3/D14_A1 | [8 empty] | 北回DS.330_GDA | 330開關箱IED RY GDA | OTHER | [5 empty] | 294 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ24 | 回24線(JJ24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/JJ24/T1 |  |  | 0175 |  | 0022 | 1-15-07 |  | 1-16 | JJ24 | 52AS | F-4(JJ24)回24線 CB |  | aahb | B2/D14_D1 | [8 empty] | 北回DS.JJ24_CB | JJ24(11KV回24線) CB | FEEDER | [5 empty] | 295 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | PHA1 |  |  | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0083 |  |  | 1-0A-03 |  |  | 340 | PHA | M-2B(340)(340) 相間電驛PHA |  |  | B3/D14_A1 | [8 empty] | 北回DS.340_PHA | 340開關箱IED RY PHA | OTHER | [5 empty] | 296 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0084 |  |  | 1-0A-04 |  |  | 340 | GDA | M-2B(340)(340) 接地電驛GDA |  |  | B3/D14_A1 | [8 empty] | 北回DS.340_GDA | 340開關箱IED RY GDA | OTHER | [5 empty] | 297 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛～北回一路(1510) |  | 25TA |  |  | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0110 |  |  | 1-0D-06 |  |  | MCC1A | 25TA | 1510 仁愛北回一路 25電驛超時警報 |  |  | B2/D14_A1 | [8 empty] | 北回DS.1510_25TA | 1510 同步校核電驛超時動作 | OTHER | [5 empty] | 298 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛～北回二路(1520) |  | 25TA |  |  | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0112 |  |  | 1-0E-00 |  |  | MCC1A | 25TA | 1520 仁愛北回二路 25電驛超時警報 |  |  | B2/D14_A1 | [8 empty] | 北回DS.1520_25TA | 1520 同步校核電驛超時動作 | OTHER | [5 empty] | 299 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | 25TA |  |  | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0114 |  |  | 1-0E-02 |  |  | MCC1A | 25TA | 1530 北回太鐵紅線 25電驛超時警報 |  |  | B2/D14_A1 | [8 empty] | 北回DS.1530_25TA | 1530 同步校核電驛超時動作 | OTHER | [5 empty] | 300 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | 25TA |  |  | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0116 |  |  | 1-0E-04 |  |  | MCC1A | 25TA | 1540 北回太鐵白線 25電驛超時警報 |  |  | B2/D14_A1 | [8 empty] | 北回DS.1540_25TA | 1540 同步校核電驛超時動作 | OTHER | [5 empty] | 301 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛～北回一路(1510) |  | DTTA |  |  | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-10-02 |  |  | MCC1A | DTTA | 1510 仁愛北回一路 遠方遙跳 |  |  | B2/D14_A1 | [8 empty] | 北回DS.1510_DTTA | 仁愛北回一路(1510) 遠方遙跳 | OTHER | [5 empty] | 302 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛～北回二路(1520) |  | DTTA |  |  | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0131 |  |  | 1-10-03 |  |  | MCC1A | DTTA | 1520 仁愛北回二路 遠方遙跳 |  |  | B2/D14_A1 | [8 empty] | 北回DS.1520_DTTA | 仁愛北回二路(1520) 遠方遙跳 | OTHER | [5 empty] | 303 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | DTTA |  |  | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0132 |  |  | 1-10-04 |  |  | MCC1A | DTTA | 1530 北回太鐵紅線 遠方遙跳 |  |  | B2/D14_A1 | [8 empty] | 北回DS.1530_DTTA | 北回太鐵紅線(1530) 遠方遙跳 | OTHER | [5 empty] | 304 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | DTTA |  |  | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0133 |  |  | 1-10-05 |  |  | MCC1A | DTTA | 1540 北回太鐵白線 遠方遙跳 |  |  | B2/D14_A1 | [8 empty] | 北回DS.1540_DTTA | 北回太鐵白線(1540) 遠方遙跳 | OTHER | [5 empty] | 305 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ25 | 回25線(JJ25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/JJ25/T1 |  |  | 0178 |  | 0023 | 1-16-02 |  | 1-17 | JJ25 | 52AS | F-5(JJ25)回25線 CB |  | aaib | B2/D14_D1 | [8 empty] | 北回DS.JJ25_CB | JJ25(11KV回25線) CB | FEEDER | [5 empty] | 306 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0161 |  |  | 1-14-01 |  |  | 210 | SCA | #1SC(210) 相間及接地電驛(SCA) |  |  | B3/D14_A1 | [8 empty] | 北回DS.210_SCA | 11KV #1SC 51,51N RY | SC | [5 empty] | 307 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0162 |  |  | 1-14-02 |  |  | 210 | UVA | #1SC(210) 欠壓電驛(UVA) |  |  | B3/D14_A1 | [8 empty] | 北回DS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | [5 empty] | 308 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | 100 | TIE(100) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/1ABus | B/2ABus |  |  | 0181 |  | 0024 | 1-16-05 |  | 1-18 | 100 | 52AS | TIE-1A(100) CB |  | aakb | B3/D14_A1 | [8 empty] | 北回DS.100_CB | 100(TIE) CB | TIE | [5 empty] | 309 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 11 | 11kV | 390 | #1SSTR(390) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0164 |  |  | 1-14-04 |  |  | 390 | PHA | #1SSTR(390) 相間電驛PHA |  |  | B3/D14_A1 | [8 empty] | 北回DS.#1SSTR_51A | #1SSTR 51RY | OTHER | [5 empty] | 310 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | 390 | #1SSTR(390) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0165 |  |  | 1-14-05 |  |  | 390 | GDA | #1SSTR(390) 接地電驛GDA |  |  | B3/D14_A1 | [8 empty] | 北回DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | [5 empty] | 311 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | T/1DTR(B) |  |  | 0069 |  | 0025 | 1-08-05 |  | 1-19 | 320 | 52AS | M-1B(320) CB |  | baca | ELEM/D14_A1 | [8 empty] | 北回DS.320_CB | 320(#1DTR) CB | MTR | [5 empty] | 312 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | JJ21 | 回21線(JJ21) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0167 |  |  | 1-14-07 |  |  | JJ21 | PHA | F-1(JJ21)回21線 相間電驛PHA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ21_PHA | 11KV回21線(JJ21) 相間RY | FEEDER | [5 empty] | 313 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ21 | 回21線(JJ21) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0168 |  |  | 1-15-00 |  |  | JJ21 | GDA | F-1(JJ21)回21線 接地電驛GDA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ21_GDA | 11KV回21線(JJ21) 接地RY | FEEDER | [5 empty] | 314 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | 220 | #2SC(220) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | C/2SC |  |  | 0184 |  | 0026 | 1-17-00 |  | 1-1A | 220 | 52AS | #2SC(220) CB |  | baib | B3/D14_A1 | [8 empty] | 北回DS.220_CB | 220(23KV #2SC) CB | SC | [5 empty] | 315 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | JJ22 | 回22線(JJ22) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0170 |  |  | 1-15-02 |  |  | JJ22 | PHA | F-2(JJ22)回22線 相間電驛PHA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ22_PHA | 11KV回22線(JJ22) 相間RY | FEEDER | [5 empty] | 316 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ22 | 回22線(JJ22) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0171 |  |  | 1-15-03 |  |  | JJ22 | GDA | F-2(JJ22)回22線 接地電驛GDA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ22_GDA | 11KV回22線(JJ22) 接地RY | FEEDER | [5 empty] | 317 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ56 | 回56線(JJ56) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/JJ56/T1 |  |  | 0187 |  | 0027 | 1-17-03 |  | 1-1B | JJ56 | 52AS | F-6(JJ56)回56線 CB |  | badb | B2/D14_D1 | [8 empty] | 北回DS.JJ56_CB | JJ56(23KV回56線) CB | FEEDER | [5 empty] | 318 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | JJ23 | 回23線(JJ23) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0173 |  |  | 1-15-05 |  |  | JJ23 | PHA | F-3(JJ23)回23線 相間電驛PHA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ23_PHA | 11KV回23線(JJ23) 相間RY | FEEDER | [5 empty] | 319 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ23 | 回23線(JJ23) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0174 |  |  | 1-15-06 |  |  | JJ23 | GDA | F-3(JJ23)回23線 接地電驛GDA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ23_GDA | 11KV回23線(JJ23) 接地RY | FEEDER | [5 empty] | 320 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ57 | 回57線(JJ57) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/JJ57/T1 |  |  | 0190 |  | 0028 | 1-17-06 |  | 1-1C | JJ57 | 52AS | F-7(JJ57)回57線 CB |  | baeb | B2/D14_D1 | [8 empty] | 北回DS.JJ57_CB | JJ57(23KV回57線) CB | FEEDER | [5 empty] | 321 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | JJ24 | 回24線(JJ24) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0176 |  |  | 1-16-00 |  |  | JJ24 | PHA | F-4(JJ24)回24線 相間電驛PHA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ24_PHA | 11KV回24線(JJ24) 相間RY | FEEDER | [5 empty] | 322 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ24 | 回24線(JJ24) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0177 |  |  | 1-16-01 |  |  | JJ24 | GDA | F-4(JJ24)回24線 接地電驛GDA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ24_GDA | 11KV回24線(JJ24) 接地RY | FEEDER | [5 empty] | 323 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ58 | 回58線(JJ58) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/JJ58/T1 |  |  | 0193 |  | 0029 | 1-18-01 |  | 1-1D | JJ58 | 52AS | F-8(JJ58)回58線 CB |  | bafb | B2/D14_D1 | [8 empty] | 北回DS.JJ58_CB | JJ58(23KV回58線) CB | FEEDER | [5 empty] | 324 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | JJ25 | 回25線(JJ25) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0179 |  |  | 1-16-03 |  |  | JJ25 | PHA | F-5(JJ25)回25線 相間電驛PHA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ25_PHA | 11KV回25線(JJ25) 相間RY | FEEDER | [5 empty] | 325 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ25 | 回25線(JJ25) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0180 |  |  | 1-16-04 |  |  | JJ25 | GDA | F-5(JJ25)回25線 接地電驛GDA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ25_GDA | 11KV回25線(JJ25) 接地RY | FEEDER | [5 empty] | 326 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ59 | 回59線(JJ59) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/JJ59/T1 |  |  | 0196 |  | 0030 | 1-18-04 |  | 1-1E | JJ59 | 52AS | F-9(JJ59)回59線 CB |  | bagb | B2/D14_D1 | [8 empty] | 北回DS.JJ59_CB | JJ59(23KV回59線) CB | FEEDER | [5 empty] | 327 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | 100 | TIE(100) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0182 |  |  | 1-16-06 |  |  | 100 | PHA | TIE-1A(100) 相間電驛PHA |  |  | B3/D14_A1 | [8 empty] | 北回DS.100_51A | 11KV TIE(100) 51RY | TIE | [5 empty] | 328 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | 100 | TIE(100) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0183 |  |  | 1-16-07 |  |  | 100 | GDA | TIE-1A(100) 接地電驛GDA |  |  | B3/D14_A1 | [8 empty] | 北回DS.100_51NA | 11KV TIE(100) 51N RY | TIE | [5 empty] | 329 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ60 | 回60線(JJ60) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/JJ60/T1 |  |  | 0199 |  | 0031 | 1-18-07 |  | 1-1F | JJ60 | 52AS | F-10(JJ60)回60線 CB |  | bahb | B2/D14_D1 | [8 empty] | 北回DS.JJ60_CB | JJ60(23KV回60線) CB | FEEDER | [5 empty] | 330 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | 220 | #2SC(220) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0185 |  |  | 1-17-01 |  |  | 220 | SCA | #2SC(220) 相間及接地電驛(SCA) |  |  | B3/D14_A1 | [8 empty] | 北回DS.220_SCA | 23KV #2SC 51,51N RY | SC | [5 empty] | 331 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | 220 | #2SC(220) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0186 |  |  | 1-17-02 |  |  | 220 | UVA | #2SC(220) 欠壓電驛(UVA) |  |  | B3/D14_A1 | [8 empty] | 北回DS.220_UVA | 23KV #2SC 27RY(欠壓) | SC | [5 empty] | 332 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | 200 | TIE(200) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/1BBus | B/2BBus |  |  | 0202 |  | 0032 | 1-19-02 |  | 1-20 | 200 | 52AS | TIE-1B(200) CB |  | bajb | B3/D14_A1 | [8 empty] | 北回DS.200_CB | 200(TIE) CB | TIE | [5 empty] | 333 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D14 | 北回DS | 22 | 22kV | JJ56 | 回56線(JJ56) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0188 |  |  | 1-17-04 |  |  | JJ56 | PHA | F-6(JJ56)回56線 相間電驛PHA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ56_PHA | 23KV回56線(JJ56) 相間RY | FEEDER | [5 empty] | 334 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ56 | 回56線(JJ56) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0189 |  |  | 1-17-05 |  |  | JJ56 | GDA | F-6(JJ56)回56線 接地電驛GDA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ56_GDA | 23KV回56線(JJ56) 接地RY | FEEDER | [5 empty] | 335 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | T/2DTR(A) |  |  | 0079 |  | 0033 | 1-09-07 |  | 1-21 | 330 | 52AS | M-2A(330) CB |  | abga | ELEM/D14_A1 | [8 empty] | 北回DS.330_CB | 330(#2DTR) CB | MTR | [5 empty] | 336 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | JJ57 | 回57線(JJ57) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0191 |  |  | 1-17-07 |  |  | JJ57 | PHA | F-7(JJ57)回57線 相間電驛PHA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ57_PHA | 23KV回57線(JJ57) 相間RY | FEEDER | [5 empty] | 337 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ57 | 回57線(JJ57) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0192 |  |  | 1-18-00 |  |  | JJ57 | GDA | F-7(JJ57)回57線 接地電驛GDA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ57_GDA | 23KV回57線(JJ57) 接地RY | FEEDER | [5 empty] | 338 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | 230 | #3SC(230) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | A/LBS230^C/3SC(A) |  |  | 0205 |  | 0034 | 1-19-05 |  | 1-22 | 230 | 52AS | #3SC(230)(230) CB |  | abfb | B3/D14_A1 | [8 empty] | 北回DS.230_CB | 230(11KV #3SC) CB | SC | [5 empty] | 339 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | JJ58 | 回58線(JJ58) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0194 |  |  | 1-18-02 |  |  | JJ58 | PHA | F-8(JJ58)回58線 相間電驛PHA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ58_PHA | 23KV回58線(JJ58) 相間RY | FEEDER | [5 empty] | 340 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ58 | 回58線(JJ58) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0195 |  |  | 1-18-03 |  |  | JJ58 | GDA | F-8(JJ58)回58線 接地電驛GDA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ58_GDA | 23KV回58線(JJ58) 接地RY | FEEDER | [5 empty] | 341 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ31 | 回31線(JJ31) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/JJ31/T1 |  |  | 0208 |  | 0035 | 1-1A-00 |  | 1-23 | JJ31 | 52AS | F11-(JJ31)回31線 CB |  | abab | B2/D14_D1 | [8 empty] | 北回DS.JJ31_CB | JJ31(11KV回31線) CB | FEEDER | [5 empty] | 342 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | JJ59 | 回59線(JJ59) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0197 |  |  | 1-18-05 |  |  | JJ59 | PHA | F-9(JJ59)回59線 相間電驛PHA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ59_PHA | 23KV回59線(JJ59) 相間RY | FEEDER | [5 empty] | 343 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ59 | 回59線(JJ59) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0198 |  |  | 1-18-06 |  |  | JJ59 | GDA | F-9(JJ59)回59線 接地電驛GDA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ59_GDA | 23KV回59線(JJ59) 接地RY | FEEDER | [5 empty] | 344 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ32 | 回32線(JJ32) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/JJ32/T1 |  |  | 0211 |  | 0036 | 1-1A-03 |  | 1-24 | JJ32 | 52AS | F12-(JJ32)回32線 CB |  | abbb | B2/D14_D1 | [8 empty] | 北回DS.JJ32_CB | JJ32(11KV回32線) CB | FEEDER | [5 empty] | 345 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | JJ60 | 回60線(JJ60) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0200 |  |  | 1-19-00 |  |  | JJ60 | PHA | F-10(JJ60)回60線 相間電驛PHA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ60_PHA | 23KV回60線(JJ60) 相間RY | FEEDER | [5 empty] | 346 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ60 | 回60線(JJ60) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0201 |  |  | 1-19-01 |  |  | JJ60 | GDA | F-10(JJ60)回60線 接地電驛GDA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ60_GDA | 23KV回60線(JJ60) 接地RY | FEEDER | [5 empty] | 347 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ33 | 回33線(JJ33) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/JJ33/T1 |  |  | 0214 |  | 0037 | 1-1A-06 |  | 1-25 | JJ33 | 52AS | F13-(JJ33)回33線 CB |  | abcb | B2/D14_D1 | [8 empty] | 北回DS.JJ33_CB | JJ33(11KV回33線) CB | FEEDER | [5 empty] | 348 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | 200 | TIE(200) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0203 |  |  | 1-19-03 |  |  | 200 | PHA | TIE-1B(200) 相間電驛PHA |  |  | B3/D14_A1 | [8 empty] | 北回DS.200_51A | 23KV TIE(200) 51RY | TIE | [5 empty] | 349 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | 200 | TIE(200) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0204 |  |  | 1-19-04 |  |  | 200 | GDA | TIE-1B(200) 接地電驛GDA |  |  | B3/D14_A1 | [8 empty] | 北回DS.200_51NA | 23KV TIE(200) 51N RY | TIE | [5 empty] | 350 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ34 | 回34線(JJ34) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/JJ34/T1 |  |  | 0217 |  | 0038 | 1-1B-01 |  | 1-26 | JJ34 | 52AS | F14-(JJ34)回34線 CB |  | abdb | B2/D14_D1 | [8 empty] | 北回DS.JJ34_CB | JJ34(11KV回34線) CB | FEEDER | [5 empty] | 351 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | 230 | #3SC(230) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0206 |  |  | 1-19-06 |  |  | 230 | SCA | #3SC(230)(230) 相間及接地電驛(SCA) |  |  | B3/D14_A1 | [8 empty] | 北回DS.230_SCA | 11KV #3SC 51,51N RY | SC | [5 empty] | 352 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | 230 | #3SC(230) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0207 |  |  | 1-19-07 |  |  | 230 | UVA | #3SC(230)(230) 欠壓電驛(UVA) |  |  | B3/D14_A1 | [8 empty] | 北回DS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | [5 empty] | 353 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ35 | 回35線(JJ35) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/JJ35/T1 |  |  | 0220 |  | 0039 | 1-1B-04 |  | 1-27 | JJ35 | 52AS | F15-(JJ35)回35線 CB |  | abeb | B2/D14_D1 | [8 empty] | 北回DS.JJ35_CB | JJ35(11KV回35線) CB | FEEDER | [5 empty] | 354 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | JJ31 | 回31線(JJ31) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0209 |  |  | 1-1A-01 |  |  | JJ31 | PHA | F11-(JJ31)回31線 相間電驛PHA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ31_PHA | 11KV回31線(JJ31) 相間RY | FEEDER | [5 empty] | 355 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ31 | 回31線(JJ31) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0210 |  |  | 1-1A-02 |  |  | JJ31 | GDA | F11-(JJ31)回31線 接地電驛GDA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ31_GDA | 11KV回31線(JJ31) 接地RY | FEEDER | [5 empty] | 356 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | T/2DTR(B) |  |  | 0082 |  | 0040 | 1-0A-02 |  | 1-28 | 340 | 52AS | M-2B(340)(340) CB |  | bbga | ELEM/D14_A1 | [8 empty] | 北回DS.340_CB | 340(#2DTR) CB | MTR | [5 empty] | 357 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | JJ32 | 回32線(JJ32) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0212 |  |  | 1-1A-04 |  |  | JJ32 | PHA | F12-(JJ32)回32線 相間電驛PHA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ32_PHA | 11KV回32線(JJ32) 相間RY | FEEDER | [5 empty] | 358 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ32 | 回32線(JJ32) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0213 |  |  | 1-1A-05 |  |  | JJ32 | GDA | F12-(JJ32)回32線 接地電驛GDA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ32_GDA | 11KV回32線(JJ32) 接地RY | FEEDER | [5 empty] | 359 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | 240 | #4SC(240) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | C/4SC |  |  | 0223 |  | 0041 | 1-1B-07 |  | 1-29 | 240 | 52AS | #4SC(240) CB |  | bbfb | B3/D14_A1 | [8 empty] | 北回DS.240_CB | 240(23KV #4SC) CB | SC | [5 empty] | 360 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | JJ33 | 回33線(JJ33) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0215 |  |  | 1-1A-07 |  |  | JJ33 | PHA | F13-(JJ33)回33線 相間電驛PHA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ33_PHA | 11KV回33線(JJ33) 相間RY | FEEDER | [5 empty] | 361 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ33 | 回33線(JJ33) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0216 |  |  | 1-1B-00 |  |  | JJ33 | GDA | F13-(JJ33)回33線 接地電驛GDA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ33_GDA | 11KV回33線(JJ33) 接地RY | FEEDER | [5 empty] | 362 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | 490 | #2SSTR(490) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | T/2SSTR |  |  | 0226 |  | 0042 | 1-1C-02 |  | 1-2A | 490 | 52AS | #2SSTR(490) CB |  | bbhb | B3/D14_A1 | [8 empty] | 北回DS.490_CB | 490(#2SSTR) CB | OTHER | [5 empty] | 363 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | JJ34 | 回34線(JJ34) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0218 |  |  | 1-1B-02 |  |  | JJ34 | PHA | F14-(JJ34)回34線 相間電驛PHA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ34_PHA | 11KV回34線(JJ34) 相間RY | FEEDER | [5 empty] | 364 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ34 | 回34線(JJ34) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0219 |  |  | 1-1B-03 |  |  | JJ34 | GDA | F14-(JJ34)回34線 接地電驛GDA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ34_GDA | 11KV回34線(JJ34) 接地RY | FEEDER | [5 empty] | 365 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ66 | 回66線(JJ66) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/JJ66/T1 |  |  | 0229 |  | 0043 | 1-1C-05 |  | 1-2B | JJ66 | 52AS | F-16(JJ66)回66線 CB |  | bbab | B2/D14_D1 | [8 empty] | 北回DS.JJ66_CB | JJ66(23KV回66線) CB | FEEDER | [5 empty] | 366 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | JJ35 | 回35線(JJ35) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0221 |  |  | 1-1B-05 |  |  | JJ35 | PHA | F15-(JJ35)回35線 相間電驛PHA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ35_PHA | 11KV回35線(JJ35) 相間RY | FEEDER | [5 empty] | 367 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ35 | 回35線(JJ35) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0222 |  |  | 1-1B-06 |  |  | JJ35 | GDA | F15-(JJ35)回35線 接地電驛GDA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ35_GDA | 11KV回35線(JJ35) 接地RY | FEEDER | [5 empty] | 368 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ67 | 回67線(JJ67) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/JJ67/T1 |  |  | 0232 |  | 0044 | 1-1D-00 |  | 1-2C | JJ67 | 52AS | F-17(JJ67)回67線 CB |  | bbbb | B2/D14_D1 | [8 empty] | 北回DS.JJ67_CB | JJ67(23KV回67線) CB | FEEDER | [5 empty] | 369 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | 240 | #4SC(240) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0224 |  |  | 1-1C-00 |  |  | 240 | SCA | #4SC(240) 相間及接地電驛(SCA) |  |  | B3/D14_A1 | [8 empty] | 北回DS.240_SCA | 23KV #4SC 51,51N RY | SC | [5 empty] | 370 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | 240 | #4SC(240) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0225 |  |  | 1-1C-01 |  |  | 240 | UVA | #4SC(240) 欠壓電驛(UVA) |  |  | B3/D14_A1 | [8 empty] | 北回DS.240_UVA | 23KV #4SC 27RY(欠壓) | SC | [5 empty] | 371 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ68 | 回68線(JJ68) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/JJ68/T1 |  |  | 0235 |  | 0045 | 1-1D-03 |  | 1-2D | JJ68 | 52AS | F-18(JJ68)回68線 CB |  | bbcb | B2/D14_D1 | [8 empty] | 北回DS.JJ68_CB | JJ68(23KV回68線) CB | FEEDER | [5 empty] | 372 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | 490 | #2SSTR(490) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0227 |  |  | 1-1C-03 |  |  | 490 | PHA | #2SSTR(490) 相間電驛PHA |  |  | B3/D14_A1 | [8 empty] | 北回DS.#2SSTR_51A | #2SSTR 51RY | OTHER | [5 empty] | 373 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | 490 | #2SSTR(490) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0228 |  |  | 1-1C-04 |  |  | 490 | GDA | #2SSTR(490) 接地電驛GDA |  |  | B3/D14_A1 | [8 empty] | 北回DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | [5 empty] | 374 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ69 | 回69線(JJ69) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/JJ69/T1 |  |  | 0238 |  | 0046 | 1-1D-06 |  | 1-2E | JJ69 | 52AS | F-19(JJ69)回69線 CB |  | bbdb | B2/D14_D1 | [8 empty] | 北回DS.JJ69_CB | JJ69(23KV回69線) CB | FEEDER | [5 empty] | 375 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | JJ66 | 回66線(JJ66) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0230 |  |  | 1-1C-06 |  |  | JJ66 | PHA | F-16(JJ66)回66線 相間電驛PHA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ66_PHA | 23KV回66線(JJ66) 相間RY | FEEDER | [5 empty] | 376 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ66 | 回66線(JJ66) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0231 |  |  | 1-1C-07 |  |  | JJ66 | GDA | F-16(JJ66)回66線 接地電驛GDA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ66_GDA | 23KV回66線(JJ66) 接地RY | FEEDER | [5 empty] | 377 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ70 | 回70線(JJ70) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/JJ70/T1 |  |  | 0241 |  | 0047 | 1-1E-01 |  | 1-2F | JJ26 | 52AS | F-20(JJ70)回70線 CB |  | bbeb | B2/D14_D1 | [8 empty] | 北回DS.JJ70_CB | JJ70(23KV回70線) CB | FEEDER | [5 empty] | 378 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | JJ67 | 回67線(JJ67) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0233 |  |  | 1-1D-01 |  |  | JJ67 | PHA | F-17(JJ67)回67線 相間電驛PHA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ67_PHA | 23KV回67線(JJ67) 相間RY | FEEDER | [5 empty] | 379 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ67 | 回67線(JJ67) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0234 |  |  | 1-1D-02 |  |  | JJ67 | GDA | F-17(JJ67)回67線 接地電驛GDA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ67_GDA | 23KV回67線(JJ67) 接地RY | FEEDER | [5 empty] | 380 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛～北回一路(1510) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0770 |  | 0069 | 2-38-02 |  | 1-45 | 100 | ES(ON) | TIE-1A(100) ES-AS |  |  | B2/D14_A1 | [8 empty] | 北回DS.1510_87UL | 仁愛北回一路(1510) 87RY U/L | LINE161 | [5 empty] | 381 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D14 | 北回DS | 22 | 22kV | JJ68 | 回68線(JJ68) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0236 |  |  | 1-1D-04 |  |  | JJ68 | PHA | F-18(JJ68)回68線 相間電驛PHA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ68_PHA | 23KV回68線(JJ68) 相間RY | FEEDER | [5 empty] | 382 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ68 | 回68線(JJ68) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0237 |  |  | 1-1D-05 |  |  | JJ68 | GDA | F-18(JJ68)回68線 接地電驛GDA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ68_GDA | 23KV回68線(JJ68) 接地RY | FEEDER | [5 empty] | 383 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛～北回一路(1510) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0772 |  | 0070 | 2-38-04 |  | 1-46 | 320 | DS(ON) | M-1B(320) DS-AS |  |  | B2/D14_A1 | [8 empty] | 北回DS.1510_79UL | 仁愛北回一路(1510) 79RY U/L | LINE161 | [5 empty] | 384 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D14 | 北回DS | 22 | 22kV | JJ69 | 回69線(JJ69) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0239 |  |  | 1-1D-07 |  |  | JJ69 | PHA | F-19(JJ69)回69線 相間電驛PHA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ69_PHA | 23KV回69線(JJ69) 相間RY | FEEDER | [5 empty] | 385 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ69 | 回69線(JJ69) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0240 |  |  | 1-1E-00 |  |  | JJ69 | GDA | F-19(JJ69)回69線 接地電驛GDA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ69_GDA | 23KV回69線(JJ69) 接地RY | FEEDER | [5 empty] | 386 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛～北回二路(1520) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0773 |  | 0071 | 2-38-05 |  | 1-47 | 320 | DS(OFF) | M-1B(320) DS-BS |  |  | B2/D14_A1 | [8 empty] | 北回DS.1520_87UL | 仁愛北回二路(1520) 87RY U/L | LINE161 | [5 empty] | 387 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D14 | 北回DS | 22 | 22kV | JJ70 | 回70線(JJ70) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0242 |  |  | 1-1E-02 |  |  | JJ26 | PHA | F-20(JJ70)回70線 相間電驛PHA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ70_PHA | 23KV回70線(JJ70) 相間RY | FEEDER | [5 empty] | 388 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ70 | 回70線(JJ70) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0243 |  |  | 1-1E-03 |  |  | JJ26 | GDA | F-20(JJ70)回70線 接地電驛GDA |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ70_GDA | 23KV回70線(JJ70) 接地RY | FEEDER | [5 empty] | 389 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛～北回二路(1520) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0775 |  | 0072 | 2-38-07 |  | 1-48 | 320 | ES(OFF) | M-1B(320) ES-BS |  |  | B2/D14_A1 | [8 empty] | 北回DS.1520_79UL | 仁愛北回二路(1520) 79RY U/L | LINE161 | [5 empty] | 390 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D14 | 北回DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0776 |  | 0073 | 2-38-08 |  | 1-49 | JJ56 | DS(ON) | F-6(JJ56)回56線 DS-AS |  |  | B2/D14_A1 | [8 empty] | 北回DS.1530_87UL | 北回太鐵紅線(1530) 87RY U/L | LINE161 | [5 empty] | 391 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D14 | 北回DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0778 |  | 0074 | 2-38-10 |  | 1-4A | JJ56 | ES(ON) | F-6(JJ56)回56線 ES-AS |  |  | B2/D14_A1 | [8 empty] | 北回DS.1530_79UL | 北回太鐵紅線(1530) 79RY U/L | LINE161 | [5 empty] | 392 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D14 | 北回DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0779 |  | 0075 | 2-38-11 |  | 1-4B | JJ56 | ES(OFF) | F-6(JJ56)回56線 ES-BS |  |  | B2/D14_A1 | [8 empty] | 北回DS.1540_87UL | 北回太鐵白線(1540) 87RY U/L | LINE161 | [5 empty] | 393 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D14 | 北回DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0781 |  | 0076 | 2-38-13 |  | 1-4C | JJ57 | DS(OFF) | F-7(JJ57)回57線 DS-BS |  |  | B2/D14_A1 | [8 empty] | 北回DS.1540_79UL | 北回太鐵白線(1540) 79RY U/L | LINE161 | [5 empty] | 394 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D14 | 北回DS |  |  | 1DTR(A) | #1DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0806 |  | 0091 | 2-3A-06 |  | 1-5B | 330 | ES(ON) | M-2A(330) ES-AS |  |  | B1/D14_A1 | [16 empty] | 395 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS |  |  | 1DTR(A) | #1DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0025 |  | 0092 | 1-99 |  | 1-5C | MCC1B |  | 1750 #1DTR ULTC TAP指示量1A | TAP_-8.5_8.5(0_2000) |  | B1/D14_A1 | [8 empty] | 北回DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | [5 empty] | 396 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D14 | 北回DS |  |  | 1DTR(B) | #1DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0807 |  | 0093 | 2-3A-07 |  | 1-5D | 330 | ES(OFF) | M-2A(330) ES-BS |  |  | B1/D14_A1 | [16 empty] | 397 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS |  |  | 1DTR(B) | #1DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0026 |  | 0094 | 1-9A |  | 1-5E | MCC1B |  | 1750 #1DTR ULTC TAP指示量1B | TAP_-8.5_8.5(0_2000) |  | B1/D14_A1 | [8 empty] | 北回DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | [5 empty] | 398 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D14 | 北回DS |  |  | 2DTR(A) | #2DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0813 |  | 0095 | 2-3A-13 |  | 1-5F | JJ32 | DS(OFF) | F12-(JJ32)回32線 DS-BS |  |  | B1/D14_A1 | [16 empty] | 399 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS |  |  | 2DTR(A) | #2DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0030 |  | 0096 | 1-9E |  | 1-60 | MCC1B |  | 1760 #2DTR ULTC TAP指示量1A | TAP_-8.5_8.5(0_2000) |  | B1/D14_A1 | [8 empty] | 北回DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | [5 empty] | 400 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D14 | 北回DS | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0800 |  |  | 2-3A-00 |  |  | 200 | DS(ON) | TIE-1B(200) DS-AS |  |  | B2/D14_A1 | [16 empty] | 401 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS |  |  | 2DTR(B) | #2DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0814 |  | 0097 | 2-3A-14 |  | 1-61 | JJ32 | ES(ON) | F12-(JJ32)回32線 ES-AS |  |  | B1/D14_A1 | [16 empty] | 402 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS |  |  | 2DTR(B) | #2DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0031 |  | 0098 | 1-9F |  | 1-62 | MCC1B |  | 1760 #2DTR ULTC TAP指示量1B | TAP_-8.5_8.5(0_2000) |  | B1/D14_A1 | [8 empty] | 北回DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | [5 empty] | 403 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D14 | 北回DS |  |  | 1DTR | #1DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0803 |  |  | 2-3A-03 |  |  | 200 | ES(OFF) | TIE-1B(200) ES-BS |  |  | B1/D14_A1 | [16 empty] | 404 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS |  |  | 1DTR(A) | #1DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0804 |  |  | 2-3A-04 |  |  | 330 | DS(ON) | M-2A(330) DS-AS |  |  | B1/D14_A1 | [16 empty] | 405 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS |  |  | 1DTR(B) | #1DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0805 |  |  | 2-3A-05 |  |  | 330 | DS(OFF) | M-2A(330) DS-BS |  |  | B1/D14_A1 | [16 empty] | 406 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 161 | 161kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0801 |  | 0101 | 2-3A-01 |  | 1-65 | 200 | DS(OFF) | TIE-1B(200) DS-BS |  |  | B2/D14_A1 | [16 empty] | 407 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 161 | 161kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0802 |  | 0102 | 2-3A-02 |  | 1-66 | 200 | ES(ON) | TIE-1B(200) ES-AS |  |  | B2/D14_A1 | [16 empty] | 408 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS |  |  | 1DTR | #1DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0808 |  |  | 2-3A-08 |  |  | JJ31 | DS(ON) | F11-(JJ31)回31線 DS-AS |  | a | B1/D14_A1 | [16 empty] | 409 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS |  |  | 1DTR | #1DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0809 |  |  | 2-3A-09 |  |  | JJ31 | DS(OFF) | F11-(JJ31)回31線 DS-BS |  |  | B1/D14_A1 | [16 empty] | 410 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS |  |  | 2DTR | #2DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0810 |  |  | 2-3A-10 |  |  | JJ31 | ES(ON) | F11-(JJ31)回31線 ES-AS |  |  | B1/D14_A1 | [16 empty] | 411 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS |  |  | 2DTR(A) | #2DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0811 |  |  | 2-3A-11 |  |  | JJ31 | ES(OFF) | F11-(JJ31)回31線 ES-BS |  |  | B1/D14_A1 | [16 empty] | 412 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS |  |  | 2DTR(B) | #2DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0812 |  |  | 2-3A-12 |  |  | JJ32 | DS(ON) | F12-(JJ32)回32線 DS-AS |  |  | B1/D14_A1 | [16 empty] | 413 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | StaDev | 所內設施 |  | Lights1 | 景觀 |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0864 |  | 0106 | 2-3E-00 |  | 1-6A | 490 | ES(OFF) | #2SSTR(490) DS-BS |  |  | B3/D14_A1 | [16 empty] | 414 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0865 |  | 0108 | 2-3E-01 |  | 1-6C | 490 | ES(OFF) | #2SSTR(490) DS-BS |  |  | B3/D14_A1 | [16 empty] | 415 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS |  |  | 2DTR | #2DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0815 |  |  | 2-3A-15 |  |  | JJ32 | ES(OFF) | F12-(JJ32)回32線 ES-BS |  | a | B1/D14_A1 | [16 empty] | 416 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS |  |  | 2DTR | #2DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0816 |  |  | 2-3B-00 |  |  | JJ33 | DS(ON) | F13-(JJ33)回33線 DS-AS |  |  | B1/D14_A1 | [16 empty] | 417 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛～北回一路(1510) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0831 |  |  | 2-3B-15 |  |  | 230 | ES(OFF) | #3SC(230) ES-BS |  |  | B2/D14_A1 | [16 empty] | 418 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛～北回一路(1510) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0832 |  |  | 2-3C-00 |  |  | 330 | DS(ON) | M-2B(340) DS-AS |  |  | B2/D14_A1 | [16 empty] | 419 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛～北回二路(1520) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0833 |  |  | 2-3C-01 |  |  | 330 | DS(OFF) | M-2B(340) DS-BS |  |  | B2/D14_A1 | [16 empty] | 420 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛～北回二路(1520) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0834 |  |  | 2-3C-02 |  |  | 330 | ES(ON) | M-2B(340) ES-AS |  |  | B2/D14_A1 | [16 empty] | 421 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0835 |  |  | 2-3C-03 |  |  | 330 | ES(OFF) | M-2B(340) ES-BS |  |  | B2/D14_A1 | [16 empty] | 422 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0836 |  |  | 2-3C-04 |  |  | JJ66 | DS(ON) | F-16(JJ66)回66線 DS-AS |  |  | B2/D14_A1 | [16 empty] | 423 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0837 |  |  | 2-3C-05 |  |  | JJ66 | DS(OFF) | F-16(JJ66)回66線 DS-BS |  |  | B2/D14_A1 | [16 empty] | 424 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0838 |  |  | 2-3C-06 |  |  | JJ66 | ES(ON) | F-16(JJ66)回66線 ES-AS |  |  | B2/D14_A1 | [16 empty] | 425 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | StaDev | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0851 |  |  | 2-3D-03 |  |  | JJ69 | ES(OFF) | F-19(JJ69)回69線 ES-BS |  |  | B3/D14_A1 | [16 empty] | 426 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | StaDev | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0852 |  |  | 2-3D-04 |  |  | JJ26 | DS(ON) | F-20(JJ70)回70線 DS-AS |  |  | B3/D14_A1 | [16 empty] | 427 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | StaDev | 所內設施 |  | Water1 | 地下室1/2水位警報 |  | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0853 |  |  | 2-3D-05 |  |  | JJ26 | DS(OFF) | F-20(JJ70)回70線 DS-BS |  |  | B3/D14_A1 | [16 empty] | 428 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | StaDev | 所內設施 |  | Water2 | 地下室頂部水位警報 |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0854 |  |  | 2-3D-06 |  |  | JJ26 | ES(ON) | F-20(JJ70)回70線 ES-AS |  |  | B3/D14_A1 | [16 empty] | 429 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | StaDev | 所內設施 |  | OilLeak1 |  |  | Status | 洩油池水位警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0855 |  |  | 2-3D-07 |  |  | JJ26 | ES(OFF) | F-20(JJ70)回70線 ES-BS |  |  | B3/D14_A1 | [16 empty] | 430 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | StaDev | 所內設施 |  | OilLeak2 |  |  | Status | 洩油池水位警報2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0856 |  |  | 2-3D-08 |  |  | 240 | DS(ON) | $4SC(240) DS-AS |  |  | B3/D14_A1 | [16 empty] | 431 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | StaDev | 所內設施 |  | NFBA |  |  | Status | NFB 跳脫監視 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0857 |  |  | 2-3D-09 |  |  | 240 | DS(OFF) | $4SC(240) DS-BS |  |  | B3/D14_A1 | [16 empty] | 432 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | StaDev | 所內設施 |  | CHG1 | #1,#2故障 |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0858 |  |  | 2-3D-10 |  |  | 240 | ES(ON) | $4SC(240) ES-AS |  |  | B3/D14_A1 | [16 empty] | 433 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0859 |  |  | 2-3D-11 |  |  | 240 | ES(OFF) | $4SC(240) ES-BS |  |  | ELEM/D14_A1 | [16 empty] | 434 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | ComPoint |  |  | OLTC_A |  |  | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0860 |  |  | 2-3D-12 |  |  | 390 | ES(OFF) | #1SSTR(390) DS-BS |  |  | B3/D14_A1 | [16 empty] | 435 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | StaDev | 所內設施 |  | ACB |  |  | Status | ACB | Close/Open | Y | 3 | DI-SP | [6 empty] | 0862 |  |  | 2-3D-14 |  |  | 390 | ES(OFF) | #1SSTR(390) ES-BS |  |  | B3/D14_A1 | [16 empty] | 436 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0863 |  |  | 2-3D-15 |  |  | 390 | ES(OFF) | #1SSTR(390) ES-BS |  |  | ELEM/D14_A1 | [16 empty] | 437 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0866 |  | 0109 | 2-3E-02 |  | 1-6D | 490 | ES(OFF) | #2SSTR(490) ES-BS |  |  | B3/D14_A1 | [16 empty] | 438 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | StaDev | 所內設施 |  | ACBT |  |  | Status | 所內電源ACB TIE | Close/Open | Y | 3 | DI-SP | [6 empty] | 0867 |  | 0110 | 2-3E-03 |  | 1-6E | 490 | ES(OFF) | #2SSTR(490)ES-BS |  |  | B3/D14_A1 | [16 empty] | 439 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛～北回一路(1510) |  | DS1 | 1511 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0896 | 897 | 0111 | 3-38-00 | 3-38-01 | 1-6F | Locate Empty | DS(ON) | F-17 DS-AS |  |  | B2/D14_A1 | [8 empty] | 北回DS.1511_DS | 1511(仁愛北回一路) DS | LINE161 | [5 empty] | 440 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛～北回一路(1510) |  | DS2 | 1512 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0898 | 899 | 0112 | 3-38-02 | 3-38-03 | 1-70 | Locate Empty | ES(ON) | F-17 ES-AS |  |  | B2/D14_A1 | [8 empty] | 北回DS.1512_DS | 1512(仁愛北回一路) DS | LINE161 | [5 empty] | 441 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D14 | 北回DS | 0 |  | StaDev | 所內設施 |  | SCADAA |  |  | Status | LocalSCADA故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0868 |  |  | 2-3E-04 |  |  | Locate Empty | DS(ON) | M-3 DS-AS |  |  | B3/D14_A1 | [16 empty] | 442 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | StaDev | 所內設施 |  | Comm_A | 通訊主機 1或2 |  | Status | 通訊處理單元故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0869 |  |  | 2-3E-05 |  |  | Locate Empty | DS(OFF) | M-3 DS-BS |  |  | B3/D14_A1 | [16 empty] | 443 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | NULL | NULL |  | 2A5Other | 待新增!!__排水泵故障1_涵洞 | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0870 |  |  | 2-3E-06 |  |  | Locate Empty | ES(ON) | M-3 ES-AS |  |  | B1/D14_A1 | [16 empty] | 444 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | StaDev | 所內設施 |  | Fire1 | 受信總機 |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0871 |  |  | 2-3E-07 |  |  | Locate Empty | ES(OFF) | M-3 ES-BS |  |  | B3/D14_A1 | [16 empty] | 445 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | NULL | NULL |  | 3A5Other | 待新增!!__揚水泵警報 | Element | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0872 |  |  | 2-3E-08 |  |  | Locate Empty | DS(ON) | F-11 DS-AS |  |  | B1/D14_A1 | [16 empty] | 446 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | NULL | NULL |  | 4A5Other | 待新增!!__污水泵故障 | Element | Status | 警報等級5動作4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0873 |  |  | 2-3E-09 |  |  | Locate Empty | DS(OFF) | F-11 DS-BS |  |  | B1/D14_A1 | [16 empty] | 447 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 161 | 161kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0874 |  |  | 2-3E-10 |  |  | Locate Empty | ES(ON) | F-11 ES-AS |  |  | B2/D14_A1 | [16 empty] | 448 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 161 | 161kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0875 |  |  | 2-3E-11 |  |  | Locate Empty | ES(OFF) | F-11 ES-BS |  |  | B2/D14_A1 | [16 empty] | 449 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | NULL | NULL |  | 5A5Other | 待新增!!__BPTA | Element | Status | 警報等級5動作5 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0876 |  |  | 2-3E-12 |  |  | Locate Empty | DS(ON) | F-12 DS-AS |  |  | B1/D14_A1 | [16 empty] | 450 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | NULL | NULL |  | 6A5Other | 待新增!!__BPTF | Element | Status | 警報等級5動作6 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0877 |  |  | 2-3E-13 |  |  | Locate Empty | DS(OFF) | F-12 DS-BS |  |  | B1/D14_A1 | [16 empty] | 451 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | StaDev | 所內設施 |  | Burglar1 | 保全 |  | Status | 無人化防盜1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0878 |  |  | 2-3E-14 |  |  | Locate Empty | ES(ON) | F-12 ES-AS |  |  | B3/D14_A1 | [16 empty] | 452 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 22 | 22kV | ComPoint |  |  | FDR_60A |  |  | Status | 11/22kV電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0879 |  |  | 2-3E-15 |  |  | Locate Empty | ES(OFF) | F-12 ES-BS |  |  | B3/D14_A1 | [16 empty] | 453 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 161 | 161kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0880 |  |  | 2-3F-00 |  |  | Locate Empty | DS(ON) | F-13 DS-AS |  |  | B3/D14_A1 | [16 empty] | 454 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 161 | 161kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0881 |  |  | 2-3F-01 |  |  | Locate Empty | DS(OFF) | F-13 DS-BS |  |  | B3/D14_A1 | [16 empty] | 455 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 22 | 22kV | ComPoint |  |  | FDR_CBA |  |  | Status | 11/22kV斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0882 |  |  | 2-3F-02 |  |  | Locate Empty | ES(ON) | F-13 ES-AS |  |  | ELEM/D14_D1 | [16 empty] | 456 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 22 | 22kV | ComPoint |  |  | FDR_CBF |  |  | Status | 11/22kV斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0883 |  |  | 2-3F-03 |  |  | Locate Empty | ES(OFF) | F-13 ES-BS |  |  | ELEM/D14_D1 | [16 empty] | 457 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0884 |  |  | 2-3F-04 |  |  | Locate Empty | DS(ON) | F-14 DS-AS |  |  | B3/D14_A1 | [16 empty] | 458 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0885 |  |  | 2-3F-05 |  |  | Locate Empty | DS(OFF) | F-14 DS-BS |  |  | B3/D14_A1 | [16 empty] | 459 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | NULL | NULL |  | 7A5Other | 待新增!!__緊急發電機運轉 | Element | Status | 警報等級5動作7 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0886 |  |  | 2-3F-06 |  |  | Locate Empty | ES(ON) | F-14 ES-AS |  |  | B1/D14_A1 | [16 empty] | 460 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 161 | 161kV | ComPoint | BUS |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0887 |  |  | 2-3F-07 |  |  | Locate Empty | ES(OFF) | F-14 ES-BS |  |  | B2/D14_A1 | [16 empty] | 461 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | StaDev | 所內設施 |  | R_Temp1 | 通訊室或控制室 |  | Status | 溫度警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0888 |  |  | 2-3F-08 |  |  | Locate Empty | DS(ON) | F-15 DS-AS |  |  | B3/D14_A1 | [16 empty] | 462 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | StaDev | 所內設施 |  | UPSA |  |  | Status | UPS故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0889 |  |  | 2-3F-09 |  |  | Locate Empty | DS(OFF) | F-15 DS-BS |  |  | B3/D14_A1 | [16 empty] | 463 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | StaDev | 所內設施 |  | Water3 | 涵洞中水位警報 |  | Status | 地下室淹水3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0893 |  |  | 2-3F-13 |  |  | Locate Empty | DS(OFF) | F-16 DS-BS |  |  | B3/D14_A1 | [16 empty] | 464 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | StaDev | 所內設施 |  | Water4 | 涵洞高水位警報 |  | Status | 地下室淹水4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0894 |  |  | 2-3F-14 |  |  | Locate Empty | ES(ON) | F-16 ES-AS |  |  | B3/D14_A1 | [16 empty] | 465 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | StaDev | 所內設施 |  | Door1 | 建築物大門 |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0895 |  |  | 2-3F-15 |  |  | Locate Empty | ES(OFF) | F-16 ES-BS |  |  | B3/D14_A1 | [16 empty] | 466 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛～北回一路(1510) |  | DS3 | 1513 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0900 | 901 | 0113 | 3-38-04 | 3-38-05 | 1-71 | Locate Empty | DS(ON) | F-18 DS-AS |  |  | B2/D14_A1 | [8 empty] | 北回DS.1513_DS | 1513(仁愛北回一路) DS | LINE161 | [5 empty] | 467 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛～北回一路(1510) |  | ES3 | 1513E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0902 |  | 0114 | 3-38-06 |  | 1-72 | Locate Empty | ES(ON) | F-18 ES-AS |  |  | B2/D14_A1 | [16 empty] | 468 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛～北回二路(1520) |  | DS1 | 1521 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0904 | 905 | 0115 | 3-38-08 | 3-38-09 | 1-73 | Locate Empty | DS(ON) | #5SC DS-AS |  |  | B2/D14_A1 | [8 empty] | 北回DS.1521_DS | 1521(仁愛北回二路) DS | LINE161 | [5 empty] | 469 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛～北回二路(1520) |  | DS2 | 1522 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0906 | 907 | 0116 | 3-38-10 | 3-38-11 | 1-74 | Locate Empty | ES(ON) | #5SC ES-AS |  |  | B2/D14_A1 | [8 empty] | 北回DS.1522_DS | 1522(仁愛北回二路) DS | LINE161 | [5 empty] | 470 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛～北回二路(1520) |  | DS3 | 1523 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0908 | 909 | 0117 | 3-38-12 | 3-38-13 | 1-75 | Locate Empty | DS(ON) | TIE-3A DS-AS |  |  | B2/D14_A1 | [8 empty] | 北回DS.1523_DS | 1523(仁愛北回二路) DS | LINE161 | [5 empty] | 471 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛～北回二路(1520) |  | ES3 | 1523E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0910 |  | 0118 | 3-38-14 |  | 1-76 | Locate Empty | ES(ON) | TIE-3A ES-AS |  |  | B2/D14_A1 | [16 empty] | 472 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | DS1 | 1531 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0912 | 913 | 0119 | 3-39-00 | 3-39-01 | 1-77 | Locate Empty | DS(ON) | M-4 DS-AS |  |  | B2/D14_A1 | [8 empty] | 北回DS.1531_DS | 1531(北回太鐵紅線) DS | LINE161 | [5 empty] | 473 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D14 | 北回DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | DS2 | 1532 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0914 | 915 | 0120 | 3-39-02 | 3-39-03 | 1-78 | Locate Empty | ES(ON) | M-4 ES-AS |  |  | B2/D14_A1 | [8 empty] | 北回DS.1532_DS | 1532(北回太鐵紅線) DS | LINE161 | [5 empty] | 474 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D14 | 北回DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | DS3 | 1533 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0916 | 917 | 0121 | 3-39-04 | 3-39-05 | 1-79 | Locate Empty | DS(ON) | F-37 DS-AS |  |  | B2/D14_A1 | [8 empty] | 北回DS.1533_DS | 1533(北回太鐵紅線) DS | LINE161 | [5 empty] | 475 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D14 | 北回DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | ES3 | 1533E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0918 |  | 0122 | 3-39-06 |  | 1-7A | Locate Empty | ES(ON) | F-37 ES-AS |  |  | B2/D14_A1 | [16 empty] | 476 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | DS1 | 1541 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0920 | 921 | 0123 | 3-39-08 | 3-39-09 | 1-7B | Locate Empty | DS(ON) | F-38 DS-AS |  |  | B2/D14_A1 | [8 empty] | 北回DS.1541_DS | 1541(北回太鐵白線) DS | LINE161 | [5 empty] | 477 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D14 | 北回DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | DS2 | 1542 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0922 | 923 | 0124 | 3-39-10 | 3-39-11 | 1-7C | Locate Empty | ES(ON) | F-38 ES-AS |  |  | B2/D14_A1 | [8 empty] | 北回DS.1542_DS | 1542(北回太鐵白線) DS | LINE161 | [5 empty] | 478 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D14 | 北回DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | DS3 | 1543 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0924 | 925 | 0125 | 3-39-12 | 3-39-13 | 1-7D | Locate Empty | DS(ON) | F-39 DS-AS |  |  | B2/D14_A1 | [8 empty] | 北回DS.1543_DS | 1543(北回太鐵白線) DS | LINE161 | [5 empty] | 479 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D14 | 北回DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | ES3 | 1543E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0926 |  | 0126 | 3-39-14 |  | 1-7E | Locate Empty | ES(ON) | F-39 ES-AS |  |  | B2/D14_A1 | [16 empty] | 480 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0976 | 977 | 0151 |  |  | 2-17 | MCC2B | DS O/C | 1501 AS |  |  | B2/D14_A1 | [8 empty] | 北回DS.1501_DS | 1501(TIE) DS | TIE |  | CDC_Mon1_NULL,CDC_Mon1_EMPTY,CDC_Mon2_EMPTY |  |  |  | 481 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D14 | 北回DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0978 | 979 | 0152 |  |  | 2-18 | MCC2B | DS O/C | 1502 AS |  |  | B2/D14_A1 | [8 empty] | 北回DS.1502_DS | 1502(TIE) DS | TIE |  | CDC_Mon1_NULL,CDC_Mon1_EMPTY,CDC_Mon2_EMPTY |  |  |  | 482 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D14 | 北回DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0980 | 981 | 0153 |  |  | 2-19 | MCC2B | DS O/C | 1751 AS |  |  | B2/D14_A1 | [8 empty] | 北回DS.1751_DS | 1751(#1DTR) DS | MTR |  | CDC_Mon1_NULL,CDC_Mon1_EMPTY,CDC_Mon2_EMPTY |  |  |  | 483 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D14 | 北回DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0982 | 983 | 0154 |  |  | 2-1A | MCC2B | DS O/C | 1752 AS |  |  | B2/D14_A1 | [8 empty] | 北回DS.1752_DS | 1752(#1DTR) DS | MTR |  | CDC_Mon1_NULL,CDC_Mon1_EMPTY,CDC_Mon2_EMPTY |  |  |  | 484 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D14 | 北回DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0984 | 985 | 0155 |  |  | 2-1B | MCC2B | DS O/C | 1761 AS |  |  | B2/D14_A1 | [8 empty] | 北回DS.1761_DS | 1761(#2DTR) DS | MTR |  | CDC_Mon1_NULL,CDC_Mon1_EMPTY,CDC_Mon2_EMPTY |  |  |  | 485 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D14 | 北回DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0986 | 987 | 0156 |  |  | 2-1C | MCC2B | DS O/C | 1762 AS |  |  | B2/D14_A1 | [8 empty] | 北回DS.1762_DS | 1762(#2DTR) DS | MTR |  | CDC_Mon1_NULL,CDC_Mon1_EMPTY,CDC_Mon2_EMPTY |  |  |  | 486 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D14 | 北回DS | 11 | 11kV | JJ21 | 回21線(JJ21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1024 |  | 0214 |  |  | 2-56 | JJ21 | 79S U/L | F-1(JJ21)回21線 79S |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ21_79UL | 11KV回21線(JJ21) 79RY U/L | FEEDER |  | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 487 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D14 | 北回DS | 11 | 11kV | JJ21 | 回21線(JJ21) |  | 51_51NUL |  |  | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1025 |  | 0215 |  |  | 2-57 | JJ21 | 51NS U/L | F-1(JJ21)回21線 51NS |  |  | B2/D14_D1 | [12 empty] | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 488 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 11 | 11kV | JJ22 | 回22線(JJ22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1026 |  | 0216 |  |  | 2-58 | JJ22 | 79S U/L | F-2(JJ22)回22線 79S |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ22_79UL | 11KV回22線(JJ22) 79RY U/L | FEEDER |  | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 489 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D14 | 北回DS | 11 | 11kV | JJ22 | 回22線(JJ22) |  | 51_51NUL |  |  | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1027 |  | 0217 |  |  | 2-59 | JJ22 | 51NS U/L | F-2(JJ22)回22線 51NS |  |  | B2/D14_D1 | [12 empty] | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 490 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 11 | 11kV | JJ23 | 回23線(JJ23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1028 |  | 0218 |  |  | 2-5A | JJ23 | 79S U/L | F-3(JJ23)回23線 79S |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ23_79UL | 11KV回23線(JJ23) 79RY U/L | FEEDER |  | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 491 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D14 | 北回DS | 11 | 11kV | JJ23 | 回23線(JJ23) |  | 51_51NUL |  |  | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1029 |  | 0219 |  |  | 2-5B | JJ23 | 51NS U/L | F-3(JJ23)回23線 51NS |  |  | B2/D14_D1 | [12 empty] | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 492 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 11 | 11kV | JJ24 | 回24線(JJ24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1030 |  | 0220 |  |  | 2-5C | JJ24 | 79S U/L | F-4(JJ24)回24線 79S |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ24_79UL | 11KV回24線(JJ24) 79RY U/L | FEEDER |  | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 493 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D14 | 北回DS | 11 | 11kV | JJ24 | 回24線(JJ24) |  | 51_51NUL |  |  | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1031 |  | 0221 |  |  | 2-5D | JJ24 | 51NS U/L | F-4(JJ24)回24線 51NS |  |  | B2/D14_D1 | [12 empty] | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 494 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 11 | 11kV | JJ25 | 回25線(JJ25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1032 |  | 0222 |  |  | 2-5E | JJ25 | 79S U/L | F-5(JJ25)回25線 79S |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ25_79UL | 11KV回25線(JJ25) 79RY U/L | FEEDER |  | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 495 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D14 | 北回DS | 11 | 11kV | JJ25 | 回25線(JJ25) |  | 51_51NUL |  |  | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1033 |  | 0223 |  |  | 2-5F | JJ25 | 51NS U/L | F-5(JJ25)回25線 51NS |  |  | B2/D14_D1 | [12 empty] | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 496 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 22 | 22kV | JJ56 | 回56線(JJ56) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1034 |  | 0224 |  |  | 2-60 | JJ56 | 79S U/L | F-6(JJ56)回56線 79S |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ56_79UL | 23KV回56線(JJ56) 79RY U/L | FEEDER |  | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 497 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D14 | 北回DS | 22 | 22kV | JJ56 | 回56線(JJ56) |  | 51_51NUL |  |  | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1035 |  | 0225 |  |  | 2-61 | JJ56 | 51NS U/L | F-6(JJ56)回56線 51NS |  |  | B2/D14_D1 | [12 empty] | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 498 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 22 | 22kV | JJ57 | 回57線(JJ57) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1036 |  | 0226 |  |  | 2-62 | JJ57 | 79S U/L | F-7(JJ57)回57線 79S |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ57_79UL | 23KV回57線(JJ57) 79RY U/L | FEEDER |  | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 499 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D14 | 北回DS | 22 | 22kV | JJ57 | 回57線(JJ57) |  | 51_51NUL |  |  | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1037 |  | 0227 |  |  | 2-63 | JJ57 | 51NS U/L | F-7(JJ57)回57線 51NS |  |  | B2/D14_D1 | [12 empty] | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 500 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 22 | 22kV | JJ58 | 回58線(JJ58) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1038 |  | 0228 |  |  | 2-64 | JJ58 | 79S U/L | F-8(JJ58)回58線 79S |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ58_79UL | 23KV回58線(JJ58) 79RY U/L | FEEDER |  | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 501 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D14 | 北回DS | 22 | 22kV | JJ58 | 回58線(JJ58) |  | 51_51NUL |  |  | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1039 |  | 0229 |  |  | 2-65 | JJ58 | 51NS U/L | F-8(JJ58)回58線 51NS |  |  | B2/D14_D1 | [12 empty] | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 502 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 22 | 22kV | JJ59 | 回59線(JJ59) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1040 |  | 0230 |  |  | 2-66 | JJ59 | 79S U/L | F-9(JJ59)回59線 79S |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ59_79UL | 23KV回59線(JJ59) 79RY U/L | FEEDER |  | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 503 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D14 | 北回DS | 22 | 22kV | JJ59 | 回59線(JJ59) |  | 51_51NUL |  |  | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1041 |  | 0231 |  |  | 2-67 | JJ59 | 51NS U/L | F-9(JJ59)回59線 51NS |  |  | B2/D14_D1 | [12 empty] | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 504 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 22 | 22kV | JJ60 | 回60線(JJ60) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1042 |  | 0232 |  |  | 2-68 | JJ60 | 79S U/L | F-10(JJ60)回60線 79S |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ60_79UL | 23KV回60線(JJ60) 79RY U/L | FEEDER |  | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 505 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D14 | 北回DS | 22 | 22kV | JJ60 | 回60線(JJ60) |  | 51_51NUL |  |  | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1043 |  | 0233 |  |  | 2-69 | JJ60 | 51NS U/L | F-10(JJ60)回60線 51NS |  |  | B2/D14_D1 | [12 empty] | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 506 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 161 | 161kV | ComPoint |  |  | 87CTFA |  | Element | Status | 87RY CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1096 | [10 empty] | B3/D14_A1 | [12 empty] | CDC_Mon1_EMPTY,PointList_NULL |  |  |  | 507 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | RTU | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 1097 | [10 empty] | ELEM/D14_A1 | [12 empty] | CDC_Mon1_EMPTY,PointList_NULL |  |  |  | 508 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | StaDev | 所內設施 |  | MCC |  |  | Status | MCC電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1099 | [10 empty] | B3/D14_A1 | [12 empty] | CDC_Mon1_EMPTY,PointList_NULL |  |  |  | 509 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | StaDev | 所內設施 |  | PMCC |  |  | Status | PMCC電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1100 | [10 empty] | B3/D14_A1 | [12 empty] | CDC_Mon1_EMPTY,PointList_NULL |  |  |  | 510 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS |  |  | 1DTR | #1DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1106 | [10 empty] | B1/D14_A1 | [12 empty] | CDC_Mon1_EMPTY,PointList_NULL |  |  |  | 511 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS |  |  | 1DTR | #1DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1107 | [10 empty] | B1/D14_A1 | [12 empty] | CDC_Mon1_EMPTY,PointList_NULL |  |  |  | 512 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS |  |  | 1DTR | #1DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1108 | [10 empty] | B1/D14_A1 | [12 empty] | CDC_Mon1_EMPTY,PointList_NULL |  |  |  | 513 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS |  |  | 1DTR | #1DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1109 | [10 empty] | B1/D14_A1 | [12 empty] | CDC_Mon1_EMPTY,PointList_NULL |  |  |  | 514 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS |  |  | 1DTR | #1DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1110 | [10 empty] | B1/D14_A1 | [12 empty] | CDC_Mon1_EMPTY,PointList_NULL |  |  |  | 515 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS |  |  | 2DTR | #2DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1111 | [10 empty] | B1/D14_A1 | [12 empty] | CDC_Mon1_EMPTY,PointList_NULL |  |  |  | 516 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS |  |  | 2DTR | #2DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1112 | [10 empty] | B1/D14_A1 | [12 empty] | CDC_Mon1_EMPTY,PointList_NULL |  |  |  | 517 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS |  |  | 2DTR | #2DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1113 | [10 empty] | B1/D14_A1 | [12 empty] | CDC_Mon1_EMPTY,PointList_NULL |  |  |  | 518 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS |  |  | 2DTR | #2DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1114 | [10 empty] | B1/D14_A1 | [12 empty] | CDC_Mon1_EMPTY,PointList_NULL |  |  |  | 519 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS |  |  | 2DTR | #2DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1115 | [10 empty] | B1/D14_A1 | [12 empty] | CDC_Mon1_EMPTY,PointList_NULL |  |  |  | 520 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | PHA2 |  |  | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1126 | [10 empty] | B3/D14_A1 | [12 empty] | CDC_Mon1_EMPTY,PointList_NULL |  |  |  | 521 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | PHA2 |  |  | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1127 | [10 empty] | B3/D14_A1 | [12 empty] | CDC_Mon1_EMPTY,PointList_NULL |  |  |  | 522 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | PHA2 |  |  | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1128 | [10 empty] | B3/D14_A1 | [12 empty] | CDC_Mon1_EMPTY,PointList_NULL |  |  |  | 523 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | PHA2 |  |  | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1129 | [10 empty] | B3/D14_A1 | [12 empty] | CDC_Mon1_EMPTY,PointList_NULL |  |  |  | 524 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 11 | 11kV | JJ31 | 回31線(JJ31) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1044 |  | 0234 |  |  | 2-6A | JJ31 | 79S U/L | F11-(JJ31)回31線 79S |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ31_79UL | 11KV回31線(JJ31) 79RY U/L | FEEDER |  | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 525 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D14 | 北回DS | 11 | 11kV | JJ31 | 回31線(JJ31) |  | 51_51NUL |  |  | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1045 |  | 0235 |  |  | 2-6B | JJ31 | 51NS U/L | F11-(JJ31)回31線 51NS |  |  | B2/D14_D1 | [12 empty] | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 526 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 11 | 11kV | JJ32 | 回32線(JJ32) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1046 |  | 0236 |  |  | 2-6C | JJ32 | 79S U/L | F12-(JJ32)回32線 79S |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ32_79UL | 11KV回32線(JJ32) 79RY U/L | FEEDER |  | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 527 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D14 | 北回DS | 11 | 11kV | JJ32 | 回32線(JJ32) |  | 51_51NUL |  |  | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1047 |  | 0237 |  |  | 2-6D | JJ32 | 51NS U/L | F12-(JJ32)回32線 51NS |  |  | B2/D14_D1 | [12 empty] | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 528 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 11 | 11kV | JJ33 | 回33線(JJ33) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1048 |  | 0238 |  |  | 2-6E | JJ33 | 79S U/L | F13-(JJ33)回33線 79S |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ33_79UL | 11KV回33線(JJ33) 79RY U/L | FEEDER |  | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 529 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D14 | 北回DS | 11 | 11kV | JJ33 | 回33線(JJ33) |  | 51_51NUL |  |  | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1049 |  | 0239 |  |  | 2-6F | JJ33 | 51NS U/L | F13-(JJ33)回33線 51NS |  |  | B2/D14_D1 | [12 empty] | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 530 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 11 | 11kV | JJ34 | 回34線(JJ34) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1050 |  | 0240 |  |  | 2-70 | JJ34 | 79S U/L | F14-(JJ34)回34線 79S |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ34_79UL | 11KV回34線(JJ34) 79RY U/L | FEEDER |  | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 531 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D14 | 北回DS | 11 | 11kV | JJ34 | 回34線(JJ34) |  | 51_51NUL |  |  | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1051 |  | 0241 |  |  | 2-71 | JJ34 | 51NS U/L | F14-(JJ34)回34線 51NS |  |  | B2/D14_D1 | [12 empty] | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 532 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 11 | 11kV | JJ35 | 回35線(JJ35) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1052 |  | 0242 |  |  | 2-72 | JJ35 | 79S U/L | F15-(JJ35)回35線 79S |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ35_79UL | 11KV回35線(JJ35) 79RY U/L | FEEDER |  | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 533 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D14 | 北回DS | 11 | 11kV | JJ35 | 回35線(JJ35) |  | 51_51NUL |  |  | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1053 |  | 0243 |  |  | 2-73 | JJ35 | 51NS U/L | F15-(JJ35)回35線 51NS |  |  | B2/D14_D1 | [12 empty] | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 534 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 22 | 22kV | JJ66 | 回66線(JJ66) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1054 |  | 0244 |  |  | 2-74 | JJ66 | 79S U/L | F-16(JJ66)回66線 79S |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ66_79UL | 23KV回66線(JJ66) 79RY U/L | FEEDER |  | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 535 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D14 | 北回DS | 22 | 22kV | JJ66 | 回66線(JJ66) |  | 51_51NUL |  |  | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1055 |  | 0245 |  |  | 2-75 | JJ66 | 51NS U/L | F-16(JJ66)回66線 51NS |  |  | B2/D14_D1 | [12 empty] | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 536 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 22 | 22kV | JJ67 | 回67線(JJ67) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1056 |  | 0246 |  |  | 2-76 | JJ67 | 79S U/L | F-17(JJ67)回67線 79S |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ67_79UL | 23KV回67線(JJ67) 79RY U/L | FEEDER |  | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 537 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D14 | 北回DS | 22 | 22kV | JJ67 | 回67線(JJ67) |  | 51_51NUL |  |  | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1057 |  | 0247 |  |  | 2-77 | JJ67 | 51NS U/L | F-17(JJ67)回67線 51NS |  |  | B2/D14_D1 | [12 empty] | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 538 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 22 | 22kV | JJ68 | 回68線(JJ68) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1058 |  | 0248 |  |  | 2-78 | JJ68 | 79S U/L | F-18(JJ68)回68線 79S |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ68_79UL | 23KV回68線(JJ68) 79RY U/L | FEEDER |  | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 539 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D14 | 北回DS | 22 | 22kV | JJ68 | 回68線(JJ68) |  | 51_51NUL |  |  | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1059 |  | 0249 |  |  | 2-79 | JJ68 | 51NS U/L | F-18(JJ68)回68線 51NS |  |  | B2/D14_D1 | [12 empty] | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 540 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 22 | 22kV | JJ69 | 回69線(JJ69) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1060 |  | 0250 |  |  | 2-7A | JJ69 | 79S U/L | F-19(JJ69)回69線 79S |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ69_79UL | 23KV回69線(JJ69) 79RY U/L | FEEDER |  | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 541 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D14 | 北回DS | 22 | 22kV | JJ69 | 回69線(JJ69) |  | 51_51NUL |  |  | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1061 |  | 0251 |  |  | 2-7B | JJ69 | 51NS U/L | F-19(JJ69)回69線 51NS |  |  | B2/D14_D1 | [12 empty] | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 542 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 22 | 22kV | JJ70 | 回70線(JJ70) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1062 |  | 0252 |  |  | 2-7C | JJ26 | 79S U/L | F-20(JJ70)回70線 79S |  |  | B2/D14_D1 | [8 empty] | 北回DS.JJ70_79UL | 23KV回70線(JJ70) 79RY U/L | FEEDER |  | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 543 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D14 | 北回DS | 22 | 22kV | JJ70 | 回70線(JJ70) |  | 51_51NUL |  |  | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1063 |  | 0253 |  |  | 2-7D | JJ26 | 51NS U/L | F-20(JJ70)回70線 51NS |  |  | B2/D14_D1 | [12 empty] | CDC_Mon1_NULL,CDC_Mon1_EMPTY |  |  |  | 544 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 11 | 11kV | LBS210 | #1SC(210) |  | LBS |  | Element | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/210 | C/1SC(B) |  |  | 0301 |  | 0296 | 2-05-05 |  | 3-28 | 210 | LBS | #1SC(210) LBS |  |  | B3/D14_A1 | [8 empty] | 北回DS.210_LBS | 210(11KV #1SC) LBS | OTHER | [5 empty] | 545 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | LBS230 | #3SC(230) |  | LBS |  | Element | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/230 | C/3SC(B) |  |  | 0303 |  | 0298 | 2-05-07 |  | 3-2A | 230 | LBS | #3SC(230) LBS |  |  | B3/D14_A1 | [8 empty] | 北回DS.230_LBS | 230(11KV #3SC) LBS | OTHER | [5 empty] | 546 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | StaDev | 所內設施 |  | Gateway1 | 光纖網路交換機故障 |  | Status | Gateway 1故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1101 | [10 empty] | B3/D14_A1 | [16 empty] | 547 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | StaDev | 所內設施 |  | TCA |  |  | Status | 斷路器跳脫迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1098 | [10 empty] | B3/D14_A1 | [16 empty] | 548 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | StaDev | 所內設施 |  | R_Temp2 | IED盤內溫控警報 |  | Status | 溫度警報2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0769 | [10 empty] | B3/D14_A1 | [16 empty] | 549 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 0 |  | StaDev | 所內設施 |  | FiberA | IED通訊光纖故障 |  | Status | SCADA光纖故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1102 | [10 empty] | B3/D14_A1 | [16 empty] | 550 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D14 | 北回DS | 161 | 161kV | ComPoint | 所內設施 |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0058 | [10 empty] | B3/D14_A1 | [16 empty] | 551 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
D14 | 北回DS | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/D14_A1 | [12 empty] | 北回DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: D14/161/1BUS/V; OPRD2: D14/161/2BUS/V
D14 | 北回DS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/D14_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: D14/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
D14 | 北回DS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/D14_A1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_4 | OPRD1: D14/161/1510/MW; OPRD2: D14/161/1520/MW; OPRD3: D14/161/1530/MW; OPRD4: D14/161/1540/MW
D14 | 北回DS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/D14_A1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: D14/0/CalcPoint/OPRN2_MW
D14 | 北回DS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/D14_A1 | [17 empty] | none
D14 | 北回DS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/D14_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: D14/0/CalcPoint/OPRN1; OPRD2: D14/0/CalcPoint/OPRN2; OPRD3: D14/0/CalcPoint/PRFL_UL
D14 | 北回DS |  |  | 1DTR | 1DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D14_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D14/11/310/I_R; OPRD2: D14/22/320/I_R
D14 | 北回DS |  |  | 1DTR | 1DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D14_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D14/11/310/I_S; OPRD2: D14/22/320/I_S
D14 | 北回DS |  |  | 1DTR | 1DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D14_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D14/11/310/I_T; OPRD2: D14/22/320/I_T
D14 | 北回DS |  |  | 2DTR | 2DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D14_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D14/11/330/I_R; OPRD2: D14/22/340/I_R
D14 | 北回DS |  |  | 2DTR | 2DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D14_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D14/11/330/I_S; OPRD2: D14/22/340/I_S
D14 | 北回DS |  |  | 2DTR | 2DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D14_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D14/11/330/I_T; OPRD2: D14/22/340/I_T
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛～北回一路(1510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D14_A1 | [12 empty] | 北回DS.1510_AMP | 仁愛北回一路 AMP | LINE161 | AMP_CAL | C20R1930 | amp_cal | OPRD1: D14/161/1510/MW; OPRD2: D14/161/1510/MVAR; OPRD3: NULL
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛～北回二路(1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D14_A1 | [12 empty] | 北回DS.1520_AMP | 仁愛北回二路 AMP | LINE161 | AMP_CAL | C20R1930 | amp_cal | OPRD1: D14/161/1520/MW; OPRD2: D14/161/1520/MVAR; OPRD3: NULL
D14 | 北回DS | 161 | 161kV | 1530 | 北回～太鐵紅線(1530) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D14_A1 | [12 empty] | 北回DS.1530_AMP | 北回太鐵紅線 AMP | LINE161 | AMP_CAL | C20R1930 | amp_cal | OPRD1: D14/161/1530/MW; OPRD2: D14/161/1530/MVAR; OPRD3: NULL
D14 | 北回DS | 161 | 161kV | 1540 | 北回～太鐵白線(1540) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D14_A1 | [12 empty] | 北回DS.1540_AMP | 北回太鐵白線 AMP | LINE161 | AMP_CAL | C20R1930 | amp_cal | OPRD1: D14/161/1540/MW; OPRD2: D14/161/1540/MVAR; OPRD3: NULL
D14 | 北回DS | 11 | 11kV | 1ABUS | #1ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D14_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D14/11/1ABUS/V
D14 | 北回DS | 11 | 11kV | 2ABUS | #2ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D14_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D14/11/2ABUS/V
D14 | 北回DS | 22 | 22kV | 1BBUS | #1BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D14_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D14/22/1BBUS/V
D14 | 北回DS | 22 | 22kV | 2BBUS | #2BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D14_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D14/22/2BBUS/V
D14 | 北回DS |  |  | 1DTR(A) | #1DTR(A) |  | TR_PERM | [9 empty] | B1/D14_A1 | [12 empty] | 北回DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D14//1DTR(A)/SupLocal; OPRD2: D14//1DTR(A)/Tap Chan
D14 | 北回DS |  |  | 1DTR(B) | #1DTR(B) |  | TR_PERM | [9 empty] | B1/D14_A1 | [12 empty] | 北回DS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D14//1DTR(B)/SupLocal; OPRD2: D14//1DTR(B)/Tap Chan
D14 | 北回DS |  |  | 2DTR(A) | #2DTR(A) |  | TR_PERM | [9 empty] | B1/D14_A1 | [12 empty] | 北回DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D14//2DTR(A)/SupLocal; OPRD2: D14//2DTR(A)/Tap Chan
D14 | 北回DS |  |  | 2DTR(B) | #2DTR(B) |  | TR_PERM | [9 empty] | B1/D14_A1 | [12 empty] | 北回DS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D14//2DTR(B)/SupLocal; OPRD2: D14//2DTR(B)/Tap Chan
D14 | 北回DS | 11 | 11kV | JJ21 | 回21線(JJ21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D14/11/JJ21/I_R; OPRD3: D14/11/JJ21/I_S; OPRD4: D14/11/JJ21/I_T
D14 | 北回DS | 11 | 11kV | JJ22 | 回22線(JJ22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D14/11/JJ22/I_R; OPRD3: D14/11/JJ22/I_S; OPRD4: D14/11/JJ22/I_T
D14 | 北回DS | 11 | 11kV | JJ23 | 回23線(JJ23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D14/11/JJ23/I_R; OPRD3: D14/11/JJ23/I_S; OPRD4: D14/11/JJ23/I_T
D14 | 北回DS | 11 | 11kV | JJ24 | 回24線(JJ24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D14/11/JJ24/I_R; OPRD3: D14/11/JJ24/I_S; OPRD4: D14/11/JJ24/I_T
D14 | 北回DS | 11 | 11kV | JJ25 | 回25線(JJ25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D14/11/JJ25/I_R; OPRD3: D14/11/JJ25/I_S; OPRD4: D14/11/JJ25/I_T
D14 | 北回DS | 11 | 11kV | JJ31 | 回31線(JJ31) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D14/11/JJ31/I_R; OPRD3: D14/11/JJ31/I_S; OPRD4: D14/11/JJ31/I_T
D14 | 北回DS | 11 | 11kV | JJ32 | 回32線(JJ32) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D14/11/JJ32/I_R; OPRD3: D14/11/JJ32/I_S; OPRD4: D14/11/JJ32/I_T
D14 | 北回DS | 11 | 11kV | JJ33 | 回33線(JJ33) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D14/11/JJ33/I_R; OPRD3: D14/11/JJ33/I_S; OPRD4: D14/11/JJ33/I_T
D14 | 北回DS | 11 | 11kV | JJ34 | 回34線(JJ34) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D14/11/JJ34/I_R; OPRD3: D14/11/JJ34/I_S; OPRD4: D14/11/JJ34/I_T
D14 | 北回DS | 11 | 11kV | JJ35 | 回35線(JJ35) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D14/11/JJ35/I_R; OPRD3: D14/11/JJ35/I_S; OPRD4: D14/11/JJ35/I_T
D14 | 北回DS | 22 | 22kV | JJ56 | 回56線(JJ56) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D14/22/JJ56/I_R; OPRD3: D14/22/JJ56/I_S; OPRD4: D14/22/JJ56/I_T
D14 | 北回DS | 22 | 22kV | JJ57 | 回57線(JJ57) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D14/22/JJ57/I_R; OPRD3: D14/22/JJ57/I_S; OPRD4: D14/22/JJ57/I_T
D14 | 北回DS | 22 | 22kV | JJ58 | 回58線(JJ58) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D14/22/JJ58/I_R; OPRD3: D14/22/JJ58/I_S; OPRD4: D14/22/JJ58/I_T
D14 | 北回DS | 22 | 22kV | JJ59 | 回59線(JJ59) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D14/22/JJ59/I_R; OPRD3: D14/22/JJ59/I_S; OPRD4: D14/22/JJ59/I_T
D14 | 北回DS | 22 | 22kV | JJ60 | 回60線(JJ60) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D14/22/JJ60/I_R; OPRD3: D14/22/JJ60/I_S; OPRD4: D14/22/JJ60/I_T
D14 | 北回DS | 22 | 22kV | JJ66 | 回66線(JJ66) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D14/22/JJ66/I_R; OPRD3: D14/22/JJ66/I_S; OPRD4: D14/22/JJ66/I_T
D14 | 北回DS | 22 | 22kV | JJ67 | 回67線(JJ67) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D14/22/JJ67/I_R; OPRD3: D14/22/JJ67/I_S; OPRD4: D14/22/JJ67/I_T
D14 | 北回DS | 22 | 22kV | JJ68 | 回68線(JJ68) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D14/22/JJ68/I_R; OPRD3: D14/22/JJ68/I_S; OPRD4: D14/22/JJ68/I_T
D14 | 北回DS | 22 | 22kV | JJ69 | 回69線(JJ69) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D14/22/JJ69/I_R; OPRD3: D14/22/JJ69/I_S; OPRD4: D14/22/JJ69/I_T
D14 | 北回DS | 22 | 22kV | JJ70 | 回70線(JJ70) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D14/22/JJ70/I_R; OPRD3: D14/22/JJ70/I_S; OPRD4: D14/22/JJ70/I_T
D14 | 北回DS | 11 | 11kV | JJ21 | 回21線(JJ21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D14/11/JJ21/kVA; OPRD2: D14/11/JJ21/KVAR
D14 | 北回DS | 11 | 11kV | JJ22 | 回22線(JJ22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D14/11/JJ22/kVA; OPRD2: D14/11/JJ22/KVAR
D14 | 北回DS | 11 | 11kV | JJ23 | 回23線(JJ23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D14/11/JJ23/kVA; OPRD2: D14/11/JJ23/KVAR
D14 | 北回DS | 11 | 11kV | JJ24 | 回24線(JJ24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D14/11/JJ24/kVA; OPRD2: D14/11/JJ24/KVAR
D14 | 北回DS | 11 | 11kV | JJ25 | 回25線(JJ25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D14/11/JJ25/kVA; OPRD2: D14/11/JJ25/KVAR
D14 | 北回DS | 11 | 11kV | JJ31 | 回31線(JJ31) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D14/11/JJ31/kVA; OPRD2: D14/11/JJ31/KVAR
D14 | 北回DS | 11 | 11kV | JJ32 | 回32線(JJ32) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D14/11/JJ32/kVA; OPRD2: D14/11/JJ32/KVAR
D14 | 北回DS | 11 | 11kV | JJ33 | 回33線(JJ33) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D14/11/JJ33/kVA; OPRD2: D14/11/JJ33/KVAR
D14 | 北回DS | 11 | 11kV | JJ34 | 回34線(JJ34) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D14/11/JJ34/kVA; OPRD2: D14/11/JJ34/KVAR
D14 | 北回DS | 11 | 11kV | JJ35 | 回35線(JJ35) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D14/11/JJ35/kVA; OPRD2: D14/11/JJ35/KVAR
D14 | 北回DS | 22 | 22kV | JJ56 | 回56線(JJ56) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D14/22/JJ56/kVA; OPRD2: D14/22/JJ56/KVAR
D14 | 北回DS | 22 | 22kV | JJ57 | 回57線(JJ57) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D14/22/JJ57/kVA; OPRD2: D14/22/JJ57/KVAR
D14 | 北回DS | 22 | 22kV | JJ58 | 回58線(JJ58) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D14/22/JJ58/kVA; OPRD2: D14/22/JJ58/KVAR
D14 | 北回DS | 22 | 22kV | JJ59 | 回59線(JJ59) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D14/22/JJ59/kVA; OPRD2: D14/22/JJ59/KVAR
D14 | 北回DS | 22 | 22kV | JJ60 | 回60線(JJ60) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D14/22/JJ60/kVA; OPRD2: D14/22/JJ60/KVAR
D14 | 北回DS | 22 | 22kV | JJ66 | 回66線(JJ66) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D14/22/JJ66/kVA; OPRD2: D14/22/JJ66/KVAR
D14 | 北回DS | 22 | 22kV | JJ67 | 回67線(JJ67) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D14/22/JJ67/kVA; OPRD2: D14/22/JJ67/KVAR
D14 | 北回DS | 22 | 22kV | JJ68 | 回68線(JJ68) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D14/22/JJ68/kVA; OPRD2: D14/22/JJ68/KVAR
D14 | 北回DS | 22 | 22kV | JJ69 | 回69線(JJ69) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D14/22/JJ69/kVA; OPRD2: D14/22/JJ69/KVAR
D14 | 北回DS | 22 | 22kV | JJ70 | 回70線(JJ70) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D14_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D14/22/JJ70/kVA; OPRD2: D14/22/JJ70/KVAR
D14 | 北回DS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D14_A1 | [12 empty] | 北回DS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: D14/11/210/CB; OPRD2: 6.9; OPRD3: 0
D14 | 北回DS | 11 | 11kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D14_A1 | [12 empty] | 北回DS.230_SC_MVAR | 11KV#3SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: D14/11/230/CB; OPRD2: 6.9; OPRD3: 0
D14 | 北回DS | 22 | 22kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D14_A1 | [12 empty] | 北回DS.220_SC_MVAR | 23KV#2SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D14/22/220/CB; OPRD2: 13.8; OPRD3: 0
D14 | 北回DS | 22 | 22kV | 240 | #4SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D14_A1 | [12 empty] | 北回DS.240_SC_MVAR | 23KV#4SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D14/22/240/CB; OPRD2: 13.8; OPRD3: 0
D14 | 北回DS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/D14_A1 | [12 empty] | 北回DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_10 |  | com_alarm_26 | OPRD1: D14//1DTR/63Q; OPRD2: D14//1DTR/GDA; OPRD3: D14//1DTR/96D; OPRD4: D14//1DTR/96B1; OPRD5: D14//1DTR/96B2; OPRD6: D14//1DTR/PHA; OPRD7: D14//1DTR/87A; OPRD8: D14//1DTR/TRA; OPRD9: D14//1DTR/51ZA; OPRD10: D14//1DTR/96PA; OPRD11: D14//2DTR/TRA; OPRD12: D14//2DTR/96B1; OPRD13: D14//2DTR/96B2; OPRD14: D14//2DTR/63Q; OPRD15: D14//2DTR/96D; OPRD16: D14//2DTR/51ZA; OPRD17: D14//2DTR/96PA; OPRD18: D14//2DTR/87A; OPRD19: D14//2DTR/PHA; OPRD20: D14//2DTR/GDA; OPRD21: D14/11/310/GDA; OPRD22: D14/11/330/GDA; OPRD23: D14/161/1BUS/87A; OPRD24: D14/161/2BUS/87A; OPRD25: D14/22/320/GDA; OPRD26: D14/22/340/GDA
D14 | 北回DS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/D14_A1 | [12 empty] | 北回DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | STATION_FAULT_2 |  | com_alarm_2 | OPRD1: D14//1DTR/TRF; OPRD2: D14//2DTR/TRF
D14 | 北回DS | 161 | 161kV | 1750_D1 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D14_D1 | [17 empty] | lamp2CC | OPRD1: D14/161/1750/CB
D14 | 北回DS | 161 | 161kV | 1760_D1 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D14_D1 | [17 empty] | lamp2CC | OPRD1: D14/161/1760/CB
D14 | 北回DS | 11 | 11kV | 310_D1 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D14_D1 | [17 empty] | lamp2CC | OPRD1: D14/11/310/CB
D14 | 北回DS | 22 | 22kV | 320_D1 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D14_D1 | [17 empty] | lamp2CC | OPRD1: D14/22/320/CB
D14 | 北回DS | 11 | 11kV | 330_D1 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D14_D1 | [17 empty] | lamp2CC | OPRD1: D14/11/330/CB
D14 | 北回DS | 22 | 22kV | 340_D1 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D14_D1 | [17 empty] | lamp2CC | OPRD1: D14/22/340/CB
D14 | 北回DS | 0 |  | StaDev_D1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D14_D1 | [17 empty] | lamp2CC | OPRD1: D14/0/StaDev/DCE
D14 | 北回DS | 0 |  | StaDev_D1 | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/D14_D1 | [17 empty] | lamp2CC | OPRD1: D14/0/StaDev/STUV
D14 | 北回DS | 0 |  | RTU_D1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/D14_D1 | [17 empty] | lamp2CC | OPRD1: D14/0/RTU/RTU_R_L

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D14 | 北回DS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 北回DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | D14/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛北回一路(1510) |  | I | [25 empty] | ADCS_N | [8 empty] | 北回DS.1510_AMP | 仁愛北回一路 AMP | LINE161 | D14/161/1510/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C20R1930 | 1737.800049 | 1737.800049 | 1930.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛北回二路(1520) |  | I | [25 empty] | ADCS_N | [8 empty] | 北回DS.1520_AMP | 仁愛北回二路 AMP | LINE161 | D14/161/1520/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C20R1930 | 1737.800049 | 1737.800049 | 1930.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D14 | 北回DS | 161 | 161kV | 1530 | 北回太鐵紅線(1530) |  | I | [25 empty] | ADCS_N | [8 empty] | 北回DS.1530_AMP | 北回太鐵紅線 AMP | LINE161 | D14/161/1530/I |  | AMP_CAL |  |  | 5 | CalcAIPoint | [21 empty] | C20R1930 | 1737.800049 | 1737.800049 | 1930.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D14 | 北回DS | 161 | 161kV | 1540 | 北回太鐵白線(1540) |  | I | [25 empty] | ADCS_N | [8 empty] | 北回DS.1540_AMP | 北回太鐵白線 AMP | LINE161 | D14/161/1540/I |  | AMP_CAL |  |  | 6 | CalcAIPoint | [21 empty] | C20R1930 | 1737.800049 | 1737.800049 | 1930.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D14 | 北回DS | 0 |  |  |  |  | 回21線KVA | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回21線KVA | 11KV回21線KVA | FEEDER |  |  | KVA_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回21線KW | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回21線KW | 11KV回21線KW | FEEDER |  |  | KW_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回22線KVA | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回22線KVA | 11KV回22線KVA | FEEDER |  |  | KVA_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回22線KW | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回22線KW | 11KV回22線KW | FEEDER |  |  | KW_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回23線KVA | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回23線KVA | 11KV回23線KVA | FEEDER |  |  | KVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回23線KW | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回23線KW | 11KV回23線KW | FEEDER |  |  | KW_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回24線KVA | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回24線KVA | 11KV回24線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回24線KW | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回24線KW | 11KV回24線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回25線KVA | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回25線KVA | 11KV回25線KVA | FEEDER |  |  | KVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回25線KW | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回25線KW | 11KV回25線KW | FEEDER |  |  | KW_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回31線KVA | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回31線KVA | 11KV回31線KVA | FEEDER |  |  | KVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回31線KW | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回31線KW | 11KV回31線KW | FEEDER |  |  | KW_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回32線KVA | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回32線KVA | 11KV回32線KVA | FEEDER |  |  | KVA_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回32線KW | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回32線KW | 11KV回32線KW | FEEDER |  |  | KW_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回33線KVA | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回33線KVA | 11KV回33線KVA | FEEDER |  |  | KVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回33線KW | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回33線KW | 11KV回33線KW | FEEDER |  |  | KW_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回34線KVA | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回34線KVA | 11KV回34線KVA | FEEDER |  |  | KVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回34線KW | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回34線KW | 11KV回34線KW | FEEDER |  |  | KW_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回35線KVA | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回35線KVA | 11KV回35線KVA | FEEDER |  |  | KVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回35線KW | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回35線KW | 11KV回35線KW | FEEDER |  |  | KW_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回56線KVA | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回56線KVA | 23KV回56線KVA | FEEDER |  |  | KVA_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回56線KW | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回56線KW | 23KV回56線KW | FEEDER |  |  | KW_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回57線KVA | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回57線KVA | 23KV回57線KVA | FEEDER |  |  | KVA_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回57線KW | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回57線KW | 23KV回57線KW | FEEDER |  |  | KW_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回58線KVA | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回58線KVA | 23KV回58線KVA | FEEDER |  |  | KVA_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回58線KW | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回58線KW | 23KV回58線KW | FEEDER |  |  | KW_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回59線KVA | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回59線KVA | 23KV回59線KVA | FEEDER |  |  | KVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回59線KW | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回59線KW | 23KV回59線KW | FEEDER |  |  | KW_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回60線KVA | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回60線KVA | 23KV回60線KVA | FEEDER |  |  | KVA_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回60線KW | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回60線KW | 23KV回60線KW | FEEDER |  |  | KW_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回66線KVA | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回66線KVA | 23KV回66線KVA | FEEDER |  |  | KVA_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回66線KW | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回66線KW | 23KV回66線KW | FEEDER |  |  | KW_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回67線KVA | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回67線KVA | 23KV回67線KVA | FEEDER |  |  | KVA_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回67線KW | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回67線KW | 23KV回67線KW | FEEDER |  |  | KW_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回68線KVA | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回68線KVA | 23KV回68線KVA | FEEDER |  |  | KVA_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回68線KW | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回68線KW | 23KV回68線KW | FEEDER |  |  | KW_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回69線KVA | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回69線KVA | 23KV回69線KVA | FEEDER |  |  | KVA_CAL |  |  | 43 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回69線KW | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回69線KW | 23KV回69線KW | FEEDER |  |  | KW_CAL |  |  | 44 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回70線KVA | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回70線KVA | 23KV回70線KVA | FEEDER |  |  | KVA_CAL |  |  | 45 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  |  |  |  | 回70線KW | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.回70線KW | 23KV回70線KW | FEEDER |  |  | KW_CAL |  |  | 46 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 北回DS.#1DTR(A)_MVA | #1DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 47 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D14 | 北回DS | 0 |  | 1DTR(A) | #1DTR(A) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 北回DS.#1DTR(A)_LOAD | #1DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 48 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D14 | 北回DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PF | [25 empty] | ADCS_N | [8 empty] | 北回DS.#1DTR(A)_PF | #1DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 49 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D14 | 北回DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 北回DS.#1DTR(B)_MVA | #1DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 50 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D14 | 北回DS | 0 |  | 1DTR(B) | #1DTR(B) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 北回DS.#1DTR(B)_LOAD | #1DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 51 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D14 | 北回DS | 0 |  | 1DTR(B) | #1DTR(B) |  | PF | [25 empty] | ADCS_N | [8 empty] | 北回DS.#1DTR(B)_PF | #1DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 52 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D14 | 北回DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 北回DS.#2DTR(A)_MVA | #2DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 53 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D14 | 北回DS | 0 |  | 2DTR(A) | #2DTR(A) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 北回DS.#2DTR(A)_LOAD | #2DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 54 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D14 | 北回DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PF | [25 empty] | ADCS_N | [8 empty] | 北回DS.#2DTR(A)_PF | #2DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 55 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D14 | 北回DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 北回DS.#2DTR(B)_MVA | #2DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 56 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D14 | 北回DS | 0 |  | 2DTR(B) | #2DTR(B) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 北回DS.#2DTR(B)_LOAD | #2DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 57 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D14 | 北回DS | 0 |  | 2DTR(B) | #2DTR(B) |  | PF | [25 empty] | ADCS_N | [8 empty] | 北回DS.#2DTR(B)_PF | #2DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 58 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D14 | 北回DS | 0 |  | 1DTR | #1DTR |  | MW | [25 empty] | ADCS_N | [8 empty] | 北回DS.#1DTR_MW | #1DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 59 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  | 1DTR | #1DTR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 北回DS.#1DTR_MVAR | #1DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 60 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  | 1DTR | #1DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 北回DS.#1DTR_MVA | #1DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 61 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D14 | 北回DS | 0 |  | 1DTR | #1DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 北回DS.#1DTR_LOAD | #1DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 62 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D14 | 北回DS | 0 |  | 2DTR | #2DTR |  | MW | [25 empty] | ADCS_N | [8 empty] | 北回DS.#2DTR_MW | #2DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 63 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  | 2DTR | #2DTR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 北回DS.#2DTR_MVAR | #2DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 64 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  | 2DTR | #2DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 北回DS.#2DTR_MVA | #2DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 65 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D14 | 北回DS | 0 |  | 2DTR | #2DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 北回DS.#2DTR_LOAD | #2DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 66 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D14 | 北回DS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 北回DS.210_SC_MVAR | 11KV#1SC MVAR | SC | D14/11/210/MVAR |  | SC_CAL_11 |  |  | 67 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 11 | 11kV | 230_SC | #3SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 北回DS.230_SC_MVAR | 11KV#3SC MVAR | SC | D14/11/230/MVAR |  | SC_CAL_11 |  |  | 68 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 22 | 22kV | 220_SC | #2SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 北回DS.220_SC_MVAR | 23KV#2SC MVAR | SC | D14/22/220/MVAR |  | SC_CAL_23 |  |  | 69 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 22 | 22kV | 240_SC | #4SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 北回DS.240_SC_MVAR | 23KV#4SC MVAR | SC | D14/22/240/MVAR |  | SC_CAL_23 |  |  | 70 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  | TRTOT | 北回主變瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 北回DS.TRTOT_MW | 北回主變瞬時供電量 MW |  |  |  | MTR_PQ_CAL |  |  | 71 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  | TRTOT | 北回主變瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 北回DS.TRTOT_MVAR | 北回主變瞬時供電量 MVAR |  |  |  | MTR_PQ_CAL |  |  | 72 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 0 |  | 100_CB | 100(100_CB) | [27 empty] | DDCS2_1 | [8 empty] | 北回DS.100_CB_2 | 100 CB (D2) | TIE |  |  | AD_LAMP_DD_1 |  |  | 73 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | 200_CB | 200(200_CB) | [27 empty] | DDCS2_1 | [8 empty] | 北回DS.200_CB_2 | 200 CB (D2) | TIE |  |  | AD_LAMP_DD_1 |  |  | 74 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | 1750_CB | #1DTR(1750_CB) | [27 empty] | DDCS2_1 | [8 empty] | 北回DS.1750_CB_2 | 1750(#1DTR) CB (D2) | MTR |  |  | AD_LAMP_DD_1 |  |  | 75 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | 310_CB | #1DTR(310_CB) | [27 empty] | DDCS2_1 | [8 empty] | 北回DS.310_CB_2 | 310(#1DTR) CB (D2) | MTR |  |  | AD_LAMP_DD_1 |  |  | 76 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | 320_CB | #1DTR(320_CB) | [27 empty] | DDCS2_1 | [8 empty] | 北回DS.320_CB_2 | 320(#1DTR) CB (D2) | MTR |  |  | AD_LAMP_DD_1 |  |  | 77 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | 1760_CB | #2DTR(1760_CB) | [27 empty] | DDCS2_1 | [8 empty] | 北回DS.1760_CB_2 | 1760(#2DTR) CB (D2) | MTR |  |  | AD_LAMP_DD_1 |  |  | 78 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | 330_CB | #2DTR(330_CB) | [27 empty] | DDCS2_1 | [8 empty] | 北回DS.330_CB_2 | 330(#2DTR) CB (D2) | MTR |  |  | AD_LAMP_DD_1 |  |  | 79 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | 340_CB | #2DTR(340_CB) | [27 empty] | DDCS2_1 | [8 empty] | 北回DS.340_CB_2 | 340(#2DTR) CB (D2) | MTR |  |  | AD_LAMP_DD_1 |  |  | 80 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | 210_CB | #1SC(210_CB) | [27 empty] | DDCS2_1 | [8 empty] | 北回DS.210_CB_2 | 210(11KV #1SC) CB (D2) | SC |  |  | AD_LAMP_DD_1 |  |  | 81 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | 230_CB | #3SC(230_CB) | [27 empty] | DDCS2_1 | [8 empty] | 北回DS.230_CB_2 | 230(11KV #3SC) CB (D2) | SC |  |  | AD_LAMP_DD_1 |  |  | 82 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | 220_CB | #2SC(220_CB) | [27 empty] | DDCS2_1 | [8 empty] | 北回DS.220_CB_2 | 220(23KV #2SC) CB (D2) | SC |  |  | AD_LAMP_DD_1 |  |  | 83 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | 240_CB | #4SC(240_CB) | [27 empty] | DDCS2_1 | [8 empty] | 北回DS.240_CB_2 | 240(23KV #4SC) CB (D2) | SC |  |  | AD_LAMP_DD_1 |  |  | 84 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | 11__CBA | 11/斷路器重故障(11__CBA) | [27 empty] | DDCS2_1 | [8 empty] | 北回DS.11/23KV_CBA_2 | 11/23KV斷路器重故障 (D2) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 85 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | 11__CBF | 11/斷路器輕故障(11__CBF) | [27 empty] | DDCS2_1 | [8 empty] | 北回DS.11/23KV_CBF_2 | 11/23KV斷路器輕故障 (D2) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 86 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_N | [8 empty] | 北回DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | D14/0/CalcPoint/SUBA |  | STATION_FAULT_10 |  |  | 87 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 變電所輕故障點燈 | 變電所輕故障點燈 |  | SUBF | [25 empty] | ADCS_N | [8 empty] | 北回DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | D14/0/CalcPoint/SUBF |  | STATION_FAULT_2 |  |  | 88 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 變電所重故障 | 變電所重故障點燈 | [27 empty] | DDCS2_1 | [8 empty] | 北回DS.變電所重故障_2 | 變電所重故障點燈 (D2) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 89 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 | [27 empty] | DDCS2_1 | [8 empty] | 北回DS.變電所輕故障_2 | 變電所輕故障點燈 (D2) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 90 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1510_AMP | 仁愛北回一路 | [27 empty] | ADCS_N | [8 empty] | 北回DS.1510_AMP_A | 仁愛北回一路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 91 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D14 | 北回DS | 161 | 161kV | 1520_AMP | 仁愛北回二路 | [27 empty] | ADCS_N | [8 empty] | 北回DS.1520_AMP_A | 仁愛北回二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 92 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D14 | 北回DS | 161 | 161kV | 1530_AMP | 北回太鐵紅線 | [27 empty] | ADCS_N | [8 empty] | 北回DS.1530_AMP_A | 北回太鐵紅線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 93 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D14 | 北回DS | 161 | 161kV | 1540_AMP | 北回太鐵白線 | [27 empty] | ADCS_N | [8 empty] | 北回DS.1540_AMP_A | 北回太鐵白線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 94 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D14 | 北回DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PERM | [25 empty] | ADCS_N | [8 empty] | 北回DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | D14//1DTR(A)/TR_PERM |  | DTR_PERM |  |  | 95 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D14 | 北回DS | 0 |  | 1DTR(B) | #1DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 北回DS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | D14//1DTR(B)/TR_PERM |  | DTR_PERM |  |  | 96 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D14 | 北回DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PERM | [25 empty] | ADCS_N | [8 empty] | 北回DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | D14//2DTR(A)/TR_PERM |  | DTR_PERM |  |  | 97 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D14 | 北回DS | 0 |  | 2DTR(B) | #2DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 北回DS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | D14//2DTR(B)/TR_PERM |  | DTR_PERM |  |  | 98 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D14 | 北回DS | 0 |  | 1DTR_MVA | #1DTR | [27 empty] | ADCS_N | [8 empty] | 北回DS.#1DTR_MVA_A | #1DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 99 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D14 | 北回DS | 0 |  | 1DTR_MVA | #1DTR(A) | [27 empty] | DDCS2_1 | [8 empty] | 北回DS.#1DTR_MVA_2 | #1DTR(A) MVA 點燈 (D2) | MTR |  |  | MAP_SET |  |  | 100 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
D14 | 北回DS | 0 |  | 1DTR_MVA | #1DTR(B) |  | 3 | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.#1DTR_MVA_3 | #1DTR(B) MVA 點燈 (D2) | MTR |  |  | MAP_SET |  |  | 101 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D14 | 北回DS | 0 |  | 2DTR_MVA | #2DTR | [27 empty] | ADCS_N | [8 empty] | 北回DS.#2DTR_MVA_A | #2DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 102 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D14 | 北回DS | 0 |  | 2DTR_MVA | #2DTR(A) | [27 empty] | DDCS2_1 | [8 empty] | 北回DS.#2DTR_MVA_2 | #2DTR(A) MVA 點燈 (D2) | MTR |  |  | MAP_SET |  |  | 103 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
D14 | 北回DS | 0 |  | 2DTR_MVA | #2DTR(B) |  | 3 | [25 empty] | DDCS2_1 | [8 empty] | 北回DS.#2DTR_MVA_3 | #2DTR(B) MVA 點燈 (D2) | MTR |  |  | MAP_SET |  |  | 104 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D14 | 北回DS | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_N | [8 empty] | 北回DS.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_DS |  |  | 105 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 1ABUS | #1ABUS |  | 11KV#1ABUSC | [25 empty] | CDCS | [8 empty] | 北回DS.11KV#1ABUSC | #1ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 106 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D14 | 北回DS | 0 |  | 1BBUS | #1BBUS |  | 23KV#1BBUSC | [25 empty] | CDCS | [8 empty] | 北回DS.23KV#1BBUSC | #1BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 107 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D14 | 北回DS | 0 |  | 2ABUS | #2ABUS |  | 11KV#2ABUSC | [25 empty] | CDCS | [8 empty] | 北回DS.11KV#2ABUSC | #2ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 108 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D14 | 北回DS | 0 |  | 2BBUS | #2BBUS |  | 23KV#2BBUSC | [25 empty] | CDCS | [8 empty] | 北回DS.23KV#2BBUSC | #2BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 109 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D14 | 北回DS | 0 |  | TAP_OVER | TAP |  | SET | [25 empty] | ADCS_N | [8 empty] | 北回DS.TAP_OVER_SET | TAP OVER HI/LO ALARM | MTR |  |  | 5000_CB_T4 |  |  | 110 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D14 | 北回DS | 0 |  | BUS_OVER | BUS |  | SET | [25 empty] | ADCS_N | [8 empty] | 北回DS.BUS_OVER_SET | BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B4 |  |  | 111 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D14 | 北回DS | 0 |  | 5000 | 虛擬5000 |  | CB動作 | [25 empty] | ADCS_N | [8 empty] | 北回DS.5000_CB動作 | 虛擬5000 CB動作,請查明原因處理 | MTR |  |  | 5000_CB_M |  |  | 112 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | 注意OLTC | 注意OLTC |  | BUS電壓異常 | [25 empty] | ADCS_N | [8 empty] | 北回DS.BUS電壓異常 | 注意OLTC Tap位置,並將RPDC閉鎖 | OTHER |  |  | STATION_FAULT_2 |  |  | 113 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | D14/161/1BUS/V |  |  |  | CDC | 114 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D14 | 北回DS | 161 | 161kV | 2BUS | #2BUS |  | V | [17 empty] | 1-83 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | D14/161/2BUS/V |  |  |  | CDC | 115 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D14 | 北回DS | 11 | 11kV | 1ABUS | #1ABUS |  | V | [17 empty] | 1-AD | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.11KV#1ABUS_KV | 11KV #1ABUS KV | BUS | D14/11/1ABUS/V |  |  |  | CDC | 116 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D14 | 北回DS | 11 | 11kV | 2ABUS | #2ABUS |  | V | [17 empty] | 1-FD | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS | D14/11/2ABUS/V |  |  |  | CDC | 117 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D14 | 北回DS | 22 | 22kV | 1BBUS | #1BBUS |  | V | [17 empty] | 1-D6 | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.23KV#1BBUS_KV | 23KV #1BBUS KV | BUS | D14/22/1BBUS/V |  |  |  | CDC | 118 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D14 | 北回DS | 22 | 22kV | 2BBUS | #2BBUS |  | V | [17 empty] | 2-A3 | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.23KV#2BBUS_KV | 23KV #2BBUS KV | BUS | D14/22/2BBUS/V |  |  |  | CDC | 119 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛北回一路(1510) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.1510_MW | 仁愛北回一路 MW | LINE161 | D14/161/1510/MW |  |  |  | CDC | 120 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛北回一路(1510) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.1510_MVAR | 仁愛北回一路 MVAR | LINE161 | D14/161/1510/MVAR |  |  |  | CDC | 121 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛北回二路(1520) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.1520_MW | 仁愛北回二路 MW | LINE161 | D14/161/1520/MW |  |  |  | CDC | 122 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛北回二路(1520) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.1520_MVAR | 仁愛北回二路 MVAR | LINE161 | D14/161/1520/MVAR |  |  |  | CDC | 123 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D14 | 北回DS | 161 | 161kV | 1530 | 北回太鐵紅線(1530) |  | MW | [17 empty] | 1-88 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.1530_MW | 北回太鐵紅線 MW | LINE161 | D14/161/1530/MW |  |  |  | CDC | 124 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D14 | 北回DS | 161 | 161kV | 1530 | 北回太鐵紅線(1530) |  | MVAR | [17 empty] | 1-89 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.1530_MVAR | 北回太鐵紅線 MVAR | LINE161 | D14/161/1530/MVAR |  |  |  | CDC | 125 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D14 | 北回DS | 161 | 161kV | 1540 | 北回太鐵白線(1540) |  | MW | [17 empty] | 1-8A | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.1540_MW | 北回太鐵白線 MW | LINE161 | D14/161/1540/MW |  |  |  | CDC | 126 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D14 | 北回DS | 161 | 161kV | 1540 | 北回太鐵白線(1540) |  | MVAR | [17 empty] | 1-8B | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.1540_MVAR | 北回太鐵白線 MVAR | LINE161 | D14/161/1540/MVAR |  |  |  | CDC | 127 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回21線 | 回21線 |  | 回21線KVAR | [17 empty] | 1-B4 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回21線KVAR | 11KV回21線 KVAR | FEEDER | D14/11/JJ21/KVAR |  |  |  | CDC | 128 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回21線 | 回21線 |  | 回21線A1 | [17 empty] | 1-B5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回21線A1 | 11KV回21線 R相AMP | FEEDER | D14/11/JJ21/I_R |  |  |  | CDC | 129 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回21線 | 回21線 |  | 回21線A2 | [17 empty] | 1-B6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回21線A2 | 11KV回21線 S相AMP | FEEDER | D14/11/JJ21/I_S |  |  |  | CDC | 130 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回21線 | 回21線 |  | 回21線A3 | [17 empty] | 1-B7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回21線A3 | 11KV回21線 T相AMP | FEEDER | D14/11/JJ21/I_T |  |  |  | CDC | 131 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回21線 | 回21線 |  | 回21線A0 | [17 empty] | 1-B8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回21線A0 | 11KV回21線 N相AMP | FEEDER | D14/11/JJ21/I_N |  |  |  | CDC | 132 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回22線 | 回22線 |  | 回22線KVAR | [17 empty] | 1-BA | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回22線KVAR | 11KV回22線 KVAR | FEEDER | D14/11/JJ22/KVAR |  |  |  | CDC | 133 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回22線 | 回22線 |  | 回22線A1 | [17 empty] | 1-BB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回22線A1 | 11KV回22線 R相AMP | FEEDER | D14/11/JJ22/I_R |  |  |  | CDC | 134 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回22線 | 回22線 |  | 回22線A2 | [17 empty] | 1-BC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回22線A2 | 11KV回22線 S相AMP | FEEDER | D14/11/JJ22/I_S |  |  |  | CDC | 135 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回22線 | 回22線 |  | 回22線A3 | [17 empty] | 1-BD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回22線A3 | 11KV回22線 T相AMP | FEEDER | D14/11/JJ22/I_T |  |  |  | CDC | 136 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回22線 | 回22線 |  | 回22線A0 | [17 empty] | 1-BE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回22線A0 | 11KV回22線 N相AMP | FEEDER | D14/11/JJ22/I_N |  |  |  | CDC | 137 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回23線 | 回23線 |  | 回23線KVAR | [17 empty] | 1-C2 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回23線KVAR | 11KV回23線 KVAR | FEEDER | D14/11/JJ23/KVAR |  |  |  | CDC | 138 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回23線 | 回23線 |  | 回23線A1 | [17 empty] | 1-C3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回23線A1 | 11KV回23線 R相AMP | FEEDER | D14/11/JJ23/I_R |  |  |  | CDC | 139 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回23線 | 回23線 |  | 回23線A2 | [17 empty] | 1-C4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回23線A2 | 11KV回23線 S相AMP | FEEDER | D14/11/JJ23/I_S |  |  |  | CDC | 140 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回23線 | 回23線 |  | 回23線A3 | [17 empty] | 1-C5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回23線A3 | 11KV回23線 T相AMP | FEEDER | D14/11/JJ23/I_T |  |  |  | CDC | 141 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回23線 | 回23線 |  | 回23線A0 | [17 empty] | 1-C6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回23線A0 | 11KV回23線 N相AMP | FEEDER | D14/11/JJ23/I_N |  |  |  | CDC | 142 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回24線 | 回24線 |  | 回24線KVAR | [17 empty] | 1-C8 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回24線KVAR | 11KV回24線 KVAR | FEEDER | D14/11/JJ24/KVAR |  |  |  | CDC | 143 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回24線 | 回24線 |  | 回24線A1 | [17 empty] | 1-C9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回24線A1 | 11KV回24線 R相AMP | FEEDER | D14/11/JJ24/I_R |  |  |  | CDC | 144 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回24線 | 回24線 |  | 回24線A2 | [17 empty] | 1-CA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回24線A2 | 11KV回24線 S相AMP | FEEDER | D14/11/JJ24/I_S |  |  |  | CDC | 145 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回24線 | 回24線 |  | 回24線A3 | [17 empty] | 1-CB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回24線A3 | 11KV回24線 T相AMP | FEEDER | D14/11/JJ24/I_T |  |  |  | CDC | 146 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回24線 | 回24線 |  | 回24線A0 | [17 empty] | 1-CC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回24線A0 | 11KV回24線 N相AMP | FEEDER | D14/11/JJ24/I_N |  |  |  | CDC | 147 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回25線 | 回25線 |  | 回25線KVAR | [17 empty] | 1-CE | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回25線KVAR | 11KV回25線 KVAR | FEEDER | D14/11/JJ25/KVAR |  |  |  | CDC | 148 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回25線 | 回25線 |  | 回25線A1 | [17 empty] | 1-CF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回25線A1 | 11KV回25線 R相AMP | FEEDER | D14/11/JJ25/I_R |  |  |  | CDC | 149 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回25線 | 回25線 |  | 回25線A2 | [17 empty] | 1-D0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回25線A2 | 11KV回25線 S相AMP | FEEDER | D14/11/JJ25/I_S |  |  |  | CDC | 150 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回25線 | 回25線 |  | 回25線A3 | [17 empty] | 1-D1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回25線A3 | 11KV回25線 T相AMP | FEEDER | D14/11/JJ25/I_T |  |  |  | CDC | 151 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回25線 | 回25線 |  | 回25線A0 | [17 empty] | 1-D2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回25線A0 | 11KV回25線 N相AMP | FEEDER | D14/11/JJ25/I_N |  |  |  | CDC | 152 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回31線 | 回31線 |  | 回31線KVAR | [17 empty] | 2-86 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回31線KVAR | 11KV回31線 KVAR | FEEDER | D14/11/JJ31/KVAR |  |  |  | CDC | 153 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回31線 | 回31線 |  | 回31線A1 | [17 empty] | 2-87 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回31線A1 | 11KV回31線 R相AMP | FEEDER | D14/11/JJ31/I_R |  |  |  | CDC | 154 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回31線 | 回31線 |  | 回31線A2 | [17 empty] | 2-88 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回31線A2 | 11KV回31線 S相AMP | FEEDER | D14/11/JJ31/I_S |  |  |  | CDC | 155 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回31線 | 回31線 |  | 回31線A3 | [17 empty] | 2-89 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回31線A3 | 11KV回31線 T相AMP | FEEDER | D14/11/JJ31/I_T |  |  |  | CDC | 156 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回31線 | 回31線 |  | 回31線A0 | [17 empty] | 2-8A | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回31線A0 | 11KV回31線 N相AMP | FEEDER | D14/11/JJ31/I_N |  |  |  | CDC | 157 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回32線 | 回32線 |  | 回32線KVAR | [17 empty] | 2-8C | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回32線KVAR | 11KV回32線 KVAR | FEEDER | D14/11/JJ32/KVAR |  |  |  | CDC | 158 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回32線 | 回32線 |  | 回32線A1 | [17 empty] | 2-8D | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回32線A1 | 11KV回32線 R相AMP | FEEDER | D14/11/JJ32/I_R |  |  |  | CDC | 159 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回32線 | 回32線 |  | 回32線A2 | [17 empty] | 2-8E | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回32線A2 | 11KV回32線 S相AMP | FEEDER | D14/11/JJ32/I_S |  |  |  | CDC | 160 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回32線 | 回32線 |  | 回32線A3 | [17 empty] | 2-8F | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回32線A3 | 11KV回32線 T相AMP | FEEDER | D14/11/JJ32/I_T |  |  |  | CDC | 161 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回32線 | 回32線 |  | 回32線A0 | [17 empty] | 2-90 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回32線A0 | 11KV回32線 N相AMP | FEEDER | D14/11/JJ32/I_N |  |  |  | CDC | 162 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回33線 | 回33線 |  | 回33線KVAR | [17 empty] | 2-92 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回33線KVAR | 11KV回33線 KVAR | FEEDER | D14/11/JJ33/KVAR |  |  |  | CDC | 163 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回33線 | 回33線 |  | 回33線A1 | [17 empty] | 2-93 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回33線A1 | 11KV回33線 R相AMP | FEEDER | D14/11/JJ33/I_R |  |  |  | CDC | 164 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回33線 | 回33線 |  | 回33線A2 | [17 empty] | 2-94 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回33線A2 | 11KV回33線 S相AMP | FEEDER | D14/11/JJ33/I_S |  |  |  | CDC | 165 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回33線 | 回33線 |  | 回33線A3 | [17 empty] | 2-95 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回33線A3 | 11KV回33線 T相AMP | FEEDER | D14/11/JJ33/I_T |  |  |  | CDC | 166 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回33線 | 回33線 |  | 回33線A0 | [17 empty] | 2-96 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回33線A0 | 11KV回33線 N相AMP | FEEDER | D14/11/JJ33/I_N |  |  |  | CDC | 167 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回34線 | 回34線 |  | 回34線KVAR | [17 empty] | 2-98 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回34線KVAR | 11KV回34線 KVAR | FEEDER | D14/11/JJ34/KVAR |  |  |  | CDC | 168 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回34線 | 回34線 |  | 回34線A1 | [17 empty] | 2-99 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回34線A1 | 11KV回34線 R相AMP | FEEDER | D14/11/JJ34/I_R |  |  |  | CDC | 169 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回34線 | 回34線 |  | 回34線A2 | [17 empty] | 2-9A | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回34線A2 | 11KV回34線 S相AMP | FEEDER | D14/11/JJ34/I_S |  |  |  | CDC | 170 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回34線 | 回34線 |  | 回34線A3 | [17 empty] | 2-9B | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回34線A3 | 11KV回34線 T相AMP | FEEDER | D14/11/JJ34/I_T |  |  |  | CDC | 171 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回34線 | 回34線 |  | 回34線A0 | [17 empty] | 2-9C | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回34線A0 | 11KV回34線 N相AMP | FEEDER | D14/11/JJ34/I_N |  |  |  | CDC | 172 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回35線 | 回35線 |  | 回35線KVAR | [17 empty] | 2-9E | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回35線KVAR | 11KV回35線 KVAR | FEEDER | D14/11/JJ35/KVAR |  |  |  | CDC | 173 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回35線 | 回35線 |  | 回35線A1 | [17 empty] | 2-9F | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回35線A1 | 11KV回35線 R相AMP | FEEDER | D14/11/JJ35/I_R |  |  |  | CDC | 174 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回35線 | 回35線 |  | 回35線A2 | [17 empty] | 2-A0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回35線A2 | 11KV回35線 S相AMP | FEEDER | D14/11/JJ35/I_S |  |  |  | CDC | 175 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回35線 | 回35線 |  | 回35線A3 | [17 empty] | 2-A1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回35線A3 | 11KV回35線 T相AMP | FEEDER | D14/11/JJ35/I_T |  |  |  | CDC | 176 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | 回35線 | 回35線 |  | 回35線A0 | [17 empty] | 2-A2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回35線A0 | 11KV回35線 N相AMP | FEEDER | D14/11/JJ35/I_N |  |  |  | CDC | 177 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回56線 | 回56線 |  | 回56線KVAR | [17 empty] | 1-DD | [5 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回56線KVAR | 23KV回56線 KVAR | FEEDER | D14/22/JJ56/KVAR |  |  |  | CDC | 178 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回56線 | 回56線 |  | 回56線A1 | [17 empty] | 1-DE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回56線A1 | 23KV回56線 R相AMP | FEEDER | D14/22/JJ56/I_R |  |  |  | CDC | 179 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回56線 | 回56線 |  | 回56線A2 | [17 empty] | 1-DF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回56線A2 | 23KV回56線 S相AMP | FEEDER | D14/22/JJ56/I_S |  |  |  | CDC | 180 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回56線 | 回56線 |  | 回56線A3 | [17 empty] | 1-E0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回56線A3 | 23KV回56線 T相AMP | FEEDER | D14/22/JJ56/I_T |  |  |  | CDC | 181 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回56線 | 回56線 |  | 回56線A0 | [17 empty] | 1-E1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回56線A0 | 23KV回56線 N相AMP | FEEDER | D14/22/JJ56/I_N |  |  |  | CDC | 182 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回57線 | 回57線 |  | 回57線KVAR | [17 empty] | 1-E3 | [5 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回57線KVAR | 23KV回57線 KVAR | FEEDER | D14/22/JJ57/KVAR |  |  |  | CDC | 183 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回57線 | 回57線 |  | 回57線A1 | [17 empty] | 1-E4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回57線A1 | 23KV回57線 R相AMP | FEEDER | D14/22/JJ57/I_R |  |  |  | CDC | 184 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回57線 | 回57線 |  | 回57線A2 | [17 empty] | 1-E5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回57線A2 | 23KV回57線 S相AMP | FEEDER | D14/22/JJ57/I_S |  |  |  | CDC | 185 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回57線 | 回57線 |  | 回57線A3 | [17 empty] | 1-E6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回57線A3 | 23KV回57線 T相AMP | FEEDER | D14/22/JJ57/I_T |  |  |  | CDC | 186 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回57線 | 回57線 |  | 回57線A0 | [17 empty] | 1-E7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回57線A0 | 23KV回57線 N相AMP | FEEDER | D14/22/JJ57/I_N |  |  |  | CDC | 187 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回58線 | 回58線 |  | 回58線KVAR | [17 empty] | 1-E9 | [5 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回58線KVAR | 23KV回58線 KVAR | FEEDER | D14/22/JJ58/KVAR |  |  |  | CDC | 188 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回58線 | 回58線 |  | 回58線A1 | [17 empty] | 1-EA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回58線A1 | 23KV回58線 R相AMP | FEEDER | D14/22/JJ58/I_R |  |  |  | CDC | 189 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回58線 | 回58線 |  | 回58線A2 | [17 empty] | 1-EB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回58線A2 | 23KV回58線 S相AMP | FEEDER | D14/22/JJ58/I_S |  |  |  | CDC | 190 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回58線 | 回58線 |  | 回58線A3 | [17 empty] | 1-EC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回58線A3 | 23KV回58線 T相AMP | FEEDER | D14/22/JJ58/I_T |  |  |  | CDC | 191 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回58線 | 回58線 |  | 回58線A0 | [17 empty] | 1-ED | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回58線A0 | 23KV回58線 N相AMP | FEEDER | D14/22/JJ58/I_N |  |  |  | CDC | 192 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回59線 | 回59線 |  | 回59線KVAR | [17 empty] | 1-EF | [5 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回59線KVAR | 23KV回59線 KVAR | FEEDER | D14/22/JJ59/KVAR |  |  |  | CDC | 193 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回59線 | 回59線 |  | 回59線A1 | [17 empty] | 1-F0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回59線A1 | 23KV回59線 R相AMP | FEEDER | D14/22/JJ59/I_R |  |  |  | CDC | 194 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回59線 | 回59線 |  | 回59線A2 | [17 empty] | 1-F1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回59線A2 | 23KV回59線 S相AMP | FEEDER | D14/22/JJ59/I_S |  |  |  | CDC | 195 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回59線 | 回59線 |  | 回59線A3 | [17 empty] | 1-F2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回59線A3 | 23KV回59線 T相AMP | FEEDER | D14/22/JJ59/I_T |  |  |  | CDC | 196 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回59線 | 回59線 |  | 回59線A0 | [17 empty] | 1-F3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回59線A0 | 23KV回59線 N相AMP | FEEDER | D14/22/JJ59/I_N |  |  |  | CDC | 197 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回60線 | 回60線 |  | 回60線KVAR | [17 empty] | 1-F5 | [5 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回60線KVAR | 23KV回60線 KVAR | FEEDER | D14/22/JJ60/KVAR |  |  |  | CDC | 198 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回60線 | 回60線 |  | 回60線A1 | [17 empty] | 1-F6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回60線A1 | 23KV回60線 R相AMP | FEEDER | D14/22/JJ60/I_R |  |  |  | CDC | 199 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回60線 | 回60線 |  | 回60線A2 | [17 empty] | 1-F7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回60線A2 | 23KV回60線 S相AMP | FEEDER | D14/22/JJ60/I_S |  |  |  | CDC | 200 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回60線 | 回60線 |  | 回60線A3 | [17 empty] | 1-F8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回60線A3 | 23KV回60線 T相AMP | FEEDER | D14/22/JJ60/I_T |  |  |  | CDC | 201 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回60線 | 回60線 |  | 回60線A0 | [17 empty] | 1-F9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回60線A0 | 23KV回60線 N相AMP | FEEDER | D14/22/JJ60/I_N |  |  |  | CDC | 202 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回66線 | 回66線 |  | 回66線KVAR | [17 empty] | 2-AA | [5 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回66線KVAR | 23KV回66線 KVAR | FEEDER | D14/22/JJ66/KVAR |  |  |  | CDC | 203 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回66線 | 回66線 |  | 回66線A1 | [17 empty] | 2-AB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回66線A1 | 23KV回66線 R相AMP | FEEDER | D14/22/JJ66/I_R |  |  |  | CDC | 204 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回66線 | 回66線 |  | 回66線A2 | [17 empty] | 2-AC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回66線A2 | 23KV回66線 S相AMP | FEEDER | D14/22/JJ66/I_S |  |  |  | CDC | 205 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回66線 | 回66線 |  | 回66線A3 | [17 empty] | 2-AD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回66線A3 | 23KV回66線 T相AMP | FEEDER | D14/22/JJ66/I_T |  |  |  | CDC | 206 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回66線 | 回66線 |  | 回66線A0 | [17 empty] | 2-AE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回66線A0 | 23KV回66線 N相AMP | FEEDER | D14/22/JJ66/I_N |  |  |  | CDC | 207 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回67線 | 回67線 |  | 回67線KVAR | [17 empty] | 2-B0 | [5 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回67線KVAR | 23KV回67線 KVAR | FEEDER | D14/22/JJ67/KVAR |  |  |  | CDC | 208 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回67線 | 回67線 |  | 回67線A1 | [17 empty] | 2-B1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回67線A1 | 23KV回67線 R相AMP | FEEDER | D14/22/JJ67/I_R |  |  |  | CDC | 209 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回67線 | 回67線 |  | 回67線A2 | [17 empty] | 2-B2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回67線A2 | 23KV回67線 S相AMP | FEEDER | D14/22/JJ67/I_S |  |  |  | CDC | 210 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回67線 | 回67線 |  | 回67線A3 | [17 empty] | 2-B3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回67線A3 | 23KV回67線 T相AMP | FEEDER | D14/22/JJ67/I_T |  |  |  | CDC | 211 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回67線 | 回67線 |  | 回67線A0 | [17 empty] | 2-B4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回67線A0 | 23KV回67線 N相AMP | FEEDER | D14/22/JJ67/I_N |  |  |  | CDC | 212 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回68線 | 回68線 |  | 回68線KVAR | [17 empty] | 2-B6 | [5 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回68線KVAR | 23KV回68線 KVAR | FEEDER | D14/22/JJ68/KVAR |  |  |  | CDC | 213 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回68線 | 回68線 |  | 回68線A1 | [17 empty] | 2-B7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回68線A1 | 23KV回68線 R相AMP | FEEDER | D14/22/JJ68/I_R |  |  |  | CDC | 214 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回68線 | 回68線 |  | 回68線A2 | [17 empty] | 2-B8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回68線A2 | 23KV回68線 S相AMP | FEEDER | D14/22/JJ68/I_S |  |  |  | CDC | 215 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回68線 | 回68線 |  | 回68線A3 | [17 empty] | 2-B9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回68線A3 | 23KV回68線 T相AMP | FEEDER | D14/22/JJ68/I_T |  |  |  | CDC | 216 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回68線 | 回68線 |  | 回68線A0 | [17 empty] | 2-BA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回68線A0 | 23KV回68線 N相AMP | FEEDER | D14/22/JJ68/I_N |  |  |  | CDC | 217 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回69線 | 回69線 |  | 回69線KVAR | [17 empty] | 2-BC | [5 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回69線KVAR | 23KV回69線 KVAR | FEEDER | D14/22/JJ69/KVAR |  |  |  | CDC | 218 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回69線 | 回69線 |  | 回69線A1 | [17 empty] | 2-BD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回69線A1 | 23KV回69線 R相AMP | FEEDER | D14/22/JJ69/I_R |  |  |  | CDC | 219 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回69線 | 回69線 |  | 回69線A2 | [17 empty] | 2-BE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回69線A2 | 23KV回69線 S相AMP | FEEDER | D14/22/JJ69/I_S |  |  |  | CDC | 220 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回69線 | 回69線 |  | 回69線A3 | [17 empty] | 2-BF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回69線A3 | 23KV回69線 T相AMP | FEEDER | D14/22/JJ69/I_T |  |  |  | CDC | 221 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回69線 | 回69線 |  | 回69線A0 | [17 empty] | 2-C2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回69線A0 | 23KV回69線 N相AMP | FEEDER | D14/22/JJ69/I_N |  |  |  | CDC | 222 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回70線 | 回70線 |  | 回70線KVAR | [17 empty] | 2-C4 | [5 empty] | KVAR_-18000_18000(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回70線KVAR | 23KV回70線 KVAR | FEEDER | D14/22/JJ70/KVAR |  |  |  | CDC | 223 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 18.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回70線 | 回70線 |  | 回70線A1 | [17 empty] | 2-C5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回70線A1 | 23KV回70線 R相AMP | FEEDER | D14/22/JJ70/I_R |  |  |  | CDC | 224 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回70線 | 回70線 |  | 回70線A2 | [17 empty] | 2-C6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回70線A2 | 23KV回70線 S相AMP | FEEDER | D14/22/JJ70/I_S |  |  |  | CDC | 225 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回70線 | 回70線 |  | 回70線A3 | [17 empty] | 2-C7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回70線A3 | 23KV回70線 T相AMP | FEEDER | D14/22/JJ70/I_T |  |  |  | CDC | 226 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | 回70線 | 回70線 |  | 回70線A0 | [17 empty] | 2-C8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS2_1 | [8 empty] | 北回DS.回70線A0 | 23KV回70線 N相AMP | FEEDER | D14/22/JJ70/I_N |  |  |  | CDC | 227 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 0 |  | 1500TIE | 1500TIE |  | I | [17 empty] | 1-98 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.1500TIE_AMP | 1500TIE AMP | TIE | D14/161/1500/I_R |  |  |  | CDC | 228 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | _100 | 100 |  | I_R | [17 empty] | 1-D3 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.11KV_100_A1 | 11KV 100 R相AMP | TIE | D14/11/100/I_R |  |  |  | CDC | 229 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | _100 | 100 |  | I_S | [17 empty] | 1-D4 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.11KV_100_A2 | 11KV 100 S相AMP | TIE | D14/11/100/I_S |  |  |  | CDC | 230 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 11 | 11kV | _100 | 100 |  | I_T | [17 empty] | 1-D5 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.11KV_100_A3 | 11KV 100 T相AMP | TIE | D14/11/100/I_T |  |  |  | CDC | 231 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | _200 | 200 |  | I_R | [17 empty] | 1-FA | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.23KV_200_A1 | 23KV 200 R相AMP | TIE | D14/22/200/I_R |  |  |  | CDC | 232 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | _200 | 200 |  | I_S | [17 empty] | 1-FB | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.23KV_200_A2 | 23KV 200 S相AMP | TIE | D14/22/200/I_S |  |  |  | CDC | 233 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 22 | 22kV | _200 | 200 |  | I_T | [17 empty] | 1-FC | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.23KV_200_A3 | 23KV 200 T相AMP | TIE | D14/22/200/I_T |  |  |  | CDC | 234 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D14 | 北回DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MW | [17 empty] | 1-AE | [5 empty] | MW_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | D14/11/310/KW |  |  |  | CDC | 235 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D14 | 北回DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVAR | [17 empty] | 1-AF | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | D14/11/310/KVAR |  |  |  | CDC | 236 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D14 | 北回DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_R | [17 empty] | 1-B0 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | D14/11/310/I_R |  |  |  | CDC | 237 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D14 | 北回DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_S | [17 empty] | 1-B1 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | D14/11/310/I_S |  |  |  | CDC | 238 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D14 | 北回DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_T | [17 empty] | 1-B2 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | D14/11/310/I_T |  |  |  | CDC | 239 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D14 | 北回DS | 0 |  | 1DTR | #1DTR |  | OilTemp | [17 empty] | 1-9B | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.#1DTR_OIL | #1DTR 油溫 | MTR | D14//1DTR/OilTemp |  |  |  | CDC | 240 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D14 | 北回DS | 0 |  | 1DTR(A) | #1DTR(A) |  | CoilTemp | [17 empty] | 1-9C | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | D14//1DTR(A)/CoilTemp |  |  |  | CDC | 241 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D14 | 北回DS | 0 |  | 1DTR(A) | #1DTR(A) |  | TapPosMv | [17 empty] | 1-99 |  | 1-5C |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 北回DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | D14//1DTR(A)/TapPosMv |  |  |  | CDC | 242 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D14 | 北回DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MW | [17 empty] | 1-D7 | [5 empty] | MW_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | D14/22/320/KW |  |  |  | CDC | 243 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D14 | 北回DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVAR | [17 empty] | 1-D8 | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | D14/22/320/KVAR |  |  |  | CDC | 244 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D14 | 北回DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_R | [17 empty] | 1-D9 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | D14/22/320/I_R |  |  |  | CDC | 245 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D14 | 北回DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_S | [17 empty] | 1-DA | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | D14/22/320/I_S |  |  |  | CDC | 246 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D14 | 北回DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_T | [17 empty] | 1-DB | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | D14/22/320/I_T |  |  |  | CDC | 247 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D14 | 北回DS | 0 |  | 1DTR(B) | #1DTR(B) |  | CoilTemp | [17 empty] | 1-9D | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | D14//1DTR(B)/CoilTemp |  |  |  | CDC | 248 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D14 | 北回DS | 0 |  | 1DTR(B) | #1DTR(B) |  | TapPosMv | [17 empty] | 1-9A |  | 1-5E |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 北回DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | D14//1DTR(B)/TapPosMv |  |  |  | CDC | 249 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D14 | 北回DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MW | [17 empty] | 1-FE | [5 empty] | MW_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | D14/11/330/KW |  |  |  | CDC | 250 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D14 | 北回DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVAR | [17 empty] | 1-FF | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | D14/11/330/KVAR |  |  |  | CDC | 251 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D14 | 北回DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_R | [17 empty] | 2-82 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | D14/11/330/I_R |  |  |  | CDC | 252 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D14 | 北回DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_S | [17 empty] | 2-83 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | D14/11/330/I_S |  |  |  | CDC | 253 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D14 | 北回DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_T | [17 empty] | 2-84 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | D14/11/330/I_T |  |  |  | CDC | 254 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D14 | 北回DS | 0 |  | 2DTR | #2DTR |  | OilTemp | [17 empty] | 1-A0 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.#2DTR_OIL | #2DTR 油溫 | MTR | D14//2DTR/OilTemp |  |  |  | CDC | 255 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D14 | 北回DS | 0 |  | 2DTR(A) | #2DTR(A) |  | CoilTemp | [17 empty] | 1-A1 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | D14//2DTR(A)/CoilTemp |  |  |  | CDC | 256 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D14 | 北回DS | 0 |  | 2DTR(A) | #2DTR(A) |  | TapPosMv | [17 empty] | 1-9E |  | 1-60 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 北回DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | D14//2DTR(A)/TapPosMv |  |  |  | CDC | 257 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D14 | 北回DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MW | [17 empty] | 2-A4 | [5 empty] | MW_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | D14/22/340/KW |  |  |  | CDC | 258 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D14 | 北回DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVAR | [17 empty] | 2-A5 | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | D14/22/340/KVAR |  |  |  | CDC | 259 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D14 | 北回DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_R | [17 empty] | 2-A6 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | D14/22/340/I_R |  |  |  | CDC | 260 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D14 | 北回DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_S | [17 empty] | 2-A7 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | D14/22/340/I_S |  |  |  | CDC | 261 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D14 | 北回DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_T | [17 empty] | 2-A8 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | D14/22/340/I_T |  |  |  | CDC | 262 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D14 | 北回DS | 0 |  | 2DTR(B) | #2DTR(B) |  | CoilTemp | [17 empty] | 1-A2 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | D14//2DTR(B)/CoilTemp |  |  |  | CDC | 263 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D14 | 北回DS | 0 |  | 2DTR(B) | #2DTR(B) |  | TapPosMv | [17 empty] | 1-9F |  | 1-62 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 北回DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | D14//2DTR(B)/TapPosMv |  |  |  | CDC | 264 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D14 | 北回DS | 0 |  | AI | AI90%參考點 |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.AI_ADCH1 | AI90%參考點 ADCH1 | OTHER | D14/0/RTU/ADCH1 |  |  |  | CDC | 265 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D14 | 北回DS | 0 |  | AI | AI90%參考點 |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.AI_ADCH2 | AI90%參考點 ADCH2 | OTHER | D14/0/RTU/ADCH2 |  |  |  | CDC | 266 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D14 | 北回DS | 0 |  | AI | AI90%參考點 |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.AI_ADCH3 | AI90%參考點 ADCH3 | OTHER | D14/0/RTU/ADCH3 |  |  |  | CDC | 267 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D14 | 北回DS | 0 |  | AI | AI90%參考點 |  | ADCH4 | [17 empty] | 2-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.AI_ADCH4 | AI90%參考點 ADCH4 | OTHER | D14/0/RTU/ADCH4 |  |  |  | CDC | 268 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D14 | 北回DS | 0 |  | AI | AI10%參考點 |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.AI_ADCL1 | AI10%參考點 ADCL1 | OTHER | D14/0/RTU/ADCL1 |  |  |  | CDC | 269 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D14 | 北回DS | 0 |  | AI | AI10%參考點 |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.AI_ADCL2 | AI10%參考點 ADCL2 | OTHER | D14/0/RTU/ADCL2 |  |  |  | CDC | 270 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D14 | 北回DS | 0 |  | AI | AI10%參考點 |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.AI_ADCL3 | AI10%參考點 ADCL3 | OTHER | D14/0/RTU/ADCL3 |  |  |  | CDC | 271 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D14 | 北回DS | 0 |  | AI | AI10%參考點 |  | ADCL4 | [17 empty] | 2-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.AI_ADCL4 | AI10%參考點 ADCL4 | OTHER | D14/0/RTU/ADCL4 |  |  |  | CDC | 272 | GENERICAIPoint | DS045_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D14 | 北回DS | 161 | 161kV | 1510LPD | 仁愛北回一路(1510) |  | V | [17 empty] | 1-94 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.1510LPD_KV | 仁愛北回一路(1510) LPD KV | LINE161 | D14/161/1510/V |  |  |  | CDC | 273 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D14 | 北回DS | 161 | 161kV | 1520LPD | 仁愛北回二路(1520) |  | V | [17 empty] | 1-95 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.1520LPD_KV | 仁愛北回二路(1520) LPD KV | LINE161 | D14/161/1520/V |  |  |  | CDC | 274 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D14 | 北回DS | 161 | 161kV | 1530LPD | 北回太鐵紅線(1530) |  | V | [17 empty] | 1-96 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.1530LPD_KV | 北回太鐵紅線(1530) LPD KV | LINE161 | D14/161/1530/V |  |  |  | CDC | 275 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D14 | 北回DS | 161 | 161kV | 1540LPD | 北回太鐵白線(1540) |  | V | [17 empty] | 1-97 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.1540LPD_KV | 北回太鐵白線(1540) LPD KV | LINE161 | D14/161/1540/V |  |  |  | CDC | 276 | GENERICAIPoint | DS045_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D14 | 北回DS | 0 |  |  |  |  | DCV_N | [17 empty] | 3-C9 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.直流N電源電壓 | 直流N電源電壓 | OTHER | D14/0/StaDev/DCV_N |  |  |  | CDC | 277 | GENERICAIPoint | DS045_L3 | CDC2_AI |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D14 | 北回DS | 0 |  |  |  |  | DCV_P | [17 empty] | 3-C8 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 北回DS.直流P電源電壓 | 直流P電源電壓 | OTHER | D14/0/StaDev/DCV_P |  |  |  | CDC | 278 | GENERICAIPoint | DS045_L3 | CDC2_AI |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛北回一路(1510) |  | PHA | [17 empty] | 1-00-03 | [7 empty] | 161KV_N | [8 empty] | 北回DS.1510_PHA | 仁愛北回一路(1510) 相間RY | LINE161 | D14/161/1510/PHA |  |  |  | CDC | 279 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛北回一路(1510) |  | GDA | [17 empty] | 1-00-04 | [7 empty] | 161KV_N | [8 empty] | 北回DS.1510_GDA | 仁愛北回一路(1510) 接地RY | LINE161 | D14/161/1510/GDA |  |  |  | CDC | 280 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛北回一路(1510) |  | 87UL | [17 empty] | 1-30-02 |  | 1-45 | [5 empty] | ADCS_N | [8 empty] | 北回DS.1510_87UL | 仁愛北回一路(1510) 87RY U/L | LINE161 | D14/161/1510/87UL |  |  |  | CDC | 281 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛北回一路(1510) |  | CB | [17 empty] | 1-00-00 |  | 1-01 | [5 empty] | 161KV_N | [8 empty] | 北回DS.1510_CB | 1510(仁愛北回一路) CB | LINE161 | D14/161/1510/CB |  |  |  | CDC | 282 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛北回一路(1510) |  | 79UL | [17 empty] | 1-30-04 |  | 1-46 | [5 empty] | ADCS_N | [8 empty] | 北回DS.1510_79UL | 仁愛北回一路(1510) 79RY U/L | LINE161 | D14/161/1510/79UL |  |  |  | CDC | 283 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛北回一路(1510) |  | DS1 | 1511 | [16 empty] | 1-38-00 | 1-38-01 | 1-6F | [5 empty] | ADCS_N | [8 empty] | 北回DS.1511_DS | 1511(仁愛北回一路) DS | LINE161 | D14/161/1510/DS1 |  |  |  | CDC | 284 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛北回一路(1510) |  | DS2 | 1512 | [16 empty] | 1-38-02 | 1-38-03 | 1-70 | [5 empty] | ADCS_N | [8 empty] | 北回DS.1512_DS | 1512(仁愛北回一路) DS | LINE161 | D14/161/1510/DS2 |  |  |  | CDC | 285 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛北回一路(1510) |  | DS3 | 1513 | [16 empty] | 1-38-04 | 1-38-05 | 1-71 | [5 empty] | ADCS_N | [8 empty] | 北回DS.1513_DS | 1513(仁愛北回一路) DS | LINE161 | D14/161/1510/DS3 |  |  |  | CDC | 286 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛北回一路(1510) |  | E3 | 1513E | [16 empty] | 1-38-06 | 1-38-07 | 1-72 | [5 empty] | ADCS_N | [8 empty] | 北回DS.1513E_ES | 1513E(仁愛北回一路) ES | LINE161 |  |  |  |  | CDC | 287 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛北回二路(1520) |  | PHA | [17 empty] | 1-01-00 | [7 empty] | 161KV_N | [8 empty] | 北回DS.1520_PHA | 仁愛北回二路(1520) 相間RY | LINE161 | D14/161/1520/PHA |  |  |  | CDC | 288 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛北回二路(1520) |  | GDA | [17 empty] | 1-01-01 | [7 empty] | 161KV_N | [8 empty] | 北回DS.1520_GDA | 仁愛北回二路(1520) 接地RY | LINE161 | D14/161/1520/GDA |  |  |  | CDC | 289 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛北回二路(1520) |  | 87UL | [17 empty] | 1-30-05 |  | 1-47 | [5 empty] | ADCS_N | [8 empty] | 北回DS.1520_87UL | 仁愛北回二路(1520) 87RY U/L | LINE161 | D14/161/1520/87UL |  |  |  | CDC | 290 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛北回二路(1520) |  | CB | [17 empty] | 1-00-05 |  | 1-02 | [5 empty] | 161KV_N | [8 empty] | 北回DS.1520_CB | 1520(仁愛北回二路) CB | LINE161 | D14/161/1520/CB |  |  |  | CDC | 291 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛北回二路(1520) |  | 79UL | [17 empty] | 1-30-07 |  | 1-48 | [5 empty] | ADCS_N | [8 empty] | 北回DS.1520_79UL | 仁愛北回二路(1520) 79RY U/L | LINE161 | D14/161/1520/79UL |  |  |  | CDC | 292 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛北回二路(1520) |  | DS1 | 1521 | [16 empty] | 1-38-08 | 1-38-09 | 1-73 | [5 empty] | ADCS_N | [8 empty] | 北回DS.1521_DS | 1521(仁愛北回二路) DS | LINE161 | D14/161/1520/DS1 |  |  |  | CDC | 293 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛北回二路(1520) |  | DS2 | 1522 | [16 empty] | 1-38-10 | 1-38-11 | 1-74 | [5 empty] | ADCS_N | [8 empty] | 北回DS.1522_DS | 1522(仁愛北回二路) DS | LINE161 | D14/161/1520/DS2 |  |  |  | CDC | 294 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛北回二路(1520) |  | DS3 | 1523 | [16 empty] | 1-38-12 | 1-38-13 | 1-75 | [5 empty] | ADCS_N | [8 empty] | 北回DS.1523_DS | 1523(仁愛北回二路) DS | LINE161 | D14/161/1520/DS3 |  |  |  | CDC | 295 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛北回二路(1520) |  | E3 | 1523E | [16 empty] | 1-38-14 | 1-38-15 | 1-76 | [5 empty] | ADCS_N | [8 empty] | 北回DS.1523E_ES | 1523E(仁愛北回二路) ES | LINE161 |  |  |  |  | CDC | 296 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D14 | 北回DS | 161 | 161kV | 1530 | 北回太鐵紅線(1530) |  | PHA | [17 empty] | 1-01-05 | [7 empty] | 161KV_N | [8 empty] | 北回DS.1530_PHA | 北回太鐵紅線(1530) 相間RY | LINE161 | D14/161/1530/PHA |  |  |  | CDC | 297 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1530 | 北回太鐵紅線(1530) |  | GDA | [17 empty] | 1-01-06 | [7 empty] | 161KV_N | [8 empty] | 北回DS.1530_GDA | 北回太鐵紅線(1530) 接地RY | LINE161 | D14/161/1530/GDA |  |  |  | CDC | 298 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1530 | 北回太鐵紅線(1530) |  | 87UL | [17 empty] | 1-30-08 |  | 1-49 | [5 empty] | ADCS_N | [8 empty] | 北回DS.1530_87UL | 北回太鐵紅線(1530) 87RY U/L | LINE161 | D14/161/1530/87UL |  |  |  | CDC | 299 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D14 | 北回DS | 161 | 161kV | 1530 | 北回太鐵紅線(1530) |  | CB | [17 empty] | 1-01-02 |  | 1-03 | [5 empty] | 161KV_N | [8 empty] | 北回DS.1530_CB | 1530(北回太鐵紅線) CB | LINE161 | D14/161/1530/CB |  |  |  | CDC | 300 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 161 | 161kV | 1530 | 北回太鐵紅線(1530) |  | 79UL | [17 empty] | 1-30-10 |  | 1-4A | [5 empty] | ADCS_N | [8 empty] | 北回DS.1530_79UL | 北回太鐵紅線(1530) 79RY U/L | LINE161 | D14/161/1530/79UL |  |  |  | CDC | 301 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D14 | 北回DS | 161 | 161kV | 1530 | 北回太鐵紅線(1530) |  | DS1 | 1531 | [16 empty] | 1-39-00 | 1-39-01 | 1-77 | [5 empty] | ADCS_N | [8 empty] | 北回DS.1531_DS | 1531(北回太鐵紅線) DS | LINE161 | D14/161/1530/DS1 |  |  |  | CDC | 302 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D14 | 北回DS | 161 | 161kV | 1530 | 北回太鐵紅線(1530) |  | DS2 | 1532 | [16 empty] | 1-39-02 | 1-39-03 | 1-78 | [5 empty] | ADCS_N | [8 empty] | 北回DS.1532_DS | 1532(北回太鐵紅線) DS | LINE161 | D14/161/1530/DS2 |  |  |  | CDC | 303 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D14 | 北回DS | 161 | 161kV | 1530 | 北回太鐵紅線(1530) |  | DS3 | 1533 | [16 empty] | 1-39-04 | 1-39-05 | 1-79 | [5 empty] | ADCS_N | [8 empty] | 北回DS.1533_DS | 1533(北回太鐵紅線) DS | LINE161 | D14/161/1530/DS3 |  |  |  | CDC | 304 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D14 | 北回DS | 161 | 161kV | 1530 | 北回太鐵紅線(1530) |  | E3 | 1533E | [16 empty] | 1-39-06 | 1-39-07 | 1-7A | [5 empty] | ADCS_N | [8 empty] | 北回DS.1533E_ES | 1533E(北回太鐵紅線) ES | LINE161 |  |  |  |  | CDC | 305 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D14 | 北回DS | 161 | 161kV | 1540 | 北回太鐵白線(1540) |  | PHA | [17 empty] | 1-02-02 | [7 empty] | 161KV_N | [8 empty] | 北回DS.1540_PHA | 北回太鐵白線(1540) 相間RY | LINE161 | D14/161/1540/PHA |  |  |  | CDC | 306 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1540 | 北回太鐵白線(1540) |  | GDA | [17 empty] | 1-02-03 | [7 empty] | 161KV_N | [8 empty] | 北回DS.1540_GDA | 北回太鐵白線(1540) 接地RY | LINE161 | D14/161/1540/GDA |  |  |  | CDC | 307 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1540 | 北回太鐵白線(1540) |  | 87UL | [17 empty] | 1-30-11 |  | 1-4B | [5 empty] | ADCS_N | [8 empty] | 北回DS.1540_87UL | 北回太鐵白線(1540) 87RY U/L | LINE161 | D14/161/1540/87UL |  |  |  | CDC | 308 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D14 | 北回DS | 161 | 161kV | 1540 | 北回太鐵白線(1540) |  | CB | [17 empty] | 1-01-07 |  | 1-04 | [5 empty] | 161KV_N | [8 empty] | 北回DS.1540_CB | 1540(北回太鐵白線) CB | LINE161 | D14/161/1540/CB |  |  |  | CDC | 309 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 161 | 161kV | 1540 | 北回太鐵白線(1540) |  | 79UL | [17 empty] | 1-30-13 |  | 1-4C | [5 empty] | ADCS_N | [8 empty] | 北回DS.1540_79UL | 北回太鐵白線(1540) 79RY U/L | LINE161 | D14/161/1540/79UL |  |  |  | CDC | 310 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D14 | 北回DS | 161 | 161kV | 1540 | 北回太鐵白線(1540) |  | DS1 | 1541 | [16 empty] | 1-39-08 | 1-39-09 | 1-7B | [5 empty] | ADCS_N | [8 empty] | 北回DS.1541_DS | 1541(北回太鐵白線) DS | LINE161 | D14/161/1540/DS1 |  |  |  | CDC | 311 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D14 | 北回DS | 161 | 161kV | 1540 | 北回太鐵白線(1540) |  | DS2 | 1542 | [16 empty] | 1-39-10 | 1-39-11 | 1-7C | [5 empty] | ADCS_N | [8 empty] | 北回DS.1542_DS | 1542(北回太鐵白線) DS | LINE161 | D14/161/1540/DS2 |  |  |  | CDC | 312 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D14 | 北回DS | 161 | 161kV | 1540 | 北回太鐵白線(1540) |  | DS3 | 1543 | [16 empty] | 1-39-12 | 1-39-13 | 1-7D | [5 empty] | ADCS_N | [8 empty] | 北回DS.1543_DS | 1543(北回太鐵白線) DS | LINE161 | D14/161/1540/DS3 |  |  |  | CDC | 313 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D14 | 北回DS | 161 | 161kV | 1540 | 北回太鐵白線(1540) |  | E3 | 1543E | [16 empty] | 1-39-14 | 1-39-15 | 1-7E | [5 empty] | ADCS_N | [8 empty] | 北回DS.1543E_ES | 1543E(北回太鐵白線) ES | LINE161 |  |  |  |  | CDC | 314 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D14 | 北回DS | 11 | 11kV | JJ21 | 回21線(JJ21) |  | PHA | [17 empty] | 1-14-07 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ21_PHA | 11KV回21線(JJ21) 相間RY | FEEDER | D14/11/JJ21/PHA |  |  |  | CDC | 315 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ21 | 回21線(JJ21) |  | GDA | [17 empty] | 1-15-00 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ21_GDA | 11KV回21線(JJ21) 接地RY | FEEDER | D14/11/JJ21/GDA |  |  |  | CDC | 316 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ21 | 回21線(JJ21) 79RY |  | 79UL | [17 empty] | 2-30-00 |  | 2-56 | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ21_79UL | 11KV回21線(JJ21) 79RY U/L | FEEDER | D14/11/JJ21/79UL |  |  |  | CDC | 317 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D14 | 北回DS | 11 | 11kV | JJ21_LCO | 回21線(JJ21) LCO |  | TapPosMv | [17 empty] | 2-30-01 |  | 2-57 | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ21_LCO_TAP | 11KV回21線(JJ21) LCO TAP | FEEDER |  |  |  |  | CDC | 318 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D14 | 北回DS | 11 | 11kV | JJ21 | JJ21(11KV回21線) |  | CB | [17 empty] | 1-14-06 |  | 1-13 | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ21_CB | JJ21(11KV回21線) CB | FEEDER | D14/11/JJ21/CB |  |  |  | CDC | 319 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | JJ22 | 回22線(JJ22) |  | PHA | [17 empty] | 1-15-02 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ22_PHA | 11KV回22線(JJ22) 相間RY | FEEDER | D14/11/JJ22/PHA |  |  |  | CDC | 320 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ22 | 回22線(JJ22) |  | GDA | [17 empty] | 1-15-03 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ22_GDA | 11KV回22線(JJ22) 接地RY | FEEDER | D14/11/JJ22/GDA |  |  |  | CDC | 321 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ22 | 回22線(JJ22) 79RY |  | 79UL | [17 empty] | 2-30-02 |  | 2-58 | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ22_79UL | 11KV回22線(JJ22) 79RY U/L | FEEDER | D14/11/JJ22/79UL |  |  |  | CDC | 322 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D14 | 北回DS | 11 | 11kV | JJ22_LCO | 回22線(JJ22) LCO |  | TapPosMv | [17 empty] | 2-30-03 |  | 2-59 | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ22_LCO_TAP | 11KV回22線(JJ22) LCO TAP | FEEDER |  |  |  |  | CDC | 323 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D14 | 北回DS | 11 | 11kV | JJ22 | JJ22(11KV回22線) |  | CB | [17 empty] | 1-15-01 |  | 1-14 | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ22_CB | JJ22(11KV回22線) CB | FEEDER | D14/11/JJ22/CB |  |  |  | CDC | 324 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | JJ23 | 回23線(JJ23) |  | PHA | [17 empty] | 1-15-05 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ23_PHA | 11KV回23線(JJ23) 相間RY | FEEDER | D14/11/JJ23/PHA |  |  |  | CDC | 325 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ23 | 回23線(JJ23) |  | GDA | [17 empty] | 1-15-06 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ23_GDA | 11KV回23線(JJ23) 接地RY | FEEDER | D14/11/JJ23/GDA |  |  |  | CDC | 326 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ23 | 回23線(JJ23) 79RY |  | 79UL | [17 empty] | 2-30-04 |  | 2-5A | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ23_79UL | 11KV回23線(JJ23) 79RY U/L | FEEDER | D14/11/JJ23/79UL |  |  |  | CDC | 327 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D14 | 北回DS | 11 | 11kV | JJ23_LCO | 回23線(JJ23) LCO |  | TapPosMv | [17 empty] | 2-30-05 |  | 2-5B | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ23_LCO_TAP | 11KV回23線(JJ23) LCO TAP | FEEDER |  |  |  |  | CDC | 328 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D14 | 北回DS | 11 | 11kV | JJ23 | JJ23(11KV回23線) |  | CB | [17 empty] | 1-15-04 |  | 1-15 | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ23_CB | JJ23(11KV回23線) CB | FEEDER | D14/11/JJ23/CB |  |  |  | CDC | 329 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | JJ24 | 回24線(JJ24) |  | PHA | [17 empty] | 1-16-00 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ24_PHA | 11KV回24線(JJ24) 相間RY | FEEDER | D14/11/JJ24/PHA |  |  |  | CDC | 330 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ24 | 回24線(JJ24) |  | GDA | [17 empty] | 1-16-01 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ24_GDA | 11KV回24線(JJ24) 接地RY | FEEDER | D14/11/JJ24/GDA |  |  |  | CDC | 331 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ24 | 回24線(JJ24) 79RY |  | 79UL | [17 empty] | 2-30-06 |  | 2-5C | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ24_79UL | 11KV回24線(JJ24) 79RY U/L | FEEDER | D14/11/JJ24/79UL |  |  |  | CDC | 332 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D14 | 北回DS | 11 | 11kV | JJ24_LCO | 回24線(JJ24) LCO |  | TapPosMv | [17 empty] | 2-30-07 |  | 2-5D | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ24_LCO_TAP | 11KV回24線(JJ24) LCO TAP | FEEDER |  |  |  |  | CDC | 333 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D14 | 北回DS | 11 | 11kV | JJ24 | JJ24(11KV回24線) |  | CB | [17 empty] | 1-15-07 |  | 1-16 | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ24_CB | JJ24(11KV回24線) CB | FEEDER | D14/11/JJ24/CB |  |  |  | CDC | 334 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | JJ25 | 回25線(JJ25) |  | PHA | [17 empty] | 1-16-03 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ25_PHA | 11KV回25線(JJ25) 相間RY | FEEDER | D14/11/JJ25/PHA |  |  |  | CDC | 335 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ25 | 回25線(JJ25) |  | GDA | [17 empty] | 1-16-04 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ25_GDA | 11KV回25線(JJ25) 接地RY | FEEDER | D14/11/JJ25/GDA |  |  |  | CDC | 336 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ25 | 回25線(JJ25) 79RY |  | 79UL | [17 empty] | 2-30-08 |  | 2-5E | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ25_79UL | 11KV回25線(JJ25) 79RY U/L | FEEDER | D14/11/JJ25/79UL |  |  |  | CDC | 337 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D14 | 北回DS | 11 | 11kV | JJ25_LCO | 回25線(JJ25) LCO |  | TapPosMv | [17 empty] | 2-30-09 |  | 2-5F | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ25_LCO_TAP | 11KV回25線(JJ25) LCO TAP | FEEDER |  |  |  |  | CDC | 338 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D14 | 北回DS | 11 | 11kV | JJ25 | JJ25(11KV回25線) |  | CB | [17 empty] | 1-16-02 |  | 1-17 | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ25_CB | JJ25(11KV回25線) CB | FEEDER | D14/11/JJ25/CB |  |  |  | CDC | 339 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | JJ31 | 回31線(JJ31) |  | PHA | [17 empty] | 1-1A-01 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ31_PHA | 11KV回31線(JJ31) 相間RY | FEEDER | D14/11/JJ31/PHA |  |  |  | CDC | 340 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ31 | 回31線(JJ31) |  | GDA | [17 empty] | 1-1A-02 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ31_GDA | 11KV回31線(JJ31) 接地RY | FEEDER | D14/11/JJ31/GDA |  |  |  | CDC | 341 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ31 | 回31線(JJ31) 79RY |  | 79UL | [17 empty] | 2-31-04 |  | 2-6A | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ31_79UL | 11KV回31線(JJ31) 79RY U/L | FEEDER | D14/11/JJ31/79UL |  |  |  | CDC | 342 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D14 | 北回DS | 11 | 11kV | JJ31_LCO | 回31線(JJ31) LCO |  | TapPosMv | [17 empty] | 2-31-05 |  | 2-6B | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ31_LCO_TAP | 11KV回31線(JJ31) LCO TAP | FEEDER |  |  |  |  | CDC | 343 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D14 | 北回DS | 11 | 11kV | JJ31 | JJ31(11KV回31線) |  | CB | [17 empty] | 1-1A-00 |  | 1-23 | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ31_CB | JJ31(11KV回31線) CB | FEEDER | D14/11/JJ31/CB |  |  |  | CDC | 344 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | JJ32 | 回32線(JJ32) |  | PHA | [17 empty] | 1-1A-04 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ32_PHA | 11KV回32線(JJ32) 相間RY | FEEDER | D14/11/JJ32/PHA |  |  |  | CDC | 345 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ32 | 回32線(JJ32) |  | GDA | [17 empty] | 1-1A-05 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ32_GDA | 11KV回32線(JJ32) 接地RY | FEEDER | D14/11/JJ32/GDA |  |  |  | CDC | 346 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ32 | 回32線(JJ32) 79RY |  | 79UL | [17 empty] | 2-31-06 |  | 2-6C | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ32_79UL | 11KV回32線(JJ32) 79RY U/L | FEEDER | D14/11/JJ32/79UL |  |  |  | CDC | 347 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D14 | 北回DS | 11 | 11kV | JJ32_LCO | 回32線(JJ32) LCO |  | TapPosMv | [17 empty] | 2-31-07 |  | 2-6D | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ32_LCO_TAP | 11KV回32線(JJ32) LCO TAP | FEEDER |  |  |  |  | CDC | 348 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D14 | 北回DS | 11 | 11kV | JJ32 | JJ32(11KV回32線) |  | CB | [17 empty] | 1-1A-03 |  | 1-24 | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ32_CB | JJ32(11KV回32線) CB | FEEDER | D14/11/JJ32/CB |  |  |  | CDC | 349 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | JJ33 | 回33線(JJ33) |  | PHA | [17 empty] | 1-1A-07 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ33_PHA | 11KV回33線(JJ33) 相間RY | FEEDER | D14/11/JJ33/PHA |  |  |  | CDC | 350 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ33 | 回33線(JJ33) |  | GDA | [17 empty] | 1-1B-00 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ33_GDA | 11KV回33線(JJ33) 接地RY | FEEDER | D14/11/JJ33/GDA |  |  |  | CDC | 351 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ33 | 回33線(JJ33) 79RY |  | 79UL | [17 empty] | 2-31-08 |  | 2-6E | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ33_79UL | 11KV回33線(JJ33) 79RY U/L | FEEDER | D14/11/JJ33/79UL |  |  |  | CDC | 352 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D14 | 北回DS | 11 | 11kV | JJ33_LCO | 回33線(JJ33) LCO |  | TapPosMv | [17 empty] | 2-31-09 |  | 2-6F | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ33_LCO_TAP | 11KV回33線(JJ33) LCO TAP | FEEDER |  |  |  |  | CDC | 353 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D14 | 北回DS | 11 | 11kV | JJ33 | JJ33(11KV回33線) |  | CB | [17 empty] | 1-1A-06 |  | 1-25 | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ33_CB | JJ33(11KV回33線) CB | FEEDER | D14/11/JJ33/CB |  |  |  | CDC | 354 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | JJ34 | 回34線(JJ34) |  | PHA | [17 empty] | 1-1B-02 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ34_PHA | 11KV回34線(JJ34) 相間RY | FEEDER | D14/11/JJ34/PHA |  |  |  | CDC | 355 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ34 | 回34線(JJ34) |  | GDA | [17 empty] | 1-1B-03 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ34_GDA | 11KV回34線(JJ34) 接地RY | FEEDER | D14/11/JJ34/GDA |  |  |  | CDC | 356 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ34 | 回34線(JJ34) 79RY |  | 79UL | [17 empty] | 2-31-10 |  | 2-70 | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ34_79UL | 11KV回34線(JJ34) 79RY U/L | FEEDER | D14/11/JJ34/79UL |  |  |  | CDC | 357 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D14 | 北回DS | 11 | 11kV | JJ34_LCO | 回34線(JJ34) LCO |  | TapPosMv | [17 empty] | 2-31-11 |  | 2-71 | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ34_LCO_TAP | 11KV回34線(JJ34) LCO TAP | FEEDER |  |  |  |  | CDC | 358 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D14 | 北回DS | 11 | 11kV | JJ34 | JJ34(11KV回34線) |  | CB | [17 empty] | 1-1B-01 |  | 1-26 | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ34_CB | JJ34(11KV回34線) CB | FEEDER | D14/11/JJ34/CB |  |  |  | CDC | 359 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | JJ35 | 回35線(JJ35) |  | PHA | [17 empty] | 1-1B-05 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ35_PHA | 11KV回35線(JJ35) 相間RY | FEEDER | D14/11/JJ35/PHA |  |  |  | CDC | 360 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ35 | 回35線(JJ35) |  | GDA | [17 empty] | 1-1B-06 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ35_GDA | 11KV回35線(JJ35) 接地RY | FEEDER | D14/11/JJ35/GDA |  |  |  | CDC | 361 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | JJ35 | 回35線(JJ35) 79RY |  | 79UL | [17 empty] | 2-31-12 |  | 2-72 | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ35_79UL | 11KV回35線(JJ35) 79RY U/L | FEEDER | D14/11/JJ35/79UL |  |  |  | CDC | 362 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D14 | 北回DS | 11 | 11kV | JJ35_LCO | 回35線(JJ35) LCO |  | TapPosMv | [17 empty] | 2-31-13 |  | 2-73 | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ35_LCO_TAP | 11KV回35線(JJ35) LCO TAP | FEEDER |  |  |  |  | CDC | 363 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D14 | 北回DS | 11 | 11kV | JJ35 | JJ35(11KV回35線) |  | CB | [17 empty] | 1-1B-04 |  | 1-27 | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ35_CB | JJ35(11KV回35線) CB | FEEDER | D14/11/JJ35/CB |  |  |  | CDC | 364 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | JJ56 | 回56線(JJ56) |  | PHA | [17 empty] | 1-17-04 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ56_PHA | 23KV回56線(JJ56) 相間RY | FEEDER | D14/22/JJ56/PHA |  |  |  | CDC | 365 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ56 | 回56線(JJ56) |  | GDA | [17 empty] | 1-17-05 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ56_GDA | 23KV回56線(JJ56) 接地RY | FEEDER | D14/22/JJ56/GDA |  |  |  | CDC | 366 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ56 | 回56線(JJ56) 79RY |  | 79UL | [17 empty] | 2-30-10 |  | 2-60 | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ56_79UL | 23KV回56線(JJ56) 79RY U/L | FEEDER | D14/22/JJ56/79UL |  |  |  | CDC | 367 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D14 | 北回DS | 22 | 22kV | JJ56_LCO | 回56線(JJ56) LCO |  | TapPosMv | [17 empty] | 2-30-11 |  | 2-61 | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ56_LCO_TAP | 23KV回56線(JJ56) LCO TAP | FEEDER |  |  |  |  | CDC | 368 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D14 | 北回DS | 22 | 22kV | JJ56 | JJ56(23KV回56線) |  | CB | [17 empty] | 1-17-03 |  | 1-1B | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ56_CB | JJ56(23KV回56線) CB | FEEDER | D14/22/JJ56/CB |  |  |  | CDC | 369 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | JJ57 | 回57線(JJ57) |  | PHA | [17 empty] | 1-17-07 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ57_PHA | 23KV回57線(JJ57) 相間RY | FEEDER | D14/22/JJ57/PHA |  |  |  | CDC | 370 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ57 | 回57線(JJ57) |  | GDA | [17 empty] | 1-18-00 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ57_GDA | 23KV回57線(JJ57) 接地RY | FEEDER | D14/22/JJ57/GDA |  |  |  | CDC | 371 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ57 | 回57線(JJ57) 79RY |  | 79UL | [17 empty] | 2-30-12 |  | 2-62 | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ57_79UL | 23KV回57線(JJ57) 79RY U/L | FEEDER | D14/22/JJ57/79UL |  |  |  | CDC | 372 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D14 | 北回DS | 22 | 22kV | JJ57_LCO | 回57線(JJ57) LCO |  | TapPosMv | [17 empty] | 2-30-13 |  | 2-63 | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ57_LCO_TAP | 23KV回57線(JJ57) LCO TAP | FEEDER |  |  |  |  | CDC | 373 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D14 | 北回DS | 22 | 22kV | JJ57 | JJ57(23KV回57線) |  | CB | [17 empty] | 1-17-06 |  | 1-1C | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ57_CB | JJ57(23KV回57線) CB | FEEDER | D14/22/JJ57/CB |  |  |  | CDC | 374 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | JJ58 | 回58線(JJ58) |  | PHA | [17 empty] | 1-18-02 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ58_PHA | 23KV回58線(JJ58) 相間RY | FEEDER | D14/22/JJ58/PHA |  |  |  | CDC | 375 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ58 | 回58線(JJ58) |  | GDA | [17 empty] | 1-18-03 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ58_GDA | 23KV回58線(JJ58) 接地RY | FEEDER | D14/22/JJ58/GDA |  |  |  | CDC | 376 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ58 | 回58線(JJ58) 79RY |  | 79UL | [17 empty] | 2-30-14 |  | 2-64 | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ58_79UL | 23KV回58線(JJ58) 79RY U/L | FEEDER | D14/22/JJ58/79UL |  |  |  | CDC | 377 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D14 | 北回DS | 22 | 22kV | JJ58_LCO | 回58線(JJ58) LCO |  | TapPosMv | [17 empty] | 2-30-15 |  | 2-65 | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ58_LCO_TAP | 23KV回58線(JJ58) LCO TAP | FEEDER |  |  |  |  | CDC | 378 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D14 | 北回DS | 22 | 22kV | JJ58 | JJ58(23KV回58線) |  | CB | [17 empty] | 1-18-01 |  | 1-1D | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ58_CB | JJ58(23KV回58線) CB | FEEDER | D14/22/JJ58/CB |  |  |  | CDC | 379 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | JJ59 | 回59線(JJ59) |  | PHA | [17 empty] | 1-18-05 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ59_PHA | 23KV回59線(JJ59) 相間RY | FEEDER | D14/22/JJ59/PHA |  |  |  | CDC | 380 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ59 | 回59線(JJ59) |  | GDA | [17 empty] | 1-18-06 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ59_GDA | 23KV回59線(JJ59) 接地RY | FEEDER | D14/22/JJ59/GDA |  |  |  | CDC | 381 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ59 | 回59線(JJ59) 79RY |  | 79UL | [17 empty] | 2-31-00 |  | 2-66 | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ59_79UL | 23KV回59線(JJ59) 79RY U/L | FEEDER | D14/22/JJ59/79UL |  |  |  | CDC | 382 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D14 | 北回DS | 22 | 22kV | JJ59_LCO | 回59線(JJ59) LCO |  | TapPosMv | [17 empty] | 2-31-01 |  | 2-67 | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ59_LCO_TAP | 23KV回59線(JJ59) LCO TAP | FEEDER |  |  |  |  | CDC | 383 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D14 | 北回DS | 22 | 22kV | JJ59 | JJ59(23KV回59線) |  | CB | [17 empty] | 1-18-04 |  | 1-1E | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ59_CB | JJ59(23KV回59線) CB | FEEDER | D14/22/JJ59/CB |  |  |  | CDC | 384 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | JJ60 | 回60線(JJ60) |  | PHA | [17 empty] | 1-19-00 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ60_PHA | 23KV回60線(JJ60) 相間RY | FEEDER | D14/22/JJ60/PHA |  |  |  | CDC | 385 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ60 | 回60線(JJ60) |  | GDA | [17 empty] | 1-19-01 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ60_GDA | 23KV回60線(JJ60) 接地RY | FEEDER | D14/22/JJ60/GDA |  |  |  | CDC | 386 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ60 | 回60線(JJ60) 79RY |  | 79UL | [17 empty] | 2-31-02 |  | 2-68 | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ60_79UL | 23KV回60線(JJ60) 79RY U/L | FEEDER | D14/22/JJ60/79UL |  |  |  | CDC | 387 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D14 | 北回DS | 22 | 22kV | JJ60_LCO | 回60線(JJ60) LCO |  | TapPosMv | [17 empty] | 2-31-03 |  | 2-69 | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ60_LCO_TAP | 23KV回60線(JJ60) LCO TAP | FEEDER |  |  |  |  | CDC | 388 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D14 | 北回DS | 22 | 22kV | JJ60 | JJ60(23KV回60線) |  | CB | [17 empty] | 1-18-07 |  | 1-1F | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ60_CB | JJ60(23KV回60線) CB | FEEDER | D14/22/JJ60/CB |  |  |  | CDC | 389 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | JJ66 | 回66線(JJ66) |  | PHA | [17 empty] | 1-1C-06 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ66_PHA | 23KV回66線(JJ66) 相間RY | FEEDER | D14/22/JJ66/PHA |  |  |  | CDC | 390 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ66 | 回66線(JJ66) |  | GDA | [17 empty] | 1-1C-07 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ66_GDA | 23KV回66線(JJ66) 接地RY | FEEDER | D14/22/JJ66/GDA |  |  |  | CDC | 391 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ66 | 回66線(JJ66) 79RY |  | 79UL | [17 empty] | 2-31-14 |  | 2-74 | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ66_79UL | 23KV回66線(JJ66) 79RY U/L | FEEDER | D14/22/JJ66/79UL |  |  |  | CDC | 392 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D14 | 北回DS | 22 | 22kV | JJ66_LCO | 回66線(JJ66) LCO |  | TapPosMv | [17 empty] | 2-31-15 |  | 2-75 | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ66_LCO_TAP | 23KV回66線(JJ66) LCO TAP | FEEDER |  |  |  |  | CDC | 393 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D14 | 北回DS | 22 | 22kV | JJ66 | JJ66(23KV回66線) |  | CB | [17 empty] | 1-1C-05 |  | 1-2B | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ66_CB | JJ66(23KV回66線) CB | FEEDER | D14/22/JJ66/CB |  |  |  | CDC | 394 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | JJ67 | 回67線(JJ67) |  | PHA | [17 empty] | 1-1D-01 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ67_PHA | 23KV回67線(JJ67) 相間RY | FEEDER | D14/22/JJ67/PHA |  |  |  | CDC | 395 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ67 | 回67線(JJ67) |  | GDA | [17 empty] | 1-1D-02 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ67_GDA | 23KV回67線(JJ67) 接地RY | FEEDER | D14/22/JJ67/GDA |  |  |  | CDC | 396 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ67 | 回67線(JJ67) 79RY |  | 79UL | [17 empty] | 2-32-00 |  | 2-76 | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ67_79UL | 23KV回67線(JJ67) 79RY U/L | FEEDER | D14/22/JJ67/79UL |  |  |  | CDC | 397 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D14 | 北回DS | 22 | 22kV | JJ67_LCO | 回67線(JJ67) LCO |  | TapPosMv | [17 empty] | 2-32-01 |  | 2-77 | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ67_LCO_TAP | 23KV回67線(JJ67) LCO TAP | FEEDER |  |  |  |  | CDC | 398 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D14 | 北回DS | 22 | 22kV | JJ67 | JJ67(23KV回67線) |  | CB | [17 empty] | 1-1D-00 |  | 1-2C | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ67_CB | JJ67(23KV回67線) CB | FEEDER | D14/22/JJ67/CB |  |  |  | CDC | 399 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | JJ68 | 回68線(JJ68) |  | PHA | [17 empty] | 1-1D-04 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ68_PHA | 23KV回68線(JJ68) 相間RY | FEEDER | D14/22/JJ68/PHA |  |  |  | CDC | 400 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ68 | 回68線(JJ68) |  | GDA | [17 empty] | 1-1D-05 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ68_GDA | 23KV回68線(JJ68) 接地RY | FEEDER | D14/22/JJ68/GDA |  |  |  | CDC | 401 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ68 | 回68線(JJ68) 79RY |  | 79UL | [17 empty] | 2-32-02 |  | 2-78 | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ68_79UL | 23KV回68線(JJ68) 79RY U/L | FEEDER | D14/22/JJ68/79UL |  |  |  | CDC | 402 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D14 | 北回DS | 22 | 22kV | JJ68_LCO | 回68線(JJ68) LCO |  | TapPosMv | [17 empty] | 2-32-03 |  | 2-79 | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ68_LCO_TAP | 23KV回68線(JJ68) LCO TAP | FEEDER |  |  |  |  | CDC | 403 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D14 | 北回DS | 22 | 22kV | JJ68 | JJ68(23KV回68線) |  | CB | [17 empty] | 1-1D-03 |  | 1-2D | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ68_CB | JJ68(23KV回68線) CB | FEEDER | D14/22/JJ68/CB |  |  |  | CDC | 404 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | JJ69 | 回69線(JJ69) |  | PHA | [17 empty] | 1-1D-07 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ69_PHA | 23KV回69線(JJ69) 相間RY | FEEDER | D14/22/JJ69/PHA |  |  |  | CDC | 405 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ69 | 回69線(JJ69) |  | GDA | [17 empty] | 1-1E-00 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ69_GDA | 23KV回69線(JJ69) 接地RY | FEEDER | D14/22/JJ69/GDA |  |  |  | CDC | 406 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ69 | 回69線(JJ69) 79RY |  | 79UL | [17 empty] | 2-32-04 |  | 2-7A | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ69_79UL | 23KV回69線(JJ69) 79RY U/L | FEEDER | D14/22/JJ69/79UL |  |  |  | CDC | 407 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D14 | 北回DS | 22 | 22kV | JJ69_LCO | 回69線(JJ69) LCO |  | TapPosMv | [17 empty] | 2-32-05 |  | 2-7B | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ69_LCO_TAP | 23KV回69線(JJ69) LCO TAP | FEEDER |  |  |  |  | CDC | 408 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D14 | 北回DS | 22 | 22kV | JJ69 | JJ69(23KV回69線) |  | CB | [17 empty] | 1-1D-06 |  | 1-2E | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ69_CB | JJ69(23KV回69線) CB | FEEDER | D14/22/JJ69/CB |  |  |  | CDC | 409 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | JJ70 | 回70線(JJ70) |  | PHA | [17 empty] | 1-1E-02 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ70_PHA | 23KV回70線(JJ70) 相間RY | FEEDER | D14/22/JJ70/PHA |  |  |  | CDC | 410 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ70 | 回70線(JJ70) |  | GDA | [17 empty] | 1-1E-03 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ70_GDA | 23KV回70線(JJ70) 接地RY | FEEDER | D14/22/JJ70/GDA |  |  |  | CDC | 411 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | JJ70 | 回70線(JJ70) 79RY |  | 79UL | [17 empty] | 2-32-06 |  | 2-7C | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ70_79UL | 23KV回70線(JJ70) 79RY U/L | FEEDER | D14/22/JJ70/79UL |  |  |  | CDC | 412 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D14 | 北回DS | 22 | 22kV | JJ70_LCO | 回70線(JJ70) LCO |  | TapPosMv | [17 empty] | 2-32-07 |  | 2-7D | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ70_LCO_TAP | 23KV回70線(JJ70) LCO TAP | FEEDER |  |  |  |  | CDC | 413 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D14 | 北回DS | 22 | 22kV | JJ70 | JJ70(23KV回70線) |  | CB | [17 empty] | 1-1E-01 |  | 1-2F | [5 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ70_CB | JJ70(23KV回70線) CB | FEEDER | D14/22/JJ70/CB |  |  |  | CDC | 414 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | 100 | TIE(100) |  | CB | [17 empty] | 1-16-05 |  | 1-18 | [5 empty] | ADCS_N | [8 empty] | 北回DS.100_CB | 100(TIE) CB | TIE | D14/11/100/CB |  |  |  | CDC | 415 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | 100 | TIE(100) |  | 51A | [17 empty] | 1-16-06 | [7 empty] | ADCS_N | [8 empty] | 北回DS.100_51A | 11KV TIE(100) 51RY | TIE | D14/11/100/PHA |  |  |  | CDC | 416 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 100 | TIE(100) |  | 51NA | [17 empty] | 1-16-07 | [7 empty] | ADCS_N | [8 empty] | 北回DS.100_51NA | 11KV TIE(100) 51N RY | TIE | D14/11/100/GDA |  |  |  | CDC | 417 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [17 empty] | 1-06-02 |  | 1-0B | [5 empty] | 161KV_N | [8 empty] | 北回DS.1500_CB | 1500(TIE) CB | TIE | D14/161/1500/CB |  |  |  | CDC | 418 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | 1500 | TIE(1500) |  | 50A | [17 empty] | 1-06-03 | [7 empty] | 161KV_N | [8 empty] | 北回DS.1500_50A | 161KV TIE(1500) 50RY | TIE | D14/161/1500/50A |  |  |  | CDC | 419 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [16 empty] | 1-3D-00 | 1-3D-01 | 2-17 | [5 empty] | ADCS_N | [8 empty] | 北回DS.1501_DS | 1501(TIE) DS | TIE | D14/161/1500/DS1 |  |  |  | CDC | 420 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D14 | 北回DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [16 empty] | 1-3D-02 | 1-3D-03 | 2-18 | [5 empty] | ADCS_N | [8 empty] | 北回DS.1502_DS | 1502(TIE) DS | TIE | D14/161/1500/DS2 |  |  |  | CDC | 421 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D14 | 北回DS | 0 |  | 200 | TIE(200) |  | CB | [17 empty] | 1-19-02 |  | 1-20 | [5 empty] | ADCS_N | [8 empty] | 北回DS.200_CB | 200(TIE) CB | TIE | D14/22/200/CB |  |  |  | CDC | 422 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | 200 | TIE(200) |  | 51A | [17 empty] | 1-19-03 | [7 empty] | ADCS_N | [8 empty] | 北回DS.200_51A | 23KV TIE(200) 51RY | TIE | D14/22/200/PHA |  |  |  | CDC | 423 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 200 | TIE(200) |  | 51NA | [17 empty] | 1-19-04 | [7 empty] | ADCS_N | [8 empty] | 北回DS.200_51NA | 23KV TIE(200) 51N RY | TIE | D14/22/200/GDA |  |  |  | CDC | 424 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 390 | #1SSTR(390) |  | CB | [17 empty] | 1-14-03 |  | 1-12 | [5 empty] | 161KV_N | [8 empty] | 北回DS.390_CB | 390(#1SSTR) CB | OTHER | D14/11/390/CB |  |  |  | CDC | 425 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | 1SSTR | #1SSTR |  | 51A | [17 empty] | 1-14-04 | [7 empty] | 161KV_N | [8 empty] | 北回DS.#1SSTR_51A | #1SSTR 51RY | OTHER | D14/11/390/PHA |  |  |  | CDC | 426 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 1SSTR | #1SSTR |  | 51NA | [17 empty] | 1-14-05 | [7 empty] | 161KV_N | [8 empty] | 北回DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | D14/11/390/GDA |  |  |  | CDC | 427 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 490 | #2SSTR(490) |  | CB | [17 empty] | 1-1C-02 |  | 1-2A | [5 empty] | 161KV_N | [8 empty] | 北回DS.490_CB | 490(#2SSTR) CB | OTHER | D14/22/490/CB |  |  |  | CDC | 428 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | 2SSTR | #2SSTR |  | 51A | [17 empty] | 1-1C-03 | [7 empty] | 161KV_N | [8 empty] | 北回DS.#2SSTR_51A | #2SSTR 51RY | OTHER | D14/22/490/PHA |  |  |  | CDC | 429 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 2SSTR | #2SSTR |  | 51NA | [17 empty] | 1-1C-04 | [7 empty] | 161KV_N | [8 empty] | 北回DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | D14/22/490/GDA |  |  |  | CDC | 430 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB | [17 empty] | 1-07-03 |  | 1-0C | [5 empty] | 161KV_N | [8 empty] | 北回DS.1750_CB | 1750(#1DTR) CB | MTR | D14/161/1750/CB |  |  |  | CDC | 431 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | 310 | #1DTR(310) |  | CB | [17 empty] | 1-08-02 |  | 1-10 | [5 empty] | ADCS_N | [8 empty] | 北回DS.310_CB | 310(#1DTR) CB | MTR | D14/11/310/CB |  |  |  | CDC | 432 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | 320 | #1DTR(320) |  | CB | [17 empty] | 1-08-05 |  | 1-19 | [5 empty] | ADCS_N | [8 empty] | 北回DS.320_CB | 320(#1DTR) CB | MTR | D14/22/320/CB |  |  |  | CDC | 433 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | 1DTR | #1DTR |  | 51A | [17 empty] | 1-08-00 | [7 empty] | 161KV_N | [8 empty] | 北回DS.#1DTR_51A | #1DTR 51RY | MTR | D14//1DTR/PHA |  |  |  | CDC | 434 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 1DTR | #1DTR |  | 51NA | [17 empty] | 1-08-01 | [7 empty] | 161KV_N | [8 empty] | 北回DS.#1DTR_51NA | #1DTR 51N RY | MTR | D14//1DTR/GDA |  |  |  | CDC | 435 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 1DTR | #1DTR |  | 51ZA | [17 empty] | 1-07-06 | [7 empty] | 161KV_N | [8 empty] | 北回DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | D14//1DTR/51ZA |  |  |  | CDC | 436 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 1DTR | #1DTR |  | 87A | [17 empty] | 1-07-04 | [7 empty] | 161KV_N | [8 empty] | 北回DS.#1DTR_87A | #1DTR 87RY | MTR | D14//1DTR/87A |  |  |  | CDC | 437 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 1DTR | #1DTR |  | 87UL | [17 empty] | 1-32-03 | [7 empty] | ADCS_N | [8 empty] | 北回DS.#1DTR_87UL | #1DTR 87RY U/L | MTR |  |  |  |  | CDC | 438 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D14 | 北回DS | 0 |  | 1DTR | #1DTR |  | 96PA | [17 empty] | 1-07-05 | [7 empty] | 161KV_N | [8 empty] | 北回DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | D14//1DTR/96PA |  |  |  | CDC | 439 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 1DTR | #1DTR |  | 96D | [17 empty] | 2-35-04 | [7 empty] | ADCS_N | [8 empty] | 北回DS.#1DTR_96D | #1DTR 96D RY | MTR |  |  |  |  | CDC | 440 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 1DTR | #1DTR |  | 96P | [17 empty] | 2-35-03 | [7 empty] | ADCS_N | [8 empty] | 北回DS.#1DTR_96P | #1DTR 96P RY | MTR |  |  |  |  | CDC | 441 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 1DTR | #1DTR |  | 63Q | [17 empty] | 2-35-02 | [7 empty] | ADCS_N | [8 empty] | 北回DS.#1DTR_63Q | #1DTR 63Q RY | MTR |  |  |  |  | CDC | 442 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 1DTR | #1DTR |  | 96B1 | [17 empty] | 2-35-05 | [7 empty] | ADCS_N | [8 empty] | 北回DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR |  |  |  |  | CDC | 443 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 1DTR | #1DTR |  | 96B2 | [17 empty] | 2-35-06 | [7 empty] | ADCS_N | [8 empty] | 北回DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR |  |  |  |  | CDC | 444 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 1DTR | #1DTR |  | TRA | [17 empty] | 1-32-08 | [7 empty] | ADCS_N | [8 empty] | 北回DS.#1DTR_TRA | #1DTR 重故障 | MTR |  |  |  |  | CDC | 445 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 1DTR | #1DTR |  | TRF | [17 empty] | 1-32-09 | [7 empty] | ADCS_N | [8 empty] | 北回DS.#1DTR_TRF | #1DTR 輕故障 | MTR |  |  |  |  | CDC | 446 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 1DTR(A) | #1DTR(A) |  | SupLocal | [17 empty] | 1-32-04 | [7 empty] | ADCS_N | [8 empty] | 北回DS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR |  |  |  |  | CDC | 447 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D14 | 北回DS | 0 |  | 1DTR(A) | #1DTR(A) |  | A_M | [17 empty] | 1-32-06 |  | 1-5B | [5 empty] | ADCS_N | [8 empty] | 北回DS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR |  |  |  |  | CDC | 448 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D14 | 北回DS | 0 |  | 1DTR(B) | #1DTR(B) |  | SupLocal | [17 empty] | 1-32-05 | [7 empty] | ADCS_N | [8 empty] | 北回DS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR |  |  |  |  | CDC | 449 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D14 | 北回DS | 0 |  | 1DTR(B) | #1DTR(B) |  | A_M | [17 empty] | 1-32-07 |  | 1-5D | [5 empty] | ADCS_N | [8 empty] | 北回DS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR |  |  |  |  | CDC | 450 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D14 | 北回DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 | [16 empty] | 1-3D-04 | 1-3D-05 | 2-19 | [5 empty] | ADCS_N | [8 empty] | 北回DS.1751_DS | 1751(#1DTR) DS | MTR | D14/161/1750/DS1 |  |  |  | CDC | 451 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D14 | 北回DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 | [16 empty] | 1-3D-06 | 1-3D-07 | 2-1A | [5 empty] | ADCS_N | [8 empty] | 北回DS.1752_DS | 1752(#1DTR) DS | MTR | D14/161/1750/DS2 |  |  |  | CDC | 452 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D14 | 北回DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB | [17 empty] | 1-09-00 |  | 1-0D | [5 empty] | 161KV_N | [8 empty] | 北回DS.1760_CB | 1760(#2DTR) CB | MTR | D14/161/1760/CB |  |  |  | CDC | 453 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | 330 | #2DTR(330) |  | CB | [17 empty] | 1-09-07 |  | 1-21 | [5 empty] | ADCS_N | [8 empty] | 北回DS.330_CB | 330(#2DTR) CB | MTR | D14/11/330/CB |  |  |  | CDC | 454 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | 340 | #2DTR(340) |  | CB | [17 empty] | 1-0A-02 |  | 1-28 | [5 empty] | ADCS_N | [8 empty] | 北回DS.340_CB | 340(#2DTR) CB | MTR | D14/22/340/CB |  |  |  | CDC | 455 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | 2DTR | #2DTR |  | 51A | [17 empty] | 1-09-05 | [7 empty] | 161KV_N | [8 empty] | 北回DS.#2DTR_51A | #2DTR 51RY | MTR | D14//2DTR/PHA |  |  |  | CDC | 456 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 2DTR | #2DTR |  | 51NA | [17 empty] | 1-09-06 | [7 empty] | 161KV_N | [8 empty] | 北回DS.#2DTR_51NA | #2DTR 51N RY | MTR | D14//2DTR/GDA |  |  |  | CDC | 457 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 2DTR | #2DTR |  | 51ZA | [17 empty] | 1-09-03 | [7 empty] | 161KV_N | [8 empty] | 北回DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | D14//2DTR/51ZA |  |  |  | CDC | 458 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 2DTR | #2DTR |  | 87A | [17 empty] | 1-09-01 | [7 empty] | 161KV_N | [8 empty] | 北回DS.#2DTR_87A | #2DTR 87RY | MTR | D14//2DTR/87A |  |  |  | CDC | 459 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 2DTR | #2DTR |  | 87UL | [17 empty] | 1-32-10 | [7 empty] | ADCS_N | [8 empty] | 北回DS.#2DTR_87UL | #2DTR 87RY U/L | MTR |  |  |  |  | CDC | 460 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D14 | 北回DS | 0 |  | 2DTR | #2DTR |  | 96PA | [17 empty] | 1-09-02 | [7 empty] | 161KV_N | [8 empty] | 北回DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | D14//2DTR/96PA |  |  |  | CDC | 461 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 2DTR | #2DTR |  | 96D | [17 empty] | 2-35-09 | [7 empty] | ADCS_N | [8 empty] | 北回DS.#2DTR_96D | #2DTR 96D RY | MTR |  |  |  |  | CDC | 462 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 2DTR | #2DTR |  | 96P | [17 empty] | 2-35-08 | [7 empty] | ADCS_N | [8 empty] | 北回DS.#2DTR_96P | #2DTR 96P RY | MTR |  |  |  |  | CDC | 463 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 2DTR | #2DTR |  | 63Q | [17 empty] | 2-35-07 | [7 empty] | ADCS_N | [8 empty] | 北回DS.#2DTR_63Q | #2DTR 63Q RY | MTR |  |  |  |  | CDC | 464 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 2DTR | #2DTR |  | 96B1 | [17 empty] | 2-35-10 | [7 empty] | ADCS_N | [8 empty] | 北回DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR |  |  |  |  | CDC | 465 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 2DTR | #2DTR |  | 96B2 | [17 empty] | 2-35-11 | [7 empty] | ADCS_N | [8 empty] | 北回DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR |  |  |  |  | CDC | 466 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 2DTR | #2DTR |  | TRA | [17 empty] | 1-32-15 | [7 empty] | ADCS_N | [8 empty] | 北回DS.#2DTR_TRA | #2DTR 重故障 | MTR |  |  |  |  | CDC | 467 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 2DTR | #2DTR |  | TRF | [17 empty] | 1-33-00 | [7 empty] | ADCS_N | [8 empty] | 北回DS.#2DTR_TRF | #2DTR 輕故障 | MTR |  |  |  |  | CDC | 468 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 2DTR(A) | #2DTR(A) |  | SupLocal | [17 empty] | 1-32-11 | [7 empty] | ADCS_N | [8 empty] | 北回DS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR |  |  |  |  | CDC | 469 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D14 | 北回DS | 0 |  | 2DTR(A) | #2DTR(A) |  | A_M | [17 empty] | 1-32-13 |  | 1-5F | [5 empty] | ADCS_N | [8 empty] | 北回DS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR |  |  |  |  | CDC | 470 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D14 | 北回DS | 0 |  | 2DTR(B) | #2DTR(B) |  | SupLocal | [17 empty] | 1-32-12 | [7 empty] | ADCS_N | [8 empty] | 北回DS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR |  |  |  |  | CDC | 471 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D14 | 北回DS | 0 |  | 2DTR(B) | #2DTR(B) |  | A_M | [17 empty] | 1-32-14 |  | 1-61 | [5 empty] | ADCS_N | [8 empty] | 北回DS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR |  |  |  |  | CDC | 472 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D14 | 北回DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 | [16 empty] | 1-3D-08 | 1-3D-09 | 2-1B | [5 empty] | ADCS_N | [8 empty] | 北回DS.1761_DS | 1761(#2DTR) DS | MTR | D14/161/1760/DS1 |  |  |  | CDC | 473 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D14 | 北回DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 | [16 empty] | 1-3D-10 | 1-3D-11 | 2-1C | [5 empty] | ADCS_N | [8 empty] | 北回DS.1762_DS | 1762(#2DTR) DS | MTR | D14/161/1760/DS2 |  |  |  | CDC | 474 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D14 | 北回DS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-14-00 |  | 1-11 | [5 empty] | ADCS_N | [8 empty] | 北回DS.210_CB | 210(11KV #1SC) CB | SC | D14/11/210/CB |  |  |  | CDC | 475 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-14-01 | [7 empty] | ADCS_N | [8 empty] | 北回DS.210_SCA | 11KV #1SC 51,51N RY | SC | D14/11/210/SCA |  |  |  | CDC | 476 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-14-02 | [7 empty] | ADCS_N | [8 empty] | 北回DS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | D14/11/210/UVA |  |  |  | CDC | 477 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | 230 | #3SC(230) |  | CB | [17 empty] | 1-19-05 |  | 1-22 | [5 empty] | ADCS_N | [8 empty] | 北回DS.230_CB | 230(11KV #3SC) CB | SC | D14/11/230/CB |  |  |  | CDC | 478 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | 230 | #3SC(230) |  | SCA | [17 empty] | 1-19-06 | [7 empty] | ADCS_N | [8 empty] | 北回DS.230_SCA | 11KV #3SC 51,51N RY | SC | D14/11/230/PHA |  |  |  | CDC | 479 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | 230 | #3SC(230) |  | UVA | [17 empty] | 1-19-07 | [7 empty] | ADCS_N | [8 empty] | 北回DS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | D14/11/230/GDA |  |  |  | CDC | 480 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | 220 | #2SC(220) |  | CB | [17 empty] | 1-17-00 |  | 1-1A | [5 empty] | ADCS_N | [8 empty] | 北回DS.220_CB | 220(23KV #2SC) CB | SC | D14/22/220/CB |  |  |  | CDC | 481 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | 220 | #2SC(220) |  | SCA | [17 empty] | 1-17-01 | [7 empty] | ADCS_N | [8 empty] | 北回DS.220_SCA | 23KV #2SC 51,51N RY | SC | D14/22/220/PHA |  |  |  | CDC | 482 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | 220 | #2SC(220) |  | UVA | [17 empty] | 1-17-02 | [7 empty] | ADCS_N | [8 empty] | 北回DS.220_UVA | 23KV #2SC 27RY(欠壓) | SC | D14/22/220/GDA |  |  |  | CDC | 483 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | 240 | #4SC(240) |  | CB | [17 empty] | 1-1B-07 |  | 1-29 | [5 empty] | ADCS_N | [8 empty] | 北回DS.240_CB | 240(23KV #4SC) CB | SC | D14/22/240/CB |  |  |  | CDC | 484 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 22 | 22kV | 240 | #4SC(240) |  | SCA | [17 empty] | 1-1C-00 | [7 empty] | ADCS_N | [8 empty] | 北回DS.240_SCA | 23KV #4SC 51,51N RY | SC | D14/22/240/PHA |  |  |  | CDC | 485 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | 240 | #4SC(240) |  | UVA | [17 empty] | 1-1C-01 | [7 empty] | ADCS_N | [8 empty] | 北回DS.240_UVA | 23KV #4SC 27RY(欠壓) | SC | D14/22/240/GDA |  |  |  | CDC | 486 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1611BUS | #1BUS |  | VUA | [17 empty] | 1-36-10 | [7 empty] | ADCS_N | [8 empty] | 北回DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS |  |  |  |  | CDC | 487 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1611BUS | #1BUS |  | 87A | [17 empty] | 1-06-04 | [7 empty] | 161KV_N | [8 empty] | 北回DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | D14/161/1BUS/87A |  |  |  | CDC | 488 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1611BUS | #1BUS |  | 87UL | [17 empty] | 1-32-01 |  | 1-65 | [5 empty] | ADCS_N | [8 empty] | 北回DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER |  |  |  |  | CDC | 489 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D14 | 北回DS | 161 | 161kV | 1612BUS | #2BUS |  | VUA | [17 empty] | 1-36-11 | [7 empty] | ADCS_N | [8 empty] | 北回DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS |  |  |  |  | CDC | 490 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1612BUS | #2BUS |  | 87A | [17 empty] | 1-06-05 | [7 empty] | 161KV_N | [8 empty] | 北回DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | D14/161/2BUS/87A |  |  |  | CDC | 491 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1612BUS | #2BUS |  | 87UL | [17 empty] | 1-32-02 |  | 1-66 | [5 empty] | ADCS_N | [8 empty] | 北回DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER |  |  |  |  | CDC | 492 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D14 | 北回DS | 22 | 22kV | 11_ | 11/ |  | CBA | [17 empty] | 1-37-02 | [7 empty] | ADCS_N | [8 empty] | 北回DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER |  |  |  |  | CDC | 493 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | 11_ | 11/ |  | CBF | [17 empty] | 1-37-03 | [7 empty] | ADCS_N | [8 empty] | 北回DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 494 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | _SC | 11/ SC |  | 60A | [17 empty] | 1-36-15 | [7 empty] | ADCS_N | [8 empty] | 北回DS.11KV_SC_60A | 11/23KV SC 60A | OTHER |  |  |  |  | CDC | 495 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV |  |  |  | CBA | [17 empty] | 1-37-00 | [7 empty] | ADCS_N | [8 empty] | 北回DS.161KV_CBA | 161KV斷路器重故障 | OTHER |  |  |  |  | CDC | 496 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV |  |  |  | CBF | [17 empty] | 1-37-01 | [7 empty] | ADCS_N | [8 empty] | 北回DS.161KV_CBF | 161KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 497 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | LINE | LINE |  | RCA | [17 empty] | 1-06-07 | [7 empty] | ADCS_N | [8 empty] | 北回DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | D14/161/ComPoint/RCA |  |  |  | CDC | 498 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | ADCS_N | [8 empty] | 北回DS.TEST_CB | TEST CB | OTHER |  |  |  |  | CDC | 499 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  |  |  |  | Fire1 | [17 empty] | 1-36-07 | [7 empty] | ADCS_N | [8 empty] | 北回DS.火災警報(1) | 火災警報(1)受信總機 | OTHER |  |  |  |  | CDC | 500 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 0 |  |  |  |  | SUBA | [17 empty] | 1-35-03 | [7 empty] | ADCS_N | [8 empty] | 北回DS.其他重故障 | 變電所內其他重故障 | OTHER |  |  |  |  | CDC | 501 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 0 |  |  |  |  | SUBF | [17 empty] | 1-35-04 | [7 empty] | ADCS_N | [8 empty] | 北回DS.其他輕故障 | 變電所內其他輕故障 | OTHER |  |  |  |  | CDC | 502 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 0 |  |  |  |  | ACB1 | [17 empty] | 1-36-01 |  | 1-6C | [5 empty] | ADCS_N | [8 empty] | 北回DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER |  |  |  |  | CDC | 503 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
D14 | 北回DS | 0 |  |  |  |  | ACB2 | [17 empty] | 1-36-02 |  | 1-6D | [5 empty] | ADCS_N | [8 empty] | 北回DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER |  |  |  |  | CDC | 504 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
D14 | 北回DS | 0 |  |  |  |  | ACBA | [17 empty] | 1-35-14 | [7 empty] | ADCS_N | [8 empty] | 北回DS.所內電源ACBA | 所內電源故障警報 | OTHER |  |  |  |  | CDC | 505 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 所內電源開關ACB | 所內電源開關ACB |  | ACBT | [17 empty] | 1-36-03 |  | 1-6E | [5 empty] | ADCS_N | [8 empty] | 北回DS.所內電源ACBT | 所內電源開關ACB TIE | OTHER |  |  |  |  | CDC | 506 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D14 | 北回DS | 0 |  |  |  |  | STUV | [17 empty] | 1-35-15 | [7 empty] | ADCS_N | [8 empty] | 北回DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER |  |  |  |  | CDC | 507 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-35-10 | [7 empty] | ADCS_N | [8 empty] | 北回DS.直流充電機故障 | #1,#2直流充電機故障 | OTHER |  |  |  |  | CDC | 508 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 0 |  |  |  |  | DCA | [17 empty] | 1-35-09 | [7 empty] | ADCS_N | [8 empty] | 北回DS.直流電源DCA | 直流電源故障警報 | OTHER |  |  |  |  | CDC | 509 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 0 |  |  |  |  | DCE | [17 empty] | 1-35-11 | [7 empty] | ADCS_N | [8 empty] | 北回DS.直流電源DCE | 直流電源接地故障警報 | OTHER |  |  |  |  | CDC | 510 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-37-04 | [7 empty] | ADCS_N | [8 empty] | 北回DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER |  |  |  |  | CDC | 511 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 0 |  |  |  |  | CommACF | [17 empty] | 1-37-05 | [7 empty] | ADCS_N | [8 empty] | 北回DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER |  |  |  |  | CDC | 512 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 0 |  |  |  |  | Door1 | [17 empty] | 1-37-15 | [7 empty] | ADCS_N | [8 empty] | 北回DS.無人化門禁(1) | 無人化門禁(1)建築物大門 | OTHER |  |  |  |  | CDC | 513 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  |  |  |  | Lights1 | [17 empty] | 1-36-00 |  | 1-6A | [5 empty] | ADCS_N | [8 empty] | 北回DS.開關場照明(A) | 景觀照明 | OTHER |  |  |  |  | CDC | 514 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D14 | 北回DS | 0 |  | 1500TIE | 1500 |  | 50SA | [17 empty] | 1-32-00 | [7 empty] | ADCS_N | [8 empty] | 北回DS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER |  |  |  |  | CDC | 515 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | TEST/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 1510 | 仁愛北回一路(1510) |  | 25TA | [17 empty] | 1-0D-06 | [7 empty] | ADCS_N | [8 empty] | 北回DS.1510_25TA | 1510 同步校核電驛超時動作 | OTHER | D14/161/1510/25TA |  |  |  | CDC | 516 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 1510 | 仁愛北回一路(1510) |  | DTTA | [17 empty] | 1-10-02 | [7 empty] | ADCS_N | [8 empty] | 北回DS.1510_DTTA | 仁愛北回一路(1510) 遠方遙跳 | OTHER | D14/161/1510/DTTA |  |  |  | CDC | 517 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 1520 | 仁愛北回二路(1520) |  | 25TA | [17 empty] | 1-0E-00 | [7 empty] | ADCS_N | [8 empty] | 北回DS.1520_25TA | 1520 同步校核電驛超時動作 | OTHER | D14/161/1520/25TA |  |  |  | CDC | 518 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 1520 | 仁愛北回二路(1520) |  | DTTA | [17 empty] | 1-10-03 | [7 empty] | ADCS_N | [8 empty] | 北回DS.1520_DTTA | 仁愛北回二路(1520) 遠方遙跳 | OTHER | D14/161/1520/DTTA |  |  |  | CDC | 519 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 1530 | 北回太鐵紅線(1530) |  | 25TA | [17 empty] | 1-0E-02 | [7 empty] | ADCS_N | [8 empty] | 北回DS.1530_25TA | 1530 同步校核電驛超時動作 | OTHER | D14/161/1530/25TA |  |  |  | CDC | 520 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 1530 | 北回太鐵紅線(1530) |  | DTTA | [17 empty] | 1-10-04 | [7 empty] | ADCS_N | [8 empty] | 北回DS.1530_DTTA | 北回太鐵紅線(1530) 遠方遙跳 | OTHER | D14/161/1530/DTTA |  |  |  | CDC | 521 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 1540 | 北回太鐵白線(1540) |  | 25TA | [17 empty] | 1-0E-04 | [7 empty] | ADCS_N | [8 empty] | 北回DS.1540_25TA | 1540 同步校核電驛超時動作 | OTHER | D14/161/1540/25TA |  |  |  | CDC | 522 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 1540 | 北回太鐵白線(1540) |  | DTTA | [17 empty] | 1-10-05 | [7 empty] | ADCS_N | [8 empty] | 北回DS.1540_DTTA | 北回太鐵白線(1540) 遠方遙跳 | OTHER | D14/161/1540/DTTA |  |  |  | CDC | 523 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV |  |  |  | OSCA | [17 empty] | 1-07-01 | [7 empty] | ADCS_N | [8 empty] | 北回DS.161KV_OSCA | 161KV示波器啟動警報 | OTHER | D14/161/ComPoint/OSCA |  |  |  | CDC | 524 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | 210 | #1SC(210) |  | LBS | [17 empty] | 2-05-05 |  | 3-28 | [5 empty] | ADCS_N | [8 empty] | 北回DS.210_LBS | 210(11KV #1SC) LBS | OTHER | D14/11/210/LBS |  |  |  | CDC | 525 | GENERICDIPoint | DS045_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 11 | 11kV | 230 | #3SC(230) |  | LBS | [17 empty] | 2-05-07 |  | 3-2A | [5 empty] | ADCS_N | [8 empty] | 北回DS.230_LBS | 230(11KV #3SC) LBS | OTHER | D14/11/230/LBS |  |  |  | CDC | 526 | GENERICDIPoint | DS045_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | 310 | #1DTR(310) |  | GDA | [17 empty] | 1-08-04 | [7 empty] | ADCS_N | [8 empty] | 北回DS.310_GDA | 310開關箱IED RY GDA | OTHER | D14/11/310/GDA |  |  |  | CDC | 527 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 310 | #1DTR(310) |  | PHA2 | [17 empty] | 2-36-06 | [7 empty] | ADCS_N | [8 empty] | 北回DS.310_PHA2 | #1DTR二次側(310) PHA | OTHER |  |  |  |  | CDC | 528 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 320 | #1DTR(320) |  | GDA | [17 empty] | 1-08-07 | [7 empty] | ADCS_N | [8 empty] | 北回DS.320_GDA | 320開關箱IED RY GDA | OTHER | D14/22/320/GDA |  |  |  | CDC | 529 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 320 | #1DTR(320) |  | PHA2 | [17 empty] | 2-36-07 | [7 empty] | ADCS_N | [8 empty] | 北回DS.320_PHA2 | #1DTR二次側(320) PHA | OTHER |  |  |  |  | CDC | 530 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 330 | #2DTR(330) |  | GDA | [17 empty] | 1-0A-01 | [7 empty] | ADCS_N | [8 empty] | 北回DS.330_GDA | 330開關箱IED RY GDA | OTHER | D14/11/330/GDA |  |  |  | CDC | 531 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 330 | #2DTR(330) |  | PHA2 | [17 empty] | 2-36-08 | [7 empty] | ADCS_N | [8 empty] | 北回DS.330_PHA2 | #2DTR二次側(330) PHA | OTHER |  |  |  |  | CDC | 532 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 340 | #2DTR(340) |  | GDA | [17 empty] | 1-0A-04 | [7 empty] | ADCS_N | [8 empty] | 北回DS.340_GDA | 340開關箱IED RY GDA | OTHER | D14/22/340/GDA |  |  |  | CDC | 533 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 340 | #2DTR(340) |  | PHA2 | [17 empty] | 2-36-09 | [7 empty] | ADCS_N | [8 empty] | 北回DS.340_PHA2 | #2DTR二次側(340) PHA | OTHER |  |  |  |  | CDC | 534 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 0 |  | BUS | BUS |  | SUBA | [17 empty] | 1-36-12 | [7 empty] | ADCS_N | [8 empty] | 北回DS.BPT重故障 | BUS PT BAY重故障 | OTHER |  |  |  |  | CDC | 535 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 0 |  | BUS | BUS |  | SUBF | [17 empty] | 1-36-13 | [7 empty] | ADCS_N | [8 empty] | 北回DS.BPT輕故障 | BUS PT BAY輕故障 | OTHER |  |  |  |  | CDC | 536 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 0 |  |  |  |  | DC電壓過低 | [17 empty] | 1-37-10 | [7 empty] | ADCS_N | [8 empty] | 北回DS.DC電壓過低 | DC電壓過低警報(120V) | OTHER |  |  |  |  | CDC | 537 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 0 |  |  |  |  | DC電壓過高 | [17 empty] | 1-37-11 | [7 empty] | ADCS_N | [8 empty] | 北回DS.DC電壓過高 | DC電壓過高警報(140V) | OTHER |  |  |  |  | CDC | 538 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 0 |  |  |  |  | 水位警報(1) | [17 empty] | 1-35-05 | [7 empty] | ADCS_N | [8 empty] | 北回DS.水位警報(1) | 地下室水位警報(1) | OTHER |  |  |  |  | CDC | 539 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 0 |  |  |  |  | 水位警報(2) | [17 empty] | 1-35-06 | [7 empty] | ADCS_N | [8 empty] | 北回DS.水位警報(2) | 地下室水位警報(2) | OTHER |  |  |  |  | CDC | 540 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 0 |  |  |  |  | 污水幫浦 | [17 empty] | 1-36-09 | [7 empty] | ADCS_N | [8 empty] | 北回DS.污水幫浦 | 污水幫浦故障 | OTHER |  |  |  |  | CDC | 541 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 0 |  |  |  |  | 涵洞排水幫浦 | [17 empty] | 1-36-06 | [7 empty] | ADCS_N | [8 empty] | 北回DS.涵洞排水幫浦 | 涵洞排水幫浦故障 | OTHER |  |  |  |  | CDC | 542 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 0 |  |  |  |  | 揚水幫浦 | [17 empty] | 1-36-08 | [7 empty] | ADCS_N | [8 empty] | 北回DS.揚水幫浦 | 揚水幫浦故障 | OTHER |  |  |  |  | CDC | 543 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛北回一路(1510) |  | 87A | [17 empty] | 1-00-01 | [7 empty] | 161KV_N | [8 empty] | 北回DS.1510_87A | 仁愛北回一路(1510) 87RY | LINE161 | D14/161/1510/87A |  |  |  | CDC | 544 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛北回二路(1520) |  | 87A | [17 empty] | 1-00-06 | [7 empty] | 161KV_N | [8 empty] | 北回DS.1520_87A | 仁愛北回二路(1520) 87RY | LINE161 | D14/161/1520/87A |  |  |  | CDC | 545 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1530 | 北回太鐵紅線(1530) |  | 87A | [17 empty] | 1-01-03 | [7 empty] | 161KV_N | [8 empty] | 北回DS.1530_87A | 北回太鐵紅線(1530) 87RY | LINE161 | D14/161/1530/87A |  |  |  | CDC | 546 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | 1540 | 北回太鐵白線(1540) |  | 87A | [17 empty] | 1-02-00 | [7 empty] | 161KV_N | [8 empty] | 北回DS.1540_87A | 北回太鐵白線(1540) 87RY | LINE161 | D14/161/1540/87A |  |  |  | CDC | 547 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 0 |  |  |  |  | Burglar1 | [17 empty] | 1-36-14 | [7 empty] | ADCS_N | [8 empty] | 北回DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER |  |  |  |  | CDC | 548 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 0 |  |  |  |  | Lights2 | [17 empty] | 1-37-12 |  | 1-6B | [5 empty] | ADCS_N | [8 empty] | 北回DS.開關場照明(B) | 路燈照明 | OTHER |  |  |  |  | CDC | 549 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D14 | 北回DS | 0 |  | 1510 | 仁愛北回一路(1510) |  | 87CFA | [17 empty] | 1-33-15 | [7 empty] | ADCS_N | [8 empty] | 北回DS.1510_87CFA | 仁愛北回一路(1510)87RY通訊故障 | OTHER |  |  |  |  | CDC | 550 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 1510 | 仁愛北回一路(1510) |  | RYFA | [17 empty] | 1-34-00 | [7 empty] | ADCS_N | [8 empty] | 北回DS.1510_RYFA | 仁愛北回一路(1510)數位電驛故障 | OTHER |  |  |  |  | CDC | 551 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 1520 | 仁愛北回二路(1520) |  | 87CFA | [17 empty] | 1-34-01 | [7 empty] | ADCS_N | [8 empty] | 北回DS.1520_87CFA | 仁愛北回二路(1520)87RY通訊故障 | OTHER |  |  |  |  | CDC | 552 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 1520 | 仁愛北回二路(1520) |  | RYFA | [17 empty] | 1-34-02 | [7 empty] | ADCS_N | [8 empty] | 北回DS.1520_RYFA | 仁愛北回二路(1520)數位電驛故障 | OTHER |  |  |  |  | CDC | 553 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 1530 | 北回太鐵紅線(1530) |  | 87CFA | [17 empty] | 1-34-03 | [7 empty] | ADCS_N | [8 empty] | 北回DS.1530_87CFA | 北回太鐵紅線(1530)87RY通訊故障 | OTHER |  |  |  |  | CDC | 554 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 1530 | 北回太鐵紅線(1530) |  | RYFA | [17 empty] | 1-34-04 | [7 empty] | ADCS_N | [8 empty] | 北回DS.1530_RYFA | 北回太鐵紅線(1530)數位電驛故障 | OTHER |  |  |  |  | CDC | 555 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 1540 | 北回太鐵白線(1540) |  | 87CFA | [17 empty] | 1-34-05 | [7 empty] | ADCS_N | [8 empty] | 北回DS.1540_87CFA | 北回太鐵白線(1540)87RY通訊故障 | OTHER |  |  |  |  | CDC | 556 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 1540 | 北回太鐵白線(1540) |  | RYFA | [17 empty] | 1-34-06 | [7 empty] | ADCS_N | [8 empty] | 北回DS.1540_RYFA | 北回太鐵白線(1540)數位電驛故障 | OTHER |  |  |  |  | CDC | 557 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 0 |  |  |  |  | COMMA | [17 empty] | 1-36-05 | [7 empty] | ADCS_N | [8 empty] | 北回DS.COMMA | 通訊處理單元故障 | OTHER |  |  |  |  | CDC | 558 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 0 |  | COMM | 通訊處理單元 |  | SupLocal | [17 empty] | 2-34-09 | [7 empty] | ADCS_N | [8 empty] | 北回DS.COMM_S/L | 通訊處理單元 SUPY/LOCAL | OTHER |  |  |  |  | CDC | 559 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D14 | 北回DS | 0 |  |  |  |  | MCC | [17 empty] | 2-34-12 | [7 empty] | ADCS_N | [8 empty] | 北回DS.MCC故障 | MCC電驛故障 | OTHER |  |  |  |  | CDC | 560 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 0 |  | MODEM | MODEM |  | MODEMA | [17 empty] | 2-34-13 | [7 empty] | ADCS_N | [8 empty] | 北回DS.MODEMA | MODEM POWER FAIL故障 | OTHER |  |  |  |  | CDC | 561 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 0 |  |  |  |  | PMCC | [17 empty] | 2-34-11 | [7 empty] | ADCS_N | [8 empty] | 北回DS.PMCC故障 | PMCC電驛故障 | OTHER |  |  |  |  | CDC | 562 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 0 |  | SCADA | SCADA |  | UPS | [17 empty] | 1-37-09 | [7 empty] | ADCS_N | [8 empty] | 北回DS.SCADA_UPS | SCADA UPS故障 | OTHER |  |  |  |  | CDC | 563 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 0 |  |  |  |  | SCADAA | [17 empty] | 1-36-04 | [7 empty] | ADCS_N | [8 empty] | 北回DS.SCADA故障 | 變電所SCADA故障 | OTHER |  |  |  |  | CDC | 564 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | NORMAL/FAULT | NORMAL
D14 | 北回DS | 0 |  |  |  |  | TCA | [17 empty] | 2-34-10 | [7 empty] | ADCS_N | [8 empty] | 北回DS.TCA | 斷路器跳脫回路故障 | OTHER |  |  |  |  | CDC | 565 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 0 |  |  |  |  | 涵洞水位(1) | [17 empty] | 1-37-13 | [7 empty] | ADCS_N | [8 empty] | 北回DS.涵洞水位(1) | 涵洞水位警報(1) | OTHER |  |  |  |  | CDC | 566 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 0 |  |  |  |  | 涵洞水位(2) | [17 empty] | 1-37-14 | [7 empty] | ADCS_N | [8 empty] | 北回DS.涵洞水位(2) | 涵洞水位警報(2) | OTHER |  |  |  |  | CDC | 567 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 0 |  |  |  |  | 通信機房溫度 | [17 empty] | 1-37-08 | [7 empty] | ADCS_N | [8 empty] | 北回DS.通信機房溫度 | 通訊室或控制室溫度警報 | OTHER |  |  |  |  | CDC | 568 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 0 |  |  |  |  | 集油池警報(1) | [17 empty] | 1-35-07 | [7 empty] | ADCS_N | [8 empty] | 北回DS.集油池警報(1) | 集油池水位警報(1) | OTHER |  |  |  |  | CDC | 569 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 0 |  |  |  |  | 集油池警報(2) | [17 empty] | 1-35-08 | [7 empty] | ADCS_N | [8 empty] | 北回DS.集油池警報(2) | 集油池水位警報(2) | OTHER |  |  |  |  | CDC | 570 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 15B1E | 15B1E |  | BE1 | 15B1E | [16 empty] | 3-3B-12 | 3-3B-13 | [6 empty] | ADCS_N | [8 empty] | 北回DS.15B1E_ES | 15B1E ES | OTHER |  |  |  |  | CDC | 571 | GENERICDIPoint | DS045_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D14 | 北回DS | 0 |  | 15B2E | 15B2E |  | BE2 | 15B2E | [16 empty] | 3-3B-14 | 3-3B-15 | [6 empty] | ADCS_N | [8 empty] | 北回DS.15B2E_ES | 15B2E ES | OTHER |  |  |  |  | CDC | 572 | GENERICDIPoint | DS045_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D14 | 北回DS | 161 | 161kV |  |  |  | OSCF | [17 empty] | 1-07-02 | [7 empty] | ADCS_N | [8 empty] | 北回DS.161KV_OSCF | 161KV示波器故障 | OTHER |  |  |  |  | CDC | 573 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 22 | 22kV | 11_ | 11/ |  | LOA | [17 empty] | 1-07-00 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.11/23KV_LOA | 11/23KV 饋線復閉失敗 | OTHER | D14/22/ComPoint/LOA |  |  |  | CDC | 574 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 0 |  | FEEDER | FEEDER |  | RCA | [17 empty] | 1-0D-01 | [7 empty] | DDCS2_1 | [8 empty] | 北回DS.FEEDER_RCA | 饋線復閉電驛動作 | OTHER |  |  |  |  | CDC | 575 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 310 | #1DTR(310) |  | PHA | [17 empty] | 1-08-03 | [7 empty] | ADCS_N | [8 empty] | 北回DS.310_PHA | 310開關箱IED RY PHA | OTHER | D14/11/310/PHA1 |  |  |  | CDC | 576 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 320 | #1DTR(320) |  | PHA | [17 empty] | 1-08-06 | [7 empty] | ADCS_N | [8 empty] | 北回DS.320_PHA | 320開關箱IED RY PHA | OTHER | D14/22/320/PHA1 |  |  |  | CDC | 577 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 330 | #2DTR(330) |  | PHA | [17 empty] | 1-0A-00 | [7 empty] | ADCS_N | [8 empty] | 北回DS.330_PHA | 330開關箱IED RY PHA | OTHER | D14/11/330/PHA1 |  |  |  | CDC | 578 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 0 |  | 340 | #2DTR(340) |  | PHA | [17 empty] | 1-0A-03 | [7 empty] | ADCS_N | [8 empty] | 北回DS.340_PHA | 340開關箱IED RY PHA | OTHER | D14/22/340/PHA1 |  |  |  | CDC | 579 | GENERICDIPoint | DS045_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D14 | 北回DS | 0 |  |  |  |  | GEN | [17 empty] | 1-37-06 | [7 empty] | ADCS_N | [8 empty] | 北回DS.GEN | 緊急發電機運轉 | OTHER |  |  |  |  | CDC | 580 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D14 | 北回DS | 161 | 161kV | _BUS | BUS |  | 87CTFA | [17 empty] | 2-34-08 | [7 empty] | ADCS_N | [8 empty] | 北回DS.161KV_BUS_CTFA | 161KV BUS 87RY CT回路故障 | OTHER |  |  |  |  | CDC | 581 | GENERICDIPoint | DS045_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 161 | 161kV | _BUS | BUS |  | RYFA | [17 empty] | 1-37-07 | [7 empty] | ADCS_N | [8 empty] | 北回DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER |  |  |  |  | CDC | 582 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D14 | 北回DS | 0 |  | OLTC | OLTC |  | OLTCA | [17 empty] | 1-35-12 | [7 empty] | ADCS_N | [8 empty] | 北回DS.OLTCA | OLTC 15分鐘連動3次 | OTHER |  |  |  |  | CDC | 583 | GENERICDIPoint | DS045_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D14 | 北回DS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 北回DS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 584 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 11 | 11kV | 230_SC | #3SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 北回DS.230_SC_CAP | 11KV#3SC 容量 | SC | [5 empty] | 585 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 22 | 22kV | 220_SC | #2SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 北回DS.220_SC_CAP | 23KV#2SC 容量 | SC | [5 empty] | 586 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 22 | 22kV | 240_SC | #4SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 北回DS.240_SC_CAP | 23KV#4SC 容量 | SC | [5 empty] | 587 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛北回一路(1510) |  | LE0 | 1510LE | [24 empty] | ADCS_N | [8 empty] | 北回DS.1510LE | 1510LE (非取樣點) | LINE161 | D14/161/1510/LE0 |  |  |  |  | 588 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 161 | 161kV | 1510 | 仁愛北回一路(1510) |  | BE0 | 1510BE | [24 empty] | ADCS_N | [8 empty] | 北回DS.1510BE | 1510BE (非取樣點) | LINE161 | D14/161/1510/BE0 |  |  |  |  | 589 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛北回二路(1520) |  | LE0 | 1520LE | [24 empty] | ADCS_N | [8 empty] | 北回DS.1520LE | 1520LE (非取樣點) | LINE161 | D14/161/1520/LE0 |  |  |  |  | 590 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 161 | 161kV | 1520 | 仁愛北回二路(1520) |  | BE0 | 1520BE | [24 empty] | ADCS_N | [8 empty] | 北回DS.1520BE | 1520BE (非取樣點) | LINE161 | D14/161/1520/BE0 |  |  |  |  | 591 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 161 | 161kV | 1530 | 北回太鐵紅線(1530) |  | LE0 | 1530LE | [24 empty] | ADCS_N | [8 empty] | 北回DS.1530LE | 1530LE (非取樣點) | LINE161 | D14/161/1530/LE0 |  |  |  |  | 592 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 161 | 161kV | 1530 | 北回太鐵紅線(1530) |  | BE0 | 1530BE | [24 empty] | ADCS_N | [8 empty] | 北回DS.1530BE | 1530BE (非取樣點) | LINE161 | D14/161/1530/BE0 |  |  |  |  | 593 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 161 | 161kV | 1540 | 北回太鐵白線(1540) |  | LE0 | 1540LE | [24 empty] | ADCS_N | [8 empty] | 北回DS.1540LE | 1540LE (非取樣點) | LINE161 | D14/161/1540/LE0 |  |  |  |  | 594 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 161 | 161kV | 1540 | 北回太鐵白線(1540) |  | BE0 | 1540BE | [24 empty] | ADCS_N | [8 empty] | 北回DS.1540BE | 1540BE (非取樣點) | LINE161 | D14/161/1540/BE0 |  |  |  |  | 595 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | JJ21 | JJ21_DS |  | DS1 | JJ21_DS | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ21_DS | JJ21_DS (非取樣點) | FEEDER | D14/11/JJ21/DS |  |  |  |  | 596 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | JJ21 | JJ21_ES |  | LE0 | JJ21_ES | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ21_ES | JJ21_ES (非取樣點) | FEEDER | D14/11/JJ21/ES |  |  |  |  | 597 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | JJ22 | JJ22_DS |  | DS1 | JJ22_DS | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ22_DS | JJ22_DS (非取樣點) | FEEDER | D14/11/JJ22/DS |  |  |  |  | 598 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | JJ22 | JJ22_ES |  | LE0 | JJ22_ES | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ22_ES | JJ22_ES (非取樣點) | FEEDER | D14/11/JJ22/ES |  |  |  |  | 599 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | JJ23 | JJ23_DS |  | DS1 | JJ23_DS | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ23_DS | JJ23_DS (非取樣點) | FEEDER | D14/11/JJ23/DS |  |  |  |  | 600 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | JJ23 | JJ23_ES |  | LE0 | JJ23_ES | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ23_ES | JJ23_ES (非取樣點) | FEEDER | D14/11/JJ23/ES |  |  |  |  | 601 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | JJ24 | JJ24_DS |  | DS1 | JJ24_DS | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ24_DS | JJ24_DS (非取樣點) | FEEDER | D14/11/JJ24/DS |  |  |  |  | 602 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | JJ24 | JJ24_ES |  | LE0 | JJ24_ES | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ24_ES | JJ24_ES (非取樣點) | FEEDER | D14/11/JJ24/ES |  |  |  |  | 603 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | JJ25 | JJ25_DS |  | DS1 | JJ25_DS | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ25_DS | JJ25_DS (非取樣點) | FEEDER | D14/11/JJ25/DS |  |  |  |  | 604 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | JJ25 | JJ25_ES |  | LE0 | JJ25_ES | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ25_ES | JJ25_ES (非取樣點) | FEEDER | D14/11/JJ25/ES |  |  |  |  | 605 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | JJ31 | JJ31_DS |  | DS1 | JJ31_DS | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ31_DS | JJ31_DS (非取樣點) | FEEDER | D14/11/JJ31/DS |  |  |  |  | 606 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | JJ31 | JJ31_ES |  | LE0 | JJ31_ES | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ31_ES | JJ31_ES (非取樣點) | FEEDER | D14/11/JJ31/ES |  |  |  |  | 607 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | JJ32 | JJ32_DS |  | DS1 | JJ32_DS | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ32_DS | JJ32_DS (非取樣點) | FEEDER | D14/11/JJ32/DS |  |  |  |  | 608 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | JJ32 | JJ32_ES |  | LE0 | JJ32_ES | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ32_ES | JJ32_ES (非取樣點) | FEEDER | D14/11/JJ32/ES |  |  |  |  | 609 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | JJ33 | JJ33_DS |  | DS1 | JJ33_DS | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ33_DS | JJ33_DS (非取樣點) | FEEDER | D14/11/JJ33/DS |  |  |  |  | 610 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | JJ33 | JJ33_ES |  | LE0 | JJ33_ES | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ33_ES | JJ33_ES (非取樣點) | FEEDER | D14/11/JJ33/ES |  |  |  |  | 611 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | JJ34 | JJ34_DS |  | DS1 | JJ34_DS | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ34_DS | JJ34_DS (非取樣點) | FEEDER | D14/11/JJ34/DS |  |  |  |  | 612 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | JJ34 | JJ34_ES |  | LE0 | JJ34_ES | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ34_ES | JJ34_ES (非取樣點) | FEEDER | D14/11/JJ34/ES |  |  |  |  | 613 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | JJ35 | JJ35_DS |  | DS1 | JJ35_DS | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ35_DS | JJ35_DS (非取樣點) | FEEDER | D14/11/JJ35/DS |  |  |  |  | 614 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | JJ35 | JJ35_ES |  | LE0 | JJ35_ES | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ35_ES | JJ35_ES (非取樣點) | FEEDER | D14/11/JJ35/ES |  |  |  |  | 615 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | JJ56 | JJ56_DS |  | DS1 | JJ56_DS | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ56_DS | JJ56_DS (非取樣點) | FEEDER | D14/22/JJ56/DS |  |  |  |  | 616 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | JJ56 | JJ56_ES |  | LE0 | JJ56_ES | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ56_ES | JJ56_ES (非取樣點) | FEEDER | D14/22/JJ56/ES |  |  |  |  | 617 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | JJ57 | JJ57_DS |  | DS1 | JJ57_DS | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ57_DS | JJ57_DS (非取樣點) | FEEDER | D14/22/JJ57/DS |  |  |  |  | 618 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | JJ57 | JJ57_ES |  | LE0 | JJ57_ES | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ57_ES | JJ57_ES (非取樣點) | FEEDER | D14/22/JJ57/ES |  |  |  |  | 619 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | JJ58 | JJ58_DS |  | DS1 | JJ58_DS | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ58_DS | JJ58_DS (非取樣點) | FEEDER | D14/22/JJ58/DS |  |  |  |  | 620 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | JJ58 | JJ58_ES |  | LE0 | JJ58_ES | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ58_ES | JJ58_ES (非取樣點) | FEEDER | D14/22/JJ58/ES |  |  |  |  | 621 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | JJ59 | JJ59_DS |  | DS1 | JJ59_DS | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ59_DS | JJ59_DS (非取樣點) | FEEDER | D14/22/JJ59/DS |  |  |  |  | 622 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | JJ59 | JJ59_ES |  | LE0 | JJ59_ES | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ59_ES | JJ59_ES (非取樣點) | FEEDER | D14/22/JJ59/ES |  |  |  |  | 623 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | JJ60 | JJ60_DS |  | DS1 | JJ60_DS | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ60_DS | JJ60_DS (非取樣點) | FEEDER | D14/22/JJ60/DS |  |  |  |  | 624 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | JJ60 | JJ60_ES |  | LE0 | JJ60_ES | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ60_ES | JJ60_ES (非取樣點) | FEEDER | D14/22/JJ60/ES |  |  |  |  | 625 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | JJ66 | JJ66_DS |  | DS1 | JJ66_DS | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ66_DS | JJ66_DS (非取樣點) | FEEDER | D14/22/JJ66/DS |  |  |  |  | 626 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | JJ66 | JJ66_ES |  | LE0 | JJ66_ES | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ66_ES | JJ66_ES (非取樣點) | FEEDER | D14/22/JJ66/ES |  |  |  |  | 627 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | JJ67 | JJ67_DS |  | DS1 | JJ67_DS | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ67_DS | JJ67_DS (非取樣點) | FEEDER | D14/22/JJ67/DS |  |  |  |  | 628 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | JJ67 | JJ67_ES |  | LE0 | JJ67_ES | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ67_ES | JJ67_ES (非取樣點) | FEEDER | D14/22/JJ67/ES |  |  |  |  | 629 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | JJ68 | JJ68_DS |  | DS1 | JJ68_DS | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ68_DS | JJ68_DS (非取樣點) | FEEDER | D14/22/JJ68/DS |  |  |  |  | 630 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | JJ68 | JJ68_ES |  | LE0 | JJ68_ES | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ68_ES | JJ68_ES (非取樣點) | FEEDER | D14/22/JJ68/ES |  |  |  |  | 631 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | JJ69 | JJ69_DS |  | DS1 | JJ69_DS | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ69_DS | JJ69_DS (非取樣點) | FEEDER | D14/22/JJ69/DS |  |  |  |  | 632 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | JJ69 | JJ69_ES |  | LE0 | JJ69_ES | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ69_ES | JJ69_ES (非取樣點) | FEEDER | D14/22/JJ69/ES |  |  |  |  | 633 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | JJ70 | JJ70_DS |  | DS1 | JJ70_DS | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ70_DS | JJ70_DS (非取樣點) | FEEDER | D14/22/JJ70/DS |  |  |  |  | 634 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | JJ70 | JJ70_ES |  | LE0 | JJ70_ES | [24 empty] | DDCS2_1 | [8 empty] | 北回DS.JJ70_ES | JJ70_ES (非取樣點) | FEEDER | D14/22/JJ70/ES |  |  |  |  | 635 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | 101 | 101 |  | 101 | 101 | [24 empty] | ADCS_N | [8 empty] | 北回DS.101 | 101 (非取樣點) | TIE | D14/11/100/D1 |  |  |  |  | 636 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | 102 | 102 |  | 102 | 102 | [24 empty] | ADCS_N | [8 empty] | 北回DS.102 | 102 (非取樣點) | TIE | D14/11/100/D2 |  |  |  |  | 637 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [24 empty] | ADCS_N | [8 empty] | 北回DS.1501E | 1501E (非取樣點) | TIE | D14/161/1500/E1 |  |  |  |  | 638 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [24 empty] | ADCS_N | [8 empty] | 北回DS.1502E | 1502E (非取樣點) | TIE | D14/161/1500/E2 |  |  |  |  | 639 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | 201 | 201 |  | 201 | 201 | [24 empty] | ADCS_N | [8 empty] | 北回DS.201 | 201 (非取樣點) | TIE | D14/22/200/D1 |  |  |  |  | 640 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | 202 | 202 |  | 202 | 202 | [24 empty] | ADCS_N | [8 empty] | 北回DS.202 | 202 (非取樣點) | TIE | D14/22/200/D2 |  |  |  |  | 641 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | 391 | 391 |  | 391 | 391 | [24 empty] | ADCS_N | [8 empty] | 北回DS.391 | 391 (非取樣點) | OTHER | D14/11/390/D1 |  |  |  |  | 642 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | 391E | 391E |  | 391E | 391E | [24 empty] | ADCS_N | [8 empty] | 北回DS.391E | 391E (非取樣點) | OTHER | D14/11/390/E1 |  |  |  |  | 643 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | 491 | 491 |  | 491 | 491 | [24 empty] | ADCS_N | [8 empty] | 北回DS.491 | 491 (非取樣點) | OTHER | D14/22/490/D1 |  |  |  |  | 644 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | 491E | 491E |  | 491E | 491E | [24 empty] | ADCS_N | [8 empty] | 北回DS.491E | 491E (非取樣點) | OTHER | D14/22/490/E1 |  |  |  |  | 645 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | 1750TE | [24 empty] | ADCS_N | [8 empty] | 北回DS.1750TE | 1750TE (非取樣點) | MTR | D14/161/1750/TE0 |  |  |  |  | 646 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | 1750BE | [24 empty] | ADCS_N | [8 empty] | 北回DS.1750BE | 1750BE (非取樣點) | MTR | D14/161/1750/BE0 |  |  |  |  | 647 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | 311 | 311 |  | 311 | 311 | [24 empty] | ADCS_N | [8 empty] | 北回DS.311 | 311 (非取樣點) | MTR | D14/11/310/D1 |  |  |  |  | 648 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | 310 | #1DTR(310) |  | E1 | 311E | [24 empty] | ADCS_N | [8 empty] | 北回DS.311E | 311E (非取樣點) | MTR | D14/11/310/E1 |  |  |  |  | 649 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | 321 | 321 |  | 321 | 321 | [24 empty] | ADCS_N | [8 empty] | 北回DS.321 | 321 (非取樣點) | MTR | D14/22/320/D1 |  |  |  |  | 650 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | 320 | #1DTR(320) |  | E1 | 321E | [24 empty] | ADCS_N | [8 empty] | 北回DS.321E | 321E (非取樣點) | MTR | D14/22/320/E1 |  |  |  |  | 651 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | 1760TE | [24 empty] | ADCS_N | [8 empty] | 北回DS.1760TE | 1760TE (非取樣點) | MTR | D14/161/1760/TE0 |  |  |  |  | 652 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | 1760BE | [24 empty] | ADCS_N | [8 empty] | 北回DS.1760BE | 1760BE (非取樣點) | MTR | D14/161/1760/BE0 |  |  |  |  | 653 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | 331 | 331 |  | 331 | 331 | [24 empty] | ADCS_N | [8 empty] | 北回DS.331 | 331 (非取樣點) | MTR | D14/11/330/D1 |  |  |  |  | 654 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | 330 | #2DTR(330) |  | E1 | 331E | [24 empty] | ADCS_N | [8 empty] | 北回DS.331E | 331E (非取樣點) | MTR | D14/11/330/E1 |  |  |  |  | 655 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | 341 | 341 |  | 341 | 341 | [24 empty] | ADCS_N | [8 empty] | 北回DS.341 | 341 (非取樣點) | MTR | D14/22/340/D1 |  |  |  |  | 656 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | 340 | #2DTR(340) |  | E1 | 341E | [24 empty] | ADCS_N | [8 empty] | 北回DS.341E | 341E (非取樣點) | MTR | D14/22/340/E1 |  |  |  |  | 657 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | 211E | 211E |  | 211E | 211E | [24 empty] | ADCS_N | [8 empty] | 北回DS.211E | 211E (非取樣點) | SC | D14/11/210/E1 |  |  |  |  | 658 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | 211 | 211 |  | 211 | 211 | [24 empty] | ADCS_N | [8 empty] | 北回DS.211 | 211 (非取樣點) | SC | D14/11/210/D1 |  |  |  |  | 659 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | 231E | 231E |  | 231E | 231E | [24 empty] | ADCS_N | [8 empty] | 北回DS.231E | 231E (非取樣點) | SC | D14/11/230/E1 |  |  |  |  | 660 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | 231 | 231 |  | 231 | 231 | [24 empty] | ADCS_N | [8 empty] | 北回DS.231 | 231 (非取樣點) | SC | D14/11/230/D1 |  |  |  |  | 661 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | 221E | 221E |  | 221E | 221E | [24 empty] | ADCS_N | [8 empty] | 北回DS.221E | 221E (非取樣點) | SC | D14/22/220/E1 |  |  |  |  | 662 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | 221 | 221 |  | 221 | 221 | [24 empty] | ADCS_N | [8 empty] | 北回DS.221 | 221 (非取樣點) | SC | D14/22/220/D1 |  |  |  |  | 663 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | 241E | 241E |  | 241E | 241E | [24 empty] | ADCS_N | [8 empty] | 北回DS.241E | 241E (非取樣點) | SC | D14/22/240/E1 |  |  |  |  | 664 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | 241 | 241 |  | 241 | 241 | [24 empty] | ADCS_N | [8 empty] | 北回DS.241 | 241 (非取樣點) | SC | D14/22/240/D1 |  |  |  |  | 665 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | 15B1E | 15B1E |  | BE1 | 15B1E | [24 empty] | ADCS_N | [8 empty] | 北回DS.15B1E | 15B1E (非取樣點) | BUS | D14/161/161B1E/BE1 |  |  |  |  | 666 | NotelDIPoint |  |  |  |  | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | 15B2E | 15B2E |  | BE2 | 15B2E | [24 empty] | ADCS_N | [8 empty] | 北回DS.15B2E | 15B2E (非取樣點) | BUS | D14/161/161B2E/BE2 |  |  |  |  | 667 | NotelDIPoint |  |  |  |  | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | ADCS_N | [8 empty] | 北回DS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 668 | NotelDIPoint | [38 empty] | START/STOP | STOP
D14 | 北回DS | 0 |  |  |  |  | 101E | 101E | [24 empty] | ADCS_N | [8 empty] | 北回DS.101E | 101E(非取樣點) | OTHER | D14/11/100/E1 |  |  |  |  | 669 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  |  |  |  | 102E | 102E | [24 empty] | ADCS_N | [8 empty] | 北回DS.102E | 102E(非取樣點) | OTHER | D14/11/100/E2 |  |  |  |  | 670 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  |  |  |  | 201E | 201E | [24 empty] | ADCS_N | [8 empty] | 北回DS.201E | 201E(非取樣點) | OTHER | D14/22/200/E1 |  |  |  |  | 671 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  |  |  |  | 202E | 202E | [24 empty] | ADCS_N | [8 empty] | 北回DS.202E | 202E(非取樣點) | OTHER | D14/22/200/E2 |  |  |  |  | 672 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | 1A | #1A |  | BE | #1A_BE | [24 empty] | ADCS_N | [8 empty] | 北回DS.#1A_BE | #1A BE(非取樣點) | OTHER | [5 empty] | 673 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | 1B | #1B |  | BE | #1B_BE | [24 empty] | ADCS_N | [8 empty] | 北回DS.#1B_BE | #1B BE(非取樣點) | OTHER | [5 empty] | 674 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | 2A | #2A |  | BE | #2A_BE | [24 empty] | ADCS_N | [8 empty] | 北回DS.#2A_BE | #2A BE(非取樣點) | OTHER | [5 empty] | 675 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | 2B | #2B |  | BE | #2B_BE | [24 empty] | ADCS_N | [8 empty] | 北回DS.#2B_BE | #2B BE(非取樣點) | OTHER | [5 empty] | 676 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | 1ABUS | 1ABUS |  | PTD | 1ABUS_PTD | [24 empty] | ADCS_N | [8 empty] | 北回DS.1ABUS_PTD | #1ABUS_PTD(非取樣點) | OTHER | [5 empty] | 677 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | 1ABUS | 1ABUS |  | PTE | 1ABUS_PTE | [24 empty] | ADCS_N | [8 empty] | 北回DS.1ABUS_PTE | #1ABUS_PTE(非取樣點) | OTHER | [5 empty] | 678 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | 1BBUS | 1BBUS |  | PTD | 1BBUS_PTD | [24 empty] | ADCS_N | [8 empty] | 北回DS.1BBUS_PTD | #1BBUS_PTD(非取樣點) | OTHER | [5 empty] | 679 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | 1BBUS | 1BBUS |  | PTE | 1BBUS_PTE | [24 empty] | ADCS_N | [8 empty] | 北回DS.1BBUS_PTE | #1BBUS_PTE(非取樣點) | OTHER | [5 empty] | 680 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | 2ABUS | 2ABUS |  | PTD | 2ABUS_PTD | [24 empty] | ADCS_N | [8 empty] | 北回DS.2ABUS_PTD | #2ABUS_PTD(非取樣點) | OTHER | [5 empty] | 681 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | 2ABUS | 2ABUS |  | PTE | 2ABUS_PTE | [24 empty] | ADCS_N | [8 empty] | 北回DS.2ABUS_PTE | #2ABUS_PTE(非取樣點) | OTHER | [5 empty] | 682 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D14 | 北回DS | 0 |  | 2BBUS | 2BBUS |  | PTD | 2BBUS_PTD | [24 empty] | ADCS_N | [8 empty] | 北回DS.2BBUS_PTD | #2BBUS_PTD(非取樣點) | OTHER | [5 empty] | 683 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D14 | 北回DS | 0 |  | 2BBUS | 2BBUS |  | PTE | 2BBUS_PTE | [24 empty] | ADCS_N | [8 empty] | 北回DS.2BBUS_PTE | #2BBUS_PTE(非取樣點) | OTHER | [5 empty] | 684 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo