## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D15 | 新化DS | 161 | 161kV | 1740 | 道爺~安南~新化線(1740) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_A1 | [8 empty] | 新化DS.1740LE | 1740LE (非取樣點) | LINE161 | [5 empty] | 2 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 161 | 161kV | 1740 | 道爺~安南~新化線(1740) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_A1 | [8 empty] | 新化DS.1740BE | 1740BE (非取樣點) | LINE161 | [5 empty] | 3 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 161 | 161kV | 1730 | 道爺~和順~新化線(1730) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_A1 | [8 empty] | 新化DS.1730LE | 1730LE (非取樣點) | LINE161 | [5 empty] | 4 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 161 | 161kV | 1730 | 道爺~和順~新化線(1730) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_A1 | [8 empty] | 新化DS.1730BE | 1730BE (非取樣點) | LINE161 | [5 empty] | 5 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_A1 | [8 empty] | 新化DS.1720LE | 1720LE (非取樣點) | LINE161 | [5 empty] | 6 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_A1 | [8 empty] | 新化DS.1720BE | 1720BE (非取樣點) | LINE161 | [5 empty] | 7 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 161 | 161kV | 1710 | 山上～新化一路(1710) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_A1 | [8 empty] | 新化DS.1710LE | 1710LE (非取樣點) | LINE161 | [5 empty] | 8 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 161 | 161kV | 1710 | 山上～新化一路(1710) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_A1 | [8 empty] | 新化DS.1710BE | 1710BE (非取樣點) | LINE161 | [5 empty] | 9 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 161 | 161kV | 1510 | 新化～永資～統實線(1510) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_A1 | [8 empty] | 新化DS.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 10 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 161 | 161kV | 1510 | 新化～永資～統實線(1510) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_A1 | [8 empty] | 新化DS.1510BE | 1510BE (非取樣點) | LINE161 | [5 empty] | 11 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_A1 | [8 empty] | 新化DS.1501E | 1501E (非取樣點) | TIE | [5 empty] | 12 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_A1 | [8 empty] | 新化DS.1502E | 1502E (非取樣點) | TIE | [5 empty] | 13 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_A1 | [8 empty] | 新化DS.1750TE | 1750TE (非取樣點) | MTR | [5 empty] | 14 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_A1 | [8 empty] | 新化DS.1750BE | 1750BE (非取樣點) | MTR | [5 empty] | 15 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D15_A1 | [8 empty] | 新化DS.310_DS | 310_DS (非取樣點) | MTR | [5 empty] | 16 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D15_A1 | [8 empty] | 新化DS.310_ES | 310_ES (非取樣點) | MTR | [5 empty] | 17 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_A1 | [8 empty] | 新化DS.1760TE | 1760TE (非取樣點) | MTR | [5 empty] | 18 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_A1 | [8 empty] | 新化DS.1760BE | 1760BE (非取樣點) | MTR | [5 empty] | 19 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D15_A1 | [8 empty] | 新化DS.320_DS | 320_DS (非取樣點) | MTR | [5 empty] | 20 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D15_A1 | [8 empty] | 新化DS.320_ES | 320_ES (非取樣點) | MTR | [5 empty] | 21 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D15_A1 | [8 empty] | 新化DS.340_DS | 340_DS (非取樣點) | MTR | [5 empty] | 22 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D15_A1 | [8 empty] | 新化DS.340_ES | 340_ES (非取樣點) | MTR | [5 empty] | 23 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D15_A1 | [8 empty] | 新化DS.330_DS | 330_DS (非取樣點) | MTR | [5 empty] | 24 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D15_A1 | [8 empty] | 新化DS.330_ES | 330_ES (非取樣點) | MTR | [5 empty] | 25 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 11 | 11kV | KY21 | 新21線(KY21) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY21_DS | KY21_DS (非取樣點) | FEEDER | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY21 | 新21線(KY21) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY21_ES | KY21_ES (非取樣點) | FEEDER | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 11 | 11kV | KY22 | 新22線(KY22) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY22_DS | KY22_DS (非取樣點) | FEEDER | [5 empty] | 28 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY22 | 新22線(KY22) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY22_ES | KY22_ES (非取樣點) | FEEDER | [5 empty] | 29 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 11 | 11kV | KY23 | 新23線(KY23) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY23_DS | KY23_DS (非取樣點) | FEEDER | [5 empty] | 30 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY23 | 新23線(KY23) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY23_ES | KY23_ES (非取樣點) | FEEDER | [5 empty] | 31 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 11 | 11kV | KY24 | 新24線(KY24) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY24_DS | KY24_DS (非取樣點) | FEEDER | [5 empty] | 32 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY24 | 新24線(KY24) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY24_ES | KY24_ES (非取樣點) | FEEDER | [5 empty] | 33 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 11 | 11kV | KY25 | 新25線(KY25) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY25_DS | KY25_DS (非取樣點) | FEEDER | [5 empty] | 34 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY25 | 新25線(KY25) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY25_ES | KY25_ES (非取樣點) | FEEDER | [5 empty] | 35 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 11 | 11kV | KY26 | 新26線(KY26) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY26_DS | KY26_DS (非取樣點) | FEEDER | [5 empty] | 36 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY26 | 新26線(KY26) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY26_ES | KY26_ES (非取樣點) | FEEDER | [5 empty] | 37 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 11 | 11kV | 210 | #1SC(210) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D15_A1 | [8 empty] | 新化DS.210_DS | 210_DS (非取樣點) | SC | [5 empty] | 38 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | 210 | #1SC(210) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D15_A1 | [8 empty] | 新化DS.210E | 210E (非取樣點) | SC | [5 empty] | 39 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 11 | 11kV | 220 | #2SC(220) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D15_A1 | [8 empty] | 新化DS.220_DS | 220_DS (非取樣點) | SC | [5 empty] | 40 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | 220 | #2SC(220) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D15_A1 | [8 empty] | 新化DS.220E | 220E (非取樣點) | SC | [5 empty] | 41 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 11 | 11kV | 100 | TIE(100) |  | DS1 | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D15_A1 | [8 empty] | 新化DS.100_DS | 100_DS (非取樣點) | TIE | [5 empty] | 42 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY27 | 新27線(KY27) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY27_DS | KY27_DS (非取樣點) | FEEDER | [5 empty] | 43 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY27 | 新27線(KY27) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY27_ES | KY27_ES (非取樣點) | FEEDER | [5 empty] | 44 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 11 | 11kV | KY28 | 新28線(KY28) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY28_DS | KY28_DS (非取樣點) | FEEDER | [5 empty] | 45 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY28 | 新28線(KY28) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY28_ES | KY28_ES (非取樣點) | FEEDER | [5 empty] | 46 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 11 | 11kV | KY29 | 新29線(KY29) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY29_DS | KY29_DS (非取樣點) | FEEDER | [5 empty] | 47 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY29 | 新29線(KY29) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY29_ES | KY29_ES (非取樣點) | FEEDER | [5 empty] | 48 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 11 | 11kV | KY30 | 新30線(KY30) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY30_DS | KY30_DS (非取樣點) | FEEDER | [5 empty] | 49 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY30 | 新30線(KY30) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY30_ES | KY30_ES (非取樣點) | FEEDER | [5 empty] | 50 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 11 | 11kV | 230 | #3SC(230) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D15_A1 | [8 empty] | 新化DS.230_DS | 230_DS (非取樣點) | SC | [5 empty] | 51 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | 230 | #3SC(230) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D15_A1 | [8 empty] | 新化DS.230E | 230E (非取樣點) | SC | [5 empty] | 52 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 11 | 11kV | KY37 | 新37線(KY37) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY37_DS | KY37_DS (非取樣點) | FEEDER | [5 empty] | 53 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY37 | 新37線(KY37) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY37_ES | KY37_ES (非取樣點) | FEEDER | [5 empty] | 54 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 11 | 11kV | KY38 | 新38線(KY38) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY38_DS | KY38_DS (非取樣點) | FEEDER | [5 empty] | 55 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY38 | 新38線(KY38) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY38_ES | KY38_ES (非取樣點) | FEEDER | [5 empty] | 56 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 11 | 11kV | KY39 | 新39線(KY39) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY39_DS | KY39_DS (非取樣點) | FEEDER | [5 empty] | 57 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY39 | 新39線(KY39) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY39_ES | KY39_ES (非取樣點) | FEEDER | [5 empty] | 58 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 11 | 11kV | KY40 | 新40線(KY40) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY40_DS | KY40_DS (非取樣點) | FEEDER | [5 empty] | 59 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY40 | 新40線(KY40) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY40_ES | KY40_ES (非取樣點) | FEEDER | [5 empty] | 60 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 11 | 11kV | 260 | #6SC(260) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D15_A1 | [8 empty] | 新化DS.260_DS | 260_DS (非取樣點) | SC | [5 empty] | 61 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | 260 | #6SC(260) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D15_A1 | [8 empty] | 新化DS.260E | 260E (非取樣點) | SC | [5 empty] | 62 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 11 | 11kV | 200 | TIE(200) |  | DS1 | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D15_A1 | [8 empty] | 新化DS.200_DS | 200_DS (非取樣點) | TIE | [5 empty] | 63 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY31 | 新31線(KY31) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY31_DS | KY31_DS (非取樣點) | FEEDER | [5 empty] | 64 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY31 | 新31線(KY31) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY31_ES | KY31_ES (非取樣點) | FEEDER | [5 empty] | 65 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 11 | 11kV | KY32 | 新32線(KY32) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY32_DS | KY32_DS (非取樣點) | FEEDER | [5 empty] | 66 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY32 | 新32線(KY32) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY32_ES | KY32_ES (非取樣點) | FEEDER | [5 empty] | 67 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 11 | 11kV | KY33 | 新33線(KY33) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY33_DS | KY33_DS (非取樣點) | FEEDER | [5 empty] | 68 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY33 | 新33線(KY33) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY33_ES | KY33_ES (非取樣點) | FEEDER | [5 empty] | 69 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 11 | 11kV | KY34 | 新34線(KY34) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY34_DS | KY34_DS (非取樣點) | FEEDER | [5 empty] | 70 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY34 | 新34線(KY34) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY34_ES | KY34_ES (非取樣點) | FEEDER | [5 empty] | 71 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 11 | 11kV | KY35 | 新35線(KY35) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY35_DS | KY35_DS (非取樣點) | FEEDER | [5 empty] | 72 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY35 | 新35線(KY35) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY35_ES | KY35_ES (非取樣點) | FEEDER | [5 empty] | 73 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 11 | 11kV | KY36 | 新36線(KY36) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY36_DS | KY36_DS (非取樣點) | FEEDER | [5 empty] | 74 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY36 | 新36線(KY36) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D15_D1 | [8 empty] | 新化DS.KY36_ES | KY36_ES (非取樣點) | FEEDER | [5 empty] | 75 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 11 | 11kV | 250 | #5SC(250) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D15_A1 | [8 empty] | 新化DS.250_DS | 250_DS (非取樣點) | SC | [5 empty] | 76 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | 250 | #5SC(250) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D15_A1 | [8 empty] | 新化DS.250E | 250E (非取樣點) | SC | [5 empty] | 77 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 11 | 11kV | 240 | #4SC(240) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D15_A1 | [8 empty] | 新化DS.240_DS | 240_DS (非取樣點) | SC | [5 empty] | 78 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | 240 | #4SC(240) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D15_A1 | [8 empty] | 新化DS.240E | 240E (非取樣點) | SC | [5 empty] | 79 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | 15B1E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aaaz | B2/D15_A1 | [8 empty] | 新化DS.15B1E | 15B1E (非取樣點) | BUS | [5 empty] | 80 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | 15B2E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/2Bus | [13 empty] | aaaz | B2/D15_A1 | [8 empty] | 新化DS.15B2E | 15B2E (非取樣點) | BUS | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 161 | 161kV | 1740 | 道爺~安南~新化線(1740) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D15TN03/T2 |  | 0000 |  | 0001 | 1-00-00 |  | 1-01 | 1740 | CB ON/OFF | 道爺安南新化線 1740 CB |  | aaca | B2/D15_A1 | [8 empty] | 新化DS.1740_CB | 1740(道爺安南新化線) CB | LINE161 | [5 empty] | 82 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 161 | 161kV | 1730 | 道爺~和順~新化線(1730) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D15TN04/T2 |  | 0005 |  | 0002 | 1-00-05 |  | 1-02 | 1730 | CB ON/OFF | 道爺和順新化線1730 CB |  | aada | B2/D15_A1 | [8 empty] | 新化DS.1730_CB | 1730(道爺和順新化線) CB | LINE161 | [5 empty] | 83 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P06D152/T2 |  | 0010 |  | 0003 | 1-01-02 |  | 1-03 | 1720 | CB ON/OFF | 山上新化二路 1720 CB |  | aaga | B2/D15_A1 | [8 empty] | 新化DS.1720_CB | 1720(山上二路) CB | LINE161 | [5 empty] | 84 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 161 | 161kV | 1710 | 山上～新化一路(1710) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P06D151/T2 |  | 0015 |  | 0004 | 1-01-07 |  | 1-04 | 1710 | CB ON/OFF | 山上新化一路 1710 CB |  | aaha | B2/D15_A1 | [8 empty] | 新化DS.1710_CB | 1710(山上一路) CB | LINE161 | [5 empty] | 85 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 161 | 161kV | 1510 | 新化～永資～統實線(1510) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D15TN13/T2 |  | 0020 |  | 0005 | 1-02-04 |  | 1-05 | 1510 | CB ON/OFF | 新化永資統實線 1510 CB |  | aaia | B2/D15_A1 | [8 empty] | 新化DS.1510_CB | 1510(統實永資線) CB | LINE161 | [5 empty] | 86 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 161 | 161kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0552 |  | 0007 | 1-32-08 |  | 1-07 | 161kV #1 BUS | USE/LOCK | 161KV #1 BUS╴87UL |  |  | B2/D15_A1 | [8 empty] | 新化DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | [5 empty] | 87 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D15 | 新化DS | 161 | 161kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0553 |  | 0008 | 1-32-09 |  | 1-08 | 161kV #2 BUS | USE/LOCK | 161KV #2 BUS╴87UL |  |  | B2/D15_A1 | [8 empty] | 新化DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | [5 empty] | 88 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D15 | 新化DS | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0040 |  | 0009 | 1-05-00 |  | 1-09 | 1500 | ON/OFF | 161KV TIE 1500 CB |  | aafz | B2/D15_A1 | [8 empty] | 新化DS.1500_CB | 1500(TIE) CB | TIE | [5 empty] | 89 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/1DTR |  | 0045 |  | 0010 | 1-05-05 |  | 1-0A | #1DTR | ON/OFF | #1DTR一次1750 CB |  | aabb | ELEM/D15_A1 | [8 empty] | 新化DS.1750_CB | 1750(#1DTR) CB | MTR | [5 empty] | 90 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2DTR | v | 0055 |  | 0011 | 1-06-07 |  | 1-0B | #2DTR | ON/OFF | #2DTR一次1760 CB |  | aaeb | ELEM/D15_A1 | [8 empty] | 新化DS.1760_CB | 1760(#2DTR) CB | MTR | [5 empty] | 91 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1ABus | T/1DTR(A) |  |  | 0051 |  | 0016 | 1-06-03 |  | 1-10 | #1BUS | ON/OFF | D1A 310 CB |  | aaca | ELEM/D15_A1 | [8 empty] | 新化DS.310_CB | 310(#1DTR) CB | MTR | [5 empty] | 92 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | 210 | #1SC(210) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1ABus | C/1SC |  |  | 0146 |  | 0018 | 1-12-02 |  | 1-12 | #1SC | CB ON/OFF | #1SC 210 CB |  | aadb | B3/D15_A1 | [8 empty] | 新化DS.210_CB | 210(11KV #1SC) CB | SC | [5 empty] | 93 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY21 | 新21線(KY21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1ABus | L/KY21/T1 |  |  | 0128 |  | 0019 | 1-10-00 |  | 1-13 | 大洋線 | CB ON/OFF | 新21線 F1 KY21 CB |  | aaeb | B2/D15_D1 | [8 empty] | 新化DS.KY21_CB | KY21(11KV新21線) CB | FEEDER | [5 empty] | 94 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY22 | 新22線(KY22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1ABus | L/KY22/T1 |  |  | 0131 |  | 0020 | 1-10-03 |  | 1-14 | 大坑線 | CB ON/OFF | 新22線 F2 KY22 KYCB |  | aafb | B2/D15_D1 | [8 empty] | 新化DS.KY22_CB | KY22(11KV新22線) CB | FEEDER | [5 empty] | 95 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY23 | 新23線(KY23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1ABus | L/KY23/T1 |  |  | 0134 |  | 0021 | 1-10-06 |  | 1-15 | 保東線 | CB ON/OFF | 新23線 F3 KY23 CB |  | aagb | B2/D15_D1 | [8 empty] | 新化DS.KY23_CB | KY23(11KV新23線) CB | FEEDER | [5 empty] | 96 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY24 | 新24線(KY24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1ABus | L/KY24/T1 |  |  | 0137 |  | 0022 | 1-11-01 |  | 1-16 | 山腳線 | CB ON/OFF | 新24線 F4 KY24 CB |  | aahb | B2/D15_D1 | [8 empty] | 新化DS.KY24_CB | KY24(11KV新24線) CB | FEEDER | [5 empty] | 97 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY25 | 新25線(KY25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1ABus | L/KY25/T1 |  |  | 0140 |  | 0023 | 1-11-04 |  | 1-17 | 化工線 | CB ON/OFF | 新25線 F5 KY25 CB |  | aaib | B2/D15_D1 | [8 empty] | 新化DS.KY25_CB | KY25(11KV新25線) CB | FEEDER | [5 empty] | 98 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY26 | 新26線(KY26) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1ABus | L/KY26/T1 |  |  | 0143 |  | 0024 | 1-11-07 |  | 1-18 | 備用線 | CB ON/OFF | 新26線F6 CB |  | aajb | B2/D15_D1 | [8 empty] | 新化DS.KY26_CB | KY26(11KV新26線) CB | FEEDER | [5 empty] | 99 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | 220 | #2SC(220) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1ABus | C/2SC |  |  | 0149 |  | 0025 | 1-12-05 |  | 1-19 | #2SC | CB ON/OFF | #2SC 220 CB |  | aakb | B3/D15_A1 | [8 empty] | 新化DS.220_CB | 220(11KV #2SC) CB | SC | [5 empty] | 100 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | 100 | TIE(100) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | SctFdr | B/1ABus | B/2ABus |  | v | 0152 |  | 0026 | 1-13-00 |  | 1-1A | #1TIE | CB ON/OFF | #1TIE 100 CB |  | aalb | B3/D15_A1 | [8 empty] | 新化DS.100_CB | 100(TIE) CB | TIE | [5 empty] | 101 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 11 | 11kV | KY27 | 新27線(KY27) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1BBus | L/KY27/T1 |  |  | 0155 |  | 0027 | 1-13-03 |  | 1-1B | 科積線 | CB ON/OFF | 新27線F7 KY27 CB |  | baab | B2/D15_D1 | [8 empty] | 新化DS.KY27_CB | KY27(11KV新27線) CB | FEEDER | [5 empty] | 102 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY28 | 新28線(KY28) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1BBus | L/KY28/T1 |  |  | 0158 |  | 0028 | 1-13-06 |  | 1-1C | 南茂線 | CB ON/OFF | 新28線F8 KY28 CB |  | babb | B2/D15_D1 | [8 empty] | 新化DS.KY28_CB | KY28(11KV新28線) CB | FEEDER | [5 empty] | 103 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY29 | 新29線(KY29) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1BBus | L/KY29/T1 |  |  | 0161 |  | 0029 | 1-14-01 |  | 1-1D | 神隆線 | CB ON/OFF | 新29線F9 KY29 CB |  | bacb | B2/D15_D1 | [8 empty] | 新化DS.KY29_CB | KY29(11KV新29線) CB | FEEDER | [5 empty] | 104 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY30 | 新30線(KY30) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1BBus | L/KY30/T1 |  |  | 0164 |  | 0030 | 1-14-04 |  | 1-1E | 備用線 | CB ON/OFF | 新30線 F10 KY30 CB |  | badb | B2/D15_D1 | [8 empty] | 新化DS.KY30_CB | KY30(11KV新30線) CB | FEEDER | [5 empty] | 105 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | 230 | #3SC(230) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1BBus | C/3SC |  |  | 0167 |  | 0031 | 1-14-07 |  | 1-1F | #3SC | CB ON/OFF | #3SC 230 CB |  | baeb | B3/D15_A1 | [8 empty] | 新化DS.230_CB | 230(11KV #3SC) CB | SC | [5 empty] | 106 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1BBus | T/1DTR(B) |  |  | 0061 |  | 0032 | 1-07-05 |  | 1-20 | D1B 320 | ON/OFF | D1B 320 CB |  | bafa | ELEM/D15_A1 | [8 empty] | 新化DS.320_CB | 320(#1DTR) CB | MTR | [5 empty] | 107 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | T/2DTR(B) |  |  | 0063 |  | 0033 | 1-07-07 |  | 1-21 | D2B 340 | ON/OFF | D2B 340 CB |  | bbba | ELEM/D15_A1 | [8 empty] | 新化DS.340_CB | 340(#2DTR) CB | MTR | [5 empty] | 108 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | 260 | #6SC(260) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | C/6SC |  | v | 0182 |  | 0034 | 1-16-06 |  | 1-22 | #6SC | CB ON/OFF | #6SC 260 CB |  | bbcb | B3/D15_A1 | [8 empty] | 新化DS.260_CB | 260(11KV #6SC) CB | SC | [5 empty] | 109 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY37 | 新37線(KY37) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | L/KY37/T1 |  |  | 0170 |  | 0035 | 1-15-02 |  | 1-23 | 科台線 | CB ON/OFF | 新37線 KY37 CB |  | bbdb | B2/D15_D1 | [8 empty] | 新化DS.KY37_CB | KY37(11KV新37線) CB | FEEDER | [5 empty] | 110 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY38 | 新38線(KY38) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | L/KY38/T1 |  |  | 0173 |  | 0036 | 1-15-05 |  | 1-24 | 科園線 | CB ON/OFF | 新38線 KY38 CB |  | bbeb | B2/D15_D1 | [8 empty] | 新化DS.KY38_CB | KY38(11KV新38線) CB | FEEDER | [5 empty] | 111 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY39 | 新39線(KY39) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | L/KY39/T1 |  |  | 0176 |  | 0037 | 1-16-00 |  | 1-25 | 科南線 | CB ON/OFF | 新39線 KY39 CB |  | bbfb | B2/D15_D1 | [8 empty] | 新化DS.KY39_CB | KY39(11KV新39線) CB | FEEDER | [5 empty] | 112 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY40 | 新40線(KY40) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | L/KY40/T1 |  |  | 0179 |  | 0038 | 1-16-03 |  | 1-26 | 備用線 | CB ON/OFF | 新40線F14 KY40 CB |  | bbgb | B2/D15_D1 | [8 empty] | 新化DS.KY40_CB | KY40(11KV新40線) CB | FEEDER | [5 empty] | 113 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | 200 | TIE(200) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | SctFdr | B/2BBus | B/1BBus |  |  | 0185 |  | 0039 | 1-17-01 |  | 1-27 | #2TIE | CB ON/OFF | #2TIE 200 CB |  | bbhb | B3/D15_A1 | [8 empty] | 新化DS.200_CB | 200(TIE) CB | TIE | [5 empty] | 114 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D15 | 新化DS | 11 | 11kV | 250 | #5SC(250) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABus | C/5SC |  | v | 0206 |  | 0040 | 1-19-06 |  | 1-28 | #5SC | CB ON/OFF | #5SC 250 CB |  | abab | B3/D15_A1 | [8 empty] | 新化DS.250_CB | 250(11KV #5SC) CB | SC | [5 empty] | 115 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY31 | 新31線(KY31) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABus | L/KY31/T1 |  |  | 0188 |  | 0042 | 1-17-04 |  | 1-2A | 永化線 | CB ON/OFF | 新31線 F15 KY31 CB |  | abbb | B2/D15_D1 | [8 empty] | 新化DS.KY31_CB | KY31(11KV新31線) CB | FEEDER | [5 empty] | 116 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY32 | 新32線(KY32) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABus | L/KY32/T1 |  |  | 0191 |  | 0043 | 1-17-07 |  | 1-2B | 遠東線 | CB ON/OFF | 新32線 F16 KY32 CB |  | abcb | B2/D15_D1 | [8 empty] | 新化DS.KY32_CB | KY32(11KV新32線) CB | FEEDER | [5 empty] | 117 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY33 | 新33線(KY33) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABus | L/KY33/T1 |  |  | 0194 |  | 0044 | 1-18-02 |  | 1-2C | 社內線 | CB ON/OFF | 新33線F17 KY33 CB |  | abdb | B2/D15_D1 | [8 empty] | 新化DS.KY33_CB | KY33(11KV新33線) CB | FEEDER | [5 empty] | 118 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY34 | 新34線(KY34) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABus | L/KY34/T1 |  |  | 0197 |  | 0045 | 1-18-05 |  | 1-2D | 新東線 | CB ON/OFF | 新34線F18 KY34 CB |  | abeb | B2/D15_D1 | [8 empty] | 新化DS.KY34_CB | KY34(11KV新34線) CB | FEEDER | [5 empty] | 119 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY35 | 新35線(KY35) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABus | L/KY35/T1 |  |  | 0200 |  | 0046 | 1-19-00 |  | 1-2E | 北勢線 | CB ON/OFF | 新35線G19 KY35 CB |  | abfb | B2/D15_D1 | [8 empty] | 新化DS.KY35_CB | KY35(11KV新35線) CB | FEEDER | [5 empty] | 120 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY36 | 新36線(KY36) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABus | L/KY36/T1 |  |  | 0203 |  | 0047 | 1-19-03 |  | 1-2F | 西勢線 | CB ON/OFF | 新36線 F20 KY36 CB |  | abgb | B2/D15_D1 | [8 empty] | 新化DS.KY36_CB | KY36(11KV新36線) CB | FEEDER | [5 empty] | 121 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | 240 | #4SC(240) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABus | C/4SC |  |  | 0209 |  | 0048 | 1-1A-01 |  | 1-30 | #4SC | CB ON/OFF | #4SC 240 CB |  | abhb | B3/D15_A1 | [8 empty] | 新化DS.240_CB | 240(11KV #4SC) CB | SC | [5 empty] | 122 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABus | T/2DTR(A) |  | v | 0071 |  | 0049 | 1-08-07 |  | 1-31 | D2A 330 | ON/OFF | D2A 330 CB |  | abia | ELEM/D15_A1 | [8 empty] | 新化DS.330_CB | 330(#2DTR) CB | MTR | [5 empty] | 123 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 161 | 161kV | 1740 | 道爺~安南~新化線(1740) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0514 |  | 0064 | 1-30-02 |  | 1-40 | 1740 | U/L | 道爺安南新化線 1740 87RY U/L |  |  | B2/D15_A1 | [8 empty] | 新化DS.1740_87UL | 道爺安南新化線(1740) 87RY U/L | LINE161 | [5 empty] | 124 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D15 | 新化DS | 161 | 161kV | 1730 | 道爺~和順~新化線(1730) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0516 |  | 0066 | 1-30-04 |  | 1-42 | 1730 | U/L | 道爺和順新化線 1730 87 RY U/L |  |  | B2/D15_A1 | [8 empty] | 新化DS.1730_87UL | 道爺和順新化線(1730) 87RY U/L | LINE161 | [5 empty] | 125 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D15 | 新化DS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0518 |  | 0068 | 1-30-06 |  | 1-44 | 1720 | U/L | 山上新化二路 1720 87 RY U/L |  |  | B2/D15_A1 | [8 empty] | 新化DS.1720_87UL | 山上二路(1720) 87RY U/L | LINE161 | [5 empty] | 126 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D15 | 新化DS | 161 | 161kV | 1710 | 山上～新化一路(1710) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0520 |  | 0070 | 1-30-08 |  | 1-46 | 1710 | U/L | 山上新化一路 1710 87 RY U/L |  |  | B2/D15_A1 | [8 empty] | 新化DS.1710_87UL | 山上一路(1710) 87RY U/L | LINE161 | [5 empty] | 127 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D15 | 新化DS | 161 | 161kV | 1740 | 道爺~安南~新化線(1740) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0530 |  | 0080 | 1-31-02 |  | 1-50 | 1740 | U/L | 道爺安南新化線 1740 79 RY U/L |  |  | B2/D15_A1 | [8 empty] | 新化DS.1740_79UL | 道爺安南新化線(1740) 79RY U/L | LINE161 | [5 empty] | 128 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D15 | 新化DS | 161 | 161kV | 1730 | 道爺~和順~新化線(1730) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0531 |  | 0081 | 1-31-03 |  | 1-51 | 1730 | U/L | 道爺和順新化線 1730 79 RY U/L |  |  | B2/D15_A1 | [8 empty] | 新化DS.1730_79UL | 道爺和順新化線(1730) 79RY U/L | LINE161 | [5 empty] | 129 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D15 | 新化DS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0532 |  | 0082 | 1-31-04 |  | 1-52 | 1720 | U/L | 山上新化二路 1720 79 RY U/L |  |  | B2/D15_A1 | [8 empty] | 新化DS.1720_79UL | 山上二路(1720) 79RY U/L | LINE161 | [5 empty] | 130 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D15 | 新化DS | 161 | 161kV | 1710 | 山上～新化一路(1710) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [5 empty] | v | 0533 |  | 0083 | 1-31-05 |  | 1-53 | 1710 | U/L | 山上新化一路 1710 79 RY U/L |  |  | B2/D15_A1 | [8 empty] | 新化DS.1710_79UL | 山上一路(1710) 79RY U/L | LINE161 | [5 empty] | 131 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D15 | 新化DS |  |  | 1DTR(A) | #1DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0556 |  | 0096 | 1-32-12 |  | 1-60 | #1A DTR | A/M | #1A DTR OLTC A/M |  |  | B1/D15_A1 | [8 empty] | 新化DS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | [5 empty] | 132 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D15 | 新化DS |  |  | 1DTR(A) | #1DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0024 |  | 0097 | 1-98 |  | 1-61 | #1A DTR | R/L | #1A DTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D15_A1 | [8 empty] | 新化DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | [5 empty] | 133 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D15 | 新化DS |  |  | 1DTR(B) | #1DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0560 |  | 0098 | 1-33-00 |  | 1-62 | #1B DTR | A/M | #1B DTR OLTC A/M |  |  | B1/D15_A1 | [8 empty] | 新化DS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | [5 empty] | 134 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D15 | 新化DS |  |  | 1DTR(B) | #1DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0025 |  | 0099 | 1-99 |  | 1-63 | #1B DTR | R/L | #1B DTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D15_A1 | [8 empty] | 新化DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | [5 empty] | 135 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D15 | 新化DS |  |  | 2DTR(A) | #2DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0563 |  | 0100 | 1-33-03 |  | 1-64 | #2A DTR | A/M | #2ATR OLTC A/M |  |  | B1/D15_A1 | [8 empty] | 新化DS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | [5 empty] | 136 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D15 | 新化DS |  |  | 2DTR(A) | #2DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0029 |  | 0101 | 1-9D |  | 1-65 | #2A DTR | R/L | #2A DTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D15_A1 | [8 empty] | 新化DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | [5 empty] | 137 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D15 | 新化DS |  |  | 2DTR(B) | #2DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0567 |  | 0102 | 1-33-07 |  | 1-66 | #2B DTR | A/M | #2B DTR OLTC A/M |  |  | B1/D15_A1 | [8 empty] | 新化DS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | [5 empty] | 138 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D15 | 新化DS |  |  | 2DTR(B) | #2DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [5 empty] | v | 0030 |  | 0103 | 1-9E |  | 1-67 | #2B DTR | R/L | #2B DTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D15_A1 | [8 empty] | 新化DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | [5 empty] | 139 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D15 | 新化DS | 161 | 161kV | 1740 | 道爺~安南~新化線(1740) |  | DS1 | 1741 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0576 | 577 | 0112 | 1-34-00 | 1-34-01 | 1-70 | 1741 DS | ON/OFF | 道爺安南新化線 1741 DS |  |  | B2/D15_A1 | [8 empty] | 新化DS.1741_DS | 1741(道爺安南新化線) DS | LINE161 | [5 empty] | 140 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D15 | 新化DS | 161 | 161kV | 1740 | 道爺~安南~新化線(1740) |  | DS2 | 1742 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0578 | 579 | 0113 | 1-34-02 | 1-34-03 | 1-71 | 1742 DS | ON/OFF | 道爺安南新化線1742 DS |  |  | B2/D15_A1 | [8 empty] | 新化DS.1742_DS | 1742(道爺安南新化線) DS | LINE161 | [5 empty] | 141 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D15 | 新化DS | 161 | 161kV | 1740 | 道爺~安南~新化線(1740) |  | DS3 | 1743 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0580 | 581 | 0114 | 1-34-04 | 1-34-05 | 1-72 | 1743 DS | ON/OFF | 道爺安南新化線 1743 DS |  |  | B2/D15_A1 | [8 empty] | 新化DS.1743_DS | 1743(道爺安南新化線) DS | LINE161 | [5 empty] | 142 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D15 | 新化DS | 161 | 161kV | 1740 | 道爺~安南~新化線(1740) |  | ES3 | 1743E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0582 | 583 | 0115 | 1-34-06 | 1-34-07 | 1-73 | 1743 E ES | ON/OFF | 道爺安南新化線 1743 EDS |  |  | B2/D15_A1 | [8 empty] | 新化DS.1743E_ES | 1743E(道爺安南新化線) ES | LINE161 | [5 empty] | 143 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D15 | 新化DS | 161 | 161kV | 1730 | 道爺~和順~新化線(1730) |  | DS1 | 1731 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0584 | 585 | 0116 | 1-34-08 | 1-34-09 | 1-74 | 1731 DS | ON/OFF | 道爺和順新化線 1731 DS |  |  | B2/D15_A1 | [8 empty] | 新化DS.1731_DS | 1731(道爺和順新化線) DS | LINE161 | [5 empty] | 144 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D15 | 新化DS | 161 | 161kV | 1730 | 道爺~和順~新化線(1730) |  | DS2 | 1732 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0586 | 587 | 0117 | 1-34-10 | 1-34-11 | 1-75 | 1732 DS | ON/OFF | 道爺和順新化線 1732 DS |  |  | B2/D15_A1 | [8 empty] | 新化DS.1732_DS | 1732(道爺和順新化線) DS | LINE161 | [5 empty] | 145 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D15 | 新化DS | 161 | 161kV | 1730 | 道爺~和順~新化線(1730) |  | DS3 | 1733 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0588 | 589 | 0118 | 1-34-12 | 1-34-13 | 1-76 | 1733 DS | ON/OFF | 道爺和順新化線 1733 DS |  |  | B2/D15_A1 | [8 empty] | 新化DS.1733_DS | 1733(道爺和順新化線) DS | LINE161 | [5 empty] | 146 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D15 | 新化DS | 161 | 161kV | 1730 | 道爺~和順~新化線(1730) |  | ES3 | 1733E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [5 empty] | v | 0590 | 591 | 0119 | 1-34-14 | 1-34-15 | 1-77 | 1733 E ES | ON/OFF | 道爺和順新化線 1733 E ES |  |  | B2/D15_A1 | [8 empty] | 新化DS.1733E_ES | 1733E(道爺和順新化線) ES | LINE161 | [5 empty] | 147 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D15 | 新化DS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | DS1 | 1721 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0592 | 593 | 0120 | 1-35-00 | 1-35-01 | 1-78 | 1721 DS | ON/OFF | 山上新化二路 1721 DS |  |  | B2/D15_A1 | [8 empty] | 新化DS.1721_DS | 1721(山上二路) DS | LINE161 | [5 empty] | 148 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D15 | 新化DS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | DS2 | 1722 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0594 | 595 | 0121 | 1-35-02 | 1-35-03 | 1-79 | 1722 DS | ON/OFF | 山上新化二路 1722 DS |  |  | B2/D15_A1 | [8 empty] | 新化DS.1722_DS | 1722(山上二路) DS | LINE161 | [5 empty] | 149 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D15 | 新化DS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | DS3 | 1723 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0596 | 597 | 0122 | 1-35-04 | 1-35-05 | 1-7A | 1723 DS | ON/OFF | 山上新化二路 1723 DS |  |  | B2/D15_A1 | [8 empty] | 新化DS.1723_DS | 1723(山上二路) DS | LINE161 | [5 empty] | 150 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D15 | 新化DS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | ES3 | 1723E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0598 | 599 | 0123 | 1-35-06 | 1-35-07 | 1-7B | 1723 E ES | ON/OFF | 山上新化二路 1723 E ES |  |  | B2/D15_A1 | [8 empty] | 新化DS.1723E_ES | 1723E(山上二路) ES | LINE161 | [5 empty] | 151 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D15 | 新化DS | 161 | 161kV | 1710 | 山上～新化一路(1710) |  | DS1 | 1711 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0600 | 601 | 0124 | 1-35-08 | 1-35-09 | 1-7C | 1711 DS | ON/OFF | 山上新化一路 1711 DS |  |  | B2/D15_A1 | [8 empty] | 新化DS.1711_DS | 1711(山上一路) DS | LINE161 | [5 empty] | 152 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D15 | 新化DS | 161 | 161kV | 1710 | 山上～新化一路(1710) |  | DS2 | 1712 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0602 | 603 | 0125 | 1-35-10 | 1-35-11 | 1-7D | 1712 DS | ON/OFF | 山上新化一路 1712 DS |  |  | B2/D15_A1 | [8 empty] | 新化DS.1712_DS | 1712(山上一路) DS | LINE161 | [5 empty] | 153 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D15 | 新化DS | 161 | 161kV | 1710 | 山上～新化一路(1710) |  | DS3 | 1713 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0604 | 605 | 0126 | 1-35-12 | 1-35-13 | 1-7E | 1713 DS | ON/OFF | 山上新化一路 1713 DS |  |  | B2/D15_A1 | [8 empty] | 新化DS.1713_DS | 1713(山上一路) DS | LINE161 | [5 empty] | 154 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D15 | 新化DS | 161 | 161kV | 1710 | 山上～新化一路(1710) |  | ES3 | 1713E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [5 empty] | v | 0606 | 607 | 0127 | 1-35-14 | 1-35-15 | 1-7F | 1713 E ES | ON/OFF | 山上新化一路 1713 E ES |  |  | B2/D15_A1 | [8 empty] | 新化DS.1713E_ES | 1713E(山上一路) ES | LINE161 | [5 empty] | 155 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D15 | 新化DS | 161 | 161kV | 1510 | 新化～永資～統實線(1510) |  | DS1 | 1511 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0864 | 865 | 0128 | 2-36-00 | 2-36-01 | 2-00 | 1511 DS | ON/OFF | 新化永資統實線 1511 DS |  |  | B2/D15_A1 | [8 empty] | 新化DS.1511_DS | 1511(統實永資線) DS | LINE161 | [5 empty] | 156 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D15 | 新化DS | 161 | 161kV | 1510 | 新化～永資～統實線(1510) |  | DS2 | 1512 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0866 | 867 | 0129 | 2-36-02 | 2-36-03 | 2-01 | 1512 DS | ON/OFF | 新化永資統實線 1512 DS |  |  | B2/D15_A1 | [8 empty] | 新化DS.1512_DS | 1512(統實永資線) DS | LINE161 | [5 empty] | 157 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D15 | 新化DS | 161 | 161kV | 1510 | 新化～永資～統實線(1510) |  | DS3 | 1513 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0868 | 869 | 0130 | 2-36-04 | 2-36-05 | 2-02 | 1513 DS | ON/OFF | 新化永資統實線 1513 DS |  |  | B2/D15_A1 | [8 empty] | 新化DS.1513_DS | 1513(統實永資線) DS | LINE161 | [5 empty] | 158 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D15 | 新化DS | 161 | 161kV | 1510 | 新化～永資～統實線(1510) |  | ES3 | 1513E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [5 empty] | v | 0870 | 871 | 0131 | 2-36-06 | 2-36-07 | 2-03 | 1513 E ES | ON/OFF | 新化永資統實線 1513 E ES |  |  | B2/D15_A1 | [8 empty] | 新化DS.1513E_ES | 1513E(統實永資線) ES | LINE161 | [5 empty] | 159 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D15 | 新化DS | 11 | 11kV | KY21 | 新21線(KY21) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0844 |  | 0136 | 2-34-12 |  | 2-08 | 大洋線 | U/L | 新21線F1 KY21 LCO分流器 |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY21_ADJ | 11KV新21線(KY21) LCO分流器 U/L | FEEDER | [5 empty] | 160 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY22 | 新22線(KY22) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0845 |  | 0137 | 2-34-13 |  | 2-09 | 大坑線 | U/L | 新22線F2 KY22 LCO分流器 |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY22_ADJ | 11KV新22線(KY22) LCO分流器 U/L | FEEDER | [5 empty] | 161 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY23 | 新23線(KY23) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0846 |  | 0138 | 2-34-14 |  | 2-0A | 保東線 | U/L | 新23線F3 KY23 LCO分流器 |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY23_ADJ | 11KV新23線(KY23) LCO分流器 U/L | FEEDER | [5 empty] | 162 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY24 | 新24線(KY24) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0847 |  | 0139 | 2-34-15 |  | 2-0B | 山腳線 | U/L | 新24線F4 KY24 LCO分流器 |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY24_ADJ | 11KV新24線(KY24) LCO分流器 U/L | FEEDER | [5 empty] | 163 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY25 | 新25線(KY25) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0848 |  | 0140 | 2-35-00 |  | 2-0C | 化工線 | U/L | 新25線F5 KY25 LCO分流器 |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY25_ADJ | 11KV新25線(KY25) LCO分流器 U/L | FEEDER | [5 empty] | 164 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY26 | 新26線(KY26) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0849 |  | 0141 | 2-35-01 |  | 2-0D | 備用線 | U/L | 新26線F6 KY26 LCO分流器 |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY26_ADJ | 11KV新26線(KY26) LCO分流器 U/L | FEEDER | [5 empty] | 165 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY27 | 新27線(KY27) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0850 |  | 0142 | 2-35-02 |  | 2-0E | 科積線 | U/L | 新27線F7 KY27 LCO分流器 |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY27_ADJ | 11KV新27線(KY27) LCO分流器 U/L | FEEDER | [5 empty] | 166 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY28 | 新28線(KY28) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0851 |  | 0143 | 2-35-03 |  | 2-0F | 南茂線 | U/L | 新28線F8 KY28 LCO分流器 |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY28_ADJ | 11KV新28線(KY28) LCO分流器 U/L | FEEDER | [5 empty] | 167 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D15 | 新化DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0896 | 897 | 0144 | 2-38-00 | 2-38-01 | 2-10 | 1501 DS | ON/OFF | 161KV TIE 1501 DS |  |  | B2/D15_A1 | [8 empty] | 新化DS.1501_DS | 1501(TIE) DS | TIE | [5 empty] | 168 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D15 | 新化DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [5 empty] | v | 0898 | 899 | 0145 | 2-38-02 | 2-38-03 | 2-11 | 1502 DS | ON/OFF | 161KV TIE 1502 DS |  |  | B2/D15_A1 | [8 empty] | 新化DS.1502_DS | 1502(TIE) DS | TIE | [5 empty] | 169 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D15 | 新化DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0900 | 901 | 0146 | 2-38-04 | 2-38-05 | 2-12 | 1751 DS | ON/OFF | #1DTR一次 1751 DS |  |  | B2/D15_A1 | [8 empty] | 新化DS.1751_DS | 1751(#1DTR) DS | MTR | [5 empty] | 170 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D15 | 新化DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0902 | 903 | 0147 | 2-38-06 | 2-38-07 | 2-13 | 1752 DS | ON/OFF | #1DTR一次 1752 DS |  |  | B2/D15_A1 | [8 empty] | 新化DS.1752_DS | 1752(#1DTR) DS | MTR | [5 empty] | 171 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D15 | 新化DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0904 | 905 | 0148 | 2-38-08 | 2-38-09 | 2-14 | 1761 DS | ON/OFF | #2DTR一次 1761 DS |  |  | B2/D15_A1 | [8 empty] | 新化DS.1761_DS | 1761(#2DTR) DS | MTR | [5 empty] | 172 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D15 | 新化DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [5 empty] | v | 0906 | 907 | 0149 | 2-38-10 | 2-38-11 | 2-15 | 1762 DS | ON/OFF | #2DTR一次 1762 DS |  |  | B2/D15_A1 | [8 empty] | 新化DS.1762_DS | 1762(#2DTR) DS | MTR | [5 empty] | 173 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D15 | 新化DS | 11 | 11kV | KY29 | 新29線(KY29) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0852 |  | 0152 | 2-35-04 |  | 2-18 | 神隆線 | U/L | 新29線F9 KY29 LCO分流器 |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY29_ADJ | 11KV新29線(KY29) LCO分流器 U/L | FEEDER | [5 empty] | 174 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY30 | 新30線(KY30) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0853 |  | 0153 | 2-35-05 |  | 2-19 | 備用線 | U/L | 新30線F10 KY30 LCO分流器 |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY30_ADJ | 11KV新30線(KY30) LCO分流器 U/L | FEEDER | [5 empty] | 175 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY37 | 新37線(KY37) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0854 |  | 0154 | 2-35-06 |  | 2-1A | 科台線 | U/L | 新37線 F11 KY37 LCO分流器 |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY37_ADJ | 11KV新37線(KY37) LCO分流器 U/L | FEEDER | [5 empty] | 176 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY38 | 新38線(KY38) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0855 |  | 0155 | 2-35-07 |  | 2-1B | 科園線 | U/L | 新38線F12 KY38 LCO分流器 |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY38_ADJ | 11KV新38線(KY38) LCO分流器 U/L | FEEDER | [5 empty] | 177 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY39 | 新39線(KY39) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0856 |  | 0156 | 2-35-08 |  | 2-1C | 科南線 | U/L | 新39線F13 KY39 LCO分流器 |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY39_ADJ | 11KV新39線(KY39) LCO分流器 U/L | FEEDER | [5 empty] | 178 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY40 | 新40線(KY40) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0857 |  | 0157 | 2-35-09 |  | 2-1D | 備用線 | U/L | 新40線F14 KY40 LCO分流器 |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY40_ADJ | 11KV新40線(KY40) LCO分流器 U/L | FEEDER | [5 empty] | 179 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY31 | 新31線(KY31) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0858 |  | 0158 | 2-35-10 |  | 2-1E | 永化線 | U/L | 新31線 F15 KY31 LCO分流器 |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY31_ADJ | 11KV新31線(KY31) LCO分流器 U/L | FEEDER | [5 empty] | 180 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY32 | 新32線(KY32) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0859 |  | 0159 | 2-35-11 |  | 2-1F | 遠東線 | U/L | 新32線 F16 KY32 LCO分流器 |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY32_ADJ | 11KV新32線(KY32) LCO分流器 U/L | FEEDER | [5 empty] | 181 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY21 | 新21線(KY21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0778 |  | 0160 | 2-30-10 |  | 2-20 | 大洋線 | U/L | 新21線F1 KY21 79RY U/L |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY21_79UL | 11KV新21線(KY21) 79RY U/L | FEEDER | [5 empty] | 182 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY22 | 新22線(KY22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0779 |  | 0161 | 2-30-11 |  | 2-21 | 大坑線 | U/L | 新22線F2 KY22 79RY U/L |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY22_79UL | 11KV新22線(KY22) 79RY U/L | FEEDER | [5 empty] | 183 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY23 | 新23線(KY23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0780 |  | 0162 | 2-30-12 |  | 2-22 | 保東線 | U/L | 新23線F3 KY23 79RY U/L |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY23_79UL | 11KV新23線(KY23) 79RY U/L | FEEDER | [5 empty] | 184 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY24 | 新24線(KY24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0781 |  | 0163 | 2-30-13 |  | 2-23 | 山腳線 | U/L | 新24線F4 KY24 79RY U/L |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY24_79UL | 11KV新24線(KY24) 79RY U/L | FEEDER | [5 empty] | 185 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY25 | 新25線(KY25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0782 |  | 0164 | 2-30-14 |  | 2-24 | 化工線 | U/L | 新25線F5 KY25 79RY U/L |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY25_79UL | 11KV新25線(KY25) 79RY U/L | FEEDER | [5 empty] | 186 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY26 | 新26線(KY26) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0783 |  | 0165 | 2-30-15 |  | 2-25 | 備用線 | U/L | 新26線F6 KY26 79RY U/L |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY26_79UL | 11KV新26線(KY26) 79RY U/L | FEEDER | [5 empty] | 187 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0784 |  | 0166 | 2-31-00 |  | 2-26 | #1SC | A/M | #1SC 210 Q-CTL A/M |  |  | B3/D15_A1 | [8 empty] | 新化DS.210_A/M | 11KV #1SC 乏控器 A/M | SC | [5 empty] | 188 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D15 | 新化DS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [5 empty] | v | 0785 |  | 0167 | 2-31-01 |  | 2-27 | #2SC | A/M | #2SC 220 Q-CTL A/M |  |  | B3/D15_A1 | [8 empty] | 新化DS.220_A/M | 11KV #2SC 乏控器 A/M | SC | [5 empty] | 189 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D15 | 新化DS | 11 | 11kV | KY27 | 新27線(KY27) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0786 |  | 0168 | 2-31-02 |  | 2-28 | 科積線 | U/L | 新27線F7 KY27 79RY U/L |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY27_79UL | 11KV新27線(KY27) 79RY U/L | FEEDER | [5 empty] | 190 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY28 | 新28線(KY28) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0787 |  | 0169 | 2-31-03 |  | 2-29 | 南茂線 | U/L | 新28線F8 KY28 79RY U/L |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY28_79UL | 11KV新28線(KY28) 79RY U/L | FEEDER | [5 empty] | 191 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY29 | 新29線(KY29) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0788 |  | 0170 | 2-31-04 |  | 2-2A | 神隆線 | U/L | 新29線F9 KY29 79RY U/L |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY29_79UL | 11KV新29線(KY29) 79RY U/L | FEEDER | [5 empty] | 192 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY30 | 新30線(KY30) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0789 |  | 0171 | 2-31-05 |  | 2-2B | 備用線 | U/L | 新30線F10 KY30 79RY U/L |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY30_79UL | 11KV新30線(KY30) 79RY U/L | FEEDER | [5 empty] | 193 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | 230 | #3SC(230) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0790 |  | 0172 | 2-31-06 |  | 2-2C | #2ASC | A/M | #3SC 230 Q-CTL A/M |  |  | B3/D15_A1 | [8 empty] | 新化DS.230_A/M | 11KV #3SC 乏控器 A/M | SC | [5 empty] | 194 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D15 | 新化DS | 11 | 11kV | KY37 | 新37線(KY37) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0791 |  | 0173 | 2-31-07 |  | 2-2D | 科台線 | U/L | 新37線F11 KY37 79RY U/L |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY37_79UL | 11KV新37線(KY37) 79RY U/L | FEEDER | [5 empty] | 195 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY38 | 新38線(KY38) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0792 |  | 0174 | 2-31-08 |  | 2-2E | 科園線 | U/L | 新38線F12 KY38 79RY U/L |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY38_79UL | 11KV新38線(KY38) 79RY U/L | FEEDER | [5 empty] | 196 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY39 | 新39線(KY39) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0793 |  | 0175 | 2-31-09 |  | 2-2F | 科南線 | U/L | 新39線F13 KY39 79RY U/L |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY39_79UL | 11KV新39線(KY39) 79RY U/L | FEEDER | [5 empty] | 197 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY40 | 新40線(KY40) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0794 |  | 0176 | 2-31-10 |  | 2-30 | F14 | U/L | 新40線F14 KY40 79RY U/L |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY40_79UL | 11KV新40線(KY40) 79RY U/L | FEEDER | [5 empty] | 198 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | 260 | #6SC(260) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0795 |  | 0177 | 2-31-11 |  | 2-31 | #6SC | A/M | #6SC 260 Q-CTL A/M |  |  | B3/D15_A1 | [8 empty] | 新化DS.260_A/M | 11KV #6SC 乏控器 A/M | SC | [5 empty] | 199 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D15 | 新化DS | 11 | 11kV | KY31 | 新31線(KY31) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0796 |  | 0178 | 2-31-12 |  | 2-32 | 永化線 | U/L | 新31線 F15 KY31 79RY U/L |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY31_79UL | 11KV新31線(KY31) 79RY U/L | FEEDER | [5 empty] | 200 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY32 | 新32線(KY32) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0797 |  | 0179 | 2-31-13 |  | 2-33 | 遠東線 | U/L | 新32線 F16 KY32 79RY U/L |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY32_79UL | 11KV新32線(KY32) 79RY U/L | FEEDER | [5 empty] | 201 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY33 | 新33線(KY33) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0798 |  | 0180 | 2-31-14 |  | 2-34 | 社內線 | U/L | 新33線 F17 KY33 79RY U/L |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY33_79UL | 11KV新33線(KY33) 79RY U/L | FEEDER | [5 empty] | 202 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY34 | 新34線(KY34) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0799 |  | 0181 | 2-31-15 |  | 2-35 | 新東線 | U/L | 新34線 F18 KY34 79RY U/L |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY34_79UL | 11KV新34線(KY34) 79RY U/L | FEEDER | [5 empty] | 203 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY35 | 新35線(KY35) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0800 |  | 0182 | 2-32-00 |  | 2-36 | 北勢線 | U/L | 新35線 F19 KY35 79RY U/L |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY35_79UL | 11KV新35線(KY35) 79RY U/L | FEEDER | [5 empty] | 204 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY36 | 新36線(KY36) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0801 |  | 0183 | 2-32-01 |  | 2-37 | 西勢線 | U/L | 新36線 KY36 79RY U/L F20 |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY36_79UL | 11KV新36線(KY36) 79RY U/L | FEEDER | [5 empty] | 205 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | 250 | #5SC(250) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0802 |  | 0184 | 2-32-02 |  | 2-38 | #3ASC | A/M | #5SC 250 Q-CTL A/M |  |  | B3/D15_A1 | [8 empty] | 新化DS.250_A/M | 11KV #5SC 乏控器 A/M | SC | [5 empty] | 206 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D15 | 新化DS | 11 | 11kV | 240 | #4SC(240) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0803 |  | 0185 | 2-32-03 |  | 2-39 | #3BSC | A/M | #4SC 240 Q-CTL A/M |  |  | B3/D15_A1 | [8 empty] | 新化DS.240_A/M | 11KV #4SC 乏控器 A/M | SC | [5 empty] | 207 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D15 | 新化DS | 11 | 11kV | KY33 | 新33線(KY33) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0860 |  | 0186 | 2-35-12 |  | 2-3A | 社內線 | U/L | 新33線 F17 KY33 LCO分流器 |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY33_ADJ | 11KV新33線(KY33) LCO分流器 U/L | FEEDER | [5 empty] | 208 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY34 | 新34線(KY34) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0861 |  | 0187 | 2-35-13 |  | 2-3B | 新東線 | U/L | 新34線 F18 KY34 LCO分流器 |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY34_ADJ | 11KV新34線(KY34) LCO分流器 U/L | FEEDER | [5 empty] | 209 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY35 | 新35線(KY35) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0862 |  | 0188 | 2-35-14 |  | 2-3C | 北勢線 | U/L | 新35線 F19 KY35 LCO分流器 |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY35_ADJ | 11KV新35線(KY35) LCO分流器 U/L | FEEDER | [5 empty] | 210 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY36 | 新36線(KY36) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0863 |  | 0189 | 2-35-15 |  | 2-3D | 西勢線 | U/L | 新36線 F20 KY36 LCO分流器 |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY36_ADJ | 11KV新36線(KY36) LCO分流器 U/L | FEEDER | [5 empty] | 211 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D15 | 新化DS | 0 |  | RTU | RTU |  | ADCL1 |  |  | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | [5 empty] | 212 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D15 | 新化DS | 0 |  | RTU | RTU |  | ADCH1 |  |  | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.1 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | [5 empty] | 213 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D15 | 新化DS | 161 | 161kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | #1BUS | KV | 161KV #1BUS電壓 | kV_-210_210(-2000_2000) | aaa | B2/D15_A1 | [8 empty] | 新化DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | [5 empty] | 214 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D15 | 新化DS | 161 | 161kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0003 |  |  | 1-83 |  |  | #1BUS | KV | 161KV #2BUS電壓 | kV_-210_210(-2000_2000) | aab | B2/D15_A1 | [8 empty] | 新化DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | [5 empty] | 215 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D15 | 新化DS | 161 | 161kV | 1740 | 道爺~安南~新化線(1740) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 1740 | MW | 道爺安南新化線1740 瓦 | MW_-448_448(-2000_2000) |  | B2/D15_A1 | [8 empty] | 新化DS.1740_MW | 道爺安南新化線 MW | LINE161 | [5 empty] | 216 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.896 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
D15 | 新化DS | 161 | 161kV | 1740 | 道爺~安南~新化線(1740) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 1740 | MVAR | 道爺安南新化線1740 乏 | MVAR_-448_448(-2000_2000) |  | B2/D15_A1 | [8 empty] | 新化DS.1740_MVAR | 道爺安南新化線 MVAR | LINE161 | [5 empty] | 217 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.896 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
D15 | 新化DS | 161 | 161kV | 1730 | 道爺~和順~新化線(1730) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 1730 | MW | 道爺和順新化線 1730 瓦 | MW_-448_448(-2000_2000) |  | B2/D15_A1 | [8 empty] | 新化DS.1730_MW | 道爺和順新化線 MW | LINE161 | [5 empty] | 218 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.896 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
D15 | 新化DS | 161 | 161kV | 1730 | 道爺~和順~新化線(1730) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 1730 | MVAR | 道爺和順新化線 1730 乏 | MVAR_-448_448(-2000_2000) |  | B2/D15_A1 | [8 empty] | 新化DS.1730_MVAR | 道爺和順新化線 MVAR | LINE161 | [5 empty] | 219 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.896 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
D15 | 新化DS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | 1720 | MW | 山上新化二路1720 瓦 | MW_-560_560(-2000_2000) |  | B2/D15_A1 | [8 empty] | 新化DS.1720_MW | 山上二路 MW | LINE161 | [5 empty] | 220 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D15 | 新化DS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 1720 | MVAR | 山上新化二路1720 乏 | MVAR_-560_560(-2000_2000) |  | B2/D15_A1 | [8 empty] | 新化DS.1720_MVAR | 山上二路 MVAR | LINE161 | [5 empty] | 221 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D15 | 新化DS | 161 | 161kV | 1710 | 山上～新化一路(1710) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | 1710 | MW | 山上新化一路1710 瓦 | MW_-560_560(-2000_2000) |  | B2/D15_A1 | [8 empty] | 新化DS.1710_MW | 山上一路 MW | LINE161 | [5 empty] | 222 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D15 | 新化DS | 161 | 161kV | 1710 | 山上～新化一路(1710) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | 1710 | MVAR | 山上新化一路1710 乏 | MVAR_-560_560(-2000_2000) |  | B2/D15_A1 | [8 empty] | 新化DS.1710_MVAR | 山上一路 MVAR | LINE161 | [5 empty] | 223 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D15 | 新化DS | 161 | 161kV | 1510 | 新化～永資～統實線(1510) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0012 |  |  | 1-8C |  |  | 1510 | MW | 新化永資統實線1510 瓦 | MW_-560_560(-2000_2000) |  | B2/D15_A1 | [8 empty] | 新化DS.1510_MW | 統實永資線 MW | LINE161 | [5 empty] | 224 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D15 | 新化DS | 161 | 161kV | 1510 | 新化～永資～統實線(1510) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0013 |  |  | 1-8D |  |  | 1510 | MVAR | 新化永資統實線1510 乏 | MVAR_-560_560(-2000_2000) |  | B2/D15_A1 | [8 empty] | 新化DS.1510_MVAR | 統實永資線 MVAR | LINE161 | [5 empty] | 225 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D15 | 新化DS | 0 |  | StaDev | 所內設施 |  | DCV_P |  |  | MvMoment | 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | Locate Empty | V | DC-P | kV_-150_150(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.直流P電源電壓 | 直流P電源電壓 | OTHER | [5 empty] | 226 |  |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 | 0.01 | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D15 | 新化DS | 0 |  | StaDev | 所內設施 |  | DCV_N |  |  | MvMoment | 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | Locate Empty | V | DC-N | kV_-150_150(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.直流N電源電壓 | 直流N電源電壓 | OTHER | [5 empty] | 227 |  |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 | 0.01 | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D15 | 新化DS | 161 | 161kV | 1500 | TIE(1500) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | 161KV | A | 161KV TIE R相電流 | A_-2000_2000(-2000_2000) |  | B2/D15_A1 | [8 empty] | 新化DS.1500TIE_AMP | 1500TIE AMP | TIE | [5 empty] | 228 |  |  |  |  | AI | [5 empty] | C20R2000 | 1900 | 2000 | 2001 | 2002 | 0.3 | -1900 | -2000 | -2001 | -2002 | 1 | 0.01 | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
D15 | 新化DS |  |  | 1DTR | #1DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | #1DTR | 油溫 | #1DTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/D15_A1 | [8 empty] | 新化DS.#1DTR_OIL | #1DTR 油溫 | MTR | [5 empty] | 229 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D15 | 新化DS |  |  | 1DTR(A) | #1DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | #1A DTR | 線溫 | #1A DTR 線溫 | COIL_-120_120(-2000_2000) |  | B1/D15_A1 | [8 empty] | 新化DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | [5 empty] | 230 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D15 | 新化DS |  |  | 1DTR(B) | #1DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | #1B DTR | 線溫 | #1B DTR 線溫 | COIL_-120_120(-2000_2000) |  | B1/D15_A1 | [8 empty] | 新化DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | [5 empty] | 231 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D15 | 新化DS |  |  | 2DTR | #2DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | #2 DTR | 油溫 | #2 DTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/D15_A1 | [8 empty] | 新化DS.#2DTR_OIL | #2DTR 油溫 | MTR | [5 empty] | 232 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D15 | 新化DS |  |  | 2DTR(A) | #2DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0027 |  |  | 1-9B |  |  | #2A DTR | 線溫 | #2A DTR 線溫 | COIL_-120_120(-2000_2000) |  | B1/D15_A1 | [8 empty] | 新化DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | [5 empty] | 233 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D15 | 新化DS |  |  | 2DTR(B) | #2DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | #2B DTR | 線溫 | #2B DTR 線溫 | COIL_-120_120(-2000_2000) |  | B1/D15_A1 | [8 empty] | 新化DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | [5 empty] | 234 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D15 | 新化DS | 161 | 161kV | 1510 | 新化～永資～統實線(1510) |  | OilPreR |  |  | MvMoment | R相油壓 |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | 1510 | KG | 新化永資統實線 1510 R相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/D15_A1 | [8 empty] | 新化DS.1510_OF_R | 新化永資統實線 R相 油壓 | OTHER | [5 empty] | 235 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 1 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D15 | 新化DS | 161 | 161kV | 1510 | 新化～永資～統實線(1510) |  | OilPreS |  |  | MvMoment | S相油壓 |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | 1510 | KG | 新化永資統實線 1510 S相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/D15_A1 | [8 empty] | 新化DS.1510_OF_S | 新化永資統實線 S相 油壓 | OTHER | [5 empty] | 236 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 1 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D15 | 新化DS | 161 | 161kV | 1510 | 新化～永資～統實線(1510) |  | OilPreT |  |  | MvMoment | T相油壓 |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | 1510 | KG | 新化永資統實線 1510 T相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/D15_A1 | [8 empty] | 新化DS.1510_OF_T | 新化永資統實線 T相 油壓 | OTHER | [5 empty] | 237 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 1 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | 310 | MW | D1A 310 瓦 | MW_-36_36(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | [5 empty] | 238 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D15 | 新化DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | 310 | MVAR | D1A 310 乏 | MVAR_-36_36(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | [5 empty] | 239 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D15 | 新化DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | 310 | A | D1A 310 R相電流 | A_-2000_2000(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | [5 empty] | 240 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | 310 | A | D1A 310 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | [5 empty] | 241 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | 310 | A | D1A 310 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | [5 empty] | 242 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY21 | 新21線(KY21) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | 大洋線 | MVAR | 新21線F1 KY21 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新21線KVAR | 11KV新21線 KVAR | FEEDER | [5 empty] | 243 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY21 | 新21線(KY21) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | 大洋線 | A | 新21線F1 KY21 R相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新21線A1 | 11KV新21線 R相AMP | FEEDER | [5 empty] | 244 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY21 | 新21線(KY21) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | 大洋線 | A | 新21線F1 KY21 S相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新21線A2 | 11KV新21線 S相AMP | FEEDER | [5 empty] | 245 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY21 | 新21線(KY21) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | 大洋線 | A | 新21線F1 KY21 T相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新21線A3 | 11KV新21線 T相AMP | FEEDER | [5 empty] | 246 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY22 | 新22線(KY22) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | 大坑線 | MVAR | 新22線F2 KY22 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新22線KVAR | 11KV新22線 KVAR | FEEDER | [5 empty] | 247 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY22 | 新22線(KY22) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | 大坑線 | A | 新22線F2 KY22 R相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新22線A1 | 11KV新22線 R相AMP | FEEDER | [5 empty] | 248 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY22 | 新22線(KY22) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | 大坑線 | A | 新22線F2 KY22 S相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新22線A2 | 11KV新22線 S相AMP | FEEDER | [5 empty] | 249 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY22 | 新22線(KY22) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | 大坑線 | A | 新22線F2 KY22 T相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新22線A3 | 11KV新22線 T相AMP | FEEDER | [5 empty] | 250 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY23 | 新23線(KY23) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | 保東線 | MVAR | 新23線F3 KY23 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新23線KVAR | 11KV新23線 KVAR | FEEDER | [5 empty] | 251 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY23 | 新23線(KY23) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | 保東線 | A | 新23線F3 KY23 R相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新23線A1 | 11KV新23線 R相AMP | FEEDER | [5 empty] | 252 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY23 | 新23線(KY23) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | 保東線 | A | 新23線F3 KY23 S相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新23線A2 | 11KV新23線 S相AMP | FEEDER | [5 empty] | 253 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY23 | 新23線(KY23) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | 保東線 | A | 新23線F3 KY23 T相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新23線A3 | 11KV新23線 T相AMP | FEEDER | [5 empty] | 254 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY24 | 新24線(KY24) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | 山腳線 | MVAR | 新24線F4 KY24 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新24線KVAR | 11KV新24線 KVAR | FEEDER | [5 empty] | 255 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY24 | 新24線(KY24) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | 山腳線 | A | 新24線F4 KY24 R相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新24線A1 | 11KV新24線 R相AMP | FEEDER | [5 empty] | 256 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY24 | 新24線(KY24) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0060 |  |  | 1-BC |  |  | 山腳線 | A | 新24線F4 KY24 S相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新24線A2 | 11KV新24線 S相AMP | FEEDER | [5 empty] | 257 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY24 | 新24線(KY24) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | 山腳線 | MVAR | 新24線F4 KY24 T相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新24線A3 | 11KV新24線 T相AMP | FEEDER | [5 empty] | 258 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY25 | 新25線(KY25) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | 化工線 | A | 新25線F5 KY25 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新25線KVAR | 11KV新25線 KVAR | FEEDER | [5 empty] | 259 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY25 | 新25線(KY25) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0063 |  |  | 1-BF |  |  | 化工線 | A | 新25線F5 KY25 R相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新25線A1 | 11KV新25線 R相AMP | FEEDER | [5 empty] | 260 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 0 |  | RTU | RTU |  | ADCL2 |  |  | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | [5 empty] | 261 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D15 | 新化DS | 0 |  | RTU | RTU |  | ADCH2 |  |  | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.2 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | [5 empty] | 262 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY25 | 新25線(KY25) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | 化工線 | A | 新25線F5 KY25 S相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新25線A2 | 11KV新25線 S相AMP | FEEDER | [5 empty] | 263 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY25 | 新25線(KY25) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | 化工線 | A | 新25線F5 KY25 T相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新25線A3 | 11KV新25線 T相AMP | FEEDER | [5 empty] | 264 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY26 | 新26線(KY26) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | F6 | MVAR | 新26線F6 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新26線KVAR | 11KV新26線 KVAR | FEEDER | [5 empty] | 265 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY26 | 新26線(KY26) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | F6 | A | 新26線F6 R相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新26線A1 | 11KV新26線 R相AMP | FEEDER | [5 empty] | 266 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY26 | 新26線(KY26) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | F6 | A | 新26線F6 S相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新26線A2 | 11KV新26線 S相AMP | FEEDER | [5 empty] | 267 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY26 | 新26線(KY26) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | F6 | A | 新26線F6 T相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新26線A3 | 11KV新26線 T相AMP | FEEDER | [5 empty] | 268 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 1ABUS | #1ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0072 |  |  | 1-C8 |  |  | D1A | KV | D1A 310 BUS PT 電壓 | kV_-9_9(-2000_2000) | aaa | B3/D15_A1 | [8 empty] | 新化DS.11KV#1ABUS_KV | 11KV #1ABUS KV | BUS | [5 empty] | 269 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D15 | 新化DS | 11 | 11kV | 100 | TIE(100) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | #1TIE | A | #1TIE R相電流 | A_-2000_2000(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.11KV_100_A1 | 11KV 100 R相AMP | TIE | [5 empty] | 270 |  |  |  |  | AI | [5 empty] | C20R1200 | 1140 | 1200 | 1320 | 1476 | 2.27 | -1140 | -1200 | -1320 | -1476 | 1 | 0.01 | C20R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 100 | TIE(100) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | #1TIE | A | #1TIE S相電流 | A_-2000_2000(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.11KV_100_A2 | 11KV 100 S相AMP | TIE | [5 empty] | 271 |  |  |  |  | AI | [5 empty] | C20R1200 | 1140 | 1200 | 1320 | 1476 | 2.27 | -1140 | -1200 | -1320 | -1476 | 1 | 0.01 | C20R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 100 | TIE(100) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | #1TIE | A | #1TIE T相電流 | A_-2000_2000(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.11KV_100_A3 | 11KV 100 T相AMP | TIE | [5 empty] | 272 |  |  |  |  | AI | [5 empty] | C20R1200 | 1140 | 1200 | 1320 | 1476 | 2.27 | -1140 | -1200 | -1320 | -1476 | 1 | 0.01 | C20R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | 320 | MW | D1B 320 瓦 | MW_-36_36(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | [5 empty] | 273 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D15 | 新化DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | 320 | MVAR | D1B 320 乏 | MVAR_-36_36(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | [5 empty] | 274 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D15 | 新化DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | 320 | A | D1B 320 R相電流 | A_-2000_2000(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | [5 empty] | 275 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | 320 | A | D1B 320 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | [5 empty] | 276 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | 320 | A | D1B 320 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | [5 empty] | 277 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY27 | 新27線(KY27) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | 科積線 | MVAR | 新27線 F7 KY27乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新27線KVAR | 11KV新27線 KVAR | FEEDER | [5 empty] | 278 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY27 | 新27線(KY27) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | 科積線 | A | 新27線 F7 KY27 R相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新27線A1 | 11KV新27線 R相AMP | FEEDER | [5 empty] | 279 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY27 | 新27線(KY27) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | 科積線 | A | 新27線 F7 KY27 S相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新27線A2 | 11KV新27線 S相AMP | FEEDER | [5 empty] | 280 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY27 | 新27線(KY27) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | 科積線 | A | 新27線 F7 KY27 T相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新27線A3 | 11KV新27線 T相AMP | FEEDER | [5 empty] | 281 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY28 | 新28線(KY28) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | 南茂線 | MVAR | 新28線 F8 KY28乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新28線KVAR | 11KV新28線 KVAR | FEEDER | [5 empty] | 282 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY28 | 新28線(KY28) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | 南茂線 | A | 新28線 F8 KY28 R相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新28線A1 | 11KV新28線 R相AMP | FEEDER | [5 empty] | 283 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY28 | 新28線(KY28) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | 南茂線 | A | 新28線 F8 KY28 S相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新28線A2 | 11KV新28線 S相AMP | FEEDER | [5 empty] | 284 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY28 | 新28線(KY28) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | 南茂線 | A | 新28線 F8 KY28 T相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新28線A3 | 11KV新28線 T相AMP | FEEDER | [5 empty] | 285 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY29 | 新29線(KY29) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | 神隆線 | MVAR | 新29線 F9 KY29乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新29線KVAR | 11KV新29線 KVAR | FEEDER | [5 empty] | 286 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY29 | 新29線(KY29) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | 神隆線 | A | 新29線 F9 KY29 R相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新29線A1 | 11KV新29線 R相AMP | FEEDER | [5 empty] | 287 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY29 | 新29線(KY29) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | 神隆線 | A | 新29線 F9 KY29 S相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新29線A2 | 11KV新29線 S相AMP | FEEDER | [5 empty] | 288 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY29 | 新29線(KY29) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | 神隆線 | A | 新29線 F9 KY29 T相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新29線A3 | 11KV新29線 T相AMP | FEEDER | [5 empty] | 289 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY30 | 新30線(KY30) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | F10 | MVAR | 新30線F10 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新30線KVAR | 11KV新30線 KVAR | FEEDER | [5 empty] | 290 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY30 | 新30線(KY30) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | F10 | A | 新30線F10 R相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新30線A1 | 11KV新30線 R相AMP | FEEDER | [5 empty] | 291 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY30 | 新30線(KY30) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | F10 | A | 新30線F10 S相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新30線A2 | 11KV新30線 S相AMP | FEEDER | [5 empty] | 292 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY30 | 新30線(KY30) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | F10 | A | 新30線F10 T相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新30線A3 | 11KV新30線 T相AMP | FEEDER | [5 empty] | 293 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 1BBUS | #1BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0097 |  |  | 1-E1 |  |  | D1B | KV | D1B 320 BUS PT電壓 | kV_-9_9(-2000_2000) | baa | B3/D15_A1 | [8 empty] | 新化DS.11KV#1BBUS_KV | 11KV #1BBUS KV | BUS | [5 empty] | 294 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D15 | 新化DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0098 |  |  | 1-E2 |  |  | 340 | MW | D2B 340 瓦 | MW_-36_36(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | [5 empty] | 295 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D15 | 新化DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | 340 | MVAR | D2B 340 乏 | MVAR_-36_36(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | [5 empty] | 296 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D15 | 新化DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | 340 | A | D2B 340 R相電流 | A_-2000_2000(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | [5 empty] | 297 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0101 |  |  | 1-E5 |  |  | 340 | A | D2B 340 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | [5 empty] | 298 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | 340 | A | D2B 340 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | [5 empty] | 299 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY37 | 新37線(KY37) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | 科台線 | MVAR | 新37線 F11 KY37乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新37線KVAR | 11KV新37線 KVAR | FEEDER | [5 empty] | 300 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY37 | 新37線(KY37) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | 科台線 | A | 新37線 F11 KY37 R相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新37線A1 | 11KV新37線 R相AMP | FEEDER | [5 empty] | 301 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY37 | 新37線(KY37) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | 科台線 | A | 新37線 F11 KY37 S相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新37線A2 | 11KV新37線 S相AMP | FEEDER | [5 empty] | 302 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY37 | 新37線(KY37) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | 科台線 | A | 新37線 F11 KY37 T相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新37線A3 | 11KV新37線 T相AMP | FEEDER | [5 empty] | 303 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY38 | 新38線(KY38) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | 科園線 | MVAR | 新28線 F12 KY38 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新38線KVAR | 11KV新38線 KVAR | FEEDER | [5 empty] | 304 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY38 | 新38線(KY38) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | 科園線 | A | 新38線 F12 KY38 R相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新38線A1 | 11KV新38線 R相AMP | FEEDER | [5 empty] | 305 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY38 | 新38線(KY38) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | 科園線 | A | 新38線 F12 KY38 S相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新38線A2 | 11KV新38線 S相AMP | FEEDER | [5 empty] | 306 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY38 | 新38線(KY38) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | 科園線 | A | 新38線 F12 KY38T相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新38線A3 | 11KV新38線 T相AMP | FEEDER | [5 empty] | 307 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY39 | 新39線(KY39) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | F13 | MVAR | 新39線 F13 乏 KY39 | KVAR_-10800_10800(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新39線KVAR | 11KV新39線 KVAR | FEEDER | [5 empty] | 308 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY39 | 新39線(KY39) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | F13 | A | 新39線 F13 KY39 R相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新39線A1 | 11KV新39線 R相AMP | FEEDER | [5 empty] | 309 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY39 | 新39線(KY39) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | F13 | A | 新39線 F13 KY39 S相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新39線A2 | 11KV新39線 S相AMP | FEEDER | [5 empty] | 310 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY39 | 新39線(KY39) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | F13 | A | 新39線 F13 KY39 T相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新39線A3 | 11KV新39線 T相AMP | FEEDER | [5 empty] | 311 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY40 | 新40線(KY40) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | F14 | MVAR | 新40線F14 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新40線KVAR | 11KV新40線 KVAR | FEEDER | [5 empty] | 312 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY40 | 新40線(KY40) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | F14 | A | 新40線F14 R相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新40線A1 | 11KV新40線 R相AMP | FEEDER | [5 empty] | 313 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY40 | 新40線(KY40) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | F14 | A | 新40線F14 S相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新40線A2 | 11KV新40線 S相AMP | FEEDER | [5 empty] | 314 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY40 | 新40線(KY40) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | F14 | A | 新40線F14 T相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新40線A3 | 11KV新40線 T相AMP | FEEDER | [5 empty] | 315 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 2BBUS | #2BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0119 |  |  | 1-F7 |  |  | D2B | KV | D2B 330 BUS PT電壓 | kV_-9_9(-2000_2000) | bba | B3/D15_A1 | [8 empty] | 新化DS.11KV#2BBUS_KV | 11KV #2BBUS KV | BUS | [5 empty] | 316 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D15 | 新化DS | 11 | 11kV | 200 | TIE(200) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | #2TIE | A | #2TIE R相電流 | A_-2000_2000(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.11KV_200_A1 | 11KV 200 R相AMP | TIE | [5 empty] | 317 |  |  |  |  | AI | [5 empty] | C20R1200 | 1140 | 1200 | 1320 | 1476 | 2.27 | -1140 | -1200 | -1320 | -1476 | 1 | 0.01 | C20R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 200 | TIE(200) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | #2TIE | A | #2TIE S相電流 | A_-2000_2000(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.11KV_200_A2 | 11KV 200 S相AMP | TIE | [5 empty] | 318 |  |  |  |  | AI | [5 empty] | C20R1200 | 1140 | 1200 | 1320 | 1476 | 2.27 | -1140 | -1200 | -1320 | -1476 | 1 | 0.01 | C20R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 200 | TIE(200) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | #2TIE | A | #2TIE T相電流 | A_-2000_2000(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.11KV_200_A3 | 11KV 200 T相AMP | TIE | [5 empty] | 319 |  |  |  |  | AI | [5 empty] | C20R1200 | 1140 | 1200 | 1320 | 1476 | 2.27 | -1140 | -1200 | -1320 | -1476 | 1 | 0.01 | C20R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | 330 | MW | D2A 330 瓦 | MW_-36_36(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | [5 empty] | 320 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D15 | 新化DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | 330 | MVAR | D2A 330 乏 | MVAR_-36_36(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | [5 empty] | 321 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D15 | 新化DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | 330 | A | D2A 330 R相電流 | A_-2000_2000(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | [5 empty] | 322 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | 330 | A | D2A 330 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | [5 empty] | 323 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | 330 | A | D2A 330 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | [5 empty] | 324 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D15 | 新化DS | 0 |  | RTU | RTU |  | ADCL3 |  |  | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.3AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | [5 empty] | 325 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D15 | 新化DS | 0 |  | RTU | RTU |  | ADCH3 |  |  | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No3AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | [5 empty] | 326 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY31 | 新31線(KY31) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | 永化線 | MVAR | 新31線 F15 KY31 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新31線KVAR | 11KV新31線 KVAR | FEEDER | [5 empty] | 327 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY31 | 新31線(KY31) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | 永化線 | A | 新31線 F15 KY31 R相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新31線A1 | 11KV新31線 R相AMP | FEEDER | [5 empty] | 328 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY31 | 新31線(KY31) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0133 |  |  | 2-85 |  |  | 永化線 | A | 新31線 F15 KY31 S相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新31線A2 | 11KV新31線 S相AMP | FEEDER | [5 empty] | 329 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY31 | 新31線(KY31) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | 永化線 | A | 新31線 F15 KY31 T相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新31線A3 | 11KV新31線 T相AMP | FEEDER | [5 empty] | 330 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY32 | 新32線(KY32) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0135 |  |  | 2-87 |  |  | 遠東線 | MVAR | 新32線 F16 KY32 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新32線KVAR | 11KV新32線 KVAR | FEEDER | [5 empty] | 331 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY32 | 新32線(KY32) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0136 |  |  | 2-88 |  |  | 遠東線 | A | 新32線 F16 KY32 R相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新32線A1 | 11KV新32線 R相AMP | FEEDER | [5 empty] | 332 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY32 | 新32線(KY32) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0137 |  |  | 2-89 |  |  | 遠東線 | A | 新32線 F16 KY32 S相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新32線A2 | 11KV新32線 S相AMP | FEEDER | [5 empty] | 333 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY32 | 新32線(KY32) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0138 |  |  | 2-8A |  |  | 遠東線 | A | 新32線 F16 KY32 T相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新32線A3 | 11KV新32線 T相AMP | FEEDER | [5 empty] | 334 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY33 | 新33線(KY33) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0139 |  |  | 2-8B |  |  | 社內線 | MVAR | 新33線 F17 KY33 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新33線KVAR | 11KV新33線 KVAR | FEEDER | [5 empty] | 335 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY33 | 新33線(KY33) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0140 |  |  | 2-8C |  |  | 社內線 | A | 新33線 F17 KY33 R相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新33線A1 | 11KV新33線 R相AMP | FEEDER | [5 empty] | 336 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY33 | 新33線(KY33) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0141 |  |  | 2-8D |  |  | 社內線 | A | 新33線 F17 KY33 S相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新33線A2 | 11KV新33線 S相AMP | FEEDER | [5 empty] | 337 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY33 | 新33線(KY33) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0142 |  |  | 2-8E |  |  | 社內線 | A | 新33線 F17 KY33 T相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新33線A3 | 11KV新33線 T相AMP | FEEDER | [5 empty] | 338 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY34 | 新34線(KY34) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0143 |  |  | 2-8F |  |  | 新東線 | MVAR | 新34線 F18 KY34 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新34線KVAR | 11KV新34線 KVAR | FEEDER | [5 empty] | 339 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY34 | 新34線(KY34) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0144 |  |  | 2-90 |  |  | 新東線 | A | 新34線 F18 KY34 R相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新34線A1 | 11KV新34線 R相AMP | FEEDER | [5 empty] | 340 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY34 | 新34線(KY34) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0145 |  |  | 2-91 |  |  | 新東線 | A | 新34線 F18 KY34 S相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新34線A2 | 11KV新34線 S相AMP | FEEDER | [5 empty] | 341 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY34 | 新34線(KY34) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0146 |  |  | 2-92 |  |  | 新東線 | A | 新34線 F18 KY34 T相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新34線A3 | 11KV新34線 T相AMP | FEEDER | [5 empty] | 342 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY35 | 新35線(KY35) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0147 |  |  | 2-93 |  |  | 北勢線 | MVAR | 新35線 F19 KY35 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新35線KVAR | 11KV新35線 KVAR | FEEDER | [5 empty] | 343 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY35 | 新35線(KY35) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0148 |  |  | 2-94 |  |  | 北勢線 | A | 新35線 F19 KY35 R相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新35線A1 | 11KV新35線 R相AMP | FEEDER | [5 empty] | 344 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY35 | 新35線(KY35) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0149 |  |  | 2-95 |  |  | 北勢線 | A | 新35線 F19 KY35 S相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新35線A2 | 11KV新35線 S相AMP | FEEDER | [5 empty] | 345 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY35 | 新35線(KY35) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0150 |  |  | 2-96 |  |  | 北勢線 | A | 新35線 F19 KY35 T相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新35線A3 | 11KV新35線 T相AMP | FEEDER | [5 empty] | 346 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY36 | 新36線(KY36) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0151 |  |  | 2-97 |  |  | 西勢線 | MVAR | 新36線 F20 KY36 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新36線KVAR | 11KV新36線 KVAR | FEEDER | [5 empty] | 347 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY36 | 新36線(KY36) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0152 |  |  | 2-98 |  |  | 西勢線 | A | 新36線 F20 KY36 R相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新36線A1 | 11KV新36線 R相AMP | FEEDER | [5 empty] | 348 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY36 | 新36線(KY36) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0153 |  |  | 2-99 |  |  | 西勢線 | A | 新36線 F20 KY36 S相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新36線A2 | 11KV新36線 S相AMP | FEEDER | [5 empty] | 349 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY36 | 新36線(KY36) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0154 |  |  | 2-9A |  |  | 西勢線 | A | 新36線 F20 KY36 T相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新36線A3 | 11KV新36線 T相AMP | FEEDER | [5 empty] | 350 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 2ABUS | #2ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0155 |  |  | 2-9B |  |  | D2A | KV | D2A 330 BUS PT電壓 | kV_-9_9(-2000_2000) | aba | B3/D15_A1 | [8 empty] | 新化DS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS | [5 empty] | 351 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D15 | 新化DS | 11 | 11kV | KY21 | 新21線(KY21) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0160 |  |  | 2-A0 |  |  | 大洋線 | A | 新21線F1 KY21 零相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新21線A0 | 11KV新21線 N相AMP | FEEDER | [5 empty] | 352 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY22 | 新22線(KY22) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0161 |  |  | 2-A1 |  |  | 大坑線 | A | 新22線F2 KY22 零相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新22線A0 | 11KV新22線 N相AMP | FEEDER | [5 empty] | 353 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY23 | 新23線(KY23) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0162 |  |  | 2-A2 |  |  | 保東線 | A | 新23線F3 KY23 零相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新23線A0 | 11KV新23線 N相AMP | FEEDER | [5 empty] | 354 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY24 | 新24線(KY24) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0163 |  |  | 2-A3 |  |  | 山腳線 | A | 新24線F4 KY24 零相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新24線A0 | 11KV新24線 N相AMP | FEEDER | [5 empty] | 355 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY25 | 新25線(KY25) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0164 |  |  | 2-A4 |  |  | 化工線 | A | 新25線F5 KY25 零相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新25線A0 | 11KV新25線 N相AMP | FEEDER | [5 empty] | 356 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY26 | 新26線(KY26) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0165 |  |  | 2-A5 |  |  | 備用線 | A | 新26線F6 KY26 零相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新26線A0 | 11KV新26線 N相AMP | FEEDER | [5 empty] | 357 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY27 | 新27線(KY27) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0166 |  |  | 2-A6 |  |  | 科積線 | A | 新27線F7 KY27 零相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新27線A0 | 11KV新27線 N相AMP | FEEDER | [5 empty] | 358 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY28 | 新28線(KY28) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0167 |  |  | 2-A7 |  |  | 南茂線 | A | 新28線F8 KY28 零相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新28線A0 | 11KV新28線 N相AMP | FEEDER | [5 empty] | 359 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY29 | 新29線(KY29) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0168 |  |  | 2-A8 |  |  | 神隆線 | A | 新29線F9 KY29 零相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新29線A0 | 11KV新29線 N相AMP | FEEDER | [5 empty] | 360 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY30 | 新30線(KY30) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0169 |  |  | 2-A9 |  |  | 備用線 | A | 新30線F10 KY30 零相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新30線A0 | 11KV新30線 N相AMP | FEEDER | [5 empty] | 361 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY37 | 新37線(KY37) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0170 |  |  | 2-AA |  |  | 科台線 | A | 新37線 F11 KY37零相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新37線A0 | 11KV新37線 N相AMP | FEEDER | [5 empty] | 362 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY38 | 新38線(KY38) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0171 |  |  | 2-AB |  |  | 科園線 | A | 新38線F12 KY38 零相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新38線A0 | 11KV新38線 N相AMP | FEEDER | [5 empty] | 363 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY39 | 新39線(KY39) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0172 |  |  | 2-AC |  |  | 科南線 | A | 新39線F13 KY39 零相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新39線A0 | 11KV新39線 N相AMP | FEEDER | [5 empty] | 364 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY40 | 新40線(KY40) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0173 |  |  | 2-AD |  |  | 備用線 | A | 新40線F14 KY40 零相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新40線A0 | 11KV新40線 N相AMP | FEEDER | [5 empty] | 365 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY31 | 新31線(KY31) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0174 |  |  | 2-AE |  |  | 永化線 | A | 新31線 F15 KY31 零相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新31線A0 | 11KV新31線 N相AMP | FEEDER | [5 empty] | 366 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY32 | 新32線(KY32) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0175 |  |  | 2-AF |  |  | 遠東線 | A | 新32線 F16 KY32 零相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新32線A0 | 11KV新32線 N相AMP | FEEDER | [5 empty] | 367 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY33 | 新33線(KY33) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0176 |  |  | 2-B0 |  |  | 社內線 | A | 新33線 F17 KY33 零相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新33線A0 | 11KV新33線 N相AMP | FEEDER | [5 empty] | 368 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY34 | 新34線(KY34) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0177 |  |  | 2-B1 |  |  | 新東線 | A | 新34線 F18 KY34 零相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新34線A0 | 11KV新34線 N相AMP | FEEDER | [5 empty] | 369 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY35 | 新35線(KY35) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0178 |  |  | 2-B2 |  |  | 北勢線 | A | 新35線 F19 KY35 零相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新35線A0 | 11KV新35線 N相AMP | FEEDER | [5 empty] | 370 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | KY36 | 新36線(KY36) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0179 |  |  | 2-B3 |  |  | 西勢線 | A | 新36線 F20 KY36 零相電流 | A_-600_600(-2000_2000) |  | B2/D15_D1 | [8 empty] | 新化DS.新36線A0 | 11KV新36線 N相AMP | FEEDER | [5 empty] | 371 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 0 |  | RTU | RTU |  | ADCL4 |  |  | MvMoment | No4 AI參考點 10% |  | Y |  | AI | [6 empty] | 0192 |  |  | 2-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.4AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | [5 empty] | 372 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D15 | 新化DS | 0 |  | RTU | RTU |  | ADCH4 |  |  | MvMoment | No4 AI參考點 90% |  | Y |  | AI | [6 empty] | 0193 |  |  | 2-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No4AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D15_A1 | [8 empty] | 新化DS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | [5 empty] | 373 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D15 | 新化DS | 161 | 161kV | 1740 | 道爺~安南~新化線(1740) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0001 |  |  | 1-00-01 |  |  | 1740 | 87A | 道爺安南新化線 1740 87A |  |  | B2/D15_A1 | [8 empty] | 新化DS.1740_87A | 道爺安南新化線(1740) 87RY | LINE161 | [5 empty] | 374 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1740 | 道爺~安南~新化線(1740) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | 1740 | PHA | 道爺安南新化線 1740 PHA |  |  | B2/D15_A1 | [8 empty] | 新化DS.1740_PHA | 道爺安南新化線(1740) 相間RY | LINE161 | [5 empty] | 375 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1740 | 道爺~安南~新化線(1740) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0004 |  |  | 1-00-04 |  |  | 1740 | GDA | 道爺安南新化線 1740 GDA |  |  | B2/D15_A1 | [8 empty] | 新化DS.1740_GDA | 道爺安南新化線(1740) 接地RY | LINE161 | [5 empty] | 376 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1730 | 道爺~和順~新化線(1730) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | 1730 | 87A | 道爺和順新化線 1730 87A |  |  | B2/D15_A1 | [8 empty] | 新化DS.1730_87A | 道爺和順新化線(1730) 87RY | LINE161 | [5 empty] | 377 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1730 | 道爺~和順~新化線(1730) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-01-00 |  |  | 1730 | PHA | 道爺和順新化線 1730 PHA |  |  | B2/D15_A1 | [8 empty] | 新化DS.1730_PHA | 道爺和順新化線(1730) 相間RY | LINE161 | [5 empty] | 378 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1730 | 道爺~和順~新化線(1730) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | 1730 | GDA | 道爺和順新化線 1730 GDA |  |  | B2/D15_A1 | [8 empty] | 新化DS.1730_GDA | 道爺和順新化線(1730) 接地RY | LINE161 | [5 empty] | 379 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-03 |  |  | 1720 | 87A | 山上新化二路 1720 87 RY |  |  | B2/D15_A1 | [8 empty] | 新化DS.1720_87A | 山上二路(1720) 87RY | LINE161 | [5 empty] | 380 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | 21A |  |  | Status | 21RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0013 |  |  | 1-01-05 |  |  | 1720 | PHA | 山上新化二路 1720 21 RY |  |  | B2/D15_A1 | [8 empty] | 新化DS.1720_PHA | 山上二路(1720) 相間RY | LINE161 | [5 empty] | 381 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | 21NA |  |  | Status | 21N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-06 |  |  | 1720 | GDA | 山上新化二路 1720 21N RY |  |  | B2/D15_A1 | [8 empty] | 新化DS.1720_GDA | 山上二路(1720) 接地RY | LINE161 | [5 empty] | 382 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1710 | 山上～新化一路(1710) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-02-00 |  |  | 1710 | 87A | 山上新化一路 1710 87 RY |  |  | B2/D15_A1 | [8 empty] | 新化DS.1710_87A | 山上一路(1710) 87RY | LINE161 | [5 empty] | 383 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1710 | 山上～新化一路(1710) |  | 21A |  |  | Status | 21RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 |  |  | 1-02-02 |  |  | 1710 | PHA | 山上新化一路 1710 21 RY |  |  | B2/D15_A1 | [8 empty] | 新化DS.1710_PHA | 山上一路(1710) 相間RY | LINE161 | [5 empty] | 384 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1710 | 山上～新化一路(1710) |  | 21NA |  |  | Status | 21N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0019 |  |  | 1-02-03 |  |  | 1710 | GDA | 山上新化一路 1710 21N RY |  |  | B2/D15_A1 | [8 empty] | 新化DS.1710_GDA | 山上一路(1710) 接地RY | LINE161 | [5 empty] | 385 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1510 | 新化～永資～統實線(1510) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-05 |  |  | 1510 | 87L1TA | 新化永資統實線 1510 87L1TA |  |  | B2/D15_A1 | [8 empty] | 新化DS.1510_87L1 | 統實永資線(1510) 87L1RY | LINE161 | [5 empty] | 386 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1510 | 新化～永資～統實線(1510) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0022 |  |  | 1-02-06 |  |  | 1510 | 87L2TA | 新化永資統實線 1510 87L2TA |  |  | B2/D15_A1 | [8 empty] | 新化DS.1510_87L2 | 統實永資線(1510) 87L2RY | LINE161 | [5 empty] | 387 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1510 | 新化～永資～統實線(1510) |  | 21A |  |  | Status | 21RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0023 |  |  | 1-02-07 |  |  | 1510 | PHA | 新化永資統實線 1510 21 RY |  |  | B2/D15_A1 | [8 empty] | 新化DS.1510_21A | 統實永資線(1510) 21RY | LINE161 | [5 empty] | 388 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1510 | 新化～永資～統實線(1510) |  | 21NA |  |  | Status | 21N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0024 |  |  | 1-03-00 |  |  | 1510 | GDA | 新化永資統實線 1510 21N RY |  |  | B2/D15_A1 | [8 empty] | 新化DS.1510_GDA | 統實永資線(1510) 接地RY | LINE161 | [5 empty] | 389 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0041 |  |  | 1-05-01 |  |  | 1500 | 50A | 161KV TIE 1500 50A |  |  | B2/D15_A1 | [8 empty] | 新化DS.1500_50A | 161KV TIE(1500) 50RY | TIE | [5 empty] | 390 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0042 |  |  | 1-05-02 |  |  | 161KV #1 BUS | 87B1A | 161KV #1BUS 87A |  |  | B2/D15_A1 | [8 empty] | 新化DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | [5 empty] | 391 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0043 |  |  | 1-05-03 |  |  | 161KV #2 BUS | 87B2A | 161KV #2BUS 87A |  |  | B2/D15_A1 | [8 empty] | 新化DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | [5 empty] | 392 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS |  |  | 1DTR | #1DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0046 |  |  | 1-05-06 |  |  | #1DTR | 87A | #1DTR 87RY |  |  | B1/D15_A1 | [8 empty] | 新化DS.#1DTR_87A | #1DTR 87RY | MTR | [5 empty] | 393 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS |  |  | 1DTR | #1DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0047 |  |  | 1-05-07 |  |  | #1DTR | 96PA | #1DTR 機械保護動作(96PA) |  |  | B1/D15_A1 | [8 empty] | 新化DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | [5 empty] | 394 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS |  |  | 1DTR | #1DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0048 |  |  | 1-06-00 |  |  | #1DTR | 51ZA | #1DTR 51Z RY |  |  | B1/D15_A1 | [8 empty] | 新化DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | [5 empty] | 395 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1750 | #1DTR(1750) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0049 |  |  | 1-06-01 |  |  | #1DTR | PHA | #1DTR一次1750 51 RY |  |  | B2/D15_A1 | [8 empty] | 新化DS.#1DTR_51A | #1DTR 51RY | MTR | [5 empty] | 396 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1750 | #1DTR(1750) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0050 |  |  | 1-06-02 |  |  | #1DTR | GDA | #1DTR一次1750 51N RY |  |  | B2/D15_A1 | [8 empty] | 新化DS.#1DTR_51NA | #1DTR 51N RY | MTR | [5 empty] | 397 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | #2BUS | 87B2A | D1A 310 51 RY |  |  | B3/D15_A1 | [8 empty] | 新化DS.310_51A | #1DTR二次側(310) 51RY | MTR | [5 empty] | 398 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS |  |  | 2DTR | #2DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0056 |  |  | 1-07-00 |  |  | #2DTR | 87A | #2DTR 87RY |  |  | B1/D15_A1 | [8 empty] | 新化DS.#2DTR_87A | #2DTR 87RY | MTR | [5 empty] | 399 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS |  |  | 2DTR | #2DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0057 |  |  | 1-07-01 |  |  | #2DTR | 96PA | #2DTR 機械保護動作(96PA) |  |  | B1/D15_A1 | [8 empty] | 新化DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | [5 empty] | 400 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS |  |  | 2DTR | #2DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0058 |  |  | 1-07-02 |  |  | #2DTR | 51ZA | #2DTR 51Z RY |  |  | B1/D15_A1 | [8 empty] | 新化DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | [5 empty] | 401 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1760 | #2DTR(1760) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0059 |  |  | 1-07-03 |  |  | #2DTR | PHA | #2DTR一次1760 51 RY |  |  | B2/D15_A1 | [8 empty] | 新化DS.#2DTR_51A | #2DTR 51RY | MTR | [5 empty] | 402 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1760 | #2DTR(1760) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0060 |  |  | 1-07-04 |  |  | #2DTR | GDA | #2DTR一次1760 51N RY |  |  | B2/D15_A1 | [8 empty] | 新化DS.#2DTR_51NA | #2DTR 51N RY | MTR | [5 empty] | 403 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0062 |  |  | 1-07-06 |  |  | D1B 320 | 51A | D1B 320 51 RY |  |  | B3/D15_A1 | [8 empty] | 新化DS.320_51A | #1DTR二次側(320) 51RY | MTR | [5 empty] | 404 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0064 |  |  | 1-08-00 |  |  | D2B 340 | 51A | D2B 340 51 RY |  |  | B3/D15_A1 | [8 empty] | 新化DS.340_51A | #2DTR二次側(340) 51RY | MTR | [5 empty] | 405 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0072 |  |  | 1-09-00 |  |  | D2A 330 | 51A | D2A 330 51 RY |  |  | B3/D15_A1 | [8 empty] | 新化DS.330_51A | #2DTR二次側(330) 51RY | MTR | [5 empty] | 406 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0073 |  |  | 1-09-01 |  |  | OSCA | A/N | 161KV示波器啟動警報OSCA |  |  | B3/D15_A1 | [8 empty] | 新化DS.OSC啟動 | 示波器啟動警報 | OTHER | [5 empty] | 407 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0074 |  |  | 1-09-02 |  |  | 79RELAY | A/N | 79RELAY警報 RCA |  |  | B3/D15_A1 | [8 empty] | 新化DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | [5 empty] | 408 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  | RTU | RTU |  | RTU_MCT |  |  | Status | RTU Master Ry | Open/Close | Y | E | DI-SP | [6 empty] | 0075 |  |  | 1-09-03 |  |  | 161RTU | MCT_ SOE | RTU MASTER RY SOE |  |  | B3/D15_A1 | [16 empty] | 409 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D15 | 新化DS | 11 | 11kV | KY21 | 新21線(KY21) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0129 |  |  | 1-10-01 |  |  | 大洋線 | PHA | 新21線 F1 KY21 51 RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY21_PHA | 11KV新21線(KY21) 相間RY | FEEDER | [5 empty] | 410 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY21 | 新21線(KY21) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-10-02 |  |  | 大洋線 | GDA | 新21線 F1 KY21 51N RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY21_GDA | 11KV新21線(KY21) 接地RY | FEEDER | [5 empty] | 411 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY22 | 新22線(KY22) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0132 |  |  | 1-10-04 |  |  | 大坑線 | PHA | 新22線 F2 KY22 51 RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY22_PHA | 11KV新22線(KY22) 相間RY | FEEDER | [5 empty] | 412 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY22 | 新22線(KY22) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0133 |  |  | 1-10-05 |  |  | 大坑線 | GDA | 新22線 F2 KY22 51N RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY22_GDA | 11KV新22線(KY22) 接地RY | FEEDER | [5 empty] | 413 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY23 | 新23線(KY23) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0135 |  |  | 1-10-07 |  |  | 保東線 | PHA | 新23線 F3 KY23 51 RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY23_PHA | 11KV新23線(KY23) 相間RY | FEEDER | [5 empty] | 414 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY23 | 新23線(KY23) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0136 |  |  | 1-11-00 |  |  | 保東線 | GDA | 新23線 F3 KY23 51N RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY23_GDA | 11KV新23線(KY23) 接地RY | FEEDER | [5 empty] | 415 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY24 | 新24線(KY24) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0138 |  |  | 1-11-02 |  |  | 山腳線 | PHA | 新24線 F4 KY24 51 RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY24_PHA | 11KV新24線(KY24) 相間RY | FEEDER | [5 empty] | 416 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY24 | 新24線(KY24) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0139 |  |  | 1-11-03 |  |  | 山腳線 | GDA | 新24線 F4 KY24 51N RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY24_GDA | 11KV新24線(KY24) 接地RY | FEEDER | [5 empty] | 417 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY25 | 新25線(KY25) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0141 |  |  | 1-11-05 |  |  | 化工線 | PHA | 新25線 F5 KY25 51 RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY25_PHA | 11KV新25線(KY25) 相間RY | FEEDER | [5 empty] | 418 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY25 | 新25線(KY25) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0142 |  |  | 1-11-06 |  |  | 化工線 | GDA | 新25線 F5 KY25 51N RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY25_GDA | 11KV新25線(KY25) 接地RY | FEEDER | [5 empty] | 419 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY26 | 新26線(KY26) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0144 |  |  | 1-12-00 |  |  | 備用線 | PHA | 新26線F6 51 RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY26_PHA | 11KV新26線(KY26) 相間RY | FEEDER | [5 empty] | 420 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY26 | 新26線(KY26) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0145 |  |  | 1-12-01 |  |  | 備用線 | GDA | 新26線F6 51N RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY26_GDA | 11KV新26線(KY26) 接地RY | FEEDER | [5 empty] | 421 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0147 |  |  | 1-12-03 |  |  | #1SC | SCA | #1SC 210 51/51N RY |  |  | B3/D15_A1 | [8 empty] | 新化DS.210_SCA | 11KV #1SC 51,51N RY | SC | [5 empty] | 422 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0148 |  |  | 1-12-04 |  |  | #1SC | UVA | #1SC 210 27 RY |  |  | B3/D15_A1 | [8 empty] | 新化DS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | [5 empty] | 423 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0150 |  |  | 1-12-06 |  |  | #2SC | SCA | #2SC 220 51/51N RY |  |  | B3/D15_A1 | [8 empty] | 新化DS.220_SCA | 11KV #2SC 51,51N RY | SC | [5 empty] | 424 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0151 |  |  | 1-12-07 |  |  | #2SC | UVA | #2SC 220 27 RY |  |  | B3/D15_A1 | [8 empty] | 新化DS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | [5 empty] | 425 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | 100 | TIE(100) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0153 |  |  | 1-13-01 |  |  | #1TIE | PHA | #1TIE 100 51 RY |  |  | B3/D15_A1 | [8 empty] | 新化DS.100_51A | 11KV TIE(100) 51RY | TIE | [5 empty] | 426 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | 100 | TIE(100) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0154 |  |  | 1-13-02 |  |  | #1TIE | GDA | #1TIE 100 51N RY |  |  | B3/D15_A1 | [8 empty] | 新化DS.100_51NA | 11KV TIE(100) 51N RY | TIE | [5 empty] | 427 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY27 | 新27線(KY27) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0156 |  |  | 1-13-04 |  |  | 科積線 | PHA | 新27線F7 KY27 51RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY27_PHA | 11KV新27線(KY27) 相間RY | FEEDER | [5 empty] | 428 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY27 | 新27線(KY27) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0157 |  |  | 1-13-05 |  |  | 科積線 | GDA | 新27線F7 KY27 51N RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY27_GDA | 11KV新27線(KY27) 接地RY | FEEDER | [5 empty] | 429 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY28 | 新28線(KY28) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0159 |  |  | 1-13-07 |  |  | 南茂線 | PHA | 新28線F8 KY28 51RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY28_PHA | 11KV新28線(KY28) 相間RY | FEEDER | [5 empty] | 430 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY28 | 新28線(KY28) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0160 |  |  | 1-14-00 |  |  | 南茂線 | GDA | 新28線F8 KY28 51NRY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY28_GDA | 11KV新28線(KY28) 接地RY | FEEDER | [5 empty] | 431 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY29 | 新29線(KY29) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0162 |  |  | 1-14-02 |  |  | 神隆線 | PHA | 新29線F9 KY29 51 RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY29_PHA | 11KV新29線(KY29) 相間RY | FEEDER | [5 empty] | 432 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY29 | 新29線(KY29) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0163 |  |  | 1-14-03 |  |  | 神隆線 | GDA | 新29線F9 KY29 51N RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY29_GDA | 11KV新29線(KY29) 接地RY | FEEDER | [5 empty] | 433 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY30 | 新30線(KY30) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0165 |  |  | 1-14-05 |  |  | 備用線 | PHA | 新30線 F10 KY30 51 RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY30_PHA | 11KV新30線(KY30) 相間RY | FEEDER | [5 empty] | 434 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY30 | 新30線(KY30) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0166 |  |  | 1-14-06 |  |  | 備用線 | GDA | 新30線 F10 KY30 51N RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY30_GDA | 11KV新30線(KY30) 接地RY | FEEDER | [5 empty] | 435 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | 230 | #3SC(230) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0168 |  |  | 1-15-00 |  |  | #3SC | SCA | #3SC 230 51/51N RY |  |  | B3/D15_A1 | [8 empty] | 新化DS.230_SCA | 11KV #3SC 51,51N RY | SC | [5 empty] | 436 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | 230 | #3SC(230) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0169 |  |  | 1-15-01 |  |  | #3SC | UVA | #3SC 230 27 RY |  |  | B3/D15_A1 | [8 empty] | 新化DS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | [5 empty] | 437 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY37 | 新37線(KY37) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0171 |  |  | 1-15-03 |  |  | 科台線 | PHA | 新37線 KY37 51RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY37_PHA | 11KV新37線(KY37) 相間RY | FEEDER | [5 empty] | 438 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY37 | 新37線(KY37) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0172 |  |  | 1-15-04 |  |  | 科台線 | GDA | 新37線 KY37 51NRY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY37_GDA | 11KV新37線(KY37) 接地RY | FEEDER | [5 empty] | 439 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY38 | 新38線(KY38) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0174 |  |  | 1-15-06 |  |  | 科園線 | PHA | 新38線 KY38 51RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY38_PHA | 11KV新38線(KY38) 相間RY | FEEDER | [5 empty] | 440 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY38 | 新38線(KY38) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0175 |  |  | 1-15-07 |  |  | 科園線 | GDA | 新38線 KY38 51NRY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY38_GDA | 11KV新38線(KY38) 接地RY | FEEDER | [5 empty] | 441 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY39 | 新39線(KY39) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0177 |  |  | 1-16-01 |  |  | 科南線 | PHA | 新39線 KY39 51RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY39_PHA | 11KV新39線(KY39) 相間RY | FEEDER | [5 empty] | 442 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY39 | 新39線(KY39) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0178 |  |  | 1-16-02 |  |  | 科南線 | GDA | 新39線 KY39 51NRY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY39_GDA | 11KV新39線(KY39) 接地RY | FEEDER | [5 empty] | 443 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY40 | 新40線(KY40) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0180 |  |  | 1-16-04 |  |  | 備用線 | PHA | 新40線F14 KY40 51 RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY40_PHA | 11KV新40線(KY40) 相間RY | FEEDER | [5 empty] | 444 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY40 | 新40線(KY40) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0181 |  |  | 1-16-05 |  |  | 備用線 | GDA | 新40線F14 KY40 51N RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY40_GDA | 11KV新40線(KY40) 接地RY | FEEDER | [5 empty] | 445 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | 260 | #6SC(260) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0183 |  |  | 1-16-07 |  |  | #6SC | SCA | #6SC 260 51/51N RY |  |  | B3/D15_A1 | [8 empty] | 新化DS.260_SCA | 11KV #6SC 51,51N RY | SC | [5 empty] | 446 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | 260 | #6SC(260) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0184 |  |  | 1-17-00 |  |  | #6SC | UVA | #6SC 260 27 RY |  |  | B3/D15_A1 | [8 empty] | 新化DS.260_UVA | 11KV #6SC 27RY(欠壓) | SC | [5 empty] | 447 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | 200 | TIE(200) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0186 |  |  | 1-17-02 |  |  | #2TIE | PHA | #2TIE 51 200 RY |  |  | B3/D15_A1 | [8 empty] | 新化DS.200_51A | 11KV TIE(200) 51RY | TIE | [5 empty] | 448 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | 200 | TIE(200) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0187 |  |  | 1-17-03 |  |  | #2TIE | GDA | #2TIE 200 51N RY |  |  | B3/D15_A1 | [8 empty] | 新化DS.200_51NA | 11KV TIE(200) 51N RY | TIE | [5 empty] | 449 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY31 | 新31線(KY31) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0189 |  |  | 1-17-05 |  |  | 永化線 | PHA | 新31線 F15 KY31 51 RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY31_PHA | 11KV新31線(KY31) 相間RY | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY31 | 新31線(KY31) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0190 |  |  | 1-17-06 |  |  | 永化線 | GDA | 新31線 F15 KY31 51N RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY31_GDA | 11KV新31線(KY31) 接地RY | FEEDER | [5 empty] | 451 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY32 | 新32線(KY32) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0192 |  |  | 1-18-00 |  |  | 遠東線 | PHA | 新32線F16 KY32 51RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY32_PHA | 11KV新32線(KY32) 相間RY | FEEDER | [5 empty] | 452 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY32 | 新32線(KY32) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0193 |  |  | 1-18-01 |  |  | 遠東線 | GDA | 新32線F16 KY32 51NRY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY32_GDA | 11KV新32線(KY32) 接地RY | FEEDER | [5 empty] | 453 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY33 | 新33線(KY33) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0195 |  |  | 1-18-03 |  |  | 社內線 | PHA | 新33線F17 KY33 51 RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY33_PHA | 11KV新33線(KY33) 相間RY | FEEDER | [5 empty] | 454 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY33 | 新33線(KY33) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0196 |  |  | 1-18-04 |  |  | 社內線 | GDA | 新33線F17 KY33 51N RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY33_GDA | 11KV新33線(KY33) 接地RY | FEEDER | [5 empty] | 455 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY34 | 新34線(KY34) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0198 |  |  | 1-18-06 |  |  | 新東線 | PHA | 新34線F18 KY34 51 RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY34_PHA | 11KV新34線(KY34) 相間RY | FEEDER | [5 empty] | 456 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY34 | 新34線(KY34) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0199 |  |  | 1-18-07 |  |  | 新東線 | GDA | 新34線F18 KY34 51N RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY34_GDA | 11KV新34線(KY34) 接地RY | FEEDER | [5 empty] | 457 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY35 | 新35線(KY35) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0201 |  |  | 1-19-01 |  |  | 北勢線 | PHA | 新35線F19 KY35 51 RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY35_PHA | 11KV新35線(KY35) 相間RY | FEEDER | [5 empty] | 458 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY35 | 新35線(KY35) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0202 |  |  | 1-19-02 |  |  | 北勢線 | GDA | 新35線F19 KY35 51N RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY35_GDA | 11KV新35線(KY35) 接地RY | FEEDER | [5 empty] | 459 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY36 | 新36線(KY36) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0204 |  |  | 1-19-04 |  |  | 西勢線 | PHA | 新36線 F20 KY36 51 RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY36_PHA | 11KV新36線(KY36) 相間RY | FEEDER | [5 empty] | 460 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY36 | 新36線(KY36) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0205 |  |  | 1-19-05 |  |  | 西勢線 | GDA | 新36線 F20 KY36 51N RY |  |  | B2/D15_D1 | [8 empty] | 新化DS.KY36_GDA | 11KV新36線(KY36) 接地RY | FEEDER | [5 empty] | 461 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | 250 | #5SC(250) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0207 |  |  | 1-19-07 |  |  | #5SC | SCA | #5SC 250 51/51N RY |  |  | B3/D15_A1 | [8 empty] | 新化DS.250_SCA | 11KV #5SC 51,51N RY | SC | [5 empty] | 462 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | 250 | #5SC(250) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0208 |  |  | 1-1A-00 |  |  | #5SC | UVA | #5SC 250 27 RY |  |  | B3/D15_A1 | [8 empty] | 新化DS.250_UVA | 11KV #5SC 27RY(欠壓) | SC | [5 empty] | 463 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | 240 | #4SC(240) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0210 |  |  | 1-1A-02 |  |  | #4SC | SCA | #4SC 240 51/51N RY |  |  | B3/D15_A1 | [8 empty] | 新化DS.240_SCA | 11KV #4SC 51,51N RY | SC | [5 empty] | 464 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | 240 | #4SC(240) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0211 |  |  | 1-1A-03 |  |  | #4SC | UVA | #4SC 240 27 RY |  |  | B3/D15_A1 | [8 empty] | 新化DS.240_UVA | 11KV #4SC 27RY(欠壓) | SC | [5 empty] | 465 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D15 | 新化DS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0512 |  | 0000 | 1-30-00 |  |  | TEST CB | ON/OFF | TEST CB |  |  | ELEM/ALL | [8 empty] | 新化DS.TEST_CB | TEST CB | OTHER | [5 empty] | 466 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | RTU | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0513 |  |  | 1-30-01 |  |  | RTU | L/S | L/R STATUS |  |  | ELEM/D15_A1 | [8 empty] | 新化DS.RTU_S/L | RTU SUPY/LOCAL | OTHER | [5 empty] | 467 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
D15 | 新化DS | 161 | 161kV | 1740 | 道爺~安南~新化線(1740) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0521 |  |  | 1-30-09 |  |  | 1740 | A/N | 道爺安南新化線 1740電驛通訊故障 |  |  | B2/D15_A1 | [8 empty] | 新化DS.1740_87CFA | 道爺安南新化(1740)87RY通訊故障 | OTHER | [5 empty] | 468 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1740 | 道爺~安南~新化線(1740) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0522 |  |  | 1-30-10 |  |  | 1740 | A/N | 道爺安南新化線 1740 電驛故障 |  |  | B2/D15_A1 | [8 empty] | 新化DS.1740_RYFA | 道爺安南新化(1740)數位電驛故障 | OTHER | [5 empty] | 469 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D15 | 新化DS | 0 |  | ComPoint |  |  | FDR_60A | 11/23kV |  | Status | 11/22kV電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0526 |  |  | 1-30-14 |  |  | 60RY | A/N | 11/23kV SC 60A警報 |  |  | B3/D15_A1 | [8 empty] | 新化DS.11KV_SC_60A | 11KV sc 60A | OTHER | [5 empty] | 470 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1510 | 新化～永資～統實線(1510) |  | 87UL | 85UL | Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0528 |  |  | 1-31-00 |  |  | 1510 | A/N | 新化永資統實線1510 85 UA |  |  | B2/D15_A1 | [8 empty] | 新化DS.1510_87CFA | 統實永資線(1510) 87RY通訊故障 | OTHER | [5 empty] | 471 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | FAULT/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1510 | 新化～永資～統實線(1510) |  | 85CFA |  |  | Status | 85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0529 |  |  | 1-31-01 |  |  | 1510 | A/N | 新化永資統實線1510 RAOA |  |  | B2/D15_A1 | [8 empty] | 新化DS.1510_RYFA | 統實永資線(1510) 數位電驛故障 | OTHER | [5 empty] | 472 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D15 | 新化DS | 0 |  | ComPoint |  |  | OLTC_A |  |  | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0534 |  |  | 1-31-06 |  |  | OLTC | OLTCA | OLTC 15分鐘內連動3次警報 |  |  | B3/D15_A1 | [8 empty] | 新化DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | [5 empty] | 473 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  | StaDev | 所內設施 |  | Water1 | 0.5M |  | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0536 |  |  | 1-31-08 |  |  | 地下室 | A/N | 地下室溢水 0.5M |  |  | B3/D15_A1 | [8 empty] | 新化DS.地下室積水(1) | 地下室積水0.5公尺 | OTHER | [5 empty] | 474 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  | StaDev | 所內設施 |  | Water2 | 1.5M |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0537 |  |  | 1-31-09 |  |  | 地下室 | A/N | 地下室溢水 1.5M |  |  | B3/D15_A1 | [8 empty] | 新化DS.地下室積水(2) | 地下室積水1.5公尺 | OTHER | [5 empty] | 475 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  | StaDev | 所內設施 |  | GEN | 緊急發電機運轉 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0538 |  |  | 1-31-10 |  |  | Locate Empty | ON/OFF | 緊急發電機運轉 |  |  | B1/D15_A1 | [8 empty] | 新化DS.GEN | 緊急發電機運轉 | OTHER | [5 empty] | 476 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ON/OFF | OFF
D15 | 新化DS | 161 | 161kV | ComPoint | BUS |  | RYFA |  |  | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0539 |  |  | 1-31-11 |  |  | 161kV BUS | A/N | 161KV BUS數位電驛故障 |  |  | B3/D15_A1 | [8 empty] | 新化DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | [5 empty] | 477 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | ComPoint | BUS |  | 87CTFA |  | Element | Status | 87RY CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0540 |  |  | 1-31-12 |  |  | 161kV BUS | A/N | 161KV BUS 87RY CT 迴路故障 |  |  | B2/D15_A1 | [8 empty] | 新化DS.161KV_BUS_CTFA | 161KV BUS 87RY CT回路故障 | OTHER | [5 empty] | 478 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0542 |  |  | 1-31-14 |  |  | 1720 | A/N | 山上新化二路 1720 87LCFA(87L通訊故障) |  |  | B2/D15_A1 | [8 empty] | 新化DS.1720_87CFA | 山上新化二路(1720)87RY通訊故障 | OTHER | [5 empty] | 479 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1710 | 山上～新化一路(1710) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0544 |  |  | 1-32-00 |  |  | 1710 | A/N | 山上新化一路 1710 87LCFA(87L通訊故障) |  |  | B2/D15_A1 | [8 empty] | 新化DS.1710_87CFA | 山上新化一路(1710)87RY通訊故障 | OTHER | [5 empty] | 480 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D15 | 新化DS |  |  | 2DTR | #2DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0545 |  |  | 1-32-01 |  |  | #2DTR | 96D | #2DTR 96D |  |  | B1/D15_A1 | [8 empty] | 新化DS.#2DTR_96D | #2DTR 96D RY | MTR | [5 empty] | 481 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D15 | 新化DS |  |  | 2DTR | #2DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0546 |  |  | 1-32-02 |  |  | #2DTR | 96P | #2DTR 96P |  |  | B1/D15_A1 | [8 empty] | 新化DS.#2DTR_96P | #2DTR 96P RY | MTR | [5 empty] | 482 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D15 | 新化DS |  |  | 1DTR | #1DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0547 |  |  | 1-32-03 |  |  | #1DTR | 96D | #1DTR 96D |  |  | B1/D15_A1 | [8 empty] | 新化DS.#1DTR_96D | #1DTR 96D RY | MTR | [5 empty] | 483 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D15 | 新化DS |  |  | 1DTR | #1DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0548 |  |  | 1-32-04 |  |  | #1DTR | 96P | #1DTR 96P |  |  | B1/D15_A1 | [8 empty] | 新化DS.#1DTR_96P | #1DTR 96P RY | MTR | [5 empty] | 484 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D15 | 新化DS |  |  | 1DTR | #1DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0549 |  |  | 1-32-05 |  |  | #1DTR | 63Q | #1DTR 63Q |  |  | B1/D15_A1 | [8 empty] | 新化DS.#1DTR_63Q | #1DTR 63Q RY | MTR | [5 empty] | 485 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D15 | 新化DS |  |  | 1DTR | #1DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0550 |  |  | 1-32-06 |  |  | #1DTR | 96B1 | #1DTR 96B1 |  |  | B1/D15_A1 | [8 empty] | 新化DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | [5 empty] | 486 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D15 | 新化DS |  |  | 1DTR | #1DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0551 |  |  | 1-32-07 |  |  | #1DTR | 96B2 | #1DTR 96B2 |  |  | B1/D15_A1 | [8 empty] | 新化DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | [5 empty] | 487 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D15 | 新化DS |  |  | 1DTR | #1DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0554 |  |  | 1-32-10 |  |  | #1DTR | U/L | #1DTR 87LS |  |  | B1/D15_A1 | [8 empty] | 新化DS.#1DTR_87UL | #1DTR 87RY U/L | MTR | [5 empty] | 488 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D15 | 新化DS |  |  | 1DTR(A) | #1DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0555 |  |  | 1-32-11 |  |  | #1A DTR | R/L | #1A DTR OLTC R/L |  | c | B1/D15_A1 | [8 empty] | 新化DS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | [5 empty] | 489 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D15 | 新化DS |  |  | 1DTR | #1DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0557 |  |  | 1-32-13 |  |  | #1DTR | TRA | #1DTR 重故障 |  | a | B1/D15_A1 | [8 empty] | 新化DS.#1DTR_TRA | #1DTR 重故障 | MTR | [5 empty] | 490 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D15 | 新化DS |  |  | 1DTR | #1DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0558 |  |  | 1-32-14 |  |  | #1DTR | TRF | #1DTR 輕故障 |  |  | B1/D15_A1 | [8 empty] | 新化DS.#1DTR_TRF | #1DTR 輕故障 | MTR | [5 empty] | 491 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D15 | 新化DS |  |  | 1DTR(B) | #1DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0559 |  |  | 1-32-15 |  |  | #1B DTR | R/L | #1B DTR OLTC R/L |  | b | B1/D15_A1 | [8 empty] | 新化DS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | [5 empty] | 492 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D15 | 新化DS |  |  | 2DTR | #2DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0561 |  |  | 1-33-01 |  |  | #2DTR | U/L | #2DTR 87LS |  |  | B1/D15_A1 | [8 empty] | 新化DS.#2DTR_87UL | #2DTR 87RY U/L | MTR | [5 empty] | 493 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D15 | 新化DS |  |  | 2DTR(A) | #2DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0562 |  |  | 1-33-02 |  |  | #2A DTR | R/L | #2A DTR OLTC R/L |  | c | B1/D15_A1 | [8 empty] | 新化DS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | [5 empty] | 494 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D15 | 新化DS |  |  | 2DTR | #2DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0564 |  |  | 1-33-04 |  |  | #2DTR | TRA | #2DTR 重故障 |  | a | B1/D15_A1 | [8 empty] | 新化DS.#2DTR_TRA | #2DTR 重故障 | MTR | [5 empty] | 495 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D15 | 新化DS |  |  | 2DTR | #2DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0565 |  |  | 1-33-05 |  |  | #2DTR | TRF | #2DTR 輕故障 |  |  | B1/D15_A1 | [8 empty] | 新化DS.#2DTR_TRF | #2DTR 輕故障 | MTR | [5 empty] | 496 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D15 | 新化DS |  |  | 2DTR(B) | #2DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0566 |  |  | 1-33-06 |  |  | #2B DTR | R/L | #2B DTR OLTC R/L |  | b | B1/D15_A1 | [8 empty] | 新化DS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | [5 empty] | 497 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D15 | 新化DS |  |  | 2DTR | #2DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0573 |  |  | 1-33-13 |  |  | #2DTR | 63Q | #2DTR 63Q |  |  | B1/D15_A1 | [8 empty] | 新化DS.#2DTR_63Q | #2DTR 63Q RY | MTR | [5 empty] | 498 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D15 | 新化DS |  |  | 2DTR | #2DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0574 |  |  | 1-33-14 |  |  | #2DTR | 96B1 | #2DTR 96B1 |  |  | B1/D15_A1 | [8 empty] | 新化DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | [5 empty] | 499 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D15 | 新化DS |  |  | 2DTR | #2DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0575 |  |  | 1-33-15 |  |  | #2DTR | 96B2 | #2DTR 96B2 |  |  | B1/D15_A1 | [8 empty] | 新化DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | [5 empty] | 500 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1730 | 道爺~和順~新化線(1730) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0768 |  |  | 2-30-00 |  |  | 1730 | A/N | 道爺和順新化線 1730 CFA(電驛通訊故障) |  |  | B2/D15_A1 | [8 empty] | 新化DS.1730_87CFA | 道爺和順新化(1730)87RY通訊故障 | OTHER | [5 empty] | 501 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1730 | 道爺~和順~新化線(1730) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0769 |  |  | 2-30-01 |  |  | 1730 | A/N | 道爺和順新化線 1730 RYFA(電驛故障) |  |  | B2/D15_A1 | [8 empty] | 新化DS.1730_RYFA | 道爺和順新化(1730)數位電驛故障 | OTHER | [5 empty] | 502 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1710 | 山上～新化一路(1710) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0770 |  |  | 2-30-02 |  |  | 87LA | A/N | 山上新化一路 1710 87LA |  |  | B2/D15_A1 | [8 empty] | 新化DS.1710_RYFA | 山上新化一路(1710)數位電驛故障 | OTHER | [5 empty] | 503 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0771 |  |  | 2-30-03 |  |  | 87LA | A/N | 山上新化二路 1720 87LA |  |  | B2/D15_A1 | [8 empty] | 新化DS.1720_RYFA | 山上新化二路(1720)數位電驛故障 | OTHER | [5 empty] | 504 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1BUS | #1BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0825 |  |  | 2-33-09 |  |  | UVA1 | A/N | UVA1 |  |  | B2/D15_A1 | [8 empty] | 新化DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | [5 empty] | 505 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 2BUS | #2BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0826 |  |  | 2-33-10 |  |  | UVA2 | A/N | UVA2 |  |  | B2/D15_A1 | [8 empty] | 新化DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | [5 empty] | 506 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  | ComPoint |  |  | GRZ100 |  |  | Status | 電驛GRZ100閉鎖 | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0804 |  |  | 2-32-04 |  |  | BVS盤 | LOCK/USE | 本所各GRZ100 Ry U/L |  |  | B3/D15_A1 | [8 empty] | 新化DS.BVS_RY | BVS GRZ100 RY U/L | OTHER | [5 empty] | 507 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | LOCK/USE | USE
D15 | 新化DS | 0 |  | StaDev | 所內設施 |  | NFBA |  |  | Status | NFB 跳脫監視 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0827 |  |  | 2-33-11 |  |  | DCA NFB跳脫 | A/N | DCA NFB跳脫 |  |  | B3/D15_A1 | [8 empty] | 新化DS.直流電源DCA | 直流電源故障警報 | OTHER |  | CDC_Mon1_DPC,DNP_DI_Mon1_DPC |  |  |  | 508 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0809 |  |  | 2-32-09 |  |  | OSCF | A/N | 161KV示波器缺紙或故障警報OSCF |  |  | B3/D15_A1 | [8 empty] | 新化DS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | [5 empty] | 509 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D15 | 新化DS | 0 |  | StaDev | 所內設施 |  | Fire1 |  |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0810 |  |  | 2-32-10 |  |  | 火災警報(1) | A/N | 火災警報(1)受信總機 |  |  | B3/D15_A1 | [8 empty] | 新化DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | [5 empty] | 510 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  | StaDev | 所內設施 |  | Fire2 |  |  | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0811 |  |  | 2-32-11 |  |  | 火災警報(2) | A/N | 火災警報(2) |  |  | B3/D15_A1 | [8 empty] | 新化DS.火災警報(2) | 火災警報(2) | OTHER | [5 empty] | 511 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  | StaDev | 所內設施 |  | Fire3 |  |  | Status | 火災警報3 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0812 |  |  | 2-32-12 |  |  | 火災警報(3) | A/N | 火災警報(3) |  |  | B3/D15_A1 | [8 empty] | 新化DS.火災警報(3) | 火災警報(3) | OTHER | [5 empty] | 512 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  | StaDev | 所內設施 |  | Burglar1 |  |  | Status | 無人化防盜1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0813 |  |  | 2-32-13 |  |  | 保全系統 | A/N | 保全系統 |  |  | B3/D15_A1 | [8 empty] | 新化DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | [5 empty] | 513 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  | StaDev | 所內設施 |  | Burglar2 |  |  | Status | 無人化防盜2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0814 |  |  | 2-32-14 |  |  | 無人化防盜(二) | A/N | 無人化防盜(二) |  |  | B3/D15_A1 | [8 empty] | 新化DS.無人化防盜(2) | 無人化防盜(2)SP | OTHER | [5 empty] | 514 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  | StaDev | 所內設施 |  | Burglar3 |  |  | Status | 無人化防盜3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0815 |  |  | 2-32-15 |  |  | 無人化防盜(三) | A/N | 無人化防盜(三) |  |  | B3/D15_A1 | [8 empty] | 新化DS.無人化防盜(3) | 無人化防盜(3)SP | OTHER | [5 empty] | 515 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  | StaDev | 所內設施 |  | Door1 |  |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0816 |  |  | 2-33-00 |  |  | 無人化門禁(一) | A/N | 無人化門禁(一)大小門 |  |  | B3/D15_A1 | [8 empty] | 新化DS.無人化門禁(1) | 無人化門禁(1)變電所大門 | OTHER | [5 empty] | 516 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | StaDev | 所內設施 |  | Door2 |  |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0817 |  |  | 2-33-01 |  |  | 無人化門禁(二) | A/N | 無人化門禁(二)鐵捲門 |  |  | B3/D15_A1 | [8 empty] | 新化DS.無人化門禁(2) | 無人化門禁(2)建築物鐵捲門 | OTHER | [5 empty] | 517 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | StaDev | 所內設施 |  | Door3 |  |  | Status | 無人化門禁3 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0818 |  |  | 2-33-02 |  |  | 無人化門禁(三) | A/N | 無人化門禁(三)(SPARE) |  |  | B3/D15_A1 | [8 empty] | 新化DS.無人化門禁(3) | 無人化門禁(3)SP | OTHER | [5 empty] | 518 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | StaDev | 所內設施 |  | AIRCON |  |  | Status | 冷氣跳脫 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0819 |  |  | 2-33-03 |  |  | 冷氣機監視 | A/N | 冷氣機運轉監視 |  |  | B3/D15_A1 | [8 empty] | 新化DS.空調機跳脫警報 | 空調機故障或電源跳脫 | OTHER | [5 empty] | 519 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | NORMAL/FAULT | NORMAL
D15 | 新化DS | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0820 |  |  | 2-33-04 |  |  | 161KV TIE | 測試/正常 | 161KV TIE (1500)50RY 測試/正常 |  |  | B2/D15_A1 | [8 empty] | 新化DS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | [5 empty] | 520 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Test | Test | 1 |  |  | TEST/NORMAL | NORMAL
D15 | 新化DS | 0 |  | ComPoint |  |  | OPA |  |  | Status | 充油電纜低壓警報 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0821 |  |  | 2-33-05 |  |  | 油壓電力電纜 | A/N | 油壓電力電纜 OPA |  |  | B3/D15_A1 | [8 empty] | 新化DS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | [5 empty] | 521 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0822 |  |  | 2-33-06 |  |  | ACB1 | ON/OFF | 所內電源ACB1 |  |  | B3/D15_A1 | [8 empty] | 新化DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | [5 empty] | 522 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D15 | 新化DS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0823 |  |  | 2-33-07 |  |  | ACB2 | ON/OFF | 所內電源ACB2 |  |  | B3/D15_A1 | [8 empty] | 新化DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | [5 empty] | 523 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D15 | 新化DS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0824 |  |  | 2-33-08 |  |  | STUV 所內欠壓 | A/N | STUV 所內欠壓 |  |  | ELEM/D15_A1 | [8 empty] | 新化DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | [5 empty] | 524 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0828 |  |  | 2-33-12 |  |  | CHG1(直流故障) | A/N | CHG1(直流故障) |  |  | B3/D15_A1 | [8 empty] | 新化DS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | [5 empty] | 525 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D15 | 新化DS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0829 |  |  | 2-33-13 |  |  | CHG2(通訊用) | A/N | 通訊充電機故障 |  |  | B3/D15_A1 | [8 empty] | 新化DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | [5 empty] | 526 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D15 | 新化DS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0830 |  |  | 2-33-14 |  |  | DCE DC接地 | A/N | DCE DC接地 |  |  | ELEM/D15_A1 | [8 empty] | 新化DS.直流電源DCE | 直流電源接地故障警報 | OTHER | [5 empty] | 527 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  | ComPoint |  |  | COMT |  |  | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0831 |  |  | 2-33-15 |  |  | 16 COMT | A/N | 16 COMT |  |  | B3/D15_A1 | [8 empty] | 新化DS.161空壓機COMT | 161KV空壓機運轉超時警報 | OTHER | [5 empty] | 528 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0832 |  |  | 2-34-00 |  |  | 161KV 重故障 | A/N | 161KV 重故障 |  |  | B3/D15_A1 | [8 empty] | 新化DS.161KV_CBA | 161KV斷路器重故障 | OTHER | [5 empty] | 529 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0833 |  |  | 2-34-01 |  |  | 161KV 輕故障 | A/N | 161KV 輕故障 |  |  | B3/D15_A1 | [8 empty] | 新化DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | [5 empty] | 530 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0834 |  |  | 2-34-02 |  |  | 11KV 重故障 | A/N | 11KV 重故障 |  |  | ELEM/D15_A1 | [8 empty] | 新化DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | [5 empty] | 531 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0835 |  |  | 2-34-03 |  |  | 11KV 輕故障 | A/N | 11KV 輕故障 |  |  | ELEM/D15_A1 | [8 empty] | 新化DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | [5 empty] | 532 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D15 | 新化DS | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0836 |  |  | 2-34-04 |  |  | ACBA | A/N | ACBA |  |  | B3/D15_A1 | [8 empty] | 新化DS.所內電源ACBA | 所內電源故障警報 | OTHER | [5 empty] | 533 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  | StaDev | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0837 |  |  | 2-34-05 |  |  | PSF其他輕故障 | A/N | PSF其他輕故障 |  |  | B3/D15_A1 | [8 empty] | 新化DS.其他輕故障 | 變電所內其他輕故障 | OTHER | [5 empty] | 534 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D15 | 新化DS | 0 |  | StaDev | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0838 |  |  | 2-34-06 |  |  | PSA其他重故障 | A/N | PSA其他重故障 |  |  | B3/D15_A1 | [8 empty] | 新化DS.其他重故障 | 變電所內其他重故障 | OTHER | [5 empty] | 535 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D15 | 新化DS | 0 |  | StaDev | 所內設施 |  | OilLeak1 |  |  | Status | 洩油池水位警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0839 |  |  | 2-34-07 |  |  | OWA集油池警報 | A/N | OWA集油池警報 |  |  | B3/D15_A1 | [8 empty] | 新化DS.洩油池水位警報 | 洩油池水位警報 | OTHER | [5 empty] | 536 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0840 |  |  | 2-34-08 |  |  | 通訊設備AC故障 | A/N | 通訊設備AC故障 |  |  | B3/D15_A1 | [8 empty] | 新化DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | [5 empty] | 537 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D15 | 新化DS | 0 |  | StaDev | 所內設施 |  | R_Temp |  |  | Status | 溫度警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0843 |  |  | 2-34-11 |  |  | 博碼調變器故障 | A/N | 通信室溫控警報 |  |  | B3/D15_A1 | [8 empty] | 新化DS.通信機房溫度 | 通信機房溫度警報 | OTHER | [5 empty] | 538 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0065 | [10 empty] | B3/D15_A1 | [16 empty] | 539 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D15 | 新化DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0066 | [10 empty] | B3/D15_A1 | [16 empty] | 540 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D15 | 新化DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0067 | [10 empty] | B3/D15_A1 | [16 empty] | 541 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D15 | 新化DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 | [10 empty] | B3/D15_A1 | [16 empty] | 542 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D15 | 新化DS | 11 | 11kV | ComPoint |  |  | FDR_IRFA |  |  | Status | 11/22 kV IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0535 | [10 empty] | ELEM/D15_D1 | [16 empty] | 543 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
D15 | 新化DS | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/D15_A1 | [12 empty] | 新化DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: D15/161/1BUS/V; OPRD2: D15/161/2BUS/V
D15 | 新化DS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/D15_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: D15/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
D15 | 新化DS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/D15_A1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_5 | OPRD1: D15/161/1510/MW; OPRD2: D15/161/1710/MW; OPRD3: D15/161/1720/MW; OPRD4: D15/161/1730/MW; OPRD5: D15/161/1740/MW
D15 | 新化DS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/D15_A1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: D15/0/CalcPoint/OPRN2_MW
D15 | 新化DS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/D15_A1 | [17 empty] | none
D15 | 新化DS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/D15_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: D15/0/CalcPoint/OPRN1; OPRD2: D15/0/CalcPoint/OPRN2; OPRD3: D15/0/CalcPoint/PRFL_UL
D15 | 新化DS |  |  | 1DTR | 1DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D15_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D15/11/310/I_R; OPRD2: D15/11/320/I_R
D15 | 新化DS |  |  | 1DTR | 1DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D15_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D15/11/310/I_S; OPRD2: D15/11/320/I_S
D15 | 新化DS |  |  | 1DTR | 1DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D15_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D15/11/310/I_T; OPRD2: D15/11/320/I_T
D15 | 新化DS |  |  | 2DTR | 2DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D15_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D15/11/340/I_R; OPRD2: D15/11/330/I_R
D15 | 新化DS |  |  | 2DTR | 2DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D15_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D15/11/340/I_S; OPRD2: D15/11/330/I_S
D15 | 新化DS |  |  | 2DTR | 2DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D15_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D15/11/340/I_T; OPRD2: D15/11/330/I_T
D15 | 新化DS | 161 | 161kV | 1510 | 新化～永資～統實線(1510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D15_A1 | [12 empty] | 新化DS.1510_AMP | 統實永資線 AMP | LINE161 | AMP_CAL | C20R1000 | amp_cal | OPRD1: D15/161/1510/MW; OPRD2: D15/161/1510/MVAR; OPRD3: D15/0/CalcPoint/Vbs4
D15 | 新化DS | 161 | 161kV | 1710 | 山上～新化一路(1710) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D15_A1 | [12 empty] | 新化DS.1710_AMP | 山上新化一路 AMP | LINE161 | AMP_CAL | C20R1790 | amp_cal | OPRD1: D15/161/1710/MW; OPRD2: D15/161/1710/MVAR; OPRD3: D15/0/CalcPoint/Vbs4
D15 | 新化DS | 161 | 161kV | 1720 | 山上～新化二路(1720) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D15_A1 | [12 empty] | 新化DS.1720_AMP | 山上新化二路 AMP | LINE161 | AMP_CAL | C20R1790 | amp_cal | OPRD1: D15/161/1720/MW; OPRD2: D15/161/1720/MVAR; OPRD3: D15/0/CalcPoint/Vbs4
D15 | 新化DS | 161 | 161kV | 1730 | 道爺~和順~新化線(1730) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D15_A1 | [12 empty] | 新化DS.1730_AMP | 道爺和順新化線 AMP | LINE161 | AMP_CAL | C16R1576 | amp_cal | OPRD1: D15/161/1730/MW; OPRD2: D15/161/1730/MVAR; OPRD3: D15/0/CalcPoint/Vbs4
D15 | 新化DS | 161 | 161kV | 1740 | 道爺~安南~新化線(1740) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D15_A1 | [12 empty] | 新化DS.1740_AMP | 道爺安南新化線 AMP | LINE161 | AMP_CAL | C16R1576 | amp_cal | OPRD1: D15/161/1740/MW; OPRD2: D15/161/1740/MVAR; OPRD3: D15/0/CalcPoint/Vbs4
D15 | 新化DS | 11 | 11kV | 1ABUS | #1ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D15_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D15/11/1ABUS/V
D15 | 新化DS | 11 | 11kV | 1BBUS | #1BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D15_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D15/11/1BBUS/V
D15 | 新化DS | 11 | 11kV | 2ABUS | #2ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D15_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D15/11/2ABUS/V
D15 | 新化DS | 11 | 11kV | 2BBUS | #2BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D15_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D15/11/2BBUS/V
D15 | 新化DS |  |  | 1DTR(A) | #1DTR(A) |  | TR_PERM | [9 empty] | B1/D15_A1 | [12 empty] | 新化DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D15//1DTR(A)/SupLocal; OPRD2: D15//1DTR(A)/Tap Chan
D15 | 新化DS |  |  | 1DTR(B) | #1DTR(B) |  | TR_PERM | [9 empty] | B1/D15_A1 | [12 empty] | 新化DS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D15//1DTR(B)/SupLocal; OPRD2: D15//1DTR(B)/Tap Chan
D15 | 新化DS |  |  | 2DTR(A) | #2DTR(A) |  | TR_PERM | [9 empty] | B1/D15_A1 | [12 empty] | 新化DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D15//2DTR(A)/SupLocal; OPRD2: D15//2DTR(A)/Tap Chan
D15 | 新化DS |  |  | 2DTR(B) | #2DTR(B) |  | TR_PERM | [9 empty] | B1/D15_A1 | [12 empty] | 新化DS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D15//2DTR(B)/SupLocal; OPRD2: D15//2DTR(B)/Tap Chan
D15 | 新化DS | 11 | 11kV | KY21 | 新21線(KY21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D15/11/1ABUS/V; OPRD2: D15/11/KY21/I_R; OPRD3: D15/11/KY21/I_S; OPRD4: D15/11/KY21/I_T
D15 | 新化DS | 11 | 11kV | KY22 | 新22線(KY22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D15/11/1ABUS/V; OPRD2: D15/11/KY22/I_R; OPRD3: D15/11/KY22/I_S; OPRD4: D15/11/KY22/I_T
D15 | 新化DS | 11 | 11kV | KY23 | 新23線(KY23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D15/11/1ABUS/V; OPRD2: D15/11/KY23/I_R; OPRD3: D15/11/KY23/I_S; OPRD4: D15/11/KY23/I_T
D15 | 新化DS | 11 | 11kV | KY24 | 新24線(KY24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D15/11/1ABUS/V; OPRD2: D15/11/KY24/I_R; OPRD3: D15/11/KY24/I_S; OPRD4: D15/11/KY24/I_T
D15 | 新化DS | 11 | 11kV | KY25 | 新25線(KY25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D15/11/1ABUS/V; OPRD2: D15/11/KY25/I_R; OPRD3: D15/11/KY25/I_S; OPRD4: D15/11/KY25/I_T
D15 | 新化DS | 11 | 11kV | KY26 | 新26線(KY26) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D15/11/1ABUS/V; OPRD2: D15/11/KY26/I_R; OPRD3: D15/11/KY26/I_S; OPRD4: D15/11/KY26/I_T
D15 | 新化DS | 11 | 11kV | KY27 | 新27線(KY27) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D15/11/1BBUS/V; OPRD2: D15/11/KY27/I_R; OPRD3: D15/11/KY27/I_S; OPRD4: D15/11/KY27/I_T
D15 | 新化DS | 11 | 11kV | KY28 | 新28線(KY28) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D15/11/1BBUS/V; OPRD2: D15/11/KY28/I_R; OPRD3: D15/11/KY28/I_S; OPRD4: D15/11/KY28/I_T
D15 | 新化DS | 11 | 11kV | KY29 | 新29線(KY29) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D15/11/1BBUS/V; OPRD2: D15/11/KY29/I_R; OPRD3: D15/11/KY29/I_S; OPRD4: D15/11/KY29/I_T
D15 | 新化DS | 11 | 11kV | KY30 | 新30線(KY30) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D15/11/1BBUS/V; OPRD2: D15/11/KY30/I_R; OPRD3: D15/11/KY30/I_S; OPRD4: D15/11/KY30/I_T
D15 | 新化DS | 11 | 11kV | KY31 | 新31線(KY31) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D15/11/2ABUS/V; OPRD2: D15/11/KY31/I_R; OPRD3: D15/11/KY31/I_S; OPRD4: D15/11/KY31/I_T
D15 | 新化DS | 11 | 11kV | KY32 | 新32線(KY32) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D15/11/2ABUS/V; OPRD2: D15/11/KY32/I_R; OPRD3: D15/11/KY32/I_S; OPRD4: D15/11/KY32/I_T
D15 | 新化DS | 11 | 11kV | KY33 | 新33線(KY33) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D15/11/2ABUS/V; OPRD2: D15/11/KY33/I_R; OPRD3: D15/11/KY33/I_S; OPRD4: D15/11/KY33/I_T
D15 | 新化DS | 11 | 11kV | KY34 | 新34線(KY34) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D15/11/2ABUS/V; OPRD2: D15/11/KY34/I_R; OPRD3: D15/11/KY34/I_S; OPRD4: D15/11/KY34/I_T
D15 | 新化DS | 11 | 11kV | KY35 | 新35線(KY35) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D15/11/2ABUS/V; OPRD2: D15/11/KY35/I_R; OPRD3: D15/11/KY35/I_S; OPRD4: D15/11/KY35/I_T
D15 | 新化DS | 11 | 11kV | KY36 | 新36線(KY36) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D15/11/2ABUS/V; OPRD2: D15/11/KY36/I_R; OPRD3: D15/11/KY36/I_S; OPRD4: D15/11/KY36/I_T
D15 | 新化DS | 11 | 11kV | KY37 | 新37線(KY37) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D15/11/2BBUS/V; OPRD2: D15/11/KY37/I_R; OPRD3: D15/11/KY37/I_S; OPRD4: D15/11/KY37/I_T
D15 | 新化DS | 11 | 11kV | KY38 | 新38線(KY38) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D15/11/2BBUS/V; OPRD2: D15/11/KY38/I_R; OPRD3: D15/11/KY38/I_S; OPRD4: D15/11/KY38/I_T
D15 | 新化DS | 11 | 11kV | KY39 | 新39線(KY39) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D15/11/2BBUS/V; OPRD2: D15/11/KY39/I_R; OPRD3: D15/11/KY39/I_S; OPRD4: D15/11/KY39/I_T
D15 | 新化DS | 11 | 11kV | KY40 | 新40線(KY40) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D15/11/2BBUS/V; OPRD2: D15/11/KY40/I_R; OPRD3: D15/11/KY40/I_S; OPRD4: D15/11/KY40/I_T
D15 | 新化DS | 11 | 11kV | KY21 | 新21線(KY21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D15/11/KY21/kVA; OPRD2: D15/11/KY21/KVAR
D15 | 新化DS | 11 | 11kV | KY22 | 新22線(KY22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D15/11/KY22/kVA; OPRD2: D15/11/KY22/KVAR
D15 | 新化DS | 11 | 11kV | KY23 | 新23線(KY23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D15/11/KY23/kVA; OPRD2: D15/11/KY23/KVAR
D15 | 新化DS | 11 | 11kV | KY24 | 新24線(KY24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D15/11/KY24/kVA; OPRD2: D15/11/KY24/KVAR
D15 | 新化DS | 11 | 11kV | KY25 | 新25線(KY25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D15/11/KY25/kVA; OPRD2: D15/11/KY25/KVAR
D15 | 新化DS | 11 | 11kV | KY26 | 新26線(KY26) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D15/11/KY26/kVA; OPRD2: D15/11/KY26/KVAR
D15 | 新化DS | 11 | 11kV | KY27 | 新27線(KY27) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D15/11/KY27/kVA; OPRD2: D15/11/KY27/KVAR
D15 | 新化DS | 11 | 11kV | KY28 | 新28線(KY28) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D15/11/KY28/kVA; OPRD2: D15/11/KY28/KVAR
D15 | 新化DS | 11 | 11kV | KY29 | 新29線(KY29) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D15/11/KY29/kVA; OPRD2: D15/11/KY29/KVAR
D15 | 新化DS | 11 | 11kV | KY30 | 新30線(KY30) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D15/11/KY30/kVA; OPRD2: D15/11/KY30/KVAR
D15 | 新化DS | 11 | 11kV | KY31 | 新31線(KY31) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D15/11/KY31/kVA; OPRD2: D15/11/KY31/KVAR
D15 | 新化DS | 11 | 11kV | KY32 | 新32線(KY32) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D15/11/KY32/kVA; OPRD2: D15/11/KY32/KVAR
D15 | 新化DS | 11 | 11kV | KY33 | 新33線(KY33) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D15/11/KY33/kVA; OPRD2: D15/11/KY33/KVAR
D15 | 新化DS | 11 | 11kV | KY34 | 新34線(KY34) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D15/11/KY34/kVA; OPRD2: D15/11/KY34/KVAR
D15 | 新化DS | 11 | 11kV | KY35 | 新35線(KY35) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D15/11/KY35/kVA; OPRD2: D15/11/KY35/KVAR
D15 | 新化DS | 11 | 11kV | KY36 | 新36線(KY36) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D15/11/KY36/kVA; OPRD2: D15/11/KY36/KVAR
D15 | 新化DS | 11 | 11kV | KY37 | 新37線(KY37) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D15/11/KY37/kVA; OPRD2: D15/11/KY37/KVAR
D15 | 新化DS | 11 | 11kV | KY38 | 新38線(KY38) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D15/11/KY38/kVA; OPRD2: D15/11/KY38/KVAR
D15 | 新化DS | 11 | 11kV | KY39 | 新39線(KY39) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D15/11/KY39/kVA; OPRD2: D15/11/KY39/KVAR
D15 | 新化DS | 11 | 11kV | KY40 | 新40線(KY40) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D15_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D15/11/KY40/kVA; OPRD2: D15/11/KY40/KVAR
D15 | 新化DS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D15_A1 | [12 empty] | 新化DS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: D15/11/210/CB; OPRD2: 6.9; OPRD3: 0
D15 | 新化DS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D15_A1 | [12 empty] | 新化DS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: D15/11/220/CB; OPRD2: 6.9; OPRD3: 0
D15 | 新化DS | 11 | 11kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D15_A1 | [12 empty] | 新化DS.230_SC_MVAR | 11KV#3SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: D15/11/230/CB; OPRD2: 6.9; OPRD3: 0
D15 | 新化DS | 11 | 11kV | 240 | #4SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D15_A1 | [12 empty] | 新化DS.240_SC_MVAR | 11KV#4SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: D15/11/240/CB; OPRD2: 6.9; OPRD3: 0
D15 | 新化DS | 11 | 11kV | 250 | #5SC(250) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D15_A1 | [12 empty] | 新化DS.250_SC_MVAR | 11KV#5SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: D15/11/250/CB; OPRD2: 6.9; OPRD3: 0
D15 | 新化DS | 11 | 11kV | 260 | #6SC(260) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D15_A1 | [12 empty] | 新化DS.260_SC_MVAR | 11KV#6SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: D15/11/260/CB; OPRD2: 6.9; OPRD3: 0
D15 | 新化DS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/D15_A1 | [12 empty] | 新化DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_10 |  | com_alarm_22 | OPRD1: D15//1DTR/63Q; OPRD2: D15//1DTR/96D; OPRD3: D15//1DTR/96B1; OPRD4: D15//1DTR/TRA; OPRD5: D15//1DTR/96B2; OPRD6: D15//1DTR/51ZA; OPRD7: D15//1DTR/96PA; OPRD8: D15//1DTR/87A; OPRD9: D15//2DTR/TRA; OPRD10: D15//2DTR/96B2; OPRD11: D15//2DTR/96B1; OPRD12: D15//2DTR/63Q; OPRD13: D15//2DTR/51ZA; OPRD14: D15//2DTR/96D; OPRD15: D15//2DTR/96PA; OPRD16: D15//2DTR/87A; OPRD17: D15/11/310/GDA; OPRD18: D15/11/320/GDA; OPRD19: D15/11/330/GDA; OPRD20: D15/11/340/GDA; OPRD21: D15/161/1BUS/87A; OPRD22: D15/161/2BUS/87A
D15 | 新化DS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/D15_A1 | [12 empty] | 新化DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | STATION_FAULT_2 |  | com_alarm_2 | OPRD1: D15//1DTR/TRF; OPRD2: D15//2DTR/TRF
D15 | 新化DS | 161 | 161kV | 1750_D1 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D15_D1 | [17 empty] | lamp2CC | OPRD1: D15/161/1750/CB
D15 | 新化DS | 161 | 161kV | 1760_D1 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D15_D1 | [17 empty] | lamp2CC | OPRD1: D15/161/1760/CB
D15 | 新化DS | 11 | 11kV | 310_D1 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D15_D1 | [17 empty] | lamp2CC | OPRD1: D15/11/310/CB
D15 | 新化DS | 11 | 11kV | 320_D1 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D15_D1 | [17 empty] | lamp2CC | OPRD1: D15/11/320/CB
D15 | 新化DS | 11 | 11kV | 340_D1 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D15_D1 | [17 empty] | lamp2CC | OPRD1: D15/11/340/CB
D15 | 新化DS | 11 | 11kV | 330_D1 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D15_D1 | [17 empty] | lamp2CC | OPRD1: D15/11/330/CB
D15 | 新化DS | 0 |  | RTU_D1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/D15_D1 | [17 empty] | lamp2CC | OPRD1: D15/0/RTU/RTU_R_L
D15 | 新化DS | 0 |  | StaDev_D1 | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/D15_D1 | [17 empty] | lamp2CC | OPRD1: D15/0/StaDev/STUV
D15 | 新化DS | 0 |  | StaDev_D1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D15_D1 | [17 empty] | lamp2CC | OPRD1: D15/0/StaDev/DCE
D15 | 新化DS | 11 | 11kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D15_D1 | [17 empty] | lamp2CC | OPRD1: D15/11/ComPoint/CBA
D15 | 新化DS | 11 | 11kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | ELEM/D15_D1 | [17 empty] | lamp2CC | OPRD1: D15/11/ComPoint/CBF

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D15 | 新化DS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 新化DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | D15/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
D15 | 新化DS | 161 | 161kV | 1510 | 統實永資線(1510) |  | I | [25 empty] | ADCS_S | [8 empty] | 新化DS.1510_AMP | 統實永資線 AMP | LINE161 | D15/161/1510/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D15 | 新化DS | 161 | 161kV | 1710 | 山上新化一路(1710) |  | I | [25 empty] | ADCS_S | [8 empty] | 新化DS.1710_AMP | 山上新化一路 AMP | LINE161 | D15/161/1710/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D15 | 新化DS | 161 | 161kV | 1720 | 山上新化二路(1720) |  | I | [25 empty] | ADCS_S | [8 empty] | 新化DS.1720_AMP | 山上新化二路 AMP | LINE161 | D15/161/1720/I |  | AMP_CAL |  |  | 5 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D15 | 新化DS | 161 | 161kV | 1740 | 道爺安南新化線(1740) |  | I | [25 empty] | ADCS_S | [8 empty] | 新化DS.1740_AMP | 道爺安南新化線 AMP | LINE161 | D15/161/1740/I |  | AMP_CAL |  |  | 6 | CalcAIPoint | [21 empty] | C16R1576 | 1418.400024 | 1418.400024 | 1576.000000 | 1600.000000 | 1.200000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D15 | 新化DS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 新化DS.210_SC_MVAR | 11KV#1SC MVAR | SC | D15/11/210/MVAR |  | SC_CAL_11 |  |  | 7 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 11 | 11kV | 220_SC | #2SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 新化DS.220_SC_MVAR | 11KV#2SC MVAR | SC | D15/11/220/MVAR |  | SC_CAL_11 |  |  | 8 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 11 | 11kV | 230_SC | #3SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 新化DS.230_SC_MVAR | 11KV#3SC MVAR | SC | D15/11/230/MVAR |  | SC_CAL_11 |  |  | 9 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 11 | 11kV | 240_SC | #4SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 新化DS.240_SC_MVAR | 11KV#4SC MVAR | SC | D15/11/240/MVAR |  | SC_CAL_11 |  |  | 10 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 11 | 11kV | 250_SC | #5SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 新化DS.250_SC_MVAR | 11KV#5SC MVAR | SC | D15/11/250/MVAR |  | SC_CAL_11 |  |  | 11 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 11 | 11kV | 260_SC | #6SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 新化DS.260_SC_MVAR | 11KV#6SC MVAR | SC | D15/11/260/MVAR |  | SC_CAL_11 |  |  | 12 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 161 | 161kV | 1730 | 道爺和順新化線(1730) |  | I | [25 empty] | ADCS_S | [8 empty] | 新化DS.1730_AMP | 道爺和順新化線 AMP | LINE161 | D15/161/1730/I |  | AMP_CAL |  |  | 13 | CalcAIPoint | [21 empty] | C16R1576 | 1418.400024 | 1418.400024 | 1576.000000 | 1600.000000 | 1.200000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D15 | 新化DS | 0 |  | TRTOT | 新化主變瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 新化DS.TRTOT_MW | 新化主變瞬時供電量 MW |  |  |  | MTR_PQ_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  | TRTOT | 新化主變瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 新化DS.TRTOT_MVAR | 新化主變瞬時供電量 MVAR |  |  |  | MTR_PQ_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新21線KVA | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新21線KVA | 11KV新21線KVA | FEEDER |  |  | KVA_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新21線KW | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新21線KW | 11KV新21線KW | FEEDER |  |  | KW_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新22線KVA | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新22線KVA | 11KV新22線KVA | FEEDER |  |  | KVA_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新22線KW | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新22線KW | 11KV新22線KW | FEEDER |  |  | KW_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新23線KVA | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新23線KVA | 11KV新23線KVA | FEEDER |  |  | KVA_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新23線KW | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新23線KW | 11KV新23線KW | FEEDER |  |  | KW_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新24線KVA | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新24線KVA | 11KV新24線KVA | FEEDER |  |  | KVA_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新24線KW | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新24線KW | 11KV新24線KW | FEEDER |  |  | KW_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新25線KVA | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新25線KVA | 11KV新25線KVA | FEEDER |  |  | KVA_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新25線KW | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新25線KW | 11KV新25線KW | FEEDER |  |  | KW_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新26線KVA | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新26線KVA | 11KV新26線KVA | FEEDER |  |  | KVA_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新26線KW | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新26線KW | 11KV新26線KW | FEEDER |  |  | KW_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新31線KVA | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新31線KVA | 11KV新31線KVA | FEEDER |  |  | KVA_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新31線KW | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新31線KW | 11KV新31線KW | FEEDER |  |  | KW_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新32線KVA | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新32線KVA | 11KV新32線KVA | FEEDER |  |  | KVA_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新32線KW | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新32線KW | 11KV新32線KW | FEEDER |  |  | KW_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新33線KVA | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新33線KVA | 11KV新33線KVA | FEEDER |  |  | KVA_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新33線KW | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新33線KW | 11KV新33線KW | FEEDER |  |  | KW_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新34線KVA | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新34線KVA | 11KV新34線KVA | FEEDER |  |  | KVA_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新34線KW | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新34線KW | 11KV新34線KW | FEEDER |  |  | KW_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新35線KVA | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新35線KVA | 11KV新35線KVA | FEEDER |  |  | KVA_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新35線KW | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新35線KW | 11KV新35線KW | FEEDER |  |  | KW_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新36線KVA | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新36線KVA | 11KV新36線KVA | FEEDER |  |  | KVA_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新36線KW | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新36線KW | 11KV新36線KW | FEEDER |  |  | KW_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新27線KVA | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新27線KVA | 11KV新27線KVA | FEEDER |  |  | KVA_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新27線KW | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新27線KW | 11KV新27線KW | FEEDER |  |  | KW_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新28線KVA | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新28線KVA | 11KV新28線KVA | FEEDER |  |  | KVA_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新28線KW | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新28線KW | 11KV新28線KW | FEEDER |  |  | KW_CAL |  |  | 43 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新29線KVA | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新29線KVA | 11KV新29線KVA | FEEDER |  |  | KVA_CAL |  |  | 44 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新29線KW | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新29線KW | 11KV新29線KW | FEEDER |  |  | KW_CAL |  |  | 45 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新30線KVA | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新30線KVA | 11KV新30線KVA | FEEDER |  |  | KVA_CAL |  |  | 46 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新30線KW | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新30線KW | 11KV新30線KW | FEEDER |  |  | KW_CAL |  |  | 47 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新37線KVA | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新37線KVA | 11KV新37線KVA | FEEDER |  |  | KVA_CAL |  |  | 48 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新37線KW | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新37線KW | 11KV新37線KW | FEEDER |  |  | KW_CAL |  |  | 49 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新38線KVA | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新38線KVA | 11KV新38線KVA | FEEDER |  |  | KVA_CAL |  |  | 50 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新38線KW | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新38線KW | 11KV新38線KW | FEEDER |  |  | KW_CAL |  |  | 51 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新39線KVA | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新39線KVA | 11KV新39線KVA | FEEDER |  |  | KVA_CAL |  |  | 52 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新39線KW | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新39線KW | 11KV新39線KW | FEEDER |  |  | KW_CAL |  |  | 53 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新40線KVA | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新40線KVA | 11KV新40線KVA | FEEDER |  |  | KVA_CAL |  |  | 54 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  |  |  |  | 新40線KW | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.新40線KW | 11KV新40線KW | FEEDER |  |  | KW_CAL |  |  | 55 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 新化DS.#1DTR(A)_MVA | #1DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 56 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D15 | 新化DS | 0 |  | 1DTR(A) | #1DTR(A) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 新化DS.#1DTR(A)_LOAD | #1DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 57 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D15 | 新化DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PF | [25 empty] | ADCS_S | [8 empty] | 新化DS.#1DTR(A)_PF | #1DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 58 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D15 | 新化DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 新化DS.#1DTR(B)_MVA | #1DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 59 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D15 | 新化DS | 0 |  | 1DTR(B) | #1DTR(B) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 新化DS.#1DTR(B)_LOAD | #1DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 60 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D15 | 新化DS | 0 |  | 1DTR(B) | #1DTR(B) |  | PF | [25 empty] | ADCS_S | [8 empty] | 新化DS.#1DTR(B)_PF | #1DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 61 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D15 | 新化DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 新化DS.#2DTR(A)_MVA | #2DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 62 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D15 | 新化DS | 0 |  | 2DTR(A) | #2DTR(A) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 新化DS.#2DTR(A)_LOAD | #2DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 63 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D15 | 新化DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PF | [25 empty] | ADCS_S | [8 empty] | 新化DS.#2DTR(A)_PF | #2DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 64 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D15 | 新化DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 新化DS.#2DTR(B)_MVA | #2DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 65 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D15 | 新化DS | 0 |  | 2DTR(B) | #2DTR(B) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 新化DS.#2DTR(B)_LOAD | #2DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 66 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D15 | 新化DS | 0 |  | 2DTR(B) | #2DTR(B) |  | PF | [25 empty] | ADCS_S | [8 empty] | 新化DS.#2DTR(B)_PF | #2DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 67 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D15 | 新化DS | 0 |  | 1DTR | #1DTR |  | MW | [25 empty] | ADCS_S | [8 empty] | 新化DS.#1DTR_MW | #1DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 68 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  | 1DTR | #1DTR |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 新化DS.#1DTR_MVAR | #1DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 69 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  | 1DTR | #1DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 新化DS.#1DTR_MVA | #1DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 70 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D15 | 新化DS | 0 |  | 1DTR | #1DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 新化DS.#1DTR_LOAD | #1DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 71 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D15 | 新化DS | 0 |  | 2DTR | #2DTR |  | MW | [25 empty] | ADCS_S | [8 empty] | 新化DS.#2DTR_MW | #2DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 72 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  | 2DTR | #2DTR |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 新化DS.#2DTR_MVAR | #2DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 73 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 0 |  | 2DTR | #2DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 新化DS.#2DTR_MVA | #2DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 74 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D15 | 新化DS | 0 |  | 2DTR | #2DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 新化DS.#2DTR_LOAD | #2DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 75 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D15 | 新化DS | 0 |  | 1750_CB | #1DTR(1750_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.1750_CB_4 | 1750(#1DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 76 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | 310_CB | #1DTR(310_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.310_CB_4 | 310(#1DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 77 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | 320_CB | #1DTR(320_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.320_CB_4 | 320(#1DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 78 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | 1760_CB | #2DTR(1760_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.1760_CB_4 | 1760(#2DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 79 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | 330_CB | #2DTR(330_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.330_CB_4 | 330(#2DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 80 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | 340_CB | #2DTR(340_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.340_CB_4 | 340(#2DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 81 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | 210_CB | #1SC(210_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.210_CB_4 | 210(11KV #1SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 82 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | 220_CB | #2SC(220_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.220_CB_4 | 220(11KV #2SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 83 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | 230_CB | #3SC(230_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.230_CB_4 | 230(11KV #3SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 84 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | 240_CB | #4SC(240_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.240_CB_4 | 240(11KV #4SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 85 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | 250_CB | #5SC(250_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.250_CB_4 | 250(11KV #5SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 86 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | 260_CB | #6SC(260_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.260_CB_4 | 260(11KV #6SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 87 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 22 | 22kV | 11__CBA | 11/斷路器重故障(11__CBA) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.11/23KV_CBA_4 | 11/23KV斷路器重故障 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 88 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D15 | 新化DS | 22 | 22kV | 11__CBF | 11/斷路器輕故障(11__CBF) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.11/23KV_CBF_4 | 11/23KV斷路器輕故障 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 89 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D15 | 新化DS | 0 |  | RTU_S_L | RTU |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.RTU_S/L_4 | RTU SUPY/LOCAL (D4) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 90 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D15 | 新化DS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_S | [8 empty] | 新化DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | D15/0/CalcPoint/SUBA |  | STATION_FAULT_10 |  |  | 91 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 變電所輕故障點燈 | 變電所輕故障點燈 |  | SUBF | [25 empty] | ADCS_S | [8 empty] | 新化DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | D15/0/CalcPoint/SUBF |  | STATION_FAULT_2 |  |  | 92 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.變電所重故障_4 | 變電所重故障點燈 (D4) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 93 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.變電所輕故障_4 | 變電所輕故障點燈 (D4) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 94 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1510_AMP | 統實永資線 | [27 empty] | ADCS_S | [8 empty] | 新化DS.1510_AMP_A | 統實永資線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 95 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D15 | 新化DS | 161 | 161kV | 1710_AMP | 山上一路 | [27 empty] | ADCS_S | [8 empty] | 新化DS.1710_AMP_A | 山上一路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 96 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D15 | 新化DS | 161 | 161kV | 1720_AMP | 山上二路 | [27 empty] | ADCS_S | [8 empty] | 新化DS.1720_AMP_A | 山上二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 97 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D15 | 新化DS | 161 | 161kV | 1740_AMP | 道爺安南新化線 | [27 empty] | ADCS_S | [8 empty] | 新化DS.1740_AMP_A | 道爺安南新化線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 98 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D15 | 新化DS | 161 | 161kV | 1730_AMP | 道爺和順新化線 | [27 empty] | ADCS_S | [8 empty] | 新化DS.1730_AMP_A | 道爺和順新化線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 99 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D15 | 新化DS | 0 |  | 100_CB | 100(100_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.100_CB_4 | 100 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 100 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | 200_CB | 200(200_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.200_CB_4 | 200 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 101 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PERM | [25 empty] | ADCS_S | [8 empty] | 新化DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | D15//1DTR(A)/TR_PERM |  | DTR_PERM |  |  | 102 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D15 | 新化DS | 0 |  | 1DTR(B) | #1DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 新化DS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | D15//1DTR(B)/TR_PERM |  | DTR_PERM |  |  | 103 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D15 | 新化DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PERM | [25 empty] | ADCS_S | [8 empty] | 新化DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | D15//2DTR(A)/TR_PERM |  | DTR_PERM |  |  | 104 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D15 | 新化DS | 0 |  | 2DTR(B) | #2DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 新化DS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | D15//2DTR(B)/TR_PERM |  | DTR_PERM |  |  | 105 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D15 | 新化DS | 0 |  | 1DTR_MVA | #1DTR | [27 empty] | ADCS_S | [8 empty] | 新化DS.#1DTR_MVA_A | #1DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 106 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D15 | 新化DS | 0 |  | 1DTR_MVA | #1DTR(A) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.#1DTR_MVA_4 | #1DTR(A) MVA 點燈 (D4) | MTR |  |  | MAP_SET |  |  | 107 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D15 | 新化DS | 0 |  | 2DTR_MVA | #2DTR | [27 empty] | ADCS_S | [8 empty] | 新化DS.#2DTR_MVA_A | #2DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 108 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D15 | 新化DS | 0 |  | 2DTR_MVA | #2DTR(A) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.#2DTR_MVA_4 | #2DTR(A) MVA 點燈 (D4) | MTR |  |  | MAP_SET |  |  | 109 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D15 | 新化DS | 0 |  | 1DTR_MVA | #1DTR(B) |  | 5 | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.#1DTR_MVA_5 | #1DTR(B) MVA 點燈 |  |  |  | MAP_SET |  |  | 110 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D15 | 新化DS | 0 |  | 2DTR_MVA | #2DTR(B) |  | 5 | [25 empty] | DDCS4_2 | [8 empty] | 新化DS.#2DTR_MVA_5 | #2DTR(B) MVA 點燈 |  |  |  | MAP_SET |  |  | 111 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D15 | 新化DS | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_S | [8 empty] | 新化DS.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_DS |  |  | 112 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 1ABUS | #1ABUS |  | 11KV#1ABUSC | [25 empty] | CDCS | [8 empty] | 新化DS.11KV#1ABUSC | #1ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 113 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D15 | 新化DS | 0 |  | 1BBUS | #1BBUS |  | 11KV#1BBUSC | [25 empty] | CDCS | [8 empty] | 新化DS.11KV#1BBUSC | #1BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 114 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D15 | 新化DS | 0 |  | 2BBUS | #2BBUS |  | 11KV#2BBUSC | [25 empty] | CDCS | [8 empty] | 新化DS.11KV#2BBUSC | #2BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 115 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D15 | 新化DS | 0 |  | 2ABUS | #2ABUS |  | 11KV#2ABUSC | [25 empty] | CDCS | [8 empty] | 新化DS.11KV#2ABUSC | #2ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 116 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D15 | 新化DS | 0 |  | TAP_OVER | TAP |  | SET | [25 empty] | ADCS_S | [8 empty] | 新化DS.TAP_OVER_SET | TAP OVER HI/LO ALARM | MTR |  |  | 5000_CB_T4 |  |  | 117 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D15 | 新化DS | 0 |  | BUS_OVER | BUS |  | SET | [25 empty] | ADCS_S | [8 empty] | 新化DS.BUS_OVER_SET | BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B4 |  |  | 118 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D15 | 新化DS | 0 |  | 5000 | 虛擬5000 |  | CB動作 | [25 empty] | ADCS_S | [8 empty] | 新化DS.5000_CB動作 | 虛擬5000 CB動作,請查明原因處理 | MTR |  |  | 5000_CB_M |  |  | 119 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | 注意OLTC | 注意OLTC |  | BUS電壓異常 | [25 empty] | ADCS_S | [8 empty] | 新化DS.BUS電壓異常 | 注意OLTC Tap位置,並將RPDC閉鎖 | OTHER |  |  | STATION_FAULT_1 |  |  | 120 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | D15/0/RTU/ADCH1 |  |  |  | CDC | 121 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D15 | 新化DS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | D15/0/RTU/ADCH2 |  |  |  | CDC | 122 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D15 | 新化DS | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | D15/0/RTU/ADCH3 |  |  |  | CDC | 123 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D15 | 新化DS | 0 |  | AI | AI |  | ADCH4 | [17 empty] | 2-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | D15/0/RTU/ADCH4 |  |  |  | CDC | 124 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D15 | 新化DS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | D15/0/RTU/ADCL1 |  |  |  | CDC | 125 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D15 | 新化DS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | D15/0/RTU/ADCL2 |  |  |  | CDC | 126 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D15 | 新化DS | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | D15/0/RTU/ADCL3 |  |  |  | CDC | 127 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D15 | 新化DS | 0 |  | AI | AI |  | ADCL4 | [17 empty] | 2-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | D15/0/RTU/ADCL4 |  |  |  | CDC | 128 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D15 | 新化DS | 161 | 161kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | D15/161/1BUS/V |  |  |  | CDC | 129 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D15 | 新化DS | 161 | 161kV | 2BUS | #2BUS |  | V | [17 empty] | 1-83 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | D15/161/2BUS/V |  |  |  | CDC | 130 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D15 | 新化DS | 11 | 11kV | 1ABUS | #1ABUS |  | V | [17 empty] | 1-C8 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.11KV#1ABUS_KV | 11KV #1ABUS KV | BUS | D15/11/1ABUS/V |  |  |  | CDC | 131 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D15 | 新化DS | 11 | 11kV | 2ABUS | #2ABUS |  | V | [17 empty] | 2-9B | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS | D15/11/2ABUS/V |  |  |  | CDC | 132 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D15 | 新化DS | 161 | 161kV | 1510 | 統實永資線(1510) |  | MW | [17 empty] | 1-8C | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.1510_MW | 統實永資線 MW | LINE161 | D15/161/1510/MW |  |  |  | CDC | 133 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D15 | 新化DS | 161 | 161kV | 1510 | 統實永資線(1510) |  | MVAR | [17 empty] | 1-8D | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.1510_MVAR | 統實永資線 MVAR | LINE161 | D15/161/1510/MVAR |  |  |  | CDC | 134 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D15 | 新化DS | 161 | 161kV | 1710 | 山上一路(1710) |  | MW | [17 empty] | 1-8A | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.1710_MW | 山上一路 MW | LINE161 | D15/161/1710/MW |  |  |  | CDC | 135 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D15 | 新化DS | 161 | 161kV | 1710 | 山上一路(1710) |  | MVAR | [17 empty] | 1-8B | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.1710_MVAR | 山上一路 MVAR | LINE161 | D15/161/1710/MVAR |  |  |  | CDC | 136 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D15 | 新化DS | 161 | 161kV | 1720 | 山上二路(1720) |  | MW | [17 empty] | 1-88 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.1720_MW | 山上二路 MW | LINE161 | D15/161/1720/MW |  |  |  | CDC | 137 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D15 | 新化DS | 161 | 161kV | 1720 | 山上二路(1720) |  | MVAR | [17 empty] | 1-89 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.1720_MVAR | 山上二路 MVAR | LINE161 | D15/161/1720/MVAR |  |  |  | CDC | 138 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D15 | 新化DS | 161 | 161kV | 1740 | 道爺安南新化線(1740) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-448_448(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.1740_MW | 道爺安南新化線 MW | LINE161 | D15/161/1740/MW |  |  |  | CDC | 139 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
D15 | 新化DS | 161 | 161kV | 1740 | 道爺安南新化線(1740) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-448_448(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.1740_MVAR | 道爺安南新化線 MVAR | LINE161 | D15/161/1740/MVAR |  |  |  | CDC | 140 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
D15 | 新化DS | 0 |  | 1500TIE | 1500TIE |  | I | [17 empty] | 1-94 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.1500TIE_AMP | 1500TIE AMP | TIE | D15/161/1500/I_R |  |  |  | CDC | 141 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
D15 | 新化DS | 0 |  |  |  |  | DCV_N | [17 empty] | 1-93 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.直流N電源電壓 | 直流N電源電壓 | OTHER | D15/0/StaDev/DCV_N |  |  |  | CDC | 142 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D15 | 新化DS | 0 |  |  |  |  | DCV_P | [17 empty] | 1-92 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.直流P電源電壓 | 直流P電源電壓 | OTHER | D15/0/StaDev/DCV_P |  |  |  | CDC | 143 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D15 | 新化DS | 161 | 161kV | 1730 | 道爺和順新化線(1730) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-448_448(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.1730_MW | 道爺和順新化線 MW | LINE161 | D15/161/1730/MW |  |  |  | CDC | 144 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
D15 | 新化DS | 161 | 161kV | 1730 | 道爺和順新化線(1730) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-448_448(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.1730_MVAR | 道爺和順新化線 MVAR | LINE161 | D15/161/1730/MVAR |  |  |  | CDC | 145 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新21線 | 新21線 |  | 新21線KVAR | [17 empty] | 1-AE | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新21線KVAR | 11KV新21線 KVAR | FEEDER | D15/11/KY21/KVAR |  |  |  | CDC | 146 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新21線 | 新21線 |  | 新21線A1 | [17 empty] | 1-AF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新21線A1 | 11KV新21線 R相AMP | FEEDER | D15/11/KY21/I_R |  |  |  | CDC | 147 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新21線 | 新21線 |  | 新21線A2 | [17 empty] | 1-B0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新21線A2 | 11KV新21線 S相AMP | FEEDER | D15/11/KY21/I_S |  |  |  | CDC | 148 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新21線 | 新21線 |  | 新21線A3 | [17 empty] | 1-B1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新21線A3 | 11KV新21線 T相AMP | FEEDER | D15/11/KY21/I_T |  |  |  | CDC | 149 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新21線 | 新21線 |  | 新21線A0 | [17 empty] | 2-A0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新21線A0 | 11KV新21線 N相AMP | FEEDER | D15/11/KY21/I_N |  |  |  | CDC | 150 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新22線 | 新22線 |  | 新22線KVAR | [17 empty] | 1-B2 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新22線KVAR | 11KV新22線 KVAR | FEEDER | D15/11/KY22/KVAR |  |  |  | CDC | 151 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新22線 | 新22線 |  | 新22線A1 | [17 empty] | 1-B3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新22線A1 | 11KV新22線 R相AMP | FEEDER | D15/11/KY22/I_R |  |  |  | CDC | 152 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新22線 | 新22線 |  | 新22線A2 | [17 empty] | 1-B4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新22線A2 | 11KV新22線 S相AMP | FEEDER | D15/11/KY22/I_S |  |  |  | CDC | 153 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新22線 | 新22線 |  | 新22線A3 | [17 empty] | 1-B5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新22線A3 | 11KV新22線 T相AMP | FEEDER | D15/11/KY22/I_T |  |  |  | CDC | 154 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新22線 | 新22線 |  | 新22線A0 | [17 empty] | 2-A1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新22線A0 | 11KV新22線 N相AMP | FEEDER | D15/11/KY22/I_N |  |  |  | CDC | 155 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新23線 | 新23線 |  | 新23線KVAR | [17 empty] | 1-B6 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新23線KVAR | 11KV新23線 KVAR | FEEDER | D15/11/KY23/KVAR |  |  |  | CDC | 156 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新23線 | 新23線 |  | 新23線A1 | [17 empty] | 1-B7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新23線A1 | 11KV新23線 R相AMP | FEEDER | D15/11/KY23/I_R |  |  |  | CDC | 157 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新23線 | 新23線 |  | 新23線A2 | [17 empty] | 1-B8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新23線A2 | 11KV新23線 S相AMP | FEEDER | D15/11/KY23/I_S |  |  |  | CDC | 158 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新23線 | 新23線 |  | 新23線A3 | [17 empty] | 1-B9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新23線A3 | 11KV新23線 T相AMP | FEEDER | D15/11/KY23/I_T |  |  |  | CDC | 159 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新23線 | 新23線 |  | 新23線A0 | [17 empty] | 2-A2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新23線A0 | 11KV新23線 N相AMP | FEEDER | D15/11/KY23/I_N |  |  |  | CDC | 160 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新24線 | 新24線 |  | 新24線KVAR | [17 empty] | 1-BA | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新24線KVAR | 11KV新24線 KVAR | FEEDER | D15/11/KY24/KVAR |  |  |  | CDC | 161 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新24線 | 新24線 |  | 新24線A1 | [17 empty] | 1-BB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新24線A1 | 11KV新24線 R相AMP | FEEDER | D15/11/KY24/I_R |  |  |  | CDC | 162 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新24線 | 新24線 |  | 新24線A2 | [17 empty] | 1-BC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新24線A2 | 11KV新24線 S相AMP | FEEDER | D15/11/KY24/I_S |  |  |  | CDC | 163 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新24線 | 新24線 |  | 新24線A3 | [17 empty] | 1-BD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新24線A3 | 11KV新24線 T相AMP | FEEDER | D15/11/KY24/I_T |  |  |  | CDC | 164 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新24線 | 新24線 |  | 新24線A0 | [17 empty] | 2-A3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新24線A0 | 11KV新24線 N相AMP | FEEDER | D15/11/KY24/I_N |  |  |  | CDC | 165 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新25線 | 新25線 |  | 新25線KVAR | [17 empty] | 1-BE | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新25線KVAR | 11KV新25線 KVAR | FEEDER | D15/11/KY25/KVAR |  |  |  | CDC | 166 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新25線 | 新25線 |  | 新25線A1 | [17 empty] | 1-BF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新25線A1 | 11KV新25線 R相AMP | FEEDER | D15/11/KY25/I_R |  |  |  | CDC | 167 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新25線 | 新25線 |  | 新25線A2 | [17 empty] | 1-C2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新25線A2 | 11KV新25線 S相AMP | FEEDER | D15/11/KY25/I_S |  |  |  | CDC | 168 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新25線 | 新25線 |  | 新25線A3 | [17 empty] | 1-C3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新25線A3 | 11KV新25線 T相AMP | FEEDER | D15/11/KY25/I_T |  |  |  | CDC | 169 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新25線 | 新25線 |  | 新25線A0 | [17 empty] | 2-A4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新25線A0 | 11KV新25線 N相AMP | FEEDER | D15/11/KY25/I_N |  |  |  | CDC | 170 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新26線 | 新26線 |  | 新26線KVAR | [17 empty] | 1-C4 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新26線KVAR | 11KV新26線 KVAR | FEEDER | D15/11/KY26/KVAR |  |  |  | CDC | 171 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新26線 | 新26線 |  | 新26線A1 | [17 empty] | 1-C5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新26線A1 | 11KV新26線 R相AMP | FEEDER | D15/11/KY26/I_R |  |  |  | CDC | 172 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新26線 | 新26線 |  | 新26線A2 | [17 empty] | 1-C6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新26線A2 | 11KV新26線 S相AMP | FEEDER | D15/11/KY26/I_S |  |  |  | CDC | 173 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新26線 | 新26線 |  | 新26線A3 | [17 empty] | 1-C7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新26線A3 | 11KV新26線 T相AMP | FEEDER | D15/11/KY26/I_T |  |  |  | CDC | 174 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新26線 | 新26線 |  | 新26線A0 | [17 empty] | 2-A5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新26線A0 | 11KV新26線 N相AMP | FEEDER | D15/11/KY26/I_N |  |  |  | CDC | 175 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新31線 | 新31線 |  | 新31線KVAR | [17 empty] | 2-83 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新31線KVAR | 11KV新31線 KVAR | FEEDER | D15/11/KY31/KVAR |  |  |  | CDC | 176 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新31線 | 新31線 |  | 新31線A1 | [17 empty] | 2-84 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新31線A1 | 11KV新31線 R相AMP | FEEDER | D15/11/KY31/I_R |  |  |  | CDC | 177 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新31線 | 新31線 |  | 新31線A2 | [17 empty] | 2-85 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新31線A2 | 11KV新31線 S相AMP | FEEDER | D15/11/KY31/I_S |  |  |  | CDC | 178 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新31線 | 新31線 |  | 新31線A3 | [17 empty] | 2-86 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新31線A3 | 11KV新31線 T相AMP | FEEDER | D15/11/KY31/I_T |  |  |  | CDC | 179 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新31線 | 新31線 |  | 新31線A0 | [17 empty] | 2-AE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新31線A0 | 11KV新31線 N相AMP | FEEDER | D15/11/KY31/I_N |  |  |  | CDC | 180 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新32線 | 新32線 |  | 新32線KVAR | [17 empty] | 2-87 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新32線KVAR | 11KV新32線 KVAR | FEEDER | D15/11/KY32/KVAR |  |  |  | CDC | 181 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新32線 | 新32線 |  | 新32線A1 | [17 empty] | 2-88 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新32線A1 | 11KV新32線 R相AMP | FEEDER | D15/11/KY32/I_R |  |  |  | CDC | 182 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新32線 | 新32線 |  | 新32線A2 | [17 empty] | 2-89 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新32線A2 | 11KV新32線 S相AMP | FEEDER | D15/11/KY32/I_S |  |  |  | CDC | 183 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新32線 | 新32線 |  | 新32線A3 | [17 empty] | 2-8A | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新32線A3 | 11KV新32線 T相AMP | FEEDER | D15/11/KY32/I_T |  |  |  | CDC | 184 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新32線 | 新32線 |  | 新32線A0 | [17 empty] | 2-AF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新32線A0 | 11KV新32線 N相AMP | FEEDER | D15/11/KY32/I_N |  |  |  | CDC | 185 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新33線 | 新33線 |  | 新33線KVAR | [17 empty] | 2-8B | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新33線KVAR | 11KV新33線 KVAR | FEEDER | D15/11/KY33/KVAR |  |  |  | CDC | 186 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新33線 | 新33線 |  | 新33線A1 | [17 empty] | 2-8C | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新33線A1 | 11KV新33線 R相AMP | FEEDER | D15/11/KY33/I_R |  |  |  | CDC | 187 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新33線 | 新33線 |  | 新33線A2 | [17 empty] | 2-8D | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新33線A2 | 11KV新33線 S相AMP | FEEDER | D15/11/KY33/I_S |  |  |  | CDC | 188 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新33線 | 新33線 |  | 新33線A3 | [17 empty] | 2-8E | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新33線A3 | 11KV新33線 T相AMP | FEEDER | D15/11/KY33/I_T |  |  |  | CDC | 189 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新33線 | 新33線 |  | 新33線A0 | [17 empty] | 2-B0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新33線A0 | 11KV新33線 N相AMP | FEEDER | D15/11/KY33/I_N |  |  |  | CDC | 190 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新34線 | 新34線 |  | 新34線KVAR | [17 empty] | 2-8F | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新34線KVAR | 11KV新34線 KVAR | FEEDER | D15/11/KY34/KVAR |  |  |  | CDC | 191 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新34線 | 新34線 |  | 新34線A1 | [17 empty] | 2-90 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新34線A1 | 11KV新34線 R相AMP | FEEDER | D15/11/KY34/I_R |  |  |  | CDC | 192 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新34線 | 新34線 |  | 新34線A2 | [17 empty] | 2-91 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新34線A2 | 11KV新34線 S相AMP | FEEDER | D15/11/KY34/I_S |  |  |  | CDC | 193 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新34線 | 新34線 |  | 新34線A3 | [17 empty] | 2-92 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新34線A3 | 11KV新34線 T相AMP | FEEDER | D15/11/KY34/I_T |  |  |  | CDC | 194 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新34線 | 新34線 |  | 新34線A0 | [17 empty] | 2-B1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新34線A0 | 11KV新34線 N相AMP | FEEDER | D15/11/KY34/I_N |  |  |  | CDC | 195 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新35線 | 新35線 |  | 新35線KVAR | [17 empty] | 2-93 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新35線KVAR | 11KV新35線 KVAR | FEEDER | D15/11/KY35/KVAR |  |  |  | CDC | 196 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新35線 | 新35線 |  | 新35線A1 | [17 empty] | 2-94 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新35線A1 | 11KV新35線 R相AMP | FEEDER | D15/11/KY35/I_R |  |  |  | CDC | 197 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新35線 | 新35線 |  | 新35線A2 | [17 empty] | 2-95 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新35線A2 | 11KV新35線 S相AMP | FEEDER | D15/11/KY35/I_S |  |  |  | CDC | 198 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新35線 | 新35線 |  | 新35線A3 | [17 empty] | 2-96 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新35線A3 | 11KV新35線 T相AMP | FEEDER | D15/11/KY35/I_T |  |  |  | CDC | 199 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新35線 | 新35線 |  | 新35線A0 | [17 empty] | 2-B2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新35線A0 | 11KV新35線 N相AMP | FEEDER | D15/11/KY35/I_N |  |  |  | CDC | 200 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新36線 | 新36線 |  | 新36線KVAR | [17 empty] | 2-97 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新36線KVAR | 11KV新36線 KVAR | FEEDER | D15/11/KY36/KVAR |  |  |  | CDC | 201 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新36線 | 新36線 |  | 新36線A1 | [17 empty] | 2-98 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新36線A1 | 11KV新36線 R相AMP | FEEDER | D15/11/KY36/I_R |  |  |  | CDC | 202 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新36線 | 新36線 |  | 新36線A2 | [17 empty] | 2-99 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新36線A2 | 11KV新36線 S相AMP | FEEDER | D15/11/KY36/I_S |  |  |  | CDC | 203 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新36線 | 新36線 |  | 新36線A3 | [17 empty] | 2-9A | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新36線A3 | 11KV新36線 T相AMP | FEEDER | D15/11/KY36/I_T |  |  |  | CDC | 204 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新36線 | 新36線 |  | 新36線A0 | [17 empty] | 2-B3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新36線A0 | 11KV新36線 N相AMP | FEEDER | D15/11/KY36/I_N |  |  |  | CDC | 205 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 1BBUS | #1BBUS |  | V | [17 empty] | 1-E1 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.11KV#1BBUS_KV | 11KV #1BBUS KV | BUS | D15/11/1BBUS/V |  |  |  | CDC | 206 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D15 | 新化DS | 11 | 11kV | 2BBUS | #2BBUS |  | V | [17 empty] | 1-F7 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.11KV#2BBUS_KV | 11KV #2BBUS KV | BUS | D15/11/2BBUS/V |  |  |  | CDC | 207 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D15 | 新化DS | 11 | 11kV | 新27線 | 新27線 |  | 新27線KVAR | [17 empty] | 1-D1 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新27線KVAR | 11KV新27線 KVAR | FEEDER | D15/11/KY27/KVAR |  |  |  | CDC | 208 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新27線 | 新27線 |  | 新27線A1 | [17 empty] | 1-D2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新27線A1 | 11KV新27線 R相AMP | FEEDER | D15/11/KY27/I_R |  |  |  | CDC | 209 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新27線 | 新27線 |  | 新27線A2 | [17 empty] | 1-D3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新27線A2 | 11KV新27線 S相AMP | FEEDER | D15/11/KY27/I_S |  |  |  | CDC | 210 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新27線 | 新27線 |  | 新27線A3 | [17 empty] | 1-D4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新27線A3 | 11KV新27線 T相AMP | FEEDER | D15/11/KY27/I_T |  |  |  | CDC | 211 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新27線 | 新27線 |  | 新27線A0 | [17 empty] | 2-A6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新27線A0 | 11KV新27線 N相AMP | FEEDER | D15/11/KY27/I_N |  |  |  | CDC | 212 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新28線 | 新28線 |  | 新28線KVAR | [17 empty] | 1-D5 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新28線KVAR | 11KV新28線 KVAR | FEEDER | D15/11/KY28/KVAR |  |  |  | CDC | 213 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新28線 | 新28線 |  | 新28線A1 | [17 empty] | 1-D6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新28線A1 | 11KV新28線 R相AMP | FEEDER | D15/11/KY28/I_R |  |  |  | CDC | 214 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新28線 | 新28線 |  | 新28線A2 | [17 empty] | 1-D7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新28線A2 | 11KV新28線 S相AMP | FEEDER | D15/11/KY28/I_S |  |  |  | CDC | 215 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新28線 | 新28線 |  | 新28線A3 | [17 empty] | 1-D8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新28線A3 | 11KV新28線 T相AMP | FEEDER | D15/11/KY28/I_T |  |  |  | CDC | 216 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新28線 | 新28線 |  | 新28線A0 | [17 empty] | 2-A7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新28線A0 | 11KV新28線 N相AMP | FEEDER | D15/11/KY28/I_N |  |  |  | CDC | 217 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新29線 | 新29線 |  | 新29線KVAR | [17 empty] | 1-D9 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新29線KVAR | 11KV新29線 KVAR | FEEDER | D15/11/KY29/KVAR |  |  |  | CDC | 218 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新29線 | 新29線 |  | 新29線A1 | [17 empty] | 1-DA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新29線A1 | 11KV新29線 R相AMP | FEEDER | D15/11/KY29/I_R |  |  |  | CDC | 219 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新29線 | 新29線 |  | 新29線A2 | [17 empty] | 1-DB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新29線A2 | 11KV新29線 S相AMP | FEEDER | D15/11/KY29/I_S |  |  |  | CDC | 220 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新29線 | 新29線 |  | 新29線A3 | [17 empty] | 1-DC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新29線A3 | 11KV新29線 T相AMP | FEEDER | D15/11/KY29/I_T |  |  |  | CDC | 221 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新29線 | 新29線 |  | 新29線A0 | [17 empty] | 2-A8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新29線A0 | 11KV新29線 N相AMP | FEEDER | D15/11/KY29/I_N |  |  |  | CDC | 222 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新30線 | 新30線 |  | 新30線KVAR | [17 empty] | 1-DD | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新30線KVAR | 11KV新30線 KVAR | FEEDER | D15/11/KY30/KVAR |  |  |  | CDC | 223 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新30線 | 新30線 |  | 新30線A1 | [17 empty] | 1-DE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新30線A1 | 11KV新30線 R相AMP | FEEDER | D15/11/KY30/I_R |  |  |  | CDC | 224 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新30線 | 新30線 |  | 新30線A2 | [17 empty] | 1-DF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新30線A2 | 11KV新30線 S相AMP | FEEDER | D15/11/KY30/I_S |  |  |  | CDC | 225 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新30線 | 新30線 |  | 新30線A3 | [17 empty] | 1-E0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新30線A3 | 11KV新30線 T相AMP | FEEDER | D15/11/KY30/I_T |  |  |  | CDC | 226 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新30線 | 新30線 |  | 新30線A0 | [17 empty] | 2-A9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新30線A0 | 11KV新30線 N相AMP | FEEDER | D15/11/KY30/I_N |  |  |  | CDC | 227 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新37線 | 新37線 |  | 新37線KVAR | [17 empty] | 1-E7 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新37線KVAR | 11KV新37線 KVAR | FEEDER | D15/11/KY37/KVAR |  |  |  | CDC | 228 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新37線 | 新37線 |  | 新37線A1 | [17 empty] | 1-E8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新37線A1 | 11KV新37線 R相AMP | FEEDER | D15/11/KY37/I_R |  |  |  | CDC | 229 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新37線 | 新37線 |  | 新37線A2 | [17 empty] | 1-E9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新37線A2 | 11KV新37線 S相AMP | FEEDER | D15/11/KY37/I_S |  |  |  | CDC | 230 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新37線 | 新37線 |  | 新37線A3 | [17 empty] | 1-EA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新37線A3 | 11KV新37線 T相AMP | FEEDER | D15/11/KY37/I_T |  |  |  | CDC | 231 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新37線 | 新37線 |  | 新37線A0 | [17 empty] | 2-AA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新37線A0 | 11KV新37線 N相AMP | FEEDER | D15/11/KY37/I_N |  |  |  | CDC | 232 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新38線 | 新38線 |  | 新38線KVAR | [17 empty] | 1-EB | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新38線KVAR | 11KV新38線 KVAR | FEEDER | D15/11/KY38/KVAR |  |  |  | CDC | 233 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新38線 | 新38線 |  | 新38線A1 | [17 empty] | 1-EC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新38線A1 | 11KV新38線 R相AMP | FEEDER | D15/11/KY38/I_R |  |  |  | CDC | 234 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新38線 | 新38線 |  | 新38線A2 | [17 empty] | 1-ED | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新38線A2 | 11KV新38線 S相AMP | FEEDER | D15/11/KY38/I_S |  |  |  | CDC | 235 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新38線 | 新38線 |  | 新38線A3 | [17 empty] | 1-EE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新38線A3 | 11KV新38線 T相AMP | FEEDER | D15/11/KY38/I_T |  |  |  | CDC | 236 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新38線 | 新38線 |  | 新38線A0 | [17 empty] | 2-AB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新38線A0 | 11KV新38線 N相AMP | FEEDER | D15/11/KY38/I_N |  |  |  | CDC | 237 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新39線 | 新39線 |  | 新39線KVAR | [17 empty] | 1-EF | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新39線KVAR | 11KV新39線 KVAR | FEEDER | D15/11/KY39/KVAR |  |  |  | CDC | 238 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新39線 | 新39線 |  | 新39線A1 | [17 empty] | 1-F0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新39線A1 | 11KV新39線 R相AMP | FEEDER | D15/11/KY39/I_R |  |  |  | CDC | 239 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新39線 | 新39線 |  | 新39線A2 | [17 empty] | 1-F1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新39線A2 | 11KV新39線 S相AMP | FEEDER | D15/11/KY39/I_S |  |  |  | CDC | 240 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新39線 | 新39線 |  | 新39線A3 | [17 empty] | 1-F2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新39線A3 | 11KV新39線 T相AMP | FEEDER | D15/11/KY39/I_T |  |  |  | CDC | 241 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新39線 | 新39線 |  | 新39線A0 | [17 empty] | 2-AC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新39線A0 | 11KV新39線 N相AMP | FEEDER | D15/11/KY39/I_N |  |  |  | CDC | 242 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新40線 | 新40線 |  | 新40線KVAR | [17 empty] | 1-F3 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新40線KVAR | 11KV新40線 KVAR | FEEDER | D15/11/KY40/KVAR |  |  |  | CDC | 243 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新40線 | 新40線 |  | 新40線A1 | [17 empty] | 1-F4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新40線A1 | 11KV新40線 R相AMP | FEEDER | D15/11/KY40/I_R |  |  |  | CDC | 244 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新40線 | 新40線 |  | 新40線A2 | [17 empty] | 1-F5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新40線A2 | 11KV新40線 S相AMP | FEEDER | D15/11/KY40/I_S |  |  |  | CDC | 245 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新40線 | 新40線 |  | 新40線A3 | [17 empty] | 1-F6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新40線A3 | 11KV新40線 T相AMP | FEEDER | D15/11/KY40/I_T |  |  |  | CDC | 246 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | 新40線 | 新40線 |  | 新40線A0 | [17 empty] | 2-AD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 新化DS.新40線A0 | 11KV新40線 N相AMP | FEEDER | D15/11/KY40/I_N |  |  |  | CDC | 247 | GENERICAIPoint | DS034_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | _100 | 100 |  | I_R | [17 empty] | 1-C9 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.11KV_100_A1 | 11KV 100 R相AMP | TIE | D15/11/100/I_R |  |  |  | CDC | 248 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C20R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | _100 | 100 |  | I_S | [17 empty] | 1-CA | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.11KV_100_A2 | 11KV 100 S相AMP | TIE | D15/11/100/I_S |  |  |  | CDC | 249 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C20R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | _100 | 100 |  | I_T | [17 empty] | 1-CB | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.11KV_100_A3 | 11KV 100 T相AMP | TIE | D15/11/100/I_T |  |  |  | CDC | 250 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C20R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | _200 | 200 |  | I_R | [17 empty] | 1-F8 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.11KV_200_A1 | 11KV 200 R相AMP | TIE | D15/11/200/I_R |  |  |  | CDC | 251 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C20R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | _200 | 200 |  | I_S | [17 empty] | 1-F9 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.11KV_200_A2 | 11KV 200 S相AMP | TIE | D15/11/200/I_S |  |  |  | CDC | 252 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C20R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 11 | 11kV | _200 | 200 |  | I_T | [17 empty] | 1-FA | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.11KV_200_A3 | 11KV 200 T相AMP | TIE | D15/11/200/I_T |  |  |  | CDC | 253 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | C20R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D15 | 新化DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MW | [17 empty] | 1-A9 | [5 empty] | MW_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | D15/11/310/KW |  |  |  | CDC | 254 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D15 | 新化DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVAR | [17 empty] | 1-AA | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | D15/11/310/KVAR |  |  |  | CDC | 255 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D15 | 新化DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_R | [17 empty] | 1-AB | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | D15/11/310/I_R |  |  |  | CDC | 256 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D15 | 新化DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_S | [17 empty] | 1-AC | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | D15/11/310/I_S |  |  |  | CDC | 257 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D15 | 新化DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_T | [17 empty] | 1-AD | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | D15/11/310/I_T |  |  |  | CDC | 258 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D15 | 新化DS | 0 |  | 1DTR | #1DTR |  | OilTemp | [17 empty] | 1-95 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.#1DTR_OIL | #1DTR 油溫 | MTR | D15//1DTR/OilTemp |  |  |  | CDC | 259 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D15 | 新化DS | 0 |  | 1DTR(A) | #1DTR(A) |  | CoilTemp | [17 empty] | 1-96 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | D15//1DTR(A)/CoilTemp |  |  |  | CDC | 260 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D15 | 新化DS | 0 |  | 1DTR(A) | #1DTR(A) |  | TapPosMv | [17 empty] | 1-98 |  | 1-61 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 新化DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | D15//1DTR(A)/TapPosMv |  |  |  | CDC | 261 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D15 | 新化DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MW | [17 empty] | 1-CC | [5 empty] | MW_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | D15/11/320/KW |  |  |  | CDC | 262 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D15 | 新化DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVAR | [17 empty] | 1-CD | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | D15/11/320/KVAR |  |  |  | CDC | 263 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D15 | 新化DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_R | [17 empty] | 1-CE | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | D15/11/320/I_R |  |  |  | CDC | 264 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D15 | 新化DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_S | [17 empty] | 1-CF | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | D15/11/320/I_S |  |  |  | CDC | 265 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D15 | 新化DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_T | [17 empty] | 1-D0 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | D15/11/320/I_T |  |  |  | CDC | 266 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D15 | 新化DS | 0 |  | 1DTR(B) | #1DTR(B) |  | CoilTemp | [17 empty] | 1-97 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | D15//1DTR(B)/CoilTemp |  |  |  | CDC | 267 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D15 | 新化DS | 0 |  | 1DTR(B) | #1DTR(B) |  | TapPosMv | [17 empty] | 1-99 |  | 1-63 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 新化DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | D15//1DTR(B)/TapPosMv |  |  |  | CDC | 268 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D15 | 新化DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MW | [17 empty] | 1-FB | [5 empty] | MW_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | D15/11/330/KW |  |  |  | CDC | 269 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D15 | 新化DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVAR | [17 empty] | 1-FC | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | D15/11/330/KVAR |  |  |  | CDC | 270 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D15 | 新化DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_R | [17 empty] | 1-FD | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | D15/11/330/I_R |  |  |  | CDC | 271 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D15 | 新化DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_S | [17 empty] | 1-FE | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | D15/11/330/I_S |  |  |  | CDC | 272 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D15 | 新化DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_T | [17 empty] | 1-FF | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | D15/11/330/I_T |  |  |  | CDC | 273 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D15 | 新化DS | 0 |  | 2DTR | #2DTR |  | OilTemp | [17 empty] | 1-9A | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.#2DTR_OIL | #2DTR 油溫 | MTR | D15//2DTR/OilTemp |  |  |  | CDC | 274 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D15 | 新化DS | 0 |  | 2DTR(A) | #2DTR(A) |  | CoilTemp | [17 empty] | 1-9B | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | D15//2DTR(A)/CoilTemp |  |  |  | CDC | 275 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D15 | 新化DS | 0 |  | 2DTR(A) | #2DTR(A) |  | TapPosMv | [17 empty] | 1-9D |  | 1-65 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 新化DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | D15//2DTR(A)/TapPosMv |  |  |  | CDC | 276 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D15 | 新化DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MW | [17 empty] | 1-E2 | [5 empty] | MW_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | D15/11/340/KW |  |  |  | CDC | 277 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D15 | 新化DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVAR | [17 empty] | 1-E3 | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | D15/11/340/KVAR |  |  |  | CDC | 278 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D15 | 新化DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_R | [17 empty] | 1-E4 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | D15/11/340/I_R |  |  |  | CDC | 279 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D15 | 新化DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_S | [17 empty] | 1-E5 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | D15/11/340/I_S |  |  |  | CDC | 280 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D15 | 新化DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_T | [17 empty] | 1-E6 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | D15/11/340/I_T |  |  |  | CDC | 281 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D15 | 新化DS | 0 |  | 2DTR(B) | #2DTR(B) |  | CoilTemp | [17 empty] | 1-9C | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | D15//2DTR(B)/CoilTemp |  |  |  | CDC | 282 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D15 | 新化DS | 0 |  | 2DTR(B) | #2DTR(B) |  | TapPosMv | [17 empty] | 1-9E |  | 1-67 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 新化DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | D15//2DTR(B)/TapPosMv |  |  |  | CDC | 283 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D15 | 新化DS | 0 |  | 1510_OF | 新化永資統實線 |  | R | [17 empty] | 1-A5 | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.1510_OF_R | 新化永資統實線 R相 油壓 | OTHER | D15/161/1510/OilPreR |  |  |  | CDC | 284 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D15 | 新化DS | 0 |  | 1510_OF | 新化永資統實線 |  | S | [17 empty] | 1-A6 | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.1510_OF_S | 新化永資統實線 S相 油壓 | OTHER | D15/161/1510/OilPreS |  |  |  | CDC | 285 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D15 | 新化DS | 0 |  | 1510_OF | 新化永資統實線 |  | T | [17 empty] | 1-A7 | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_S | [8 empty] | 新化DS.1510_OF_T | 新化永資統實線 T相 油壓 | OTHER | D15/161/1510/OilPreT |  |  |  | CDC | 286 | GENERICAIPoint | DS034_L1 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D15 | 新化DS | 161 | 161kV | 1510 | 統實永資線(1510) |  | GDA | [17 empty] | 1-03-00 | [7 empty] | 161KV_S | [8 empty] | 新化DS.1510_GDA | 統實永資線(1510) 接地RY | LINE161 | D15/161/1510/21NA |  |  |  | CDC | 287 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1510 | 統實永資線(1510) |  | 21A | [17 empty] | 1-02-07 | [7 empty] | 161KV_S | [8 empty] | 新化DS.1510_21A | 統實永資線(1510) 21RY | LINE161 | D15/161/1510/21A |  |  |  | CDC | 288 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1510 | 統實永資線(1510) |  | CB | [17 empty] | 1-02-04 |  | 1-05 | [5 empty] | 161KV_S | [8 empty] | 新化DS.1510_CB | 1510(統實永資線) CB | LINE161 | D15/161/1510/CB |  |  |  | CDC | 289 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 161 | 161kV | 1510 | 統實永資線(1510) |  | DS1 | 1511 | [16 empty] | 2-36-00 | 2-36-01 | 2-00 | [5 empty] | ADCS_S | [8 empty] | 新化DS.1511_DS | 1511(統實永資線) DS | LINE161 | D15/161/1510/DS1 |  |  |  | CDC | 290 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D15 | 新化DS | 161 | 161kV | 1510 | 統實永資線(1510) |  | DS2 | 1512 | [16 empty] | 2-36-02 | 2-36-03 | 2-01 | [5 empty] | ADCS_S | [8 empty] | 新化DS.1512_DS | 1512(統實永資線) DS | LINE161 | D15/161/1510/DS2 |  |  |  | CDC | 291 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D15 | 新化DS | 161 | 161kV | 1510 | 統實永資線(1510) |  | DS3 | 1513 | [16 empty] | 2-36-04 | 2-36-05 | 2-02 | [5 empty] | ADCS_S | [8 empty] | 新化DS.1513_DS | 1513(統實永資線) DS | LINE161 | D15/161/1510/DS3 |  |  |  | CDC | 292 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D15 | 新化DS | 161 | 161kV | 1510 | 統實永資線(1510) |  | E3 | 1513E | [16 empty] | 2-36-06 | 2-36-07 | 2-03 | [5 empty] | ADCS_S | [8 empty] | 新化DS.1513E_ES | 1513E(統實永資線) ES | LINE161 | D15/161/1510/ES3 |  |  |  | CDC | 293 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D15 | 新化DS | 161 | 161kV | 1710 | 山上一路(1710) |  | GDA | [17 empty] | 1-02-03 | [7 empty] | 161KV_S | [8 empty] | 新化DS.1710_GDA | 山上一路(1710) 接地RY | LINE161 | D15/161/1710/21NA |  |  |  | CDC | 294 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1710 | 山上一路(1710) |  | CB | [17 empty] | 1-01-07 |  | 1-04 | [5 empty] | 161KV_S | [8 empty] | 新化DS.1710_CB | 1710(山上一路) CB | LINE161 | D15/161/1710/CB |  |  |  | CDC | 295 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 161 | 161kV | 1710 | 山上一路(1710) |  | 79UL | [17 empty] | 1-31-05 |  | 1-53 | [5 empty] | ADCS_S | [8 empty] | 新化DS.1710_79UL | 山上一路(1710) 79RY U/L | LINE161 | D15/161/1710/79UL |  |  |  | CDC | 296 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D15 | 新化DS | 161 | 161kV | 1710 | 山上一路(1710) |  | DS1 | 1711 | [16 empty] | 1-35-08 | 1-35-09 | 1-7C | [5 empty] | ADCS_S | [8 empty] | 新化DS.1711_DS | 1711(山上一路) DS | LINE161 | D15/161/1710/DS1 |  |  |  | CDC | 297 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D15 | 新化DS | 161 | 161kV | 1710 | 山上一路(1710) |  | DS2 | 1712 | [16 empty] | 1-35-10 | 1-35-11 | 1-7D | [5 empty] | ADCS_S | [8 empty] | 新化DS.1712_DS | 1712(山上一路) DS | LINE161 | D15/161/1710/DS2 |  |  |  | CDC | 298 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D15 | 新化DS | 161 | 161kV | 1710 | 山上一路(1710) |  | DS3 | 1713 | [16 empty] | 1-35-12 | 1-35-13 | 1-7E | [5 empty] | ADCS_S | [8 empty] | 新化DS.1713_DS | 1713(山上一路) DS | LINE161 | D15/161/1710/DS3 |  |  |  | CDC | 299 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D15 | 新化DS | 161 | 161kV | 1710 | 山上一路(1710) |  | E3 | 1713E | [16 empty] | 1-35-14 | 1-35-15 | 1-7F | [5 empty] | ADCS_S | [8 empty] | 新化DS.1713E_ES | 1713E(山上一路) ES | LINE161 | D15/161/1710/ES3 |  |  |  | CDC | 300 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D15 | 新化DS | 161 | 161kV | 1720 | 山上二路(1720) |  | GDA | [17 empty] | 1-01-06 | [7 empty] | 161KV_S | [8 empty] | 新化DS.1720_GDA | 山上二路(1720) 接地RY | LINE161 | D15/161/1720/21NA |  |  |  | CDC | 301 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1720 | 山上二路(1720) |  | CB | [17 empty] | 1-01-02 |  | 1-03 | [5 empty] | 161KV_S | [8 empty] | 新化DS.1720_CB | 1720(山上二路) CB | LINE161 | D15/161/1720/CB |  |  |  | CDC | 302 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 161 | 161kV | 1720 | 山上二路(1720) |  | 79UL | [17 empty] | 1-31-04 |  | 1-52 | [5 empty] | ADCS_S | [8 empty] | 新化DS.1720_79UL | 山上二路(1720) 79RY U/L | LINE161 | D15/161/1720/79UL |  |  |  | CDC | 303 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D15 | 新化DS | 161 | 161kV | 1720 | 山上二路(1720) |  | DS1 | 1721 | [16 empty] | 1-35-00 | 1-35-01 | 1-78 | [5 empty] | ADCS_S | [8 empty] | 新化DS.1721_DS | 1721(山上二路) DS | LINE161 | D15/161/1720/DS1 |  |  |  | CDC | 304 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D15 | 新化DS | 161 | 161kV | 1720 | 山上二路(1720) |  | DS2 | 1722 | [16 empty] | 1-35-02 | 1-35-03 | 1-79 | [5 empty] | ADCS_S | [8 empty] | 新化DS.1722_DS | 1722(山上二路) DS | LINE161 | D15/161/1720/DS2 |  |  |  | CDC | 305 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D15 | 新化DS | 161 | 161kV | 1720 | 山上二路(1720) |  | DS3 | 1723 | [16 empty] | 1-35-04 | 1-35-05 | 1-7A | [5 empty] | ADCS_S | [8 empty] | 新化DS.1723_DS | 1723(山上二路) DS | LINE161 | D15/161/1720/DS3 |  |  |  | CDC | 306 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D15 | 新化DS | 161 | 161kV | 1720 | 山上二路(1720) |  | E3 | 1723E | [16 empty] | 1-35-06 | 1-35-07 | 1-7B | [5 empty] | ADCS_S | [8 empty] | 新化DS.1723E_ES | 1723E(山上二路) ES | LINE161 | D15/161/1720/ES3 |  |  |  | CDC | 307 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D15 | 新化DS | 161 | 161kV | 1740 | 道爺安南新化線(1740) |  | GDA | [17 empty] | 1-00-04 | [7 empty] | 161KV_S | [8 empty] | 新化DS.1740_GDA | 道爺安南新化線(1740) 接地RY | LINE161 | D15/161/1740/GDA |  |  |  | CDC | 308 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1740 | 道爺安南新化線(1740) |  | CB | [17 empty] | 1-00-00 |  | 1-01 | [5 empty] | 161KV_S | [8 empty] | 新化DS.1740_CB | 1740(道爺安南新化線) CB | LINE161 | D15/161/1740/CB |  |  |  | CDC | 309 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 161 | 161kV | 1740 | 道爺安南新化線(1740) |  | 79UL | [17 empty] | 1-31-02 |  | 1-50 | [5 empty] | ADCS_S | [8 empty] | 新化DS.1740_79UL | 道爺安南新化線(1740) 79RY U/L | LINE161 | D15/161/1740/79UL |  |  |  | CDC | 310 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D15 | 新化DS | 161 | 161kV | 1740 | 道爺安南新化線(1740) |  | DS1 | 1741 | [16 empty] | 1-34-00 | 1-34-01 | 1-70 | [5 empty] | ADCS_S | [8 empty] | 新化DS.1741_DS | 1741(道爺安南新化線) DS | LINE161 | D15/161/1740/DS1 |  |  |  | CDC | 311 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D15 | 新化DS | 161 | 161kV | 1740 | 道爺安南新化線(1740) |  | DS2 | 1742 | [16 empty] | 1-34-02 | 1-34-03 | 1-71 | [5 empty] | ADCS_S | [8 empty] | 新化DS.1742_DS | 1742(道爺安南新化線) DS | LINE161 | D15/161/1740/DS2 |  |  |  | CDC | 312 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D15 | 新化DS | 161 | 161kV | 1740 | 道爺安南新化線(1740) |  | DS3 | 1743 | [16 empty] | 1-34-04 | 1-34-05 | 1-72 | [5 empty] | ADCS_S | [8 empty] | 新化DS.1743_DS | 1743(道爺安南新化線) DS | LINE161 | D15/161/1740/DS3 |  |  |  | CDC | 313 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D15 | 新化DS | 161 | 161kV | 1740 | 道爺安南新化線(1740) |  | E3 | 1743E | [16 empty] | 1-34-06 | 1-34-07 | 1-73 | [5 empty] | ADCS_S | [8 empty] | 新化DS.1743E_ES | 1743E(道爺安南新化線) ES | LINE161 | D15/161/1740/ES3 |  |  |  | CDC | 314 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D15 | 新化DS | 11 | 11kV | KY21 | 新21線(KY21) |  | PHA | [17 empty] | 1-10-01 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY21_PHA | 11KV新21線(KY21) 相間RY | FEEDER | D15/11/KY21/51A |  |  |  | CDC | 315 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY21 | 新21線(KY21) |  | GDA | [17 empty] | 1-10-02 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY21_GDA | 11KV新21線(KY21) 接地RY | FEEDER | D15/11/KY21/51NA |  |  |  | CDC | 316 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY21 | 新21線(KY21) 79RY |  | 79UL | [17 empty] | 2-30-10 |  | 2-20 | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY21_79UL | 11KV新21線(KY21) 79RY U/L | FEEDER | D15/11/KY21/79UL |  |  |  | CDC | 317 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY21 | 新21線(KY21) LCO分流器 |  | ADJ | [17 empty] | 2-34-12 |  | 2-08 | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY21_ADJ | 11KV新21線(KY21) LCO分流器 U/L | FEEDER | D15/11/KY21/ADJ |  |  |  | CDC | 318 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY21 | KY21(11KV新21線) |  | CB | [17 empty] | 1-10-00 |  | 1-13 | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY21_CB | KY21(11KV新21線) CB | FEEDER | D15/11/KY21/CB |  |  |  | CDC | 319 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY22 | 新22線(KY22) |  | PHA | [17 empty] | 1-10-04 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY22_PHA | 11KV新22線(KY22) 相間RY | FEEDER | D15/11/KY22/51A |  |  |  | CDC | 320 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY22 | 新22線(KY22) |  | GDA | [17 empty] | 1-10-05 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY22_GDA | 11KV新22線(KY22) 接地RY | FEEDER | D15/11/KY22/51NA |  |  |  | CDC | 321 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY22 | 新22線(KY22) 79RY |  | 79UL | [17 empty] | 2-30-11 |  | 2-21 | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY22_79UL | 11KV新22線(KY22) 79RY U/L | FEEDER | D15/11/KY22/79UL |  |  |  | CDC | 322 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY22 | 新22線(KY22) LCO分流器 |  | ADJ | [17 empty] | 2-34-13 |  | 2-09 | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY22_ADJ | 11KV新22線(KY22) LCO分流器 U/L | FEEDER | D15/11/KY22/ADJ |  |  |  | CDC | 323 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY22 | KY22(11KV新22線) |  | CB | [17 empty] | 1-10-03 |  | 1-14 | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY22_CB | KY22(11KV新22線) CB | FEEDER | D15/11/KY22/CB |  |  |  | CDC | 324 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY23 | 新23線(KY23) |  | PHA | [17 empty] | 1-10-07 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY23_PHA | 11KV新23線(KY23) 相間RY | FEEDER | D15/11/KY23/51A |  |  |  | CDC | 325 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY23 | 新23線(KY23) |  | GDA | [17 empty] | 1-11-00 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY23_GDA | 11KV新23線(KY23) 接地RY | FEEDER | D15/11/KY23/51NA |  |  |  | CDC | 326 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY23 | 新23線(KY23) 79RY |  | 79UL | [17 empty] | 2-30-12 |  | 2-22 | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY23_79UL | 11KV新23線(KY23) 79RY U/L | FEEDER | D15/11/KY23/79UL |  |  |  | CDC | 327 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY23 | 新23線(KY23) LCO分流器 |  | ADJ | [17 empty] | 2-34-14 |  | 2-0A | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY23_ADJ | 11KV新23線(KY23) LCO分流器 U/L | FEEDER | D15/11/KY23/ADJ |  |  |  | CDC | 328 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY23 | KY23(11KV新23線) |  | CB | [17 empty] | 1-10-06 |  | 1-15 | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY23_CB | KY23(11KV新23線) CB | FEEDER | D15/11/KY23/CB |  |  |  | CDC | 329 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY24 | 新24線(KY24) |  | PHA | [17 empty] | 1-11-02 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY24_PHA | 11KV新24線(KY24) 相間RY | FEEDER | D15/11/KY24/51A |  |  |  | CDC | 330 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY24 | 新24線(KY24) |  | GDA | [17 empty] | 1-11-03 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY24_GDA | 11KV新24線(KY24) 接地RY | FEEDER | D15/11/KY24/51NA |  |  |  | CDC | 331 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY24 | 新24線(KY24) 79RY |  | 79UL | [17 empty] | 2-30-13 |  | 2-23 | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY24_79UL | 11KV新24線(KY24) 79RY U/L | FEEDER | D15/11/KY24/79UL |  |  |  | CDC | 332 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY24 | 新24線(KY24) LCO分流器 |  | ADJ | [17 empty] | 2-34-15 |  | 2-0B | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY24_ADJ | 11KV新24線(KY24) LCO分流器 U/L | FEEDER | D15/11/KY24/ADJ |  |  |  | CDC | 333 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY24 | KY24(11KV新24線) |  | CB | [17 empty] | 1-11-01 |  | 1-16 | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY24_CB | KY24(11KV新24線) CB | FEEDER | D15/11/KY24/CB |  |  |  | CDC | 334 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY25 | 新25線(KY25) |  | PHA | [17 empty] | 1-11-05 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY25_PHA | 11KV新25線(KY25) 相間RY | FEEDER | D15/11/KY25/51A |  |  |  | CDC | 335 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY25 | 新25線(KY25) |  | GDA | [17 empty] | 1-11-06 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY25_GDA | 11KV新25線(KY25) 接地RY | FEEDER | D15/11/KY25/51NA |  |  |  | CDC | 336 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY25 | 新25線(KY25) 79RY |  | 79UL | [17 empty] | 2-30-14 |  | 2-24 | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY25_79UL | 11KV新25線(KY25) 79RY U/L | FEEDER | D15/11/KY25/79UL |  |  |  | CDC | 337 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY25 | 新25線(KY25) LCO分流器 |  | ADJ | [17 empty] | 2-35-00 |  | 2-0C | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY25_ADJ | 11KV新25線(KY25) LCO分流器 U/L | FEEDER | D15/11/KY25/ADJ |  |  |  | CDC | 338 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY25 | KY25(11KV新25線) |  | CB | [17 empty] | 1-11-04 |  | 1-17 | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY25_CB | KY25(11KV新25線) CB | FEEDER | D15/11/KY25/CB |  |  |  | CDC | 339 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY31 | 新31線(KY31) |  | PHA | [17 empty] | 1-17-05 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY31_PHA | 11KV新31線(KY31) 相間RY | FEEDER | D15/11/KY31/51A |  |  |  | CDC | 340 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY31 | 新31線(KY31) |  | GDA | [17 empty] | 1-17-06 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY31_GDA | 11KV新31線(KY31) 接地RY | FEEDER | D15/11/KY31/51NA |  |  |  | CDC | 341 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY31 | 新31線(KY31) 79RY |  | 79UL | [17 empty] | 2-31-12 |  | 2-32 | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY31_79UL | 11KV新31線(KY31) 79RY U/L | FEEDER | D15/11/KY31/79UL |  |  |  | CDC | 342 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY31 | 新31線(KY31) LCO分流器 |  | ADJ | [17 empty] | 2-35-10 |  | 2-1E | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY31_ADJ | 11KV新31線(KY31) LCO分流器 U/L | FEEDER | D15/11/KY31/ADJ |  |  |  | CDC | 343 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY31 | KY31(11KV新31線) |  | CB | [17 empty] | 1-17-04 |  | 1-2A | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY31_CB | KY31(11KV新31線) CB | FEEDER | D15/11/KY31/CB |  |  |  | CDC | 344 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY32 | 新32線(KY32) |  | PHA | [17 empty] | 1-18-00 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY32_PHA | 11KV新32線(KY32) 相間RY | FEEDER | D15/11/KY32/51A |  |  |  | CDC | 345 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY32 | 新32線(KY32) |  | GDA | [17 empty] | 1-18-01 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY32_GDA | 11KV新32線(KY32) 接地RY | FEEDER | D15/11/KY32/51NA |  |  |  | CDC | 346 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY32 | 新32線(KY32) 79RY |  | 79UL | [17 empty] | 2-31-13 |  | 2-33 | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY32_79UL | 11KV新32線(KY32) 79RY U/L | FEEDER | D15/11/KY32/79UL |  |  |  | CDC | 347 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY32 | 新32線(KY32) LCO分流器 |  | ADJ | [17 empty] | 2-35-11 |  | 2-1F | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY32_ADJ | 11KV新32線(KY32) LCO分流器 U/L | FEEDER | D15/11/KY32/ADJ |  |  |  | CDC | 348 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY32 | KY32(11KV新32線) |  | CB | [17 empty] | 1-17-07 |  | 1-2B | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY32_CB | KY32(11KV新32線) CB | FEEDER | D15/11/KY32/CB |  |  |  | CDC | 349 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY33 | 新33線(KY33) |  | PHA | [17 empty] | 1-18-03 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY33_PHA | 11KV新33線(KY33) 相間RY | FEEDER | D15/11/KY33/51A |  |  |  | CDC | 350 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY33 | 新33線(KY33) |  | GDA | [17 empty] | 1-18-04 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY33_GDA | 11KV新33線(KY33) 接地RY | FEEDER | D15/11/KY33/51NA |  |  |  | CDC | 351 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY33 | 新33線(KY33) 79RY |  | 79UL | [17 empty] | 2-31-14 |  | 2-34 | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY33_79UL | 11KV新33線(KY33) 79RY U/L | FEEDER | D15/11/KY33/79UL |  |  |  | CDC | 352 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY33 | 新33線(KY33) LCO分流器 |  | ADJ | [17 empty] | 2-35-12 |  | 2-3A | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY33_ADJ | 11KV新33線(KY33) LCO分流器 U/L | FEEDER | D15/11/KY33/ADJ |  |  |  | CDC | 353 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY33 | KY33(11KV新33線) |  | CB | [17 empty] | 1-18-02 |  | 1-2C | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY33_CB | KY33(11KV新33線) CB | FEEDER | D15/11/KY33/CB |  |  |  | CDC | 354 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY34 | 新34線(KY34) |  | PHA | [17 empty] | 1-18-06 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY34_PHA | 11KV新34線(KY34) 相間RY | FEEDER | D15/11/KY34/51A |  |  |  | CDC | 355 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY34 | 新34線(KY34) |  | GDA | [17 empty] | 1-18-07 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY34_GDA | 11KV新34線(KY34) 接地RY | FEEDER | D15/11/KY34/51NA |  |  |  | CDC | 356 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY34 | 新34線(KY34) 79RY |  | 79UL | [17 empty] | 2-31-15 |  | 2-35 | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY34_79UL | 11KV新34線(KY34) 79RY U/L | FEEDER | D15/11/KY34/79UL |  |  |  | CDC | 357 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY34 | 新34線(KY34) LCO分流器 |  | ADJ | [17 empty] | 2-35-13 |  | 2-3B | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY34_ADJ | 11KV新34線(KY34) LCO分流器 U/L | FEEDER | D15/11/KY34/ADJ |  |  |  | CDC | 358 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY34 | KY34(11KV新34線) |  | CB | [17 empty] | 1-18-05 |  | 1-2D | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY34_CB | KY34(11KV新34線) CB | FEEDER | D15/11/KY34/CB |  |  |  | CDC | 359 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY35 | 新35線(KY35) |  | PHA | [17 empty] | 1-19-01 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY35_PHA | 11KV新35線(KY35) 相間RY | FEEDER | D15/11/KY35/51A |  |  |  | CDC | 360 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY35 | 新35線(KY35) |  | GDA | [17 empty] | 1-19-02 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY35_GDA | 11KV新35線(KY35) 接地RY | FEEDER | D15/11/KY35/51NA |  |  |  | CDC | 361 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY35 | 新35線(KY35) 79RY |  | 79UL | [17 empty] | 2-32-00 |  | 2-36 | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY35_79UL | 11KV新35線(KY35) 79RY U/L | FEEDER | D15/11/KY35/79UL |  |  |  | CDC | 362 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY35 | 新35線(KY35) LCO分流器 |  | ADJ | [17 empty] | 2-35-14 |  | 2-3C | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY35_ADJ | 11KV新35線(KY35) LCO分流器 U/L | FEEDER | D15/11/KY35/ADJ |  |  |  | CDC | 363 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY35 | KY35(11KV新35線) |  | CB | [17 empty] | 1-19-00 |  | 1-2E | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY35_CB | KY35(11KV新35線) CB | FEEDER | D15/11/KY35/CB |  |  |  | CDC | 364 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY36 | 新36線(KY36) |  | PHA | [17 empty] | 1-19-04 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY36_PHA | 11KV新36線(KY36) 相間RY | FEEDER | D15/11/KY36/51A |  |  |  | CDC | 365 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY36 | 新36線(KY36) |  | GDA | [17 empty] | 1-19-05 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY36_GDA | 11KV新36線(KY36) 接地RY | FEEDER | D15/11/KY36/51NA |  |  |  | CDC | 366 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY36 | 新36線(KY36) 79RY |  | 79UL | [17 empty] | 2-32-01 |  | 2-37 | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY36_79UL | 11KV新36線(KY36) 79RY U/L | FEEDER | D15/11/KY36/79UL |  |  |  | CDC | 367 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY36 | 新36線(KY36) LCO分流器 |  | ADJ | [17 empty] | 2-35-15 |  | 2-3D | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY36_ADJ | 11KV新36線(KY36) LCO分流器 U/L | FEEDER | D15/11/KY36/ADJ |  |  |  | CDC | 368 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY36 | KY36(11KV新36線) |  | CB | [17 empty] | 1-19-03 |  | 1-2F | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY36_CB | KY36(11KV新36線) CB | FEEDER | D15/11/KY36/CB |  |  |  | CDC | 369 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [17 empty] | 1-05-00 |  | 1-09 | [5 empty] | 161KV_S | [8 empty] | 新化DS.1500_CB | 1500(TIE) CB | TIE | D15/161/1500/CB |  |  |  | CDC | 370 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | 1500 | TIE(1500) |  | 50A | [17 empty] | 1-05-01 | [7 empty] | 161KV_S | [8 empty] | 新化DS.1500_50A | 161KV TIE(1500) 50RY | TIE | D15/161/1500/50A |  |  |  | CDC | 371 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [16 empty] | 2-38-00 | 2-38-01 | 2-10 | [5 empty] | ADCS_S | [8 empty] | 新化DS.1501_DS | 1501(TIE) DS | TIE | D15/161/1500/DS1 |  |  |  | CDC | 372 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D15 | 新化DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [16 empty] | 2-38-02 | 2-38-03 | 2-11 | [5 empty] | ADCS_S | [8 empty] | 新化DS.1502_DS | 1502(TIE) DS | TIE | D15/161/1500/DS2 |  |  |  | CDC | 373 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D15 | 新化DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB | [17 empty] | 1-05-05 |  | 1-0A | [5 empty] | 161KV_S | [8 empty] | 新化DS.1750_CB | 1750(#1DTR) CB | MTR | D15/161/1750/CB |  |  |  | CDC | 374 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | 310 | #1DTR(310) |  | CB | [17 empty] | 1-06-03 |  | 1-10 | [5 empty] | ADCS_S | [8 empty] | 新化DS.310_CB | 310(#1DTR) CB | MTR | D15/11/310/CB |  |  |  | CDC | 375 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | 320 | #1DTR(320) |  | CB | [17 empty] | 1-07-05 |  | 1-20 | [5 empty] | ADCS_S | [8 empty] | 新化DS.320_CB | 320(#1DTR) CB | MTR | D15/11/320/CB |  |  |  | CDC | 376 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | 310 | #1DTR(310) |  | 51A | [17 empty] | 1-06-04 | [7 empty] | ADCS_S | [8 empty] | 新化DS.310_51A | #1DTR二次側(310) 51RY | MTR | D15/11/310/51A |  |  |  | CDC | 377 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 320 | #1DTR(320) |  | 51A | [17 empty] | 1-07-06 | [7 empty] | ADCS_S | [8 empty] | 新化DS.320_51A | #1DTR二次側(320) 51RY | MTR | D15/11/320/51A |  |  |  | CDC | 378 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 | [16 empty] | 2-38-04 | 2-38-05 | 2-12 | [5 empty] | ADCS_S | [8 empty] | 新化DS.1751_DS | 1751(#1DTR) DS | MTR | D15/161/1750/DS1 |  |  |  | CDC | 379 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D15 | 新化DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 | [16 empty] | 2-38-06 | 2-38-07 | 2-13 | [5 empty] | ADCS_S | [8 empty] | 新化DS.1752_DS | 1752(#1DTR) DS | MTR | D15/161/1750/DS2 |  |  |  | CDC | 380 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D15 | 新化DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB | [17 empty] | 1-06-07 |  | 1-0B | [5 empty] | 161KV_S | [8 empty] | 新化DS.1760_CB | 1760(#2DTR) CB | MTR | D15/161/1760/CB |  |  |  | CDC | 381 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | 330 | #2DTR(330) |  | CB | [17 empty] | 1-08-07 |  | 1-31 | [5 empty] | ADCS_S | [8 empty] | 新化DS.330_CB | 330(#2DTR) CB | MTR | D15/11/330/CB |  |  |  | CDC | 382 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | 340 | #2DTR(340) |  | CB | [17 empty] | 1-07-07 |  | 1-21 | [5 empty] | ADCS_S | [8 empty] | 新化DS.340_CB | 340(#2DTR) CB | MTR | D15/11/340/CB |  |  |  | CDC | 383 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | 330 | #2DTR(330) |  | 51A | [17 empty] | 1-09-00 | [7 empty] | ADCS_S | [8 empty] | 新化DS.330_51A | #2DTR二次側(330) 51RY | MTR | D15/11/330/51A |  |  |  | CDC | 384 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 340 | #2DTR(340) |  | 51A | [17 empty] | 1-08-00 | [7 empty] | ADCS_S | [8 empty] | 新化DS.340_51A | #2DTR二次側(340) 51RY | MTR | D15/11/340/51A |  |  |  | CDC | 385 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 | [16 empty] | 2-38-08 | 2-38-09 | 2-14 | [5 empty] | ADCS_S | [8 empty] | 新化DS.1761_DS | 1761(#2DTR) DS | MTR | D15/161/1760/DS1 |  |  |  | CDC | 386 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D15 | 新化DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 | [16 empty] | 2-38-10 | 2-38-11 | 2-15 | [5 empty] | ADCS_S | [8 empty] | 新化DS.1762_DS | 1762(#2DTR) DS | MTR | D15/161/1760/DS2 |  |  |  | CDC | 387 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D15 | 新化DS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-12-02 |  | 1-12 | [5 empty] | ADCS_S | [8 empty] | 新化DS.210_CB | 210(11KV #1SC) CB | SC | D15/11/210/CB |  |  |  | CDC | 388 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M | [17 empty] | 2-31-00 |  | 2-26 | [5 empty] | ADCS_S | [8 empty] | 新化DS.210_A/M | 11KV #1SC 乏控器 A/M | SC | D15/11/210/SC_A_M |  |  |  | CDC | 389 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D15 | 新化DS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-12-03 | [7 empty] | ADCS_S | [8 empty] | 新化DS.210_SCA | 11KV #1SC 51,51N RY | SC | D15/11/210/SCA |  |  |  | CDC | 390 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-12-04 | [7 empty] | ADCS_S | [8 empty] | 新化DS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | D15/11/210/UVA |  |  |  | CDC | 391 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 1-12-05 |  | 1-19 | [5 empty] | ADCS_S | [8 empty] | 新化DS.220_CB | 220(11KV #2SC) CB | SC | D15/11/220/CB |  |  |  | CDC | 392 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M | [17 empty] | 2-31-01 |  | 2-27 | [5 empty] | ADCS_S | [8 empty] | 新化DS.220_A/M | 11KV #2SC 乏控器 A/M | SC | D15/11/220/SC_A_M |  |  |  | CDC | 393 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D15 | 新化DS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 1-12-06 | [7 empty] | ADCS_S | [8 empty] | 新化DS.220_SCA | 11KV #2SC 51,51N RY | SC | D15/11/220/SCA |  |  |  | CDC | 394 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 1-12-07 | [7 empty] | ADCS_S | [8 empty] | 新化DS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | D15/11/220/UVA |  |  |  | CDC | 395 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | 230 | #3SC(230) |  | CB | [17 empty] | 1-14-07 |  | 1-1F | [5 empty] | ADCS_S | [8 empty] | 新化DS.230_CB | 230(11KV #3SC) CB | SC | D15/11/230/CB |  |  |  | CDC | 396 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | 230 | #3SC(230) |  | SC_A_M | [17 empty] | 2-31-06 |  | 2-2C | [5 empty] | ADCS_S | [8 empty] | 新化DS.230_A/M | 11KV #3SC 乏控器 A/M | SC | D15/11/230/SC_A_M |  |  |  | CDC | 397 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D15 | 新化DS | 11 | 11kV | 230 | #3SC(230) |  | SCA | [17 empty] | 1-15-00 | [7 empty] | ADCS_S | [8 empty] | 新化DS.230_SCA | 11KV #3SC 51,51N RY | SC | D15/11/230/SCA |  |  |  | CDC | 398 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | 230 | #3SC(230) |  | UVA | [17 empty] | 1-15-01 | [7 empty] | ADCS_S | [8 empty] | 新化DS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | D15/11/230/UVA |  |  |  | CDC | 399 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | 240 | #4SC(240) |  | CB | [17 empty] | 1-1A-01 |  | 1-30 | [5 empty] | ADCS_S | [8 empty] | 新化DS.240_CB | 240(11KV #4SC) CB | SC | D15/11/240/CB |  |  |  | CDC | 400 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | 240 | #4SC(240) |  | SC_A_M | [17 empty] | 2-32-03 |  | 2-39 | [5 empty] | ADCS_S | [8 empty] | 新化DS.240_A/M | 11KV #4SC 乏控器 A/M | SC | D15/11/240/SC_A_M |  |  |  | CDC | 401 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D15 | 新化DS | 11 | 11kV | 240 | #4SC(240) |  | SCA | [17 empty] | 1-1A-02 | [7 empty] | ADCS_S | [8 empty] | 新化DS.240_SCA | 11KV #4SC 51,51N RY | SC | D15/11/240/SCA |  |  |  | CDC | 402 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | 240 | #4SC(240) |  | UVA | [17 empty] | 1-1A-03 | [7 empty] | ADCS_S | [8 empty] | 新化DS.240_UVA | 11KV #4SC 27RY(欠壓) | SC | D15/11/240/UVA |  |  |  | CDC | 403 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | 250 | #5SC(250) |  | CB | [17 empty] | 1-19-06 |  | 1-28 | [5 empty] | ADCS_S | [8 empty] | 新化DS.250_CB | 250(11KV #5SC) CB | SC | D15/11/250/CB |  |  |  | CDC | 404 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | 250 | #5SC(250) |  | SC_A_M | [17 empty] | 2-32-02 |  | 2-38 | [5 empty] | ADCS_S | [8 empty] | 新化DS.250_A/M | 11KV #5SC 乏控器 A/M | SC | D15/11/250/SC_A_M |  |  |  | CDC | 405 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D15 | 新化DS | 11 | 11kV | 250 | #5SC(250) |  | SCA | [17 empty] | 1-19-07 | [7 empty] | ADCS_S | [8 empty] | 新化DS.250_SCA | 11KV #5SC 51,51N RY | SC | D15/11/250/SCA |  |  |  | CDC | 406 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | 250 | #5SC(250) |  | UVA | [17 empty] | 1-1A-00 | [7 empty] | ADCS_S | [8 empty] | 新化DS.250_UVA | 11KV #5SC 27RY(欠壓) | SC | D15/11/250/UVA |  |  |  | CDC | 407 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | 260 | #6SC(260) |  | CB | [17 empty] | 1-16-06 |  | 1-22 | [5 empty] | ADCS_S | [8 empty] | 新化DS.260_CB | 260(11KV #6SC) CB | SC | D15/11/260/CB |  |  |  | CDC | 408 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | 260 | #6SC(260) |  | SC_A_M | [17 empty] | 2-31-11 |  | 2-31 | [5 empty] | ADCS_S | [8 empty] | 新化DS.260_A/M | 11KV #6SC 乏控器 A/M | SC | D15/11/260/SC_A_M |  |  |  | CDC | 409 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D15 | 新化DS | 11 | 11kV | 260 | #6SC(260) |  | SCA | [17 empty] | 1-16-07 | [7 empty] | ADCS_S | [8 empty] | 新化DS.260_SCA | 11KV #6SC 51,51N RY | SC | D15/11/260/SCA |  |  |  | CDC | 410 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | 260 | #6SC(260) |  | UVA | [17 empty] | 1-17-00 | [7 empty] | ADCS_S | [8 empty] | 新化DS.260_UVA | 11KV #6SC 27RY(欠壓) | SC | D15/11/260/UVA |  |  |  | CDC | 411 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1611BUS | #1BUS |  | VUA | [17 empty] | 2-33-09 | [7 empty] | ADCS_S | [8 empty] | 新化DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | D15/161/1BUS/UVA |  |  |  | CDC | 412 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1611BUS | #1BUS |  | 87A | [17 empty] | 1-05-02 | [7 empty] | 161KV_S | [8 empty] | 新化DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | D15/161/1BUS/87A |  |  |  | CDC | 413 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1611BUS | #1BUS |  | 87UL | [17 empty] | 1-32-08 |  | 1-07 | [5 empty] | ADCS_S | [8 empty] | 新化DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | D15/161/1BUS/87UL |  |  |  | CDC | 414 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D15 | 新化DS | 161 | 161kV | 1612BUS | #2BUS |  | VUA | [17 empty] | 2-33-10 | [7 empty] | ADCS_S | [8 empty] | 新化DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | D15/161/2BUS/UVA |  |  |  | CDC | 415 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1612BUS | #2BUS |  | 87A | [17 empty] | 1-05-03 | [7 empty] | 161KV_S | [8 empty] | 新化DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | D15/161/2BUS/87A |  |  |  | CDC | 416 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1612BUS | #2BUS |  | 87UL | [17 empty] | 1-32-09 |  | 1-08 | [5 empty] | ADCS_S | [8 empty] | 新化DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | D15/161/2BUS/87UL |  |  |  | CDC | 417 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D15 | 新化DS | 22 | 22kV | 11_ | 11/ |  | CBA | [17 empty] | 2-34-02 | [7 empty] | ADCS_S | [8 empty] | 新化DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | D15/11/ComPoint/CBA |  |  |  | CDC | 418 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D15 | 新化DS | 22 | 22kV | 11_ | 11/ |  | CBF | [17 empty] | 2-34-03 | [7 empty] | ADCS_S | [8 empty] | 新化DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | D15/11/ComPoint/CBF |  |  |  | CDC | 419 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | _SC | sc |  | 60A | [17 empty] | 1-30-14 | [7 empty] | ADCS_S | [8 empty] | 新化DS.11KV_SC_60A | 11KV sc 60A | OTHER | D15/0/ComPoint/FDR_60A |  |  |  | CDC | 420 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV |  |  |  | CBA | [17 empty] | 2-34-00 | [7 empty] | ADCS_S | [8 empty] | 新化DS.161KV_CBA | 161KV斷路器重故障 | OTHER | D15/161/ComPoint/CBA |  |  |  | CDC | 421 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV |  |  |  | CBF | [17 empty] | 2-34-01 | [7 empty] | ADCS_S | [8 empty] | 新化DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | D15/161/ComPoint/CBF |  |  |  | CDC | 422 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | LINE | LINE |  | RCA | [17 empty] | 1-09-02 | [7 empty] | ADCS_S | [8 empty] | 新化DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | D15/0/ComPoint/RCA |  |  |  | CDC | 423 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV |  |  |  | COMT | [17 empty] | 2-33-15 | [7 empty] | ADCS_S | [8 empty] | 新化DS.161空壓機COMT | 161KV空壓機運轉超時警報 | OTHER | D15/0/ComPoint/COMT |  |  |  | CDC | 424 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  |  |  |  | OSCA | [17 empty] | 1-09-01 | [7 empty] | ADCS_S | [8 empty] | 新化DS.OSC啟動 | 示波器啟動警報 | OTHER | D15/161/ComPoint/OSCA |  |  |  | CDC | 425 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | ADCS_S | [8 empty] | 新化DS.RTU_S/L | RTU SUPY/LOCAL | OTHER | D15/0/RTU/RTU_R_L |  |  |  | CDC | 426 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D15 | 新化DS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | ADCS_S | [8 empty] | 新化DS.TEST_CB | TEST CB | OTHER | D15/0/RTU/Test_CB |  |  |  | CDC | 427 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  |  |  |  | Fire1 | [17 empty] | 2-32-10 | [7 empty] | ADCS_S | [8 empty] | 新化DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | D15/0/StaDev/Fire1 |  |  |  | CDC | 428 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  |  |  |  | Fire2 | [17 empty] | 2-32-11 | [7 empty] | ADCS_S | [8 empty] | 新化DS.火災警報(2) | 火災警報(2) | OTHER | D15/0/StaDev/Fire2 |  |  |  | CDC | 429 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  |  |  |  | Fire3 | [17 empty] | 2-32-12 | [7 empty] | ADCS_S | [8 empty] | 新化DS.火災警報(3) | 火災警報(3) | OTHER | D15/0/StaDev/Fire3 |  |  |  | CDC | 430 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  |  |  |  | OPA | [17 empty] | 2-33-05 | [7 empty] | ADCS_S | [8 empty] | 新化DS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | D15/0/ComPoint/OPA |  |  |  | CDC | 431 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  |  |  |  | SUBA | [17 empty] | 2-34-06 | [7 empty] | ADCS_S | [8 empty] | 新化DS.其他重故障 | 變電所內其他重故障 | OTHER | D15/0/StaDev/PSA |  |  |  | CDC | 432 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D15 | 新化DS | 0 |  |  |  |  | SUBF | [17 empty] | 2-34-05 | [7 empty] | ADCS_S | [8 empty] | 新化DS.其他輕故障 | 變電所內其他輕故障 | OTHER | D15/0/StaDev/PSF |  |  |  | CDC | 433 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D15 | 新化DS | 0 |  |  |  |  | ACB1 | [17 empty] | 2-33-06 | [7 empty] | ADCS_S | [8 empty] | 新化DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | D15/0/StaDev/ACB1 |  |  |  | CDC | 434 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
D15 | 新化DS | 0 |  |  |  |  | ACB2 | [17 empty] | 2-33-07 | [7 empty] | ADCS_S | [8 empty] | 新化DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | D15/0/StaDev/ACB2 |  |  |  | CDC | 435 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
D15 | 新化DS | 0 |  |  |  |  | ACBA | [17 empty] | 2-34-04 | [7 empty] | ADCS_S | [8 empty] | 新化DS.所內電源ACBA | 所內電源故障警報 | OTHER | D15/0/StaDev/ACBA |  |  |  | CDC | 436 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  |  |  |  | STUV | [17 empty] | 2-33-08 | [7 empty] | ADCS_S | [8 empty] | 新化DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | D15/0/StaDev/STUV |  |  |  | CDC | 437 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  |  |  |  | CHG1 | [17 empty] | 2-33-12 | [7 empty] | ADCS_S | [8 empty] | 新化DS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | D15/0/StaDev/CHG1 |  |  |  | CDC | 438 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D15 | 新化DS | 0 |  |  |  |  | DCA | [17 empty] | 2-33-11 | [7 empty] | ADCS_S | [8 empty] | 新化DS.直流電源DCA | 直流電源故障警報 | OTHER | D15/0/StaDev/NFBA |  |  |  | CDC | 439 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  |  |  |  | DCE | [17 empty] | 2-33-14 | [7 empty] | ADCS_S | [8 empty] | 新化DS.直流電源DCE | 直流電源接地故障警報 | OTHER | D15/0/StaDev/DCE |  |  |  | CDC | 440 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  |  |  |  | OilLeak | [17 empty] | 2-34-07 | [7 empty] | ADCS_S | [8 empty] | 新化DS.洩油池水位警報 | 洩油池水位警報 | OTHER | D15/0/StaDev/OilLeak1 |  |  |  | CDC | 441 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  |  |  |  | CHG2 | [17 empty] | 2-33-13 | [7 empty] | ADCS_S | [8 empty] | 新化DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | D15/0/StaDev/CHG2 |  |  |  | CDC | 442 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D15 | 新化DS | 0 |  |  |  |  | CommACF | [17 empty] | 2-34-08 | [7 empty] | ADCS_S | [8 empty] | 新化DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | D15/0/StaDev/CommACF |  |  |  | CDC | 443 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D15 | 新化DS | 0 |  |  |  |  | Burglar1 | [17 empty] | 2-32-13 | [7 empty] | ADCS_S | [8 empty] | 新化DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | D15/0/StaDev/Burglar1 |  |  |  | CDC | 444 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  |  |  |  | Burglar2 | [17 empty] | 2-32-14 | [7 empty] | ADCS_S | [8 empty] | 新化DS.無人化防盜(2) | 無人化防盜(2)SP | OTHER | D15/0/StaDev/Burglar2 |  |  |  | CDC | 445 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  |  |  |  | Burglar3 | [17 empty] | 2-32-15 | [7 empty] | ADCS_S | [8 empty] | 新化DS.無人化防盜(3) | 無人化防盜(3)SP | OTHER | D15/0/StaDev/Burglar3 |  |  |  | CDC | 446 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  |  |  |  | Door1 | [17 empty] | 2-33-00 | [7 empty] | ADCS_S | [8 empty] | 新化DS.無人化門禁(1) | 無人化門禁(1)變電所大門 | OTHER | D15/0/StaDev/Door1 |  |  |  | CDC | 447 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  |  |  |  | Door2 | [17 empty] | 2-33-01 | [7 empty] | ADCS_S | [8 empty] | 新化DS.無人化門禁(2) | 無人化門禁(2)建築物鐵捲門 | OTHER | D15/0/StaDev/Door2 |  |  |  | CDC | 448 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  |  |  |  | Door3 | [17 empty] | 2-33-02 | [7 empty] | ADCS_S | [8 empty] | 新化DS.無人化門禁(3) | 無人化門禁(3)SP | OTHER | D15/0/StaDev/Door3 |  |  |  | CDC | 449 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  |  |  |  | 地下室積水(1) | [17 empty] | 1-31-08 | [7 empty] | ADCS_S | [8 empty] | 新化DS.地下室積水(1) | 地下室積水0.5公尺 | OTHER | D15/0/StaDev/Water1 |  |  |  | CDC | 450 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  |  |  |  | 地下室積水(2) | [17 empty] | 1-31-09 | [7 empty] | ADCS_S | [8 empty] | 新化DS.地下室積水(2) | 地下室積水1.5公尺 | OTHER | D15/0/StaDev/Water2 |  |  |  | CDC | 451 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  |  |  |  | 空調機跳脫警報 | [17 empty] | 2-33-03 | [7 empty] | ADCS_S | [8 empty] | 新化DS.空調機跳脫警報 | 空調機故障或電源跳脫 | OTHER | D15/0/StaDev/AIRCON |  |  |  | CDC | 452 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | NORMAL/FAULT | NORMAL
D15 | 新化DS | 161 | 161kV | 1730 | 道爺和順新化線(1730) |  | PHA | [17 empty] | 1-01-00 | [7 empty] | 161KV_S | [8 empty] | 新化DS.1730_PHA | 道爺和順新化線(1730) 相間RY | LINE161 | D15/161/1730/PHA |  |  |  | CDC | 453 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1730 | 道爺和順新化線(1730) |  | GDA | [17 empty] | 1-01-01 | [7 empty] | 161KV_S | [8 empty] | 新化DS.1730_GDA | 道爺和順新化線(1730) 接地RY | LINE161 | D15/161/1730/GDA |  |  |  | CDC | 454 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1730 | 道爺和順新化線(1730) |  | CB | [17 empty] | 1-00-05 |  | 1-02 | [5 empty] | 161KV_S | [8 empty] | 新化DS.1730_CB | 1730(道爺和順新化線) CB | LINE161 | D15/161/1730/CB |  |  |  | CDC | 455 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 161 | 161kV | 1730 | 道爺和順新化線(1730) |  | 79UL | [17 empty] | 1-31-03 |  | 1-51 | [5 empty] | ADCS_S | [8 empty] | 新化DS.1730_79UL | 道爺和順新化線(1730) 79RY U/L | LINE161 | D15/161/1730/79UL |  |  |  | CDC | 456 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D15 | 新化DS | 161 | 161kV | 1730 | 道爺和順新化線(1730) |  | DS1 | 1731 | [16 empty] | 1-34-08 | 1-34-09 | 1-74 | [5 empty] | ADCS_S | [8 empty] | 新化DS.1731_DS | 1731(道爺和順新化線) DS | LINE161 | D15/161/1730/DS1 |  |  |  | CDC | 457 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D15 | 新化DS | 161 | 161kV | 1730 | 道爺和順新化線(1730) |  | DS2 | 1732 | [16 empty] | 1-34-10 | 1-34-11 | 1-75 | [5 empty] | ADCS_S | [8 empty] | 新化DS.1732_DS | 1732(道爺和順新化線) DS | LINE161 | D15/161/1730/DS2 |  |  |  | CDC | 458 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D15 | 新化DS | 161 | 161kV | 1730 | 道爺和順新化線(1730) |  | DS3 | 1733 | [16 empty] | 1-34-12 | 1-34-13 | 1-76 | [5 empty] | ADCS_S | [8 empty] | 新化DS.1733_DS | 1733(道爺和順新化線) DS | LINE161 | D15/161/1730/DS3 |  |  |  | CDC | 459 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D15 | 新化DS | 161 | 161kV | 1730 | 道爺和順新化線(1730) |  | E3 | 1733E | [16 empty] | 1-34-14 | 1-34-15 | 1-77 | [5 empty] | ADCS_S | [8 empty] | 新化DS.1733E_ES | 1733E(道爺和順新化線) ES | LINE161 | D15/161/1730/ES3 |  |  |  | CDC | 460 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D15 | 新化DS | 161 | 161kV | 1740 | 道爺安南新化線(1740) |  | PHA | [17 empty] | 1-00-03 | [7 empty] | 161KV_S | [8 empty] | 新化DS.1740_PHA | 道爺安南新化線(1740) 相間RY | LINE161 | D15/161/1740/PHA |  |  |  | CDC | 461 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1510 | 統實永資線(1510) |  | 87L1 | [17 empty] | 1-02-05 | [7 empty] | 161KV_S | [8 empty] | 新化DS.1510_87L1 | 統實永資線(1510) 87L1RY | LINE161 | D15/161/1510/87A1 |  |  |  | CDC | 462 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1510 | 統實永資線(1510) |  | 87L2 | [17 empty] | 1-02-06 | [7 empty] | 161KV_S | [8 empty] | 新化DS.1510_87L2 | 統實永資線(1510) 87L2RY | LINE161 | D15/161/1510/87A2 |  |  |  | CDC | 463 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY26 | 新26線(KY26) |  | PHA | [17 empty] | 1-12-00 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY26_PHA | 11KV新26線(KY26) 相間RY | FEEDER | D15/11/KY26/51A |  |  |  | CDC | 464 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY26 | 新26線(KY26) |  | GDA | [17 empty] | 1-12-01 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY26_GDA | 11KV新26線(KY26) 接地RY | FEEDER | D15/11/KY26/51NA |  |  |  | CDC | 465 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY26 | 新26線(KY26) 79RY |  | 79UL | [17 empty] | 2-30-15 |  | 2-25 | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY26_79UL | 11KV新26線(KY26) 79RY U/L | FEEDER | D15/11/KY26/79UL |  |  |  | CDC | 466 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY26 | 新26線(KY26) LCO分流器 |  | ADJ | [17 empty] | 2-35-01 |  | 2-0D | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY26_ADJ | 11KV新26線(KY26) LCO分流器 U/L | FEEDER | D15/11/KY26/ADJ |  |  |  | CDC | 467 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY26 | KY26(11KV新26線) |  | CB | [17 empty] | 1-11-07 |  | 1-18 | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY26_CB | KY26(11KV新26線) CB | FEEDER | D15/11/KY26/CB |  |  |  | CDC | 468 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY27 | 新27線(KY27) |  | PHA | [17 empty] | 1-13-04 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY27_PHA | 11KV新27線(KY27) 相間RY | FEEDER | D15/11/KY27/51A |  |  |  | CDC | 469 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY27 | 新27線(KY27) |  | GDA | [17 empty] | 1-13-05 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY27_GDA | 11KV新27線(KY27) 接地RY | FEEDER | D15/11/KY27/51NA |  |  |  | CDC | 470 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY27 | 新27線(KY27) 79RY |  | 79UL | [17 empty] | 2-31-02 |  | 2-28 | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY27_79UL | 11KV新27線(KY27) 79RY U/L | FEEDER | D15/11/KY27/79UL |  |  |  | CDC | 471 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY27 | 新27線(KY27) LCO分流器 |  | ADJ | [17 empty] | 2-35-02 |  | 2-0E | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY27_ADJ | 11KV新27線(KY27) LCO分流器 U/L | FEEDER | D15/11/KY27/ADJ |  |  |  | CDC | 472 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY27 | KY27(11KV新27線) |  | CB | [17 empty] | 1-13-03 |  | 1-1B | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY27_CB | KY27(11KV新27線) CB | FEEDER | D15/11/KY27/CB |  |  |  | CDC | 473 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY28 | 新28線(KY28) |  | PHA | [17 empty] | 1-13-07 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY28_PHA | 11KV新28線(KY28) 相間RY | FEEDER | D15/11/KY28/51A |  |  |  | CDC | 474 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY28 | 新28線(KY28) |  | GDA | [17 empty] | 1-14-00 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY28_GDA | 11KV新28線(KY28) 接地RY | FEEDER | D15/11/KY28/51NA |  |  |  | CDC | 475 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY28 | 新28線(KY28) 79RY |  | 79UL | [17 empty] | 2-31-03 |  | 2-29 | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY28_79UL | 11KV新28線(KY28) 79RY U/L | FEEDER | D15/11/KY28/79UL |  |  |  | CDC | 476 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY28 | 新28線(KY28) LCO分流器 |  | ADJ | [17 empty] | 2-35-03 |  | 2-0F | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY28_ADJ | 11KV新28線(KY28) LCO分流器 U/L | FEEDER | D15/11/KY28/ADJ |  |  |  | CDC | 477 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY28 | KY28(11KV新28線) |  | CB | [17 empty] | 1-13-06 |  | 1-1C | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY28_CB | KY28(11KV新28線) CB | FEEDER | D15/11/KY28/CB |  |  |  | CDC | 478 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY29 | 新29線(KY29) |  | PHA | [17 empty] | 1-14-02 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY29_PHA | 11KV新29線(KY29) 相間RY | FEEDER | D15/11/KY29/51A |  |  |  | CDC | 479 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY29 | 新29線(KY29) |  | GDA | [17 empty] | 1-14-03 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY29_GDA | 11KV新29線(KY29) 接地RY | FEEDER | D15/11/KY29/51NA |  |  |  | CDC | 480 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY29 | 新29線(KY29) 79RY |  | 79UL | [17 empty] | 2-31-04 |  | 2-2A | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY29_79UL | 11KV新29線(KY29) 79RY U/L | FEEDER | D15/11/KY29/79UL |  |  |  | CDC | 481 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY29 | 新29線(KY29) LCO分流器 |  | ADJ | [17 empty] | 2-35-04 |  | 2-18 | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY29_ADJ | 11KV新29線(KY29) LCO分流器 U/L | FEEDER | D15/11/KY29/ADJ |  |  |  | CDC | 482 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY29 | KY29(11KV新29線) |  | CB | [17 empty] | 1-14-01 |  | 1-1D | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY29_CB | KY29(11KV新29線) CB | FEEDER | D15/11/KY29/CB |  |  |  | CDC | 483 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY30 | 新30線(KY30) |  | PHA | [17 empty] | 1-14-05 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY30_PHA | 11KV新30線(KY30) 相間RY | FEEDER | D15/11/KY30/51A |  |  |  | CDC | 484 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY30 | 新30線(KY30) |  | GDA | [17 empty] | 1-14-06 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY30_GDA | 11KV新30線(KY30) 接地RY | FEEDER | D15/11/KY30/51NA |  |  |  | CDC | 485 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY30 | 新30線(KY30) 79RY |  | 79UL | [17 empty] | 2-31-05 |  | 2-2B | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY30_79UL | 11KV新30線(KY30) 79RY U/L | FEEDER | D15/11/KY30/79UL |  |  |  | CDC | 486 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY30 | 新30線(KY30) LCO分流器 |  | ADJ | [17 empty] | 2-35-05 |  | 2-19 | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY30_ADJ | 11KV新30線(KY30) LCO分流器 U/L | FEEDER | D15/11/KY30/ADJ |  |  |  | CDC | 487 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY30 | KY30(11KV新30線) |  | CB | [17 empty] | 1-14-04 |  | 1-1E | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY30_CB | KY30(11KV新30線) CB | FEEDER | D15/11/KY30/CB |  |  |  | CDC | 488 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY37 | 新37線(KY37) |  | PHA | [17 empty] | 1-15-03 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY37_PHA | 11KV新37線(KY37) 相間RY | FEEDER | D15/11/KY37/51A |  |  |  | CDC | 489 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY37 | 新37線(KY37) |  | GDA | [17 empty] | 1-15-04 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY37_GDA | 11KV新37線(KY37) 接地RY | FEEDER | D15/11/KY37/51NA |  |  |  | CDC | 490 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY37 | 新37線(KY37) 79RY |  | 79UL | [17 empty] | 2-31-07 |  | 2-2D | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY37_79UL | 11KV新37線(KY37) 79RY U/L | FEEDER | D15/11/KY37/79UL |  |  |  | CDC | 491 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY37 | 新37線(KY37) LCO分流器 |  | ADJ | [17 empty] | 2-35-06 |  | 2-1A | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY37_ADJ | 11KV新37線(KY37) LCO分流器 U/L | FEEDER | D15/11/KY37/ADJ |  |  |  | CDC | 492 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY37 | KY37(11KV新37線) |  | CB | [17 empty] | 1-15-02 |  | 1-23 | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY37_CB | KY37(11KV新37線) CB | FEEDER | D15/11/KY37/CB |  |  |  | CDC | 493 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY38 | 新38線(KY38) |  | PHA | [17 empty] | 1-15-06 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY38_PHA | 11KV新38線(KY38) 相間RY | FEEDER | D15/11/KY38/51A |  |  |  | CDC | 494 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY38 | 新38線(KY38) |  | GDA | [17 empty] | 1-15-07 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY38_GDA | 11KV新38線(KY38) 接地RY | FEEDER | D15/11/KY38/51NA |  |  |  | CDC | 495 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY38 | 新38線(KY38) 79RY |  | 79UL | [17 empty] | 2-31-08 |  | 2-2E | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY38_79UL | 11KV新38線(KY38) 79RY U/L | FEEDER | D15/11/KY38/79UL |  |  |  | CDC | 496 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY38 | 新38線(KY38) LCO分流器 |  | ADJ | [17 empty] | 2-35-07 |  | 2-1B | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY38_ADJ | 11KV新38線(KY38) LCO分流器 U/L | FEEDER | D15/11/KY38/ADJ |  |  |  | CDC | 497 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY38 | KY38(11KV新38線) |  | CB | [17 empty] | 1-15-05 |  | 1-24 | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY38_CB | KY38(11KV新38線) CB | FEEDER | D15/11/KY38/CB |  |  |  | CDC | 498 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY39 | 新39線(KY39) |  | PHA | [17 empty] | 1-16-01 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY39_PHA | 11KV新39線(KY39) 相間RY | FEEDER | D15/11/KY39/51A |  |  |  | CDC | 499 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY39 | 新39線(KY39) |  | GDA | [17 empty] | 1-16-02 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY39_GDA | 11KV新39線(KY39) 接地RY | FEEDER | D15/11/KY39/51NA |  |  |  | CDC | 500 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY39 | 新39線(KY39) 79RY |  | 79UL | [17 empty] | 2-31-09 |  | 2-2F | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY39_79UL | 11KV新39線(KY39) 79RY U/L | FEEDER | D15/11/KY39/79UL |  |  |  | CDC | 501 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY39 | 新39線(KY39) LCO分流器 |  | ADJ | [17 empty] | 2-35-08 |  | 2-1C | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY39_ADJ | 11KV新39線(KY39) LCO分流器 U/L | FEEDER | D15/11/KY39/ADJ |  |  |  | CDC | 502 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY39 | KY39(11KV新39線) |  | CB | [17 empty] | 1-16-00 |  | 1-25 | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY39_CB | KY39(11KV新39線) CB | FEEDER | D15/11/KY39/CB |  |  |  | CDC | 503 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 11 | 11kV | KY40 | 新40線(KY40) |  | PHA | [17 empty] | 1-16-04 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY40_PHA | 11KV新40線(KY40) 相間RY | FEEDER | D15/11/KY40/51A |  |  |  | CDC | 504 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY40 | 新40線(KY40) |  | GDA | [17 empty] | 1-16-05 | [7 empty] | DDCS4_2 | [8 empty] | 新化DS.KY40_GDA | 11KV新40線(KY40) 接地RY | FEEDER | D15/11/KY40/51NA |  |  |  | CDC | 505 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | KY40 | 新40線(KY40) 79RY |  | 79UL | [17 empty] | 2-31-10 |  | 2-30 | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY40_79UL | 11KV新40線(KY40) 79RY U/L | FEEDER | D15/11/KY40/79UL |  |  |  | CDC | 506 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D15 | 新化DS | 11 | 11kV | KY40 | 新40線(KY40) LCO分流器 |  | ADJ | [17 empty] | 2-35-09 |  | 2-1D | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY40_ADJ | 11KV新40線(KY40) LCO分流器 U/L | FEEDER | D15/11/KY40/ADJ |  |  |  | CDC | 507 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D15 | 新化DS | 11 | 11kV | KY40 | KY40(11KV新40線) |  | CB | [17 empty] | 1-16-03 |  | 1-26 | [5 empty] | DDCS4_2 | [8 empty] | 新化DS.KY40_CB | KY40(11KV新40線) CB | FEEDER | D15/11/KY40/CB |  |  |  | CDC | 508 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | 100 | TIE(100) |  | CB | [17 empty] | 1-13-00 |  | 1-1A | [5 empty] | ADCS_S | [8 empty] | 新化DS.100_CB | 100(TIE) CB | TIE | D15/11/100/CB |  |  |  | CDC | 509 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | 100 | TIE(100) |  | 51A | [17 empty] | 1-13-01 | [7 empty] | ADCS_S | [8 empty] | 新化DS.100_51A | 11KV TIE(100) 51RY | TIE | D15/11/100/51A |  |  |  | CDC | 510 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 100 | TIE(100) |  | 51NA | [17 empty] | 1-13-02 | [7 empty] | ADCS_S | [8 empty] | 新化DS.100_51NA | 11KV TIE(100) 51N RY | TIE | D15/11/100/51NA |  |  |  | CDC | 511 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 200 | TIE(200) |  | CB | [17 empty] | 1-17-01 |  | 1-27 | [5 empty] | ADCS_S | [8 empty] | 新化DS.200_CB | 200(TIE) CB | TIE | D15/11/200/CB |  |  |  | CDC | 512 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | 200 | TIE(200) |  | 51A | [17 empty] | 1-17-02 | [7 empty] | ADCS_S | [8 empty] | 新化DS.200_51A | 11KV TIE(200) 51RY | TIE | D15/11/200/51A |  |  |  | CDC | 513 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 200 | TIE(200) |  | 51NA | [17 empty] | 1-17-03 | [7 empty] | ADCS_S | [8 empty] | 新化DS.200_51NA | 11KV TIE(200) 51N RY | TIE | D15/11/200/51NA |  |  |  | CDC | 514 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 1DTR | #1DTR |  | 51A | [17 empty] | 1-06-01 | [7 empty] | 161KV_S | [8 empty] | 新化DS.#1DTR_51A | #1DTR 51RY | MTR | D15/161/1750/51A |  |  |  | CDC | 515 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 1DTR | #1DTR |  | 51NA | [17 empty] | 1-06-02 | [7 empty] | 161KV_S | [8 empty] | 新化DS.#1DTR_51NA | #1DTR 51N RY | MTR | D15/161/1750/51NA |  |  |  | CDC | 516 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 1DTR | #1DTR |  | 51ZA | [17 empty] | 1-06-00 | [7 empty] | 161KV_S | [8 empty] | 新化DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | D15//1DTR/51ZA |  |  |  | CDC | 517 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 1DTR | #1DTR |  | 87A | [17 empty] | 1-05-06 | [7 empty] | 161KV_S | [8 empty] | 新化DS.#1DTR_87A | #1DTR 87RY | MTR | D15//1DTR/87A |  |  |  | CDC | 518 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 1DTR | #1DTR |  | 87UL | [17 empty] | 1-32-10 | [7 empty] | ADCS_S | [8 empty] | 新化DS.#1DTR_87UL | #1DTR 87RY U/L | MTR | D15//1DTR/87UL |  |  |  | CDC | 519 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D15 | 新化DS | 0 |  | 1DTR | #1DTR |  | 96PA | [17 empty] | 1-05-07 | [7 empty] | 161KV_S | [8 empty] | 新化DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | D15//1DTR/96PA |  |  |  | CDC | 520 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 1DTR | #1DTR |  | 96D | [17 empty] | 1-32-03 | [7 empty] | ADCS_S | [8 empty] | 新化DS.#1DTR_96D | #1DTR 96D RY | MTR | D15//1DTR/96D |  |  |  | CDC | 521 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 1DTR | #1DTR |  | 96P | [17 empty] | 1-32-04 | [7 empty] | ADCS_S | [8 empty] | 新化DS.#1DTR_96P | #1DTR 96P RY | MTR | D15//1DTR/96P |  |  |  | CDC | 522 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 1DTR | #1DTR |  | 63Q | [17 empty] | 1-32-05 | [7 empty] | ADCS_S | [8 empty] | 新化DS.#1DTR_63Q | #1DTR 63Q RY | MTR | D15//1DTR/63Q |  |  |  | CDC | 523 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 1DTR | #1DTR |  | 96B1 | [17 empty] | 1-32-06 | [7 empty] | ADCS_S | [8 empty] | 新化DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | D15//1DTR/96B1 |  |  |  | CDC | 524 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 1DTR | #1DTR |  | 96B2 | [17 empty] | 1-32-07 | [7 empty] | ADCS_S | [8 empty] | 新化DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | D15//1DTR/96B2 |  |  |  | CDC | 525 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 1DTR | #1DTR |  | TRA | [17 empty] | 1-32-13 | [7 empty] | ADCS_S | [8 empty] | 新化DS.#1DTR_TRA | #1DTR 重故障 | MTR | D15//1DTR/TRA |  |  |  | CDC | 526 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 1DTR | #1DTR |  | TRF | [17 empty] | 1-32-14 | [7 empty] | ADCS_S | [8 empty] | 新化DS.#1DTR_TRF | #1DTR 輕故障 | MTR | D15//1DTR/TRF |  |  |  | CDC | 527 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 1DTR(A) | #1DTR(A) |  | SupLocal | [17 empty] | 1-32-11 | [7 empty] | ADCS_S | [8 empty] | 新化DS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | D15//1DTR(A)/SupLocal |  |  |  | CDC | 528 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D15 | 新化DS | 0 |  | 1DTR(A) | #1DTR(A) |  | A_M | [17 empty] | 1-32-12 |  | 1-60 | [5 empty] | ADCS_S | [8 empty] | 新化DS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | D15//1DTR(A)/Tap Chan |  |  |  | CDC | 529 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D15 | 新化DS | 0 |  | 1DTR(B) | #1DTR(B) |  | SupLocal | [17 empty] | 1-32-15 | [7 empty] | ADCS_S | [8 empty] | 新化DS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | D15//1DTR(B)/SupLocal |  |  |  | CDC | 530 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D15 | 新化DS | 0 |  | 1DTR(B) | #1DTR(B) |  | A_M | [17 empty] | 1-33-00 |  | 1-62 | [5 empty] | ADCS_S | [8 empty] | 新化DS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | D15//1DTR(B)/Tap Chan |  |  |  | CDC | 531 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D15 | 新化DS | 0 |  | 2DTR | #2DTR |  | 51A | [17 empty] | 1-07-03 | [7 empty] | 161KV_S | [8 empty] | 新化DS.#2DTR_51A | #2DTR 51RY | MTR | D15/161/1760/51A |  |  |  | CDC | 532 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 2DTR | #2DTR |  | 51NA | [17 empty] | 1-07-04 | [7 empty] | 161KV_S | [8 empty] | 新化DS.#2DTR_51NA | #2DTR 51N RY | MTR | D15/161/1760/51NA |  |  |  | CDC | 533 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 2DTR | #2DTR |  | 51ZA | [17 empty] | 1-07-02 | [7 empty] | 161KV_S | [8 empty] | 新化DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | D15//2DTR/51ZA |  |  |  | CDC | 534 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 2DTR | #2DTR |  | 87A | [17 empty] | 1-07-00 | [7 empty] | 161KV_S | [8 empty] | 新化DS.#2DTR_87A | #2DTR 87RY | MTR | D15//2DTR/87A |  |  |  | CDC | 535 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 2DTR | #2DTR |  | 87UL | [17 empty] | 1-33-01 | [7 empty] | ADCS_S | [8 empty] | 新化DS.#2DTR_87UL | #2DTR 87RY U/L | MTR | D15//2DTR/87UL |  |  |  | CDC | 536 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D15 | 新化DS | 0 |  | 2DTR | #2DTR |  | 96PA | [17 empty] | 1-07-01 | [7 empty] | 161KV_S | [8 empty] | 新化DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | D15//2DTR/96PA |  |  |  | CDC | 537 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 2DTR | #2DTR |  | 96D | [17 empty] | 1-32-01 | [7 empty] | ADCS_S | [8 empty] | 新化DS.#2DTR_96D | #2DTR 96D RY | MTR | D15//2DTR/96D |  |  |  | CDC | 538 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 2DTR | #2DTR |  | 96P | [17 empty] | 1-32-02 | [7 empty] | ADCS_S | [8 empty] | 新化DS.#2DTR_96P | #2DTR 96P RY | MTR | D15//2DTR/96P |  |  |  | CDC | 539 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 2DTR | #2DTR |  | 63Q | [17 empty] | 1-33-13 | [7 empty] | ADCS_S | [8 empty] | 新化DS.#2DTR_63Q | #2DTR 63Q RY | MTR | D15//2DTR/63Q |  |  |  | CDC | 540 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 2DTR | #2DTR |  | 96B1 | [17 empty] | 1-33-14 | [7 empty] | ADCS_S | [8 empty] | 新化DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | D15//2DTR/96B1 |  |  |  | CDC | 541 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 2DTR | #2DTR |  | 96B2 | [17 empty] | 1-33-15 | [7 empty] | ADCS_S | [8 empty] | 新化DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | D15//2DTR/96B2 |  |  |  | CDC | 542 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 2DTR | #2DTR |  | TRA | [17 empty] | 1-33-04 | [7 empty] | ADCS_S | [8 empty] | 新化DS.#2DTR_TRA | #2DTR 重故障 | MTR | D15//2DTR/TRA |  |  |  | CDC | 543 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 2DTR | #2DTR |  | TRF | [17 empty] | 1-33-05 | [7 empty] | ADCS_S | [8 empty] | 新化DS.#2DTR_TRF | #2DTR 輕故障 | MTR | D15//2DTR/TRF |  |  |  | CDC | 544 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 2DTR(A) | #2DTR(A) |  | SupLocal | [17 empty] | 1-33-02 | [7 empty] | ADCS_S | [8 empty] | 新化DS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | D15//2DTR(A)/SupLocal |  |  |  | CDC | 545 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D15 | 新化DS | 0 |  | 2DTR(A) | #2DTR(A) |  | A_M | [17 empty] | 1-33-03 |  | 1-64 | [5 empty] | ADCS_S | [8 empty] | 新化DS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | D15//2DTR(A)/Tap Chan |  |  |  | CDC | 546 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D15 | 新化DS | 0 |  | 2DTR(B) | #2DTR(B) |  | SupLocal | [17 empty] | 1-33-06 | [7 empty] | ADCS_S | [8 empty] | 新化DS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | D15//2DTR(B)/SupLocal |  |  |  | CDC | 547 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D15 | 新化DS | 0 |  | 2DTR(B) | #2DTR(B) |  | A_M | [17 empty] | 1-33-07 |  | 1-66 | [5 empty] | ADCS_S | [8 empty] | 新化DS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | D15//2DTR(B)/Tap Chan |  |  |  | CDC | 548 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D15 | 新化DS | 0 |  | 1500TIE | 1500 |  | 50SA | [17 empty] | 2-33-04 | [7 empty] | ADCS_S | [8 empty] | 新化DS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | D15/161/1500/50SA |  |  |  | CDC | 549 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | TEST/NORMAL | NORMAL
D15 | 新化DS | 0 |  | CH1 | RTU |  | STATE | [17 empty] | 2-3F-06 | [7 empty] | ADCS_S | [8 empty] | 新化DS.CH1_STATE | RTU 通訊狀態 Channel 1 | OTHER |  |  |  |  | CDC | 550 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | IDLE/UP | UP
D15 | 新化DS | 0 |  | CH2 | RTU |  | STATE | [17 empty] | 2-3F-08 | [7 empty] | ADCS_S | [8 empty] | 新化DS.CH2_STATE | RTU 通訊狀態 Channel 2 | OTHER |  |  |  |  | CDC | 551 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | IDLE/UP | UP
D15 | 新化DS | 0 |  |  |  |  | 通信機房溫度 | [17 empty] | 2-34-11 | [7 empty] | ADCS_S | [8 empty] | 新化DS.通信機房溫度 | 通信機房溫度警報 | OTHER | D15/0/StaDev/R_Temp |  |  |  | CDC | 552 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1710 | 山上一路(1710) |  | 87A | [17 empty] | 1-02-00 | [7 empty] | 161KV_S | [8 empty] | 新化DS.1710_87A | 山上一路(1710) 87RY | LINE161 | D15/161/1710/87A |  |  |  | CDC | 553 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1710 | 山上一路(1710) |  | 87UL | [17 empty] | 1-30-08 |  | 1-46 | [5 empty] | ADCS_S | [8 empty] | 新化DS.1710_87UL | 山上一路(1710) 87RY U/L | LINE161 | D15/161/1710/87UL |  |  |  | CDC | 554 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D15 | 新化DS | 161 | 161kV | 1710 | 山上一路(1710) |  | PHA | [17 empty] | 1-02-02 | [7 empty] | 161KV_S | [8 empty] | 新化DS.1710_PHA | 山上一路(1710) 相間RY | LINE161 | D15/161/1710/21A |  |  |  | CDC | 555 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1720 | 山上二路(1720) |  | PHA | [17 empty] | 1-01-05 | [7 empty] | 161KV_S | [8 empty] | 新化DS.1720_PHA | 山上二路(1720) 相間RY | LINE161 | D15/161/1720/21A |  |  |  | CDC | 556 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1720 | 山上二路(1720) |  | 87A | [17 empty] | 1-01-03 | [7 empty] | 161KV_S | [8 empty] | 新化DS.1720_87A | 山上二路(1720) 87RY | LINE161 | D15/161/1720/87A |  |  |  | CDC | 557 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1720 | 山上二路(1720) |  | 87UL | [17 empty] | 1-30-06 |  | 1-44 | [5 empty] | ADCS_S | [8 empty] | 新化DS.1720_87UL | 山上二路(1720) 87RY U/L | LINE161 | D15/161/1720/87UL |  |  |  | CDC | 558 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D15 | 新化DS | 161 | 161kV |  |  |  | OSCF | [17 empty] | 2-32-09 | [7 empty] | ADCS_S | [8 empty] | 新化DS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | D15/161/ComPoint/OSCF |  |  |  | CDC | 559 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 1510 | 統實永資線(1510) |  | 87CFA | [17 empty] | 1-31-00 | [7 empty] | ADCS_S | [8 empty] | 新化DS.1510_87CFA | 統實永資線(1510) 87RY通訊故障 | OTHER | D15/161/1510/87UL |  |  |  | CDC | 560 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 1510 | 統實永資線(1510) |  | RYFA | [17 empty] | 1-31-01 | [7 empty] | ADCS_S | [8 empty] | 新化DS.1510_RYFA | 統實永資線(1510) 數位電驛故障 | OTHER | D15/161/1510/85CFA |  |  |  | CDC | 561 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 1710 | 山上一路(1710) |  | 87CFA | [17 empty] | 1-32-00 | [7 empty] | ADCS_S | [8 empty] | 新化DS.1710_87CFA | 山上新化一路(1710)87RY通訊故障 | OTHER | D15/161/1710/87CFA |  |  |  | CDC | 562 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 1710 | 山上一路(1710) |  | RYFA | [17 empty] | 2-30-02 | [7 empty] | ADCS_S | [8 empty] | 新化DS.1710_RYFA | 山上新化一路(1710)數位電驛故障 | OTHER | D15/161/1710/87A1 |  |  |  | CDC | 563 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 1720 | 山上二路(1720) |  | 87CFA | [17 empty] | 1-31-14 | [7 empty] | ADCS_S | [8 empty] | 新化DS.1720_87CFA | 山上新化二路(1720)87RY通訊故障 | OTHER | D15/161/1720/87CFA |  |  |  | CDC | 564 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 1720 | 山上二路(1720) |  | RYFA | [17 empty] | 2-30-03 | [7 empty] | ADCS_S | [8 empty] | 新化DS.1720_RYFA | 山上新化二路(1720)數位電驛故障 | OTHER | D15/161/1720/87A2 |  |  |  | CDC | 565 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 1730 | 道爺和順新化線(1730) |  | RYFA | [17 empty] | 2-30-01 | [7 empty] | ADCS_S | [8 empty] | 新化DS.1730_RYFA | 道爺和順新化(1730)數位電驛故障 | OTHER | D15/161/1730/RYFA |  |  |  | CDC | 566 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 1740 | 道爺安南新化線(1740) |  | RYFA | [17 empty] | 1-30-10 | [7 empty] | ADCS_S | [8 empty] | 新化DS.1740_RYFA | 道爺安南新化(1740)數位電驛故障 | OTHER | D15/161/1740/RYFA |  |  |  | CDC | 567 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1740 | 道爺安南新化線(1740) |  | 87A | [17 empty] | 1-00-01 | [7 empty] | 161KV_S | [8 empty] | 新化DS.1740_87A | 道爺安南新化線(1740) 87RY | LINE161 | D15/161/1740/87A |  |  |  | CDC | 568 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1740 | 道爺安南新化線(1740) |  | 87UL | [17 empty] | 1-30-02 |  | 1-40 | [5 empty] | ADCS_S | [8 empty] | 新化DS.1740_87UL | 道爺安南新化線(1740) 87RY U/L | LINE161 | D15/161/1740/87UL |  |  |  | CDC | 569 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D15 | 新化DS | 0 |  | 1740 | 道爺安南新化線(1740) |  | 87CFA | [17 empty] | 1-30-09 | [7 empty] | ADCS_S | [8 empty] | 新化DS.1740_87CFA | 道爺安南新化(1740)87RY通訊故障 | OTHER | D15/161/1740/87CFA |  |  |  | CDC | 570 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1730 | 道爺和順新化線(1730) |  | 87A | [17 empty] | 1-00-06 | [7 empty] | 161KV_S | [8 empty] | 新化DS.1730_87A | 道爺和順新化線(1730) 87RY | LINE161 | D15/161/1730/87A |  |  |  | CDC | 571 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | 1730 | 道爺和順新化線(1730) |  | 87UL | [17 empty] | 1-30-04 |  | 1-42 | [5 empty] | ADCS_S | [8 empty] | 新化DS.1730_87UL | 道爺和順新化線(1730) 87RY U/L | LINE161 | D15/161/1730/87UL |  |  |  | CDC | 572 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D15 | 新化DS | 0 |  | 1730 | 道爺和順新化線(1730) |  | 87CFA | [17 empty] | 2-30-00 | [7 empty] | ADCS_S | [8 empty] | 新化DS.1730_87CFA | 道爺和順新化(1730)87RY通訊故障 | OTHER | D15/161/1730/87CFA |  |  |  | CDC | 573 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D15 | 新化DS | 0 |  | BVS | BVS |  | RY | [17 empty] | 2-32-04 | [7 empty] | ADCS_S | [8 empty] | 新化DS.BVS_RY | BVS GRZ100 RY U/L | OTHER | D15/0/ComPoint/GRZ100 |  |  |  | CDC | 574 | GENERICDIPoint | DS034_L2 | CDC2_DI |  | DI | [34 empty] | LOCK/USE | USE
D15 | 新化DS | 0 |  |  |  |  | GEN | [17 empty] | 1-31-10 | [7 empty] | ADCS_S | [8 empty] | 新化DS.GEN | 緊急發電機運轉 | OTHER | D15/0/NULL/1A5Other |  |  |  | CDC | 575 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D15 | 新化DS | 161 | 161kV | _BUS | BUS |  | 87CTFA | [17 empty] | 1-31-12 | [7 empty] | ADCS_S | [8 empty] | 新化DS.161KV_BUS_CTFA | 161KV BUS 87RY CT回路故障 | OTHER | D15/161/NULL/87CTFA |  |  |  | CDC | 576 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D15 | 新化DS | 161 | 161kV | _BUS | BUS |  | RYFA | [17 empty] | 1-31-11 | [7 empty] | ADCS_S | [8 empty] | 新化DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | D15/161/ComPoint/BUS_RYFA |  |  |  | CDC | 577 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D15 | 新化DS | 0 |  | OLTC | OLTC |  | OLTCA | [17 empty] | 1-31-06 | [7 empty] | ADCS_S | [8 empty] | 新化DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | D15/0/ComPoint/OLTC_A |  |  |  | CDC | 578 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D15 | 新化DS | 11 | 11kV | IED故障 | IED故障 |  | RYFA | [17 empty] | 1-31-07 | [7 empty] | ADCS_S | [8 empty] | 新化DS.11KV_RYFA | 11kV IED故障 #1#2DTR二次側 | OTHER |  |  |  |  | CDC | 579 | GENERICDIPoint | DS034_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 310 | #1DTR(310) |  | GDA | [17 empty] | 1-08-01 | [7 empty] | ADCS_S | [8 empty] | 新化DS.310_GDA | 11KV M1A(310) 51N RY | OTHER |  |  |  |  | CDC | 580 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 320 | #1DTR(320) |  | GDA | [17 empty] | 1-08-02 | [7 empty] | ADCS_S | [8 empty] | 新化DS.320_GDA | 11KV M1B(320) 51N RY | OTHER |  |  |  |  | CDC | 581 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 330 | #2DTR(330) |  | GDA | [17 empty] | 1-08-03 | [7 empty] | ADCS_S | [8 empty] | 新化DS.330_GDA | 11KV M2A(330) 51N RY | OTHER |  |  |  |  | CDC | 582 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 0 |  | 340 | #2DTR(340) |  | GDA | [17 empty] | 1-08-04 | [7 empty] | ADCS_S | [8 empty] | 新化DS.340_GDA | 11KV M2B(340) 51N RY | OTHER |  |  |  |  | CDC | 583 | GENERICDIPoint | DS034_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D15 | 新化DS | 0 |  | TRD | 新化DS |  | 093 | [25 empty] | TRAIN_AD | [8 empty] | 新化DS.TRD_093 | 新化DS NT #1ADTR 11KV_Hi_Limit | [6 empty] | 584 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D15 | 新化DS | 0 |  | TRD | 新化DS |  | 094 | [25 empty] | TRAIN_AD | [8 empty] | 新化DS.TRD_094 | 新化DS NT #1ADTR 11KV_Lo_Limit | [6 empty] | 585 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D15 | 新化DS | 0 |  | TRD | 新化DS |  | 095 | [25 empty] | TRAIN_AD | [8 empty] | 新化DS.TRD_095 | 新化DS NT #2BDTR 11KV_Hi_Limit | [6 empty] | 586 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D15 | 新化DS | 0 |  | TRD | 新化DS |  | 096 | [25 empty] | TRAIN_AD | [8 empty] | 新化DS.TRD_096 | 新化DS NT #2BDTR 11KV_Lo_Limit | [6 empty] | 587 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D15 | 新化DS | 0 |  | TRD | 新化DS |  | 097 | [25 empty] | TRAIN_AD | [8 empty] | 新化DS.TRD_097 | 新化DS NT #2ADTR 11KV_Hi_Limit | [6 empty] | 588 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D15 | 新化DS | 0 |  | TRD | 新化DS |  | 098 | [25 empty] | TRAIN_AD | [8 empty] | 新化DS.TRD_098 | 新化DS NT #2ADTR 11KV_Lo_Limit | [6 empty] | 589 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D15 | 新化DS | 0 |  | TRD | 新化DS |  | 099 | [25 empty] | TRAIN_AD | [8 empty] | 新化DS.TRD_099 | 新化DS NT #1BDTR 11KV_Hi_Limit | [6 empty] | 590 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D15 | 新化DS | 0 |  | TRD | 新化DS |  | 100 | [25 empty] | TRAIN_AD | [8 empty] | 新化DS.TRD_100 | 新化DS NT #1BDTR 11KV_Lo_Limit | [6 empty] | 591 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D15 | 新化DS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 新化DS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 592 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 11 | 11kV | 220_SC | #2SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 新化DS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 593 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 11 | 11kV | 230_SC | #3SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 新化DS.230_SC_CAP | 11KV#3SC 容量 | SC | [5 empty] | 594 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 11 | 11kV | 240_SC | #4SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 新化DS.240_SC_CAP | 11KV#4SC 容量 | SC | [5 empty] | 595 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 11 | 11kV | 250_SC | #5SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 新化DS.250_SC_CAP | 11KV#5SC 容量 | SC | [5 empty] | 596 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 11 | 11kV | 260_SC | #6SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 新化DS.260_SC_CAP | 11KV#6SC 容量 | SC | [5 empty] | 597 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D15 | 新化DS | 161 | 161kV | 1510 | 統實永資線(1510) |  | LE0 | 1510LE | [24 empty] | ADCS_S | [8 empty] | 新化DS.1510LE | 1510LE (非取樣點) | LINE161 | D15/161/1510/LE0 |  |  |  |  | 598 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 161 | 161kV | 1510 | 統實永資線(1510) |  | BE0 | 1510BE | [24 empty] | ADCS_S | [8 empty] | 新化DS.1510BE | 1510BE (非取樣點) | LINE161 | D15/161/1510/BE0 |  |  |  |  | 599 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 161 | 161kV | 1710 | 山上一路(1710) |  | LE0 | 1710LE | [24 empty] | ADCS_S | [8 empty] | 新化DS.1710LE | 1710LE (非取樣點) | LINE161 | D15/161/1710/LE0 |  |  |  |  | 600 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 161 | 161kV | 1710 | 山上一路(1710) |  | BE0 | 1710BE | [24 empty] | ADCS_S | [8 empty] | 新化DS.1710BE | 1710BE (非取樣點) | LINE161 | D15/161/1710/BE0 |  |  |  |  | 601 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 161 | 161kV | 1720 | 山上二路(1720) |  | LE0 | 1720LE | [24 empty] | ADCS_S | [8 empty] | 新化DS.1720LE | 1720LE (非取樣點) | LINE161 | D15/161/1720/LE0 |  |  |  |  | 602 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 161 | 161kV | 1720 | 山上二路(1720) |  | BE0 | 1720BE | [24 empty] | ADCS_S | [8 empty] | 新化DS.1720BE | 1720BE (非取樣點) | LINE161 | D15/161/1720/BE0 |  |  |  |  | 603 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 161 | 161kV | 1740 | 道爺安南新化線(1740) |  | LE0 | 1740LE | [24 empty] | ADCS_S | [8 empty] | 新化DS.1740LE | 1740LE (非取樣點) | LINE161 | D15/161/1740/LE0 |  |  |  |  | 604 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 161 | 161kV | 1740 | 道爺安南新化線(1740) |  | BE0 | 1740BE | [24 empty] | ADCS_S | [8 empty] | 新化DS.1740BE | 1740BE (非取樣點) | LINE161 | D15/161/1740/BE0 |  |  |  |  | 605 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | KY21 | KY21_DS |  | DS1 | KY21_DS | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY21_DS | KY21_DS (非取樣點) | FEEDER | D15/11/KY21/DS |  |  |  |  | 606 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | KY21 | KY21_ES |  | LE0 | KY21_ES | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY21_ES | KY21_ES (非取樣點) | FEEDER | D15/11/KY21/ES |  |  |  |  | 607 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | KY22 | KY22_DS |  | DS1 | KY22_DS | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY22_DS | KY22_DS (非取樣點) | FEEDER | D15/11/KY22/DS |  |  |  |  | 608 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | KY22 | KY22_ES |  | LE0 | KY22_ES | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY22_ES | KY22_ES (非取樣點) | FEEDER | D15/11/KY22/ES |  |  |  |  | 609 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | KY23 | KY23_DS |  | DS1 | KY23_DS | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY23_DS | KY23_DS (非取樣點) | FEEDER | D15/11/KY23/DS |  |  |  |  | 610 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | KY23 | KY23_ES |  | LE0 | KY23_ES | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY23_ES | KY23_ES (非取樣點) | FEEDER | D15/11/KY23/ES |  |  |  |  | 611 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | KY24 | KY24_DS |  | DS1 | KY24_DS | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY24_DS | KY24_DS (非取樣點) | FEEDER | D15/11/KY24/DS |  |  |  |  | 612 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | KY24 | KY24_ES |  | LE0 | KY24_ES | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY24_ES | KY24_ES (非取樣點) | FEEDER | D15/11/KY24/ES |  |  |  |  | 613 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | KY25 | KY25_DS |  | DS1 | KY25_DS | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY25_DS | KY25_DS (非取樣點) | FEEDER | D15/11/KY25/DS |  |  |  |  | 614 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | KY25 | KY25_ES |  | LE0 | KY25_ES | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY25_ES | KY25_ES (非取樣點) | FEEDER | D15/11/KY25/ES |  |  |  |  | 615 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | KY31 | KY31_DS |  | DS1 | KY31_DS | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY31_DS | KY31_DS (非取樣點) | FEEDER | D15/11/KY31/DS |  |  |  |  | 616 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | KY31 | KY31_ES |  | LE0 | KY31_ES | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY31_ES | KY31_ES (非取樣點) | FEEDER | D15/11/KY31/ES |  |  |  |  | 617 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | KY32 | KY32_DS |  | DS1 | KY32_DS | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY32_DS | KY32_DS (非取樣點) | FEEDER | D15/11/KY32/DS |  |  |  |  | 618 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | KY32 | KY32_ES |  | LE0 | KY32_ES | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY32_ES | KY32_ES (非取樣點) | FEEDER | D15/11/KY32/ES |  |  |  |  | 619 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | KY33 | KY33_DS |  | DS1 | KY33_DS | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY33_DS | KY33_DS (非取樣點) | FEEDER | D15/11/KY33/DS |  |  |  |  | 620 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | KY33 | KY33_ES |  | LE0 | KY33_ES | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY33_ES | KY33_ES (非取樣點) | FEEDER | D15/11/KY33/ES |  |  |  |  | 621 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | KY34 | KY34_DS |  | DS1 | KY34_DS | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY34_DS | KY34_DS (非取樣點) | FEEDER | D15/11/KY34/DS |  |  |  |  | 622 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | KY34 | KY34_ES |  | LE0 | KY34_ES | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY34_ES | KY34_ES (非取樣點) | FEEDER | D15/11/KY34/ES |  |  |  |  | 623 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | KY35 | KY35_DS |  | DS1 | KY35_DS | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY35_DS | KY35_DS (非取樣點) | FEEDER | D15/11/KY35/DS |  |  |  |  | 624 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | KY35 | KY35_ES |  | LE0 | KY35_ES | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY35_ES | KY35_ES (非取樣點) | FEEDER | D15/11/KY35/ES |  |  |  |  | 625 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | KY36 | KY36_DS |  | DS1 | KY36_DS | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY36_DS | KY36_DS (非取樣點) | FEEDER | D15/11/KY36/DS |  |  |  |  | 626 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | KY36 | KY36_ES |  | LE0 | KY36_ES | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY36_ES | KY36_ES (非取樣點) | FEEDER | D15/11/KY36/ES |  |  |  |  | 627 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [24 empty] | ADCS_S | [8 empty] | 新化DS.1501E | 1501E (非取樣點) | TIE | D15/161/1500/E1 |  |  |  |  | 628 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [24 empty] | ADCS_S | [8 empty] | 新化DS.1502E | 1502E (非取樣點) | TIE | D15/161/1500/E2 |  |  |  |  | 629 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | 1750TE | [24 empty] | ADCS_S | [8 empty] | 新化DS.1750TE | 1750TE (非取樣點) | MTR | D15/161/1750/TE0 |  |  |  |  | 630 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | 1750BE | [24 empty] | ADCS_S | [8 empty] | 新化DS.1750BE | 1750BE (非取樣點) | MTR | D15/161/1750/BE0 |  |  |  |  | 631 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | 310 | #1DTR(310) |  | DS1 | 310_DS | [24 empty] | ADCS_S | [8 empty] | 新化DS.310_DS | 310_DS (非取樣點) | MTR | D15/11/310/DS |  |  |  |  | 632 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | 310 | #1DTR(310) |  | LE0 | 310_ES | [24 empty] | ADCS_S | [8 empty] | 新化DS.310_ES | 310_ES (非取樣點) | MTR | D15/11/310/ES |  |  |  |  | 633 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | 320 | #1DTR(320) |  | DS1 | 320_DS | [24 empty] | ADCS_S | [8 empty] | 新化DS.320_DS | 320_DS (非取樣點) | MTR | D15/11/320/DS |  |  |  |  | 634 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | 320 | #1DTR(320) |  | LE0 | 320_ES | [24 empty] | ADCS_S | [8 empty] | 新化DS.320_ES | 320_ES (非取樣點) | MTR | D15/11/320/ES |  |  |  |  | 635 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | 1760TE | [24 empty] | ADCS_S | [8 empty] | 新化DS.1760TE | 1760TE (非取樣點) | MTR | D15/161/1760/TE0 |  |  |  |  | 636 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | 1760BE | [24 empty] | ADCS_S | [8 empty] | 新化DS.1760BE | 1760BE (非取樣點) | MTR | D15/161/1760/BE0 |  |  |  |  | 637 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | 330 | #2DTR(330) |  | DS1 | 330_DS | [24 empty] | ADCS_S | [8 empty] | 新化DS.330_DS | 330_DS (非取樣點) | MTR | D15/11/330/DS |  |  |  |  | 638 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | 330 | #2DTR(330) |  | LE0 | 330_ES | [24 empty] | ADCS_S | [8 empty] | 新化DS.330_ES | 330_ES (非取樣點) | MTR | D15/11/330/ES |  |  |  |  | 639 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | 340 | #2DTR(340) |  | DS1 | 340_DS | [24 empty] | ADCS_S | [8 empty] | 新化DS.340_DS | 340_DS (非取樣點) | MTR | D15/11/340/DS |  |  |  |  | 640 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | 340 | #2DTR(340) |  | LE0 | 340_ES | [24 empty] | ADCS_S | [8 empty] | 新化DS.340_ES | 340_ES (非取樣點) | MTR | D15/11/340/ES |  |  |  |  | 641 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | 210 | #1SC(210) |  | LE0 | 210_ES | [24 empty] | ADCS_S | [8 empty] | 新化DS.210_ES | 210_ES (非取樣點) | SC | [5 empty] | 642 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | 210 | #1SC(210) |  | DS1 | 210_DS | [24 empty] | ADCS_S | [8 empty] | 新化DS.210_DS | 210_DS (非取樣點) | SC | D15/11/210/DS |  |  |  |  | 643 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | 220 | #2SC(220) |  | LE0 | 220_ES | [24 empty] | ADCS_S | [8 empty] | 新化DS.220_ES | 220_ES (非取樣點) | SC | [5 empty] | 644 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | 220 | #2SC(220) |  | DS1 | 220_DS | [24 empty] | ADCS_S | [8 empty] | 新化DS.220_DS | 220_DS (非取樣點) | SC | D15/11/220/DS |  |  |  |  | 645 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | 230 | #3SC(230) |  | LE0 | 230_ES | [24 empty] | ADCS_S | [8 empty] | 新化DS.230_ES | 230_ES (非取樣點) | SC | [5 empty] | 646 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | 230 | #3SC(230) |  | DS1 | 230_DS | [24 empty] | ADCS_S | [8 empty] | 新化DS.230_DS | 230_DS (非取樣點) | SC | D15/11/230/DS |  |  |  |  | 647 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | 240 | #4SC(240) |  | LE0 | 240_ES | [24 empty] | ADCS_S | [8 empty] | 新化DS.240_ES | 240_ES (非取樣點) | SC | [5 empty] | 648 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | 240 | #4SC(240) |  | DS1 | 240_DS | [24 empty] | ADCS_S | [8 empty] | 新化DS.240_DS | 240_DS (非取樣點) | SC | D15/11/240/DS |  |  |  |  | 649 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | 250 | #5SC(250) |  | LE0 | 250_ES | [24 empty] | ADCS_S | [8 empty] | 新化DS.250_ES | 250_ES (非取樣點) | SC | [5 empty] | 650 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | 250 | #5SC(250) |  | DS1 | 250_DS | [24 empty] | ADCS_S | [8 empty] | 新化DS.250_DS | 250_DS (非取樣點) | SC | D15/11/250/DS |  |  |  |  | 651 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | 260 | #6SC(260) |  | LE0 | 260_ES | [24 empty] | ADCS_S | [8 empty] | 新化DS.260_ES | 260_ES (非取樣點) | SC | [5 empty] | 652 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | 260 | #6SC(260) |  | DS1 | 260_DS | [24 empty] | ADCS_S | [8 empty] | 新化DS.260_DS | 260_DS (非取樣點) | SC | D15/11/260/DS |  |  |  |  | 653 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | 15B1E | 15B1E |  | BE1 | 15B1E | [24 empty] | ADCS_S | [8 empty] | 新化DS.15B1E | 15B1E (非取樣點) | BUS | D15/161/161B1E/BE1 |  |  |  |  | 654 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | 15B2E | 15B2E |  | BE2 | 15B2E | [24 empty] | ADCS_S | [8 empty] | 新化DS.15B2E | 15B2E (非取樣點) | BUS | D15/161/161B2E/BE2 |  |  |  |  | 655 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | ADCS_S | [8 empty] | 新化DS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 656 | NotelDIPoint | [38 empty] | START/STOP | STOP
D15 | 新化DS | 161 | 161kV | 1730 | 道爺和順新化線(1730) |  | LE0 | 1730LE | [24 empty] | ADCS_S | [8 empty] | 新化DS.1730LE | 1730LE (非取樣點) | LINE161 | D15/161/1730/LE0 |  |  |  |  | 657 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 161 | 161kV | 1730 | 道爺和順新化線(1730) |  | BE0 | 1730BE | [24 empty] | ADCS_S | [8 empty] | 新化DS.1730BE | 1730BE (非取樣點) | LINE161 | D15/161/1730/BE0 |  |  |  |  | 658 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 69 | 69kV | 1710 | 山上一路(1710) |  | PW1UL | 1710_PW1UL | [24 empty] | ADCS_S | [8 empty] | 新化DS.1710_PW1UL | 山上一路(1710)PW1_UL(非取樣點) | LINE69 | [5 empty] | 659 | NotelDIPoint | [38 empty] | USE/LOCK | USE
D15 | 新化DS | 69 | 69kV | 1710 | 山上一路(1710) |  | PW2UL | 1710_PW2UL | [24 empty] | ADCS_S | [8 empty] | 新化DS.1710_PW2UL | 山上一路(1710)PW2_UL(非取樣點) | LINE69 | [5 empty] | 660 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
D15 | 新化DS | 69 | 69kV | 1710 | 山上一路(1710) |  | HCBUL | 1710_HCBUL | [24 empty] | ADCS_S | [8 empty] | 新化DS.1710_HCBUL | 山上一路(1710)HCB_UL(非取樣點) | LINE69 | [5 empty] | 661 | NotelDIPoint | [38 empty] | USE/LOCK | USE
D15 | 新化DS | 69 | 69kV | 1720 | 山上二路(1720) |  | PW1UL | 1720_PW1UL | [24 empty] | ADCS_S | [8 empty] | 新化DS.1720_PW1UL | 山上二路(1720)PW1_UL(非取樣點) | LINE69 | [5 empty] | 662 | NotelDIPoint | [38 empty] | USE/LOCK | USE
D15 | 新化DS | 69 | 69kV | 1720 | 山上二路(1720) |  | PW2UL | 1720_PW2UL | [24 empty] | ADCS_S | [8 empty] | 新化DS.1720_PW2UL | 山上二路(1720)PW2_UL(非取樣點) | LINE69 | [5 empty] | 663 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
D15 | 新化DS | 69 | 69kV | 1720 | 山上二路(1720) |  | HCBUL | 1720_HCBUL | [24 empty] | ADCS_S | [8 empty] | 新化DS.1720_HCBUL | 山上二路(1720)HCB_UL(非取樣點) | LINE69 | [5 empty] | 664 | NotelDIPoint | [38 empty] | USE/LOCK | USE
D15 | 新化DS | 0 |  | 1SSTR | #1SSTR |  | LBS | #1SSTR_LBS | [24 empty] | ADCS_S | [8 empty] | 新化DS.#1SSTR_LBS | #1SSTR LBS(非取樣點) | OTHER | [5 empty] | 665 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | 1SSTR | #1SSTR |  | PF | #1SSTR_PF | [24 empty] | ADCS_S | [8 empty] | 新化DS.#1SSTR_PF | #1SSTR PF(非取樣點) | OTHER | [5 empty] | 666 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | 2SSTR | #2SSTR |  | LBS | #2SSTR_LBS | [24 empty] | ADCS_S | [8 empty] | 新化DS.#2SSTR_LBS | #2SSTR LBS(非取樣點) | OTHER | [5 empty] | 667 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | 2SSTR | #2SSTR |  | PF | #2SSTR_PF | [24 empty] | ADCS_S | [8 empty] | 新化DS.#2SSTR_PF | #2SSTR PF(非取樣點) | OTHER | [5 empty] | 668 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | KY26 | KY26_DS |  | DS1 | KY26_DS | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY26_DS | KY26_DS (非取樣點) | FEEDER | D15/11/KY26/DS |  |  |  |  | 669 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | KY26 | KY26_ES |  | LE0 | KY26_ES | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY26_ES | KY26_ES (非取樣點) | FEEDER | D15/11/KY26/ES |  |  |  |  | 670 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | KY27 | KY27_DS |  | DS1 | KY27_DS | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY27_DS | KY27_DS (非取樣點) | FEEDER | D15/11/KY27/DS |  |  |  |  | 671 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | KY27 | KY27_ES |  | LE0 | KY27_ES | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY27_ES | KY27_ES (非取樣點) | FEEDER | D15/11/KY27/ES |  |  |  |  | 672 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | KY28 | KY28_DS |  | DS1 | KY28_DS | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY28_DS | KY28_DS (非取樣點) | FEEDER | D15/11/KY28/DS |  |  |  |  | 673 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | KY28 | KY28_ES |  | LE0 | KY28_ES | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY28_ES | KY28_ES (非取樣點) | FEEDER | D15/11/KY28/ES |  |  |  |  | 674 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | KY29 | KY29_DS |  | DS1 | KY29_DS | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY29_DS | KY29_DS (非取樣點) | FEEDER | D15/11/KY29/DS |  |  |  |  | 675 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | KY29 | KY29_ES |  | LE0 | KY29_ES | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY29_ES | KY29_ES (非取樣點) | FEEDER | D15/11/KY29/ES |  |  |  |  | 676 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | KY30 | KY30_DS |  | DS1 | KY30_DS | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY30_DS | KY30_DS (非取樣點) | FEEDER | D15/11/KY30/DS |  |  |  |  | 677 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | KY30 | KY30_ES |  | LE0 | KY30_ES | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY30_ES | KY30_ES (非取樣點) | FEEDER | D15/11/KY30/ES |  |  |  |  | 678 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | KY37 | KY37_DS |  | DS1 | KY37_DS | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY37_DS | KY37_DS (非取樣點) | FEEDER | D15/11/KY37/DS |  |  |  |  | 679 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | KY37 | KY37_ES |  | LE0 | KY37_ES | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY37_ES | KY37_ES (非取樣點) | FEEDER | D15/11/KY37/ES |  |  |  |  | 680 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | KY38 | KY38_DS |  | DS1 | KY38_DS | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY38_DS | KY38_DS (非取樣點) | FEEDER | D15/11/KY38/DS |  |  |  |  | 681 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | KY38 | KY38_ES |  | LE0 | KY38_ES | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY38_ES | KY38_ES (非取樣點) | FEEDER | D15/11/KY38/ES |  |  |  |  | 682 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | KY39 | KY39_DS |  | DS1 | KY39_DS | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY39_DS | KY39_DS (非取樣點) | FEEDER | D15/11/KY39/DS |  |  |  |  | 683 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | KY39 | KY39_ES |  | LE0 | KY39_ES | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY39_ES | KY39_ES (非取樣點) | FEEDER | D15/11/KY39/ES |  |  |  |  | 684 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | KY40 | KY40_DS |  | DS1 | KY40_DS | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY40_DS | KY40_DS (非取樣點) | FEEDER | D15/11/KY40/DS |  |  |  |  | 685 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | KY40 | KY40_ES |  | LE0 | KY40_ES | [24 empty] | DDCS4_2 | [8 empty] | 新化DS.KY40_ES | KY40_ES (非取樣點) | FEEDER | D15/11/KY40/ES |  |  |  |  | 686 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | 100 | TIE(100) |  | DS1 | 100_DS | [24 empty] | ADCS_S | [8 empty] | 新化DS.100_DS | 100_DS (非取樣點) | TIE | D15/11/100/DS |  |  |  |  | 687 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | 200 | TIE(200) |  | DS1 | 200_DS | [24 empty] | ADCS_S | [8 empty] | 新化DS.200_DS | 200_DS (非取樣點) | TIE | D15/11/200/DS |  |  |  |  | 688 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | 210E | 210E |  | 210E | 210E | [24 empty] | ADCS_S | [8 empty] | 新化DS.210E | 210E (非取樣點) | SC | D15/11/210/ES |  |  |  |  | 689 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | 220E | 220E |  | 220E | 220E | [24 empty] | ADCS_S | [8 empty] | 新化DS.220E | 220E (非取樣點) | SC | D15/11/220/ES |  |  |  |  | 690 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | 230E | 230E |  | 230E | 230E | [24 empty] | ADCS_S | [8 empty] | 新化DS.230E | 230E (非取樣點) | SC | D15/11/230/ES |  |  |  |  | 691 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | 240E | 240E |  | 240E | 240E | [24 empty] | ADCS_S | [8 empty] | 新化DS.240E | 240E (非取樣點) | SC | D15/11/240/ES |  |  |  |  | 692 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | 250E | 250E |  | 250E | 250E | [24 empty] | ADCS_S | [8 empty] | 新化DS.250E | 250E (非取樣點) | SC | D15/11/250/ES |  |  |  |  | 693 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | 260E | 260E |  | 260E | 260E | [24 empty] | ADCS_S | [8 empty] | 新化DS.260E | 260E (非取樣點) | SC | D15/11/260/ES |  |  |  |  | 694 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D15 | 新化DS | 0 |  | 1ABUS | 1ABUS |  | PTD | 1ABUS_PTD | [24 empty] | ADCS_S | [8 empty] | 新化DS.1ABUS_PTD | #1ABUS_PTD(非取樣點) | OTHER | [5 empty] | 695 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | 1BBUS | 1BBUS |  | PTD | 1BBUS_PTD | [24 empty] | ADCS_S | [8 empty] | 新化DS.1BBUS_PTD | #1BBUS_PTD(非取樣點) | OTHER | [5 empty] | 696 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | 2ABUS | 2ABUS |  | PTD | 2ABUS_PTD | [24 empty] | ADCS_S | [8 empty] | 新化DS.2ABUS_PTD | #2ABUS_PTD(非取樣點) | OTHER | [5 empty] | 697 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D15 | 新化DS | 0 |  | 2BBUS | 2BBUS |  | PTD | 2BBUS_PTD | [24 empty] | ADCS_S | [8 empty] | 新化DS.2BBUS_PTD | #2BBUS_PTD(非取樣點) | OTHER | [5 empty] | 698 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo