## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D17 | 二甲DS | 161 | 161kV | 1550 | 二甲～奇美實紅線(1550) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D17_A1 | [8 empty] | 二甲DS.1550LE | 1550LE (非取樣點) | LINE161 | [5 empty] | 2 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 1550 | 二甲～奇美實紅線(1550) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D17_A1 | [8 empty] | 二甲DS.1550BE | 1550BE (非取樣點) | LINE161 | [5 empty] | 3 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 1560 | 二甲～奇美實白線(1560) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D17_A1 | [8 empty] | 二甲DS.1560LE | 1560LE (非取樣點) | LINE161 | [5 empty] | 4 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 1560 | 二甲～奇美實白線(1560) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D17_A1 | [8 empty] | 二甲DS.1560BE | 1560BE (非取樣點) | LINE161 | [5 empty] | 5 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 1570 | 仁德～二甲紅線(1570) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D17_A1 | [8 empty] | 二甲DS.1570LE | 1570LE (非取樣點) | LINE161 | [5 empty] | 6 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 1570 | 仁德～二甲紅線(1570) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D17_A1 | [8 empty] | 二甲DS.1570BE | 1570BE (非取樣點) | LINE161 | [5 empty] | 7 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 1580 | 仁德～二甲白線(1580) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D17_A1 | [8 empty] | 二甲DS.1580LE | 1580LE (非取樣點) | LINE161 | [5 empty] | 8 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 1580 | 仁德～二甲白線(1580) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D17_A1 | [8 empty] | 二甲DS.1580BE | 1580BE (非取樣點) | LINE161 | [5 empty] | 9 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D17_A1 | [8 empty] | 二甲DS.1610LE | 1610LE (非取樣點) | LINE161 | [5 empty] | 10 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D17_A1 | [8 empty] | 二甲DS.1610BE | 1610BE (非取樣點) | LINE161 | [5 empty] | 11 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D17_A1 | [8 empty] | 二甲DS.1620LE | 1620LE (非取樣點) | LINE161 | [5 empty] | 12 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D17_A1 | [8 empty] | 二甲DS.1620BE | 1620BE (非取樣點) | LINE161 | [5 empty] | 13 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D17_A1 | [8 empty] | 二甲DS.1501E | 1501E (非取樣點) | TIE | [5 empty] | 14 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D17_A1 | [8 empty] | 二甲DS.1502E | 1502E (非取樣點) | TIE | [5 empty] | 15 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D17_A1 | [8 empty] | 二甲DS.1770TE | 1770TE (非取樣點) | MTR | [5 empty] | 16 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D17_A1 | [8 empty] | 二甲DS.1770BE | 1770BE (非取樣點) | MTR | [5 empty] | 17 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 11 | 11kV | 350 | #3DTR(A)(350) |  | D1 | 351(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D17_A1 | [8 empty] | 二甲DS.351 | 351 (非取樣點) | MTR | [5 empty] | 18 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | 350 | #3DTR(A)(350) |  | E1 | 351E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D17_A1 | [8 empty] | 二甲DS.351E | 351E (非取樣點) | MTR | [5 empty] | 19 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 11 | 11kV | 360 | #3DTR(B)(360) |  | D1 | 361(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D17_A1 | [8 empty] | 二甲DS.361 | 361 (非取樣點) | MTR | [5 empty] | 20 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | 360 | #3DTR(B)(360) |  | E1 | 361E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D17_A1 | [8 empty] | 二甲DS.361E | 361E (非取樣點) | MTR | [5 empty] | 21 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 1780 | #4DTR(1780) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D17_A1 | [8 empty] | 二甲DS.1780TE | 1780TE (非取樣點) | MTR | [5 empty] | 22 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 1780 | #4DTR(1780) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D17_A1 | [8 empty] | 二甲DS.1780BE | 1780BE (非取樣點) | MTR | [5 empty] | 23 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 11 | 11kV | 370 | #4DTR(A)(370) |  | D1 | 371(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D17_A1 | [8 empty] | 二甲DS.371 | 371 (非取樣點) | MTR | [5 empty] | 24 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | 370 | #4DTR(A)(370) |  | E1 | 371E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D17_A1 | [8 empty] | 二甲DS.371E | 371E (非取樣點) | MTR | [5 empty] | 25 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 11 | 11kV | 380 | #4DTR(B)(380) |  | D1 | 381(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D17_A1 | [8 empty] | 二甲DS.381 | 381 (非取樣點) | MTR | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | 380 | #4DTR(B)(380) |  | E1 | 381E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D17_A1 | [8 empty] | 二甲DS.381E | 381E (非取樣點) | MTR | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 11 | 11kV | 250 | #5SC(250) |  | E1 | 251E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D17_A1 | [8 empty] | 二甲DS.251E | 251E (非取樣點) | SC | [5 empty] | 28 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 11 | 11kV | 250 | #5SC(250) |  | D1 | 251(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D17_A1 | [8 empty] | 二甲DS.251 | 251 (非取樣點) | SC | [5 empty] | 29 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | 300 | TIE(300) |  | E1 | 301E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D17_A1 | [8 empty] | 二甲DS.301E | 301E (非取樣點) | TIE | [5 empty] | 30 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 11 | 11kV | 300 | TIE(300) |  | E2 | 302E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D17_A1 | [8 empty] | 二甲DS.302E | 302E (非取樣點) | TIE | [5 empty] | 31 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 11 | 11kV | 300 | TIE(300) |  | D1 | 301(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D17_A1 | [8 empty] | 二甲DS.301 | 301 (非取樣點) | TIE | [5 empty] | 32 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | 300 | TIE(300) |  | D2 | 302(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D17_A1 | [8 empty] | 二甲DS.302 | 302 (非取樣點) | TIE | [5 empty] | 33 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | 390 | #1SSTR(390) |  | D1 | 391(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D17_A1 | [8 empty] | 二甲DS.391 | 391 (非取樣點) | OTHER | [5 empty] | 34 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | 390 | #1SSTR(390) |  | E1 | 391E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D17_A1 | [8 empty] | 二甲DS.391E | 391E (非取樣點) | OTHER | [5 empty] | 35 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 11 | 11kV | 260 | #6SC(260) |  | E1 | 261E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D17_A1 | [8 empty] | 二甲DS.261E | 261E (非取樣點) | SC | [5 empty] | 36 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 11 | 11kV | 260 | #6SC(260) |  | D1 | 261(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D17_A1 | [8 empty] | 二甲DS.261 | 261 (非取樣點) | SC | [5 empty] | 37 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | 400 | TIE(400) |  | E1 | 401E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D17_A1 | [8 empty] | 二甲DS.401E | 401E (非取樣點) | TIE | [5 empty] | 38 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 11 | 11kV | 400 | TIE(400) |  | E2 | 402E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D17_A1 | [8 empty] | 二甲DS.402E | 402E (非取樣點) | TIE | [5 empty] | 39 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 11 | 11kV | 400 | TIE(400) |  | D1 | 401(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D17_A1 | [8 empty] | 二甲DS.401 | 401 (非取樣點) | TIE | [5 empty] | 40 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | 400 | TIE(400) |  | D2 | 402(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D17_A1 | [8 empty] | 二甲DS.402 | 402 (非取樣點) | TIE | [5 empty] | 41 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | 270 | #7SC(270) |  | E1 | 271E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D17_A1 | [8 empty] | 二甲DS.271E | 271E (非取樣點) | SC | [5 empty] | 42 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 11 | 11kV | 270 | #7SC(270) |  | D1 | 271(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D17_A1 | [8 empty] | 二甲DS.271 | 271 (非取樣點) | SC | [5 empty] | 43 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | 280 | #8SC(280) |  | E1 | 281E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D17_A1 | [8 empty] | 二甲DS.281E | 281E (非取樣點) | SC | [5 empty] | 44 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 11 | 11kV | 280 | #8SC(280) |  | D1 | 281(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D17_A1 | [8 empty] | 二甲DS.281 | 281 (非取樣點) | SC | [5 empty] | 45 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | 490 | #2SSTR(490) |  | D1 | 491(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D17_A1 | [8 empty] | 二甲DS.491 | 491 (非取樣點) | OTHER | [5 empty] | 46 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | 490 | #2SSTR(490) |  | E1 | 491E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D17_A1 | [8 empty] | 二甲DS.491E | 491E (非取樣點) | OTHER | [5 empty] | 47 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | 15B1E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aajz | B2/D17_A1 | [8 empty] | 二甲DS.15B1E | 15B1E (非取樣點) | BUS | [5 empty] | 48 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | 15B2E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/2Bus | [13 empty] | aajz | B2/D17_A1 | [8 empty] | 二甲DS.15B2E | 15B2E (非取樣點) | BUS | [5 empty] | 49 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | RTU | RTU |  | ADCL1 |  |  | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% TEST |  |  |  |  | B3/D17_A1 | [16 empty] | 50 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D17 | 二甲DS | 0 |  | RTU | RTU |  | ADCH1 |  |  | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% TEST |  |  |  |  | B3/D17_A1 | [16 empty] | 51 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D17 | 二甲DS | 161 | 161kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 161KV NO.1 BUS 電壓 |  |  | kV_-210_210(-2000_2000) | aaa | B2/D17_A1 | [8 empty] | 二甲DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | [5 empty] | 52 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D17 | 二甲DS | 161 | 161kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0003 |  |  | 1-83 |  |  | 161KV NO.2 BUS 電壓 |  |  | kV_-210_210(-2000_2000) | aab | B2/D17_A1 | [8 empty] | 二甲DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | [5 empty] | 53 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D17 | 二甲DS | 161 | 161kV | 1550 | 二甲～奇美實紅線(1550) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0012 |  |  | 1-8C |  |  | 二甲奇美實紅線1550 瓦 |  |  | MW_-560_560(-2000_2000) |  | B2/D17_A1 | [8 empty] | 二甲DS.1550_MW | 二甲奇美實紅線 MW | LINE161 | [5 empty] | 54 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D17 | 二甲DS | 161 | 161kV | 1550 | 二甲～奇美實紅線(1550) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0013 |  |  | 1-8D |  |  | 二甲奇美實紅線1550 乏 |  |  | MVAR_-560_560(-2000_2000) |  | B2/D17_A1 | [8 empty] | 二甲DS.1550_MVAR | 二甲奇美實紅線 MVAR | LINE161 | [5 empty] | 55 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D17 | 二甲DS | 161 | 161kV | 1560 | 二甲～奇美實白線(1560) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0014 |  |  | 1-8E |  |  | 二甲奇美實白線1560 瓦 |  |  | MW_-560_560(-2000_2000) |  | B2/D17_A1 | [8 empty] | 二甲DS.1560_MW | 二甲奇美實白線 MW | LINE161 | [5 empty] | 56 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D17 | 二甲DS | 161 | 161kV | 1560 | 二甲～奇美實白線(1560) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0015 |  |  | 1-8F |  |  | 二甲奇美實白線1560 乏 |  |  | MVAR_-560_560(-2000_2000) |  | B2/D17_A1 | [8 empty] | 二甲DS.1560_MVAR | 二甲奇美實白線 MVAR | LINE161 | [5 empty] | 57 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D17 | 二甲DS | 161 | 161kV | 1570 | 仁德～二甲紅線(1570) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0016 |  |  | 1-90 |  |  | 仁德二甲紅線1570 瓦 |  |  | MW_-560_560(-2000_2000) |  | B2/D17_A1 | [8 empty] | 二甲DS.1570_MW | 仁德二甲紅線 MW | LINE161 | [5 empty] | 58 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D17 | 二甲DS | 161 | 161kV | 1570 | 仁德～二甲紅線(1570) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0017 |  |  | 1-91 |  |  | 仁德二甲紅線1570 乏 |  |  | MVAR_-560_560(-2000_2000) |  | B2/D17_A1 | [8 empty] | 二甲DS.1570_MVAR | 仁德二甲紅線 MVAR | LINE161 | [5 empty] | 59 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D17 | 二甲DS | 161 | 161kV | 1580 | 仁德～二甲白線(1580) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | 仁德二甲白線1580 瓦 |  |  | MW_-560_560(-2000_2000) |  | B2/D17_A1 | [8 empty] | 二甲DS.1580_MW | 仁德二甲白線 MW | LINE161 | [5 empty] | 60 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D17 | 二甲DS | 161 | 161kV | 1580 | 仁德～二甲白線(1580) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | 仁德二甲白線1580 乏 |  |  | MVAR_-560_560(-2000_2000) |  | B2/D17_A1 | [8 empty] | 二甲DS.1580_MVAR | 仁德二甲白線 MVAR | LINE161 | [5 empty] | 61 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D17 | 二甲DS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | 龍崎山上二甲三路1610 瓦 |  |  | MW_-560_560(-2000_2000) |  | B2/D17_A1 | [8 empty] | 二甲DS.1610_MW | 龍崎山上三路 MW | LINE161 | [5 empty] | 62 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D17 | 二甲DS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | 龍崎山上二甲三路1610 乏 |  |  | MVAR_-560_560(-2000_2000) |  | B2/D17_A1 | [8 empty] | 二甲DS.1610_MVAR | 龍崎山上三路 MVAR | LINE161 | [5 empty] | 63 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D17 | 二甲DS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | 龍崎山上二甲四路1620 瓦 |  |  | MW_-560_560(-2000_2000) |  | B2/D17_A1 | [8 empty] | 二甲DS.1620_MW | 龍崎山上四路 MW | LINE161 | [5 empty] | 64 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D17 | 二甲DS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | 龍崎山上二甲四路1620 乏 |  |  | MVAR_-560_560(-2000_2000) |  | B2/D17_A1 | [8 empty] | 二甲DS.1620_MVAR | 龍崎山上四路 MVAR | LINE161 | [5 empty] | 65 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D17 | 二甲DS | 161 | 161kV | 1500 | TIE(1500) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0024 |  |  | 1-98 |  |  | TIE (1500 ) R 相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/D17_A1 | [8 empty] | 二甲DS.1500TIE_AMP | 1500TIE AMP | TIE | [5 empty] | 66 |  |  |  |  | AI | [5 empty] | C20R1600 | 1520 | 1600 | 1760 | 1968 | 2.27 | -1520 | -1600 | -1760 | -1968 | 1 | 0.01 | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 0 |  | StaDev | 所內設施 |  | DCV_P |  |  | MvMoment | 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | DC 125V P 電壓 |  |  | kV_-150_150(-2000_2000) |  | B3/D17_A1 | [8 empty] | 二甲DS.直流P電源電壓 | 直流P電源電壓 | OTHER | [5 empty] | 67 |  |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 | 0.01 | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D17 | 二甲DS | 0 |  | StaDev | 所內設施 |  | DCV_N |  |  | MvMoment | 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | DC 125V N 電壓 |  |  | kV_-150_150(-2000_2000) |  | B3/D17_A1 | [8 empty] | 二甲DS.直流N電源電壓 | 直流N電源電壓 | OTHER | [5 empty] | 68 |  |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 | 0.01 | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D17 | 二甲DS | 0 |  | RTU | RTU |  | ADCL2 |  |  | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | 10% TEST |  |  |  |  | B3/D17_A1 | [16 empty] | 69 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D17 | 二甲DS | 0 |  | RTU | RTU |  | ADCH2 |  |  | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | 90% TEST |  |  |  |  | B3/D17_A1 | [16 empty] | 70 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D17 | 二甲DS |  |  | 3DTR | #3DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | NO.3 D.TR. 油溫 |  |  | OIL_-120_120(-2000_2000) |  | B1/D17_A1 | [8 empty] | 二甲DS.#3DTR_OIL | #3DTR 油溫 | MTR | [5 empty] | 71 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D17 | 二甲DS |  |  | 3DTR(A) | #3DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | NO.3 D.TR.(A) 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/D17_A1 | [8 empty] | 二甲DS.#3DTR(A)_COIL | #3DTR(A) 線溫 | MTR | [5 empty] | 72 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D17 | 二甲DS |  |  | 3DTR(B) | #3DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | NO.3 D.TR.(B) 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/D17_A1 | [8 empty] | 二甲DS.#3DTR(B)_COIL | #3DTR(B) 線溫 | MTR | [5 empty] | 73 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D17 | 二甲DS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0512 |  | 0000 | 1-30-00 |  | 1-00 | TEST CB ON/OFF |  |  |  |  | ELEM/ALL | [8 empty] | 二甲DS.TEST_CB | TEST CB | OTHER | [5 empty] | 74 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 161 | 161kV | 1550 | 二甲～奇美實紅線(1550) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D17C40R/T1 |  | 0016 |  | 0005 | 1-02-00 |  | 1-05 | 二甲奇美實紅線1550 CB ON/OFF |  | PPU-1 |  | aaaa | B2/D17_A1 | [8 empty] | 二甲DS.1550_CB | 1550(二甲奇美實紅線) CB | LINE161 | [5 empty] | 75 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS |  |  | 4DTR | #4DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | NO.4 D.TR. 油溫 |  |  | OIL_-120_120(-2000_2000) |  | B1/D17_A1 | [8 empty] | 二甲DS.#4DTR_OIL | #4DTR 油溫 | MTR | [5 empty] | 76 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D17 | 二甲DS |  |  | 4DTR(A) | #4DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | NO.4 D.TR.(A) 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/D17_A1 | [8 empty] | 二甲DS.#4DTR(A)_COIL | #4DTR(A) 線溫 | MTR | [5 empty] | 77 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D17 | 二甲DS |  |  | 4DTR(B) | #4DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | NO.4 D.TR.(B) 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/D17_A1 | [8 empty] | 二甲DS.#4DTR(B)_COIL | #4DTR(B) 線溫 | MTR | [5 empty] | 78 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D17 | 二甲DS | 161 | 161kV | 1560 | 二甲～奇美實白線(1560) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D17C40W/T1 |  | 0020 |  | 0006 | 1-02-04 |  | 1-06 | 二甲奇美實白線1560 CB ON/OFF |  | PPU-1 |  | aaba | B2/D17_A1 | [8 empty] | 二甲DS.1560_CB | 1560(二甲奇美實白線) CB | LINE161 | [5 empty] | 79 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 161 | 161kV | 1570 | 仁德～二甲紅線(1570) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D16D17R/T2 |  | 0024 |  | 0007 | 1-03-00 |  | 1-07 | 仁德二甲紅線1570 CB ON/OFF |  | PPU-1 |  | aaca | B2/D17_A1 | [8 empty] | 二甲DS.1570_CB | 1570(仁德二甲紅線) CB | LINE161 | [5 empty] | 80 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | RTU | RTU |  | ADCL3 |  |  | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% TEST |  |  |  |  | B3/D17_A1 | [16 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D17 | 二甲DS | 0 |  | RTU | RTU |  | ADCH3 |  |  | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% TEST |  |  |  |  | B3/D17_A1 | [16 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D17 | 二甲DS | 11 | 11kV | 350 | #3DTR(A)(350) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | 350(M-3A) 瓦 |  |  | MW_-54_54(-2000_2000) |  | B3/D17_A1 | [8 empty] | 二甲DS.#3DTR(A)_MW | #3DTR二次側(A) MW | MTR | [5 empty] | 83 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.054 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.054000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 350 | #3DTR(A)(350) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | 350(M-3A) 乏 |  |  | MVAR_-36_36(-2000_2000) |  | B3/D17_A1 | [8 empty] | 二甲DS.#3DTR(A)_MVAR | #3DTR二次側(A) MVAR | MTR | [5 empty] | 84 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.036 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.036000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 350 | #3DTR(A)(350) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0098 |  |  | 1-E2 |  |  | 350(M-3A) R 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D17_A1 | [8 empty] | 二甲DS.#3DTR(A)_A1 | #3DTR二次側(A) R相AMP | MTR | [5 empty] | 85 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 350 | #3DTR(A)(350) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | 350(M-3A) S 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D17_A1 | [8 empty] | 二甲DS.#3DTR(A)_A2 | #3DTR二次側(A) S相AMP | MTR | [5 empty] | 86 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 350 | #3DTR(A)(350) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | 350(M-3A) T 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D17_A1 | [8 empty] | 二甲DS.#3DTR(A)_A3 | #3DTR二次側(A) T相AMP | MTR | [5 empty] | 87 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 3ABUS | #3ABUS |  | V_R |  | Element | MvMoment | R相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0101 |  |  | 1-E5 |  |  | 11KV-3A BUS R 相電壓 |  |  | kV_-9_9(-2000_2000) | aaa | B3/D17_A1 | [8 empty] | 二甲DS.11KV#3ABUS_KV | 11KV #3ABUS KV | BUS | [5 empty] | 88 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D17 | 二甲DS | 11 | 11kV | F17 | 甲11線(F17) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | 甲11線(F17) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲11線KVAR | 11KV甲11線 KVAR | FEEDER | [5 empty] | 89 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F17 | 甲11線(F17) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | 甲11線(F17) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲11線A1 | 11KV甲11線 R相AMP | FEEDER | [5 empty] | 90 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F17 | 甲11線(F17) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | 甲11線(F17) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲11線A2 | 11KV甲11線 S相AMP | FEEDER | [5 empty] | 91 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F17 | 甲11線(F17) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | 甲11線(F17) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲11線A3 | 11KV甲11線 T相AMP | FEEDER | [5 empty] | 92 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F17 | 甲11線(F17) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | 甲11線(F17) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲11線A0 | 11KV甲11線 N相AMP | FEEDER | [5 empty] | 93 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F18 | 甲12線(F18) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | 甲12線(F18) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲12線KVAR | 11KV甲12線 KVAR | FEEDER | [5 empty] | 94 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F18 | 甲12線(F18) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | 甲12線(F18) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲12線A1 | 11KV甲12線 R相AMP | FEEDER | [5 empty] | 95 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F18 | 甲12線(F18) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | 甲12線(F18) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲12線A2 | 11KV甲12線 S相AMP | FEEDER | [5 empty] | 96 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F18 | 甲12線(F18) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | 甲12線(F18) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲12線A3 | 11KV甲12線 T相AMP | FEEDER | [5 empty] | 97 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F18 | 甲12線(F18) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | 甲12線(F18) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲12線A0 | 11KV甲12線 N相AMP | FEEDER | [5 empty] | 98 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F19 | 甲13線(F19) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | 甲13線(F19) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲13線KVAR | 11KV甲13線 KVAR | FEEDER | [5 empty] | 99 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F19 | 甲13線(F19) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | 甲13線(F19) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲13線A1 | 11KV甲13線 R相AMP | FEEDER | [5 empty] | 100 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F19 | 甲13線(F19) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | 甲13線(F19) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲13線A2 | 11KV甲13線 S相AMP | FEEDER | [5 empty] | 101 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F19 | 甲13線(F19) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | 甲13線(F19) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲13線A3 | 11KV甲13線 T相AMP | FEEDER | [5 empty] | 102 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F19 | 甲13線(F19) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | 甲13線(F19) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲13線A0 | 11KV甲13線 N相AMP | FEEDER | [5 empty] | 103 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F20 | 甲14線(F20) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | 甲14線(F20) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲14線KVAR | 11KV甲14線 KVAR | FEEDER | [5 empty] | 104 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F20 | 甲14線(F20) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | 甲14線(F20) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲14線A1 | 11KV甲14線 R相AMP | FEEDER | [5 empty] | 105 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F20 | 甲14線(F20) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | 甲14線(F20) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲14線A2 | 11KV甲14線 S相AMP | FEEDER | [5 empty] | 106 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F20 | 甲14線(F20) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | 甲14線(F20) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲14線A3 | 11KV甲14線 T相AMP | FEEDER | [5 empty] | 107 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F20 | 甲14線(F20) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | 甲14線(F20) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲14線A0 | 11KV甲14線 N相AMP | FEEDER | [5 empty] | 108 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F21 | 甲15線(F21) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | 甲15線(F21) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲15線KVAR | 11KV甲15線 KVAR | FEEDER | [5 empty] | 109 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F21 | 甲15線(F21) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | 甲15線(F21) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲15線A1 | 11KV甲15線 R相AMP | FEEDER | [5 empty] | 110 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F21 | 甲15線(F21) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | 甲15線(F21) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲15線A2 | 11KV甲15線 S相AMP | FEEDER | [5 empty] | 111 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F21 | 甲15線(F21) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | 甲15線(F21) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲15線A3 | 11KV甲15線 T相AMP | FEEDER | [5 empty] | 112 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F21 | 甲15線(F21) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | 甲15線(F21) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲15線A0 | 11KV甲15線 N相AMP | FEEDER | [5 empty] | 113 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 300 | TIE(300) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | 300(TIE-3A) R 相電流 |  |  | A_-2000_2000(-2000_2000) |  | B3/D17_A1 | [8 empty] | 二甲DS.11KV_300_A1 | 11KV 300 R相AMP | TIE | [5 empty] | 114 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 300 | TIE(300) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 300(TIE-3A) S 相電流 |  | SP | A_-2000_2000(-2000_2000) |  | B3/D17_A1 | [8 empty] | 二甲DS.11KV_300_A2 | 11KV 300 S相AMP | TIE | [5 empty] | 115 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 300 | TIE(300) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 300(TIE-3A) T 相電流 |  | " | A_-2000_2000(-2000_2000) |  | B3/D17_A1 | [8 empty] | 二甲DS.11KV_300_A3 | 11KV 300 T相AMP | TIE | [5 empty] | 116 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 360 | #3DTR(B)(360) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | 360(M-3B) 瓦 |  | " | MW_-54_54(-2000_2000) |  | B3/D17_A1 | [8 empty] | 二甲DS.#3DTR(B)_MW | #3DTR二次側(B) MW | MTR | [5 empty] | 117 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.054 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.054000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 360 | #3DTR(B)(360) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | 360(M-3B) 乏 |  | " | MVAR_-36_36(-2000_2000) |  | B3/D17_A1 | [8 empty] | 二甲DS.#3DTR(B)_MVAR | #3DTR二次側(B) MVAR | MTR | [5 empty] | 118 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.036 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.036000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 360 | #3DTR(B)(360) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | 360(M-3B) R 相電流 |  | " | A_-3000_3000(-2000_2000) |  | B3/D17_A1 | [8 empty] | 二甲DS.#3DTR(B)_A1 | #3DTR二次側(B) R相AMP | MTR | [5 empty] | 119 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 360 | #3DTR(B)(360) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0133 |  |  | 2-85 |  |  | 360(M-3B) S 相電流 |  | " | A_-3000_3000(-2000_2000) |  | B3/D17_A1 | [8 empty] | 二甲DS.#3DTR(B)_A2 | #3DTR二次側(B) S相AMP | MTR | [5 empty] | 120 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 360 | #3DTR(B)(360) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | 360(M-3B) T 相電流 |  | " | A_-3000_3000(-2000_2000) |  | B3/D17_A1 | [8 empty] | 二甲DS.#3DTR(B)_A3 | #3DTR二次側(B) T相AMP | MTR | [5 empty] | 121 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 3BBUS | #3BBUS |  | V_R |  | Element | MvMoment | R相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0135 |  |  | 2-87 |  |  | 11KV-3B BUS R 相電壓 |  | " | kV_-9_9(-2000_2000) | baa | B3/D17_A1 | [8 empty] | 二甲DS.11KV#3BBUS_KV | 11KV #3BBUS KV | BUS | [5 empty] | 122 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D17 | 二甲DS | 11 | 11kV | F22 | 甲21線(F22) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0136 |  |  | 2-88 |  |  | 甲21線(F22) 乏 |  | " | KVAR_-10800_10800(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲21線KVAR | 11KV甲21線 KVAR | FEEDER | [5 empty] | 123 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F22 | 甲21線(F22) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0137 |  |  | 2-89 |  |  | 甲21線(F22) R 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲21線A1 | 11KV甲21線 R相AMP | FEEDER | [5 empty] | 124 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F22 | 甲21線(F22) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0138 |  |  | 2-8A |  |  | 甲21線(F22) S 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲21線A2 | 11KV甲21線 S相AMP | FEEDER | [5 empty] | 125 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F22 | 甲21線(F22) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0139 |  |  | 2-8B |  |  | 甲21線(F22) T 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲21線A3 | 11KV甲21線 T相AMP | FEEDER | [5 empty] | 126 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F22 | 甲21線(F22) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0140 |  |  | 2-8C |  |  | 甲21線(F22) N 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲21線A0 | 11KV甲21線 N相AMP | FEEDER | [5 empty] | 127 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F23 | 甲22線(F23) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0141 |  |  | 2-8D |  |  | 甲22線(F23) 乏 |  | " | KVAR_-10800_10800(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲22線KVAR | 11KV甲22線 KVAR | FEEDER | [5 empty] | 128 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F23 | 甲22線(F23) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0142 |  |  | 2-8E |  |  | 甲22線(F23) R 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲22線A1 | 11KV甲22線 R相AMP | FEEDER | [5 empty] | 129 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F23 | 甲22線(F23) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0143 |  |  | 2-8F |  |  | 甲22線(F23) S 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲22線A2 | 11KV甲22線 S相AMP | FEEDER | [5 empty] | 130 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F23 | 甲22線(F23) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0144 |  |  | 2-90 |  |  | 甲22線(F23) T 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲22線A3 | 11KV甲22線 T相AMP | FEEDER | [5 empty] | 131 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F23 | 甲22線(F23) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0145 |  |  | 2-91 |  |  | 甲22線(F23) N 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲22線A0 | 11KV甲22線 N相AMP | FEEDER | [5 empty] | 132 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F24 | 甲23線(F24) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0146 |  |  | 2-92 |  |  | 甲23線(F24) 乏 |  | " | KVAR_-10800_10800(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲23線KVAR | 11KV甲23線 KVAR | FEEDER | [5 empty] | 133 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F24 | 甲23線(F24) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0147 |  |  | 2-93 |  |  | 甲23線(F24) R 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲23線A1 | 11KV甲23線 R相AMP | FEEDER | [5 empty] | 134 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F24 | 甲23線(F24) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0148 |  |  | 2-94 |  |  | 甲23線(F24) S 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲23線A2 | 11KV甲23線 S相AMP | FEEDER | [5 empty] | 135 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F24 | 甲23線(F24) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0149 |  |  | 2-95 |  |  | 甲23線(F24) T 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲23線A3 | 11KV甲23線 T相AMP | FEEDER | [5 empty] | 136 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F24 | 甲23線(F24) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0150 |  |  | 2-96 |  |  | 甲23線(F24) N 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲23線A0 | 11KV甲23線 N相AMP | FEEDER | [5 empty] | 137 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F25 | 甲24線(F25) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0151 |  |  | 2-97 |  |  | 甲24線(F25) 乏 |  | " | KVAR_-10800_10800(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲24線KVAR | 11KV甲24線 KVAR | FEEDER | [5 empty] | 138 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F25 | 甲24線(F25) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0152 |  |  | 2-98 |  |  | 甲24線(F25) R 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲24線A1 | 11KV甲24線 R相AMP | FEEDER | [5 empty] | 139 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F25 | 甲24線(F25) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0153 |  |  | 2-99 |  |  | 甲24線(F25) S 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲24線A2 | 11KV甲24線 S相AMP | FEEDER | [5 empty] | 140 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F25 | 甲24線(F25) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0154 |  |  | 2-9A |  |  | 甲24線(F25) T 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲24線A3 | 11KV甲24線 T相AMP | FEEDER | [5 empty] | 141 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F25 | 甲24線(F25) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0155 |  |  | 2-9B |  |  | 甲24線(F25) N 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲24線A0 | 11KV甲24線 N相AMP | FEEDER | [5 empty] | 142 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F26 | 甲25線(F26) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0156 |  |  | 2-9C |  |  | 甲25線(F26) 乏 |  | " | KVAR_-10800_10800(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲25線KVAR | 11KV甲25線 KVAR | FEEDER | [5 empty] | 143 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F26 | 甲25線(F26) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0157 |  |  | 2-9D |  |  | 甲25線(F26) R 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲25線A1 | 11KV甲25線 R相AMP | FEEDER | [5 empty] | 144 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F26 | 甲25線(F26) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0158 |  |  | 2-9E |  |  | 甲25線(F26) S 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲25線A2 | 11KV甲25線 S相AMP | FEEDER | [5 empty] | 145 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F26 | 甲25線(F26) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0159 |  |  | 2-9F |  |  | 甲25線(F26) T 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲25線A3 | 11KV甲25線 T相AMP | FEEDER | [5 empty] | 146 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F26 | 甲25線(F26) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0160 |  |  | 2-A0 |  |  | 甲25線(F26) N 相電流 |  | SP | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲25線A0 | 11KV甲25線 N相AMP | FEEDER | [5 empty] | 147 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 400 | TIE(400) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0161 |  |  | 2-A1 |  |  | 400(TIE-3B) R 相電流 |  | " | A_-2000_2000(-2000_2000) |  | B3/D17_A1 | [8 empty] | 二甲DS.11KV_400_A1 | 11KV 400 R相AMP | TIE | [5 empty] | 148 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 400 | TIE(400) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0162 |  |  | 2-A2 |  |  | 400(TIE-3B) S 相電流 |  | " | A_-2000_2000(-2000_2000) |  | B3/D17_A1 | [8 empty] | 二甲DS.11KV_400_A2 | 11KV 400 S相AMP | TIE | [5 empty] | 149 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 400 | TIE(400) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0163 |  |  | 2-A3 |  |  | 400(TIE-3B) T 相電流 |  | " | A_-2000_2000(-2000_2000) |  | B3/D17_A1 | [8 empty] | 二甲DS.11KV_400_A3 | 11KV 400 T相AMP | TIE | [5 empty] | 150 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 370 | #4DTR(A)(370) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0164 |  |  | 2-A4 |  |  | 370(M-4A) 瓦 |  | " | MW_-54_54(-2000_2000) |  | B3/D17_A1 | [8 empty] | 二甲DS.#4DTR(A)_MW | #4DTR二次側(A) MW | MTR | [5 empty] | 151 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.054 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.054000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 370 | #4DTR(A)(370) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0165 |  |  | 2-A5 |  |  | 370(M-4A) 乏 |  | " | MVAR_-36_36(-2000_2000) |  | B3/D17_A1 | [8 empty] | 二甲DS.#4DTR(A)_MVAR | #4DTR二次側(A) MVAR | MTR | [5 empty] | 152 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.036 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.036000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 370 | #4DTR(A)(370) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0166 |  |  | 2-A6 |  |  | 370(M-4A) R 相電流 |  | " | A_-3000_3000(-2000_2000) |  | B3/D17_A1 | [8 empty] | 二甲DS.#4DTR(A)_A1 | #4DTR二次側(A) R相AMP | MTR | [5 empty] | 153 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 370 | #4DTR(A)(370) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0167 |  |  | 2-A7 |  |  | 370(M-4A) S 相電流 |  | " | A_-3000_3000(-2000_2000) |  | B3/D17_A1 | [8 empty] | 二甲DS.#4DTR(A)_A2 | #4DTR二次側(A) S相AMP | MTR | [5 empty] | 154 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 370 | #4DTR(A)(370) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0168 |  |  | 2-A8 |  |  | 370(M-4A) T 相電流 |  | " | A_-3000_3000(-2000_2000) |  | B3/D17_A1 | [8 empty] | 二甲DS.#4DTR(A)_A3 | #4DTR二次側(A) T相AMP | MTR | [5 empty] | 155 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 4ABUS | #4ABUS |  | V_R |  | Element | MvMoment | R相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0169 |  |  | 2-A9 |  |  | 11KV-4A BUS R 相電壓 |  | " | kV_-9_9(-2000_2000) | aba | B3/D17_A1 | [8 empty] | 二甲DS.11KV#4ABUS_KV | 11KV #4ABUS KV | BUS | [5 empty] | 156 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D17 | 二甲DS | 11 | 11kV | F27 | 甲31線(F27) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0170 |  |  | 2-AA |  |  | 甲31線(F27) 乏 |  | " | KVAR_-10800_10800(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲31線KVAR | 11KV甲31線 KVAR | FEEDER | [5 empty] | 157 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F27 | 甲31線(F27) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0171 |  |  | 2-AB |  |  | 甲31線(F27) R 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲31線A1 | 11KV甲31線 R相AMP | FEEDER | [5 empty] | 158 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F27 | 甲31線(F27) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0172 |  |  | 2-AC |  |  | 甲31線(F27) S 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲31線A2 | 11KV甲31線 S相AMP | FEEDER | [5 empty] | 159 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F27 | 甲31線(F27) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0173 |  |  | 2-AD |  |  | 甲31線(F27) T 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲31線A3 | 11KV甲31線 T相AMP | FEEDER | [5 empty] | 160 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F27 | 甲31線(F27) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0174 |  |  | 2-AE |  |  | 甲31線(F27) N 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲31線A0 | 11KV甲31線 N相AMP | FEEDER | [5 empty] | 161 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F28 | 甲32線(F28) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0175 |  |  | 2-AF |  |  | 甲32線(F28) 乏 |  | " | KVAR_-10800_10800(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲32線KVAR | 11KV甲32線 KVAR | FEEDER | [5 empty] | 162 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F28 | 甲32線(F28) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0176 |  |  | 2-B0 |  |  | 甲32線(F28) R 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲32線A1 | 11KV甲32線 R相AMP | FEEDER | [5 empty] | 163 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F28 | 甲32線(F28) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0177 |  |  | 2-B1 |  |  | 甲32線(F28) S 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲32線A2 | 11KV甲32線 S相AMP | FEEDER | [5 empty] | 164 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F28 | 甲32線(F28) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0178 |  |  | 2-B2 |  |  | 甲32線(F28) T 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲32線A3 | 11KV甲32線 T相AMP | FEEDER | [5 empty] | 165 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F28 | 甲32線(F28) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0179 |  |  | 2-B3 |  |  | 甲32線(F28) N 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲32線A0 | 11KV甲32線 N相AMP | FEEDER | [5 empty] | 166 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F29 | 甲33線(F29) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0180 |  |  | 2-B4 |  |  | 甲33線(F29) 乏 |  | " | KVAR_-10800_10800(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲33線KVAR | 11KV甲33線 KVAR | FEEDER | [5 empty] | 167 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F29 | 甲33線(F29) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0181 |  |  | 2-B5 |  |  | 甲33線(F29) R 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲33線A1 | 11KV甲33線 R相AMP | FEEDER | [5 empty] | 168 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F29 | 甲33線(F29) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0182 |  |  | 2-B6 |  |  | 甲33線(F29) S 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲33線A2 | 11KV甲33線 S相AMP | FEEDER | [5 empty] | 169 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F29 | 甲33線(F29) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0183 |  |  | 2-B7 |  |  | 甲33線(F29) T 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲33線A3 | 11KV甲33線 T相AMP | FEEDER | [5 empty] | 170 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F29 | 甲33線(F29) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0184 |  |  | 2-B8 |  |  | 甲33線(F29) N 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲33線A0 | 11KV甲33線 N相AMP | FEEDER | [5 empty] | 171 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F30 | 甲34線(F30) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0185 |  |  | 2-B9 |  |  | 甲34線(F30) 乏 |  | " | KVAR_-10800_10800(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲34線KVAR | 11KV甲34線 KVAR | FEEDER | [5 empty] | 172 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F30 | 甲34線(F30) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0186 |  |  | 2-BA |  |  | 甲34線(F30) R 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲34線A1 | 11KV甲34線 R相AMP | FEEDER | [5 empty] | 173 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F30 | 甲34線(F30) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0187 |  |  | 2-BB |  |  | 甲34線(F30) S 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲34線A2 | 11KV甲34線 S相AMP | FEEDER | [5 empty] | 174 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F30 | 甲34線(F30) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0188 |  |  | 2-BC |  |  | 甲34線(F30) T 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲34線A3 | 11KV甲34線 T相AMP | FEEDER | [5 empty] | 175 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F30 | 甲34線(F30) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0189 |  |  | 2-BD |  |  | 甲34線(F30) N 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲34線A0 | 11KV甲34線 N相AMP | FEEDER | [5 empty] | 176 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F31 | 甲35線(F31) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0190 |  |  | 2-BE |  |  | 甲35線(F31) 乏 |  | " | KVAR_-10800_10800(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲35線KVAR | 11KV甲35線 KVAR | FEEDER | [5 empty] | 177 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F31 | 甲35線(F31) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0191 |  |  | 2-BF |  |  | 甲35線(F31) R 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲35線A1 | 11KV甲35線 R相AMP | FEEDER | [5 empty] | 178 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F31 | 甲35線(F31) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0192 |  |  | 2-C0 |  |  | 甲35線(F31) S 相電流 |  | SP | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲35線A2 | 11KV甲35線 S相AMP | FEEDER | [5 empty] | 179 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F31 | 甲35線(F31) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0193 |  |  | 2-C1 |  |  | 甲35線(F31) T 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲35線A3 | 11KV甲35線 T相AMP | FEEDER | [5 empty] | 180 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F31 | 甲35線(F31) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0194 |  |  | 2-C2 |  |  | 甲35線(F31) N 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲35線A0 | 11KV甲35線 N相AMP | FEEDER | [5 empty] | 181 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 380 | #4DTR(B)(380) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0195 |  |  | 2-C3 |  |  | 380(M-4B) 瓦 |  | " | MW_-54_54(-2000_2000) |  | B3/D17_A1 | [8 empty] | 二甲DS.#4DTR(B)_MW | #4DTR二次側(B) MW | MTR | [5 empty] | 182 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.054 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.054000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 380 | #4DTR(B)(380) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0196 |  |  | 2-C4 |  |  | 380(M-4B) 乏 |  | " | MVAR_-36_36(-2000_2000) |  | B3/D17_A1 | [8 empty] | 二甲DS.#4DTR(B)_MVAR | #4DTR二次側(B) MVAR | MTR | [5 empty] | 183 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.036 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.036000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 380 | #4DTR(B)(380) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0197 |  |  | 2-C5 |  |  | 380(M-4B) R 相電流 |  | " | A_-3000_3000(-2000_2000) |  | B3/D17_A1 | [8 empty] | 二甲DS.#4DTR(B)_A1 | #4DTR二次側(B) R相AMP | MTR | [5 empty] | 184 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 380 | #4DTR(B)(380) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0198 |  |  | 2-C6 |  |  | 380(M-4B) S 相電流 |  | " | A_-3000_3000(-2000_2000) |  | B3/D17_A1 | [8 empty] | 二甲DS.#4DTR(B)_A2 | #4DTR二次側(B) S相AMP | MTR | [5 empty] | 185 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 380 | #4DTR(B)(380) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0199 |  |  | 2-C7 |  |  | 380(M-4B) T 相電流 |  | " | A_-3000_3000(-2000_2000) |  | B3/D17_A1 | [8 empty] | 二甲DS.#4DTR(B)_A3 | #4DTR二次側(B) T相AMP | MTR | [5 empty] | 186 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 4BBUS | #4BBUS |  | V_R |  | Element | MvMoment | R相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0200 |  |  | 2-C8 |  |  | 11KV-4B BUS R 相電壓 |  | " | kV_-9_9(-2000_2000) | bba | B3/D17_A1 | [8 empty] | 二甲DS.11KV#4BBUS_KV | 11KV #4BBUS KV | BUS | [5 empty] | 187 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D17 | 二甲DS | 11 | 11kV | F32 | 甲41線(F32) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0201 |  |  | 2-C9 |  |  | 甲41線(F32) 乏 |  | " | KVAR_-10800_10800(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲41線KVAR | 11KV甲41線 KVAR | FEEDER | [5 empty] | 188 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F32 | 甲41線(F32) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0202 |  |  | 2-CA |  |  | 甲41線(F32) R 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲41線A1 | 11KV甲41線 R相AMP | FEEDER | [5 empty] | 189 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F32 | 甲41線(F32) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0203 |  |  | 2-CB |  |  | 甲41線(F32) S 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲41線A2 | 11KV甲41線 S相AMP | FEEDER | [5 empty] | 190 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F32 | 甲41線(F32) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0204 |  |  | 2-CC |  |  | 甲41線(F32) T 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲41線A3 | 11KV甲41線 T相AMP | FEEDER | [5 empty] | 191 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F32 | 甲41線(F32) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0205 |  |  | 2-CD |  |  | 甲41線(F32) N 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲41線A0 | 11KV甲41線 N相AMP | FEEDER | [5 empty] | 192 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F33 | 甲42線(F33) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0206 |  |  | 2-CE |  |  | 甲42線(F33) 乏 |  | " | KVAR_-10800_10800(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲42線KVAR | 11KV甲42線 KVAR | FEEDER | [5 empty] | 193 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F33 | 甲42線(F33) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0207 |  |  | 2-CF |  |  | 甲42線(F33) R 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲42線A1 | 11KV甲42線 R相AMP | FEEDER | [5 empty] | 194 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F33 | 甲42線(F33) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0208 |  |  | 2-D0 |  |  | 甲42線(F33) S 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲42線A2 | 11KV甲42線 S相AMP | FEEDER | [5 empty] | 195 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F33 | 甲42線(F33) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0209 |  |  | 2-D1 |  |  | 甲42線(F33) T 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲42線A3 | 11KV甲42線 T相AMP | FEEDER | [5 empty] | 196 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F33 | 甲42線(F33) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0210 |  |  | 2-D2 |  |  | 甲42線(F33) N 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲42線A0 | 11KV甲42線 N相AMP | FEEDER | [5 empty] | 197 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F34 | 甲43線(F34) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0211 |  |  | 2-D3 |  |  | 甲43線(F34) 乏 |  | " | KVAR_-10800_10800(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲43線KVAR | 11KV甲43線 KVAR | FEEDER | [5 empty] | 198 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F34 | 甲43線(F34) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0212 |  |  | 2-D4 |  |  | 甲43線(F34) R 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲43線A1 | 11KV甲43線 R相AMP | FEEDER | [5 empty] | 199 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F34 | 甲43線(F34) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0213 |  |  | 2-D5 |  |  | 甲43線(F34) S 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲43線A2 | 11KV甲43線 S相AMP | FEEDER | [5 empty] | 200 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F34 | 甲43線(F34) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0214 |  |  | 2-D6 |  |  | 甲43線(F34) T 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲43線A3 | 11KV甲43線 T相AMP | FEEDER | [5 empty] | 201 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F34 | 甲43線(F34) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0215 |  |  | 2-D7 |  |  | 甲43線(F34) N 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲43線A0 | 11KV甲43線 N相AMP | FEEDER | [5 empty] | 202 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F35 | 甲44線(F35) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0216 |  |  | 2-D8 |  |  | 甲44線(F35) 乏 |  | " | KVAR_-10800_10800(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲44線KVAR | 11KV甲44線 KVAR | FEEDER | [5 empty] | 203 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F35 | 甲44線(F35) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0217 |  |  | 2-D9 |  |  | 甲44線(F35) R 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲44線A1 | 11KV甲44線 R相AMP | FEEDER | [5 empty] | 204 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F35 | 甲44線(F35) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0218 |  |  | 2-DA |  |  | 甲44線(F35) S 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲44線A2 | 11KV甲44線 S相AMP | FEEDER | [5 empty] | 205 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F35 | 甲44線(F35) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0219 |  |  | 2-DB |  |  | 甲44線(F35) T 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲44線A3 | 11KV甲44線 T相AMP | FEEDER | [5 empty] | 206 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F35 | 甲44線(F35) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0220 |  |  | 2-DC |  |  | 甲44線(F35) N 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲44線A0 | 11KV甲44線 N相AMP | FEEDER | [5 empty] | 207 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F36 | 甲45線(F36) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0221 |  |  | 2-DD |  |  | 甲45線(F36) 乏 |  | " | KVAR_-10800_10800(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲45線KVAR | 11KV甲45線 KVAR | FEEDER | [5 empty] | 208 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F36 | 甲45線(F36) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0222 |  |  | 2-DE |  |  | 甲45線(F36) R 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲45線A1 | 11KV甲45線 R相AMP | FEEDER | [5 empty] | 209 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F36 | 甲45線(F36) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0223 |  |  | 2-DF |  |  | 甲45線(F36) S 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲45線A2 | 11KV甲45線 S相AMP | FEEDER | [5 empty] | 210 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F36 | 甲45線(F36) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0224 |  |  | 2-E0 |  |  | 甲45線(F36) T 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲45線A3 | 11KV甲45線 T相AMP | FEEDER | [5 empty] | 211 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | F36 | 甲45線(F36) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0225 |  |  | 2-E1 |  |  | 甲45線(F36) N 相電流 |  | " | A_-600_600(-2000_2000) |  | B2/D17_D1 | [8 empty] | 二甲DS.甲45線A0 | 11KV甲45線 N相AMP | FEEDER | [5 empty] | 212 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 161 | 161kV | 1580 | 仁德～二甲白線(1580) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D16D17W/T2 |  | 0028 |  | 0008 | 1-03-04 |  | 1-08 | 仁德二甲白線1580 CB ON/OFF |  | PPU-1 |  | aada | B2/D17_A1 | [8 empty] | 二甲DS.1580_CB | 1580(仁德二甲白線) CB | LINE161 | [5 empty] | 213 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 161 | 161kV | 1550 | 二甲～奇美實紅線(1550) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0017 |  |  | 1-02-01 |  |  | 二甲奇美實紅線1550 87A1 |  | PPU-1 |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1550_87A1 | 二甲奇美實紅線(1550)#1 87RY | OTHER | [5 empty] | 214 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1550 | 二甲～奇美實紅線(1550) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 |  |  | 1-02-02 |  |  | 二甲奇美實紅線1550 5PHA |  | PPU-1 |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1550_PHA | 二甲奇美實紅線(1550) 相間RY | LINE161 | [5 empty] | 215 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1550 | 二甲～奇美實紅線(1550) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0019 |  |  | 1-02-03 |  |  | 二甲奇美實紅線1550 5GDA |  | PPU-1 |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1550_GDA | 二甲奇美實紅線(1550) 接地RY | LINE161 | [5 empty] | 216 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D17TN113/T2 |  | 0032 |  | 0009 | 1-04-00 |  | 1-09 | 龍崎山上二甲三路1610 CB ON/OFF |  | PPU-1 |  | aaga | B2/D17_A1 | [8 empty] | 二甲DS.1610_CB | 1610(龍崎山上三路) CB | LINE161 | [5 empty] | 217 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 161 | 161kV | 1560 | 二甲～奇美實白線(1560) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-05 |  |  | 二甲奇美實白線1560 87A1 |  | PPU-1 |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1560_87A1 | 二甲奇美實白線(1560)#1 87RY | OTHER | [5 empty] | 218 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1560 | 二甲～奇美實白線(1560) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0022 |  |  | 1-02-06 |  |  | 二甲奇美實白線1560 6PHA |  | PPU-1 |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1560_PHA | 二甲奇美實白線(1560) 相間RY | LINE161 | [5 empty] | 219 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1560 | 二甲～奇美實白線(1560) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0023 |  |  | 1-02-07 |  |  | 二甲奇美實白線1560 6GDA |  | PPU-1 |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1560_GDA | 二甲奇美實白線(1560) 接地RY | LINE161 | [5 empty] | 220 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D17TN124/T2 |  | 0036 |  | 0010 | 1-04-04 |  | 1-0A | 龍崎山上二甲四路1620 CB ON/OFF |  | PPU-1 |  | aaha | B2/D17_A1 | [8 empty] | 二甲DS.1620_CB | 1620(龍崎山上四路) CB | LINE161 | [5 empty] | 221 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 161 | 161kV | 1570 | 仁德～二甲紅線(1570) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0025 |  |  | 1-03-01 |  |  | 仁德二甲紅線1570 787A |  | PPU-1 |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1570_87A | 仁德二甲紅線(1570) 87RY | LINE161 | [5 empty] | 222 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1570 | 仁德～二甲紅線(1570) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0026 |  |  | 1-03-02 |  |  | 仁德二甲紅線1570 7PHA |  | PPU-1 |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1570_PHA | 仁德二甲紅線(1570) 相間RY | LINE161 | [5 empty] | 223 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1570 | 仁德～二甲紅線(1570) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0027 |  |  | 1-03-03 |  |  | 仁德二甲紅線1570 7GDA |  | PPU-1 |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1570_GDA | 仁德二甲紅線(1570) 接地RY | LINE161 | [5 empty] | 224 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0040 |  | 0011 | 1-05-00 |  | 1-0B | 1500 CB ON/OFF |  | PPU-1 |  | aaez | B2/D17_A1 | [8 empty] | 二甲DS.1500_CB | 1500(TIE) CB | TIE | [5 empty] | 225 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 161 | 161kV | 1580 | 仁德～二甲白線(1580) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0029 |  |  | 1-03-05 |  |  | 仁德二甲白線1580 887A |  | PPU-1 |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1580_87A | 仁德二甲白線(1580) 87RY | LINE161 | [5 empty] | 226 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1580 | 仁德～二甲白線(1580) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0030 |  |  | 1-03-06 |  |  | 仁德二甲白線1580 8PHA |  | PPU-1 |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1580_PHA | 仁德二甲白線(1580) 相間RY | LINE161 | [5 empty] | 227 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1580 | 仁德～二甲白線(1580) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0031 |  |  | 1-03-07 |  |  | 仁德二甲白線1580 8GDA |  | PPU-1 |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1580_GDA | 仁德二甲白線(1580) 接地RY | LINE161 | [5 empty] | 228 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/3DTR |  | 0070 |  | 0014 | 1-08-06 |  | 1-0E | 1770 CB ON/OFF |  | PPU-2 |  | aafb | ELEM/D17_A1 | [8 empty] | 二甲DS.1770_CB | 1770(#3DTR) CB | MTR | [5 empty] | 229 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0033 |  |  | 1-04-01 |  |  | 龍崎山上二甲三路1610 987A |  | PPU-1 |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1610_87A | 龍崎山上三路(1610) 87RY | LINE161 | [5 empty] | 230 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0034 |  |  | 1-04-02 |  |  | 龍崎山上二甲三路1610 9PHA |  | PPU-1 |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1610_PHA | 龍崎山上三路(1610) 相間RY | LINE161 | [5 empty] | 231 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0035 |  |  | 1-04-03 |  |  | 龍崎山上二甲三路1610 9GDA |  | PPU-1 |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1610_GDA | 龍崎山上三路(1610) 接地RY | LINE161 | [5 empty] | 232 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1780 | #4DTR(1780) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/4DTR |  | 0086 |  | 0015 | 1-0A-06 |  | 1-0F | 1780 CB ON/OFF |  | PPU-2 |  | aaib | ELEM/D17_A1 | [8 empty] | 二甲DS.1780_CB | 1780(#4DTR) CB | MTR | [5 empty] | 233 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0037 |  |  | 1-04-05 |  |  | 龍崎山上二甲四路1620 1087A |  | PPU-1 |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1620_87A | 龍崎山上四路(1620) 87RY | LINE161 | [5 empty] | 234 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0038 |  |  | 1-04-06 |  |  | 龍崎山上二甲四路1620 10PHA |  | PPU-1 |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1620_PHA | 龍崎山上四路(1620) 相間RY | LINE161 | [5 empty] | 235 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | 350 | #3DTR(A)(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3ABus | T/3DTR(A) |  |  | 0078 |  | 0018 | 1-09-06 |  | 1-12 | 350(M3A) CB ON/OFF |  | PPU-2 |  | aaba | ELEM/D17_A1 | [8 empty] | 二甲DS.350_CB | 350(#3DTR) CB | MTR | [5 empty] | 236 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | 360 | #3DTR(B)(360) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3BBus | T/3DTR(B) |  |  | 0082 |  | 0019 | 1-0A-02 |  | 1-13 | 360(M3B) CB ON/OFF |  | PPU-2 |  | baaa | ELEM/D17_A1 | [8 empty] | 二甲DS.360_CB | 360(#3DTR) CB | MTR | [5 empty] | 237 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0041 |  |  | 1-05-01 |  |  | 1500 50A |  | PPU-1 |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1500_50A | 161KV TIE(1500) 50RY | TIE | [5 empty] | 238 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0042 |  |  | 1-05-02 |  |  | 87B1A |  | PPU-1 |  |  | B2/D17_A1 | [8 empty] | 二甲DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | [5 empty] | 239 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0043 |  |  | 1-05-03 |  | 1-3D | 87B2A |  | PPU-1 |  |  | B2/D17_A1 | [8 empty] | 二甲DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | [5 empty] | 240 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0045 |  |  | 1-05-05 |  |  | 161KV RCA |  | PPU-1 |  |  | B3/D17_A1 | [8 empty] | 二甲DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | [5 empty] | 241 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | 370 | #4DTR(A)(370) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4ABus | T/4DTR(A) |  |  | 0094 |  | 0020 | 1-0B-06 |  | 1-14 | 370(M4A) CB ON/OFF |  | PPU-2 |  | abaa | ELEM/D17_A1 | [8 empty] | 二甲DS.370_CB | 370(#4DTR) CB | MTR | [5 empty] | 242 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS |  |  | 3DTR | #3DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0071 |  |  | 1-08-07 |  |  | NO.3 DTR 87A |  | PPU-2 |  |  | B1/D17_A1 | [8 empty] | 二甲DS.#3DTR_87A | #3DTR 87RY | MTR | [5 empty] | 243 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS |  |  | 3DTR | #3DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0072 |  |  | 1-09-00 |  |  | NO.3 DTR 96A |  | PPU-2 |  |  | B1/D17_A1 | [8 empty] | 二甲DS.#3DTR_96PA | #3DTR 機械保護動作 | MTR | [5 empty] | 244 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS |  |  | 3DTR | #3DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0073 |  |  | 1-09-01 |  |  | NO.3 DTR 51ZA |  | PPU-2 |  |  | B1/D17_A1 | [8 empty] | 二甲DS.#3DTR_51ZA | #3DTR 51Z RY | MTR | [5 empty] | 245 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS |  |  | 3DTR | #3DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-09-02 |  |  | NO.3 DTR PHA |  | PPU-2 |  |  | B1/D17_A1 | [8 empty] | 二甲DS.#3DTR_51A | #3DTR 51RY | MTR | [5 empty] | 246 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS |  |  | 3DTR | #3DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0075 |  |  | 1-09-03 |  |  | NO.3 DTR GDA |  | PPU-2 |  |  | B1/D17_A1 | [8 empty] | 二甲DS.#3DTR_51NA | #3DTR 51N RY | MTR | [5 empty] | 247 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | 350 | #3DTR(A)(350) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0076 |  |  | 1-09-04 |  |  | 350(M3A) PHA(51-3ψ) |  | PPU-2 |  |  | B3/D17_A1 | [8 empty] | 二甲DS.350_51A | #3DTR二次側(350) 51RY | MTR | [5 empty] | 248 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | 360 | #3DTR(B)(360) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0077 |  |  | 1-09-05 |  |  | 360(M3B) PHA(51-3ψ) |  | PPU-2 |  |  | B3/D17_A1 | [8 empty] | 二甲DS.360_51A | #3DTR二次側(360) 51RY | MTR | [5 empty] | 249 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | 380 | #4DTR(B)(380) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4BBus | T/4DTR(B) |  |  | 0098 |  | 0021 | 1-0C-02 |  | 1-15 | 380(M4B) CB ON/OFF |  | PPU-3 |  | bbba | ELEM/D17_A1 | [8 empty] | 二甲DS.380_CB | 380(#4DTR) CB | MTR | [5 empty] | 250 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | 350 | #3DTR(A)(350) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0079 |  |  | 1-09-07 |  |  | 350(M3A) PHA |  | PPU-2 |  |  | B3/D17_A1 | [8 empty] | 二甲DS.350_PHA2 | 350開關箱IED RY PHA | OTHER | [5 empty] | 251 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | 350 | #3DTR(A)(350) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0080 |  |  | 1-0A-00 |  |  | 350(M3A) GDA |  | PPU-2 |  |  | B3/D17_A1 | [8 empty] | 二甲DS.350_GDA | 350開關箱IED RY GDA | OTHER | [5 empty] | 252 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | 350 | #3DTR(A)(350) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0081 |  |  | 1-0A-01 |  |  | 350(M3A) 81A |  | PPU-2 |  |  | ELEM/D17_A1 | [8 empty] | 二甲DS.350_81A | 350 #3DTR(A) 81RY動作 | OTHER | [5 empty] | 253 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1550 | 二甲～奇美實紅線(1550) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0594 |  | 0032 | 1-35-02 |  | 1-20 | 二甲奇美實紅線1550 87UL1 |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1550_87UL1 | 二甲奇美實紅線(1550)#187RY U/L | OTHER | [5 empty] | 254 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | 360 | #3DTR(B)(360) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0083 |  |  | 1-0A-03 |  |  | 360(M3B) PHA |  | PPU-2 |  |  | B3/D17_A1 | [8 empty] | 二甲DS.360_PHA2 | 360開關箱IED RY PHA | OTHER | [5 empty] | 255 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | 360 | #3DTR(B)(360) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0084 |  |  | 1-0A-04 |  |  | 360(M3B) GDA |  | PPU-2 |  |  | B3/D17_A1 | [8 empty] | 二甲DS.360_GDA | 360開關箱IED RY GDA | OTHER | [5 empty] | 256 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | 360 | #3DTR(B)(360) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0085 |  |  | 1-0A-05 |  |  | 360(M3B) 81A |  | PPU-2 |  |  | ELEM/D17_A1 | [8 empty] | 二甲DS.360_81A | 360 #3DTR(B) 81RY動作 | OTHER | [5 empty] | 257 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1550 | 二甲～奇美實紅線(1550) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0595 |  | 0033 | 1-35-03 |  | 1-21 | 二甲奇美實紅線1550 87UL2 |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1550_87UL2 | 二甲奇美實紅線(1550)#287RY U/L | OTHER | [5 empty] | 258 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS |  |  | 4DTR | #4DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0087 |  |  | 1-0A-07 |  |  | NO.4 DTR 87A |  | PPU-2 |  |  | B1/D17_A1 | [8 empty] | 二甲DS.#4DTR_87A | #4DTR 87RY | MTR | [5 empty] | 259 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS |  |  | 4DTR | #4DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0088 |  |  | 1-0B-00 |  |  | NO.4 DTR 96A |  | PPU-2 |  |  | B1/D17_A1 | [8 empty] | 二甲DS.#4DTR_96PA | #4DTR 機械保護動作 | MTR | [5 empty] | 260 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS |  |  | 4DTR | #4DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0089 |  |  | 1-0B-01 |  |  | NO.4 DTR 51ZA |  | PPU-2 |  |  | B1/D17_A1 | [8 empty] | 二甲DS.#4DTR_51ZA | #4DTR 51Z RY | MTR | [5 empty] | 261 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS |  |  | 4DTR | #4DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0090 |  |  | 1-0B-02 |  |  | NO.4 DTR PHA |  | PPU-2 |  |  | B1/D17_A1 | [8 empty] | 二甲DS.#4DTR_51A | #4DTR 51RY | MTR | [5 empty] | 262 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS |  |  | 4DTR | #4DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0091 |  |  | 1-0B-03 |  |  | NO.4 DTR GDA |  | PPU-2 |  |  | B1/D17_A1 | [8 empty] | 二甲DS.#4DTR_51NA | #4DTR 51N RY | MTR | [5 empty] | 263 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | 370 | #4DTR(A)(370) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0092 |  |  | 1-0B-04 |  |  | 370(M4A) PHA(51-3ψ) |  | PPU-2 |  |  | B3/D17_A1 | [8 empty] | 二甲DS.370_51A | #4DTR二次側(370) 51RY | MTR | [5 empty] | 264 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | 380 | #4DTR(B)(380) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0093 |  |  | 1-0B-05 |  |  | 380(M4B) PHA(51-3ψ) |  | PPU-2 |  |  | B3/D17_A1 | [8 empty] | 二甲DS.380_51A | #4DTR二次側(380) 51RY | MTR | [5 empty] | 265 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1560 | 二甲～奇美實白線(1560) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0596 |  | 0034 | 1-35-04 |  | 1-22 | 二甲奇美實白線1560 87UL1 |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1560_87UL1 | 二甲奇美實白線(1560)#187RY U/L | OTHER | [5 empty] | 266 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | 370 | #4DTR(A)(370) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0095 |  |  | 1-0B-07 |  |  | 370(M4A) PHA |  | PPU-2 |  |  | B3/D17_A1 | [8 empty] | 二甲DS.370_PHA2 | 370開關箱IED RY PHA | OTHER | [5 empty] | 267 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | 370 | #4DTR(A)(370) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0096 |  |  | 1-0C-00 |  |  | 370(M4A) GDA |  | PPU-3 |  |  | B3/D17_A1 | [8 empty] | 二甲DS.370_GDA | 370開關箱IED RY GDA | OTHER | [5 empty] | 268 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | 370 | #4DTR(A)(370) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0097 |  |  | 1-0C-01 |  |  | 370(M4A) 81A |  | PPU-3 |  |  | ELEM/D17_A1 | [8 empty] | 二甲DS.370_81A | 370 #4DTR(A) 81RY動作 | OTHER | [5 empty] | 269 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1560 | 二甲～奇美實白線(1560) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0597 |  | 0035 | 1-35-05 |  | 1-23 | 二甲奇美實白線1560 87UL2 |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1560_87UL2 | 二甲奇美實白線(1560)#287RY U/L | OTHER | [5 empty] | 270 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | 380 | #4DTR(B)(380) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0099 |  |  | 1-0C-03 |  |  | 380(M4B) PHA |  | PPU-3 |  |  | B3/D17_A1 | [8 empty] | 二甲DS.380_PHA2 | 380開關箱IED RY PHA | OTHER | [5 empty] | 271 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | 380 | #4DTR(B)(380) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0100 |  |  | 1-0C-04 |  |  | 380(M4B) GDA |  | PPU-3 |  |  | B3/D17_A1 | [8 empty] | 二甲DS.380_GDA | 380開關箱IED RY GDA | OTHER | [5 empty] | 272 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | 380 | #4DTR(B)(380) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0101 |  |  | 1-0C-05 |  |  | 380(M4B) 81A |  | PPU-3 |  |  | ELEM/D17_A1 | [8 empty] | 二甲DS.380_81A | 380 #4DTR(B) 81RY動作 | OTHER | [5 empty] | 273 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | RTU | RTU |  | RTU_MCT |  |  | Status | RTU Master Ry | Open/Close | Y | E | DI-SP | [6 empty] | 0108 |  |  | 1-0D-04 |  |  | RTU MASTER Ry SOE |  | PPU-3 |  |  | B3/D17_A1 | [16 empty] | 274 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D17 | 二甲DS | 0 |  | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0109 |  |  | 1-0D-05 |  |  | OSCA1 示波器啟動 |  | PPU-3 |  |  | B3/D17_A1 | [8 empty] | 二甲DS.161KV_OSCA_1 | 161KV示波器啟動警報 | OTHER | [5 empty] | 275 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0110 |  |  | 1-0D-06 |  |  | OSCA2 示波器故障 |  | PPU-3 |  |  | B3/D17_A1 | [8 empty] | 二甲DS.161KV_OSCF_1 | 161KV示波器故障 | OTHER | [5 empty] | 276 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | ComPoint |  |  | 1A5Other | OSCPF | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0111 |  |  | 1-0D-07 |  |  | OSCA3 示波器DC fail |  | PPU-3 |  |  | B3/D17_A1 | [8 empty] | 二甲DS.161KV_OSCF_2 | 161KV示波器啟DC故障 | OTHER | [5 empty] | 277 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1550 | 二甲～奇美實紅線(1550) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0112 |  |  | 1-0E-00 |  |  | 二甲奇美實紅線1550 87A2 |  | PPU-3 |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1550_87A2 | 二甲奇美實紅線(1550)#2 87RY | OTHER | [5 empty] | 278 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1560 | 二甲～奇美實白線(1560) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0113 |  |  | 1-0E-01 |  |  | 二甲奇美實白線1560 87A2 |  | PPU-3 |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1560_87A2 | 二甲奇美實白線(1560)#2 87RY | OTHER | [5 empty] | 279 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1570 | 仁德～二甲紅線(1570) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0598 |  | 0036 | 1-35-06 |  | 1-24 | 仁德二甲紅線1570 87S |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1570_87UL | 仁德二甲紅線(1570) 87RY U/L | LINE161 | [5 empty] | 280 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | F17 | 甲11線(F17) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0327 |  |  | 2-08-07 |  |  | 甲11線(F17) PHA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K611_PHA | 11KV甲11線(K611) 相間RY | FEEDER | [5 empty] | 281 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F17 | 甲11線(F17) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0328 |  |  | 2-09-00 |  |  | 甲11線(F17) GDA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K611_GDA | 11KV甲11線(K611) 接地RY | FEEDER | [5 empty] | 282 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F17 | 甲11線(F17) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0329 |  |  | 2-09-01 |  |  | 甲11線(F17) 81A |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K611_81A | 11KV甲11線(K611) 81RY | OTHER | [5 empty] | 283 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1570 | 仁德～二甲紅線(1570) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0599 |  | 0037 | 1-35-07 |  | 1-25 | 仁德二甲紅線1570 79S |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1570_79UL | 仁德二甲紅線(1570) 79RY U/L | LINE161 | [5 empty] | 284 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | F18 | 甲12線(F18) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0331 |  |  | 2-09-03 |  |  | 甲12線(F18) PHA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K612_PHA | 11KV甲12線(K612) 相間RY | FEEDER | [5 empty] | 285 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F18 | 甲12線(F18) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0332 |  |  | 2-09-04 |  |  | 甲12線(F18) GDA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K612_GDA | 11KV甲12線(K612) 接地RY | FEEDER | [5 empty] | 286 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F18 | 甲12線(F18) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0333 |  |  | 2-09-05 |  |  | 甲12線(F18) 81A |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K612_81A | 11KV甲12線(K612) 81RY | OTHER | [5 empty] | 287 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1580 | 仁德～二甲白線(1580) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0600 |  | 0038 | 1-35-08 |  | 1-26 | 仁德二甲白線1580 87S |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1580_87UL | 仁德二甲白線(1580) 87RY U/L | LINE161 | [5 empty] | 288 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | F19 | 甲13線(F19) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0335 |  |  | 2-09-07 |  |  | 甲13線(F19) PHA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K613_PHA | 11KV甲13線(K613) 相間RY | FEEDER | [5 empty] | 289 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F19 | 甲13線(F19) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0336 |  |  | 2-0A-00 |  |  | 甲13線(F19) GDA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K613_GDA | 11KV甲13線(K613) 接地RY | FEEDER | [5 empty] | 290 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F19 | 甲13線(F19) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0337 |  |  | 2-0A-01 |  |  | 甲13線(F19) 81A |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K613_81A | 11KV甲13線(K613) 81RY | OTHER | [5 empty] | 291 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1580 | 仁德～二甲白線(1580) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0601 |  | 0039 | 1-35-09 |  | 1-27 | 仁德二甲白線1580 79S |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1580_79UL | 仁德二甲白線(1580) 79RY U/L | LINE161 | [5 empty] | 292 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | F20 | 甲14線(F20) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0339 |  |  | 2-0A-03 |  |  | 甲14線(F20) PHA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K614_PHA | 11KV甲14線(K614) 相間RY | FEEDER | [5 empty] | 293 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F20 | 甲14線(F20) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0340 |  |  | 2-0A-04 |  |  | 甲14線(F20) GDA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K614_GDA | 11KV甲14線(K614) 接地RY | FEEDER | [5 empty] | 294 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F20 | 甲14線(F20) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0341 |  |  | 2-0A-05 |  |  | 甲14線(F20) 81A |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K614_81A | 11KV甲14線(K614) 81RY | OTHER | [5 empty] | 295 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0602 |  | 0040 | 1-35-10 |  | 1-28 | 龍崎山上二甲三路1610 87S |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1610_87UL | 龍崎山上三路(1610) 87RY U/L | LINE161 | [5 empty] | 296 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | F21 | 甲15線(F21) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0343 |  |  | 2-0A-07 |  |  | 甲15線(F21) PHA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K615_PHA | 11KV甲15線(K615) 相間RY | FEEDER | [5 empty] | 297 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F21 | 甲15線(F21) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0344 |  |  | 2-0B-00 |  |  | 甲15線(F21) GDA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K615_GDA | 11KV甲15線(K615) 接地RY | FEEDER | [5 empty] | 298 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F21 | 甲15線(F21) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0345 |  |  | 2-0B-01 |  |  | 甲15線(F21) 81A |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K615_81A | 11KV甲15線(K615) 81RY | OTHER | [5 empty] | 299 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0603 |  | 0041 | 1-35-11 |  | 1-29 | 龍崎山上二甲三路1610 79S |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1610_79UL | 龍崎山上三路(1610) 79RY U/L | LINE161 | [5 empty] | 300 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | 250 | #5SC(250) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0347 |  |  | 2-0B-03 |  |  | 250(SC-5) SCA |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.250_SCA | 11KV #5SC 51,51N RY | SC | [5 empty] | 301 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | 250 | #5SC(250) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0348 |  |  | 2-0B-04 |  |  | 250(SC-5) UVA |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.250_OUVA | 11KV #5SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 302 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0604 |  | 0042 | 1-35-12 |  | 1-2A | 龍崎山上二甲四路1620 87S |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1620_87UL | 龍崎山上四路(1620) 87RY U/L | LINE161 | [5 empty] | 303 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | 300 | TIE(300) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0350 |  |  | 2-0B-06 |  |  | 300(TIE-3A ) PHA |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.300_51A | 11KV TIE(300) 51RY | TIE | [5 empty] | 304 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | 300 | TIE(300) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0351 |  |  | 2-0B-07 |  |  | 300(TIE-3A ) GDA |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.300_51NA | 11KV TIE(300) 51N RY | TIE | [5 empty] | 305 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0605 |  | 0043 | 1-35-13 |  | 1-2B | 龍崎山上二甲四路1620 79S |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1620_79UL | 龍崎山上四路(1620) 79RY U/L | LINE161 | [5 empty] | 306 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | 390 | #1SSTR(390) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0353 |  |  | 2-0C-01 |  |  | 390(SSTR1 ) PHA |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.#1SSTR_51A | #1SSTR 51RY | OTHER | [5 empty] | 307 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | 390 | #1SSTR(390) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0354 |  |  | 2-0C-02 |  |  | 390(SSTR1 ) GDA |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | [5 empty] | 308 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0538 |  | 0044 | 1-31-10 |  | 1-2C | 161KV #1BUS 87RY U/L（87B1S） |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | BUS | [5 empty] | 309 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | F22 | 甲21線(F22) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0356 |  |  | 2-0C-04 |  |  | 甲21線(F22) PHA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K621_PHA | 11KV甲21線(K621) 相間RY | FEEDER | [5 empty] | 310 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F22 | 甲21線(F22) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0357 |  |  | 2-0C-05 |  |  | 甲21線(F22) GDA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K621_GDA | 11KV甲21線(K621) 接地RY | FEEDER | [5 empty] | 311 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F22 | 甲21線(F22) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0358 |  |  | 2-0C-06 |  |  | 甲21線(F22) 81A |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K621_81A | 11KV甲21線(K621) 81RY | OTHER | [5 empty] | 312 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0539 |  | 0045 | 1-31-11 |  | 1-2D | 161KV #2BUS 87RY U/L（87B2S） |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | BUS | [5 empty] | 313 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | F23 | 甲22線(F23) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0360 |  |  | 2-0D-00 |  |  | 甲22線(F23) PHA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K622_PHA | 11KV甲22線(K622) 相間RY | FEEDER | [5 empty] | 314 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F23 | 甲22線(F23) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0361 |  |  | 2-0D-01 |  |  | 甲22線(F23) GDA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K622_GDA | 11KV甲22線(K622) 接地RY | FEEDER | [5 empty] | 315 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F23 | 甲22線(F23) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0362 |  |  | 2-0D-02 |  |  | 甲22線(F23) 81A |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K622_81A | 11KV甲22線(K622) 81RY | OTHER | [5 empty] | 316 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0039 |  | 0059 | 1-04-07 |  | 1-3B | 龍崎山上二甲四路1620 10GDA |  | PPU-1 |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1620_GDA | 龍崎山上四路(1620) 接地RY | LINE161 | [5 empty] | 317 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F24 | 甲23線(F24) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0364 |  |  | 2-0D-04 |  |  | 甲23線(F24) PHA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K623_PHA | 11KV甲23線(K623) 相間RY | FEEDER | [5 empty] | 318 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F24 | 甲23線(F24) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0365 |  |  | 2-0D-05 |  |  | 甲23線(F24) GDA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K623_GDA | 11KV甲23線(K623) 接地RY | FEEDER | [5 empty] | 319 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F24 | 甲23線(F24) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0366 |  |  | 2-0D-06 |  |  | 甲23線(F24) 81A |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K623_81A | 11KV甲23線(K623) 81RY | OTHER | [5 empty] | 320 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS |  |  | 3DTR(A) | #3DTR(A) |  | Tap Chan |  | B3,Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0526 |  | 0060 | 1-30-14 |  | 1-3C | NO.3A DTR OLTC A/M |  |  |  |  | B1/D17_A1 | [8 empty] | 二甲DS.#3DTR(A)_A/M | #3DTR(A) OLTC A/M | MTR | [5 empty] | 321 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D17 | 二甲DS | 11 | 11kV | F25 | 甲24線(F25) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0368 |  |  | 2-0E-00 |  |  | 甲24線(F25) PHA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K624_PHA | 11KV甲24線(K624) 相間RY | FEEDER | [5 empty] | 322 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F25 | 甲24線(F25) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0369 |  |  | 2-0E-01 |  |  | 甲24線(F25) GDA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K624_GDA | 11KV甲24線(K624) 接地RY | FEEDER | [5 empty] | 323 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F25 | 甲24線(F25) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0370 |  |  | 2-0E-02 |  |  | 甲24線(F25) 81A |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K624_81A | 11KV甲24線(K624) 81RY | OTHER | [5 empty] | 324 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS |  |  | 3DTR(A) | #3DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0043 |  | 0061 | 1-AB |  | 1-3D | NO.3 D.TR.(A) TAP |  | 對應CO-62/1 | TAP_-8.5_8.5(0_2000) |  | B1/D17_A1 | [8 empty] | 二甲DS.#3DTR(A)_TAP | #3DTR(A) OLTC TAP | MTR | [5 empty] | 325 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D17 | 二甲DS | 11 | 11kV | F26 | 甲25線(F26) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0372 |  |  | 2-0E-04 |  |  | 甲25線(F26) PHA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K625_PHA | 11KV甲25線(K625) 相間RY | FEEDER | [5 empty] | 326 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F26 | 甲25線(F26) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0373 |  |  | 2-0E-05 |  |  | 甲25線(F26) GDA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K625_GDA | 11KV甲25線(K625) 接地RY | FEEDER | [5 empty] | 327 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F26 | 甲25線(F26) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0374 |  |  | 2-0E-06 |  |  | 甲25線(F26) 81A |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K625_81A | 11KV甲25線(K625) 81RY | OTHER | [5 empty] | 328 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS |  |  | 3DTR(B) | #3DTR(B) |  | Tap Chan |  | B3,Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0530 |  | 0062 | 1-31-02 |  | 1-3E | NO.3B DTR OLTC A/M |  |  |  |  | B1/D17_A1 | [8 empty] | 二甲DS.#3DTR(B)_A/M | #3DTR(B) OLTC A/M | MTR | [5 empty] | 329 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D17 | 二甲DS | 11 | 11kV | 260 | #6SC(260) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0376 |  |  | 2-0F-00 |  |  | 260(SC-6) SCA |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.260_SCA | 11KV #6SC 51,51N RY | SC | [5 empty] | 330 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | 260 | #6SC(260) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0377 |  |  | 2-0F-01 |  |  | 260(SC-6) UVA |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.260_OUVA | 11KV #6SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 331 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS |  |  | 3DTR(B) | #3DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0044 |  | 0063 | 1-AC |  | 1-3F | NO.3 D.TR.(B) TAP |  | 對應CO-64/1 | TAP_-8.5_8.5(0_2000) |  | B1/D17_A1 | [8 empty] | 二甲DS.#3DTR(B)_TAP | #3DTR(B) OLTC TAP | MTR | [5 empty] | 332 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D17 | 二甲DS | 11 | 11kV | 400 | TIE(400) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0379 |  |  | 2-0F-03 |  |  | 400(TIE-3B ) PHA |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.400_51A | 11KV TIE(400) 51RY | TIE | [5 empty] | 333 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | 400 | TIE(400) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0380 |  |  | 2-0F-04 |  |  | 400(TIE-3B ) GDA |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.400_51NA | 11KV TIE(400) 51N RY | TIE | [5 empty] | 334 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS |  |  | 4DTR(A) | #4DTR(A) |  | Tap Chan |  | B3,Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0533 |  | 0064 | 1-31-05 |  | 1-40 | NO.4A DTR OLTC A/M |  |  |  |  | B1/D17_A1 | [8 empty] | 二甲DS.#4DTR(A)_A/M | #4DTR(A) OLTC A/M | MTR | [5 empty] | 335 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D17 | 二甲DS | 11 | 11kV | F27 | 甲31線(F27) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0382 |  |  | 2-0F-06 |  |  | 甲31線(F27) PHA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K631_PHA | 11KV甲31線(K631) 相間RY | FEEDER | [5 empty] | 336 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F27 | 甲31線(F27) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0383 |  |  | 2-0F-07 |  |  | 甲31線(F27) GDA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K631_GDA | 11KV甲31線(K631) 接地RY | FEEDER | [5 empty] | 337 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F27 | 甲31線(F27) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0384 |  |  | 2-10-00 |  |  | 甲31線(F27) 81A |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K631_81A | 11KV甲31線(K631) 81RY | OTHER | [5 empty] | 338 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS |  |  | 4DTR(A) | #4DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0048 |  | 0065 | 1-B0 |  | 1-41 | NO.4 D.TR.(A) TAP |  | 對應CO-66/1 | TAP_-8.5_8.5(0_2000) |  | B1/D17_A1 | [8 empty] | 二甲DS.#4DTR(A)_TAP | #4DTR(A) OLTC TAP | MTR | [5 empty] | 339 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D17 | 二甲DS | 11 | 11kV | F28 | 甲32線(F28) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0386 |  |  | 2-10-02 |  |  | 甲32線(F28) PHA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K632_PHA | 11KV甲32線(K632) 相間RY | FEEDER | [5 empty] | 340 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F28 | 甲32線(F28) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0387 |  |  | 2-10-03 |  |  | 甲32線(F28) GDA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K632_GDA | 11KV甲32線(K632) 接地RY | FEEDER | [5 empty] | 341 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F28 | 甲32線(F28) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0388 |  |  | 2-10-04 |  |  | 甲32線(F28) 81A |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K632_81A | 11KV甲32線(K632) 81RY | OTHER | [5 empty] | 342 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS |  |  | 4DTR(B) | #4DTR(B) |  | Tap Chan |  | B3,Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0537 |  | 0066 | 1-31-09 |  | 1-42 | NO.4B DTR OLTC A/M |  |  |  |  | B1/D17_A1 | [8 empty] | 二甲DS.#4DTR(B)_A/M | #4DTR(B) OLTC A/M | MTR | [5 empty] | 343 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D17 | 二甲DS | 11 | 11kV | F29 | 甲33線(F29) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0390 |  |  | 2-10-06 |  |  | 甲33線(F29) PHA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K633_PHA | 11KV甲33線(K633) 相間RY | FEEDER | [5 empty] | 344 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F29 | 甲33線(F29) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0391 |  |  | 2-10-07 |  |  | 甲33線(F29) GDA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K633_GDA | 11KV甲33線(K633) 接地RY | FEEDER | [5 empty] | 345 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F29 | 甲33線(F29) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0392 |  |  | 2-11-00 |  |  | 甲33線(F29) 81A |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K633_81A | 11KV甲33線(K633) 81RY | OTHER | [5 empty] | 346 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS |  |  | 4DTR(B) | #4DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0049 |  | 0067 | 1-B1 |  | 1-43 | NO.4 D.TR.(B) TAP |  | 對應CO-68/1 | TAP_-8.5_8.5(0_2000) |  | B1/D17_A1 | [8 empty] | 二甲DS.#4DTR(B)_TAP | #4DTR(B) OLTC TAP | MTR | [5 empty] | 347 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D17 | 二甲DS | 11 | 11kV | F30 | 甲34線(F30) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0394 |  |  | 2-11-02 |  |  | 甲34線(F30) PHA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K634_PHA | 11KV甲34線(K634) 相間RY | FEEDER | [5 empty] | 348 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F30 | 甲34線(F30) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0395 |  |  | 2-11-03 |  |  | 甲34線(F30) GDA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K634_GDA | 11KV甲34線(K634) 接地RY | FEEDER | [5 empty] | 349 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F30 | 甲34線(F30) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0396 |  |  | 2-11-04 |  |  | 甲34線(F30) 81A |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K634_81A | 11KV甲34線(K634) 81RY | OTHER | [5 empty] | 350 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1550 | 二甲～奇美實紅線(1550) |  | DS1 | 1551 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0644 | 645 | 0088 | 1-38-04 | 1-38-05 | 1-58 | 二甲奇美實紅線1551 DS-AS |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1551_DS | 1551(二甲奇美實紅線) DS | LINE161 | [5 empty] | 351 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 11 | 11kV | F31 | 甲35線(F31) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0398 |  |  | 2-11-06 |  |  | 甲35線(F31) PHA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K635_PHA | 11KV甲35線(K635) 相間RY | FEEDER | [5 empty] | 352 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F31 | 甲35線(F31) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0399 |  |  | 2-11-07 |  |  | 甲35線(F31) GDA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K635_GDA | 11KV甲35線(K635) 接地RY | FEEDER | [5 empty] | 353 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F31 | 甲35線(F31) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0400 |  |  | 2-12-00 |  |  | 甲35線(F31) 81A |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K635_81A | 11KV甲35線(K635) 81RY | OTHER | [5 empty] | 354 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1550 | 二甲～奇美實紅線(1550) |  | DS2 | 1552 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0646 | 647 | 0089 | 1-38-06 | 1-38-07 | 1-59 | 二甲奇美實紅線1552 DS-AS |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1552_DS | 1552(二甲奇美實紅線) DS | LINE161 | [5 empty] | 355 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D17 | 二甲DS | 11 | 11kV | 270 | #7SC(270) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0402 |  |  | 2-12-02 |  |  | 270(SC-7 ) SCA |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.270_SCA | 11KV #7SC 51,51N RY | SC | [5 empty] | 356 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | 270 | #7SC(270) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0403 |  |  | 2-12-03 |  |  | 270(SC-7 ) UVA |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.270_OUVA | 11KV #7SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 357 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1550 | 二甲～奇美實紅線(1550) |  | DS3 | 1553 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0648 | 649 | 0090 | 1-38-08 | 1-38-09 | 1-5A | 二甲奇美實紅線1553 DS-AS |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1553_DS | 1553(二甲奇美實紅線) DS | LINE161 | [5 empty] | 358 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 11 | 11kV | F32 | 甲41線(F32) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0405 |  |  | 2-12-05 |  |  | 甲41線(F32) PHA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K641_PHA | 11KV甲41線(K641) 相間RY | FEEDER | [5 empty] | 359 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F32 | 甲41線(F32) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0406 |  |  | 2-12-06 |  |  | 甲41線(F32) GDA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K641_GDA | 11KV甲41線(K641) 接地RY | FEEDER | [5 empty] | 360 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F32 | 甲41線(F32) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0407 |  |  | 2-12-07 |  |  | 甲41線(F32) 81A |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K641_81A | 11KV甲41線(K641) 81RY | OTHER | [5 empty] | 361 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1550 | 二甲～奇美實紅線(1550) |  | ES3 | 1553E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0650 | 651 | 0091 | 1-38-10 | 1-38-11 | 1-5B | 二甲奇美實紅線1553E ES-AS |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1553E_ES | 1553E(二甲奇美實紅線) ES | LINE161 | [5 empty] | 362 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D17 | 二甲DS | 11 | 11kV | F33 | 甲42線(F33) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0409 |  |  | 2-13-01 |  |  | 甲42線(F33) PHA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K642_PHA | 11KV甲42線(K642) 相間RY | FEEDER | [5 empty] | 363 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F33 | 甲42線(F33) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0410 |  |  | 2-13-02 |  |  | 甲42線(F33) GDA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K642_GDA | 11KV甲42線(K642) 接地RY | FEEDER | [5 empty] | 364 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F33 | 甲42線(F33) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0411 |  |  | 2-13-03 |  |  | 甲42線(F33) 81A |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K642_81A | 11KV甲42線(K642) 81RY | OTHER | [5 empty] | 365 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1560 | 二甲～奇美實白線(1560) |  | DS1 | 1561 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0652 | 653 | 0092 | 1-38-12 | 1-38-13 | 1-5C | 二甲奇美實白線1561 DS-AS |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1561_DS | 1561(二甲奇美實白線) DS | LINE161 | [5 empty] | 366 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D17 | 二甲DS | 11 | 11kV | F34 | 甲43線(F34) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0413 |  |  | 2-13-05 |  |  | 甲43線(F34) PHA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K643_PHA | 11KV甲43線(K643) 相間RY | FEEDER | [5 empty] | 367 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F34 | 甲43線(F34) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0414 |  |  | 2-13-06 |  |  | 甲43線(F34) GDA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K643_GDA | 11KV甲43線(K643) 接地RY | FEEDER | [5 empty] | 368 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F34 | 甲43線(F34) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0415 |  |  | 2-13-07 |  |  | 甲43線(F34) 81A |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K643_81A | 11KV甲43線(K643) 81RY | OTHER | [5 empty] | 369 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1560 | 二甲～奇美實白線(1560) |  | DS2 | 1562 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0654 | 655 | 0093 | 1-38-14 | 1-38-15 | 1-5D | 二甲奇美實白線1562 DS-AS |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1562_DS | 1562(二甲奇美實白線) DS | LINE161 | [5 empty] | 370 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 11 | 11kV | F35 | 甲44線(F35) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0417 |  |  | 2-14-01 |  |  | 甲44線(F35) PHA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K644_PHA | 11KV甲44線(K644) 相間RY | FEEDER | [5 empty] | 371 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F35 | 甲44線(F35) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0418 |  |  | 2-14-02 |  |  | 甲44線(F35) GDA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K644_GDA | 11KV甲44線(K644) 接地RY | FEEDER | [5 empty] | 372 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F35 | 甲44線(F35) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0419 |  |  | 2-14-03 |  |  | 甲44線(F35) 81A |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K644_81A | 11KV甲44線(K644) 81RY | OTHER | [5 empty] | 373 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1560 | 二甲～奇美實白線(1560) |  | DS3 | 1563 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0656 | 657 | 0094 | 1-39-00 | 1-39-01 | 1-5E | 二甲奇美實白線1563 DS-AS |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1563_DS | 1563(二甲奇美實白線) DS | LINE161 | [5 empty] | 374 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 11 | 11kV | F36 | 甲45線(F36) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0421 |  |  | 2-14-05 |  |  | 甲45線(F36) PHA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K645_PHA | 11KV甲45線(K645) 相間RY | FEEDER | [5 empty] | 375 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F36 | 甲45線(F36) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0422 |  |  | 2-14-06 |  |  | 甲45線(F36) GDA |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K645_GDA | 11KV甲45線(K645) 接地RY | FEEDER | [5 empty] | 376 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | F36 | 甲45線(F36) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0423 |  |  | 2-14-07 |  |  | 甲45線(F36) 81A |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K645_81A | 11KV甲45線(K645) 81RY | OTHER | [5 empty] | 377 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1560 | 二甲～奇美實白線(1560) |  | ES3 | 1563E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0658 | 659 | 0095 | 1-39-02 | 1-39-03 | 1-5F | 二甲奇美實白線1563E ES-AS |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1563E_ES | 1563E(二甲奇美實白線) ES | LINE161 | [5 empty] | 378 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D17 | 二甲DS | 11 | 11kV | 280 | #8SC(280) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0425 |  |  | 2-15-01 |  |  | 280(SC-8 ) SCA |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.280_SCA | 11KV #8SC 51,51N RY | SC | [5 empty] | 379 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | 280 | #8SC(280) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0426 |  |  | 2-15-02 |  |  | 280(SC-8 ) UVA |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.280_OUVA | 11KV #8SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 380 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1570 | 仁德～二甲紅線(1570) |  | DS1 | 1571 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0660 | 661 | 0096 | 1-39-04 | 1-39-05 | 1-60 | 仁德二甲紅線1571 DS-AS |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1571_DS | 1571(仁德二甲紅線) DS | LINE161 | [5 empty] | 381 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 11 | 11kV | 490 | #2SSTR(490) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0428 |  |  | 2-15-04 |  |  | 490(SSTR2 ) PHA |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.#2SSTR_51A | #2SSTR 51RY | OTHER | [5 empty] | 382 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | 490 | #2SSTR(490) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0429 |  |  | 2-15-05 |  |  | 490(SSTR2 ) GDA |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | [5 empty] | 383 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1570 | 仁德～二甲紅線(1570) |  | DS2 | 1572 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0662 | 663 | 0097 | 1-39-06 | 1-39-07 | 1-61 | 仁德二甲紅線1572 DS-AS |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1572_DS | 1572(仁德二甲紅線) DS | LINE161 | [5 empty] | 384 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D17 | 二甲DS | 0 |  | RTU | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0513 |  |  | 1-30-01 |  |  | L/R STATUS ON/OFF |  |  |  |  | ELEM/D17_A1 | [8 empty] | 二甲DS.RTU_S/L | RTU SUPY/LOCAL | OTHER | [5 empty] | 385 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
D17 | 二甲DS |  |  | 3DTR | #3DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0524 |  |  | 1-30-12 |  |  | NO.3 DTR 87S |  |  |  |  | B1/D17_A1 | [8 empty] | 二甲DS.#3DTR_87UL1 | #3DTR 第一套 87RY U/L | OTHER | [5 empty] | 386 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS |  |  | 3DTR(A) | #3DTR(A) |  | SupLocal |  | B3 | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0525 |  |  | 1-30-13 |  |  | NO.3A DTR OLTC S/L |  |  |  | c | B1/D17_A1 | [8 empty] | 二甲DS.#3DTR(A)_S/L | #3DTR(A) OLTC S/L | MTR | [5 empty] | 387 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D17 | 二甲DS | 161 | 161kV | 1570 | 仁德～二甲紅線(1570) |  | DS3 | 1573 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0664 | 665 | 0098 | 1-39-08 | 1-39-09 | 1-62 | 仁德二甲紅線1573 DS-AS |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1573_DS | 1573(仁德二甲紅線) DS | LINE161 | [5 empty] | 388 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS |  |  | 3DTR | #3DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0527 |  |  | 1-30-15 |  |  | NO.3 DTR TRA |  |  |  | a | B1/D17_A1 | [8 empty] | 二甲DS.#3DTR_TRA | #3DTR 重故障 | MTR | [5 empty] | 389 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D17 | 二甲DS |  |  | 3DTR | #3DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0528 |  |  | 1-31-00 |  |  | NO.3 DTR TRF |  |  |  |  | B1/D17_A1 | [8 empty] | 二甲DS.#3DTR_TRF | #3DTR 輕故障 | MTR | [5 empty] | 390 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D17 | 二甲DS |  |  | 3DTR(B) | #3DTR(B) |  | SupLocal |  | B3 | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0529 |  |  | 1-31-01 |  |  | NO.3B DTR OLTC S/L |  |  |  | b | B1/D17_A1 | [8 empty] | 二甲DS.#3DTR(B)_S/L | #3DTR(B) OLTC S/L | MTR | [5 empty] | 391 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D17 | 二甲DS | 161 | 161kV | 1570 | 仁德～二甲紅線(1570) |  | ES3 | 1573E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0666 | 667 | 0099 | 1-39-10 | 1-39-11 | 1-63 | 仁德二甲紅線1573E ES-AS |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1573E_ES | 1573E(仁德二甲紅線) ES | LINE161 | [5 empty] | 392 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D17 | 二甲DS |  |  | 4DTR | #4DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0531 |  |  | 1-31-03 |  |  | NO.4 DTR 87S |  |  |  |  | B1/D17_A1 | [8 empty] | 二甲DS.#4DTR_87UL1 | #4DTR 第一套 87RY U/L | OTHER | [5 empty] | 393 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS |  |  | 4DTR(A) | #4DTR(A) |  | SupLocal |  | B3 | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0532 |  |  | 1-31-04 |  |  | NO.4A DTR OLTC S/L |  |  |  | c | B1/D17_A1 | [8 empty] | 二甲DS.#4DTR(A)_S/L | #4DTR(A) OLTC S/L | MTR | [5 empty] | 394 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D17 | 二甲DS | 161 | 161kV | 1580 | 仁德～二甲白線(1580) |  | DS1 | 1581 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0668 | 669 | 0100 | 1-39-12 | 1-39-13 | 1-64 | 仁德二甲白線1581 DS-AS |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1581_DS | 1581(仁德二甲白線) DS | LINE161 | [5 empty] | 395 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D17 | 二甲DS |  |  | 4DTR | #4DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0534 |  |  | 1-31-06 |  |  | NO.4 DTR TRA |  |  |  | a | B1/D17_A1 | [8 empty] | 二甲DS.#4DTR_TRA | #4DTR 重故障 | MTR | [5 empty] | 396 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D17 | 二甲DS |  |  | 4DTR | #4DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0535 |  |  | 1-31-07 |  |  | NO.4 DTR TRF |  |  |  |  | B1/D17_A1 | [8 empty] | 二甲DS.#4DTR_TRF | #4DTR 輕故障 | MTR | [5 empty] | 397 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D17 | 二甲DS |  |  | 4DTR(B) | #4DTR(B) |  | SupLocal |  | B3 | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0536 |  |  | 1-31-08 |  |  | NO.4B DTR OLTC S/L |  |  |  | b | B1/D17_A1 | [8 empty] | 二甲DS.#4DTR(B)_S/L | #4DTR(B) OLTC S/L | MTR | [5 empty] | 398 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D17 | 二甲DS | 161 | 161kV | 1580 | 仁德～二甲白線(1580) |  | DS2 | 1582 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0670 | 671 | 0101 | 1-39-14 | 1-39-15 | 1-65 | 仁德二甲白線1582 DS-AS |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1582_DS | 1582(仁德二甲白線) DS | LINE161 | [5 empty] | 399 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 161 | 161kV | 1580 | 仁德～二甲白線(1580) |  | DS3 | 1583 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0672 | 673 | 0102 | 1-3A-00 | 1-3A-01 | 1-66 | 仁德二甲白線1583 DS-AS |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1583_DS | 1583(仁德二甲白線) DS | LINE161 | [5 empty] | 400 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 161 | 161kV | 1580 | 仁德～二甲白線(1580) |  | ES3 | 1583E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0674 | 675 | 0103 | 1-3A-02 | 1-3A-03 | 1-67 | 仁德二甲白線1583E ES-AS |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1583E_ES | 1583E(仁德二甲白線) ES | LINE161 | [5 empty] | 401 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D17 | 二甲DS | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0540 |  |  | 1-31-12 |  |  | 1500SA |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1500_50SA | 161KV TIE(1500) 50RY 測試/正常 | TIE | [5 empty] | 402 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Test | Test | 1 |  |  | TEST/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | StaDev | 所內設施 |  | GEN | 緊急發電機運轉 | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0541 |  |  | 1-31-13 |  |  | 緊急發電機運轉 ON/OFF |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.GEN | 緊急發電機運轉 | OTHER | [5 empty] | 403 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ON/OFF | OFF
D17 | 二甲DS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | DS1 | 1611 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0676 | 677 | 0104 | 1-3A-04 | 1-3A-05 | 1-68 | 龍崎山上二甲三路1611 DS-AS |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1611_DS | 1611(龍崎山上三路) DS | LINE161 | [5 empty] | 404 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | DS2 | 1612 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0678 | 679 | 0105 | 1-3A-06 | 1-3A-08 | 1-69 | 龍崎山上二甲三路1612 DS-AS |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1612_DS | 1612(龍崎山上三路) DS | LINE161 |  | CDC_Mon1_DPC |  |  |  | 405 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D17 | 二甲DS | 161 | 161kV | 1550 | 二甲～奇美實紅線(1550) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0552 |  |  | 1-32-08 |  |  | 1550 87CFA 通訊 故障 |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1550_87CFA | 二甲奇美實紅線(1550)RY通訊故障 | OTHER | [5 empty] | 406 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1550 | 二甲～奇美實紅線(1550) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0553 |  |  | 1-32-09 |  |  | 1550 RYFA 電驛 故障 |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1550_RYFA | 二甲奇美實紅線(1550)數位RY故障 | OTHER | [5 empty] | 407 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1560 | 二甲～奇美實白線(1560) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0554 |  |  | 1-32-10 |  |  | 1560 87CFA 通訊 故障 |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1560_87CFA | 二甲奇美實白線(1560)RY通訊故障 | OTHER | [5 empty] | 408 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1560 | 二甲～奇美實白線(1560) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0555 |  |  | 1-32-11 |  |  | 1560 RYFA 電驛 故障 |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1560_RYFA | 二甲奇美實白線(1560)數位RY故障 | OTHER | [5 empty] | 409 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1570 | 仁德～二甲紅線(1570) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0556 |  |  | 1-32-12 |  |  | 1570 87CFA 通訊 故障 |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1570_87CFA | 仁德二甲紅線(1570)87RY通訊故障 | OTHER | [5 empty] | 410 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1570 | 仁德～二甲紅線(1570) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0557 |  |  | 1-32-13 |  |  | 1570 RYFA 電驛 故障 |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1570_RYFA | 仁德二甲紅線(1570)數位電驛故障 | OTHER | [5 empty] | 411 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1580 | 仁德～二甲白線(1580) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0558 |  |  | 1-32-14 |  |  | 1580 87CFA 通訊 故障 |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1580_87CFA | 仁德二甲白線(1580)87RY通訊故障 | OTHER | [5 empty] | 412 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1580 | 仁德～二甲白線(1580) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0559 |  |  | 1-32-15 |  |  | 1580 RYFA 電驛 故障 |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1580_RYFA | 仁德二甲白線(1580)數位電驛故障 | OTHER | [5 empty] | 413 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0560 |  |  | 1-33-00 |  |  | 1610 87CFA 通訊 故障 |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1610_87CFA | 龍崎山上三路(1610)87RY通訊故障 | OTHER | [5 empty] | 414 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0561 |  |  | 1-33-01 |  |  | 1610 RYFA 電驛 故障 |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1610_RYFA | 龍崎山上三路(1610)數位電驛故障 | OTHER | [5 empty] | 415 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | DTTA |  |  | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0562 |  |  | 1-33-02 |  |  | 1610 DTTA |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1610_DTTA | 龍崎山上三路(1610) 遠方遙跳 | OTHER | [5 empty] | 416 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0563 |  |  | 1-33-03 |  |  | 1620 87CFA 通訊 故障 |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1620_87CFA | 龍崎山上四路(1620)87RY通訊故障 | OTHER | [5 empty] | 417 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0564 |  |  | 1-33-04 |  |  | 1620 RYFA 電驛 故障 |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1620_RYFA | 龍崎山上四路(1620)數位電驛故障 | OTHER | [5 empty] | 418 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | DTTA |  |  | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0565 |  |  | 1-33-05 |  |  | 1620 DTTA |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1620_DTTA | 龍崎山上四路(1620) 遠方遙跳 | OTHER | [5 empty] | 419 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D17 | 二甲DS |  |  | 3DTR | #3DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0576 |  |  | 1-34-00 |  |  | NO.3 DTR 96B1 |  |  |  |  | B1/D17_A1 | [8 empty] | 二甲DS.#3DTR_96B1 | #3DTR 96B1 RY | MTR | [5 empty] | 420 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D17 | 二甲DS |  |  | 3DTR | #3DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0577 |  |  | 1-34-01 |  |  | NO.3 DTR 96B2 |  |  |  |  | B1/D17_A1 | [8 empty] | 二甲DS.#3DTR_96B2 | #3DTR 96B2 RY | MTR | [5 empty] | 421 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D17 | 二甲DS |  |  | 3DTR | #3DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0578 |  |  | 1-34-02 |  |  | NO.3 DTR 96D |  |  |  |  | B1/D17_A1 | [8 empty] | 二甲DS.#3DTR_96D | #3DTR 96D RY | MTR | [5 empty] | 422 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D17 | 二甲DS |  |  | 3DTR | #3DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0579 |  |  | 1-34-03 |  |  | NO.3 DTR 96P |  |  |  |  | B1/D17_A1 | [8 empty] | 二甲DS.#3DTR_96P | #3DTR 96P RY | MTR | [5 empty] | 423 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D17 | 二甲DS |  |  | 3DTR | #3DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0580 |  |  | 1-34-04 |  |  | NO.3 DTR 63Q |  |  |  |  | B1/D17_A1 | [8 empty] | 二甲DS.#3DTR_63Q | #3DTR 63Q RY | MTR | [5 empty] | 424 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D17 | 二甲DS |  |  | 4DTR | #4DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0581 |  |  | 1-34-05 |  |  | NO.4 DTR 96B1 |  |  |  |  | B1/D17_A1 | [8 empty] | 二甲DS.#4DTR_96B1 | #4DTR 96B1 RY | MTR | [5 empty] | 425 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D17 | 二甲DS |  |  | 4DTR | #4DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0582 |  |  | 1-34-06 |  |  | NO.4 DTR 96B2 |  |  |  |  | B1/D17_A1 | [8 empty] | 二甲DS.#4DTR_96B2 | #4DTR 96B2 RY | MTR | [5 empty] | 426 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D17 | 二甲DS |  |  | 4DTR | #4DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0583 |  |  | 1-34-07 |  |  | NO.4 DTR 96D |  |  |  |  | B1/D17_A1 | [8 empty] | 二甲DS.#4DTR_96D | #4DTR 96D RY | MTR | [5 empty] | 427 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D17 | 二甲DS |  |  | 4DTR | #4DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0584 |  |  | 1-34-08 |  |  | NO.4 DTR 96P |  |  |  |  | B1/D17_A1 | [8 empty] | 二甲DS.#4DTR_96P | #4DTR 96P RY | MTR | [5 empty] | 428 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D17 | 二甲DS |  |  | 4DTR | #4DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0585 |  |  | 1-34-09 |  |  | NO.4 DTR 63Q |  |  |  |  | B1/D17_A1 | [8 empty] | 二甲DS.#4DTR_63Q | #4DTR 63Q RY | MTR | [5 empty] | 429 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | DS3 | 1613 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0680 | 681 | 0106 | 1-3A-08 | 1-3A-09 | 1-6A | 龍崎山上二甲三路1612 DS-BS |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1613_DS | 1613(龍崎山上三路) DS | LINE161 |  | CDC_Mon1_DPC |  |  |  | 430 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | ES3 | 1613E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0682 | 683 | 0107 | 1-3A-10 | 1-3A-11 | 1-6B | 龍崎山上二甲三路1613E ES-AS |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1613E_ES | 1613E(龍崎山上三路) ES | LINE161 | [5 empty] | 431 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D17 | 二甲DS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | DS1 | 1621 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0684 | 685 | 0108 | 1-3A-12 | 1-3A-13 | 1-6C | 龍崎山上二甲四路1621 DS-AS |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1621_DS | 1621(龍崎山上四路) DS | LINE161 | [5 empty] | 432 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D17 | 二甲DS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | DS2 | 1622 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0686 | 687 | 0109 | 1-3A-14 | 1-3A-15 | 1-6D | 龍崎山上二甲四路1622 DS-AS |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1622_DS | 1622(龍崎山上四路) DS | LINE161 | [5 empty] | 433 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | DS3 | 1623 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0688 | 689 | 0110 | 1-3B-00 | 1-3B-01 | 1-6E | 龍崎山上二甲四路1623 DS-AS |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1623_DS | 1623(龍崎山上四路) DS | LINE161 | [5 empty] | 434 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | ES3 | 1623E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0690 | 691 | 0111 | 1-3B-02 | 1-3B-03 | 1-6F | 龍崎山上二甲四路1623E ES-AS |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1623E_ES | 1623E(龍崎山上四路) ES | LINE161 | [5 empty] | 435 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D17 | 二甲DS | 161 | 161kV | 1500 | TIE (1500) |  | DS1 | 1501 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0608 | 609 | 0112 | 1-36-00 | 1-36-01 | 1-70 | TIE(1501) DS-AS |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1501_DS | 1501(TIE) DS | TIE | [5 empty] | 436 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 161 | 161kV | 1500 | TIE (1500) |  | DS2 | 1502 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0610 | 611 | 0113 | 1-36-02 | 1-36-03 | 1-71 | TIE(1502) DS-AS |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1502_DS | 1502(TIE) DS | TIE | [5 empty] | 437 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0700 | 701 | 0118 | 1-3B-12 | 1-3B-13 | 1-76 | NO.3 DTR(1771) DS-AS |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1771_DS | 1771(#3DTR) DS | MTR | [5 empty] | 438 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0702 | 703 | 0119 | 1-3B-14 | 1-3B-15 | 1-77 | NO.3 DTR(1772) DS-AS |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1772_DS | 1772(#3DTR) DS | MTR | [5 empty] | 439 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D17 | 二甲DS | 161 | 161kV | 1780 | #4DTR(1780) |  | DS1 | 1781 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0704 | 705 | 0120 | 1-3C-00 | 1-3C-01 | 1-78 | NO.4 DTR(1781) DS-AS |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1781_DS | 1781(#4DTR) DS | MTR | [5 empty] | 440 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D17 | 二甲DS | 161 | 161kV | 1780 | #4DTR(1780) |  | DS2 | 1782 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0706 | 707 | 0121 | 1-3C-02 | 1-3C-03 | 1-79 | NO.4 DTR(1782) DS-AS |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.1782_DS | 1782(#4DTR) DS | MTR | [5 empty] | 441 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 11 | 11kV | B5SC | #3DTR(A)(5SC) |  | LBS |  | Element | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/250 | C/5SC(B) |  |  | 0708 | 709 | 0122 | 1-3C-04 | 1-3C-05 | 1-7A | 250(SC-5) LBS LBS-AS |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.250_LBS | 250(11KV #5SC) LBS | SC | [5 empty] | 442 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 11 | 11kV | B6SC | #3DTR(B)(6SC) |  | LBS |  | Element | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/260 | C/6SC(B) |  |  | 0710 | 711 | 0123 | 1-3C-06 | 1-3C-07 | 1-7B | 260(SC-6) LBS LBS-AS |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.260_LBS | 260(11KV #6SC) LBS | SC | [5 empty] | 443 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 11 | 11kV | B7SC | #4DTR(A)(7SC) |  | LBS |  | Element | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/270 | C/7SC(B) |  |  | 0712 | 713 | 0124 | 1-3C-08 | 1-3C-09 | 1-7C | 270(SC-7 ) LBS LBS-AS |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.270_LBS | 270(11KV #7SC) LBS | SC | [5 empty] | 444 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 11 | 11kV | B8SC | #4DTR(B)(8SC) |  | LBS |  | Element | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/280 | C/8SC(B) |  |  | 0714 | 715 | 0125 | 1-3C-10 | 1-3C-11 | 1-7D | 280(SC-8 ) LBS LBS-AS |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.280_LBS | 280(11KV #8SC) LBS | SC | [5 empty] | 445 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 0 |  | StaDev | 所內設施 |  | Lights1 | 景觀照明 |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0542 |  | 0126 | 1-31-14 |  | 1-7E | 景觀照明 (A) |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.開關場照明(A) | 景觀照明(A) | OTHER | [5 empty] | 446 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
D17 | 二甲DS | 0 |  | StaDev | 所內設施 |  | Lights2 | 景觀照明 |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0543 |  | 0127 | 1-31-15 |  | 1-7F | 景觀照明 (B) |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.開關場照明(B) | 景觀照明(B) | OTHER | [5 empty] | 447 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
D17 | 二甲DS | 11 | 11kV | 390 | #1SSTR(390) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3ABus | T/1SSTR |  |  | 0352 |  | 0149 | 2-0C-00 |  | 2-15 | 390(SSTR1 ) CB ON/OFF |  |  |  | aaab | B3/D17_A1 | [8 empty] | 二甲DS.390_CB | 390(#1SSTR) CB | OTHER | [5 empty] | 448 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | 250 | #5SC(250) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3ABus | C/5SC |  |  | 0346 |  | 0150 | 2-0B-02 |  | 2-16 | 250(SC-5) CB ON/OFF |  |  |  | aacb | B3/D17_A1 | [8 empty] | 二甲DS.250_CB | 250(11KV #5SC) CB | SC | [5 empty] | 449 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F17 | 甲11線(F17) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3ABus | L/F17/T1 |  |  | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F17 | 甲11線(F17) |  | DS |  | ADD | Status | DS | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F17 | 甲11線(F17) |  | ES |  | ADD | Status | ES | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F18 | 甲12線(F18) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3ABus | L/F18/T1 |  |  | 0330 |  | 0152 | 2-09-02 |  | 2-18 | 甲12線(F18) CB ON/OFF |  |  |  | aaeb | B2/D17_D1 | [8 empty] | 二甲DS.K612_CB | K612(11KV甲12線) CB | FEEDER | [5 empty] | 451 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F18 | 甲12線(F18) |  | DS |  | ADD | Status | DS | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F18 | 甲12線(F18) |  | ES |  | ADD | Status | ES | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F19 | 甲13線(F19) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3ABus | L/F19/T1 |  |  | 0334 |  | 0153 | 2-09-06 |  | 2-19 | 甲13線(F19) CB ON/OFF |  |  |  | aafb | B2/D17_D1 | [8 empty] | 二甲DS.K613_CB | K613(11KV甲13線) CB | FEEDER | [5 empty] | 452 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F19 | 甲13線(F19) |  | DS |  | ADD | Status | DS | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F19 | 甲13線(F19) |  | ES |  | ADD | Status | ES | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F20 | 甲14線(F20) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3ABus | L/F20/T1 |  |  | 0338 |  | 0154 | 2-0A-02 |  | 2-1A | 甲14線(F20) CB ON/OFF |  |  |  | aahb | B2/D17_D1 | [8 empty] | 二甲DS.K614_CB | K614(11KV甲14線) CB | FEEDER | [5 empty] | 453 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F20 | 甲14線(F20) |  | DS |  | ADD | Status | DS | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F20 | 甲14線(F20) |  | ES |  | ADD | Status | ES | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F21 | 甲15線(F21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3ABus | L/F21/T1 |  |  | 0342 |  | 0155 | 2-0A-06 |  | 2-1B | 甲15線(F21) CB ON/OFF |  |  |  | aaib | B2/D17_D1 | [8 empty] | 二甲DS.K615_CB | K615(11KV甲15線) CB | FEEDER | [5 empty] | 454 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F21 | 甲15線(F21) |  | DS |  | ADD | Status | DS | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F21 | 甲15線(F21) |  | ES |  | ADD | Status | ES | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | 300 | TIE(300) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/3ABus | B/4ABus |  |  | 0349 |  | 0156 | 2-0B-05 |  | 2-1C | 300(TIE-3A ) CB ON/OFF |  |  |  | aajb | B3/D17_A1 | [8 empty] | 二甲DS.300_CB | 300(TIE) CB | TIE | [5 empty] | 455 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 11 | 11kV | 260 | #6SC(260) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3BBus | C/6SC |  |  | 0375 |  | 0157 | 2-0E-07 |  | 2-1D | 260(SC-6) CB ON/OFF |  |  |  | babb | B3/D17_A1 | [8 empty] | 二甲DS.260_CB | 260(11KV #6SC) CB | SC | [5 empty] | 456 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F22 | 甲21線(F22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BBus | L/F22/T1 |  |  | 0355 |  | 0158 | 2-0C-03 |  | 2-1E | 甲21線(F22) CB ON/OFF |  |  |  | bacb | B2/D17_D1 | [8 empty] | 二甲DS.K621_CB | K621(11KV甲21線) CB | FEEDER | [5 empty] | 457 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F22 | 甲21線(F22) |  | DS |  | ADD | Status | DS | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F22 | 甲21線(F22) |  | ES |  | ADD | Status | ES | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F23 | 甲22線(F23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BBus | L/F23/T1 |  |  | 0359 |  | 0159 | 2-0C-07 |  | 2-1F | 甲22線(F23) CB ON/OFF |  |  |  | badb | B2/D17_D1 | [8 empty] | 二甲DS.K622_CB | K622(11KV甲22線) CB | FEEDER | [5 empty] | 458 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F23 | 甲22線(F23) |  | DS |  | ADD | Status | DS | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F23 | 甲22線(F23) |  | ES |  | ADD | Status | ES | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F24 | 甲23線(F24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BBus | L/F24/T1 |  |  | 0363 |  | 0160 | 2-0D-03 |  | 2-20 | 甲23線(F24) CB ON/OFF |  |  |  | baeb | B2/D17_D1 | [8 empty] | 二甲DS.K623_CB | K623(11KV甲23線) CB | FEEDER | [5 empty] | 459 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F24 | 甲23線(F24) |  | DS |  | ADD | Status | DS | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F24 | 甲23線(F24) |  | ES |  | ADD | Status | ES | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F25 | 甲24線(F25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BBus | L/F25/T1 |  |  | 0367 |  | 0161 | 2-0D-07 |  | 2-21 | 甲24線(F25) CB ON/OFF |  |  |  | bagb | B2/D17_D1 | [8 empty] | 二甲DS.K624_CB | K624(11KV甲24線) CB | FEEDER | [5 empty] | 460 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F25 | 甲24線(F25) |  | DS |  | ADD | Status | DS | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F25 | 甲24線(F25) |  | ES |  | ADD | Status | ES | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F26 | 甲25線(F26) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BBus | L/F26/T1 |  |  | 0371 |  | 0162 | 2-0E-03 |  | 2-22 | 甲25線(F26) CB ON/OFF |  |  |  | bahb | B2/D17_D1 | [8 empty] | 二甲DS.K625_CB | K625(11KV甲25線) CB | FEEDER | [5 empty] | 461 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F26 | 甲25線(F26) |  | DS |  | ADD | Status | DS | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F26 | 甲25線(F26) |  | ES |  | ADD | Status | ES | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | 400 | TIE(400) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/3BBus | B/4BBus |  |  | 0378 |  | 0163 | 2-0F-02 |  | 2-23 | 400(TIE-3B ) CB ON/OFF |  |  |  | baib | B3/D17_A1 | [8 empty] | 二甲DS.400_CB | 400(TIE) CB | TIE | [5 empty] | 462 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D17 | 二甲DS | 11 | 11kV | 270 | #7SC(270) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4ABus | C/7SC |  |  | 0401 |  | 0164 | 2-12-01 |  | 2-24 | 270(SC-7 ) CB ON/OFF |  |  |  | abbb | B3/D17_A1 | [8 empty] | 二甲DS.270_CB | 270(11KV #7SC) CB | SC | [5 empty] | 463 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F27 | 甲31線(F27) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4ABus | L/F27/T1 |  |  | 0381 |  | 0165 | 2-0F-05 |  | 2-25 | 甲31線(F27) CB ON/OFF |  |  |  | abdb | B2/D17_D1 | [8 empty] | 二甲DS.K631_CB | K631(11KV甲31線) CB | FEEDER | [5 empty] | 464 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F27 | 甲31線(F27) |  | DS |  | ADD | Status | DS | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F27 | 甲31線(F27) |  | ES |  | ADD | Status | ES | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F28 | 甲32線(F28) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4ABus | L/F28/T1 |  |  | 0385 |  | 0166 | 2-10-01 |  | 2-26 | 甲32線(F28) CB ON/OFF |  |  |  | abeb | B2/D17_D1 | [8 empty] | 二甲DS.K632_CB | K632(11KV甲32線) CB | FEEDER | [5 empty] | 465 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F28 | 甲32線(F28) |  | DS |  | ADD | Status | DS | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F28 | 甲32線(F28) |  | ES |  | ADD | Status | ES | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F29 | 甲33線(F29) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4ABus | L/F29/T1 |  |  | 0389 |  | 0167 | 2-10-05 |  | 2-27 | 甲33線(F29) CB ON/OFF |  |  |  | abfb | B2/D17_D1 | [8 empty] | 二甲DS.K633_CB | K633(11KV甲33線) CB | FEEDER | [5 empty] | 466 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F29 | 甲33線(F29) |  | DS |  | ADD | Status | DS | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F29 | 甲33線(F29) |  | ES |  | ADD | Status | ES | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F30 | 甲34線(F30) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4ABus | L/F30/T1 |  |  | 0393 |  | 0168 | 2-11-01 |  | 2-28 | 甲34線(F30) CB ON/OFF |  |  |  | abgb | B2/D17_D1 | [8 empty] | 二甲DS.K634_CB | K634(11KV甲34線) CB | FEEDER | [5 empty] | 467 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F30 | 甲34線(F30) |  | DS |  | ADD | Status | DS | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F30 | 甲34線(F30) |  | ES |  | ADD | Status | ES | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F31 | 甲35線(F31) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4ABus | L/F31/T1 |  |  | 0397 |  | 0169 | 2-11-05 |  | 2-29 | 甲35線(F31) CB ON/OFF |  |  |  | abhb | B2/D17_D1 | [8 empty] | 二甲DS.K635_CB | K635(11KV甲35線) CB | FEEDER | [5 empty] | 468 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F31 | 甲35線(F31) |  | DS |  | ADD | Status | DS | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F31 | 甲35線(F31) |  | ES |  | ADD | Status | ES | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | 280 | #8SC(280) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4BBus | C/8SC |  |  | 0424 |  | 0170 | 2-15-00 |  | 2-2A | 280(SC-8 ) CB ON/OFF |  |  |  | bbcb | B3/D17_A1 | [8 empty] | 二甲DS.280_CB | 280(11KV #8SC) CB | SC | [5 empty] | 469 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | 490 | #2SSTR(490) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4BBus | T/2SSTR |  |  | 0427 |  | 0171 | 2-15-03 |  | 2-2B | 490(SSTR2 ) CB ON/OFF |  |  |  | bbab | B3/D17_A1 | [8 empty] | 二甲DS.490_CB | 490(#2SSTR) CB | OTHER | [5 empty] | 470 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F32 | 甲41線(F32) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4BBus | L/F32/T1 |  |  | 0404 |  | 0172 | 2-12-04 |  | 2-2C | 甲41線(F32) CB ON/OFF |  |  |  | bbeb | B2/D17_D1 | [8 empty] | 二甲DS.K641_CB | K641(11KV甲41線) CB | FEEDER | [5 empty] | 471 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F32 | 甲41線(F32) |  | DS |  | ADD | Status | DS | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F32 | 甲41線(F32) |  | ES |  | ADD | Status | ES | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F33 | 甲42線(F33) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4BBus | L/F33/T1 |  |  | 0408 |  | 0173 | 2-13-00 |  | 2-2D | 甲42線(F33) CB ON/OFF |  |  |  | bbfb | B2/D17_D1 | [8 empty] | 二甲DS.K642_CB | K642(11KV甲42線) CB | FEEDER | [5 empty] | 472 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F33 | 甲42線(F33) |  | DS |  | ADD | Status | DS | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F33 | 甲42線(F33) |  | ES |  | ADD | Status | ES | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F34 | 甲43線(F34) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4BBus | L/F34/T1 |  |  | 0412 |  | 0174 | 2-13-04 |  | 2-2E | 甲43線(F34) CB ON/OFF |  |  |  | bbgb | B2/D17_D1 | [8 empty] | 二甲DS.K643_CB | K643(11KV甲43線) CB | FEEDER | [5 empty] | 473 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F34 | 甲43線(F34) |  | DS |  | ADD | Status | DS | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F34 | 甲43線(F34) |  | ES |  | ADD | Status | ES | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F35 | 甲44線(F35) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4BBus | L/F35/T1 |  |  | 0416 |  | 0175 | 2-14-00 |  | 2-2F | 甲44線(F35) CB ON/OFF |  |  |  | bbhb | B2/D17_D1 | [8 empty] | 二甲DS.K644_CB | K644(11KV甲44線) CB | FEEDER | [5 empty] | 474 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F35 | 甲44線(F35) |  | DS |  | ADD | Status | DS | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F35 | 甲44線(F35) |  | ES |  | ADD | Status | ES | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F36 | 甲45線(F36) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4BBus | L/F36/T1 |  |  | 0420 |  | 0176 | 2-14-04 |  | 2-30 | 甲45線(F36) CB ON/OFF |  |  |  | bbib | B2/D17_D1 | [8 empty] | 二甲DS.K645_CB | K645(11KV甲45線) CB | FEEDER | [5 empty] | 475 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F36 | 甲45線(F36) |  | DS |  | ADD | Status | DS | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | F36 | 甲45線(F36) |  | ES |  | ADD | Status | ES | Close/Open | Y | 1 | DI-SP | [6 empty] | 0326 |  | 0151 | 2-08-06 |  | 2-17 | 甲11線(F17) CB ON/OFF |  |  |  | aadb | B2/D17_D1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | 350 | #3DTR(A)(350) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0970 |  | 0180 | 2-3C-10 |  | 2-34 | 350(M3A) 81S |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.350_81UL | 350 #3DTR(A) 81RY U/L | OTHER | [5 empty] | 476 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | 360 | #3DTR(B)(360) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0971 |  | 0181 | 2-3C-11 |  | 2-35 | 360(M3B) 81S |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.360_81UL | 360 #3DTR(B) 81RY U/L | OTHER | [5 empty] | 477 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | 370 | #4DTR(A)(370) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0972 |  | 0182 | 2-3C-12 |  | 2-36 | 370(M4A) 81S |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.370_81UL | 370 #4DTR(A) 81RY U/L | OTHER | [5 empty] | 478 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | 380 | #4DTR(B)(380) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0973 |  | 0183 | 2-3C-13 |  | 2-37 | 380(M4B) 81S |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.380_81UL | 380 #4DTR(B) 81RY U/L | OTHER | [5 empty] | 479 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | F17 | 甲11線(F17) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0928 |  | 0216 | 2-3A-00 |  | 2-58 | 甲11線(F17) 79S |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K611_79UL | 11KV甲11線(K611) 79RY U/L | FEEDER | [5 empty] | 480 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | F17 | 甲11線(F17) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0929 |  | 0217 | 2-3A-01 |  | 2-59 | 甲11線(F17) 51NS |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K611_LCO_TAP | 11KV甲11線(K611) LCO TAP | FEEDER | [5 empty] | 481 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | F18 | 甲12線(F18) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0930 |  | 0218 | 2-3A-02 |  | 2-5A | 甲12線(F18) 79S |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K612_79UL | 11KV甲12線(K612) 79RY U/L | FEEDER | [5 empty] | 482 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | F18 | 甲12線(F18) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0931 |  | 0219 | 2-3A-03 |  | 2-5B | 甲12線(F18) 51NS |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K612_LCO_TAP | 11KV甲12線(K612) LCO TAP | FEEDER | [5 empty] | 483 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | F19 | 甲13線(F19) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0932 |  | 0220 | 2-3A-04 |  | 2-5C | 甲13線(F19) 79S |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K613_79UL | 11KV甲13線(K613) 79RY U/L | FEEDER | [5 empty] | 484 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | F19 | 甲13線(F19) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0933 |  | 0221 | 2-3A-05 |  | 2-5D | 甲13線(F19) 51NS |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K613_LCO_TAP | 11KV甲13線(K613) LCO TAP | FEEDER | [5 empty] | 485 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | F20 | 甲14線(F20) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0934 |  | 0222 | 2-3A-06 |  | 2-5E | 甲14線(F20) 79S |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K614_79UL | 11KV甲14線(K614) 79RY U/L | FEEDER | [5 empty] | 486 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | F20 | 甲14線(F20) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0935 |  | 0223 | 2-3A-07 |  | 2-5F | 甲14線(F20) 51NS |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K614_LCO_TAP | 11KV甲14線(K614) LCO TAP | FEEDER | [5 empty] | 487 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | F21 | 甲15線(F21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0936 |  | 0224 | 2-3A-08 |  | 2-60 | 甲15線(F21) 79S |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K615_79UL | 11KV甲15線(K615) 79RY U/L | FEEDER | [5 empty] | 488 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | F21 | 甲15線(F21) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0937 |  | 0225 | 2-3A-09 |  | 2-61 | 甲15線(F21) 51NS |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K615_LCO_TAP | 11KV甲15線(K615) LCO TAP | FEEDER | [5 empty] | 489 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | F22 | 甲21線(F22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0938 |  | 0226 | 2-3A-10 |  | 2-62 | 甲21線(F22) 79S |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K621_79UL | 11KV甲21線(K621) 79RY U/L | FEEDER | [5 empty] | 490 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | F22 | 甲21線(F22) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0939 |  | 0227 | 2-3A-11 |  | 2-63 | 甲21線(F22) 51NS |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K621_LCO_TAP | 11KV甲21線(K621) LCO TAP | FEEDER | [5 empty] | 491 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | F23 | 甲22線(F23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0940 |  | 0228 | 2-3A-12 |  | 2-64 | 甲22線(F23) 79S |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K622_79UL | 11KV甲22線(K622) 79RY U/L | FEEDER | [5 empty] | 492 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | F23 | 甲22線(F23) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0941 |  | 0229 | 2-3A-13 |  | 2-65 | 甲22線(F23) 51NS |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K622_LCO_TAP | 11KV甲22線(K622) LCO TAP | FEEDER | [5 empty] | 493 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | F24 | 甲23線(F24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0942 |  | 0230 | 2-3A-14 |  | 2-66 | 甲23線(F24) 79S |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K623_79UL | 11KV甲23線(K623) 79RY U/L | FEEDER | [5 empty] | 494 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | F24 | 甲23線(F24) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0943 |  | 0231 | 2-3A-15 |  | 2-67 | 甲23線(F24) 51NS |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K623_LCO_TAP | 11KV甲23線(K623) LCO TAP | FEEDER | [5 empty] | 495 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | F25 | 甲24線(F25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0944 |  | 0232 | 2-3B-00 |  | 2-68 | 甲24線(F25) 79S |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K624_79UL | 11KV甲24線(K624) 79RY U/L | FEEDER | [5 empty] | 496 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | F25 | 甲24線(F25) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0945 |  | 0233 | 2-3B-01 |  | 2-69 | 甲24線(F25) 51NS |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K624_LCO_TAP | 11KV甲24線(K624) LCO TAP | FEEDER | [5 empty] | 497 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | F26 | 甲25線(F26) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0946 |  | 0234 | 2-3B-02 |  | 2-6A | 甲25線(F26) 79S |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K625_79UL | 11KV甲25線(K625) 79RY U/L | FEEDER | [5 empty] | 498 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | F26 | 甲25線(F26) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0947 |  | 0235 | 2-3B-03 |  | 2-6B | 甲25線(F26) 51NS |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K625_LCO_TAP | 11KV甲25線(K625) LCO TAP | FEEDER | [5 empty] | 499 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | F27 | 甲31線(F27) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0948 |  | 0236 | 2-3B-04 |  | 2-6C | 甲31線(F27) 79S |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K631_79UL | 11KV甲31線(K631) 79RY U/L | FEEDER | [5 empty] | 500 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | F27 | 甲31線(F27) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0949 |  | 0237 | 2-3B-05 |  | 2-6D | 甲31線(F27) 51NS |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K631_LCO_TAP | 11KV甲31線(K631) LCO TAP | FEEDER | [5 empty] | 501 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | F28 | 甲32線(F28) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0950 |  | 0238 | 2-3B-06 |  | 2-6E | 甲32線(F28) 79S |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K632_79UL | 11KV甲32線(K632) 79RY U/L | FEEDER | [5 empty] | 502 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | F28 | 甲32線(F28) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0951 |  | 0239 | 2-3B-07 |  | 2-6F | 甲32線(F28) 51NS |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K632_LCO_TAP | 11KV甲32線(K632) LCO TAP | FEEDER | [5 empty] | 503 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | F29 | 甲33線(F29) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0952 |  | 0240 | 2-3B-08 |  | 2-70 | 甲33線(F29) 79S |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K633_79UL | 11KV甲33線(K633) 79RY U/L | FEEDER | [5 empty] | 504 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | F29 | 甲33線(F29) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0953 |  | 0241 | 2-3B-09 |  | 2-71 | 甲33線(F29) 51NS |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K633_LCO_TAP | 11KV甲33線(K633) LCO TAP | FEEDER | [5 empty] | 505 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | F30 | 甲34線(F30) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0954 |  | 0242 | 2-3B-10 |  | 2-72 | 甲34線(F30) 79S |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K634_79UL | 11KV甲34線(K634) 79RY U/L | FEEDER | [5 empty] | 506 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | F30 | 甲34線(F30) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0955 |  | 0243 | 2-3B-11 |  | 2-73 | 甲34線(F30) 51NS |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K634_LCO_TAP | 11KV甲34線(K634) LCO TAP | FEEDER | [5 empty] | 507 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | F31 | 甲35線(F31) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0956 |  | 0244 | 2-3B-12 |  | 2-74 | 甲35線(F31) 79S |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K635_79UL | 11KV甲35線(K635) 79RY U/L | FEEDER | [5 empty] | 508 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | F31 | 甲35線(F31) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0957 |  | 0245 | 2-3B-13 |  | 2-75 | 甲35線(F31) 51NS |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K635_LCO_TAP | 11KV甲35線(K635) LCO TAP | FEEDER | [5 empty] | 509 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | F32 | 甲41線(F32) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0958 |  | 0246 | 2-3B-14 |  | 2-76 | 甲41線(F32) 79S |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K641_79UL | 11KV甲41線(K641) 79RY U/L | FEEDER | [5 empty] | 510 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | F32 | 甲41線(F32) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0959 |  | 0247 | 2-3B-15 |  | 2-77 | 甲41線(F32) 51NS |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K641_LCO_TAP | 11KV甲41線(K641) LCO TAP | FEEDER | [5 empty] | 511 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | F33 | 甲42線(F33) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0960 |  | 0248 | 2-3C-00 |  | 2-78 | 甲42線(F33) 79S |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K642_79UL | 11KV甲42線(K642) 79RY U/L | FEEDER | [5 empty] | 512 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | F33 | 甲42線(F33) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0961 |  | 0249 | 2-3C-01 |  | 2-79 | 甲42線(F33) 51NS |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K642_LCO_TAP | 11KV甲42線(K642) LCO TAP | FEEDER | [5 empty] | 513 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | F34 | 甲43線(F34) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0962 |  | 0250 | 2-3C-02 |  | 2-7A | 甲43線(F34) 79S |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K643_79UL | 11KV甲43線(K643) 79RY U/L | FEEDER | [5 empty] | 514 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | F34 | 甲43線(F34) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0963 |  | 0251 | 2-3C-03 |  | 2-7B | 甲43線(F34) 51NS |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K643_LCO_TAP | 11KV甲43線(K643) LCO TAP | FEEDER | [5 empty] | 515 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | F35 | 甲44線(F35) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0964 |  | 0252 | 2-3C-04 |  | 2-7C | 甲44線(F35) 79S |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K644_79UL | 11KV甲44線(K644) 79RY U/L | FEEDER | [5 empty] | 516 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | F35 | 甲44線(F35) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0965 |  | 0253 | 2-3C-05 |  | 2-7D | 甲44線(F35) 51NS |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K644_LCO_TAP | 11KV甲44線(K644) LCO TAP | FEEDER | [5 empty] | 517 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | F36 | 甲45線(F36) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0966 |  | 0254 | 2-3C-06 |  | 2-7E | 甲45線(F36) 79S |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K645_79UL | 11KV甲45線(K645) 79RY U/L | FEEDER | [5 empty] | 518 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | F36 | 甲45線(F36) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0967 |  | 0255 | 2-3C-07 |  | 2-7F | 甲45線(F36) 51NS |  |  |  |  | B2/D17_D1 | [8 empty] | 二甲DS.K645_LCO_TAP | 11KV甲45線(K645) LCO TAP | FEEDER | [5 empty] | 519 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0978 |  |  | 2-3D-02 |  |  | 23KV CBA |  |  |  |  | ELEM/D17_A1 | [8 empty] | 二甲DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | [5 empty] | 520 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0979 |  |  | 2-3D-03 |  |  | 23KV CBF |  |  |  |  | ELEM/D17_A1 | [8 empty] | 二甲DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | [5 empty] | 521 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | ComPoint |  |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0980 |  |  | 2-3D-04 |  |  | 23KV LOA |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.11/23KV_LOA | 11/23KV饋線復閉失敗閉鎖 | OTHER | [5 empty] | 522 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0981 |  |  | 2-3D-05 |  |  | CHG2 (通訊用直流電源故障) |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | [5 empty] | 523 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0982 |  |  | 2-3D-06 |  |  | ACFA (通訊設備AC故障) |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | [5 empty] | 524 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | StaDev | 所內設施 |  | R_Temp | 通訊室或控制室 |  | Status | 溫度警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0985 |  |  | 2-3D-09 |  |  | 通訊室或控制室溫度警報 |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.通信機房溫度 | 通訊室或控制室溫度警報 | OTHER | [5 empty] | 525 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | ComPoint |  |  | 25TA |  |  | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0986 |  |  | 2-3D-10 |  |  | 25TA 同步校核裝置超時 |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | [5 empty] | 526 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | ComPoint |  |  | 25PFA |  |  | Status | 同步校核電驛電源 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0987 |  |  | 2-3D-11 |  |  | 25PFA同步校核裝置電源 |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER | [5 empty] | 527 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | ComPoint |  |  | GRZ100 |  |  | Status | 電驛GRZ100閉鎖 | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0988 |  |  | 2-3D-12 |  |  | 本所各GRZ100 Ry LOCK/USE |  | LOCK為1 |  |  | B3/D17_A1 | [8 empty] | 二甲DS.BVS_RY | BVS GRZ100 RY U/L | OTHER | [5 empty] | 528 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | LOCK/USE | USE
D17 | 二甲DS | 0 |  | StaDev | 所內設施 |  | Fire1 | 受信總機 |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0992 |  |  | 2-3E-00 |  |  | 火災警報(1)受信總機 |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | [5 empty] | 529 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | StaDev | 所內設施 |  | Fire2 |  |  | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0993 |  |  | 2-3E-01 |  |  | 火災警報(2) |  | 所內門禁，目前無使用 |  |  | B3/D17_A1 | [8 empty] | 二甲DS.火災警報(2) | 火災警報(2) | OTHER | [5 empty] | 530 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | StaDev | 所內設施 |  | Burglar1 | 保全 |  | Status | 無人化防盜1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0995 |  |  | 2-3E-03 |  |  | 無人化防盜 (一) 保全 |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | [5 empty] | 531 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | StaDev | 所內設施 |  | Door1 | 外圍 |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0998 |  |  | 2-3E-06 |  |  | 無人化門禁 (一) 外圍 |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.無人化門禁(1) | 無人化門禁(1)外圍 | OTHER | [5 empty] | 532 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 1001 |  |  | 2-3E-09 |  |  | 所內電源 ACB1 |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | [5 empty] | 533 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D17 | 二甲DS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 1002 |  |  | 2-3E-10 |  |  | 所內電源 ACB2 |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | [5 empty] | 534 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D17 | 二甲DS | 0 |  | StaDev | 所內設施 |  | ACBT |  |  | Status | 所內電源ACB TIE | Close/Open | Y | 3 | DI-SP | [6 empty] | 1003 |  |  | 2-3E-11 |  |  | 所內電源 ACB TIE |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | [5 empty] | 535 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ON/OFF | OFF
D17 | 二甲DS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1004 |  |  | 2-3E-12 |  |  | STUV (所內欠壓警報) |  |  |  |  | ELEM/D17_A1 | [8 empty] | 二甲DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | [5 empty] | 536 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1005 |  |  | 2-3E-13 |  |  | 161KV CBA |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.161KV_CBA | 161KV斷路器重故障 | OTHER | [5 empty] | 537 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1006 |  |  | 2-3E-14 |  |  | 161KV CBF |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | [5 empty] | 538 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1007 |  |  | 2-3E-15 |  |  | VUA1 161kV#1BUS衡相Ry動作 |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | [5 empty] | 539 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1008 |  |  | 2-3F-00 |  |  | VUA2 161kV#2BUS衡相Ry動作 |  |  |  |  | B2/D17_A1 | [8 empty] | 二甲DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | [5 empty] | 540 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1009 |  |  | 2-3F-01 |  |  | DCE |  |  |  |  | ELEM/D17_A1 | [8 empty] | 二甲DS.直流電源DCE | 直流電源接地故障警報 | OTHER | [5 empty] | 541 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1010 |  |  | 2-3F-02 |  |  | CHG1 (直流電源故障) |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.直流充電機故障 | 直流充電機故障 | OTHER | [5 empty] | 542 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1011 |  |  | 2-3F-03 |  |  | ACBA |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.所內電源ACBA | 所內電源故障警報 | OTHER | [5 empty] | 543 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1012 |  |  | 2-3F-04 |  |  | DCA |  |  |  |  | ELEM/D17_A1 | [8 empty] | 二甲DS.直流電源DCA | 直流電源故障警報 | OTHER | [5 empty] | 544 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | ComPoint |  |  | BUS_RYFA |  |  | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1013 |  |  | 2-3F-05 |  |  | 161kV BUS 數位電驛故障 |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | [5 empty] | 545 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | ComPoint |  |  | 12B_CTFA | BUS_87CTFA | Element | Status | #1#2 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1014 |  |  | 2-3F-06 |  |  | 161kV BUS CT回路故障 |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.161KV_BUS_CTFA | 161KV BUS CT 回路故障 | OTHER | [5 empty] | 546 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | StaDev | 所內設施 |  | Water1 |  |  | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1015 |  |  | 2-3F-08 |  |  | UW1 (地下室水位警報 1) |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.水位警報(1) | 地下室水位警報(1) | OTHER |  | CDC_Mon1_DPC |  |  |  | 547 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | StaDev | 所內設施 |  | Water2 |  |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1016 |  |  | 2-3F-08 |  |  | UW1 (地下室水位警報 1) |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.水位警報(2) | 地下室水位警報(2) | OTHER |  | CDC_Mon1_DPC |  |  |  | 548 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | ComPoint |  |  | OLTC_A |  |  | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1017 |  |  | 2-3F-09 |  |  | OLTC 15分鐘內連動3次警報 OLTCA |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | [5 empty] | 549 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | ComPoint |  |  | 60A |  |  | Status | 電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 1018 |  |  | 2-3F-10 |  |  | 60A |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.23KV_SC_60A | 11/23KV SC 60A | OTHER | [5 empty] | 550 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | StaDev | 所內設施 |  | OilLeak1 |  |  | Status | 洩油池水位警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1019 |  |  | 2-3F-11 |  |  | 洩油池（中水位） |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.洩油池警報(1) | 洩油池水位(中)警報 | OTHER | [5 empty] | 551 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | StaDev | 所內設施 |  | OilLeak2 |  |  | Status | 洩油池水位警報2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1020 |  |  | 2-3F-12 |  |  | 洩油池（高水位） |  |  |  |  | B3/D17_A1 | [8 empty] | 二甲DS.洩油池警報(2) | 洩油池水位(高)警報 | OTHER | [5 empty] | 552 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | StaDev | 所內設施 |  | DD_Light |  |  | Status | 路燈照明 | OFF/ON | Y | 5 | DI-SP | [6 empty] | 1021 |  | 0256 | 2-3F-13 |  | 3-00 | 路燈 |  | SPARE |  |  | B3/D17_A1 | [8 empty] | 二甲DS.開關場照明(C) | 路燈照明 | OTHER | [5 empty] | 553 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
D17 | 二甲DS | 0 |  | StaDev | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1023 |  |  | 2-3F-15 |  |  | PMA |  |  |  |  | ELEM/D17_A1 | [8 empty] | 二甲DS.PMA | 電力量測表計故障 | OTHER | [5 empty] | 554 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
D17 | 二甲DS | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/D17_A1 | [12 empty] | 二甲DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: D17/161/1BUS/V; OPRD2: D17/161/2BUS/V
D17 | 二甲DS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/D17_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: D17/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
D17 | 二甲DS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/D17_A1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_6 | OPRD1: D17/161/1550/MW; OPRD2: D17/161/1560/MW; OPRD3: D17/161/1570/MW; OPRD4: D17/161/1580/MW; OPRD5: D17/161/1610/MW; OPRD6: D17/161/1620/MW
D17 | 二甲DS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/D17_A1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: D17/0/CalcPoint/OPRN2_MW
D17 | 二甲DS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/D17_A1 | [17 empty] | none
D17 | 二甲DS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/D17_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: D17/0/CalcPoint/OPRN1; OPRD2: D17/0/CalcPoint/OPRN2; OPRD3: D17/0/CalcPoint/PRFL_UL
D17 | 二甲DS |  |  | 3DTR | 3DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D17_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D17/11/350/I_R; OPRD2: D17/11/360/I_R
D17 | 二甲DS |  |  | 3DTR | 3DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D17_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D17/11/350/I_S; OPRD2: D17/11/360/I_S
D17 | 二甲DS |  |  | 3DTR | 3DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D17_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D17/11/350/I_T; OPRD2: D17/11/360/I_T
D17 | 二甲DS |  |  | 4DTR | 4DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D17_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D17/11/370/I_R; OPRD2: D17/11/380/I_R
D17 | 二甲DS |  |  | 4DTR | 4DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D17_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D17/11/370/I_S; OPRD2: D17/11/380/I_S
D17 | 二甲DS |  |  | 4DTR | 4DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D17_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D17/11/370/I_T; OPRD2: D17/11/380/I_T
D17 | 二甲DS | 161 | 161kV | 1550 | 二甲～奇美實紅線(1550) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D17_A1 | [12 empty] | 二甲DS.1550_AMP | 二甲奇美實紅線 AMP | LINE161 | AMP_CAL | C20R0964 | amp_cal | OPRD1: D17/161/1550/MW; OPRD2: D17/161/1550/MVAR; OPRD3: D17/0/CalcPoint/Vbs4
D17 | 二甲DS | 161 | 161kV | 1560 | 二甲～奇美實白線(1560) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D17_A1 | [12 empty] | 二甲DS.1560_AMP | 二甲奇美實白線 AMP | LINE161 | AMP_CAL | C20R0964 | amp_cal | OPRD1: D17/161/1560/MW; OPRD2: D17/161/1560/MVAR; OPRD3: D17/0/CalcPoint/Vbs4
D17 | 二甲DS | 161 | 161kV | 1570 | 仁德～二甲紅線(1570) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D17_A1 | [12 empty] | 二甲DS.1570_AMP | 仁德二甲紅線 AMP | LINE161 | AMP_CAL | C20R1930 | amp_cal | OPRD1: D17/161/1570/MW; OPRD2: D17/161/1570/MVAR; OPRD3: D17/0/CalcPoint/Vbs4
D17 | 二甲DS | 161 | 161kV | 1580 | 仁德～二甲白線(1580) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D17_A1 | [12 empty] | 二甲DS.1580_AMP | 仁德二甲白線 AMP | LINE161 | AMP_CAL | C20R1930 | amp_cal | OPRD1: D17/161/1580/MW; OPRD2: D17/161/1580/MVAR; OPRD3: D17/0/CalcPoint/Vbs4
D17 | 二甲DS | 161 | 161kV | 1610 | 龍崎～山上、二甲三路(1610) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D17_A1 | [12 empty] | 二甲DS.1610_AMP | 龍崎山上三路 AMP | LINE161 | AMP_CAL | C20R1790 | amp_cal | OPRD1: D17/161/1610/MW; OPRD2: D17/161/1610/MVAR; OPRD3: D17/0/CalcPoint/Vbs4
D17 | 二甲DS | 161 | 161kV | 1620 | 龍崎～山上、二甲四路(1620) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D17_A1 | [12 empty] | 二甲DS.1620_AMP | 龍崎山上四路 AMP | LINE161 | AMP_CAL | C20R1790 | amp_cal | OPRD1: D17/161/1620/MW; OPRD2: D17/161/1620/MVAR; OPRD3: D17/0/CalcPoint/Vbs4
D17 | 二甲DS |  |  | 3DTR(A) | #3DTR(A) |  | TR_PERM | [9 empty] | B1/D17_A1 | [12 empty] | 二甲DS.#3DTR(A)_PERM | #3DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D17//3DTR(A)/SupLocal; OPRD2: D17//3DTR(A)/Tap Chan
D17 | 二甲DS |  |  | 3DTR(B) | #3DTR(B) |  | TR_PERM | [9 empty] | B1/D17_A1 | [12 empty] | 二甲DS.#3DTR(B)_PERM | #3DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D17//3DTR(B)/SupLocal; OPRD2: D17//3DTR(B)/Tap Chan
D17 | 二甲DS |  |  | 4DTR(A) | #4DTR(A) |  | TR_PERM | [9 empty] | B1/D17_A1 | [12 empty] | 二甲DS.#4DTR(A)_PERM | #4DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D17//4DTR(A)/SupLocal; OPRD2: D17//4DTR(A)/Tap Chan
D17 | 二甲DS |  |  | 4DTR(B) | #4DTR(B) |  | TR_PERM | [9 empty] | B1/D17_A1 | [12 empty] | 二甲DS.#4DTR(B)_PERM | #4DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D17//4DTR(B)/SupLocal; OPRD2: D17//4DTR(B)/Tap Chan
D17 | 二甲DS | 11 | 11kV | 250 | #5SC(250) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D17_A1 | [12 empty] | 二甲DS.250_SC_MVAR | 11KV#5SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D17/11/250/CB; OPRD2: 6.9; OPRD3: 0
D17 | 二甲DS | 11 | 11kV | 260 | #6SC(260) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D17_A1 | [12 empty] | 二甲DS.260_SC_MVAR | 11KV#6SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D17/11/260/CB; OPRD2: 6.9; OPRD3: 0
D17 | 二甲DS | 11 | 11kV | 270 | #7SC(270) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D17_A1 | [12 empty] | 二甲DS.270_SC_MVAR | 11KV#7SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D17/11/270/CB; OPRD2: 6.9; OPRD3: 0
D17 | 二甲DS | 11 | 11kV | 280 | #8SC(280) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D17_A1 | [12 empty] | 二甲DS.280_SC_MVAR | 11KV#8SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D17/11/280/CB; OPRD2: 6.9; OPRD3: 0
D17 | 二甲DS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/D17_A1 | [12 empty] | 二甲DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_11 |  | com_alarm_30 | D17//3DTR/96B1 | D17//3DTR/GDA | D17//3DTR/96B2 | D17//3DTR/96D | D17//3DTR/63Q | D17//3DTR/PHA | D17//3DTR/87A | D17//3DTR/TRA | D17//3DTR/51ZA | D17//3DTR/96PA | D17//4DTR/TRA | D17//4DTR/96D | D17//4DTR/63Q | D17//4DTR/96B1 | D17//4DTR/96B2 | D17//4DTR/GDA | D17//4DTR/51ZA | D17//4DTR/PHA | D17//4DTR/87A | D17//4DTR/96PA | D17/11/350/GDA | D17/11/350/PHA | D17/11/360/GDA | D17/11/360/PHA | D17/11/370/GDA | D17/11/370/PHA | D17/11/380/GDA | D17/11/380/PHA | D17/161/1BUS/87A | D17/161/2BUS/87A
D17 | 二甲DS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/D17_A1 | [12 empty] | 二甲DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | STATION_FAULT_2 |  | com_alarm_2 | OPRD1: D17//3DTR/TRF; OPRD2: D17//4DTR/TRF
D17 | 二甲DS | 161 | 161kV | 1770_D1 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D17_D1 | [17 empty] | lamp2CC | OPRD1: D17/161/1770/CB
D17 | 二甲DS | 161 | 161kV | 1780_D1 | #4DTR(1780) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D17_D1 | [17 empty] | lamp2CC | OPRD1: D17/161/1780/CB
D17 | 二甲DS | 11 | 11kV | 350_D1 | #3DTR(A)(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D17_D1 | [17 empty] | lamp2CC | OPRD1: D17/11/350/CB
D17 | 二甲DS | 11 | 11kV | 360_D1 | #3DTR(B)(360) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D17_D1 | [17 empty] | lamp2CC | OPRD1: D17/11/360/CB
D17 | 二甲DS | 11 | 11kV | 370_D1 | #4DTR(A)(370) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D17_D1 | [17 empty] | lamp2CC | OPRD1: D17/11/370/CB
D17 | 二甲DS | 11 | 11kV | 380_D1 | #4DTR(B)(380) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D17_D1 | [17 empty] | lamp2CC | OPRD1: D17/11/380/CB
D17 | 二甲DS | 11 | 11kV | 350_D1 | #3DTR(A)(350) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/D17_D1 | [17 empty] | lamp2CC | OPRD1: D17/11/350/81A
D17 | 二甲DS | 11 | 11kV | 360_D1 | #3DTR(B)(360) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/D17_D1 | [17 empty] | lamp2CC | OPRD1: D17/11/360/81A
D17 | 二甲DS | 11 | 11kV | 370_D1 | #4DTR(A)(370) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/D17_D1 | [17 empty] | lamp2CC | OPRD1: D17/11/370/81A
D17 | 二甲DS | 11 | 11kV | 380_D1 | #4DTR(B)(380) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/D17_D1 | [17 empty] | lamp2CC | OPRD1: D17/11/380/81A
D17 | 二甲DS | 0 |  | RTU_D1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/D17_D1 | [17 empty] | lamp2CC | OPRD1: D17/0/RTU/RTU_R_L
D17 | 二甲DS | 11 | 11kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D17_D1 | [17 empty] | lamp2CC | OPRD1: D17/11/ComPoint/CBA
D17 | 二甲DS | 11 | 11kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | ELEM/D17_D1 | [17 empty] | lamp2CC | OPRD1: D17/11/ComPoint/CBF
D17 | 二甲DS | 0 |  | StaDev_D1 | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/D17_D1 | [17 empty] | lamp2CC | OPRD1: D17/0/StaDev/STUV
D17 | 二甲DS | 0 |  | StaDev_D1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D17_D1 | [17 empty] | lamp2CC | OPRD1: D17/0/StaDev/DCE
D17 | 二甲DS | 0 |  | StaDev_D1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D17_D1 | [17 empty] | lamp2CC | OPRD1: D17/0/StaDev/DCA
D17 | 二甲DS | 0 |  | StaDev_D1 | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D17_D1 | [17 empty] | lamp2CC | OPRD1: D17/0/StaDev/PMA

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D17 | 二甲DS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 二甲DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | D17/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
D17 | 二甲DS | 161 | 161kV | 1550 | 二甲奇美實紅線(1550) |  | I | [25 empty] | ADCS_S | [8 empty] | 二甲DS.1550_AMP | 二甲奇美實紅線 AMP | LINE161 | D17/161/1550/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C20R0964 | 867.599976 | 867.599976 | 964.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D17 | 二甲DS | 161 | 161kV | 1560 | 二甲奇美實白線(1560) |  | I | [25 empty] | ADCS_S | [8 empty] | 二甲DS.1560_AMP | 二甲奇美實白線 AMP | LINE161 | D17/161/1560/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C20R0964 | 867.599976 | 867.599976 | 964.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D17 | 二甲DS | 161 | 161kV | 1570 | 仁德二甲紅線(1570) |  | I | [25 empty] | ADCS_S | [8 empty] | 二甲DS.1570_AMP | 仁德二甲紅線 AMP | LINE161 | D17/161/1570/I |  | AMP_CAL |  |  | 5 | CalcAIPoint | [21 empty] | C20R1930 | 1737.800049 | 1737.800049 | 1930.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D17 | 二甲DS | 161 | 161kV | 1580 | 仁德二甲白線(1580) |  | I | [25 empty] | ADCS_S | [8 empty] | 二甲DS.1580_AMP | 仁德二甲白線 AMP | LINE161 | D17/161/1580/I |  | AMP_CAL |  |  | 6 | CalcAIPoint | [21 empty] | C20R1930 | 1737.800049 | 1737.800049 | 1930.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D17 | 二甲DS | 161 | 161kV | 1610 | 龍崎山上三路(1610) |  | I | [25 empty] | ADCS_S | [8 empty] | 二甲DS.1610_AMP | 龍崎山上三路 AMP | LINE161 | D17/161/1610/I |  | AMP_CAL |  |  | 7 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D17 | 二甲DS | 161 | 161kV | 1620 | 龍崎山上四路(1620) |  | I | [25 empty] | ADCS_S | [8 empty] | 二甲DS.1620_AMP | 龍崎山上四路 AMP | LINE161 | D17/161/1620/I |  | AMP_CAL |  |  | 8 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲11線KVA | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲11線KVA | 11KV甲11線KVA | FEEDER |  |  | KVA_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲11線KW | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲11線KW | 11KV甲11線KW | FEEDER |  |  | KW_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲12線KVA | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲12線KVA | 11KV甲12線KVA | FEEDER |  |  | KVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲12線KW | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲12線KW | 11KV甲12線KW | FEEDER |  |  | KW_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲13線KVA | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲13線KVA | 11KV甲13線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲13線KW | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲13線KW | 11KV甲13線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲14線KVA | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲14線KVA | 11KV甲14線KVA | FEEDER |  |  | KVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲14線KW | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲14線KW | 11KV甲14線KW | FEEDER |  |  | KW_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲15線KVA | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲15線KVA | 11KV甲15線KVA | FEEDER |  |  | KVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲15線KW | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲15線KW | 11KV甲15線KW | FEEDER |  |  | KW_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲21線KVA | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲21線KVA | 11KV甲21線KVA | FEEDER |  |  | KVA_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲21線KW | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲21線KW | 11KV甲21線KW | FEEDER |  |  | KW_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲22線KVA | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲22線KVA | 11KV甲22線KVA | FEEDER |  |  | KVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲22線KW | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲22線KW | 11KV甲22線KW | FEEDER |  |  | KW_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲23線KVA | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲23線KVA | 11KV甲23線KVA | FEEDER |  |  | KVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲23線KW | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲23線KW | 11KV甲23線KW | FEEDER |  |  | KW_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲24線KVA | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲24線KVA | 11KV甲24線KVA | FEEDER |  |  | KVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲24線KW | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲24線KW | 11KV甲24線KW | FEEDER |  |  | KW_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲25線KVA | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲25線KVA | 11KV甲25線KVA | FEEDER |  |  | KVA_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲25線KW | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲25線KW | 11KV甲25線KW | FEEDER |  |  | KW_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲31線KVA | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲31線KVA | 11KV甲31線KVA | FEEDER |  |  | KVA_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲31線KW | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲31線KW | 11KV甲31線KW | FEEDER |  |  | KW_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲32線KVA | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲32線KVA | 11KV甲32線KVA | FEEDER |  |  | KVA_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲32線KW | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲32線KW | 11KV甲32線KW | FEEDER |  |  | KW_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲33線KVA | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲33線KVA | 11KV甲33線KVA | FEEDER |  |  | KVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲33線KW | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲33線KW | 11KV甲33線KW | FEEDER |  |  | KW_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲34線KVA | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲34線KVA | 11KV甲34線KVA | FEEDER |  |  | KVA_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲34線KW | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲34線KW | 11KV甲34線KW | FEEDER |  |  | KW_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲35線KVA | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲35線KVA | 11KV甲35線KVA | FEEDER |  |  | KVA_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲35線KW | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲35線KW | 11KV甲35線KW | FEEDER |  |  | KW_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲41線KVA | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲41線KVA | 11KV甲41線KVA | FEEDER |  |  | KVA_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲41線KW | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲41線KW | 11KV甲41線KW | FEEDER |  |  | KW_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲42線KVA | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲42線KVA | 11KV甲42線KVA | FEEDER |  |  | KVA_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲42線KW | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲42線KW | 11KV甲42線KW | FEEDER |  |  | KW_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲43線KVA | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲43線KVA | 11KV甲43線KVA | FEEDER |  |  | KVA_CAL |  |  | 43 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲43線KW | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲43線KW | 11KV甲43線KW | FEEDER |  |  | KW_CAL |  |  | 44 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲44線KVA | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲44線KVA | 11KV甲44線KVA | FEEDER |  |  | KVA_CAL |  |  | 45 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲44線KW | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲44線KW | 11KV甲44線KW | FEEDER |  |  | KW_CAL |  |  | 46 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲45線KVA | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲45線KVA | 11KV甲45線KVA | FEEDER |  |  | KVA_CAL |  |  | 47 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  |  |  |  | 甲45線KW | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.甲45線KW | 11KV甲45線KW | FEEDER |  |  | KW_CAL |  |  | 48 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 二甲DS.#3DTR(A)_MVA | #3DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 49 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D17 | 二甲DS | 0 |  | 3DTR(A) | #3DTR(A) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 二甲DS.#3DTR(A)_LOAD | #3DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 50 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D17 | 二甲DS | 0 |  | 3DTR(A) | #3DTR(A) |  | PF | [25 empty] | ADCS_S | [8 empty] | 二甲DS.#3DTR(A)_PF | #3DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 51 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D17 | 二甲DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 二甲DS.#3DTR(B)_MVA | #3DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 52 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D17 | 二甲DS | 0 |  | 3DTR(B) | #3DTR(B) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 二甲DS.#3DTR(B)_LOAD | #3DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 53 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D17 | 二甲DS | 0 |  | 3DTR(B) | #3DTR(B) |  | PF | [25 empty] | ADCS_S | [8 empty] | 二甲DS.#3DTR(B)_PF | #3DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 54 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D17 | 二甲DS | 0 |  | 4DTR(A) | #4DTR二次側(A) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 二甲DS.#4DTR(A)_MVA | #4DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 55 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D17 | 二甲DS | 0 |  | 4DTR(A) | #4DTR(A) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 二甲DS.#4DTR(A)_LOAD | #4DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 56 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D17 | 二甲DS | 0 |  | 4DTR(A) | #4DTR(A) |  | PF | [25 empty] | ADCS_S | [8 empty] | 二甲DS.#4DTR(A)_PF | #4DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 57 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D17 | 二甲DS | 0 |  | 4DTR(B) | #4DTR二次側(B) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 二甲DS.#4DTR(B)_MVA | #4DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 58 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D17 | 二甲DS | 0 |  | 4DTR(B) | #4DTR(B) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 二甲DS.#4DTR(B)_LOAD | #4DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 59 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D17 | 二甲DS | 0 |  | 4DTR(B) | #4DTR(B) |  | PF | [25 empty] | ADCS_S | [8 empty] | 二甲DS.#4DTR(B)_PF | #4DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 60 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D17 | 二甲DS | 0 |  | 3DTR | #3DTR |  | MW | [25 empty] | ADCS_S | [8 empty] | 二甲DS.#3DTR_MW | #3DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 61 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  | 3DTR | #3DTR |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 二甲DS.#3DTR_MVAR | #3DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 62 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  | 3DTR | #3DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 二甲DS.#3DTR_MVA | #3DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 63 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D17 | 二甲DS | 0 |  | 3DTR | #3DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 二甲DS.#3DTR_LOAD | #3DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 64 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D17 | 二甲DS | 0 |  | 3DTR | #3DTR |  | PF | [25 empty] | ADCS_S | [8 empty] | 二甲DS.#3DTR_PF | #3DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 65 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D17 | 二甲DS | 0 |  | 4DTR | #4DTR |  | MW | [25 empty] | ADCS_S | [8 empty] | 二甲DS.#4DTR_MW | #4DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 66 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  | 4DTR | #4DTR |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 二甲DS.#4DTR_MVAR | #4DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 67 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  | 4DTR | #4DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 二甲DS.#4DTR_MVA | #4DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 68 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D17 | 二甲DS | 0 |  | 4DTR | #4DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 二甲DS.#4DTR_LOAD | #4DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 69 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D17 | 二甲DS | 0 |  | 4DTR | #4DTR |  | PF | [25 empty] | ADCS_S | [8 empty] | 二甲DS.#4DTR_PF | #4DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 70 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D17 | 二甲DS | 11 | 11kV | 250_SC | #5SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 二甲DS.250_SC_MVAR | 11KV#5SC MVAR | SC | D17/11/250/MVAR |  | SC_LBS_11 |  |  | 71 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 11 | 11kV | 260_SC | #6SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 二甲DS.260_SC_MVAR | 11KV#6SC MVAR | SC | D17/11/260/MVAR |  | SC_LBS_11 |  |  | 72 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 11 | 11kV | 270_SC | #7SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 二甲DS.270_SC_MVAR | 11KV#7SC MVAR | SC | D17/11/270/MVAR |  | SC_LBS_11 |  |  | 73 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 11 | 11kV | 280_SC | #8SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 二甲DS.280_SC_MVAR | 11KV#8SC MVAR | SC | D17/11/280/MVAR |  | SC_LBS_11 |  |  | 74 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  | TRTOT | 二甲主變瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 二甲DS.TRTOT_MW | 二甲主變瞬時供電量 MW |  |  |  | MTR_PQ_CAL |  |  | 75 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  | TRTOT | 二甲主變瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 二甲DS.TRTOT_MVAR | 二甲主變瞬時供電量 MVAR |  |  |  | MTR_PQ_CAL |  |  | 76 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  | TEN_DAYS18 | (1550+1560 MW) |  | MW | [25 empty] | CDCS | [8 empty] | 二甲DS.TEN_DAYS18_MW | (1550+1560 MW) |  |  |  | MTR_PQ_CAL |  |  | 77 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 0 |  | 300_CB | 300(300_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.300_CB_4 | 300 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 78 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | 400_CB | 400(400_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.400_CB_4 | 400 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 79 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 22 | 22kV | 11__CBA | 11/斷路器重故障(11__CBA) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.11/23KV_CBA_4 | 11/23KV斷路器重故障 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 80 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 22 | 22kV | 11__CBF | 11/斷路器輕故障(11__CBF) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.11/23KV_CBF_4 | 11/23KV斷路器輕故障 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 81 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | RTU_S_L | RTU |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 二甲DS.RTU_S/L_4 | RTU SUPY/LOCAL (D4) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 82 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D17 | 二甲DS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_S | [8 empty] | 二甲DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | D17/0/CalcPoint/SUBA |  | STATION_FAULT_11 |  |  | 83 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 變電所輕故障點燈 | 變電所輕故障點燈 |  | SUBF | [25 empty] | ADCS_S | [8 empty] | 二甲DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | D17/0/CalcPoint/SUBF |  | STATION_FAULT_2 |  |  | 84 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1550_AMP | 二甲奇美實紅線 | [27 empty] | ADCS_S | [8 empty] | 二甲DS.1550_AMP_A | 二甲奇美實紅線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 85 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D17 | 二甲DS | 161 | 161kV | 1560_AMP | 二甲奇美實白線 | [27 empty] | ADCS_S | [8 empty] | 二甲DS.1560_AMP_A | 二甲奇美實白線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 86 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D17 | 二甲DS | 161 | 161kV | 1570_AMP | 仁德二甲紅線 | [27 empty] | ADCS_S | [8 empty] | 二甲DS.1570_AMP_A | 仁德二甲紅線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 87 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D17 | 二甲DS | 161 | 161kV | 1580_AMP | 仁德二甲白線 | [27 empty] | ADCS_S | [8 empty] | 二甲DS.1580_AMP_A | 仁德二甲白線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 88 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D17 | 二甲DS | 161 | 161kV | 1610_AMP | 龍崎山上三路 | [27 empty] | ADCS_S | [8 empty] | 二甲DS.1610_AMP_A | 龍崎山上三路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 89 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D17 | 二甲DS | 161 | 161kV | 1620_AMP | 龍崎山上四路 | [27 empty] | ADCS_S | [8 empty] | 二甲DS.1620_AMP_A | 龍崎山上四路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 90 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D17 | 二甲DS | 0 |  | 3DTR(A) | #3DTR(A) |  | PERM | [25 empty] | ADCS_S | [8 empty] | 二甲DS.#3DTR(A)_PERM | #3DTR(A) TAP PERMISSION POINT | MTR | D17//3DTR(A)/TR_PERM |  | DTR_PERM |  |  | 91 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D17 | 二甲DS | 0 |  | 3DTR(B) | #3DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 二甲DS.#3DTR(B)_PERM | #3DTR TAP PERMISSION POINT | MTR | D17//3DTR(B)/TR_PERM |  | DTR_PERM |  |  | 92 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D17 | 二甲DS | 0 |  | 4DTR(A) | #4DTR(A) |  | PERM | [25 empty] | ADCS_S | [8 empty] | 二甲DS.#4DTR(A)_PERM | #4DTR(A) TAP PERMISSION POINT | MTR | D17//4DTR(A)/TR_PERM |  | DTR_PERM |  |  | 93 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D17 | 二甲DS | 0 |  | 4DTR(B) | #4DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 二甲DS.#4DTR(B)_PERM | #4DTR TAP PERMISSION POINT | MTR | D17//4DTR(B)/TR_PERM |  | DTR_PERM |  |  | 94 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D17 | 二甲DS | 0 |  | 3DTR_MVA | #3DTR | [27 empty] | ADCS_S | [8 empty] | 二甲DS.#3DTR_MVA_A | #3DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 95 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D17 | 二甲DS | 0 |  | 4DTR_MVA | #4DTR | [27 empty] | ADCS_S | [8 empty] | 二甲DS.#4DTR_MVA_A | #4DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 96 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D17 | 二甲DS | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_S | [8 empty] | 二甲DS.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_DS |  |  | 97 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 3ABUS | #3ABUS |  | 11KV#3ABUSC | [25 empty] | CDCS | [8 empty] | 二甲DS.11KV#3ABUSC | #3ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 98 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D17 | 二甲DS | 0 |  | 3BBUS | #3BBUS |  | 11KV#3BBUSC | [25 empty] | CDCS | [8 empty] | 二甲DS.11KV#3BBUSC | #3BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 99 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D17 | 二甲DS | 0 |  | 4ABUS | #4ABUS |  | 11KV#4ABUSC | [25 empty] | CDCS | [8 empty] | 二甲DS.11KV#4ABUSC | #4ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 100 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D17 | 二甲DS | 0 |  | 4BBUS | #4BBUS |  | 11KV#4BBUSC | [25 empty] | CDCS | [8 empty] | 二甲DS.11KV#4BBUSC | #4BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 101 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D17 | 二甲DS | 0 |  | TAP_OVER | TAP |  | SET | [25 empty] | ADCS_S | [8 empty] | 二甲DS.TAP_OVER_SET | TAP OVER HI/LO ALARM | MTR |  |  | 5000_CB_T4 |  |  | 102 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D17 | 二甲DS | 0 |  | BUS_OVER | BUS |  | SET | [25 empty] | ADCS_S | [8 empty] | 二甲DS.BUS_OVER_SET | BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B4 |  |  | 103 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D17 | 二甲DS | 0 |  | 5000 | 虛擬5000 |  | CB動作 | [25 empty] | ADCS_S | [8 empty] | 二甲DS.5000_CB動作 | 虛擬5000 CB動作,請查明原因處理 | MTR |  |  | 5000_CB_M |  |  | 104 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | 注意OLTC | 注意OLTC |  | BUS電壓異常 | [25 empty] | ADCS_S | [8 empty] | 二甲DS.BUS電壓異常 | 注意OLTC Tap位置,並將RPDC閉鎖 | OTHER |  |  | STATION_FAULT_2 |  |  | 105 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1BUS | #1BUS |  | V | [14 empty] | 0002 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | D17/161/1BUS/V |  |  |  | DNP | 106 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D17 | 二甲DS | 161 | 161kV | 2BUS | #2BUS |  | V | [14 empty] | 0003 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | D17/161/2BUS/V |  |  |  | DNP | 107 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D17 | 二甲DS | 11 | 11kV | 3ABUS | #3ABUS |  | V | [14 empty] | 0101 | [8 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.11KV#3ABUS_KV | 11KV #3ABUS KV | BUS | D17/11/3ABUS/V_R |  |  |  | DNP | 108 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D17 | 二甲DS | 11 | 11kV | 3BBUS | #3BBUS |  | V | [14 empty] | 0135 | [8 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.11KV#3BBUS_KV | 11KV #3BBUS KV | BUS | D17/11/3BBUS/V_R |  |  |  | DNP | 109 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D17 | 二甲DS | 11 | 11kV | 4ABUS | #4ABUS |  | V | [14 empty] | 0169 | [8 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.11KV#4ABUS_KV | 11KV #4ABUS KV | BUS | D17/11/4ABUS/V_R |  |  |  | DNP | 110 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D17 | 二甲DS | 11 | 11kV | 4BBUS | #4BBUS |  | V | [14 empty] | 0200 | [8 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.11KV#4BBUS_KV | 11KV #4BBUS KV | BUS | D17/11/4BBUS/V_R |  |  |  | DNP | 111 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D17 | 二甲DS | 161 | 161kV | 1550 | 二甲奇美實紅線(1550) |  | MW | [14 empty] | 0012 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.1550_MW | 二甲奇美實紅線 MW | LINE161 | D17/161/1550/MW |  |  |  | DNP | 112 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D17 | 二甲DS | 161 | 161kV | 1550 | 二甲奇美實紅線(1550) |  | MVAR | [14 empty] | 0013 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.1550_MVAR | 二甲奇美實紅線 MVAR | LINE161 | D17/161/1550/MVAR |  |  |  | DNP | 113 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D17 | 二甲DS | 161 | 161kV | 1560 | 二甲奇美實白線(1560) |  | MW | [14 empty] | 0014 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.1560_MW | 二甲奇美實白線 MW | LINE161 | D17/161/1560/MW |  |  |  | DNP | 114 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D17 | 二甲DS | 161 | 161kV | 1560 | 二甲奇美實白線(1560) |  | MVAR | [14 empty] | 0015 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.1560_MVAR | 二甲奇美實白線 MVAR | LINE161 | D17/161/1560/MVAR |  |  |  | DNP | 115 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D17 | 二甲DS | 161 | 161kV | 1570 | 仁德二甲紅線(1570) |  | MW | [14 empty] | 0016 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.1570_MW | 仁德二甲紅線 MW | LINE161 | D17/161/1570/MW |  |  |  | DNP | 116 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D17 | 二甲DS | 161 | 161kV | 1570 | 仁德二甲紅線(1570) |  | MVAR | [14 empty] | 0017 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.1570_MVAR | 仁德二甲紅線 MVAR | LINE161 | D17/161/1570/MVAR |  |  |  | DNP | 117 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D17 | 二甲DS | 161 | 161kV | 1580 | 仁德二甲白線(1580) |  | MW | [14 empty] | 0018 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.1580_MW | 仁德二甲白線 MW | LINE161 | D17/161/1580/MW |  |  |  | DNP | 118 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D17 | 二甲DS | 161 | 161kV | 1580 | 仁德二甲白線(1580) |  | MVAR | [14 empty] | 0019 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.1580_MVAR | 仁德二甲白線 MVAR | LINE161 | D17/161/1580/MVAR |  |  |  | DNP | 119 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D17 | 二甲DS | 161 | 161kV | 1610 | 龍崎山上三路(1610) |  | MW | [14 empty] | 0020 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.1610_MW | 龍崎山上三路 MW | LINE161 | D17/161/1610/MW |  |  |  | DNP | 120 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D17 | 二甲DS | 161 | 161kV | 1610 | 龍崎山上三路(1610) |  | MVAR | [14 empty] | 0021 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.1610_MVAR | 龍崎山上三路 MVAR | LINE161 | D17/161/1610/MVAR |  |  |  | DNP | 121 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D17 | 二甲DS | 161 | 161kV | 1620 | 龍崎山上四路(1620) |  | MW | [14 empty] | 0022 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.1620_MW | 龍崎山上四路 MW | LINE161 | D17/161/1620/MW |  |  |  | DNP | 122 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D17 | 二甲DS | 161 | 161kV | 1620 | 龍崎山上四路(1620) |  | MVAR | [14 empty] | 0023 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.1620_MVAR | 龍崎山上四路 MVAR | LINE161 | D17/161/1620/MVAR |  |  |  | DNP | 123 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲11線 | 甲11線 |  | 甲11線KVAR | [14 empty] | 0102 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲11線KVAR | 11KV甲11線 KVAR | FEEDER | D17/11/F17/KVAR |  |  |  | DNP | 124 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲11線 | 甲11線 |  | 甲11線A1 | [14 empty] | 0103 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲11線A1 | 11KV甲11線 R相AMP | FEEDER | D17/11/F17/I_R |  |  |  | DNP | 125 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲11線 | 甲11線 |  | 甲11線A2 | [14 empty] | 0104 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲11線A2 | 11KV甲11線 S相AMP | FEEDER | D17/11/F17/I_S |  |  |  | DNP | 126 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲11線 | 甲11線 |  | 甲11線A3 | [14 empty] | 0105 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲11線A3 | 11KV甲11線 T相AMP | FEEDER | D17/11/F17/I_T |  |  |  | DNP | 127 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲11線 | 甲11線 |  | 甲11線A0 | [14 empty] | 0106 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲11線A0 | 11KV甲11線 N相AMP | FEEDER | D17/11/F17/I_N |  |  |  | DNP | 128 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲12線 | 甲12線 |  | 甲12線KVAR | [14 empty] | 0107 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲12線KVAR | 11KV甲12線 KVAR | FEEDER | D17/11/F18/KVAR |  |  |  | DNP | 129 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲12線 | 甲12線 |  | 甲12線A1 | [14 empty] | 0108 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲12線A1 | 11KV甲12線 R相AMP | FEEDER | D17/11/F18/I_R |  |  |  | DNP | 130 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲12線 | 甲12線 |  | 甲12線A2 | [14 empty] | 0109 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲12線A2 | 11KV甲12線 S相AMP | FEEDER | D17/11/F18/I_S |  |  |  | DNP | 131 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲12線 | 甲12線 |  | 甲12線A3 | [14 empty] | 0110 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲12線A3 | 11KV甲12線 T相AMP | FEEDER | D17/11/F18/I_T |  |  |  | DNP | 132 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲12線 | 甲12線 |  | 甲12線A0 | [14 empty] | 0111 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲12線A0 | 11KV甲12線 N相AMP | FEEDER | D17/11/F18/I_N |  |  |  | DNP | 133 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲13線 | 甲13線 |  | 甲13線KVAR | [14 empty] | 0112 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲13線KVAR | 11KV甲13線 KVAR | FEEDER | D17/11/F19/KVAR |  |  |  | DNP | 134 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲13線 | 甲13線 |  | 甲13線A1 | [14 empty] | 0113 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲13線A1 | 11KV甲13線 R相AMP | FEEDER | D17/11/F19/I_R |  |  |  | DNP | 135 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲13線 | 甲13線 |  | 甲13線A2 | [14 empty] | 0114 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲13線A2 | 11KV甲13線 S相AMP | FEEDER | D17/11/F19/I_S |  |  |  | DNP | 136 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲13線 | 甲13線 |  | 甲13線A3 | [14 empty] | 0115 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲13線A3 | 11KV甲13線 T相AMP | FEEDER | D17/11/F19/I_T |  |  |  | DNP | 137 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲13線 | 甲13線 |  | 甲13線A0 | [14 empty] | 0116 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲13線A0 | 11KV甲13線 N相AMP | FEEDER | D17/11/F19/I_N |  |  |  | DNP | 138 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲14線 | 甲14線 |  | 甲14線KVAR | [14 empty] | 0117 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲14線KVAR | 11KV甲14線 KVAR | FEEDER | D17/11/F20/KVAR |  |  |  | DNP | 139 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲14線 | 甲14線 |  | 甲14線A1 | [14 empty] | 0118 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲14線A1 | 11KV甲14線 R相AMP | FEEDER | D17/11/F20/I_R |  |  |  | DNP | 140 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲14線 | 甲14線 |  | 甲14線A2 | [14 empty] | 0119 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲14線A2 | 11KV甲14線 S相AMP | FEEDER | D17/11/F20/I_S |  |  |  | DNP | 141 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲14線 | 甲14線 |  | 甲14線A3 | [14 empty] | 0120 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲14線A3 | 11KV甲14線 T相AMP | FEEDER | D17/11/F20/I_T |  |  |  | DNP | 142 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲14線 | 甲14線 |  | 甲14線A0 | [14 empty] | 0121 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲14線A0 | 11KV甲14線 N相AMP | FEEDER | D17/11/F20/I_N |  |  |  | DNP | 143 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲15線 | 甲15線 |  | 甲15線KVAR | [14 empty] | 0122 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲15線KVAR | 11KV甲15線 KVAR | FEEDER | D17/11/F21/KVAR |  |  |  | DNP | 144 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲15線 | 甲15線 |  | 甲15線A1 | [14 empty] | 0123 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲15線A1 | 11KV甲15線 R相AMP | FEEDER | D17/11/F21/I_R |  |  |  | DNP | 145 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲15線 | 甲15線 |  | 甲15線A2 | [14 empty] | 0124 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲15線A2 | 11KV甲15線 S相AMP | FEEDER | D17/11/F21/I_S |  |  |  | DNP | 146 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲15線 | 甲15線 |  | 甲15線A3 | [14 empty] | 0125 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲15線A3 | 11KV甲15線 T相AMP | FEEDER | D17/11/F21/I_T |  |  |  | DNP | 147 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲15線 | 甲15線 |  | 甲15線A0 | [14 empty] | 0126 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲15線A0 | 11KV甲15線 N相AMP | FEEDER | D17/11/F21/I_N |  |  |  | DNP | 148 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲21線 | 甲21線 |  | 甲21線KVAR | [14 empty] | 0136 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲21線KVAR | 11KV甲21線 KVAR | FEEDER | D17/11/F22/KVAR |  |  |  | DNP | 149 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲21線 | 甲21線 |  | 甲21線A1 | [14 empty] | 0137 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲21線A1 | 11KV甲21線 R相AMP | FEEDER | D17/11/F22/I_R |  |  |  | DNP | 150 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲21線 | 甲21線 |  | 甲21線A2 | [14 empty] | 0138 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲21線A2 | 11KV甲21線 S相AMP | FEEDER | D17/11/F22/I_S |  |  |  | DNP | 151 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲21線 | 甲21線 |  | 甲21線A3 | [14 empty] | 0139 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲21線A3 | 11KV甲21線 T相AMP | FEEDER | D17/11/F22/I_T |  |  |  | DNP | 152 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲21線 | 甲21線 |  | 甲21線A0 | [14 empty] | 0140 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲21線A0 | 11KV甲21線 N相AMP | FEEDER | D17/11/F22/I_N |  |  |  | DNP | 153 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲22線 | 甲22線 |  | 甲22線KVAR | [14 empty] | 0141 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲22線KVAR | 11KV甲22線 KVAR | FEEDER | D17/11/F23/KVAR |  |  |  | DNP | 154 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲22線 | 甲22線 |  | 甲22線A1 | [14 empty] | 0142 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲22線A1 | 11KV甲22線 R相AMP | FEEDER | D17/11/F23/I_R |  |  |  | DNP | 155 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲22線 | 甲22線 |  | 甲22線A2 | [14 empty] | 0143 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲22線A2 | 11KV甲22線 S相AMP | FEEDER | D17/11/F23/I_S |  |  |  | DNP | 156 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲22線 | 甲22線 |  | 甲22線A3 | [14 empty] | 0144 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲22線A3 | 11KV甲22線 T相AMP | FEEDER | D17/11/F23/I_T |  |  |  | DNP | 157 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲22線 | 甲22線 |  | 甲22線A0 | [14 empty] | 0145 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲22線A0 | 11KV甲22線 N相AMP | FEEDER | D17/11/F23/I_N |  |  |  | DNP | 158 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲23線 | 甲23線 |  | 甲23線KVAR | [14 empty] | 0146 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲23線KVAR | 11KV甲23線 KVAR | FEEDER | D17/11/F24/KVAR |  |  |  | DNP | 159 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲23線 | 甲23線 |  | 甲23線A1 | [14 empty] | 0147 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲23線A1 | 11KV甲23線 R相AMP | FEEDER | D17/11/F24/I_R |  |  |  | DNP | 160 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲23線 | 甲23線 |  | 甲23線A2 | [14 empty] | 0148 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲23線A2 | 11KV甲23線 S相AMP | FEEDER | D17/11/F24/I_S |  |  |  | DNP | 161 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲23線 | 甲23線 |  | 甲23線A3 | [14 empty] | 0149 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲23線A3 | 11KV甲23線 T相AMP | FEEDER | D17/11/F24/I_T |  |  |  | DNP | 162 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲23線 | 甲23線 |  | 甲23線A0 | [14 empty] | 0150 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲23線A0 | 11KV甲23線 N相AMP | FEEDER | D17/11/F24/I_N |  |  |  | DNP | 163 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲24線 | 甲24線 |  | 甲24線KVAR | [14 empty] | 0151 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲24線KVAR | 11KV甲24線 KVAR | FEEDER | D17/11/F25/KVAR |  |  |  | DNP | 164 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲24線 | 甲24線 |  | 甲24線A1 | [14 empty] | 0152 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲24線A1 | 11KV甲24線 R相AMP | FEEDER | D17/11/F25/I_R |  |  |  | DNP | 165 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲24線 | 甲24線 |  | 甲24線A2 | [14 empty] | 0153 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲24線A2 | 11KV甲24線 S相AMP | FEEDER | D17/11/F25/I_S |  |  |  | DNP | 166 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲24線 | 甲24線 |  | 甲24線A3 | [14 empty] | 0154 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲24線A3 | 11KV甲24線 T相AMP | FEEDER | D17/11/F25/I_T |  |  |  | DNP | 167 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲24線 | 甲24線 |  | 甲24線A0 | [14 empty] | 0155 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲24線A0 | 11KV甲24線 N相AMP | FEEDER | D17/11/F25/I_N |  |  |  | DNP | 168 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲25線 | 甲25線 |  | 甲25線KVAR | [14 empty] | 0156 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲25線KVAR | 11KV甲25線 KVAR | FEEDER | D17/11/F26/KVAR |  |  |  | DNP | 169 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲25線 | 甲25線 |  | 甲25線A1 | [14 empty] | 0157 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲25線A1 | 11KV甲25線 R相AMP | FEEDER | D17/11/F26/I_R |  |  |  | DNP | 170 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲25線 | 甲25線 |  | 甲25線A2 | [14 empty] | 0158 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲25線A2 | 11KV甲25線 S相AMP | FEEDER | D17/11/F26/I_S |  |  |  | DNP | 171 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲25線 | 甲25線 |  | 甲25線A3 | [14 empty] | 0159 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲25線A3 | 11KV甲25線 T相AMP | FEEDER | D17/11/F26/I_T |  |  |  | DNP | 172 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲25線 | 甲25線 |  | 甲25線A0 | [14 empty] | 0160 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲25線A0 | 11KV甲25線 N相AMP | FEEDER | D17/11/F26/I_N |  |  |  | DNP | 173 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲31線 | 甲31線 |  | 甲31線KVAR | [14 empty] | 0170 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲31線KVAR | 11KV甲31線 KVAR | FEEDER | D17/11/F27/KVAR |  |  |  | DNP | 174 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲31線 | 甲31線 |  | 甲31線A1 | [14 empty] | 0171 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲31線A1 | 11KV甲31線 R相AMP | FEEDER | D17/11/F27/I_R |  |  |  | DNP | 175 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲31線 | 甲31線 |  | 甲31線A2 | [14 empty] | 0172 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲31線A2 | 11KV甲31線 S相AMP | FEEDER | D17/11/F27/I_S |  |  |  | DNP | 176 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲31線 | 甲31線 |  | 甲31線A3 | [14 empty] | 0173 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲31線A3 | 11KV甲31線 T相AMP | FEEDER | D17/11/F27/I_T |  |  |  | DNP | 177 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲31線 | 甲31線 |  | 甲31線A0 | [14 empty] | 0174 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲31線A0 | 11KV甲31線 N相AMP | FEEDER | D17/11/F27/I_N |  |  |  | DNP | 178 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲32線 | 甲32線 |  | 甲32線KVAR | [14 empty] | 0175 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲32線KVAR | 11KV甲32線 KVAR | FEEDER | D17/11/F28/KVAR |  |  |  | DNP | 179 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲32線 | 甲32線 |  | 甲32線A1 | [14 empty] | 0176 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲32線A1 | 11KV甲32線 R相AMP | FEEDER | D17/11/F28/I_R |  |  |  | DNP | 180 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲32線 | 甲32線 |  | 甲32線A2 | [14 empty] | 0177 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲32線A2 | 11KV甲32線 S相AMP | FEEDER | D17/11/F28/I_S |  |  |  | DNP | 181 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲32線 | 甲32線 |  | 甲32線A3 | [14 empty] | 0178 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲32線A3 | 11KV甲32線 T相AMP | FEEDER | D17/11/F28/I_T |  |  |  | DNP | 182 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲32線 | 甲32線 |  | 甲32線A0 | [14 empty] | 0179 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲32線A0 | 11KV甲32線 N相AMP | FEEDER | D17/11/F28/I_N |  |  |  | DNP | 183 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲33線 | 甲33線 |  | 甲33線KVAR | [14 empty] | 0180 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲33線KVAR | 11KV甲33線 KVAR | FEEDER | D17/11/F29/KVAR |  |  |  | DNP | 184 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲33線 | 甲33線 |  | 甲33線A1 | [14 empty] | 0181 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲33線A1 | 11KV甲33線 R相AMP | FEEDER | D17/11/F29/I_R |  |  |  | DNP | 185 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲33線 | 甲33線 |  | 甲33線A2 | [14 empty] | 0182 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲33線A2 | 11KV甲33線 S相AMP | FEEDER | D17/11/F29/I_S |  |  |  | DNP | 186 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲33線 | 甲33線 |  | 甲33線A3 | [14 empty] | 0183 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲33線A3 | 11KV甲33線 T相AMP | FEEDER | D17/11/F29/I_T |  |  |  | DNP | 187 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲33線 | 甲33線 |  | 甲33線A0 | [14 empty] | 0184 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲33線A0 | 11KV甲33線 N相AMP | FEEDER | D17/11/F29/I_N |  |  |  | DNP | 188 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲34線 | 甲34線 |  | 甲34線KVAR | [14 empty] | 0185 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲34線KVAR | 11KV甲34線 KVAR | FEEDER | D17/11/F30/KVAR |  |  |  | DNP | 189 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲34線 | 甲34線 |  | 甲34線A1 | [14 empty] | 0186 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲34線A1 | 11KV甲34線 R相AMP | FEEDER | D17/11/F30/I_R |  |  |  | DNP | 190 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲34線 | 甲34線 |  | 甲34線A2 | [14 empty] | 0187 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲34線A2 | 11KV甲34線 S相AMP | FEEDER | D17/11/F30/I_S |  |  |  | DNP | 191 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲34線 | 甲34線 |  | 甲34線A3 | [14 empty] | 0188 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲34線A3 | 11KV甲34線 T相AMP | FEEDER | D17/11/F30/I_T |  |  |  | DNP | 192 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲34線 | 甲34線 |  | 甲34線A0 | [14 empty] | 0189 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲34線A0 | 11KV甲34線 N相AMP | FEEDER | D17/11/F30/I_N |  |  |  | DNP | 193 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲35線 | 甲35線 |  | 甲35線KVAR | [14 empty] | 0190 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲35線KVAR | 11KV甲35線 KVAR | FEEDER | D17/11/F31/KVAR |  |  |  | DNP | 194 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲35線 | 甲35線 |  | 甲35線A1 | [14 empty] | 0191 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲35線A1 | 11KV甲35線 R相AMP | FEEDER | D17/11/F31/I_R |  |  |  | DNP | 195 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲35線 | 甲35線 |  | 甲35線A2 | [14 empty] | 0192 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲35線A2 | 11KV甲35線 S相AMP | FEEDER | D17/11/F31/I_S |  |  |  | DNP | 196 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲35線 | 甲35線 |  | 甲35線A3 | [14 empty] | 0193 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲35線A3 | 11KV甲35線 T相AMP | FEEDER | D17/11/F31/I_T |  |  |  | DNP | 197 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲35線 | 甲35線 |  | 甲35線A0 | [14 empty] | 0194 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲35線A0 | 11KV甲35線 N相AMP | FEEDER | D17/11/F31/I_N |  |  |  | DNP | 198 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲41線 | 甲41線 |  | 甲41線KVAR | [14 empty] | 0201 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲41線KVAR | 11KV甲41線 KVAR | FEEDER | D17/11/F32/KVAR |  |  |  | DNP | 199 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲41線 | 甲41線 |  | 甲41線A1 | [14 empty] | 0202 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲41線A1 | 11KV甲41線 R相AMP | FEEDER | D17/11/F32/I_R |  |  |  | DNP | 200 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲41線 | 甲41線 |  | 甲41線A2 | [14 empty] | 0203 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲41線A2 | 11KV甲41線 S相AMP | FEEDER | D17/11/F32/I_S |  |  |  | DNP | 201 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲41線 | 甲41線 |  | 甲41線A3 | [14 empty] | 0204 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲41線A3 | 11KV甲41線 T相AMP | FEEDER | D17/11/F32/I_T |  |  |  | DNP | 202 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲41線 | 甲41線 |  | 甲41線A0 | [14 empty] | 0205 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲41線A0 | 11KV甲41線 N相AMP | FEEDER | D17/11/F32/I_N |  |  |  | DNP | 203 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲42線 | 甲42線 |  | 甲42線KVAR | [14 empty] | 0206 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲42線KVAR | 11KV甲42線 KVAR | FEEDER | D17/11/F33/KVAR |  |  |  | DNP | 204 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲42線 | 甲42線 |  | 甲42線A1 | [14 empty] | 0207 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲42線A1 | 11KV甲42線 R相AMP | FEEDER | D17/11/F33/I_R |  |  |  | DNP | 205 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲42線 | 甲42線 |  | 甲42線A2 | [14 empty] | 0208 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲42線A2 | 11KV甲42線 S相AMP | FEEDER | D17/11/F33/I_S |  |  |  | DNP | 206 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲42線 | 甲42線 |  | 甲42線A3 | [14 empty] | 0209 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲42線A3 | 11KV甲42線 T相AMP | FEEDER | D17/11/F33/I_T |  |  |  | DNP | 207 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲42線 | 甲42線 |  | 甲42線A0 | [14 empty] | 0210 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲42線A0 | 11KV甲42線 N相AMP | FEEDER | D17/11/F33/I_N |  |  |  | DNP | 208 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲43線 | 甲43線 |  | 甲43線KVAR | [14 empty] | 0211 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲43線KVAR | 11KV甲43線 KVAR | FEEDER | D17/11/F34/KVAR |  |  |  | DNP | 209 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲43線 | 甲43線 |  | 甲43線A1 | [14 empty] | 0212 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲43線A1 | 11KV甲43線 R相AMP | FEEDER | D17/11/F34/I_R |  |  |  | DNP | 210 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲43線 | 甲43線 |  | 甲43線A2 | [14 empty] | 0213 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲43線A2 | 11KV甲43線 S相AMP | FEEDER | D17/11/F34/I_S |  |  |  | DNP | 211 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲43線 | 甲43線 |  | 甲43線A3 | [14 empty] | 0214 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲43線A3 | 11KV甲43線 T相AMP | FEEDER | D17/11/F34/I_T |  |  |  | DNP | 212 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲43線 | 甲43線 |  | 甲43線A0 | [14 empty] | 0215 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲43線A0 | 11KV甲43線 N相AMP | FEEDER | D17/11/F34/I_N |  |  |  | DNP | 213 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲44線 | 甲44線 |  | 甲44線KVAR | [14 empty] | 0216 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲44線KVAR | 11KV甲44線 KVAR | FEEDER | D17/11/F35/KVAR |  |  |  | DNP | 214 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲44線 | 甲44線 |  | 甲44線A1 | [14 empty] | 0217 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲44線A1 | 11KV甲44線 R相AMP | FEEDER | D17/11/F35/I_R |  |  |  | DNP | 215 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲44線 | 甲44線 |  | 甲44線A2 | [14 empty] | 0218 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲44線A2 | 11KV甲44線 S相AMP | FEEDER | D17/11/F35/I_S |  |  |  | DNP | 216 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲44線 | 甲44線 |  | 甲44線A3 | [14 empty] | 0219 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲44線A3 | 11KV甲44線 T相AMP | FEEDER | D17/11/F35/I_T |  |  |  | DNP | 217 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲44線 | 甲44線 |  | 甲44線A0 | [14 empty] | 0220 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲44線A0 | 11KV甲44線 N相AMP | FEEDER | D17/11/F35/I_N |  |  |  | DNP | 218 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲45線 | 甲45線 |  | 甲45線KVAR | [14 empty] | 0221 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲45線KVAR | 11KV甲45線 KVAR | FEEDER | D17/11/F36/KVAR |  |  |  | DNP | 219 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲45線 | 甲45線 |  | 甲45線A1 | [14 empty] | 0222 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲45線A1 | 11KV甲45線 R相AMP | FEEDER | D17/11/F36/I_R |  |  |  | DNP | 220 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲45線 | 甲45線 |  | 甲45線A2 | [14 empty] | 0223 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲45線A2 | 11KV甲45線 S相AMP | FEEDER | D17/11/F36/I_S |  |  |  | DNP | 221 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲45線 | 甲45線 |  | 甲45線A3 | [14 empty] | 0224 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲45線A3 | 11KV甲45線 T相AMP | FEEDER | D17/11/F36/I_T |  |  |  | DNP | 222 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | 甲45線 | 甲45線 |  | 甲45線A0 | [14 empty] | 0225 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 二甲DS.甲45線A0 | 11KV甲45線 N相AMP | FEEDER | D17/11/F36/I_N |  |  |  | DNP | 223 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 0 |  | 1500TIE | 1500TIE |  | I | [14 empty] | 0024 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.1500TIE_AMP | 1500TIE AMP | TIE | D17/161/1500/I_R |  |  |  | DNP | 224 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | _300 | 300 |  | I_R | [14 empty] | 0127 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.11KV_300_A1 | 11KV 300 R相AMP | TIE | D17/11/300/I_R |  |  |  | DNP | 225 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | _300 | 300 |  | I_S | [14 empty] | 0128 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.11KV_300_A2 | 11KV 300 S相AMP | TIE | D17/11/300/I_S |  |  |  | DNP | 226 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | _300 | 300 |  | I_T | [14 empty] | 0129 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.11KV_300_A3 | 11KV 300 T相AMP | TIE | D17/11/300/I_T |  |  |  | DNP | 227 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | _400 | 400 |  | I_R | [14 empty] | 0161 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.11KV_400_A1 | 11KV 400 R相AMP | TIE | D17/11/340/I_R |  |  |  | DNP | 228 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | _400 | 400 |  | I_S | [14 empty] | 0162 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.11KV_400_A2 | 11KV 400 S相AMP | TIE | D17/11/340/I_S |  |  |  | DNP | 229 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 11 | 11kV | _400 | 400 |  | I_T | [14 empty] | 0163 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.11KV_400_A3 | 11KV 400 T相AMP | TIE | D17/11/340/I_T |  |  |  | DNP | 230 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | MW | [14 empty] | 0096 | [8 empty] | MW_-54_54(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.#3DTR(A)_MW | #3DTR二次側(A) MW | MTR | D17/11/350/KW |  |  |  | DNP | 231 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.054000 | 0.010000
D17 | 二甲DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | MVAR | [14 empty] | 0097 | [8 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.#3DTR(A)_MVAR | #3DTR二次側(A) MVAR | MTR | D17/11/350/KVAR |  |  |  | DNP | 232 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.036000 | 0.010000
D17 | 二甲DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | I_R | [14 empty] | 0098 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.#3DTR(A)_A1 | #3DTR二次側(A) R相AMP | MTR | D17/11/350/I_R |  |  |  | DNP | 233 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | I_S | [14 empty] | 0099 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.#3DTR(A)_A2 | #3DTR二次側(A) S相AMP | MTR | D17/11/350/I_S |  |  |  | DNP | 234 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | I_T | [14 empty] | 0100 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.#3DTR(A)_A3 | #3DTR二次側(A) T相AMP | MTR | D17/11/350/I_T |  |  |  | DNP | 235 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 0 |  | 3DTR | #3DTR |  | OilTemp | [14 empty] | 0040 | [8 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.#3DTR_OIL | #3DTR 油溫 | MTR | D17//3DTR/OilTemp |  |  |  | DNP | 236 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D17 | 二甲DS | 0 |  | 3DTR(A) | #3DTR(A) |  | CoilTemp | [14 empty] | 0041 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.#3DTR(A)_COIL | #3DTR(A) 線溫 | MTR | D17//3DTR(A)/CoilTemp |  |  |  | DNP | 237 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D17 | 二甲DS | 0 |  | 3DTR(A) | #3DTR(A) |  | TapPosMv | [14 empty] | 0043 |  | 0061 | [6 empty] | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 二甲DS.#3DTR(A)_TAP | #3DTR(A) OLTC TAP | MTR | D17//3DTR(A)/TapPosMv |  |  |  | DNP | 238 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D17 | 二甲DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | MW | [14 empty] | 0130 | [8 empty] | MW_-54_54(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.#3DTR(B)_MW | #3DTR二次側(B) MW | MTR | D17/11/360/KW |  |  |  | DNP | 239 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.054000 | 0.010000
D17 | 二甲DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | MVAR | [14 empty] | 0131 | [8 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.#3DTR(B)_MVAR | #3DTR二次側(B) MVAR | MTR | D17/11/360/KVAR |  |  |  | DNP | 240 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.036000 | 0.010000
D17 | 二甲DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | I_R | [14 empty] | 0132 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.#3DTR(B)_A1 | #3DTR二次側(B) R相AMP | MTR | D17/11/360/I_R |  |  |  | DNP | 241 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | I_S | [14 empty] | 0133 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.#3DTR(B)_A2 | #3DTR二次側(B) S相AMP | MTR | D17/11/360/I_S |  |  |  | DNP | 242 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | I_T | [14 empty] | 0134 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.#3DTR(B)_A3 | #3DTR二次側(B) T相AMP | MTR | D17/11/360/I_T |  |  |  | DNP | 243 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 0 |  | 3DTR(B) | #3DTR(B) |  | CoilTemp | [14 empty] | 0042 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.#3DTR(B)_COIL | #3DTR(B) 線溫 | MTR | D17//3DTR(B)/CoilTemp |  |  |  | DNP | 244 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D17 | 二甲DS | 0 |  | 3DTR(B) | #3DTR(B) |  | TapPosMv | [14 empty] | 0044 |  | 0063 | [6 empty] | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 二甲DS.#3DTR(B)_TAP | #3DTR(B) OLTC TAP | MTR | D17//3DTR(B)/TapPosMv |  |  |  | DNP | 245 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D17 | 二甲DS | 0 |  | 4DTR(A) | #4DTR二次側(A) |  | MW | [14 empty] | 0164 | [8 empty] | MW_-54_54(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.#4DTR(A)_MW | #4DTR二次側(A) MW | MTR | D17/11/370/KW |  |  |  | DNP | 246 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.054000 | 0.010000
D17 | 二甲DS | 0 |  | 4DTR(A) | #4DTR二次側(A) |  | MVAR | [14 empty] | 0165 | [8 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.#4DTR(A)_MVAR | #4DTR二次側(A) MVAR | MTR | D17/11/370/KVAR |  |  |  | DNP | 247 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.036000 | 0.010000
D17 | 二甲DS | 0 |  | 4DTR(A) | #4DTR二次側(A) |  | I_R | [14 empty] | 0166 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.#4DTR(A)_A1 | #4DTR二次側(A) R相AMP | MTR | D17/11/370/I_R |  |  |  | DNP | 248 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 0 |  | 4DTR(A) | #4DTR二次側(A) |  | I_S | [14 empty] | 0167 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.#4DTR(A)_A2 | #4DTR二次側(A) S相AMP | MTR | D17/11/370/I_S |  |  |  | DNP | 249 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 0 |  | 4DTR(A) | #4DTR二次側(A) |  | I_T | [14 empty] | 0168 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.#4DTR(A)_A3 | #4DTR二次側(A) T相AMP | MTR | D17/11/370/I_T |  |  |  | DNP | 250 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 0 |  | 4DTR | #4DTR |  | OilTemp | [14 empty] | 0045 | [8 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.#4DTR_OIL | #4DTR 油溫 | MTR | D17//4DTR/OilTemp |  |  |  | DNP | 251 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D17 | 二甲DS | 0 |  | 4DTR(A) | #4DTR(A) |  | CoilTemp | [14 empty] | 0046 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.#4DTR(A)_COIL | #4DTR(A) 線溫 | MTR | D17//4DTR(A)/CoilTemp |  |  |  | DNP | 252 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D17 | 二甲DS | 0 |  | 4DTR(A) | #4DTR(A) |  | TapPosMv | [14 empty] | 0048 |  | 0065 | [6 empty] | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 二甲DS.#4DTR(A)_TAP | #4DTR(A) OLTC TAP | MTR | D17//4DTR(A)/TapPosMv |  |  |  | DNP | 253 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D17 | 二甲DS | 0 |  | 4DTR(B) | #4DTR二次側(B) |  | MW | [14 empty] | 0195 | [8 empty] | MW_-54_54(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.#4DTR(B)_MW | #4DTR二次側(B) MW | MTR | D17/11/380/KW |  |  |  | DNP | 254 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.054000 | 0.010000
D17 | 二甲DS | 0 |  | 4DTR(B) | #4DTR二次側(B) |  | MVAR | [14 empty] | 0196 | [8 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.#4DTR(B)_MVAR | #4DTR二次側(B) MVAR | MTR | D17/11/380/KVAR |  |  |  | DNP | 255 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.036000 | 0.010000
D17 | 二甲DS | 0 |  | 4DTR(B) | #4DTR二次側(B) |  | I_R | [14 empty] | 0197 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.#4DTR(B)_A1 | #4DTR二次側(B) R相AMP | MTR | D17/11/380/I_R |  |  |  | DNP | 256 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 0 |  | 4DTR(B) | #4DTR二次側(B) |  | I_S | [14 empty] | 0198 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.#4DTR(B)_A2 | #4DTR二次側(B) S相AMP | MTR | D17/11/380/I_S |  |  |  | DNP | 257 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 0 |  | 4DTR(B) | #4DTR二次側(B) |  | I_T | [14 empty] | 0199 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.#4DTR(B)_A3 | #4DTR二次側(B) T相AMP | MTR | D17/11/380/I_T |  |  |  | DNP | 258 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 0 |  | 4DTR(B) | #4DTR(B) |  | CoilTemp | [14 empty] | 0047 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.#4DTR(B)_COIL | #4DTR(B) 線溫 | MTR | D17//4DTR(B)/CoilTemp |  |  |  | DNP | 259 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D17 | 二甲DS | 0 |  | 4DTR(B) | #4DTR(B) |  | TapPosMv | [14 empty] | 0049 |  | 0067 | [6 empty] | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 二甲DS.#4DTR(B)_TAP | #4DTR(B) OLTC TAP | MTR | D17//4DTR(B)/TapPosMv |  |  |  | DNP | 260 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D17 | 二甲DS | 0 |  |  |  |  | DCV_N | [14 empty] | 0026 | [8 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.直流N電源電壓 | 直流N電源電壓 | OTHER | D17/0/StaDev/DCV_N |  |  |  | DNP | 261 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D17 | 二甲DS | 0 |  |  |  |  | DCV_P | [14 empty] | 0025 | [8 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 二甲DS.直流P電源電壓 | 直流P電源電壓 | OTHER | D17/0/StaDev/DCV_P |  |  |  | DNP | 262 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D17 | 二甲DS | 22 | 22kV | 安集大成(K461) | 安集大成(K461) |  | 安集大成KVAR | [14 empty] | 0322 | [8 empty] | KVAR_-6000_6000(-2000_2000) |  | DDCS4_1 | [8 empty] | 仁德DS.安集大成KVAR | 23KV安集大成(K461) KVAR | FEEDER |  |  |  |  | DNP | 263 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 14.400000 | 0.010000
D17 | 二甲DS | 22 | 22kV | 安集大成(K461) | 安集大成(K461) |  | 安集大成A1 | [14 empty] | 0323 | [8 empty] | A_-400_400(-2000_2000) |  | DDCS4_1 | [8 empty] | 仁德DS.安集大成A1 | 23KV安集大成(K461) R相AMP | FEEDER |  |  |  |  | DNP | 264 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 22 | 22kV | 安集大成(K461) | 安集大成(K461) |  | 安集大成A2 | [14 empty] | 0324 | [8 empty] | A_-400_400(-2000_2000) |  | DDCS4_1 | [8 empty] | 仁德DS.安集大成A2 | 23KV安集大成(K461) S相AMP | FEEDER |  |  |  |  | DNP | 265 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 22 | 22kV | 安集大成(K461) | 安集大成(K461) |  | 安集大成A3 | [14 empty] | 0325 | [8 empty] | A_-400_400(-2000_2000) |  | DDCS4_1 | [8 empty] | 仁德DS.安集大成A3 | 23KV安集大成(K461) T相AMP | FEEDER |  |  |  |  | DNP | 266 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D17 | 二甲DS | 22 | 22kV | 安集大成 | 安集大成(K461) |  | KV1 | [14 empty] | 0327 | [8 empty] | kV_-18_18(-2000_2000) |  | DDCS4_1 | [8 empty] | 仁德DS.安集大成_KV1 | 23KV安集大成(K461) R相KV | OTHER |  |  |  |  | DNP | 267 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D17 | 二甲DS | 22 | 22kV | 安集大成 | 安集大成(K461) |  | KV2 | [14 empty] | 0328 | [8 empty] | kV_-18_18(-2000_2000) |  | DDCS4_1 | [8 empty] | 仁德DS.安集大成_KV2 | 23KV安集大成(K461) S相KV | OTHER |  |  |  |  | DNP | 268 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D17 | 二甲DS | 22 | 22kV | 安集大成 | 安集大成(K461) |  | KV3 | [14 empty] | 0329 | [8 empty] | kV_-18_18(-2000_2000) |  | DDCS4_1 | [8 empty] | 仁德DS.安集大成_KV3 | 23KV安集大成(K461) T相KV | OTHER |  |  |  |  | DNP | 269 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D17 | 二甲DS | 22 | 22kV | 安集大成 | 安集大成(K461) |  | KW | [14 empty] | 0321 | [8 empty] | KW_-6000_6000(-2000_2000) |  | DDCS4_1 | [8 empty] | 仁德DS.安集大成_KW | 23KV安集大成(K461) KW | OTHER |  |  |  |  | DNP | 270 | DNPAIPoint | DS055 |  |  | AI | [17 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 2.700000 | 0.010000
D17 | 二甲DS | 161 | 161kV | 1550 | 二甲奇美實紅線(1550) |  | PHA | [14 empty] | 0018 | [10 empty] | 161KV_S | [8 empty] | 二甲DS.1550_PHA | 二甲奇美實紅線(1550) 相間RY | LINE161 | D17/161/1550/PHA |  |  |  | DNP | 271 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1550 | 二甲奇美實紅線(1550) |  | GDA | [14 empty] | 0019 | [10 empty] | 161KV_S | [8 empty] | 二甲DS.1550_GDA | 二甲奇美實紅線(1550) 接地RY | LINE161 | D17/161/1550/GDA |  |  |  | DNP | 272 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1550 | 二甲奇美實紅線(1550) |  | CB | [14 empty] | 0016 |  | 0005 | [8 empty] | 161KV_S | [8 empty] | 二甲DS.1550_CB | 1550(二甲奇美實紅線) CB | LINE161 | D17/161/1550/CB |  |  |  | DNP | 273 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 161 | 161kV | 1550 | 二甲奇美實紅線(1550) |  | DS1 | 1551 | [13 empty] | 0644 | 645 | 0088 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1551_DS | 1551(二甲奇美實紅線) DS | LINE161 | D17/161/1550/DS1 |  |  |  | DNP | 274 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 161 | 161kV | 1550 | 二甲奇美實紅線(1550) |  | DS2 | 1552 | [13 empty] | 0646 | 647 | 0089 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1552_DS | 1552(二甲奇美實紅線) DS | LINE161 | D17/161/1550/DS2 |  |  |  | DNP | 275 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D17 | 二甲DS | 161 | 161kV | 1550 | 二甲奇美實紅線(1550) |  | DS3 | 1553 | [13 empty] | 0648 | 649 | 0090 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1553_DS | 1553(二甲奇美實紅線) DS | LINE161 | D17/161/1550/DS3 |  |  |  | DNP | 276 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 161 | 161kV | 1550 | 二甲奇美實紅線(1550) |  | E3 | 1553E | [13 empty] | 0650 | 651 | 0091 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1553E_ES | 1553E(二甲奇美實紅線) ES | LINE161 | D17/161/1550/ES3 |  |  |  | DNP | 277 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D17 | 二甲DS | 161 | 161kV | 1560 | 二甲奇美實白線(1560) |  | PHA | [14 empty] | 0022 | [10 empty] | 161KV_S | [8 empty] | 二甲DS.1560_PHA | 二甲奇美實白線(1560) 相間RY | LINE161 | D17/161/1560/PHA |  |  |  | DNP | 278 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1560 | 二甲奇美實白線(1560) |  | GDA | [14 empty] | 0023 | [10 empty] | 161KV_S | [8 empty] | 二甲DS.1560_GDA | 二甲奇美實白線(1560) 接地RY | LINE161 | D17/161/1560/GDA |  |  |  | DNP | 279 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1560 | 二甲奇美實白線(1560) |  | CB | [14 empty] | 0020 |  | 0006 | [8 empty] | 161KV_S | [8 empty] | 二甲DS.1560_CB | 1560(二甲奇美實白線) CB | LINE161 | D17/161/1560/CB |  |  |  | DNP | 280 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 161 | 161kV | 1560 | 二甲奇美實白線(1560) |  | DS1 | 1561 | [13 empty] | 0652 | 653 | 0092 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1561_DS | 1561(二甲奇美實白線) DS | LINE161 | D17/161/1560/DS1 |  |  |  | DNP | 281 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D17 | 二甲DS | 161 | 161kV | 1560 | 二甲奇美實白線(1560) |  | DS2 | 1562 | [13 empty] | 0654 | 655 | 0093 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1562_DS | 1562(二甲奇美實白線) DS | LINE161 | D17/161/1560/DS2 |  |  |  | DNP | 282 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 161 | 161kV | 1560 | 二甲奇美實白線(1560) |  | DS3 | 1563 | [13 empty] | 0656 | 657 | 0094 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1563_DS | 1563(二甲奇美實白線) DS | LINE161 | D17/161/1560/DS3 |  |  |  | DNP | 283 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 161 | 161kV | 1560 | 二甲奇美實白線(1560) |  | E3 | 1563E | [13 empty] | 0658 | 659 | 0095 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1563E_ES | 1563E(二甲奇美實白線) ES | LINE161 | D17/161/1560/ES3 |  |  |  | DNP | 284 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D17 | 二甲DS | 161 | 161kV | 1570 | 仁德二甲紅線(1570) |  | PHA | [14 empty] | 0026 | [10 empty] | 161KV_S | [8 empty] | 二甲DS.1570_PHA | 仁德二甲紅線(1570) 相間RY | LINE161 | D17/161/1570/PHA |  |  |  | DNP | 285 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1570 | 仁德二甲紅線(1570) |  | GDA | [14 empty] | 0027 | [10 empty] | 161KV_S | [8 empty] | 二甲DS.1570_GDA | 仁德二甲紅線(1570) 接地RY | LINE161 | D17/161/1570/GDA |  |  |  | DNP | 286 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1570 | 仁德二甲紅線(1570) |  | 87A | [14 empty] | 0025 | [10 empty] | 161KV_S | [8 empty] | 二甲DS.1570_87A | 仁德二甲紅線(1570) 87RY | LINE161 | D17/161/1570/87A |  |  |  | DNP | 287 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1570 | 仁德二甲紅線(1570) |  | 87UL | [14 empty] | 0598 |  | 0036 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1570_87UL | 仁德二甲紅線(1570) 87RY U/L | LINE161 | D17/161/1570/87UL |  |  |  | DNP | 288 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 161 | 161kV | 1570 | 仁德二甲紅線(1570) |  | CB | [14 empty] | 0024 |  | 0007 | [8 empty] | 161KV_S | [8 empty] | 二甲DS.1570_CB | 1570(仁德二甲紅線) CB | LINE161 | D17/161/1570/CB |  |  |  | DNP | 289 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 161 | 161kV | 1570 | 仁德二甲紅線(1570) |  | 79UL | [14 empty] | 0599 |  | 0037 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1570_79UL | 仁德二甲紅線(1570) 79RY U/L | LINE161 | D17/161/1570/79UL |  |  |  | DNP | 290 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 161 | 161kV | 1570 | 仁德二甲紅線(1570) |  | DS1 | 1571 | [13 empty] | 0660 | 661 | 0096 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1571_DS | 1571(仁德二甲紅線) DS | LINE161 | D17/161/1570/DS1 |  |  |  | DNP | 291 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 161 | 161kV | 1570 | 仁德二甲紅線(1570) |  | DS2 | 1572 | [13 empty] | 0662 | 663 | 0097 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1572_DS | 1572(仁德二甲紅線) DS | LINE161 | D17/161/1570/DS2 |  |  |  | DNP | 292 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D17 | 二甲DS | 161 | 161kV | 1570 | 仁德二甲紅線(1570) |  | DS3 | 1573 | [13 empty] | 0664 | 665 | 0098 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1573_DS | 1573(仁德二甲紅線) DS | LINE161 | D17/161/1570/DS3 |  |  |  | DNP | 293 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 161 | 161kV | 1570 | 仁德二甲紅線(1570) |  | E3 | 1573E | [13 empty] | 0666 | 667 | 0099 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1573E_ES | 1573E(仁德二甲紅線) ES | LINE161 | D17/161/1570/ES3 |  |  |  | DNP | 294 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D17 | 二甲DS | 161 | 161kV | 1580 | 仁德二甲白線(1580) |  | PHA | [14 empty] | 0030 | [10 empty] | 161KV_S | [8 empty] | 二甲DS.1580_PHA | 仁德二甲白線(1580) 相間RY | LINE161 | D17/161/1580/PHA |  |  |  | DNP | 295 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1580 | 仁德二甲白線(1580) |  | GDA | [14 empty] | 0031 | [10 empty] | 161KV_S | [8 empty] | 二甲DS.1580_GDA | 仁德二甲白線(1580) 接地RY | LINE161 | D17/161/1580/GDA |  |  |  | DNP | 296 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1580 | 仁德二甲白線(1580) |  | 87A | [14 empty] | 0029 | [10 empty] | 161KV_S | [8 empty] | 二甲DS.1580_87A | 仁德二甲白線(1580) 87RY | LINE161 | D17/161/1580/87A |  |  |  | DNP | 297 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1580 | 仁德二甲白線(1580) |  | 87UL | [14 empty] | 0600 |  | 0038 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1580_87UL | 仁德二甲白線(1580) 87RY U/L | LINE161 | D17/161/1580/87UL |  |  |  | DNP | 298 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 161 | 161kV | 1580 | 仁德二甲白線(1580) |  | CB | [14 empty] | 0028 |  | 0008 | [8 empty] | 161KV_S | [8 empty] | 二甲DS.1580_CB | 1580(仁德二甲白線) CB | LINE161 | D17/161/1580/CB |  |  |  | DNP | 299 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 161 | 161kV | 1580 | 仁德二甲白線(1580) |  | 79UL | [14 empty] | 0601 |  | 0039 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1580_79UL | 仁德二甲白線(1580) 79RY U/L | LINE161 | D17/161/1580/79UL |  |  |  | DNP | 300 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 161 | 161kV | 1580 | 仁德二甲白線(1580) |  | DS1 | 1581 | [13 empty] | 0668 | 669 | 0100 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1581_DS | 1581(仁德二甲白線) DS | LINE161 | D17/161/1580/DS1 |  |  |  | DNP | 301 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D17 | 二甲DS | 161 | 161kV | 1580 | 仁德二甲白線(1580) |  | DS2 | 1582 | [13 empty] | 0670 | 671 | 0101 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1582_DS | 1582(仁德二甲白線) DS | LINE161 | D17/161/1580/DS2 |  |  |  | DNP | 302 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 161 | 161kV | 1580 | 仁德二甲白線(1580) |  | DS3 | 1583 | [13 empty] | 0672 | 673 | 0102 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1583_DS | 1583(仁德二甲白線) DS | LINE161 | D17/161/1580/DS3 |  |  |  | DNP | 303 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 161 | 161kV | 1580 | 仁德二甲白線(1580) |  | E3 | 1583E | [13 empty] | 0674 | 675 | 0103 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1583E_ES | 1583E(仁德二甲白線) ES | LINE161 | D17/161/1580/ES3 |  |  |  | DNP | 304 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D17 | 二甲DS | 161 | 161kV | 1610 | 龍崎山上三路(1610) |  | PHA | [14 empty] | 0034 | [10 empty] | 161KV_S | [8 empty] | 二甲DS.1610_PHA | 龍崎山上三路(1610) 相間RY | LINE161 | D17/161/1610/PHA |  |  |  | DNP | 305 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1610 | 龍崎山上三路(1610) |  | GDA | [14 empty] | 0035 | [10 empty] | 161KV_S | [8 empty] | 二甲DS.1610_GDA | 龍崎山上三路(1610) 接地RY | LINE161 | D17/161/1610/GDA |  |  |  | DNP | 306 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1610 | 龍崎山上三路(1610) |  | 87A | [14 empty] | 0033 | [10 empty] | 161KV_S | [8 empty] | 二甲DS.1610_87A | 龍崎山上三路(1610) 87RY | LINE161 | D17/161/1610/87A |  |  |  | DNP | 307 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1610 | 龍崎山上三路(1610) |  | 87UL | [14 empty] | 0602 |  | 0040 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1610_87UL | 龍崎山上三路(1610) 87RY U/L | LINE161 | D17/161/1610/87UL |  |  |  | DNP | 308 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 161 | 161kV | 1610 | 龍崎山上三路(1610) |  | CB | [14 empty] | 0032 |  | 0009 | [8 empty] | 161KV_S | [8 empty] | 二甲DS.1610_CB | 1610(龍崎山上三路) CB | LINE161 | D17/161/1610/CB |  |  |  | DNP | 309 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 161 | 161kV | 1610 | 龍崎山上三路(1610) |  | 79UL | [14 empty] | 0603 |  | 0041 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1610_79UL | 龍崎山上三路(1610) 79RY U/L | LINE161 | D17/161/1610/79UL |  |  |  | DNP | 310 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 161 | 161kV | 1610 | 龍崎山上三路(1610) |  | DS1 | 1611 | [13 empty] | 0676 | 677 | 0104 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1611_DS | 1611(龍崎山上三路) DS | LINE161 | D17/161/1610/DS1 |  |  |  | DNP | 311 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 161 | 161kV | 1610 | 龍崎山上三路(1610) |  | DS2 | 1612 | [13 empty] | 0678 | 679 | 0105 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1612_DS | 1612(龍崎山上三路) DS | LINE161 | D17/161/1610/DS2 |  |  |  | DNP | 312 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D17 | 二甲DS | 161 | 161kV | 1610 | 龍崎山上三路(1610) |  | DS3 | 1613 | [13 empty] | 0680 | 681 | 0106 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1613_DS | 1613(龍崎山上三路) DS | LINE161 | D17/161/1610/DS3 |  |  |  | DNP | 313 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 161 | 161kV | 1610 | 龍崎山上三路(1610) |  | E3 | 1613E | [13 empty] | 0682 | 683 | 0107 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1613E_ES | 1613E(龍崎山上三路) ES | LINE161 | D17/161/1610/ES3 |  |  |  | DNP | 314 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D17 | 二甲DS | 161 | 161kV | 1620 | 龍崎山上四路(1620) |  | PHA | [14 empty] | 0038 | [10 empty] | 161KV_S | [8 empty] | 二甲DS.1620_PHA | 龍崎山上四路(1620) 相間RY | LINE161 | D17/161/1620/PHA |  |  |  | DNP | 315 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1620 | 龍崎山上四路(1620) |  | GDA | [14 empty] | 0039 | [10 empty] | 161KV_S | [8 empty] | 二甲DS.1620_GDA | 龍崎山上四路(1620) 接地RY | LINE161 | D17/161/1620/GDA |  |  |  | DNP | 316 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1620 | 龍崎山上四路(1620) |  | 87A | [14 empty] | 0037 | [10 empty] | 161KV_S | [8 empty] | 二甲DS.1620_87A | 龍崎山上四路(1620) 87RY | LINE161 | D17/161/1620/87A |  |  |  | DNP | 317 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1620 | 龍崎山上四路(1620) |  | 87UL | [14 empty] | 0604 |  | 0042 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1620_87UL | 龍崎山上四路(1620) 87RY U/L | LINE161 | D17/161/1620/87UL |  |  |  | DNP | 318 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 161 | 161kV | 1620 | 龍崎山上四路(1620) |  | CB | [14 empty] | 0036 |  | 0010 | [8 empty] | 161KV_S | [8 empty] | 二甲DS.1620_CB | 1620(龍崎山上四路) CB | LINE161 | D17/161/1620/CB |  |  |  | DNP | 319 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 161 | 161kV | 1620 | 龍崎山上四路(1620) |  | 79UL | [14 empty] | 0605 |  | 0043 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1620_79UL | 龍崎山上四路(1620) 79RY U/L | LINE161 | D17/161/1620/79UL |  |  |  | DNP | 320 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 161 | 161kV | 1620 | 龍崎山上四路(1620) |  | DS1 | 1621 | [13 empty] | 0684 | 685 | 0108 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1621_DS | 1621(龍崎山上四路) DS | LINE161 | D17/161/1620/DS1 |  |  |  | DNP | 321 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D17 | 二甲DS | 161 | 161kV | 1620 | 龍崎山上四路(1620) |  | DS2 | 1622 | [13 empty] | 0686 | 687 | 0109 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1622_DS | 1622(龍崎山上四路) DS | LINE161 | D17/161/1620/DS2 |  |  |  | DNP | 322 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 161 | 161kV | 1620 | 龍崎山上四路(1620) |  | DS3 | 1623 | [13 empty] | 0688 | 689 | 0110 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1623_DS | 1623(龍崎山上四路) DS | LINE161 | D17/161/1620/DS3 |  |  |  | DNP | 323 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 161 | 161kV | 1620 | 龍崎山上四路(1620) |  | E3 | 1623E | [13 empty] | 0690 | 691 | 0111 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1623E_ES | 1623E(龍崎山上四路) ES | LINE161 | D17/161/1620/ES3 |  |  |  | DNP | 324 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D17 | 二甲DS | 11 | 11kV | K611 | 甲11線(K611) |  | PHA | [14 empty] | 0327 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K611_PHA | 11KV甲11線(K611) 相間RY | FEEDER | D17/11/F17/PHA |  |  |  | DNP | 325 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K611 | 甲11線(K611) |  | GDA | [14 empty] | 0328 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K611_GDA | 11KV甲11線(K611) 接地RY | FEEDER | D17/11/F17/GDA |  |  |  | DNP | 326 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K611 | 甲11線(K611) 79RY |  | 79UL | [14 empty] | 0928 |  | 0216 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K611_79UL | 11KV甲11線(K611) 79RY U/L | FEEDER | D17/11/F17/79UL |  |  |  | DNP | 327 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | K611_LCO | 甲11線(K611) LCO |  | TapPosMv | [14 empty] | 0929 |  | 0217 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K611_LCO_TAP | 11KV甲11線(K611) LCO TAP | FEEDER | D17/11/F17/ADJ |  |  |  | DNP | 328 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | K611 | K6(11KV甲11線) |  | CB | [14 empty] | 0326 |  | 0151 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K611_CB | K611(11KV甲11線) CB | FEEDER | D17/11/F17/CB |  |  |  | DNP | 329 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | K612 | 甲12線(K612) |  | PHA | [14 empty] | 0331 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K612_PHA | 11KV甲12線(K612) 相間RY | FEEDER | D17/11/F18/PHA |  |  |  | DNP | 330 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K612 | 甲12線(K612) |  | GDA | [14 empty] | 0332 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K612_GDA | 11KV甲12線(K612) 接地RY | FEEDER | D17/11/F18/GDA |  |  |  | DNP | 331 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K612 | 甲12線(K612) 79RY |  | 79UL | [14 empty] | 0930 |  | 0218 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K612_79UL | 11KV甲12線(K612) 79RY U/L | FEEDER | D17/11/F18/79UL |  |  |  | DNP | 332 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | K612_LCO | 甲12線(K612) LCO |  | TapPosMv | [14 empty] | 0931 |  | 0219 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K612_LCO_TAP | 11KV甲12線(K612) LCO TAP | FEEDER | D17/11/F18/ADJ |  |  |  | DNP | 333 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | K612 | K612(11KV甲12線) |  | CB | [14 empty] | 0330 |  | 0152 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K612_CB | K612(11KV甲12線) CB | FEEDER | D17/11/F18/CB |  |  |  | DNP | 334 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | K613 | 甲13線(K613) |  | PHA | [14 empty] | 0335 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K613_PHA | 11KV甲13線(K613) 相間RY | FEEDER | D17/11/F19/PHA |  |  |  | DNP | 335 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K613 | 甲13線(K613) |  | GDA | [14 empty] | 0336 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K613_GDA | 11KV甲13線(K613) 接地RY | FEEDER | D17/11/F19/GDA |  |  |  | DNP | 336 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K613 | 甲13線(K613) 79RY |  | 79UL | [14 empty] | 0932 |  | 0220 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K613_79UL | 11KV甲13線(K613) 79RY U/L | FEEDER | D17/11/F19/79UL |  |  |  | DNP | 337 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | K613_LCO | 甲13線(K613) LCO |  | TapPosMv | [14 empty] | 0933 |  | 0221 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K613_LCO_TAP | 11KV甲13線(K613) LCO TAP | FEEDER | D17/11/F19/ADJ |  |  |  | DNP | 338 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | K613 | K613(11KV甲13線) |  | CB | [14 empty] | 0334 |  | 0153 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K613_CB | K613(11KV甲13線) CB | FEEDER | D17/11/F19/CB |  |  |  | DNP | 339 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | K614 | 甲14線(K614) |  | PHA | [14 empty] | 0339 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K614_PHA | 11KV甲14線(K614) 相間RY | FEEDER | D17/11/F20/PHA |  |  |  | DNP | 340 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K614 | 甲14線(K614) |  | GDA | [14 empty] | 0340 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K614_GDA | 11KV甲14線(K614) 接地RY | FEEDER | D17/11/F20/GDA |  |  |  | DNP | 341 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K614 | 甲14線(K614) 79RY |  | 79UL | [14 empty] | 0934 |  | 0222 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K614_79UL | 11KV甲14線(K614) 79RY U/L | FEEDER | D17/11/F20/79UL |  |  |  | DNP | 342 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | K614_LCO | 甲14線(K614) LCO |  | TapPosMv | [14 empty] | 0935 |  | 0223 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K614_LCO_TAP | 11KV甲14線(K614) LCO TAP | FEEDER | D17/11/F20/ADJ |  |  |  | DNP | 343 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | K614 | K614(11KV甲14線) |  | CB | [14 empty] | 0338 |  | 0154 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K614_CB | K614(11KV甲14線) CB | FEEDER | D17/11/F20/CB |  |  |  | DNP | 344 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | K615 | 甲15線(K615) |  | PHA | [14 empty] | 0343 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K615_PHA | 11KV甲15線(K615) 相間RY | FEEDER | D17/11/F21/PHA |  |  |  | DNP | 345 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K615 | 甲15線(K615) |  | GDA | [14 empty] | 0344 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K615_GDA | 11KV甲15線(K615) 接地RY | FEEDER | D17/11/F21/GDA |  |  |  | DNP | 346 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K615 | 甲15線(K615) 79RY |  | 79UL | [14 empty] | 0936 |  | 0224 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K615_79UL | 11KV甲15線(K615) 79RY U/L | FEEDER | D17/11/F21/79UL |  |  |  | DNP | 347 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | K615_LCO | 甲15線(K615) LCO |  | TapPosMv | [14 empty] | 0937 |  | 0225 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K615_LCO_TAP | 11KV甲15線(K615) LCO TAP | FEEDER | D17/11/F21/ADJ |  |  |  | DNP | 348 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | K615 | K615(11KV甲15線) |  | CB | [14 empty] | 0342 |  | 0155 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K615_CB | K615(11KV甲15線) CB | FEEDER | D17/11/F21/CB |  |  |  | DNP | 349 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | K621 | 甲21線(K621) |  | PHA | [14 empty] | 0356 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K621_PHA | 11KV甲21線(K621) 相間RY | FEEDER | D17/11/F22/PHA |  |  |  | DNP | 350 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K621 | 甲21線(K621) |  | GDA | [14 empty] | 0357 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K621_GDA | 11KV甲21線(K621) 接地RY | FEEDER | D17/11/F22/GDA |  |  |  | DNP | 351 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K621 | 甲21線(K621) 79RY |  | 79UL | [14 empty] | 0938 |  | 0226 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K621_79UL | 11KV甲21線(K621) 79RY U/L | FEEDER | D17/11/F22/79UL |  |  |  | DNP | 352 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | K621_LCO | 甲21線(K621) LCO |  | TapPosMv | [14 empty] | 0939 |  | 0227 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K621_LCO_TAP | 11KV甲21線(K621) LCO TAP | FEEDER | D17/11/F22/ADJ |  |  |  | DNP | 353 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | K621 | K621(11KV甲21線) |  | CB | [14 empty] | 0355 |  | 0158 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K621_CB | K621(11KV甲21線) CB | FEEDER | D17/11/F22/CB |  |  |  | DNP | 354 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | K622 | 甲22線(K622) |  | PHA | [14 empty] | 0360 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K622_PHA | 11KV甲22線(K622) 相間RY | FEEDER | D17/11/F23/PHA |  |  |  | DNP | 355 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K622 | 甲22線(K622) |  | GDA | [14 empty] | 0361 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K622_GDA | 11KV甲22線(K622) 接地RY | FEEDER | D17/11/F23/GDA |  |  |  | DNP | 356 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K622 | 甲22線(K622) 79RY |  | 79UL | [14 empty] | 0940 |  | 0228 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K622_79UL | 11KV甲22線(K622) 79RY U/L | FEEDER | D17/11/F23/79UL |  |  |  | DNP | 357 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | K622_LCO | 甲22線(K622) LCO |  | TapPosMv | [14 empty] | 0941 |  | 0229 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K622_LCO_TAP | 11KV甲22線(K622) LCO TAP | FEEDER | D17/11/F23/ADJ |  |  |  | DNP | 358 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | K622 | K622(11KV甲22線) |  | CB | [14 empty] | 0359 |  | 0159 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K622_CB | K622(11KV甲22線) CB | FEEDER | D17/11/F23/CB |  |  |  | DNP | 359 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | K623 | 甲23線(K623) |  | PHA | [14 empty] | 0364 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K623_PHA | 11KV甲23線(K623) 相間RY | FEEDER | D17/11/F24/PHA |  |  |  | DNP | 360 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K623 | 甲23線(K623) |  | GDA | [14 empty] | 0365 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K623_GDA | 11KV甲23線(K623) 接地RY | FEEDER | D17/11/F24/GDA |  |  |  | DNP | 361 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K623 | 甲23線(K623) 79RY |  | 79UL | [14 empty] | 0942 |  | 0230 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K623_79UL | 11KV甲23線(K623) 79RY U/L | FEEDER | D17/11/F24/79UL |  |  |  | DNP | 362 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | K623_LCO | 甲23線(K623) LCO |  | TapPosMv | [14 empty] | 0943 |  | 0231 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K623_LCO_TAP | 11KV甲23線(K623) LCO TAP | FEEDER | D17/11/F24/ADJ |  |  |  | DNP | 363 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | K623 | K623(11KV甲23線) |  | CB | [14 empty] | 0363 |  | 0160 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K623_CB | K623(11KV甲23線) CB | FEEDER | D17/11/F24/CB |  |  |  | DNP | 364 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | K624 | 甲24線(K624) |  | PHA | [14 empty] | 0368 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K624_PHA | 11KV甲24線(K624) 相間RY | FEEDER | D17/11/F25/PHA |  |  |  | DNP | 365 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K624 | 甲24線(K624) |  | GDA | [14 empty] | 0369 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K624_GDA | 11KV甲24線(K624) 接地RY | FEEDER | D17/11/F25/GDA |  |  |  | DNP | 366 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K624 | 甲24線(K624) 79RY |  | 79UL | [14 empty] | 0944 |  | 0232 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K624_79UL | 11KV甲24線(K624) 79RY U/L | FEEDER | D17/11/F25/79UL |  |  |  | DNP | 367 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | K624_LCO | 甲24線(K624) LCO |  | TapPosMv | [14 empty] | 0945 |  | 0233 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K624_LCO_TAP | 11KV甲24線(K624) LCO TAP | FEEDER | D17/11/F25/ADJ |  |  |  | DNP | 368 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | K624 | K624(11KV甲24線) |  | CB | [14 empty] | 0367 |  | 0161 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K624_CB | K624(11KV甲24線) CB | FEEDER | D17/11/F25/CB |  |  |  | DNP | 369 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | K625 | 甲25線(K625) |  | PHA | [14 empty] | 0372 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K625_PHA | 11KV甲25線(K625) 相間RY | FEEDER | D17/11/F26/PHA |  |  |  | DNP | 370 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K625 | 甲25線(K625) |  | GDA | [14 empty] | 0373 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K625_GDA | 11KV甲25線(K625) 接地RY | FEEDER | D17/11/F26/GDA |  |  |  | DNP | 371 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K625 | 甲25線(K625) 79RY |  | 79UL | [14 empty] | 0946 |  | 0234 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K625_79UL | 11KV甲25線(K625) 79RY U/L | FEEDER | D17/11/F26/79UL |  |  |  | DNP | 372 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | K625_LCO | 甲25線(K625) LCO |  | TapPosMv | [14 empty] | 0947 |  | 0235 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K625_LCO_TAP | 11KV甲25線(K625) LCO TAP | FEEDER | D17/11/F26/ADJ |  |  |  | DNP | 373 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | K625 | K625(11KV甲25線) |  | CB | [14 empty] | 0371 |  | 0162 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K625_CB | K625(11KV甲25線) CB | FEEDER | D17/11/F26/CB |  |  |  | DNP | 374 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | K631 | 甲31線(K631) |  | PHA | [14 empty] | 0382 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K631_PHA | 11KV甲31線(K631) 相間RY | FEEDER | D17/11/F27/PHA |  |  |  | DNP | 375 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K631 | 甲31線(K631) |  | GDA | [14 empty] | 0383 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K631_GDA | 11KV甲31線(K631) 接地RY | FEEDER | D17/11/F27/GDA |  |  |  | DNP | 376 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K631 | 甲31線(K631) 79RY |  | 79UL | [14 empty] | 0948 |  | 0236 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K631_79UL | 11KV甲31線(K631) 79RY U/L | FEEDER | D17/11/F27/79UL |  |  |  | DNP | 377 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | K631_LCO | 甲31線(K631) LCO |  | TapPosMv | [14 empty] | 0949 |  | 0237 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K631_LCO_TAP | 11KV甲31線(K631) LCO TAP | FEEDER | D17/11/F27/ADJ |  |  |  | DNP | 378 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | K631 | K631(11KV甲31線) |  | CB | [14 empty] | 0381 |  | 0165 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K631_CB | K631(11KV甲31線) CB | FEEDER | D17/11/F27/CB |  |  |  | DNP | 379 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | K632 | 甲32線(K632) |  | PHA | [14 empty] | 0386 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K632_PHA | 11KV甲32線(K632) 相間RY | FEEDER | D17/11/F28/PHA |  |  |  | DNP | 380 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K632 | 甲32線(K632) |  | GDA | [14 empty] | 0387 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K632_GDA | 11KV甲32線(K632) 接地RY | FEEDER | D17/11/F28/GDA |  |  |  | DNP | 381 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K632 | 甲32線(K632) 79RY |  | 79UL | [14 empty] | 0950 |  | 0238 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K632_79UL | 11KV甲32線(K632) 79RY U/L | FEEDER | D17/11/F28/79UL |  |  |  | DNP | 382 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | K632_LCO | 甲32線(K632) LCO |  | TapPosMv | [14 empty] | 0951 |  | 0239 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K632_LCO_TAP | 11KV甲32線(K632) LCO TAP | FEEDER | D17/11/F28/ADJ |  |  |  | DNP | 383 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | K632 | K632(11KV甲32線) |  | CB | [14 empty] | 0385 |  | 0166 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K632_CB | K632(11KV甲32線) CB | FEEDER | D17/11/F28/CB |  |  |  | DNP | 384 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | K633 | 甲33線(K633) |  | PHA | [14 empty] | 0390 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K633_PHA | 11KV甲33線(K633) 相間RY | FEEDER | D17/11/F29/PHA |  |  |  | DNP | 385 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K633 | 甲33線(K633) |  | GDA | [14 empty] | 0391 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K633_GDA | 11KV甲33線(K633) 接地RY | FEEDER | D17/11/F29/GDA |  |  |  | DNP | 386 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K633 | 甲33線(K633) 79RY |  | 79UL | [14 empty] | 0952 |  | 0240 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K633_79UL | 11KV甲33線(K633) 79RY U/L | FEEDER | D17/11/F29/79UL |  |  |  | DNP | 387 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | K633_LCO | 甲33線(K633) LCO |  | TapPosMv | [14 empty] | 0953 |  | 0241 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K633_LCO_TAP | 11KV甲33線(K633) LCO TAP | FEEDER | D17/11/F29/ADJ |  |  |  | DNP | 388 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | K633 | K633(11KV甲33線) |  | CB | [14 empty] | 0389 |  | 0167 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K633_CB | K633(11KV甲33線) CB | FEEDER | D17/11/F29/CB |  |  |  | DNP | 389 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | K634 | 甲34線(K634) |  | PHA | [14 empty] | 0394 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K634_PHA | 11KV甲34線(K634) 相間RY | FEEDER | D17/11/F30/PHA |  |  |  | DNP | 390 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K634 | 甲34線(K634) |  | GDA | [14 empty] | 0395 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K634_GDA | 11KV甲34線(K634) 接地RY | FEEDER | D17/11/F30/GDA |  |  |  | DNP | 391 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K634 | 甲34線(K634) 79RY |  | 79UL | [14 empty] | 0954 |  | 0242 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K634_79UL | 11KV甲34線(K634) 79RY U/L | FEEDER | D17/11/F30/79UL |  |  |  | DNP | 392 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | K634_LCO | 甲34線(K634) LCO |  | TapPosMv | [14 empty] | 0955 |  | 0243 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K634_LCO_TAP | 11KV甲34線(K634) LCO TAP | FEEDER | D17/11/F30/ADJ |  |  |  | DNP | 393 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | K634 | K634(11KV甲34線) |  | CB | [14 empty] | 0393 |  | 0168 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K634_CB | K634(11KV甲34線) CB | FEEDER | D17/11/F30/CB |  |  |  | DNP | 394 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | K635 | 甲35線(K635) |  | PHA | [14 empty] | 0398 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K635_PHA | 11KV甲35線(K635) 相間RY | FEEDER | D17/11/F31/PHA |  |  |  | DNP | 395 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K635 | 甲35線(K635) |  | GDA | [14 empty] | 0399 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K635_GDA | 11KV甲35線(K635) 接地RY | FEEDER | D17/11/F31/GDA |  |  |  | DNP | 396 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K635 | 甲35線(K635) 79RY |  | 79UL | [14 empty] | 0956 |  | 0244 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K635_79UL | 11KV甲35線(K635) 79RY U/L | FEEDER | D17/11/F31/79UL |  |  |  | DNP | 397 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | K635_LCO | 甲35線(K635) LCO |  | TapPosMv | [14 empty] | 0957 |  | 0245 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K635_LCO_TAP | 11KV甲35線(K635) LCO TAP | FEEDER | D17/11/F31/ADJ |  |  |  | DNP | 398 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | K635 | K635(11KV甲35線) |  | CB | [14 empty] | 0397 |  | 0169 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K635_CB | K635(11KV甲35線) CB | FEEDER | D17/11/F31/CB |  |  |  | DNP | 399 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | K641 | 甲41線(K641) |  | PHA | [14 empty] | 0405 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K641_PHA | 11KV甲41線(K641) 相間RY | FEEDER | D17/11/F32/PHA |  |  |  | DNP | 400 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K641 | 甲41線(K641) |  | GDA | [14 empty] | 0406 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K641_GDA | 11KV甲41線(K641) 接地RY | FEEDER | D17/11/F32/GDA |  |  |  | DNP | 401 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K641 | 甲41線(K641) 79RY |  | 79UL | [14 empty] | 0958 |  | 0246 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K641_79UL | 11KV甲41線(K641) 79RY U/L | FEEDER | D17/11/F32/79UL |  |  |  | DNP | 402 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | K641_LCO | 甲41線(K641) LCO |  | TapPosMv | [14 empty] | 0959 |  | 0247 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K641_LCO_TAP | 11KV甲41線(K641) LCO TAP | FEEDER | D17/11/F32/ADJ |  |  |  | DNP | 403 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | K641 | K641(11KV甲41線) |  | CB | [14 empty] | 0404 |  | 0172 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K641_CB | K641(11KV甲41線) CB | FEEDER | D17/11/F32/CB |  |  |  | DNP | 404 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | K642 | 甲42線(K642) |  | PHA | [14 empty] | 0409 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K642_PHA | 11KV甲42線(K642) 相間RY | FEEDER | D17/11/F33/PHA |  |  |  | DNP | 405 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K642 | 甲42線(K642) |  | GDA | [14 empty] | 0410 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K642_GDA | 11KV甲42線(K642) 接地RY | FEEDER | D17/11/F33/GDA |  |  |  | DNP | 406 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K642 | 甲42線(K642) 79RY |  | 79UL | [14 empty] | 0960 |  | 0248 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K642_79UL | 11KV甲42線(K642) 79RY U/L | FEEDER | D17/11/F33/79UL |  |  |  | DNP | 407 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | K642_LCO | 甲42線(K642) LCO |  | TapPosMv | [14 empty] | 0961 |  | 0249 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K642_LCO_TAP | 11KV甲42線(K642) LCO TAP | FEEDER | D17/11/F33/ADJ |  |  |  | DNP | 408 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | K642 | K642(11KV甲42線) |  | CB | [14 empty] | 0408 |  | 0173 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K642_CB | K642(11KV甲42線) CB | FEEDER | D17/11/F33/CB |  |  |  | DNP | 409 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | K643 | 甲43線(K643) |  | PHA | [14 empty] | 0413 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K643_PHA | 11KV甲43線(K643) 相間RY | FEEDER | D17/11/F34/PHA |  |  |  | DNP | 410 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K643 | 甲43線(K643) |  | GDA | [14 empty] | 0414 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K643_GDA | 11KV甲43線(K643) 接地RY | FEEDER | D17/11/F34/GDA |  |  |  | DNP | 411 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K643 | 甲43線(K643) 79RY |  | 79UL | [14 empty] | 0962 |  | 0250 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K643_79UL | 11KV甲43線(K643) 79RY U/L | FEEDER | D17/11/F34/79UL |  |  |  | DNP | 412 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | K643_LCO | 甲43線(K643) LCO |  | TapPosMv | [14 empty] | 0963 |  | 0251 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K643_LCO_TAP | 11KV甲43線(K643) LCO TAP | FEEDER | D17/11/F34/ADJ |  |  |  | DNP | 413 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | K643 | K643(11KV甲43線) |  | CB | [14 empty] | 0412 |  | 0174 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K643_CB | K643(11KV甲43線) CB | FEEDER | D17/11/F34/CB |  |  |  | DNP | 414 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | K644 | 甲44線(K644) |  | PHA | [14 empty] | 0417 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K644_PHA | 11KV甲44線(K644) 相間RY | FEEDER | D17/11/F35/PHA |  |  |  | DNP | 415 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K644 | 甲44線(K644) |  | GDA | [14 empty] | 0418 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K644_GDA | 11KV甲44線(K644) 接地RY | FEEDER | D17/11/F35/GDA |  |  |  | DNP | 416 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K644 | 甲44線(K644) 79RY |  | 79UL | [14 empty] | 0964 |  | 0252 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K644_79UL | 11KV甲44線(K644) 79RY U/L | FEEDER | D17/11/F35/79UL |  |  |  | DNP | 417 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | K644_LCO | 甲44線(K644) LCO |  | TapPosMv | [14 empty] | 0965 |  | 0253 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K644_LCO_TAP | 11KV甲44線(K644) LCO TAP | FEEDER | D17/11/F35/ADJ |  |  |  | DNP | 418 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | K644 | K644(11KV甲44線) |  | CB | [14 empty] | 0416 |  | 0175 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K644_CB | K644(11KV甲44線) CB | FEEDER | D17/11/F35/CB |  |  |  | DNP | 419 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | K645 | 甲45線(K645) |  | PHA | [14 empty] | 0421 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K645_PHA | 11KV甲45線(K645) 相間RY | FEEDER | D17/11/F36/PHA |  |  |  | DNP | 420 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K645 | 甲45線(K645) |  | GDA | [14 empty] | 0422 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K645_GDA | 11KV甲45線(K645) 接地RY | FEEDER | D17/11/F36/GDA |  |  |  | DNP | 421 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K645 | 甲45線(K645) 79RY |  | 79UL | [14 empty] | 0966 |  | 0254 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K645_79UL | 11KV甲45線(K645) 79RY U/L | FEEDER | D17/11/F36/79UL |  |  |  | DNP | 422 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | K645_LCO | 甲45線(K645) LCO |  | TapPosMv | [14 empty] | 0967 |  | 0255 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K645_LCO_TAP | 11KV甲45線(K645) LCO TAP | FEEDER | D17/11/F36/ADJ |  |  |  | DNP | 423 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D17 | 二甲DS | 11 | 11kV | K645 | K645(11KV甲45線) |  | CB | [14 empty] | 0420 |  | 0176 | [8 empty] | DDCS4_1 | [8 empty] | 二甲DS.K645_CB | K645(11KV甲45線) CB | FEEDER | D17/11/F36/CB |  |  |  | DNP | 424 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [14 empty] | 0040 |  | 0011 | [8 empty] | 161KV_S | [8 empty] | 二甲DS.1500_CB | 1500(TIE) CB | TIE | D17/161/1500/CB |  |  |  | DNP | 425 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | 1500 | TIE(1500) |  | 50A | [14 empty] | 0041 | [10 empty] | 161KV_S | [8 empty] | 二甲DS.1500_50A | 161KV TIE(1500) 50RY | TIE | D17/161/1500/50A |  |  |  | DNP | 426 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [13 empty] | 0608 | 609 | 0112 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1501_DS | 1501(TIE) DS | TIE | D17/161/1500/DS1 |  |  |  | DNP | 427 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [13 empty] | 0610 | 611 | 0113 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1502_DS | 1502(TIE) DS | TIE | D17/161/1500/DS2 |  |  |  | DNP | 428 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 0 |  | 1500 | TIE(1500) |  | 50SA | [14 empty] | 0540 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.1500_50SA | 161KV TIE(1500) 50RY 測試/正常 | TIE | D17/161/1500/50SA |  |  |  | DNP | 429 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TEST/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 300 | TIE(300) |  | CB | [14 empty] | 0349 |  | 0156 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.300_CB | 300(TIE) CB | TIE | D17/11/300/CB |  |  |  | DNP | 430 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | 300 | TIE(300) |  | 51A | [14 empty] | 0350 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.300_51A | 11KV TIE(300) 51RY | TIE | D17/11/300/PHA |  |  |  | DNP | 431 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 300 | TIE(300) |  | 51NA | [14 empty] | 0351 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.300_51NA | 11KV TIE(300) 51N RY | TIE | D17/11/300/GDA |  |  |  | DNP | 432 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 400 | TIE(400) |  | CB | [14 empty] | 0378 |  | 0163 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.400_CB | 400(TIE) CB | TIE | D17/11/400/CB |  |  |  | DNP | 433 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | 400 | TIE(400) |  | 51A | [14 empty] | 0379 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.400_51A | 11KV TIE(400) 51RY | TIE | D17/11/400/PHA |  |  |  | DNP | 434 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 400 | TIE(400) |  | 51NA | [14 empty] | 0380 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.400_51NA | 11KV TIE(400) 51N RY | TIE | D17/11/400/GDA |  |  |  | DNP | 435 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 390 | #1SSTR(390) |  | CB | [14 empty] | 0352 |  | 0149 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.390_CB | 390(#1SSTR) CB | OTHER | D17/11/390/CB |  |  |  | DNP | 436 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | 1SSTR | #1SSTR |  | 51A | [14 empty] | 0353 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.#1SSTR_51A | #1SSTR 51RY | OTHER | D17/11/390/PHA |  |  |  | DNP | 437 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 1SSTR | #1SSTR |  | 51NA | [14 empty] | 0354 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | D17/11/390/GDA |  |  |  | DNP | 438 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 490 | #2SSTR(490) |  | CB | [14 empty] | 0427 |  | 0171 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.490_CB | 490(#2SSTR) CB | OTHER | D17/11/490/CB |  |  |  | DNP | 439 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | 2SSTR | #2SSTR |  | 51A | [14 empty] | 0428 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.#2SSTR_51A | #2SSTR 51RY | OTHER | D17/11/490/PHA |  |  |  | DNP | 440 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 2SSTR | #2SSTR |  | 51NA | [14 empty] | 0429 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | D17/11/490/GDA |  |  |  | DNP | 441 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB | [14 empty] | 0070 |  | 0014 | [8 empty] | 161KV_S | [8 empty] | 二甲DS.1770_CB | 1770(#3DTR) CB | MTR | D17/161/1770/CB |  |  |  | DNP | 442 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | 350 | #3DTR(350) |  | CB | [14 empty] | 0078 |  | 0018 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.350_CB | 350(#3DTR) CB | MTR | D17/11/350/CB |  |  |  | DNP | 443 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | 360 | #3DTR(360) |  | CB | [14 empty] | 0082 |  | 0019 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.360_CB | 360(#3DTR) CB | MTR | D17/11/360/CB |  |  |  | DNP | 444 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | 3DTR | #3DTR |  | 51A | [14 empty] | 0074 | [10 empty] | 161KV_S | [8 empty] | 二甲DS.#3DTR_51A | #3DTR 51RY | MTR | D17//3DTR/PHA |  |  |  | DNP | 445 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 3DTR | #3DTR |  | 51NA | [14 empty] | 0075 | [10 empty] | 161KV_S | [8 empty] | 二甲DS.#3DTR_51NA | #3DTR 51N RY | MTR | D17//3DTR/GDA |  |  |  | DNP | 446 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 3DTR | #3DTR |  | 51ZA | [14 empty] | 0073 | [10 empty] | 161KV_S | [8 empty] | 二甲DS.#3DTR_51ZA | #3DTR 51Z RY | MTR | D17//3DTR/51ZA |  |  |  | DNP | 447 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 3DTR | #3DTR |  | 87A | [14 empty] | 0071 | [10 empty] | 161KV_S | [8 empty] | 二甲DS.#3DTR_87A | #3DTR 87RY | MTR | D17//3DTR/87A |  |  |  | DNP | 448 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 350 | #3DTR(350) |  | 51A | [14 empty] | 0076 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.350_51A | #3DTR二次側(350) 51RY | MTR | D17/11/350/51A |  |  |  | DNP | 449 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 360 | #3DTR(360) |  | 51A | [14 empty] | 0077 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.360_51A | #3DTR二次側(360) 51RY | MTR | D17/11/360/51A |  |  |  | DNP | 450 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 3DTR | #3DTR |  | 96PA | [14 empty] | 0072 | [10 empty] | 161KV_S | [8 empty] | 二甲DS.#3DTR_96PA | #3DTR 機械保護動作 | MTR | D17//3DTR/96PA |  |  |  | DNP | 451 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 3DTR | #3DTR |  | 96D | [14 empty] | 0578 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.#3DTR_96D | #3DTR 96D RY | MTR | D17//3DTR/96D |  |  |  | DNP | 452 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 3DTR | #3DTR |  | 96P | [14 empty] | 0579 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.#3DTR_96P | #3DTR 96P RY | MTR | D17//3DTR/96P |  |  |  | DNP | 453 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 3DTR | #3DTR |  | 63Q | [14 empty] | 0580 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.#3DTR_63Q | #3DTR 63Q RY | MTR | D17//3DTR/63Q |  |  |  | DNP | 454 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 3DTR | #3DTR |  | 96B1 | [14 empty] | 0576 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.#3DTR_96B1 | #3DTR 96B1 RY | MTR | D17//3DTR/96B1 |  |  |  | DNP | 455 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 3DTR | #3DTR |  | 96B2 | [14 empty] | 0577 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.#3DTR_96B2 | #3DTR 96B2 RY | MTR | D17//3DTR/96B2 |  |  |  | DNP | 456 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 3DTR | #3DTR |  | TRA | [14 empty] | 0527 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.#3DTR_TRA | #3DTR 重故障 | MTR | D17//3DTR/TRA |  |  |  | DNP | 457 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 3DTR | #3DTR |  | TRF | [14 empty] | 0528 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.#3DTR_TRF | #3DTR 輕故障 | MTR | D17//3DTR/TRF |  |  |  | DNP | 458 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 3DTR(A) | #3DTR(A) |  | SupLocal | [14 empty] | 0525 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.#3DTR(A)_S/L | #3DTR(A) OLTC S/L | MTR | D17//3DTR(A)/SupLocal |  |  |  | DNP | 459 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D17 | 二甲DS | 0 |  | 3DTR(A) | #3DTR(A) |  | A_M | [14 empty] | 0526 |  | 0060 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.#3DTR(A)_A/M | #3DTR(A) OLTC A/M | MTR | D17//3DTR(A)/Tap Chan |  |  |  | DNP | 460 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D17 | 二甲DS | 0 |  | 3DTR(B) | #3DTR(B) |  | SupLocal | [14 empty] | 0529 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.#3DTR(B)_S/L | #3DTR(B) OLTC S/L | MTR | D17//3DTR(B)/SupLocal |  |  |  | DNP | 461 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D17 | 二甲DS | 0 |  | 3DTR(B) | #3DTR(B) |  | A_M | [14 empty] | 0530 |  | 0062 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.#3DTR(B)_A/M | #3DTR(B) OLTC A/M | MTR | D17//3DTR(B)/Tap Chan |  |  |  | DNP | 462 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D17 | 二甲DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 | [13 empty] | 0700 | 701 | 0118 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1771_DS | 1771(#3DTR) DS | MTR | D17/161/1770/DS1 |  |  |  | DNP | 463 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 | [13 empty] | 0702 | 703 | 0119 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1772_DS | 1772(#3DTR) DS | MTR | D17/161/1770/DS2 |  |  |  | DNP | 464 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D17 | 二甲DS | 161 | 161kV | 1780 | #4DTR(1780) |  | CB | [14 empty] | 0086 |  | 0015 | [8 empty] | 161KV_S | [8 empty] | 二甲DS.1780_CB | 1780(#4DTR) CB | MTR | D17/161/1780/CB |  |  |  | DNP | 465 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | 370 | #4DTR(370) |  | CB | [14 empty] | 0094 |  | 0020 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.370_CB | 370(#4DTR) CB | MTR | D17/11/370/CB |  |  |  | DNP | 466 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | 380 | #4DTR(380) |  | CB | [14 empty] | 0098 |  | 0021 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.380_CB | 380(#4DTR) CB | MTR | D17/11/380/CB |  |  |  | DNP | 467 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | 4DTR | #4DTR |  | 51A | [14 empty] | 0090 | [10 empty] | 161KV_S | [8 empty] | 二甲DS.#4DTR_51A | #4DTR 51RY | MTR | D17//4DTR/PHA |  |  |  | DNP | 468 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 4DTR | #4DTR |  | 51NA | [14 empty] | 0091 | [10 empty] | 161KV_S | [8 empty] | 二甲DS.#4DTR_51NA | #4DTR 51N RY | MTR | D17//4DTR/GDA |  |  |  | DNP | 469 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 4DTR | #4DTR |  | 51ZA | [14 empty] | 0089 | [10 empty] | 161KV_S | [8 empty] | 二甲DS.#4DTR_51ZA | #4DTR 51Z RY | MTR | D17//4DTR/51ZA |  |  |  | DNP | 470 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 4DTR | #4DTR |  | 87A | [14 empty] | 0087 | [10 empty] | 161KV_S | [8 empty] | 二甲DS.#4DTR_87A | #4DTR 87RY | MTR | D17//4DTR/87A |  |  |  | DNP | 471 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 370 | #4DTR(370) |  | 51A | [14 empty] | 0092 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.370_51A | #4DTR二次側(370) 51RY | MTR | D17/11/370/51A |  |  |  | DNP | 472 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 380 | #4DTR(380) |  | 51A | [14 empty] | 0093 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.380_51A | #4DTR二次側(380) 51RY | MTR | D17/11/380/51A |  |  |  | DNP | 473 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 4DTR | #4DTR |  | 96PA | [14 empty] | 0088 | [10 empty] | 161KV_S | [8 empty] | 二甲DS.#4DTR_96PA | #4DTR 機械保護動作 | MTR | D17//4DTR/96PA |  |  |  | DNP | 474 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 4DTR | #4DTR |  | 96D | [14 empty] | 0583 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.#4DTR_96D | #4DTR 96D RY | MTR | D17//4DTR/96D |  |  |  | DNP | 475 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 4DTR | #4DTR |  | 96P | [14 empty] | 0584 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.#4DTR_96P | #4DTR 96P RY | MTR | D17//4DTR/96P |  |  |  | DNP | 476 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 4DTR | #4DTR |  | 63Q | [14 empty] | 0585 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.#4DTR_63Q | #4DTR 63Q RY | MTR | D17//4DTR/63Q |  |  |  | DNP | 477 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 4DTR | #4DTR |  | 96B1 | [14 empty] | 0581 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.#4DTR_96B1 | #4DTR 96B1 RY | MTR | D17//4DTR/96B1 |  |  |  | DNP | 478 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 4DTR | #4DTR |  | 96B2 | [14 empty] | 0582 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.#4DTR_96B2 | #4DTR 96B2 RY | MTR | D17//4DTR/96B2 |  |  |  | DNP | 479 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 4DTR | #4DTR |  | TRA | [14 empty] | 0534 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.#4DTR_TRA | #4DTR 重故障 | MTR | D17//4DTR/TRA |  |  |  | DNP | 480 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 4DTR | #4DTR |  | TRF | [14 empty] | 0535 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.#4DTR_TRF | #4DTR 輕故障 | MTR | D17//4DTR/TRF |  |  |  | DNP | 481 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 4DTR(A) | #4DTR(A) |  | SupLocal | [14 empty] | 0532 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.#4DTR(A)_S/L | #4DTR(A) OLTC S/L | MTR | D17//4DTR(A)/SupLocal |  |  |  | DNP | 482 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D17 | 二甲DS | 0 |  | 4DTR(A) | #4DTR(A) |  | A_M | [14 empty] | 0533 |  | 0064 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.#4DTR(A)_A/M | #4DTR(A) OLTC A/M | MTR | D17//4DTR(A)/Tap Chan |  |  |  | DNP | 483 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D17 | 二甲DS | 0 |  | 4DTR(B) | #4DTR(B) |  | SupLocal | [14 empty] | 0536 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.#4DTR(B)_S/L | #4DTR(B) OLTC S/L | MTR | D17//4DTR(B)/SupLocal |  |  |  | DNP | 484 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D17 | 二甲DS | 0 |  | 4DTR(B) | #4DTR(B) |  | A_M | [14 empty] | 0537 |  | 0066 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.#4DTR(B)_A/M | #4DTR(B) OLTC A/M | MTR | D17//4DTR(B)/Tap Chan |  |  |  | DNP | 485 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D17 | 二甲DS | 161 | 161kV | 1780 | #4DTR(1780) |  | DS1 | 1781 | [13 empty] | 0704 | 705 | 0120 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1781_DS | 1781(#4DTR) DS | MTR | D17/161/1780/DS1 |  |  |  | DNP | 486 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D17 | 二甲DS | 161 | 161kV | 1780 | #4DTR(1780) |  | DS2 | 1782 | [13 empty] | 0706 | 707 | 0121 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1782_DS | 1782(#4DTR) DS | MTR | D17/161/1780/DS2 |  |  |  | DNP | 487 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 11 | 11kV | 250 | #5SC(250) |  | CB | [14 empty] | 0346 |  | 0150 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.250_CB | 250(11KV #5SC) CB | SC | D17/11/250/CB |  |  |  | DNP | 488 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | 250 | #5SC(250) |  | SCA | [14 empty] | 0347 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.250_SCA | 11KV #5SC 51,51N RY | SC | D17/11/250/SCA |  |  |  | DNP | 489 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | 250 | #5SC(250) |  | UVA | [14 empty] | 0348 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.250_OUVA | 11KV #5SC 27,59RY(欠壓或過壓) | SC | D17/11/250/UVA |  |  |  | DNP | 490 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | 260 | #6SC(260) |  | CB | [14 empty] | 0375 |  | 0157 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.260_CB | 260(11KV #6SC) CB | SC | D17/11/260/CB |  |  |  | DNP | 491 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | 260 | #6SC(260) |  | SCA | [14 empty] | 0376 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.260_SCA | 11KV #6SC 51,51N RY | SC | D17/11/260/SCA |  |  |  | DNP | 492 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | 260 | #6SC(260) |  | UVA | [14 empty] | 0377 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.260_OUVA | 11KV #6SC 27,59RY(欠壓或過壓) | SC | D17/11/260/UVA |  |  |  | DNP | 493 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | 260 | #6SC(260) |  | LBS | [14 empty] | 0710 | 711 | 0123 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.260_LBS | 260(11KV #6SC) LBS | SC | D17/11/6SC/LBS |  |  |  | DNP | 494 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 11 | 11kV | 270 | #7SC(270) |  | CB | [14 empty] | 0401 |  | 0164 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.270_CB | 270(11KV #7SC) CB | SC | D17/11/270/CB |  |  |  | DNP | 495 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | 270 | #7SC(270) |  | SCA | [14 empty] | 0402 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.270_SCA | 11KV #7SC 51,51N RY | SC | D17/11/270/SCA |  |  |  | DNP | 496 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | 270 | #7SC(270) |  | UVA | [14 empty] | 0403 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.270_OUVA | 11KV #7SC 27,59RY(欠壓或過壓) | SC | D17/11/270/UVA |  |  |  | DNP | 497 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | 270 | #7SC(270) |  | LBS | [14 empty] | 0712 | 713 | 0124 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.270_LBS | 270(11KV #7SC) LBS | SC | D17/11/7SC/LBS |  |  |  | DNP | 498 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 11 | 11kV | 280 | #8SC(280) |  | CB | [14 empty] | 0424 |  | 0170 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.280_CB | 280(11KV #8SC) CB | SC | D17/11/280/CB |  |  |  | DNP | 499 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 11 | 11kV | 280 | #8SC(280) |  | SCA | [14 empty] | 0425 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.280_SCA | 11KV #8SC 51,51N RY | SC | D17/11/280/SCA |  |  |  | DNP | 500 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | 280 | #8SC(280) |  | UVA | [14 empty] | 0426 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.280_OUVA | 11KV #8SC 27,59RY(欠壓或過壓) | SC | D17/11/280/UVA |  |  |  | DNP | 501 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | 280 | #8SC(280) |  | LBS | [14 empty] | 0714 | 715 | 0125 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.280_LBS | 280(11KV #8SC) LBS | SC | D17/11/8SC/LBS |  |  |  | DNP | 502 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 161 | 161kV | 1611BUS | #1BUS |  | VUA | [14 empty] | 1007 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | D17/161/1BUS/BUS_VUA |  |  |  | DNP | 503 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1611BUS | #1BUS |  | 87A | [14 empty] | 0042 | [10 empty] | 161KV_S | [8 empty] | 二甲DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | D17/161/1BUS/87A |  |  |  | DNP | 504 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1611BUS | #1BUS |  | 87UL | [14 empty] | 0538 |  | 0044 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | BUS | D17/161/1BUS/87UL |  |  |  | DNP | 505 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 161 | 161kV | 1612BUS | #2BUS |  | VUA | [14 empty] | 1008 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | D17/161/2BUS/BUS_VUA |  |  |  | DNP | 506 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1612BUS | #2BUS |  | 87A | [14 empty] | 0043 | [10 empty] | 161KV_S | [8 empty] | 二甲DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | D17/161/2BUS/87A |  |  |  | DNP | 507 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | 1612BUS | #2BUS |  | 87UL | [14 empty] | 0539 |  | 0045 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | BUS | D17/161/2BUS/87UL |  |  |  | DNP | 508 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 161 | 161kV | 161ABUS | #ABUS |  | 87A | [14 empty] | 0044 | [10 empty] | 161KV_S | [8 empty] | 二甲DS.161#ABUS_87A | 161KV #ABUS 87RY | BUS |  |  |  |  | DNP | 509 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 22 | 22kV | 11_ | 11/ |  | CBA | [14 empty] | 0978 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | D17/11/ComPoint/CBA |  |  |  | DNP | 510 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 22 | 22kV | 11_ | 11/ |  | CBF | [14 empty] | 0979 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | D17/11/ComPoint/CBF |  |  |  | DNP | 511 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV |  |  |  | CBA | [14 empty] | 1005 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.161KV_CBA | 161KV斷路器重故障 | OTHER | D17/161/ComPoint/CBA |  |  |  | DNP | 512 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV |  |  |  | CBF | [14 empty] | 1006 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | D17/161/ComPoint/CBF |  |  |  | DNP | 513 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | LINE | LINE |  | RCA | [14 empty] | 0045 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | D17/161/ComPoint/RCA |  |  |  | DNP | 514 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 22 | 22kV | _SC | 11/ SC |  | 60A | [14 empty] | 1018 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.23KV_SC_60A | 11/23KV SC 60A | OTHER | D17/0/ComPoint/60A |  |  |  | DNP | 515 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | RTU | RTU |  | SupLocal | [14 empty] | 0513 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.RTU_S/L | RTU SUPY/LOCAL | OTHER | D17/0/RTU/RTU_R_L |  |  |  | DNP | 516 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D17 | 二甲DS | 0 |  | TEST | TEST |  | CB | [14 empty] | 0512 |  | 0000 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.TEST_CB | TEST CB | OTHER | D17/0/RTU/Test_CB |  |  |  | DNP | 517 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  |  |  |  | Fire1 | [14 empty] | 0992 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | D17/0/StaDev/Fire1 |  |  |  | DNP | 518 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  |  |  |  | Fire2 | [14 empty] | 0993 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.火災警報(2) | 火災警報(2) | OTHER | D17/0/StaDev/Fire2 |  |  |  | DNP | 519 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  |  |  |  | 25PFA | [14 empty] | 0987 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER | D17/0/ComPoint/25PFA |  |  |  | DNP | 520 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  |  |  |  | 25TA | [14 empty] | 0986 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | D17/0/ComPoint/25TA |  |  |  | DNP | 521 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  |  |  |  | ACB1 | [14 empty] | 1001 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | D17/0/StaDev/ACB1 |  |  |  | DNP | 522 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ON/OFF | ON
D17 | 二甲DS | 0 |  |  |  |  | ACB2 | [14 empty] | 1002 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | D17/0/StaDev/ACB2 |  |  |  | DNP | 523 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ON/OFF | ON
D17 | 二甲DS | 0 |  |  |  |  | ACBA | [14 empty] | 1011 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.所內電源ACBA | 所內電源故障警報 | OTHER | D17/0/StaDev/ACBA |  |  |  | DNP | 524 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 所內電源開關ACB | 所內電源開關ACB |  | ACBT | [14 empty] | 1003 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | D17/0/StaDev/ACBT |  |  |  | DNP | 525 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ON/OFF | OFF
D17 | 二甲DS | 0 |  |  |  |  | STUV | [14 empty] | 1004 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | D17/0/StaDev/STUV |  |  |  | DNP | 526 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  |  |  |  | CHG1 | [14 empty] | 1010 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.直流充電機故障 | 直流充電機故障 | OTHER | D17/0/StaDev/CHG1 |  |  |  | DNP | 527 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 0 |  |  |  |  | DCA | [14 empty] | 1012 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.直流電源DCA | 直流電源故障警報 | OTHER | D17/0/StaDev/DCA |  |  |  | DNP | 528 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  |  |  |  | DCE | [14 empty] | 1009 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.直流電源DCE | 直流電源接地故障警報 | OTHER | D17/0/StaDev/DCE |  |  |  | DNP | 529 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  |  |  |  | CHG2 | [14 empty] | 0981 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | D17/0/StaDev/CHG2 |  |  |  | DNP | 530 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 0 |  |  |  |  | CommACF | [14 empty] | 0982 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | D17/0/StaDev/CommACF |  |  |  | DNP | 531 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 0 |  |  |  |  | Burglar1 | [14 empty] | 0995 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | D17/0/StaDev/Burglar1 |  |  |  | DNP | 532 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  |  |  |  | Door1 | [14 empty] | 0998 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.無人化門禁(1) | 無人化門禁(1)外圍 | OTHER | D17/0/StaDev/Door1 |  |  |  | DNP | 533 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  |  |  |  | Lights1 | [14 empty] | 0542 |  | 0126 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.開關場照明(A) | 景觀照明(A) | OTHER | D17/0/StaDev/Lights1 |  |  |  | DNP | 534 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ON/OFF | OFF
D17 | 二甲DS | 0 |  |  |  |  | Lights2 | [14 empty] | 0543 |  | 0127 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.開關場照明(B) | 景觀照明(B) | OTHER | D17/0/StaDev/Lights2 |  |  |  | DNP | 535 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ON/OFF | OFF
D17 | 二甲DS | 0 |  |  |  |  | Lights3 | [14 empty] | 1021 |  | 0256 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.開關場照明(C) | 路燈照明 | OTHER | D17/0/StaDev/DD_Light |  |  |  | DNP | 536 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ON/OFF | OFF
D17 | 二甲DS | 22 | 22kV | 11_ | 11/ |  | LOA | [14 empty] | 0980 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.11/23KV_LOA | 11/23KV饋線復閉失敗閉鎖 | OTHER | D17/11/ComPoint/LOA |  |  |  | DNP | 537 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 1550 | 二甲奇美實紅線(1550) |  | 87CFA | [14 empty] | 0552 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.1550_87CFA | 二甲奇美實紅線(1550)RY通訊故障 | OTHER | D17/161/1550/87CFA |  |  |  | DNP | 538 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 1550 | 二甲奇美實紅線(1550) |  | RYFA | [14 empty] | 0553 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.1550_RYFA | 二甲奇美實紅線(1550)數位RY故障 | OTHER | D17/161/1550/RYFA |  |  |  | DNP | 539 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 1560 | 二甲奇美實白線(1560) |  | 87CFA | [14 empty] | 0554 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.1560_87CFA | 二甲奇美實白線(1560)RY通訊故障 | OTHER | D17/161/1560/87CFA |  |  |  | DNP | 540 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 1560 | 二甲奇美實白線(1560) |  | RYFA | [14 empty] | 0555 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.1560_RYFA | 二甲奇美實白線(1560)數位RY故障 | OTHER | D17/161/1560/RYFA |  |  |  | DNP | 541 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 1570 | 仁德二甲紅線(1570) |  | 87CFA | [14 empty] | 0556 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.1570_87CFA | 仁德二甲紅線(1570)87RY通訊故障 | OTHER | D17/161/1570/87CFA |  |  |  | DNP | 542 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 1570 | 仁德二甲紅線(1570) |  | RYFA | [14 empty] | 0557 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.1570_RYFA | 仁德二甲紅線(1570)數位電驛故障 | OTHER | D17/161/1570/RYFA |  |  |  | DNP | 543 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 1580 | 仁德二甲白線(1580) |  | 87CFA | [14 empty] | 0558 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.1580_87CFA | 仁德二甲白線(1580)87RY通訊故障 | OTHER | D17/161/1580/87CFA |  |  |  | DNP | 544 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 1580 | 仁德二甲白線(1580) |  | RYFA | [14 empty] | 0559 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.1580_RYFA | 仁德二甲白線(1580)數位電驛故障 | OTHER | D17/161/1580/RYFA |  |  |  | DNP | 545 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 1610 | 龍崎山上三路(1610) |  | 87CFA | [14 empty] | 0560 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.1610_87CFA | 龍崎山上三路(1610)87RY通訊故障 | OTHER | D17/161/1610/87CFA |  |  |  | DNP | 546 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 1610 | 龍崎山上三路(1610) |  | DTTA | [14 empty] | 0562 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.1610_DTTA | 龍崎山上三路(1610) 遠方遙跳 | OTHER | D17/161/1610/DTTA |  |  |  | DNP | 547 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 1610 | 龍崎山上三路(1610) |  | RYFA | [14 empty] | 0561 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.1610_RYFA | 龍崎山上三路(1610)數位電驛故障 | OTHER | D17/161/1610/RYFA |  |  |  | DNP | 548 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | _BUS | BUS |  | 87CTFA | [14 empty] | 1014 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.161KV_BUS_CTFA | 161KV BUS CT 回路故障 | OTHER | D17/161/ComPoint/12B_CTFA |  |  |  | DNP | 549 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | _OSCA | _OSCA |  | 1 | [14 empty] | 0109 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.161KV_OSCA_1 | 161KV示波器啟動警報 | OTHER | D17/0/ComPoint/OSCA |  |  |  | DNP | 550 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | _OSCF | _OSCF |  | 1 | [14 empty] | 0110 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.161KV_OSCF_1 | 161KV示波器故障 | OTHER | D17/0/ComPoint/OSCF |  |  |  | DNP | 551 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 161 | 161kV | _OSCF | _OSCF | [16 empty] | 0111 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.161KV_OSCF_2 | 161KV示波器啟DC故障 | OTHER | D17/161/ComPoint/1A5Other |  |  |  | DNP | 552 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 1620 | 龍崎山上四路(1620) |  | 87CFA | [14 empty] | 0563 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.1620_87CFA | 龍崎山上四路(1620)87RY通訊故障 | OTHER | D17/161/1620/87CFA |  |  |  | DNP | 553 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 1620 | 龍崎山上四路(1620) |  | DTTA | [14 empty] | 0565 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.1620_DTTA | 龍崎山上四路(1620) 遠方遙跳 | OTHER | D17/161/1620/DTTA |  |  |  | DNP | 554 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 1620 | 龍崎山上四路(1620) |  | RYFA | [14 empty] | 0564 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.1620_RYFA | 龍崎山上四路(1620)數位電驛故障 | OTHER | D17/161/1620/RYFA |  |  |  | DNP | 555 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 350 | #3DTR(350) |  | 81A | [14 empty] | 0081 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.350_81A | 350 #3DTR(A) 81RY動作 | OTHER | D17/11/350/81A |  |  |  | DNP | 556 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 350 | #3DTR(350) |  | 81UL | [14 empty] | 0970 |  | 0180 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.350_81UL | 350 #3DTR(A) 81RY U/L | OTHER | D17/11/350/81UL |  |  |  | DNP | 557 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 0 |  | 350 | #3DTR(350) |  | GDA | [14 empty] | 0080 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.350_GDA | 350開關箱IED RY GDA | OTHER | D17/11/350/GDA |  |  |  | DNP | 558 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 350 | #3DTR(350) |  | PHA2 | [14 empty] | 0079 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.350_PHA2 | 350開關箱IED RY PHA | OTHER | D17/11/350/PHA |  |  |  | DNP | 559 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 360 | #3DTR(360) |  | 81A | [14 empty] | 0085 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.360_81A | 360 #3DTR(B) 81RY動作 | OTHER | D17/11/360/81A |  |  |  | DNP | 560 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 360 | #3DTR(360) |  | 81UL | [14 empty] | 0971 |  | 0181 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.360_81UL | 360 #3DTR(B) 81RY U/L | OTHER | D17/11/360/81UL |  |  |  | DNP | 561 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 0 |  | 360 | #3DTR(360) |  | GDA | [14 empty] | 0084 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.360_GDA | 360開關箱IED RY GDA | OTHER | D17/11/360/GDA |  |  |  | DNP | 562 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 360 | #3DTR(360) |  | PHA2 | [14 empty] | 0083 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.360_PHA2 | 360開關箱IED RY PHA | OTHER | D17/11/360/PHA |  |  |  | DNP | 563 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 370 | #4DTR(370) |  | 81A | [14 empty] | 0097 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.370_81A | 370 #4DTR(A) 81RY動作 | OTHER | D17/11/370/81A |  |  |  | DNP | 564 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 370 | #4DTR(370) |  | 81UL | [14 empty] | 0972 |  | 0182 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.370_81UL | 370 #4DTR(A) 81RY U/L | OTHER | D17/11/370/81UL |  |  |  | DNP | 565 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 0 |  | 370 | #4DTR(370) |  | GDA | [14 empty] | 0096 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.370_GDA | 370開關箱IED RY GDA | OTHER | D17/11/370/GDA |  |  |  | DNP | 566 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 370 | #4DTR(370) |  | PHA2 | [14 empty] | 0095 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.370_PHA2 | 370開關箱IED RY PHA | OTHER | D17/11/370/PHA |  |  |  | DNP | 567 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 380 | #4DTR(380) |  | 81A | [14 empty] | 0101 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.380_81A | 380 #4DTR(B) 81RY動作 | OTHER | D17/11/380/81A |  |  |  | DNP | 568 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 380 | #4DTR(380) |  | 81UL | [14 empty] | 0973 |  | 0183 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.380_81UL | 380 #4DTR(B) 81RY U/L | OTHER | D17/11/380/81UL |  |  |  | DNP | 569 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 0 |  | 380 | #4DTR(380) |  | GDA | [14 empty] | 0100 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.380_GDA | 380開關箱IED RY GDA | OTHER | D17/11/380/GDA |  |  |  | DNP | 570 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 380 | #4DTR(380) |  | PHA2 | [14 empty] | 0099 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.380_PHA2 | 380開關箱IED RY PHA | OTHER | D17/11/380/PHA |  |  |  | DNP | 571 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K611 | 甲11線(K611) |  | 81A | [14 empty] | 0329 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K611_81A | 11KV甲11線(K611) 81RY | OTHER | D17/11/F17/81A |  |  |  | DNP | 572 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K612 | 甲12線(K612) |  | 81A | [14 empty] | 0333 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K612_81A | 11KV甲12線(K612) 81RY | OTHER | D17/11/F18/81A |  |  |  | DNP | 573 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K613 | 甲13線(K613) |  | 81A | [14 empty] | 0337 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K613_81A | 11KV甲13線(K613) 81RY | OTHER | D17/11/F19/81A |  |  |  | DNP | 574 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K614 | 甲14線(K614) |  | 81A | [14 empty] | 0341 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K614_81A | 11KV甲14線(K614) 81RY | OTHER | D17/11/F20/81A |  |  |  | DNP | 575 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K615 | 甲15線(K615) |  | 81A | [14 empty] | 0345 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K615_81A | 11KV甲15線(K615) 81RY | OTHER | D17/11/F21/81A |  |  |  | DNP | 576 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K621 | 甲21線(K621) |  | 81A | [14 empty] | 0358 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K621_81A | 11KV甲21線(K621) 81RY | OTHER | D17/11/F22/81A |  |  |  | DNP | 577 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K622 | 甲22線(K622) |  | 81A | [14 empty] | 0362 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K622_81A | 11KV甲22線(K622) 81RY | OTHER | D17/11/F23/81A |  |  |  | DNP | 578 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K623 | 甲23線(K623) |  | 81A | [14 empty] | 0366 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K623_81A | 11KV甲23線(K623) 81RY | OTHER | D17/11/F24/81A |  |  |  | DNP | 579 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K624 | 甲24線(K624) |  | 81A | [14 empty] | 0370 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K624_81A | 11KV甲24線(K624) 81RY | OTHER | D17/11/F25/81A |  |  |  | DNP | 580 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K625 | 甲25線(K625) |  | 81A | [14 empty] | 0374 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K625_81A | 11KV甲25線(K625) 81RY | OTHER | D17/11/F26/81A |  |  |  | DNP | 581 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K631 | 甲31線(K631) |  | 81A | [14 empty] | 0384 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K631_81A | 11KV甲31線(K631) 81RY | OTHER | D17/11/F27/81A |  |  |  | DNP | 582 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K632 | 甲32線(K632) |  | 81A | [14 empty] | 0388 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K632_81A | 11KV甲32線(K632) 81RY | OTHER | D17/11/F28/81A |  |  |  | DNP | 583 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K633 | 甲33線(K633) |  | 81A | [14 empty] | 0392 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K633_81A | 11KV甲33線(K633) 81RY | OTHER | D17/11/F29/81A |  |  |  | DNP | 584 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K634 | 甲34線(K634) |  | 81A | [14 empty] | 0396 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K634_81A | 11KV甲34線(K634) 81RY | OTHER | D17/11/F30/81A |  |  |  | DNP | 585 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K635 | 甲35線(K635) |  | 81A | [14 empty] | 0400 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K635_81A | 11KV甲35線(K635) 81RY | OTHER | D17/11/F31/81A |  |  |  | DNP | 586 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K641 | 甲41線(K641) |  | 81A | [14 empty] | 0407 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K641_81A | 11KV甲41線(K641) 81RY | OTHER | D17/11/F32/81A |  |  |  | DNP | 587 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K642 | 甲42線(K642) |  | 81A | [14 empty] | 0411 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K642_81A | 11KV甲42線(K642) 81RY | OTHER | D17/11/F33/81A |  |  |  | DNP | 588 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K643 | 甲43線(K643) |  | 81A | [14 empty] | 0415 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K643_81A | 11KV甲43線(K643) 81RY | OTHER | D17/11/F34/81A |  |  |  | DNP | 589 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K644 | 甲44線(K644) |  | 81A | [14 empty] | 0419 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K644_81A | 11KV甲44線(K644) 81RY | OTHER | D17/11/F35/81A |  |  |  | DNP | 590 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | K645 | 甲45線(K645) |  | 81A | [14 empty] | 0423 | [10 empty] | DDCS4_1 | [8 empty] | 二甲DS.K645_81A | 11KV甲45線(K645) 81RY | OTHER | D17/11/F36/81A |  |  |  | DNP | 591 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  |  |  |  | PMA | [14 empty] | 1023 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.PMA | 電力量測表計故障 | OTHER | D17/0/StaDev/PMA |  |  |  | DNP | 592 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 0 |  |  |  |  | 水位警報(1) | [14 empty] | 1015 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.水位警報(1) | 地下室水位警報(1) | OTHER | D17/0/StaDev/Water1 |  |  |  | DNP | 593 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  |  |  |  | 水位警報(2) | [14 empty] | 1016 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.水位警報(2) | 地下室水位警報(2) | OTHER | D17/0/StaDev/Water2 |  |  |  | DNP | 594 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  |  |  |  | OilLeak1 | [14 empty] | 1019 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.洩油池警報(1) | 洩油池水位(中)警報 | OTHER | D17/0/StaDev/OilLeak1 |  |  |  | DNP | 595 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  |  |  |  | OilLeak2 | [14 empty] | 1020 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.洩油池警報(2) | 洩油池水位(高)警報 | OTHER | D17/0/StaDev/OilLeak2 |  |  |  | DNP | 596 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  |  |  |  | 通信機房溫度 | [14 empty] | 0985 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.通信機房溫度 | 通訊室或控制室溫度警報 | OTHER | D17/0/StaDev/R_Temp |  |  |  | DNP | 597 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 11 | 11kV | 250 | #5SC(250) |  | LBS | [14 empty] | 0708 | 709 | 0122 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.250_LBS | 250(11KV #5SC) LBS | SC | D17/11/5SC/LBS |  |  |  | DNP | 598 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 161 | 161kV | _BUS | BUS |  | RYFA | [14 empty] | 1013 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | D17/161/ComPoint/BUS_RYFA |  |  |  | DNP | 599 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 1550 | 二甲奇美實紅線(1550) |  | 87A1 | [14 empty] | 0017 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.1550_87A1 | 二甲奇美實紅線(1550)#1 87RY | OTHER | D17/161/1550/87A1 |  |  |  | DNP | 600 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 1550 | 二甲奇美實紅線(1550) |  | 87A2 | [14 empty] | 0112 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.1550_87A2 | 二甲奇美實紅線(1550)#2 87RY | OTHER | D17/161/1550/87A2 |  |  |  | DNP | 601 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 1550 | 二甲奇美實紅線(1550) |  | 1_87UL1 | [14 empty] | 0594 |  | 0032 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1550_87UL1 | 二甲奇美實紅線(1550)#187RY U/L | OTHER | D17/161/1550/1_87UL1 |  |  |  | DNP | 602 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 0 |  | 1550 | 二甲奇美實紅線(1550) |  | 1_87UL2 | [14 empty] | 0595 |  | 0033 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1550_87UL2 | 二甲奇美實紅線(1550)#287RY U/L | OTHER | D17/161/1550/1_87UL2 |  |  |  | DNP | 603 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 0 |  | 1560 | 二甲奇美實白線(1560) |  | 87A1 | [14 empty] | 0021 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.1560_87A1 | 二甲奇美實白線(1560)#1 87RY | OTHER | D17/161/1560/87A1 |  |  |  | DNP | 604 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 1560 | 二甲奇美實白線(1560) |  | 87A2 | [14 empty] | 0113 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.1560_87A2 | 二甲奇美實白線(1560)#2 87RY | OTHER | D17/161/1560/87A2 |  |  |  | DNP | 605 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 1560 | 二甲奇美實白線(1560) |  | 1_87UL1 | [14 empty] | 0596 |  | 0034 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1560_87UL1 | 二甲奇美實白線(1560)#187RY U/L | OTHER | D17/161/1560/1_87UL1 |  |  |  | DNP | 606 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 0 |  | 1560 | 二甲奇美實白線(1560) |  | 1_87UL2 | [14 empty] | 0597 |  | 0035 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.1560_87UL2 | 二甲奇美實白線(1560)#287RY U/L | OTHER | D17/161/1560/1_87UL2 |  |  |  | DNP | 607 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 0 |  | BVS | BVS |  | RY | [14 empty] | 0988 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.BVS_RY | BVS GRZ100 RY U/L | OTHER | D17/0/ComPoint/GRZ100 |  |  |  | DNP | 608 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | LOCK/USE | USE
D17 | 二甲DS | 0 |  |  |  |  | GEN | [14 empty] | 0541 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.GEN | 緊急發電機運轉 | OTHER | D17/0/StaDev/2A5Other |  |  |  | DNP | 609 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ON/OFF | OFF
D17 | 二甲DS | 0 |  | OLTC | OLTC |  | OLTCA | [14 empty] | 1017 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | D17/0/ComPoint/OLTC_A |  |  |  | DNP | 610 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 22 | 22kV | 安集大成 | 安集大成(K461) |  | 59V0 | [14 empty] | 0434 | [10 empty] | DDCS4_1 | [8 empty] | 仁德DS.安集大成_59V0 | 23KV安集大成(K461) 59V0 | OTHER |  |  |  |  | DNP | 611 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 22 | 22kV | 安集大成 | 安集大成(K461) |  | 81A | [14 empty] | 0435 | [10 empty] | DDCS4_1 | [8 empty] | 仁德DS.安集大成_81A | 23KV安集大成(K461) 81A | OTHER |  |  |  |  | DNP | 612 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 22 | 22kV | 安集大成 | 安集大成(K461) |  | CB | [14 empty] | 0430 | [10 empty] | DDCS4_1 | [8 empty] | 仁德DS.安集大成_CB | 23KV安集大成(K461) CB | OTHER |  |  |  |  | DNP | 613 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 22 | 22kV | 安集大成 | 安集大成(K461) |  | DS1 | 安集大成 | [13 empty] | 0716 | 717 | [9 empty] | DDCS4_1 | [8 empty] | 仁德DS.安集大成_DS | 23KV安集大成(K461) DS | OTHER |  |  |  |  | DNP | 614 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 22 | 22kV | 安集大成 | 安集大成(K461) |  | GDA | [14 empty] | 0432 | [10 empty] | DDCS4_1 | [8 empty] | 仁德DS.安集大成_GDA | 23KV安集大成(K461) GDA | OTHER |  |  |  |  | DNP | 615 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 22 | 22kV | 安集大成 | 安集大成(K461) |  | PHA | [14 empty] | 0431 | [10 empty] | DDCS4_1 | [8 empty] | 仁德DS.安集大成_PHA | 23KV安集大成(K461) PHA | OTHER |  |  |  |  | DNP | 616 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 22 | 22kV | 安集大成 | 安集大成(K461) |  | PTDS | [14 empty] | 0718 | 719 | [9 empty] | DDCS4_1 | [8 empty] | 仁德DS.安集大成_PTDS | 23KV安集大成(K461) PTDS | OTHER |  |  |  |  | DNP | 617 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D17 | 二甲DS | 22 | 22kV | 安集大成 | 安集大成(K461) |  | RYFA | [14 empty] | 0433 | [10 empty] | DDCS4_1 | [8 empty] | 仁德DS.安集大成_RYA | 23KV安集大成(K461) 27/59A | OTHER |  |  |  |  | DNP | 618 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 3DTR | #3DTR |  | DTR_86A | [14 empty] | 0046 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.#3DTR_86A | #3DTR 86(50/50N/51Z/87/96)RY | OTHER |  |  |  |  | DNP | 619 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 3DTR | #3DTR |  | 1_87UL1 | [14 empty] | 0524 |  | 0046 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.#3DTR_87UL1 | #3DTR 第一套 87RY U/L | OTHER | D17//3DTR/87UL |  |  |  | DNP | 620 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 0 |  | 3DTR | #3DTR |  | 1_87UL2 | [14 empty] | 0974 |  | 0047 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.#3DTR_87UL2 | #3DTR 第二套 87RY U/L | OTHER |  |  |  |  | DNP | 621 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 0 |  | 3DTR | #3DTR |  | RYFA | [14 empty] | 0976 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.#3DTR_RYFA | #3DTR 數位電驛故障 | OTHER |  |  |  |  | DNP | 622 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 3DTR | #3DTR |  | 51Z_UL | [14 empty] | 0975 |  | 0048 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.#3DTR_51ZUL | #3DTR 51Z RY U/L | OTHER |  |  |  |  | DNP | 623 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 0 |  | 4DTR | #4DTR |  | DTR_86A | [14 empty] | 0047 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.#4DTR_86A | #4DTR 86(50/50N/51Z/87/96)RY | OTHER |  |  |  |  | DNP | 624 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 4DTR | #4DTR |  | 1_87UL1 | [14 empty] | 0531 |  | 0049 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.#4DTR_87UL1 | #4DTR 第一套 87RY U/L | OTHER | D17//4DTR/87UL |  |  |  | DNP | 625 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 0 |  | 4DTR | #4DTR |  | 1_87UL2 | [14 empty] | 0989 |  | 0050 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.#4DTR_87UL2 | #4DTR 第二套 87RY U/L | OTHER |  |  |  |  | DNP | 626 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 0 |  | 4DTR | #4DTR |  | RYFA | [14 empty] | 0991 | [10 empty] | ADCS_S | [8 empty] | 二甲DS.#4DTR_RYFA | #4DTR 數位電驛故障 | OTHER |  |  |  |  | DNP | 627 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D17 | 二甲DS | 0 |  | 4DTR | #4DTR |  | 51Z_UL | [14 empty] | 0990 |  | 0051 | [8 empty] | ADCS_S | [8 empty] | 二甲DS.#4DTR_51ZUL | #4DTR 51Z RY U/L | OTHER |  |  |  |  | DNP | 628 | DNPDIPoint | DS055 |  |  | DI | [34 empty] | USE/LOCK | USE
D17 | 二甲DS | 11 | 11kV | 250_SC | #5SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 二甲DS.250_SC_CAP | 11KV#5SC 容量 | SC | [5 empty] | 629 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 11 | 11kV | 260_SC | #6SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 二甲DS.260_SC_CAP | 11KV#6SC 容量 | SC | [5 empty] | 630 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 11 | 11kV | 270_SC | #7SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 二甲DS.270_SC_CAP | 11KV#7SC 容量 | SC | [5 empty] | 631 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 11 | 11kV | 280_SC | #8SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 二甲DS.280_SC_CAP | 11KV#8SC 容量 | SC | [5 empty] | 632 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D17 | 二甲DS | 161 | 161kV | 1550 | 二甲奇美實紅線(1550) |  | LE0 | 1550LE | [24 empty] | ADCS_S | [8 empty] | 二甲DS.1550LE | 1550LE (非取樣點) | LINE161 | D17/161/1550/LE0 |  |  |  |  | 633 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 1550 | 二甲奇美實紅線(1550) |  | BE0 | 1550BE | [24 empty] | ADCS_S | [8 empty] | 二甲DS.1550BE | 1550BE (非取樣點) | LINE161 | D17/161/1550/BE0 |  |  |  |  | 634 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 1560 | 二甲奇美實白線(1560) |  | LE0 | 1560LE | [24 empty] | ADCS_S | [8 empty] | 二甲DS.1560LE | 1560LE (非取樣點) | LINE161 | D17/161/1560/LE0 |  |  |  |  | 635 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 1560 | 二甲奇美實白線(1560) |  | BE0 | 1560BE | [24 empty] | ADCS_S | [8 empty] | 二甲DS.1560BE | 1560BE (非取樣點) | LINE161 | D17/161/1560/BE0 |  |  |  |  | 636 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 1570 | 仁德二甲紅線(1570) |  | LE0 | 1570LE | [24 empty] | ADCS_S | [8 empty] | 二甲DS.1570LE | 1570LE (非取樣點) | LINE161 | D17/161/1570/LE0 |  |  |  |  | 637 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 1570 | 仁德二甲紅線(1570) |  | BE0 | 1570BE | [24 empty] | ADCS_S | [8 empty] | 二甲DS.1570BE | 1570BE (非取樣點) | LINE161 | D17/161/1570/BE0 |  |  |  |  | 638 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 1580 | 仁德二甲白線(1580) |  | LE0 | 1580LE | [24 empty] | ADCS_S | [8 empty] | 二甲DS.1580LE | 1580LE (非取樣點) | LINE161 | D17/161/1580/LE0 |  |  |  |  | 639 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 1580 | 仁德二甲白線(1580) |  | BE0 | 1580BE | [24 empty] | ADCS_S | [8 empty] | 二甲DS.1580BE | 1580BE (非取樣點) | LINE161 | D17/161/1580/BE0 |  |  |  |  | 640 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 1610 | 龍崎山上三路(1610) |  | LE0 | 1610LE | [24 empty] | ADCS_S | [8 empty] | 二甲DS.1610LE | 1610LE (非取樣點) | LINE161 | D17/161/1610/LE0 |  |  |  |  | 641 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 1610 | 龍崎山上三路(1610) |  | BE0 | 1610BE | [24 empty] | ADCS_S | [8 empty] | 二甲DS.1610BE | 1610BE (非取樣點) | LINE161 | D17/161/1610/BE0 |  |  |  |  | 642 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 1620 | 龍崎山上四路(1620) |  | LE0 | 1620LE | [24 empty] | ADCS_S | [8 empty] | 二甲DS.1620LE | 1620LE (非取樣點) | LINE161 | D17/161/1620/LE0 |  |  |  |  | 643 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 1620 | 龍崎山上四路(1620) |  | BE0 | 1620BE | [24 empty] | ADCS_S | [8 empty] | 二甲DS.1620BE | 1620BE (非取樣點) | LINE161 | D17/161/1620/BE0 |  |  |  |  | 644 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | K611 | K611_DS |  | DS1 | K611_DS | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K611_DS | K611_DS (非取樣點) | FEEDER | [5 empty] | 645 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | K611 | K611_ES |  | LE0 | K611_ES | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K611_ES | K611_ES (非取樣點) | FEEDER | [5 empty] | 646 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | K612 | K612_DS |  | DS1 | K612_DS | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K612_DS | K612_DS (非取樣點) | FEEDER | [5 empty] | 647 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | K612 | K612_ES |  | LE0 | K612_ES | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K612_ES | K612_ES (非取樣點) | FEEDER | [5 empty] | 648 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | K613 | K613_DS |  | DS1 | K613_DS | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K613_DS | K613_DS (非取樣點) | FEEDER | [5 empty] | 649 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | K613 | K613_ES |  | LE0 | K613_ES | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K613_ES | K613_ES (非取樣點) | FEEDER | [5 empty] | 650 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | K614 | K614_DS |  | DS1 | K614_DS | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K614_DS | K614_DS (非取樣點) | FEEDER | [5 empty] | 651 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | K614 | K614_ES |  | LE0 | K614_ES | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K614_ES | K614_ES (非取樣點) | FEEDER | [5 empty] | 652 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | K615 | K615_DS |  | DS1 | K615_DS | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K615_DS | K615_DS (非取樣點) | FEEDER | [5 empty] | 653 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | K615 | K615_ES |  | LE0 | K615_ES | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K615_ES | K615_ES (非取樣點) | FEEDER | [5 empty] | 654 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | K621 | K621_DS |  | DS1 | K621_DS | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K621_DS | K621_DS (非取樣點) | FEEDER | [5 empty] | 655 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | K621 | K621_ES |  | LE0 | K621_ES | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K621_ES | K621_ES (非取樣點) | FEEDER | [5 empty] | 656 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | K622 | K622_DS |  | DS1 | K622_DS | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K622_DS | K622_DS (非取樣點) | FEEDER | [5 empty] | 657 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | K622 | K622_ES |  | LE0 | K622_ES | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K622_ES | K622_ES (非取樣點) | FEEDER | [5 empty] | 658 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | K623 | K623_DS |  | DS1 | K623_DS | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K623_DS | K623_DS (非取樣點) | FEEDER | [5 empty] | 659 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | K623 | K623_ES |  | LE0 | K623_ES | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K623_ES | K623_ES (非取樣點) | FEEDER | [5 empty] | 660 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | K624 | K624_DS |  | DS1 | K624_DS | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K624_DS | K624_DS (非取樣點) | FEEDER | [5 empty] | 661 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | K624 | K624_ES |  | LE0 | K624_ES | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K624_ES | K624_ES (非取樣點) | FEEDER | [5 empty] | 662 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | K625 | K625_DS |  | DS1 | K625_DS | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K625_DS | K625_DS (非取樣點) | FEEDER | [5 empty] | 663 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | K625 | K625_ES |  | LE0 | K625_ES | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K625_ES | K625_ES (非取樣點) | FEEDER | [5 empty] | 664 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | K631 | K631_DS |  | DS1 | K631_DS | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K631_DS | K631_DS (非取樣點) | FEEDER | [5 empty] | 665 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | K631 | K631_ES |  | LE0 | K631_ES | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K631_ES | K631_ES (非取樣點) | FEEDER | [5 empty] | 666 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | K632 | K632_DS |  | DS1 | K632_DS | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K632_DS | K632_DS (非取樣點) | FEEDER | [5 empty] | 667 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | K632 | K632_ES |  | LE0 | K632_ES | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K632_ES | K632_ES (非取樣點) | FEEDER | [5 empty] | 668 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | K633 | K633_DS |  | DS1 | K633_DS | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K633_DS | K633_DS (非取樣點) | FEEDER | [5 empty] | 669 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | K633 | K633_ES |  | LE0 | K633_ES | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K633_ES | K633_ES (非取樣點) | FEEDER | [5 empty] | 670 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | K634 | K634_DS |  | DS1 | K634_DS | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K634_DS | K634_DS (非取樣點) | FEEDER | [5 empty] | 671 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | K634 | K634_ES |  | LE0 | K634_ES | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K634_ES | K634_ES (非取樣點) | FEEDER | [5 empty] | 672 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | K635 | K635_DS |  | DS1 | K635_DS | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K635_DS | K635_DS (非取樣點) | FEEDER | [5 empty] | 673 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | K635 | K635_ES |  | LE0 | K635_ES | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K635_ES | K635_ES (非取樣點) | FEEDER | [5 empty] | 674 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | K641 | K641_DS |  | DS1 | K641_DS | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K641_DS | K641_DS (非取樣點) | FEEDER | [5 empty] | 675 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | K641 | K641_ES |  | LE0 | K641_ES | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K641_ES | K641_ES (非取樣點) | FEEDER | [5 empty] | 676 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | K642 | K642_DS |  | DS1 | K642_DS | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K642_DS | K642_DS (非取樣點) | FEEDER | [5 empty] | 677 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | K642 | K642_ES |  | LE0 | K642_ES | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K642_ES | K642_ES (非取樣點) | FEEDER | [5 empty] | 678 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | K643 | K643_DS |  | DS1 | K643_DS | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K643_DS | K643_DS (非取樣點) | FEEDER | [5 empty] | 679 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | K643 | K643_ES |  | LE0 | K643_ES | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K643_ES | K643_ES (非取樣點) | FEEDER | [5 empty] | 680 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | K644 | K644_DS |  | DS1 | K644_DS | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K644_DS | K644_DS (非取樣點) | FEEDER | [5 empty] | 681 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | K644 | K644_ES |  | LE0 | K644_ES | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K644_ES | K644_ES (非取樣點) | FEEDER | [5 empty] | 682 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | K645 | K645_DS |  | DS1 | K645_DS | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K645_DS | K645_DS (非取樣點) | FEEDER | [5 empty] | 683 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | K645 | K645_ES |  | LE0 | K645_ES | [24 empty] | DDCS4_1 | [8 empty] | 二甲DS.K645_ES | K645_ES (非取樣點) | FEEDER | [5 empty] | 684 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [24 empty] | ADCS_S | [8 empty] | 二甲DS.1501E | 1501E (非取樣點) | TIE | D17/161/1500/E1 |  |  |  |  | 685 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [24 empty] | ADCS_S | [8 empty] | 二甲DS.1502E | 1502E (非取樣點) | TIE | D17/161/1500/E2 |  |  |  |  | 686 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | 300 | TIE(300) |  | E1 | 301E | [24 empty] | ADCS_S | [8 empty] | 二甲DS.301E | 301E (非取樣點) | TIE | D17/11/300/E1 |  |  |  |  | 687 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | 300 | TIE(300) |  | E2 | 302E | [24 empty] | ADCS_S | [8 empty] | 二甲DS.302E | 302E (非取樣點) | TIE | D17/11/300/E2 |  |  |  |  | 688 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | 301 | 301 |  | 301 | 301 | [24 empty] | ADCS_S | [8 empty] | 二甲DS.301 | 301 (非取樣點) | TIE | D17/11/300/D1 |  |  |  |  | 689 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | 302 | 302 |  | 302 | 302 | [24 empty] | ADCS_S | [8 empty] | 二甲DS.302 | 302 (非取樣點) | TIE | D17/11/300/D2 |  |  |  |  | 690 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | 400 | TIE(400) |  | E1 | 401E | [24 empty] | ADCS_S | [8 empty] | 二甲DS.401E | 401E (非取樣點) | TIE | D17/11/400/E1 |  |  |  |  | 691 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | 400 | TIE(400) |  | E2 | 402E | [24 empty] | ADCS_S | [8 empty] | 二甲DS.402E | 402E (非取樣點) | TIE | D17/11/400/E2 |  |  |  |  | 692 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | 401 | 401 |  | 401 | 401 | [24 empty] | ADCS_S | [8 empty] | 二甲DS.401 | 401 (非取樣點) | TIE | D17/11/400/D1 |  |  |  |  | 693 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | 402 | 402 |  | 402 | 402 | [24 empty] | ADCS_S | [8 empty] | 二甲DS.402 | 402 (非取樣點) | TIE | D17/11/400/D2 |  |  |  |  | 694 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | 391 | 391 |  | 391 | 391 | [24 empty] | ADCS_S | [8 empty] | 二甲DS.391 | 391 (非取樣點) | OTHER | D17/11/390/D1 |  |  |  |  | 695 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | 391E | 391E |  | 391E | 391E | [24 empty] | ADCS_S | [8 empty] | 二甲DS.391E | 391E (非取樣點) | OTHER | D17/11/390/E1 |  |  |  |  | 696 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | 491 | 491 |  | 491 | 491 | [24 empty] | ADCS_S | [8 empty] | 二甲DS.491 | 491 (非取樣點) | OTHER | D17/11/490/D1 |  |  |  |  | 697 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | 491E | 491E |  | 491E | 491E | [24 empty] | ADCS_S | [8 empty] | 二甲DS.491E | 491E (非取樣點) | OTHER | D17/11/490/E1 |  |  |  |  | 698 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | 1770TE | [24 empty] | ADCS_S | [8 empty] | 二甲DS.1770TE | 1770TE (非取樣點) | MTR | D17/161/1770/TE0 |  |  |  |  | 699 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | 1770BE | [24 empty] | ADCS_S | [8 empty] | 二甲DS.1770BE | 1770BE (非取樣點) | MTR | D17/161/1770/BE0 |  |  |  |  | 700 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | 351 | 351 |  | 351 | 351 | [24 empty] | ADCS_S | [8 empty] | 二甲DS.351 | 351 (非取樣點) | MTR | D17/11/350/D1 |  |  |  |  | 701 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | 350 | #3DTR(350) |  | E1 | 351E | [24 empty] | ADCS_S | [8 empty] | 二甲DS.351E | 351E (非取樣點) | MTR | D17/11/350/E1 |  |  |  |  | 702 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | 361 | 361 |  | 361 | 361 | [24 empty] | ADCS_S | [8 empty] | 二甲DS.361 | 361 (非取樣點) | MTR | D17/11/360/D1 |  |  |  |  | 703 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | 360 | #3DTR(360) |  | E1 | 361E | [24 empty] | ADCS_S | [8 empty] | 二甲DS.361E | 361E (非取樣點) | MTR | D17/11/360/E1 |  |  |  |  | 704 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 1780 | #4DTR(1780) |  | TE0 | 1780TE | [24 empty] | ADCS_S | [8 empty] | 二甲DS.1780TE | 1780TE (非取樣點) | MTR | D17/161/1780/TE0 |  |  |  |  | 705 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 161 | 161kV | 1780 | #4DTR(1780) |  | BE0 | 1780BE | [24 empty] | ADCS_S | [8 empty] | 二甲DS.1780BE | 1780BE (非取樣點) | MTR | D17/161/1780/BE0 |  |  |  |  | 706 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | 371 | 371 |  | 371 | 371 | [24 empty] | ADCS_S | [8 empty] | 二甲DS.371 | 371 (非取樣點) | MTR | D17/11/370/D1 |  |  |  |  | 707 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | 370 | #4DTR(370) |  | E1 | 371E | [24 empty] | ADCS_S | [8 empty] | 二甲DS.371E | 371E (非取樣點) | MTR | D17/11/370/E1 |  |  |  |  | 708 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | 381 | 381 |  | 381 | 381 | [24 empty] | ADCS_S | [8 empty] | 二甲DS.381 | 381 (非取樣點) | MTR | D17/11/380/D1 |  |  |  |  | 709 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | 380 | #4DTR(380) |  | E1 | 381E | [24 empty] | ADCS_S | [8 empty] | 二甲DS.381E | 381E (非取樣點) | MTR | D17/11/380/E1 |  |  |  |  | 710 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | 251E | 251E |  | 251E | 251E | [24 empty] | ADCS_S | [8 empty] | 二甲DS.251E | 251E (非取樣點) | SC | D17/11/250/E1 |  |  |  |  | 711 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | 261E | 261E |  | 261E | 261E | [24 empty] | ADCS_S | [8 empty] | 二甲DS.261E | 261E (非取樣點) | SC | D17/11/260/E1 |  |  |  |  | 712 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | 261 | 261 |  | 261 | 261 | [24 empty] | ADCS_S | [8 empty] | 二甲DS.261 | 261 (非取樣點) | SC | D17/11/260/D1 |  |  |  |  | 713 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | 271E | 271E |  | 271E | 271E | [24 empty] | ADCS_S | [8 empty] | 二甲DS.271E | 271E (非取樣點) | SC | D17/11/270/E1 |  |  |  |  | 714 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | 271 | 271 |  | 271 | 271 | [24 empty] | ADCS_S | [8 empty] | 二甲DS.271 | 271 (非取樣點) | SC | D17/11/270/D1 |  |  |  |  | 715 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | 281E | 281E |  | 281E | 281E | [24 empty] | ADCS_S | [8 empty] | 二甲DS.281E | 281E (非取樣點) | SC | D17/11/280/E1 |  |  |  |  | 716 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | 281 | 281 |  | 281 | 281 | [24 empty] | ADCS_S | [8 empty] | 二甲DS.281 | 281 (非取樣點) | SC | D17/11/280/D1 |  |  |  |  | 717 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | 15B1E | 15B1E |  | BE1 | 15B1E | [24 empty] | ADCS_S | [8 empty] | 二甲DS.15B1E | 15B1E (非取樣點) | BUS | D17/161/161B1E/BE1 |  |  |  |  | 718 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | 15B2E | 15B2E |  | BE2 | 15B2E | [24 empty] | ADCS_S | [8 empty] | 二甲DS.15B2E | 15B2E (非取樣點) | BUS | D17/161/161B2E/BE2 |  |  |  |  | 719 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | ADCS_S | [8 empty] | 二甲DS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 720 | NotelDIPoint | [38 empty] | START/STOP | STOP
D17 | 二甲DS | 0 |  | 251 | 251 |  | 251 | 251 | [24 empty] | ADCS_S | [8 empty] | 二甲DS.251 | 251 (非取樣點) | SC | D17/11/250/D1 |  |  |  |  | 721 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | 3A | #3A |  | BE | #3A_BE | [24 empty] | ADCS_S | [8 empty] | 二甲DS.#3A_BE | #3A BE(非取樣點) | OTHER | [5 empty] | 722 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | 3B | #3B |  | BE | #3B_BE | [24 empty] | ADCS_S | [8 empty] | 二甲DS.#3B_BE | #3B BE(非取樣點) | OTHER | [5 empty] | 723 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | 4A | #4A |  | BE | #4A_BE | [24 empty] | ADCS_S | [8 empty] | 二甲DS.#4A_BE | #4A BE(非取樣點) | OTHER | [5 empty] | 724 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | 4B | #4B |  | BE | #4B_BE | [24 empty] | ADCS_S | [8 empty] | 二甲DS.#4B_BE | #4B BE(非取樣點) | OTHER | [5 empty] | 725 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | 3ABUS | 3ABUS |  | PTD | 3ABUS_PTD | [24 empty] | ADCS_S | [8 empty] | 二甲DS.3ABUS_PTD | #3ABUS_PTD(非取樣點) | OTHER | [5 empty] | 726 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | 3ABUS | 3ABUS |  | PTE | 3ABUS_PTE | [24 empty] | ADCS_S | [8 empty] | 二甲DS.3ABUS_PTE | #3ABUS_PTE(非取樣點) | OTHER | [5 empty] | 727 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | 3BBUS | 3BBUS |  | PTD | 3BBUS_PTD | [24 empty] | ADCS_S | [8 empty] | 二甲DS.3BBUS_PTD | #3BBUS_PTD(非取樣點) | OTHER | [5 empty] | 728 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | 3BBUS | 3BBUS |  | PTE | 3BBUS_PTE | [24 empty] | ADCS_S | [8 empty] | 二甲DS.3BBUS_PTE | #3BBUS_PTE(非取樣點) | OTHER | [5 empty] | 729 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | 4ABUS | 4ABUS |  | PTD | 4ABUS_PTD | [24 empty] | ADCS_S | [8 empty] | 二甲DS.4ABUS_PTD | #4ABUS_PTD(非取樣點) | OTHER | [5 empty] | 730 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | 4ABUS | 4ABUS |  | PTE | 4ABUS_PTE | [24 empty] | ADCS_S | [8 empty] | 二甲DS.4ABUS_PTE | #4ABUS_PTE(非取樣點) | OTHER | [5 empty] | 731 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D17 | 二甲DS | 0 |  | 4BBUS | 4BBUS |  | PTD | 4BBUS_PTD | [24 empty] | ADCS_S | [8 empty] | 二甲DS.4BBUS_PTD | #4BBUS_PTD(非取樣點) | OTHER | [5 empty] | 732 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D17 | 二甲DS | 0 |  | 4BBUS | 4BBUS |  | PTE | 4BBUS_PTE | [24 empty] | ADCS_S | [8 empty] | 二甲DS.4BBUS_PTE | #4BBUS_PTE(非取樣點) | OTHER | [5 empty] | 733 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo