## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D18 | 忠孝DS | 161 | 161kV | 1510 | 台南～忠孝一路(1510) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_A1 | [8 empty] | 忠孝DS.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 2 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 161 | 161kV | 1510 | 台南～忠孝一路(1510) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_A1 | [8 empty] | 忠孝DS.1510BE | 1510BE (非取樣點) | LINE161 | [5 empty] | 3 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南～忠孝二路(1520) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_A1 | [8 empty] | 忠孝DS.1520LE | 1520LE (非取樣點) | LINE161 | [5 empty] | 4 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南～忠孝二路(1520) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_A1 | [8 empty] | 忠孝DS.1520BE | 1520BE (非取樣點) | LINE161 | [5 empty] | 5 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝～延平線(1530) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_A1 | [8 empty] | 忠孝DS.1530LE | 1530LE (非取樣點) | LINE161 | [5 empty] | 6 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝～延平線(1530) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_A1 | [8 empty] | 忠孝DS.1530BE | 1530BE (非取樣點) | LINE161 | [5 empty] | 7 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_A1 | [8 empty] | 忠孝DS.1501E | 1501E (非取樣點) | TIE | [5 empty] | 8 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_A1 | [8 empty] | 忠孝DS.1502E | 1502E (非取樣點) | TIE | [5 empty] | 9 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_A1 | [8 empty] | 忠孝DS.1750TE | 1750TE (非取樣點) | MTR | [5 empty] | 10 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_A1 | [8 empty] | 忠孝DS.1750BE | 1750BE (非取樣點) | MTR | [5 empty] | 11 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | D1 | 311(非取樣點) | B3 | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.311 | 311 (非取樣點) | MTR | [5 empty] | 12 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | E1 | 311E(非取樣點) | B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.311E | 311E (非取樣點) | MTR | [5 empty] | 13 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | D1 | 321(非取樣點) | B3 | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.321 | 321 (非取樣點) | MTR | [5 empty] | 14 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | E1 | 321E(非取樣點) | B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.321E | 321E (非取樣點) | MTR | [5 empty] | 15 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_A1 | [8 empty] | 忠孝DS.1760TE | 1760TE (非取樣點) | MTR | [5 empty] | 16 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_A1 | [8 empty] | 忠孝DS.1760BE | 1760BE (非取樣點) | MTR | [5 empty] | 17 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | D1 | 331(非取樣點) | B3 | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.331 | 331 (非取樣點) | MTR | [5 empty] | 18 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | E1 | 331E(非取樣點) | B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.331E | 331E (非取樣點) | MTR | [5 empty] | 19 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | D1 | 341(非取樣點) | B3 | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.341 | 341 (非取樣點) | MTR | [5 empty] | 20 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | E1 | 341E(非取樣點) | B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.341E | 341E (非取樣點) | MTR | [5 empty] | 21 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_A1 | [8 empty] | 忠孝DS.1770TE | 1770TE (非取樣點) | MTR | [5 empty] | 22 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_A1 | [8 empty] | 忠孝DS.1770BE | 1770BE (非取樣點) | MTR | [5 empty] | 23 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | D1 | 351(非取樣點) | B3 | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.351 | 351 (非取樣點) | MTR | [5 empty] | 24 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | E1 | 351E(非取樣點) | B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.351E | 351E (非取樣點) | MTR | [5 empty] | 25 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | D1 | 361(非取樣點) | B3 | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.361 | 361 (非取樣點) | MTR | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | E1 | 361E(非取樣點) | B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.361E | 361E (非取樣點) | MTR | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 161 | 161kV | 1950 | #1SHR(1950) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_A1 | [8 empty] | 忠孝DS.1950BE | 1950BE(非取樣點) | OTHER | [5 empty] | 28 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 161 | 161kV | 1950 | #1SHR(1950) |  | RE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_A1 | [8 empty] | 忠孝DS.1950RE | 1950RE(非取樣點) | OTHER | [5 empty] | 29 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | 210 | #1SC(210) |  | E1 | 211E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.211E | 211E (非取樣點) | SC | [5 empty] | 30 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | 210 | #1SC(210) |  | D1 | 211(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.211 | 211 (非取樣點) | SC | [5 empty] | 31 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 390 | #1SSTR(390) |  | D1 | 391(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.391 | 391 (非取樣點) | OTHER | [5 empty] | 32 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 390 | #1SSTR(390) |  | E1 | 391E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.391E | 391E (非取樣點) | OTHER | [5 empty] | 33 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | KE51 | 忠51線(KE51) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE51_DS | KE51_DS (非取樣點) | FEEDER | [5 empty] | 34 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE51 | 忠51線(KE51) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE51_ES | KE51_ES (非取樣點) | FEEDER | [5 empty] | 35 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | KE52 | 忠52線(KE52) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE52_DS | KE52_DS (非取樣點) | FEEDER | [5 empty] | 36 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE52 | 忠52線(KE52) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE52_ES | KE52_ES (非取樣點) | FEEDER | [5 empty] | 37 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | KE53 | 忠53線(KE53) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE53_DS | KE53_DS (非取樣點) | FEEDER | [5 empty] | 38 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE53 | 忠53線(KE53) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE53_ES | KE53_ES (非取樣點) | FEEDER | [5 empty] | 39 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | KE54 | 忠54線(KE54) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE54_DS | KE54_DS (非取樣點) | FEEDER | [5 empty] | 40 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE54 | 忠54線(KE54) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE54_ES | KE54_ES (非取樣點) | FEEDER | [5 empty] | 41 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | 100 | TIE(100) |  | E1 | 101E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.101E | 101E (非取樣點) | TIE | [5 empty] | 42 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | 100 | TIE(100) |  | E2 | 102E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.102E | 102E (非取樣點) | TIE | [5 empty] | 43 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | 100 | TIE(100) |  | D1 | 101(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.101 | 101 (非取樣點) | TIE | [5 empty] | 44 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 100 | TIE(100) |  | D2 | 102(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.102 | 102 (非取樣點) | TIE | [5 empty] | 45 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 220 | #2SC(220) |  | E1 | 221E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.221E | 221E (非取樣點) | SC | [5 empty] | 46 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | 220 | #2SC(220) |  | D1 | 221(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.221 | 221 (非取樣點) | SC | [5 empty] | 47 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE55 | 忠55線(KE55) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE55_DS | KE55_DS (非取樣點) | FEEDER | [5 empty] | 48 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE55 | 忠55線(KE55) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE55_ES | KE55_ES (非取樣點) | FEEDER | [5 empty] | 49 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | KE56 | 忠56線(KE56) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE56_DS | KE56_DS (非取樣點) | FEEDER | [5 empty] | 50 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE56 | 忠56線(KE56) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE56_ES | KE56_ES (非取樣點) | FEEDER | [5 empty] | 51 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | KE57 | 忠57線(KE57) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE57_DS | KE57_DS (非取樣點) | FEEDER | [5 empty] | 52 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE57 | 忠57線(KE57) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE57_ES | KE57_ES (非取樣點) | FEEDER | [5 empty] | 53 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | KE58 | 忠58線(KE58) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE58_DS | KE58_DS (非取樣點) | FEEDER | [5 empty] | 54 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE58 | 忠58線(KE58) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE58_ES | KE58_ES (非取樣點) | FEEDER | [5 empty] | 55 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | 230 | #3SC(230) |  | E1 | 231E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.231E | 231E (非取樣點) | SC | [5 empty] | 56 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | 230 | #3SC(230) |  | D1 | 231(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.231 | 231 (非取樣點) | SC | [5 empty] | 57 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE61 | 忠61線(KE61) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE61_DS | KE61_DS (非取樣點) | FEEDER | [5 empty] | 58 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE61 | 忠61線(KE61) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE61_ES | KE61_ES (非取樣點) | FEEDER | [5 empty] | 59 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | KE62 | 忠62線(KE62) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE62_DS | KE62_DS (非取樣點) | FEEDER | [5 empty] | 60 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE62 | 忠62線(KE62) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE62_ES | KE62_ES (非取樣點) | FEEDER | [5 empty] | 61 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | KE63 | 忠63線(KE63) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE63_DS | KE63_DS (非取樣點) | FEEDER | [5 empty] | 62 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE63 | 忠63線(KE63) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE63_ES | KE63_ES (非取樣點) | FEEDER | [5 empty] | 63 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | KE64 | 忠64線(KE64) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE64_DS | KE64_DS (非取樣點) | FEEDER | [5 empty] | 64 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE64 | 忠64線(KE64) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE64_ES | KE64_ES (非取樣點) | FEEDER | [5 empty] | 65 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | 200 | TIE(200) |  | E1 | 201E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.201E | 201E (非取樣點) | TIE | [5 empty] | 66 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | 200 | TIE(200) |  | E2 | 202E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.202E | 202E (非取樣點) | TIE | [5 empty] | 67 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | 200 | TIE(200) |  | D1 | 201(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.201 | 201 (非取樣點) | TIE | [5 empty] | 68 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 200 | TIE(200) |  | D2 | 202(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.202 | 202 (非取樣點) | TIE | [5 empty] | 69 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 490 | #2SSTR(490) |  | D1 | 491(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.491 | 491 (非取樣點) | OTHER | [5 empty] | 70 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 490 | #2SSTR(490) |  | E1 | 491E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.491E | 491E (非取樣點) | OTHER | [5 empty] | 71 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | 240 | #4SC(240) |  | E1 | 241E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.241E | 241E (非取樣點) | SC | [5 empty] | 72 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | 240 | #4SC(240) |  | D1 | 241(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.241 | 241 (非取樣點) | SC | [5 empty] | 73 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE65 | 忠65線(KE65) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE65_DS | KE65_DS (非取樣點) | FEEDER | [5 empty] | 74 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE65 | 忠65線(KE65) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE65_ES | KE65_ES (非取樣點) | FEEDER | [5 empty] | 75 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | KE66 | 忠66線(KE66) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE66_DS | KE66_DS (非取樣點) | FEEDER | [5 empty] | 76 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE66 | 忠66線(KE66) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE66_ES | KE66_ES (非取樣點) | FEEDER | [5 empty] | 77 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | KE67 | 忠67線(KE67) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE67_DS | KE67_DS (非取樣點) | FEEDER | [5 empty] | 78 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE67 | 忠67線(KE67) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE67_ES | KE67_ES (非取樣點) | FEEDER | [5 empty] | 79 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | KE68 | 忠68線(KE68) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE68_DS | KE68_DS (非取樣點) | FEEDER | [5 empty] | 80 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE68 | 忠68線(KE68) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE68_ES | KE68_ES (非取樣點) | FEEDER | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | 250 | #5SC(250) |  | E1 | 251E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.251E | 251E (非取樣點) | SC | [5 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | 250 | #5SC(250) |  | D1 | 251(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.251 | 251 (非取樣點) | SC | [5 empty] | 83 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE71 | 忠71線(KE71) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE71_DS | KE71_DS (非取樣點) | FEEDER | [5 empty] | 84 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE71 | 忠71線(KE71) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE71_ES | KE71_ES (非取樣點) | FEEDER | [5 empty] | 85 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | KE72 | 忠72線(KE72) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE72_DS | KE72_DS (非取樣點) | FEEDER | [5 empty] | 86 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE72 | 忠72線(KE72) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE72_ES | KE72_ES (非取樣點) | FEEDER | [5 empty] | 87 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | KE73 | 忠73線(KE73) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE73_DS | KE73_DS (非取樣點) | FEEDER | [5 empty] | 88 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE73 | 忠73線(KE73) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE73_ES | KE73_ES (非取樣點) | FEEDER | [5 empty] | 89 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | KE74 | 忠74線(KE74) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE74_DS | KE74_DS (非取樣點) | FEEDER | [5 empty] | 90 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE74 | 忠74線(KE74) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE74_ES | KE74_ES (非取樣點) | FEEDER | [5 empty] | 91 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | 300 | TIE(300) |  | E1 | 301E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.301E | 301E (非取樣點) | TIE | [5 empty] | 92 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | 300 | TIE(300) |  | E2 | 302E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.302E | 302E (非取樣點) | TIE | [5 empty] | 93 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | 300 | TIE(300) |  | D1 | 301(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.301 | 301 (非取樣點) | TIE | [5 empty] | 94 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 300 | TIE(300) |  | D2 | 302(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.302 | 302 (非取樣點) | TIE | [5 empty] | 95 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 260 | #6SC(260) |  | BE0 | 261E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.261E | 261E (非取樣點) | SC | [5 empty] | 96 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | 260 | #6SC(260) |  | D1 | 261(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D18_A1 | [8 empty] | 忠孝DS.261 | 261 (非取樣點) | SC | [5 empty] | 97 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE75 | 忠75線(KE75) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE75_DS | KE75_DS (非取樣點) | FEEDER | [5 empty] | 98 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE75 | 忠75線(KE75) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE75_ES | KE75_ES (非取樣點) | FEEDER | [5 empty] | 99 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | KE76 | 忠76線(KE76) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE76_DS | KE76_DS (非取樣點) | FEEDER | [5 empty] | 100 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE76 | 忠76線(KE76) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE76_ES | KE76_ES (非取樣點) | FEEDER | [5 empty] | 101 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | KE77 | 忠77線(KE77) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE77_DS | KE77_DS (非取樣點) | FEEDER | [5 empty] | 102 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE77 | 忠77線(KE77) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE77_ES | KE77_ES (非取樣點) | FEEDER | [5 empty] | 103 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | KE78 | 忠78線(KE78) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE78_DS | KE78_DS (非取樣點) | FEEDER | [5 empty] | 104 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE78 | 忠78線(KE78) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D18_D1 | [8 empty] | 忠孝DS.KE78_ES | KE78_ES (非取樣點) | FEEDER | [5 empty] | 105 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | 15B1E(非取樣點) | B2,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aaaz | B2/D18_A1 | [8 empty] | 忠孝DS.15B1E | 15B1E (非取樣點) | BUS | [5 empty] | 106 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | 15B2E(非取樣點) | B2,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/2Bus | [13 empty] | aaaz | B2/D18_A1 | [8 empty] | 忠孝DS.15B2E | 15B2E (非取樣點) | BUS | [5 empty] | 107 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | RTU | RTU |  | ADCL1 |  |  | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% TEST |  |  |  |  | B3/D18_A1 | [16 empty] | 108 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D18 | 忠孝DS | 0 |  | RTU | RTU |  | ADCH1 |  |  | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% TEST |  |  |  |  | B3/D18_A1 | [16 empty] | 109 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D18 | 忠孝DS | 161 | 161kV | 1BUS | #1BUS |  | V |  | B3 | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 161kV #1 BUS 電壓 |  |  | kV_-210_210(-2000_2000) | aaa | B2/D18_A1 | [8 empty] | 忠孝DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | [5 empty] | 110 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D18 | 忠孝DS | 161 | 161kV | 2BUS | #2BUS |  | V |  | B3 | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0003 |  |  | 1-83 |  |  | 161kV #2 BUS 電壓 |  |  | kV_-210_210(-2000_2000) | aab | B2/D18_A1 | [8 empty] | 忠孝DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | [5 empty] | 111 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D18 | 忠孝DS | 161 | 161kV | 1510 | 台南～忠孝一路(1510) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 台南忠孝一路1510 瓦 |  |  | MW_-560_560(-2000_2000) |  | B2/D18_A1 | [8 empty] | 忠孝DS.1510_MW | 台南忠孝一路 MW | LINE161 | [5 empty] | 112 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D18 | 忠孝DS | 161 | 161kV | 1510 | 台南～忠孝一路(1510) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 台南忠孝一路1510 乏 |  |  | MVAR_-560_560(-2000_2000) |  | B2/D18_A1 | [8 empty] | 忠孝DS.1510_MVAR | 台南忠孝一路 MVAR | LINE161 | [5 empty] | 113 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南～忠孝二路(1520) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 台南忠孝二路1520 瓦 |  |  | MW_-560_560(-2000_2000) |  | B2/D18_A1 | [8 empty] | 忠孝DS.1520_MW | 台南忠孝二路 MW | LINE161 | [5 empty] | 114 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南～忠孝二路(1520) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 台南忠孝二路1520 乏 |  |  | MVAR_-560_560(-2000_2000) |  | B2/D18_A1 | [8 empty] | 忠孝DS.1520_MVAR | 台南忠孝二路 MVAR | LINE161 | [5 empty] | 115 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝～延平線(1530) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | 忠孝延平線 1530 瓦 |  |  | MW_-560_560(-2000_2000) |  | B2/D18_A1 | [8 empty] | 忠孝DS.1530_MW | 忠孝延平線 MW | LINE161 | [5 empty] | 116 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝～延平線(1530) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 忠孝延平線 1530 乏 |  |  | MVAR_-560_560(-2000_2000) |  | B2/D18_A1 | [8 empty] | 忠孝DS.1530_MVAR | 忠孝延平線 MVAR | LINE161 | [5 empty] | 117 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D18 | 忠孝DS | 161 | 161kV | 1500 | TIE(1500) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0024 |  |  | 1-98 |  |  | TIE (1500) R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/D18_A1 | [8 empty] | 忠孝DS.1500TIE_AMP | 1500TIE AMP | TIE | [5 empty] | 118 |  |  |  |  | AI | [5 empty] | C20R1600 | 1520 | 1600 | 1760 | 1968 | 2.27 | -1520 | -1600 | -1760 | -1968 | 1 | 0.01 | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南～忠孝二路(1520) |  | OilPreR |  |  | MvMoment | R相油壓 |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | 1520 台南忠孝二路 R相充油電纜油壓 |  |  | OilPre_-9.3_9.3(-2000_2000) |  | B2/D18_A1 | [8 empty] | 忠孝DS.1520_OF_R | 台南忠孝二路 R相 油壓 | OTHER | [5 empty] | 119 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 1 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南～忠孝二路(1520) |  | OilPreS |  |  | MvMoment | S相油壓 |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | 1520 台南忠孝二路 S相充油電纜油壓 |  |  | OilPre_-9.3_9.3(-2000_2000) |  | B2/D18_A1 | [8 empty] | 忠孝DS.1520_OF_S | 台南忠孝二路 S相 油壓 | OTHER | [5 empty] | 120 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 1 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南～忠孝二路(1520) |  | OilPreT |  |  | MvMoment | T相油壓 |  | Y |  | AI | [6 empty] | 0027 |  |  | 1-9B |  |  | 1520 台南忠孝二路 T相充油電纜油壓 |  |  | OilPre_-9.3_9.3(-2000_2000) |  | B2/D18_A1 | [8 empty] | 忠孝DS.1520_OF_T | 台南忠孝二路 T相 油壓 | OTHER | [5 empty] | 121 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 1 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝～延平線(1530) |  | OilPreR |  |  | MvMoment | R相油壓 |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | 1530 忠孝延平線 R相充油電纜油壓 |  |  | OilPre_-9.3_9.3(-2000_2000) |  | B2/D18_A1 | [8 empty] | 忠孝DS.1530_OF_R | 忠孝延平線 R相 油壓 | OTHER | [5 empty] | 122 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 1 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝～延平線(1530) |  | OilPreS |  |  | MvMoment | S相油壓 |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | 1530 忠孝延平線 S相充油電纜油壓 |  |  | OilPre_-9.3_9.3(-2000_2000) |  | B2/D18_A1 | [8 empty] | 忠孝DS.1530_OF_S | 忠孝延平線 S相 油壓 | OTHER | [5 empty] | 123 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 1 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝～延平線(1530) |  | OilPreT |  |  | MvMoment | T相油壓 |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | 1530 忠孝延平線 T相充油電纜油壓 |  |  | OilPre_-9.3_9.3(-2000_2000) |  | B2/D18_A1 | [8 empty] | 忠孝DS.1530_OF_T | 忠孝延平線 T相 油壓 | OTHER | [5 empty] | 124 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 1 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D18 | 忠孝DS |  |  | 1DTR | #1DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | #1DTR 油溫 |  |  | OIL_-120_120(-2000_2000) |  | B1/D18_A1 | [8 empty] | 忠孝DS.#1DTR_OIL | #1DTR 油溫 | MTR | [5 empty] | 125 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D18 | 忠孝DS |  |  | 1DTR | #1DTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | #1DTR 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/D18_A1 | [8 empty] | 忠孝DS.#1DTR_COIL | #1DTR 線溫 | MTR | [5 empty] | 126 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D18 | 忠孝DS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0512 |  | 0000 | 1-30-00 |  | 1-00 | TEST CB ON/OFF |  |  |  |  | ELEM/ALL | [8 empty] | 忠孝DS.TEST_CB | TEST CB | OTHER | [5 empty] | 127 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS |  |  | 2DTR | #2DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | #2DTR 油溫 |  |  | OIL_-120_120(-2000_2000) |  | B1/D18_A1 | [8 empty] | 忠孝DS.#2DTR_OIL | #2DTR 油溫 | MTR | [5 empty] | 128 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D18 | 忠孝DS |  |  | 2DTR | #2DTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | #2DTR 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/D18_A1 | [8 empty] | 忠孝DS.#2DTR_COIL | #2DTR 線溫 | MTR | [5 empty] | 129 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D18 | 忠孝DS | 161 | 161kV | 1510 | 台南～忠孝一路(1510) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P07D181/T2 |  | 0000 |  | 0001 | 1-00-00 |  | 1-01 | 台南忠孝一路1510 CB |  | PPU-1 |  | aada | B2/D18_A1 | [8 empty] | 忠孝DS.1510_CB | 1510(台南忠孝一路) CB | LINE161 | [5 empty] | 130 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS |  |  | 3DTR | #3DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | #3DTR 油溫 |  |  | OIL_-120_120(-2000_2000) |  | B1/D18_A1 | [8 empty] | 忠孝DS.#3DTR_OIL | #3DTR 油溫 | MTR | [5 empty] | 131 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D18 | 忠孝DS |  |  | 3DTR | #3DTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | #3DTR 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/D18_A1 | [8 empty] | 忠孝DS.#3DTR_COIL | #3DTR 線溫 | MTR | [5 empty] | 132 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南～忠孝二路(1520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P07D182/T2 |  | 0004 |  | 0002 | 1-00-04 |  | 1-02 | 台南忠孝二路1520 CB |  | PPU-1 |  | aafa | B2/D18_A1 | [8 empty] | 忠孝DS.1520_CB | 1520(台南忠孝二路) CB | LINE161 | [5 empty] | 133 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 161 | 161kV | 1950 | #1SHR(1950) |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | #1SHR 油溫 |  |  | OIL_-120_120(-2000_2000) | [10 empty] | 忠孝DS.161#1SHR_OIL | 161KV #1SHR 油溫 | OTHER | [5 empty] | 134 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D18 | 忠孝DS | 161 | 161kV | 1950 | #1SHR(1950) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | #1SHR 線溫 |  |  | COIL_-120_120(-2000_2000) | [10 empty] | 忠孝DS.161#1SHR_COIL | 161KV #1SHR 線溫 | OTHER | [5 empty] | 135 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D18 | 忠孝DS | 0 |  | StaDev | 所內設施 |  | DCV_P |  |  | MvMoment | 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | DCP 電壓 |  |  | kV_-150_150(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.直流P電源電壓 | 直流P電源電壓 | OTHER | [5 empty] | 136 |  |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 | 0.01 | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D18 | 忠孝DS | 0 |  | StaDev | 所內設施 |  | DCV_N |  |  | MvMoment | 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | DCN 電壓 |  |  | kV_-150_150(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.直流N電源電壓 | 直流N電源電壓 | OTHER | [5 empty] | 137 |  |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 | 0.01 | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D18 | 忠孝DS | 0 |  | RTU | RTU |  | ADCL2 |  |  | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% TEST |  |  |  |  | B3/D18_A1 | [16 empty] | 138 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D18 | 忠孝DS | 0 |  | RTU | RTU |  | ADCH2 |  |  | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% TEST |  |  |  |  | B3/D18_A1 | [16 empty] | 139 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D18 | 忠孝DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | KW |  | B3 | MvMoment | KW |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 310(M1A) 瓦 |  |  | MW_-108_108(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | [5 empty] | 140 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 310(M1A 乏 |  |  | MVAR_-72_72(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | [5 empty] | 141 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | 310(M1A) R 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | [5 empty] | 142 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | 310(M1A) S 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | [5 empty] | 143 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | 310(M1A) T 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | [5 empty] | 144 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 1ABUS | #1ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0133 |  |  | 2-85 |  |  | 22KV #1A BUS #1A PT R相電壓 |  |  | kV_-18_18(-2000_2000) | aaa | B3/D18_A1 | [8 empty] | 忠孝DS.23KV#1ABUS_KV | 23KV #1ABUS KV | BUS | [5 empty] | 145 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D18 | 忠孝DS | 22 | 22kV | KE51 | 忠51線(KE51) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | 忠51線(KE51) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠51線KVAR | 23KV忠51線 KVAR | FEEDER | [5 empty] | 146 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE51 | 忠51線(KE51) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0135 |  |  | 2-87 |  |  | 忠51線(KE51) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠51線A1 | 23KV忠51線 R相AMP | FEEDER | [5 empty] | 147 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE51 | 忠51線(KE51) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0136 |  |  | 2-88 |  |  | 忠51線(KE51) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠51線A2 | 23KV忠51線 S相AMP | FEEDER | [5 empty] | 148 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE51 | 忠51線(KE51) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0137 |  |  | 2-89 |  |  | 忠51線(KE51) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠51線A3 | 23KV忠51線 T相AMP | FEEDER | [5 empty] | 149 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE51 | 忠51線(KE51) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0138 |  |  | 2-8A |  |  | 忠51線(KE51) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠51線A0 | 23KV忠51線 N相AMP | FEEDER | [5 empty] | 150 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE52 | 忠52線(KE52) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0139 |  |  | 2-8B |  |  | 忠52線(KE52) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠52線KVAR | 23KV忠52線 KVAR | FEEDER | [5 empty] | 151 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE52 | 忠52線(KE52) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0140 |  |  | 2-8C |  |  | 忠52線(KE52) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠52線A1 | 23KV忠52線 R相AMP | FEEDER | [5 empty] | 152 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE52 | 忠52線(KE52) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0141 |  |  | 2-8D |  |  | 忠52線(KE52) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠52線A2 | 23KV忠52線 S相AMP | FEEDER | [5 empty] | 153 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE52 | 忠52線(KE52) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0142 |  |  | 2-8E |  |  | 忠52線(KE52) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠52線A3 | 23KV忠52線 T相AMP | FEEDER | [5 empty] | 154 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE52 | 忠52線(KE52) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0143 |  |  | 2-8F |  |  | 忠52線(KE52) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠52線A0 | 23KV忠52線 N相AMP | FEEDER | [5 empty] | 155 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE53 | 忠53線(KE53) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0144 |  |  | 2-90 |  |  | 忠53線(KE53) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠53線KVAR | 23KV忠53線 KVAR | FEEDER | [5 empty] | 156 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE53 | 忠53線(KE53) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0145 |  |  | 2-91 |  |  | 忠53線(KE53) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠53線A1 | 23KV忠53線 R相AMP | FEEDER | [5 empty] | 157 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE53 | 忠53線(KE53) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0146 |  |  | 2-92 |  |  | 忠53線(KE53) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠53線A2 | 23KV忠53線 S相AMP | FEEDER | [5 empty] | 158 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE53 | 忠53線(KE53) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0147 |  |  | 2-93 |  |  | 忠53線(KE53) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠53線A3 | 23KV忠53線 T相AMP | FEEDER | [5 empty] | 159 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE53 | 忠53線(KE53) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0148 |  |  | 2-94 |  |  | 忠53線(KE53) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠53線A0 | 23KV忠53線 N相AMP | FEEDER | [5 empty] | 160 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE54 | 忠54線(KE54) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0149 |  |  | 2-95 |  |  | 忠54線(KE54) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠54線KVAR | 23KV忠54線 KVAR | FEEDER | [5 empty] | 161 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE54 | 忠54線(KE54) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0150 |  |  | 2-96 |  |  | 忠54線(KE54) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠54線A1 | 23KV忠54線 R相AMP | FEEDER | [5 empty] | 162 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE54 | 忠54線(KE54) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0151 |  |  | 2-97 |  |  | 忠54線(KE54) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠54線A2 | 23KV忠54線 S相AMP | FEEDER | [5 empty] | 163 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE54 | 忠54線(KE54) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0152 |  |  | 2-98 |  |  | 忠54線(KE54) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠54線A3 | 23KV忠54線 T相AMP | FEEDER | [5 empty] | 164 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE54 | 忠54線(KE54) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0153 |  |  | 2-99 |  |  | 忠54線(KE54) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠54線A0 | 23KV忠54線 N相AMP | FEEDER | [5 empty] | 165 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | KW |  | B3 | MvMoment | KW |  | Y |  | AI | [6 empty] | 0154 |  |  | 2-9A |  |  | 320(M1B) 瓦 |  |  | MW_-108_108(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | [5 empty] | 166 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0155 |  |  | 2-9B |  |  | 320(M1B) 乏 |  |  | MVAR_-72_72(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | [5 empty] | 167 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0156 |  |  | 2-9C |  |  | 320(M1B) R 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | [5 empty] | 168 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0157 |  |  | 2-9D |  |  | 320(M1B) S 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | [5 empty] | 169 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0158 |  |  | 2-9E |  |  | 320(M1B) T 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | [5 empty] | 170 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 1BBUS | #1BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0159 |  |  | 2-9F |  |  | 22KV #1B BUS #1B PT R相電壓 |  |  | kV_-18_18(-2000_2000) | baa | B3/D18_A1 | [8 empty] | 忠孝DS.23KV#1BBUS_KV | 23KV #1BBUS KV | BUS | [5 empty] | 171 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D18 | 忠孝DS | 22 | 22kV | KE55 | 忠55線(KE55) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0160 |  |  | 2-A0 |  |  | 忠55線(KE55) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠55線KVAR | 23KV忠55線 KVAR | FEEDER | [5 empty] | 172 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE55 | 忠55線(KE55) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0161 |  |  | 2-A1 |  |  | 忠55線(KE55) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠55線A1 | 23KV忠55線 R相AMP | FEEDER | [5 empty] | 173 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE55 | 忠55線(KE55) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0162 |  |  | 2-A2 |  |  | 忠55線(KE55) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠55線A2 | 23KV忠55線 S相AMP | FEEDER | [5 empty] | 174 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE55 | 忠55線(KE55) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0163 |  |  | 2-A3 |  |  | 忠55線(KE55) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠55線A3 | 23KV忠55線 T相AMP | FEEDER | [5 empty] | 175 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE55 | 忠55線(KE55) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0164 |  |  | 2-A4 |  |  | 忠55線(KE55) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠55線A0 | 23KV忠55線 N相AMP | FEEDER | [5 empty] | 176 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE56 | 忠56線(KE56) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0165 |  |  | 2-A5 |  |  | 忠56線(KE56) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠56線KVAR | 23KV忠56線 KVAR | FEEDER | [5 empty] | 177 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE56 | 忠56線(KE56) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0166 |  |  | 2-A6 |  |  | 忠56線(KE56) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠56線A1 | 23KV忠56線 R相AMP | FEEDER | [5 empty] | 178 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE56 | 忠56線(KE56) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0167 |  |  | 2-A7 |  |  | 忠56線(KE56) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠56線A2 | 23KV忠56線 S相AMP | FEEDER | [5 empty] | 179 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE56 | 忠56線(KE56) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0168 |  |  | 2-A8 |  |  | 忠56線(KE56) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠56線A3 | 23KV忠56線 T相AMP | FEEDER | [5 empty] | 180 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE56 | 忠56線(KE56) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0169 |  |  | 2-A9 |  |  | 忠56線(KE56) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠56線A0 | 23KV忠56線 N相AMP | FEEDER | [5 empty] | 181 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE57 | 忠57線(KE57) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0170 |  |  | 2-AA |  |  | 忠57線(KE57) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠57線KVAR | 23KV忠57線 KVAR | FEEDER | [5 empty] | 182 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE57 | 忠57線(KE57) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0171 |  |  | 2-AB |  |  | 忠57線(KE57) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠57線A1 | 23KV忠57線 R相AMP | FEEDER | [5 empty] | 183 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE57 | 忠57線(KE57) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0172 |  |  | 2-AC |  |  | 忠57線(KE57) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠57線A2 | 23KV忠57線 S相AMP | FEEDER | [5 empty] | 184 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE57 | 忠57線(KE57) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0173 |  |  | 2-AD |  |  | 忠57線(KE57) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠57線A3 | 23KV忠57線 T相AMP | FEEDER | [5 empty] | 185 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE57 | 忠57線(KE57) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0174 |  |  | 2-AE |  |  | 忠57線(KE57) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠57線A0 | 23KV忠57線 N相AMP | FEEDER | [5 empty] | 186 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE58 | 忠58線(KE58) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0175 |  |  | 2-AF |  |  | 忠58線(KE58) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠58線KVAR | 23KV忠58線 KVAR | FEEDER | [5 empty] | 187 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE58 | 忠58線(KE58) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0176 |  |  | 2-B0 |  |  | 忠58線(KE58) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠58線A1 | 23KV忠58線 R相AMP | FEEDER | [5 empty] | 188 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE58 | 忠58線(KE58) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0177 |  |  | 2-B1 |  |  | 忠58線(KE58) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠58線A2 | 23KV忠58線 S相AMP | FEEDER | [5 empty] | 189 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE58 | 忠58線(KE58) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0178 |  |  | 2-B2 |  |  | 忠58線(KE58) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠58線A3 | 23KV忠58線 T相AMP | FEEDER | [5 empty] | 190 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE58 | 忠58線(KE58) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0179 |  |  | 2-B3 |  |  | 忠58線(KE58) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠58線A0 | 23KV忠58線 N相AMP | FEEDER | [5 empty] | 191 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 100 | TIE(100) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0180 |  |  | 2-B4 |  |  | 100(TIE-1) R 相電流 |  |  | A_-2000_2000(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.23KV_100_A1 | 23KV 100 R相AMP | TIE | [5 empty] | 192 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 100 | TIE(100) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0181 |  |  | 2-B5 |  |  | 100(TIE-1) S 相電流 |  |  | A_-2000_2000(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.23KV_100_A2 | 23KV 100 S相AMP | TIE | [5 empty] | 193 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 100 | TIE(100) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0182 |  |  | 2-B6 |  |  | 100(TIE-1) T 相電流 |  |  | A_-2000_2000(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.23KV_100_A3 | 23KV 100 T相AMP | TIE | [5 empty] | 194 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | KW |  | B3 | MvMoment | KW |  | Y |  | AI | [6 empty] | 0183 |  |  | 2-B7 |  |  | 330(M2A) 瓦 |  |  | MW_-108_108(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | [5 empty] | 195 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0184 |  |  | 2-B8 |  |  | 330(M2A) 乏 |  |  | MVAR_-72_72(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | [5 empty] | 196 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0185 |  |  | 2-B9 |  |  | 330(M2A) R 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | [5 empty] | 197 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0186 |  |  | 2-BA |  |  | 330(M2A) S 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | [5 empty] | 198 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0187 |  |  | 2-BB |  |  | 330(M2A) T 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | [5 empty] | 199 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 2ABUS | #2ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0188 |  |  | 2-BC |  |  | 22KV #2A BUS #2A PT R相電壓 |  |  | kV_-18_18(-2000_2000) | aba | B3/D18_A1 | [8 empty] | 忠孝DS.23KV#2ABUS_KV | 23KV #2ABUS KV | BUS | [5 empty] | 200 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D18 | 忠孝DS | 22 | 22kV | KE61 | 忠61線(KE61) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0189 |  |  | 2-BD |  |  | 忠61線(KE61) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠61線KVAR | 23KV忠61線 KVAR | FEEDER | [5 empty] | 201 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE61 | 忠61線(KE61) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0190 |  |  | 2-BE |  |  | 忠61線(KE61) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠61線A1 | 23KV忠61線 R相AMP | FEEDER | [5 empty] | 202 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE61 | 忠61線(KE61) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0191 |  |  | 2-BF |  |  | 忠61線(KE61) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠61線A2 | 23KV忠61線 S相AMP | FEEDER | [5 empty] | 203 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE61 | 忠61線(KE61) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0192 |  |  | 2-C0 |  |  | 忠61線(KE61) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠61線A3 | 23KV忠61線 T相AMP | FEEDER | [5 empty] | 204 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE61 | 忠61線(KE61) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0193 |  |  | 2-C1 |  |  | 忠61線(KE61) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠61線A0 | 23KV忠61線 N相AMP | FEEDER | [5 empty] | 205 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE62 | 忠62線(KE62) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0194 |  |  | 2-C2 |  |  | 忠62線(KE62) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠62線KVAR | 23KV忠62線 KVAR | FEEDER | [5 empty] | 206 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE62 | 忠62線(KE62) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0195 |  |  | 2-C3 |  |  | 忠62線(KE62) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠62線A1 | 23KV忠62線 R相AMP | FEEDER | [5 empty] | 207 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE62 | 忠62線(KE62) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0196 |  |  | 2-C4 |  |  | 忠62線(KE62) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠62線A2 | 23KV忠62線 S相AMP | FEEDER | [5 empty] | 208 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE62 | 忠62線(KE62) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0197 |  |  | 2-C5 |  |  | 忠62線(KE62) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠62線A3 | 23KV忠62線 T相AMP | FEEDER | [5 empty] | 209 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE62 | 忠62線(KE62) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0198 |  |  | 2-C6 |  |  | 忠62線(KE62) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠62線A0 | 23KV忠62線 N相AMP | FEEDER | [5 empty] | 210 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE63 | 忠63線(KE63) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0199 |  |  | 2-C7 |  |  | 忠63線(KE63) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠63線KVAR | 23KV忠63線 KVAR | FEEDER | [5 empty] | 211 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE63 | 忠63線(KE63) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0200 |  |  | 2-C8 |  |  | 忠63線(KE63) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠63線A1 | 23KV忠63線 R相AMP | FEEDER | [5 empty] | 212 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE63 | 忠63線(KE63) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0201 |  |  | 2-C9 |  |  | 忠63線(KE63) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠63線A2 | 23KV忠63線 S相AMP | FEEDER | [5 empty] | 213 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE63 | 忠63線(KE63) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0202 |  |  | 2-CA |  |  | 忠63線(KE63) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠63線A3 | 23KV忠63線 T相AMP | FEEDER | [5 empty] | 214 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE63 | 忠63線(KE63) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0203 |  |  | 2-CB |  |  | 忠63線(KE63) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠63線A0 | 23KV忠63線 N相AMP | FEEDER | [5 empty] | 215 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE64 | 忠64線(KE64) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0204 |  |  | 2-CC |  |  | 忠64線(KE64) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠64線KVAR | 23KV忠64線 KVAR | FEEDER | [5 empty] | 216 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE64 | 忠64線(KE64) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0205 |  |  | 2-CD |  |  | 忠64線(KE64) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠64線A1 | 23KV忠64線 R相AMP | FEEDER | [5 empty] | 217 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE64 | 忠64線(KE64) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0206 |  |  | 2-CE |  |  | 忠64線(KE64) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠64線A2 | 23KV忠64線 S相AMP | FEEDER | [5 empty] | 218 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE64 | 忠64線(KE64) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0207 |  |  | 2-CF |  |  | 忠64線(KE64) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠64線A3 | 23KV忠64線 T相AMP | FEEDER | [5 empty] | 219 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE64 | 忠64線(KE64) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0208 |  |  | 2-D0 |  |  | 忠64線(KE64) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠64線A0 | 23KV忠64線 N相AMP | FEEDER | [5 empty] | 220 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | KW |  | B3 | MvMoment | KW |  | Y |  | AI | [6 empty] | 0209 |  |  | 2-D1 |  |  | 340(M2B) 瓦 |  |  | MW_-108_108(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | [5 empty] | 221 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0210 |  |  | 2-D2 |  |  | 340(M2B) 乏 |  |  | MVAR_-72_72(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | [5 empty] | 222 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0211 |  |  | 2-D3 |  |  | 340(M2B) R 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | [5 empty] | 223 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0212 |  |  | 2-D4 |  |  | 340(M2B) S 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | [5 empty] | 224 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0213 |  |  | 2-D5 |  |  | 340(M2B) T 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | [5 empty] | 225 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 2BBUS | #2BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0214 |  |  | 2-D6 |  |  | 22KV #2B BUS #2B PT R相電壓 |  |  | kV_-18_18(-2000_2000) | bba | B3/D18_A1 | [8 empty] | 忠孝DS.23KV#2BBUS_KV | 23KV #2BBUS KV | BUS | [5 empty] | 226 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D18 | 忠孝DS | 22 | 22kV | KE65 | 忠65線(KE65) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0215 |  |  | 2-D7 |  |  | 忠65線(KE65) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠65線KVAR | 23KV忠65線 KVAR | FEEDER | [5 empty] | 227 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE65 | 忠65線(KE65) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0216 |  |  | 2-D8 |  |  | 忠65線(KE65) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠65線A1 | 23KV忠65線 R相AMP | FEEDER | [5 empty] | 228 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE65 | 忠65線(KE65) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0217 |  |  | 2-D9 |  |  | 忠65線(KE65) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠65線A2 | 23KV忠65線 S相AMP | FEEDER | [5 empty] | 229 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE65 | 忠65線(KE65) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0218 |  |  | 2-DA |  |  | 忠65線(KE65) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠65線A3 | 23KV忠65線 T相AMP | FEEDER | [5 empty] | 230 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE65 | 忠65線(KE65) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0219 |  |  | 2-DB |  |  | 忠65線(KE65) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠65線A0 | 23KV忠65線 N相AMP | FEEDER | [5 empty] | 231 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE66 | 忠66線(KE66) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0220 |  |  | 2-DC |  |  | 忠66線(KE66) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠66線KVAR | 23KV忠66線 KVAR | FEEDER | [5 empty] | 232 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE66 | 忠66線(KE66) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0221 |  |  | 2-DD |  |  | 忠66線(KE66) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠66線A1 | 23KV忠66線 R相AMP | FEEDER | [5 empty] | 233 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE66 | 忠66線(KE66) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0222 |  |  | 2-DE |  |  | 忠66線(KE66) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠66線A2 | 23KV忠66線 S相AMP | FEEDER | [5 empty] | 234 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE66 | 忠66線(KE66) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0223 |  |  | 2-DF |  |  | 忠66線(KE66) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠66線A3 | 23KV忠66線 T相AMP | FEEDER | [5 empty] | 235 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE66 | 忠66線(KE66) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0224 |  |  | 2-E0 |  |  | 忠66線(KE66) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠66線A0 | 23KV忠66線 N相AMP | FEEDER | [5 empty] | 236 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE67 | 忠67線(KE67) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0225 |  |  | 2-E1 |  |  | 忠67線(KE67) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠67線KVAR | 23KV忠67線 KVAR | FEEDER | [5 empty] | 237 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE67 | 忠67線(KE67) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0226 |  |  | 2-E2 |  |  | 忠67線(KE67) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠67線A1 | 23KV忠67線 R相AMP | FEEDER | [5 empty] | 238 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE67 | 忠67線(KE67) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0227 |  |  | 2-E3 |  |  | 忠67線(KE67) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠67線A2 | 23KV忠67線 S相AMP | FEEDER | [5 empty] | 239 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE67 | 忠67線(KE67) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0228 |  |  | 2-E4 |  |  | 忠67線(KE67) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠67線A3 | 23KV忠67線 T相AMP | FEEDER | [5 empty] | 240 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE67 | 忠67線(KE67) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0229 |  |  | 2-E5 |  |  | 忠67線(KE67) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠67線A0 | 23KV忠67線 N相AMP | FEEDER | [5 empty] | 241 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE68 | 忠68線(KE68) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0230 |  |  | 2-E6 |  |  | 忠68線(KE68) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠68線KVAR | 23KV忠68線 KVAR | FEEDER | [5 empty] | 242 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE68 | 忠68線(KE68) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0231 |  |  | 2-E7 |  |  | 忠68線(KE68) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠68線A1 | 23KV忠68線 R相AMP | FEEDER | [5 empty] | 243 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE68 | 忠68線(KE68) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0232 |  |  | 2-E8 |  |  | 忠68線(KE68) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠68線A2 | 23KV忠68線 S相AMP | FEEDER | [5 empty] | 244 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE68 | 忠68線(KE68) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0233 |  |  | 2-E9 |  |  | 忠68線(KE68) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠68線A3 | 23KV忠68線 T相AMP | FEEDER | [5 empty] | 245 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE68 | 忠68線(KE68) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0234 |  |  | 2-EA |  |  | 忠68線(KE68) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠68線A0 | 23KV忠68線 N相AMP | FEEDER | [5 empty] | 246 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 200 | TIE(200) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0235 |  |  | 2-EB |  |  | 200(TIE-2) R 相電流 |  |  | A_-2000_2000(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.23KV_200_A1 | 23KV 200 R相AMP | TIE | [5 empty] | 247 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 200 | TIE(200) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0236 |  |  | 2-EC |  |  | 200(TIE-2) S 相電流 |  |  | A_-2000_2000(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.23KV_200_A2 | 23KV 200 S相AMP | TIE | [5 empty] | 248 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 200 | TIE(200) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0237 |  |  | 2-ED |  |  | 200(TIE-2) T 相電流 |  |  | A_-2000_2000(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.23KV_200_A3 | 23KV 200 T相AMP | TIE | [5 empty] | 249 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | KW |  | B3 | MvMoment | KW |  | Y |  | AI | [6 empty] | 0238 |  |  | 2-EE |  |  | 350(M3A) 瓦 |  |  | MW_-108_108(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.#3DTR(A)_MW | #3DTR二次側(A) MW | MTR | [5 empty] | 250 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0239 |  |  | 2-EF |  |  | 350(M3A) 乏 |  |  | MVAR_-72_72(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.#3DTR(A)_MVAR | #3DTR二次側(A) MVAR | MTR | [5 empty] | 251 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0240 |  |  | 2-F0 |  |  | 350(M3A) R 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.#3DTR(A)_A1 | #3DTR二次側(A) R相AMP | MTR | [5 empty] | 252 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0241 |  |  | 2-F1 |  |  | 350(M3A) S 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.#3DTR(A)_A2 | #3DTR二次側(A) S相AMP | MTR | [5 empty] | 253 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0242 |  |  | 2-F2 |  |  | 350(M3A) T 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.#3DTR(A)_A3 | #3DTR二次側(A) T相AMP | MTR | [5 empty] | 254 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 3ABUS | #3ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0243 |  |  | 2-F3 |  |  | 22KV #3A BUS #3A PT R相電壓 |  |  | kV_-18_18(-2000_2000) | aca | B3/D18_A1 | [8 empty] | 忠孝DS.23KV#3ABUS_KV | 23KV #3ABUS KV | BUS | [5 empty] | 255 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D18 | 忠孝DS | 22 | 22kV | KE71 | 忠71線(KE71) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0244 |  |  | 2-F4 |  |  | 忠71線(KE71) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠71線KVAR | 23KV忠71線 KVAR | FEEDER | [5 empty] | 256 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE71 | 忠71線(KE71) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0245 |  |  | 2-F5 |  |  | 忠71線(KE71) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠71線A1 | 23KV忠71線 R相AMP | FEEDER | [5 empty] | 257 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE71 | 忠71線(KE71) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0246 |  |  | 2-F6 |  |  | 忠71線(KE71) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠71線A2 | 23KV忠71線 S相AMP | FEEDER | [5 empty] | 258 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE71 | 忠71線(KE71) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0247 |  |  | 2-F7 |  |  | 忠71線(KE71) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠71線A3 | 23KV忠71線 T相AMP | FEEDER | [5 empty] | 259 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE71 | 忠71線(KE71) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0248 |  |  | 2-F8 |  |  | 忠71線(KE71) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠71線A0 | 23KV忠71線 N相AMP | FEEDER | [5 empty] | 260 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE72 | 忠72線(KE72) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0249 |  |  | 2-F9 |  |  | 忠72線(KE72) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠72線KVAR | 23KV忠72線 KVAR | FEEDER | [5 empty] | 261 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE72 | 忠72線(KE72) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0250 |  |  | 2-FA |  |  | 忠72線(KE72) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠72線A1 | 23KV忠72線 R相AMP | FEEDER | [5 empty] | 262 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE72 | 忠72線(KE72) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0251 |  |  | 2-FB |  |  | 忠72線(KE72) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠72線A2 | 23KV忠72線 S相AMP | FEEDER | [5 empty] | 263 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE72 | 忠72線(KE72) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0252 |  |  | 2-FC |  |  | 忠72線(KE72) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠72線A3 | 23KV忠72線 T相AMP | FEEDER | [5 empty] | 264 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE72 | 忠72線(KE72) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0253 |  |  | 2-FD |  |  | 忠72線(KE72) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠72線A0 | 23KV忠72線 N相AMP | FEEDER | [5 empty] | 265 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE73 | 忠73線(KE73) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0254 |  |  | 2-FE |  |  | 忠73線(KE73) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠73線KVAR | 23KV忠73線 KVAR | FEEDER | [5 empty] | 266 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE73 | 忠73線(KE73) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0255 |  |  | 2-FF |  |  | 忠73線(KE73) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠73線A1 | 23KV忠73線 R相AMP | FEEDER | [5 empty] | 267 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE73 | 忠73線(KE73) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0256 |  |  | 3-80 |  |  | 忠73線(KE73) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠73線A2 | 23KV忠73線 S相AMP | FEEDER | [5 empty] | 268 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE73 | 忠73線(KE73) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0257 |  |  | 3-81 |  |  | 忠73線(KE73) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠73線A3 | 23KV忠73線 T相AMP | FEEDER | [5 empty] | 269 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE73 | 忠73線(KE73) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0258 |  |  | 3-82 |  |  | 忠73線(KE73) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠73線A0 | 23KV忠73線 N相AMP | FEEDER | [5 empty] | 270 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE74 | 忠74線(KE74) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0259 |  |  | 3-83 |  |  | 忠74線(KE74) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠74線KVAR | 23KV忠74線 KVAR | FEEDER | [5 empty] | 271 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE74 | 忠74線(KE74) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0260 |  |  | 3-84 |  |  | 忠74線(KE74) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠74線A1 | 23KV忠74線 R相AMP | FEEDER | [5 empty] | 272 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE74 | 忠74線(KE74) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0261 |  |  | 3-85 |  |  | 忠74線(KE74) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠74線A2 | 23KV忠74線 S相AMP | FEEDER | [5 empty] | 273 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE74 | 忠74線(KE74) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0262 |  |  | 3-86 |  |  | 忠74線(KE74) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠74線A3 | 23KV忠74線 T相AMP | FEEDER | [5 empty] | 274 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE74 | 忠74線(KE74) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0263 |  |  | 3-87 |  |  | 忠74線(KE74) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠74線A0 | 23KV忠74線 N相AMP | FEEDER | [5 empty] | 275 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | KW |  | B3 | MvMoment | KW |  | Y |  | AI | [6 empty] | 0264 |  |  | 3-88 |  |  | 360(M3B) 瓦 |  |  | MW_-108_108(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.#3DTR(B)_MW | #3DTR二次側(B) MW | MTR | [5 empty] | 276 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0265 |  |  | 3-89 |  |  | 360(M3B) 乏 |  |  | MVAR_-72_72(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.#3DTR(B)_MVAR | #3DTR二次側(B) MVAR | MTR | [5 empty] | 277 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0266 |  |  | 3-8A |  |  | 360(M3B) R 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.#3DTR(B)_A1 | #3DTR二次側(B) R相AMP | MTR | [5 empty] | 278 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0267 |  |  | 3-8B |  |  | 360(M3B) S 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.#3DTR(B)_A2 | #3DTR二次側(B) S相AMP | MTR | [5 empty] | 279 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0268 |  |  | 3-8C |  |  | 360(M3B) T 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.#3DTR(B)_A3 | #3DTR二次側(B) T相AMP | MTR | [5 empty] | 280 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 3BBUS | #3BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0269 |  |  | 3-8D |  |  | 22KV #3B BUS #3B PT R相電壓 |  |  | kV_-18_18(-2000_2000) | bca | B3/D18_A1 | [8 empty] | 忠孝DS.23KV#3BBUS_KV | 23KV #3BBUS KV | BUS | [5 empty] | 281 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D18 | 忠孝DS | 22 | 22kV | KE75 | 忠75線(KE75) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0270 |  |  | 3-8E |  |  | 忠75線(KE75) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠75線KVAR | 23KV忠75線 KVAR | FEEDER | [5 empty] | 282 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE75 | 忠75線(KE75) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0271 |  |  | 3-8F |  |  | 忠75線(KE75) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠75線A1 | 23KV忠75線 R相AMP | FEEDER | [5 empty] | 283 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE75 | 忠75線(KE75) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0272 |  |  | 3-90 |  |  | 忠75線(KE75) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠75線A2 | 23KV忠75線 S相AMP | FEEDER | [5 empty] | 284 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE75 | 忠75線(KE75) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0273 |  |  | 3-91 |  |  | 忠75線(KE75) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠75線A3 | 23KV忠75線 T相AMP | FEEDER | [5 empty] | 285 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE75 | 忠75線(KE75) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0274 |  |  | 3-92 |  |  | 忠75線(KE75) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠75線A0 | 23KV忠75線 N相AMP | FEEDER | [5 empty] | 286 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE76 | 忠76線(KE76) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0275 |  |  | 3-93 |  |  | 忠76線(KE76) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠76線KVAR | 23KV忠76線 KVAR | FEEDER | [5 empty] | 287 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE76 | 忠76線(KE76) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0276 |  |  | 3-94 |  |  | 忠76線(KE76) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠76線A1 | 23KV忠76線 R相AMP | FEEDER | [5 empty] | 288 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE76 | 忠76線(KE76) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0277 |  |  | 3-95 |  |  | 忠76線(KE76) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠76線A2 | 23KV忠76線 S相AMP | FEEDER | [5 empty] | 289 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE76 | 忠76線(KE76) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0278 |  |  | 3-96 |  |  | 忠76線(KE76) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠76線A3 | 23KV忠76線 T相AMP | FEEDER | [5 empty] | 290 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE76 | 忠76線(KE76) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0279 |  |  | 3-97 |  |  | 忠76線(KE76) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠76線A0 | 23KV忠76線 N相AMP | FEEDER | [5 empty] | 291 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE77 | 忠77線(KE77) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0280 |  |  | 3-98 |  |  | 忠77線(KE77) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠77線KVAR | 23KV忠77線 KVAR | FEEDER | [5 empty] | 292 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE77 | 忠77線(KE77) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0281 |  |  | 3-99 |  |  | 忠77線(KE77) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠77線A1 | 23KV忠77線 R相AMP | FEEDER | [5 empty] | 293 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE77 | 忠77線(KE77) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0282 |  |  | 3-9A |  |  | 忠776線(KE77) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠77線A2 | 23KV忠77線 S相AMP | FEEDER | [5 empty] | 294 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE77 | 忠77線(KE77) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0283 |  |  | 3-9B |  |  | 忠77線(KE77) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠77線A3 | 23KV忠77線 T相AMP | FEEDER | [5 empty] | 295 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE77 | 忠77線(KE77) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0284 |  |  | 3-9C |  |  | 忠77線(KE77) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠77線A0 | 23KV忠77線 N相AMP | FEEDER | [5 empty] | 296 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE78 | 忠78線(KE78) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0285 |  |  | 3-9D |  |  | 忠78線(KE78) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠78線KVAR | 23KV忠78線 KVAR | FEEDER | [5 empty] | 297 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE78 | 忠78線(KE78) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0286 |  |  | 3-9E |  |  | 忠78線(KE78) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠78線A1 | 23KV忠78線 R相AMP | FEEDER | [5 empty] | 298 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE78 | 忠78線(KE78) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0287 |  |  | 3-9F |  |  | 忠78線(KE78) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠78線A2 | 23KV忠78線 S相AMP | FEEDER | [5 empty] | 299 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE78 | 忠78線(KE78) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0288 |  |  | 3-A0 |  |  | 忠78線(KE78) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠78線A3 | 23KV忠78線 T相AMP | FEEDER | [5 empty] | 300 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | KE78 | 忠78線(KE78) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0289 |  |  | 3-A1 |  |  | 忠78線(KE78) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D18_D1 | [8 empty] | 忠孝DS.忠78線A0 | 23KV忠78線 N相AMP | FEEDER | [5 empty] | 301 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 300 | TIE(300) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0290 |  |  | 3-A2 |  |  | 300(TIE-3) R 相電流 |  |  | A_-2000_2000(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.23KV_300_A1 | 23KV 300 R相AMP | TIE | [5 empty] | 302 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 300 | TIE(300) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0291 |  |  | 3-A3 |  |  | 300(TIE-3) S 相電流 |  |  | A_-2000_2000(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.23KV_300_A2 | 23KV 300 S相AMP | TIE | [5 empty] | 303 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 300 | TIE(300) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0292 |  |  | 3-A4 |  |  | 300(TIE-3) T 相電流 |  |  | A_-2000_2000(-2000_2000) |  | B3/D18_A1 | [8 empty] | 忠孝DS.23KV_300_A3 | 23KV 300 T相AMP | TIE | [5 empty] | 304 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝～延平線(1530) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D18D25/T1 |  | 0008 |  | 0003 | 1-01-00 |  | 1-03 | 忠孝延平線 1530 CB |  | PPU-1 |  | aaga | B2/D18_A1 | [8 empty] | 忠孝DS.1530_CB | 1530(忠孝延平線) CB | LINE161 | [5 empty] | 305 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 161 | 161kV | 1510 | 台南～忠孝一路(1510) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0001 |  |  | 1-00-01 |  |  | 台南忠孝一路1510 87A1 |  | PPU-1 |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1510_87A1 | 台南忠孝一路(1510)第一套87RY | LINE161 | [5 empty] | 306 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1510 | 台南～忠孝一路(1510) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0002 |  |  | 1-00-02 |  |  | 台南忠孝一路1510 PHA |  | PPU-1 |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1510_PHA | 台南忠孝一路(1510) 相間RY | LINE161 | [5 empty] | 307 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1510 | 台南～忠孝一路(1510) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | 台南忠孝一路1510 GDA |  | PPU-1 |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1510_GDA | 台南忠孝一路(1510) 接地RY | LINE161 | [5 empty] | 308 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0040 |  | 0011 | 1-05-00 |  | 1-0B | TIE(1500) CB |  | PPU-1 |  | aacz | B2/D18_A1 | [8 empty] | 忠孝DS.1500_CB | 1500(TIE) CB | TIE | [5 empty] | 309 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南～忠孝二路(1520) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0005 |  |  | 1-00-05 |  |  | 台南忠孝二路1520 87A1 |  | PPU-1 |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1520_87A1 | 台南忠孝二路(1520)第一套87RY | LINE161 | [5 empty] | 310 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南～忠孝二路(1520) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | 台南忠孝二路1520 PHA |  | PPU-1 |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1520_PHA | 台南忠孝二路(1520) 相間RY | LINE161 | [5 empty] | 311 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南～忠孝二路(1520) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-07 |  |  | 台南忠孝二路1520 GDA |  | PPU-1 |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1520_GDA | 台南忠孝二路(1520) 接地RY | LINE161 | [5 empty] | 312 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/1DTR |  | 0048 |  | 0012 | 1-06-00 |  | 1-0C | #1DTR 1750 CB |  | PPU-2 |  | aabb | ELEM/D18_A1 | [8 empty] | 忠孝DS.1750_CB | 1750(#1DTR) CB | MTR | [5 empty] | 313 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝～延平線(1530) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | 忠孝延平線 1530 87A1 |  | PPU-1 |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1530_87A1 | 忠孝延平線(1530)第一套87RY | LINE161 | [5 empty] | 314 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝～延平線(1530) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0010 |  |  | 1-01-02 |  |  | 忠孝延平線 1530 PHA |  | PPU-1 |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1530_PHA | 忠孝延平線(1530) 相間RY | LINE161 | [5 empty] | 315 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝～延平線(1530) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-03 |  |  | 忠孝延平線 1530 GDA |  | PPU-1 |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1530_GDA | 忠孝延平線(1530) 接地RY | LINE161 | [5 empty] | 316 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1510 | 台南～忠孝一路(1510) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0024 |  |  | 1-03-00 |  |  | 台南忠孝一路1510 87A2 |  | PPU-1 |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1510_87A2 | 台南忠孝一路(1510)第二套87RY | OTHER | [5 empty] | 317 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南～忠孝二路(1520) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0025 |  |  | 1-03-01 |  |  | 台南忠孝二路1520 87A2 |  | PPU-1 |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1520_87A2 | 台南忠孝二路(1520)第二套87RY | OTHER | [5 empty] | 318 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝～延平線(1530) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0026 |  |  | 1-03-02 |  |  | 忠孝延平線 1530 87A2 |  | PPU-1 |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1530_87A2 | 忠孝延平線(1530)第二套87RY | OTHER | [5 empty] | 319 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2DTR |  | 0062 |  | 0013 | 1-07-06 |  | 1-0D | #2DTR 1760 CB |  | PPU-2 |  | aaeb | ELEM/D18_A1 | [8 empty] | 忠孝DS.1760_CB | 1760(#2DTR) CB | MTR | [5 empty] | 320 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0041 |  |  | 1-05-01 |  |  | TIE(1500) 50A |  | PPU-1 |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1500_50A | 161KV TIE(1500) 50RY | TIE | [5 empty] | 321 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0042 |  |  | 1-05-02 |  |  | 161KV #1BUS 87A1 |  | PPU-1 |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | [5 empty] | 322 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0043 |  |  | 1-05-03 |  |  | 161KV #2BUS 87A2 |  | PPU-1 |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | [5 empty] | 323 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0044 |  |  | 1-05-04 |  |  | 示波器故障警報(OSCF) |  | PPU-1 |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.161KV_OSCF | 161KV OSC故障/缺紙,電源跳脫 | OTHER | [5 empty] | 324 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0045 |  |  | 1-05-05 |  |  | 示波器啟動警報(OSCA) |  | PPU-1 |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.161KV_OSCA | 161KV示波器啟動警報 | OTHER | [5 empty] | 325 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | StaDev | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0046 |  |  | 1-05-06 |  |  | 電力量測表計故障 PMA |  | PPU-1 |  |  | ELEM/D18_A1 | [8 empty] | 忠孝DS.PMA | 電力量測表計故障 | OTHER | [5 empty] | 326 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0047 |  |  | 1-05-07 |  |  | 161KV 79 RY RCA |  | PPU-1 |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | [5 empty] | 327 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/3DTR |  | 0076 |  | 0014 | 1-09-04 |  | 1-0E | #3DTR 1770 CB |  | PPU-2 |  | aahb | ELEM/D18_A1 | [8 empty] | 忠孝DS.1770_CB | 1770(#3DTR) CB | MTR | [5 empty] | 328 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS |  |  | 1DTR | #1DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0049 |  |  | 1-06-01 |  |  | #1DTR 87A |  | PPU-2 |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#1DTR_87A | #1DTR 87RY | MTR | [5 empty] | 329 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 1DTR | #1DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0050 |  |  | 1-06-02 |  |  | #1DTR 96PA |  | PPU-2 |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | [5 empty] | 330 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 1DTR | #1DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0051 |  |  | 1-06-03 |  |  | #1DTR 51ZA |  | PPU-2 |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | [5 empty] | 331 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 1DTR | #1DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | #1DTR PHA |  | PPU-2 |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#1DTR_PHA | #1DTR PHA | MTR | [5 empty] | 332 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 1DTR | #1DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0053 |  |  | 1-06-05 |  |  | #1DTR 86A |  | PPU-2 |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#1DTR_86A | #1DTR 86(50/50N/51Z/87/96)RY | OTHER | [5 empty] | 333 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 1DTR | #1DTR |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0054 |  |  | 1-06-06 |  |  | #1DTR 81A |  | PPU-2 |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#1DTR_81A | #1DTR 81RY動作 | OTHER | [5 empty] | 334 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 1DTR | #1DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0055 |  |  | 1-06-07 |  |  | #1DTR GDA |  | PPU-2 |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#1DTR_GDA | #1DTR GDA | MTR | [5 empty] | 335 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1950 | #1SHR(1950) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | R/1SHR |  | 0090 |  | 0015 | 1-0B-02 |  | 1-0F | #1SHR(1950) CB |  | PPU-2 |  | aaib | B2/D18_A1 | [8 empty] | 忠孝DS.1950_CB | 1950(161KV #1SHR) CB | OTHER | [5 empty] | 336 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0057 |  |  | 1-07-01 |  |  | 310(M1A) PHA |  | PPU-2 |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.310_PHA | #1DTR二次側(310) PHA | MTR | [5 empty] | 337 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | GDA |  | B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0058 |  |  | 1-07-02 |  |  | 310(M1A) GDA |  | PPU-2 |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.310_GDA | #1DTR二次側(310) GDA | OTHER | [5 empty] | 338 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | A/320^T/1DTR(A) |  |  | 0056 |  | 0016 | 1-07-00 |  | 1-10 | 310(M1A) CB |  | PPU-2 |  | aaba | ELEM/D18_A1 | [8 empty] | 忠孝DS.310_CB | 310(#1DTR) CB | MTR | [5 empty] | 339 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0060 |  |  | 1-07-04 |  |  | 320(M1B) PHA |  | PPU-2 |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.320_PHA | #1DTR二次側(320) PHA | MTR | [5 empty] | 340 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | GDA |  | B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0061 |  |  | 1-07-05 |  |  | 320(M1B) GDA |  | PPU-2 |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.320_GDA | #1DTR二次側(320) GDA | OTHER | [5 empty] | 341 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | A/310^T/1DTR(B) |  |  | 0059 |  | 0017 | 1-07-03 |  | 1-11 | 320(M1B) CB |  | PPU-2 |  | baba | ELEM/D18_A1 | [8 empty] | 忠孝DS.320_CB | 320(#1DTR) CB | MTR | [5 empty] | 342 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS |  |  | 2DTR | #2DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0063 |  |  | 1-07-07 |  |  | #2DTR 87A |  | PPU-2 |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#2DTR_87A | #2DTR 87RY | MTR | [5 empty] | 343 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 2DTR | #2DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0064 |  |  | 1-08-00 |  |  | #2DTR 96PA |  | PPU-2 |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | [5 empty] | 344 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 2DTR | #2DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0065 |  |  | 1-08-01 |  |  | #2DTR 51ZA |  | PPU-2 |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | [5 empty] | 345 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 2DTR | #2DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0066 |  |  | 1-08-02 |  |  | #2DTR PHA |  | PPU-2 |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#2DTR_PHA | #2DTR PHA | MTR | [5 empty] | 346 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 2DTR | #2DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0067 |  |  | 1-08-03 |  |  | #2DTR 86A |  | PPU-2 |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#2DTR_86A | #2DTR 86(50/50N/51Z/87/96)RY | OTHER | [5 empty] | 347 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 2DTR | #2DTR |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 |  |  | 1-08-04 |  |  | #2DTR 81A |  | PPU-2 |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#2DTR_81A | #2DTR 81RY動作 | OTHER | [5 empty] | 348 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 2DTR | #2DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 |  |  | 1-08-05 |  |  | #2DTR GDA |  | PPU-2 |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#2DTR_GDA | #2DTR GDA | MTR | [5 empty] | 349 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | A/340^T/2DTR(A) |  |  | 0070 |  | 0018 | 1-08-06 |  | 1-12 | 330(M2A) CB |  | PPU-2 |  | abba | ELEM/D18_A1 | [8 empty] | 忠孝DS.330_CB | 330(#2DTR) CB | MTR | [5 empty] | 350 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0071 |  |  | 1-08-07 |  |  | 330(M2A) PHA |  | PPU-2 |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.330_PHA | #2DTR二次側(330) PHA | MTR | [5 empty] | 351 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | GDA |  | B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0072 |  |  | 1-09-00 |  |  | 330(M2A) GDA |  | PPU-2 |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.330_GDA | #2DTR二次側(330) GDA | OTHER | [5 empty] | 352 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | A/330^T/2DTR(B) |  |  | 0073 |  | 0019 | 1-09-01 |  | 1-13 | 340(M2B) CB |  | PPU-2 |  | bbda | ELEM/D18_A1 | [8 empty] | 忠孝DS.340_CB | 340(#2DTR) CB | MTR | [5 empty] | 353 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-09-02 |  |  | 340(M2B) PHA |  | PPU-2 |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.340_PHA | #2DTR二次側(340) PHA | MTR | [5 empty] | 354 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | GDA |  | B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0075 |  |  | 1-09-03 |  |  | 340(M2B) GDA |  | PPU-2 |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.340_GDA | #2DTR二次側(340) GDA | OTHER | [5 empty] | 355 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3ABus | A/360^T/3DTR(A) |  |  | 0084 |  | 0020 | 1-0A-04 |  | 1-14 | 350(M3A) CB |  | PPU-2 |  | acaa | ELEM/D18_A1 | [8 empty] | 忠孝DS.350_CB | 350(#3DTR) CB | MTR | [5 empty] | 356 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS |  |  | 3DTR | #3DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0077 |  |  | 1-09-05 |  |  | #3DTR 87A |  | PPU-2 |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#3DTR_87A | #3DTR 87RY | MTR | [5 empty] | 357 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 3DTR | #3DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0078 |  |  | 1-09-06 |  |  | #3DTR 96PA |  | PPU-2 |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#3DTR_96PA | #3DTR 機械保護動作 | MTR | [5 empty] | 358 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 3DTR | #3DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0079 |  |  | 1-09-07 |  |  | #3DTR 51ZA |  | PPU-2 |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#3DTR_51ZA | #3DTR 51Z RY | MTR | [5 empty] | 359 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 3DTR | #3DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0080 |  |  | 1-0A-00 |  |  | #3DTR PHA |  | PPU-2 |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#3DTR_PHA | #3DTR PHA | MTR | [5 empty] | 360 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 3DTR | #3DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0081 |  |  | 1-0A-01 |  |  | #3DTR 86A |  | PPU-2 |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#3DTR_86A | #3DTR 86(50/50N/51Z/87/96)RY | OTHER | [5 empty] | 361 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 3DTR | #3DTR |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0082 |  |  | 1-0A-02 |  |  | #3DTR 81A |  | PPU-2 |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#3DTR_81A | #3DTR 81RY動作 | OTHER | [5 empty] | 362 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 3DTR | #3DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0083 |  |  | 1-0A-03 |  |  | #3DTR GDA |  | PPU-2 |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#3DTR_GDA | #3DTR GDA | MTR | [5 empty] | 363 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3BBus | A/350^T/3DTR(B) |  |  | 0087 |  | 0021 | 1-0A-07 |  | 1-15 | 360(M3B) CB |  | PPU-2 |  | bcba | ELEM/D18_A1 | [8 empty] | 忠孝DS.360_CB | 360(#3DTR) CB | MTR | [5 empty] | 364 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0085 |  |  | 1-0A-05 |  |  | 350(M3A) PHA |  | PPU-2 |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.350_PHA | #3DTR二次側(350) PHA | MTR | [5 empty] | 365 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | GDA |  | B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0086 |  |  | 1-0A-06 |  |  | 350(M3A) GDA |  | PPU-2 |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.350_GDA | #3DTR二次側(350) GDA | OTHER | [5 empty] | 366 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 210 | #1SC(210) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | C/1SC |  |  | 0192 |  | 0022 | 1-18-00 |  | 1-16 | 210(#1 SC) CB |  |  |  | aacb | B3/D18_A1 | [8 empty] | 忠孝DS.210_CB | 210(23KV #1SC) CB | SC | [5 empty] | 367 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0088 |  |  | 1-0B-00 |  |  | 360(M3B) PHA |  | PPU-2 |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.360_PHA | #3DTR二次側(360) PHA | MTR | [5 empty] | 368 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | GDA |  | B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0089 |  |  | 1-0B-01 |  |  | 360(M3B) GDA |  | PPU-2 |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.360_GDA | #3DTR二次側(360) GDA | OTHER | [5 empty] | 369 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 390 | #1SSTR(390) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | T/1SSTR |  |  | 0195 |  | 0023 | 1-18-03 |  | 1-17 | 390(#1 SSTR) CB |  |  |  | aafb | B3/D18_A1 | [8 empty] | 忠孝DS.390_CB | 390(#1SSTR) CB | OTHER | [5 empty] | 370 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 87A |  | B3 | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0091 |  |  | 1-0B-03 |  |  | #1SHR 87A |  | PPU-2 |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.161#1SHR_87A | 161KV #1SHR 87RY | OTHER | [5 empty] | 371 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 86A |  | B3,Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0092 |  |  | 1-0B-04 |  |  | #1SHR 86A |  | PPU-2 |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.161#1SHR_86A | 161KV #1SHR 86RY | OTHER | [5 empty] | 372 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 51A |  | B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0093 |  |  | 1-0B-05 |  |  | #1SHR 51A |  | PPU-2 |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.161#1SHR_51A | 161KV #1SHR 51RY | OTHER | [5 empty] | 373 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 96PA |  | B3 | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0094 |  |  | 1-0B-06 |  |  | #1SHR 96PA |  | PPU-2 |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.161#1SHR96PA | 161KV #1SHR 機械保護動作 | OTHER | [5 empty] | 374 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | RTU | RTU |  | RTU_MCT |  |  | Status | RTU Master Ry | Open/Close | Y | E | DI-SP | [6 empty] | 0095 |  |  | 1-0B-07 |  |  | RTU MASTER Ry SOE |  | PPU-2 |  |  | B3/D18_A1 | [16 empty] | 375 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D18 | 忠孝DS | 22 | 22kV | KE51 | 忠51線(KE51) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/KE51/T1 |  |  | 0198 |  | 0024 | 1-18-06 |  | 1-18 | 忠51線(KE51) CB |  |  |  | aadb | B2/D18_D1 | [8 empty] | 忠孝DS.KE51_CB | KE51(23KV忠51線) CB | FEEDER | [5 empty] | 376 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 210 | #1SC(210) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0193 |  |  | 1-18-01 |  |  | 210(#1 SC) SCA |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.210_SCA | 23KV #1SC 51,51N RY | SC | [5 empty] | 377 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 210 | #1SC(210) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0194 |  |  | 1-18-02 |  |  | 210(#1 SC) UVA |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.210_OUVA | 23KV #1SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 378 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE52 | 忠52線(KE52) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/KE52/T1 |  |  | 0201 |  | 0025 | 1-19-01 |  | 1-19 | 忠52線(KE52) CB |  |  |  | aaeb | B2/D18_D1 | [8 empty] | 忠孝DS.KE52_CB | KE52(23KV忠52線) CB | FEEDER | [5 empty] | 379 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 390 | #1SSTR(390) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0196 |  |  | 1-18-04 |  |  | 390(#1 SSTR) PHA |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.#1SSTR_51A | #1SSTR 51RY | OTHER | [5 empty] | 380 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 390 | #1SSTR(390) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0197 |  |  | 1-18-05 |  |  | 390(#1 SSTR) GDA |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | [5 empty] | 381 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE53 | 忠53線(KE53) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/KE53/T1 |  |  | 0204 |  | 0026 | 1-19-04 |  | 1-1A | 忠53線(KE53) CB |  |  |  | aagb | B2/D18_D1 | [8 empty] | 忠孝DS.KE53_CB | KE53(23KV忠53線) CB | FEEDER | [5 empty] | 382 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE51 | 忠51線(KE51) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0199 |  |  | 1-18-07 |  |  | 忠51線(KE51) PHA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE51_PHA | 23KV忠51線(KE51) 相間RY | FEEDER | [5 empty] | 383 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE51 | 忠51線(KE51) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0200 |  |  | 1-19-00 |  |  | 忠51線(KE51) GDA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE51_GDA | 23KV忠51線(KE51) 接地RY | FEEDER | [5 empty] | 384 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE54 | 忠54線(KE54) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/KE54/T1 |  |  | 0207 |  | 0027 | 1-19-07 |  | 1-1B | 忠54線(KE54) CB |  |  |  | aahb | B2/D18_D1 | [8 empty] | 忠孝DS.KE54_CB | KE54(23KV忠54線) CB | FEEDER | [5 empty] | 385 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE52 | 忠52線(KE52) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0202 |  |  | 1-19-02 |  |  | 忠52線(KE52) PHA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE52_PHA | 23KV忠52線(KE52) 相間RY | FEEDER | [5 empty] | 386 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE52 | 忠52線(KE52) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0203 |  |  | 1-19-03 |  |  | 忠52線(KE52) GDA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE52_GDA | 23KV忠52線(KE52) 接地RY | FEEDER | [5 empty] | 387 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 100 | TIE(100) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/1BBus | B/2ABus |  |  | 0210 |  | 0028 | 1-1A-02 |  | 1-1C | 100(TIE-1) CB |  |  |  | bahb | B3/D18_A1 | [8 empty] | 忠孝DS.100_CB | 100(TIE) CB | TIE | [5 empty] | 388 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | KE53 | 忠53線(KE53) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0205 |  |  | 1-19-05 |  |  | 忠53線(KE53) PHA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE53_PHA | 23KV忠53線(KE53) 相間RY | FEEDER | [5 empty] | 389 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE53 | 忠53線(KE53) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0206 |  |  | 1-19-06 |  |  | 忠53線(KE53) GDA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE53_GDA | 23KV忠53線(KE53) 接地RY | FEEDER | [5 empty] | 390 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 220 | #2SC(220) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | C/2SC |  |  | 0213 |  | 0029 | 1-1A-05 |  | 1-1D | 220(#2 SC) CB |  |  |  | bacb | B3/D18_A1 | [8 empty] | 忠孝DS.220_CB | 220(23KV #2SC) CB | SC | [5 empty] | 391 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE54 | 忠54線(KE54) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0208 |  |  | 1-1A-00 |  |  | 忠54線(KE54) PHA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE54_PHA | 23KV忠54線(KE54) 相間RY | FEEDER | [5 empty] | 392 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE54 | 忠54線(KE54) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0209 |  |  | 1-1A-01 |  |  | 忠54線(KE54) GDA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE54_GDA | 23KV忠54線(KE54) 接地RY | FEEDER | [5 empty] | 393 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE55 | 忠55線(KE55) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/KE55/T1 |  |  | 0216 |  | 0030 | 1-1B-00 |  | 1-1E | 忠55線(KE55) CB |  |  |  | badb | B2/D18_D1 | [8 empty] | 忠孝DS.KE55_CB | KE55(23KV忠55線) CB | FEEDER | [5 empty] | 394 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 100 | TIE(100) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0211 |  |  | 1-1A-03 |  |  | 100(TIE-1) PHA |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.100_51A | 23KV TIE(100) 51RY | TIE | [5 empty] | 395 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 100 | TIE(100) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0212 |  |  | 1-1A-04 |  |  | 100(TIE-1) GDA |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.100_51NA | 23KV TIE(100) 51N RY | TIE | [5 empty] | 396 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE56 | 忠56線(KE56) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/KE56/T1 |  |  | 0219 |  | 0031 | 1-1B-03 |  | 1-1F | 忠56線(KE56) CB |  |  |  | baeb | B2/D18_D1 | [8 empty] | 忠孝DS.KE56_CB | KE56(23KV忠56線) CB | FEEDER | [5 empty] | 397 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 220 | #2SC(220) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0214 |  |  | 1-1A-06 |  |  | 220(#2 SC) SCA |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.220_SCA | 23KV #2SC 51,51N RY | SC | [5 empty] | 398 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 220 | #2SC(220) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0215 |  |  | 1-1A-07 |  |  | 220(#2 SC) UVA |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.220_OUVA | 23KV #2SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 399 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE57 | 忠57線(KE57) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/KE57/T1 |  |  | 0222 |  | 0032 | 1-1B-06 |  | 1-20 | 忠57線(KE57) CB |  |  |  | bafb | B2/D18_D1 | [8 empty] | 忠孝DS.KE57_CB | KE57(23KV忠57線) CB | FEEDER | [5 empty] | 400 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE55 | 忠55線(KE55) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0217 |  |  | 1-1B-01 |  |  | 忠55線(KE55) PHA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE55_PHA | 23KV忠55線(KE55) 相間RY | FEEDER | [5 empty] | 401 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE55 | 忠55線(KE55) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0218 |  |  | 1-1B-02 |  |  | 忠55線(KE55) GDA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE55_GDA | 23KV忠55線(KE55) 接地RY | FEEDER | [5 empty] | 402 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE58 | 忠58線(KE58) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/KE58/T1 |  |  | 0225 |  | 0033 | 1-1C-01 |  | 1-21 | 忠58線(KE58) CB |  |  |  | bagb | B2/D18_D1 | [8 empty] | 忠孝DS.KE58_CB | KE58(23KV忠58線) CB | FEEDER | [5 empty] | 403 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE56 | 忠56線(KE56) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0220 |  |  | 1-1B-04 |  |  | 忠56線(KE56) PHA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE56_PHA | 23KV忠56線(KE56) 相間RY | FEEDER | [5 empty] | 404 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE56 | 忠56線(KE56) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0221 |  |  | 1-1B-05 |  |  | 忠56線(KE56) GDA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE56_GDA | 23KV忠56線(KE56) 接地RY | FEEDER | [5 empty] | 405 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 230 | #3SC(230) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | C/3SC |  |  | 0228 |  | 0034 | 1-1C-04 |  | 1-22 | 230(#3 SC) CB |  |  |  | abcb | B3/D18_A1 | [8 empty] | 忠孝DS.230_CB | 230(23KV #3SC) CB | SC | [5 empty] | 406 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE57 | 忠57線(KE57) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0223 |  |  | 1-1B-07 |  |  | 忠57線(KE57) PHA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE57_PHA | 23KV忠57線(KE57) 相間RY | FEEDER | [5 empty] | 407 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE57 | 忠57線(KE57) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0224 |  |  | 1-1C-00 |  |  | 忠57線(KE57) GDA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE57_GDA | 23KV忠57線(KE57) 接地RY | FEEDER | [5 empty] | 408 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE61 | 忠61線(KE61) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/KE61/T1 |  |  | 0231 |  | 0035 | 1-1C-07 |  | 1-23 | 忠61線(KE61) CB |  |  |  | abdb | B2/D18_D1 | [8 empty] | 忠孝DS.KE61_CB | KE61(23KV忠61線) CB | FEEDER | [5 empty] | 409 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE58 | 忠58線(KE58) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0226 |  |  | 1-1C-02 |  |  | 忠58線(KE58) PHA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE58_PHA | 23KV忠58線(KE58) 相間RY | FEEDER | [5 empty] | 410 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE58 | 忠58線(KE58) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0227 |  |  | 1-1C-03 |  |  | 忠58線(KE58) GDA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE58_GDA | 23KV忠58線(KE58) 接地RY | FEEDER | [5 empty] | 411 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE62 | 忠62線(KE62) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/KE62/T1 |  |  | 0234 |  | 0036 | 1-1D-02 |  | 1-24 | 忠62線(KE62) CB |  |  |  | abeb | B2/D18_D1 | [8 empty] | 忠孝DS.KE62_CB | KE62(23KV忠62線) CB | FEEDER | [5 empty] | 412 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 230 | #3SC(230) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0229 |  |  | 1-1C-05 |  |  | 230(#3 SC) SCA |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.230_SCA | 23KV #3SC 51,51N RY | SC | [5 empty] | 413 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 230 | #3SC(230) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0230 |  |  | 1-1C-06 |  |  | 230(#3 SC) UVA |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.230_OUVA | 23KV #3SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 414 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE63 | 忠63線(KE63) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/KE63/T1 |  |  | 0237 |  | 0037 | 1-1D-05 |  | 1-25 | 忠63線(KE63) CB |  |  |  | abfb | B2/D18_D1 | [8 empty] | 忠孝DS.KE63_CB | KE63(23KV忠63線) CB | FEEDER | [5 empty] | 415 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE61 | 忠61線(KE61) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0232 |  |  | 1-1D-00 |  |  | 忠61線(KE61) PHA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE61_PHA | 23KV忠61線(KE61) 相間RY | FEEDER | [5 empty] | 416 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE61 | 忠61線(KE61) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0233 |  |  | 1-1D-01 |  |  | 忠61線(KE61) GDA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE61_GDA | 23KV忠61線(KE61) 接地RY | FEEDER | [5 empty] | 417 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE64 | 忠64線(KE64) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/KE64/T1 |  |  | 0240 |  | 0038 | 1-1E-00 |  | 1-26 | 忠64線(KE64) CB |  |  |  | abgb | B2/D18_D1 | [8 empty] | 忠孝DS.KE64_CB | KE64(23KV忠64線) CB | FEEDER | [5 empty] | 418 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE62 | 忠62線(KE62) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0235 |  |  | 1-1D-03 |  |  | 忠62線(KE62) PHA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE62_PHA | 23KV忠62線(KE62) 相間RY | FEEDER | [5 empty] | 419 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE62 | 忠62線(KE62) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0236 |  |  | 1-1D-04 |  |  | 忠62線(KE62) GDA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE62_GDA | 23KV忠62線(KE62) 接地RY | FEEDER | [5 empty] | 420 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 200 | TIE(200) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/2BBus | B/3ABus |  |  | 0243 |  | 0039 | 1-1E-03 |  | 1-27 | 200(TIE-2) CB |  |  |  | bbbb | B3/D18_A1 | [8 empty] | 忠孝DS.200_CB | 200(TIE) CB | TIE | [5 empty] | 421 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | KE63 | 忠63線(KE63) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0238 |  |  | 1-1D-06 |  |  | 忠63線(KE63) PHA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE63_PHA | 23KV忠63線(KE63) 相間RY | FEEDER | [5 empty] | 422 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE63 | 忠63線(KE63) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0239 |  |  | 1-1D-07 |  |  | 忠63線(KE63) GDA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE63_GDA | 23KV忠63線(KE63) 接地RY | FEEDER | [5 empty] | 423 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 490 | #2SSTR(490) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | T/2SSTR |  |  | 0246 |  | 0040 | 1-1E-06 |  | 1-28 | 490(#2 SSTR) CB |  |  |  | bbcb | B3/D18_A1 | [8 empty] | 忠孝DS.490_CB | 490(#2SSTR) CB | OTHER | [5 empty] | 424 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE64 | 忠64線(KE64) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0241 |  |  | 1-1E-01 |  |  | 忠64線(KE64) PHA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE64_PHA | 23KV忠64線(KE64) 相間RY | FEEDER | [5 empty] | 425 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE64 | 忠64線(KE64) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0242 |  |  | 1-1E-02 |  |  | 忠64線(KE64) GDA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE64_GDA | 23KV忠64線(KE64) 接地RY | FEEDER | [5 empty] | 426 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 240 | #4SC(240) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | C/4SC |  |  | 0249 |  | 0041 | 1-1F-01 |  | 1-29 | 240(#4 SC) CB |  |  |  | bbeb | B3/D18_A1 | [8 empty] | 忠孝DS.240_CB | 240(23KV #4SC) CB | SC | [5 empty] | 427 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 200 | TIE(200) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0244 |  |  | 1-1E-04 |  |  | 200(TIE-2) PHA |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.200_51A | 23KV TIE(200) 51RY | TIE | [5 empty] | 428 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 200 | TIE(200) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0245 |  |  | 1-1E-05 |  |  | 200(TIE-2) GDA |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.200_51NA | 23KV TIE(200) 51N RY | TIE | [5 empty] | 429 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE65 | 忠65線(KE65) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/KE65/T1 |  |  | 0252 |  | 0042 | 1-1F-04 |  | 1-2A | 忠65線(KE65) CB |  |  |  | bbfb | B2/D18_D1 | [8 empty] | 忠孝DS.KE65_CB | KE65(23KV忠65線) CB | FEEDER | [5 empty] | 430 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 490 | #2SSTR(490) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0247 |  |  | 1-1E-07 |  |  | 490(#2 SSTR) PHA |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.#2SSTR_51A | #2SSTR 51RY | OTHER | [5 empty] | 431 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 490 | #2SSTR(490) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0248 |  |  | 1-1F-00 |  |  | 490(#2 SSTR) GDA |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | [5 empty] | 432 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE66 | 忠66線(KE66) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/KE66/T1 |  |  | 0255 |  | 0043 | 1-1F-07 |  | 1-2B | 忠66線(KE66) CB |  |  |  | bbgb | B2/D18_D1 | [8 empty] | 忠孝DS.KE66_CB | KE66(23KV忠66線) CB | FEEDER | [5 empty] | 433 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 240 | #4SC(240) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0250 |  |  | 1-1F-02 |  |  | 240(#4 SC) SCA |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.240_SCA | 23KV #4SC 51,51N RY | SC | [5 empty] | 434 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 240 | #4SC(240) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0251 |  |  | 1-1F-03 |  |  | 240(#4 SC) UVA |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.240_OUVA | 23KV #4SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 435 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE67 | 忠67線(KE67) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/KE67/T1 |  |  | 0258 |  | 0044 | 2-00-02 |  | 1-2C | 忠67線(KE67) CB |  |  |  | bbhb | B2/D18_D1 | [8 empty] | 忠孝DS.KE67_CB | KE67(23KV忠67線) CB | FEEDER | [5 empty] | 436 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE65 | 忠65線(KE65) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0253 |  |  | 1-1F-05 |  |  | 忠65線(KE65) PHA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE65_PHA | 23KV忠65線(KE65) 相間RY | FEEDER | [5 empty] | 437 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE65 | 忠65線(KE65) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0254 |  |  | 1-1F-06 |  |  | 忠65線(KE65) GDA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE65_GDA | 23KV忠65線(KE65) 接地RY | FEEDER | [5 empty] | 438 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE68 | 忠68線(KE68) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/KE68/T1 |  |  | 0261 |  | 0045 | 2-00-05 |  | 1-2D | 忠68線(KE68) CB |  |  |  | bbib | B2/D18_D1 | [8 empty] | 忠孝DS.KE68_CB | KE68(23KV忠68線) CB | FEEDER | [5 empty] | 439 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE66 | 忠66線(KE66) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0256 |  |  | 2-00-00 |  |  | 忠66線(KE66) PHA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE66_PHA | 23KV忠66線(KE66) 相間RY | FEEDER | [5 empty] | 440 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE66 | 忠66線(KE66) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0257 |  |  | 2-00-01 |  |  | 忠66線(KE66) GDA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE66_GDA | 23KV忠66線(KE66) 接地RY | FEEDER | [5 empty] | 441 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 250 | #5SC(250) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3ABus | C/5SC |  |  | 0264 |  | 0046 | 2-01-00 |  | 1-2E | 250(#5 SC) CB |  |  |  | acbb | B3/D18_A1 | [8 empty] | 忠孝DS.250_CB | 250(23KV #5SC) CB | SC | [5 empty] | 442 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE67 | 忠67線(KE67) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0259 |  |  | 2-00-03 |  |  | 忠67線(KE67) PHA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE67_PHA | 23KV忠67線(KE67) 相間RY | FEEDER | [5 empty] | 443 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE67 | 忠67線(KE67) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0260 |  |  | 2-00-04 |  |  | 忠67線(KE67) GDA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE67_GDA | 23KV忠67線(KE67) 接地RY | FEEDER | [5 empty] | 444 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE71 | 忠71線(KE71) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3ABus | L/KE71/T1 |  |  | 0267 |  | 0047 | 2-01-03 |  | 1-2F | 忠71線(KE71) CB |  |  |  | accb | B2/D18_D1 | [8 empty] | 忠孝DS.KE71_CB | KE71(23KV忠71線) CB | FEEDER | [5 empty] | 445 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE68 | 忠68線(KE68) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0262 |  |  | 2-00-06 |  |  | 忠68線(KE68) PHA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE68_PHA | 23KV忠68線(KE68) 相間RY | FEEDER | [5 empty] | 446 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE68 | 忠68線(KE68) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0263 |  |  | 2-00-07 |  |  | 忠68線(KE68) GDA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE68_GDA | 23KV忠68線(KE68) 接地RY | FEEDER | [5 empty] | 447 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE72 | 忠72線(KE72) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3ABus | L/KE72/T1 |  |  | 0270 |  | 0048 | 2-01-06 |  | 1-30 | 忠72線(KE72) CB |  |  |  | acdb | B2/D18_D1 | [8 empty] | 忠孝DS.KE72_CB | KE72(23KV忠72線) CB | FEEDER | [5 empty] | 448 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 250 | #5SC(250) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0265 |  |  | 2-01-01 |  |  | 250(#5 SC) SCA |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.250_SCA | 23KV #5SC 51,51N RY | SC | [5 empty] | 449 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 250 | #5SC(250) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0266 |  |  | 2-01-02 |  |  | 250(#5 SC) UVA |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.250_OUVA | 23KV #5SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE73 | 忠73線(KE73) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3ABus | L/KE73/T1 |  |  | 0273 |  | 0049 | 2-02-01 |  | 1-31 | 忠73線(KE73) CB |  |  |  | aceb | B2/D18_D1 | [8 empty] | 忠孝DS.KE73_CB | KE73(23KV忠73線) CB | FEEDER | [5 empty] | 451 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE71 | 忠71線(KE71) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0268 |  |  | 2-01-04 |  |  | 忠71線(KE71) PHA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE71_PHA | 23KV忠71線(KE71) 相間RY | FEEDER | [5 empty] | 452 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE71 | 忠71線(KE71) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0269 |  |  | 2-01-05 |  |  | 忠71線(KE71) GDA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE71_GDA | 23KV忠71線(KE71) 接地RY | FEEDER | [5 empty] | 453 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE74 | 忠74線(KE74) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3ABus | L/KE74/T1 |  |  | 0276 |  | 0050 | 2-02-04 |  | 1-32 | 忠74線(KE74) CB |  |  |  | acfb | B2/D18_D1 | [8 empty] | 忠孝DS.KE74_CB | KE74(23KV忠74線) CB | FEEDER | [5 empty] | 454 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE72 | 忠72線(KE72) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0271 |  |  | 2-01-07 |  |  | 忠72線(KE72) PHA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE72_PHA | 23KV忠72線(KE72) 相間RY | FEEDER | [5 empty] | 455 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE72 | 忠72線(KE72) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0272 |  |  | 2-02-00 |  |  | 忠72線(KE72) GDA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE72_GDA | 23KV忠72線(KE72) 接地RY | FEEDER | [5 empty] | 456 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 300 | TIE(300) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/3BBus | B/1ABus |  |  | 0279 |  | 0051 | 2-02-07 |  | 1-33 | 300(TIE-3) CB |  |  |  | bchb | B3/D18_A1 | [8 empty] | 忠孝DS.300_CB | 300(TIE) CB | TIE | [5 empty] | 457 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | KE73 | 忠73線(KE73) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0274 |  |  | 2-02-02 |  |  | 忠73線(KE73) PHA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE73_PHA | 23KV忠73線(KE73) 相間RY | FEEDER | [5 empty] | 458 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE73 | 忠73線(KE73) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0275 |  |  | 2-02-03 |  |  | 忠73線(KE73) GDA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE73_GDA | 23KV忠73線(KE73) 接地RY | FEEDER | [5 empty] | 459 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 260 | #6SC(260) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3BBus | C/6SC |  |  | 0282 |  | 0052 | 2-03-02 |  | 1-34 | 260(#6 SC) CB |  |  |  | bccb | B3/D18_A1 | [8 empty] | 忠孝DS.260_CB | 260(23KV #6SC) CB | SC | [5 empty] | 460 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE74 | 忠74線(KE74) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0277 |  |  | 2-02-05 |  |  | 忠74線(KE74) PHA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE74_PHA | 23KV忠74線(KE74) 相間RY | FEEDER | [5 empty] | 461 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE74 | 忠74線(KE74) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0278 |  |  | 2-02-06 |  |  | 忠74線(KE74) GDA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE74_GDA | 23KV忠74線(KE74) 接地RY | FEEDER | [5 empty] | 462 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE75 | 忠75線(KE75) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BBus | L/KE75/T1 |  |  | 0285 |  | 0053 | 2-03-05 |  | 1-35 | 忠75線(KE75) CB |  |  |  | bcdb | B2/D18_D1 | [8 empty] | 忠孝DS.KE75_CB | KE75(23KV忠75線) CB | FEEDER | [5 empty] | 463 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 300 | TIE(300) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0280 |  |  | 2-03-00 |  |  | 300(TIE-3) PHA |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.300_51A | 23KV TIE(300) 51RY | TIE | [5 empty] | 464 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 300 | TIE(300) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0281 |  |  | 2-03-01 |  |  | 300(TIE-3) GDA |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.300_51NA | 23KV TIE(300) 51N RY | TIE | [5 empty] | 465 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE76 | 忠76線(KE76) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BBus | L/KE76/T1 |  |  | 0288 |  | 0054 | 2-04-00 |  | 1-36 | 忠76線(KE76) CB |  |  |  | bcb | B2/D18_D1 | [8 empty] | 忠孝DS.KE76_CB | KE76(23KV忠76線) CB | FEEDER | [5 empty] | 466 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 260 | #6SC(260) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0283 |  |  | 2-03-03 |  |  | 260(#6 SC) SCA |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.260_SCA | 23KV #6SC 51,51N RY | SC | [5 empty] | 467 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 260 | #6SC(260) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0284 |  |  | 2-03-04 |  |  | 260(#6 SC) UVA |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.260_OUVA | 23KV #6SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 468 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE77 | 忠77線(KE77) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BBus | L/KE77/T1 |  |  | 0291 |  | 0055 | 2-04-03 |  | 1-37 | 忠77線(KE77) CB |  |  |  | bcfb | B2/D18_D1 | [8 empty] | 忠孝DS.KE77_CB | KE77(23KV忠77線) CB | FEEDER | [5 empty] | 469 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE75 | 忠75線(KE75) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0286 |  |  | 2-03-06 |  |  | 忠75線(KE75) PHA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE75_PHA | 23KV忠75線(KE75) 相間RY | FEEDER | [5 empty] | 470 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE75 | 忠75線(KE75) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0287 |  |  | 2-03-07 |  |  | 忠75線(KE75) GDA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE75_GDA | 23KV忠75線(KE75) 接地RY | FEEDER | [5 empty] | 471 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE78 | 忠78線(KE78) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BBus | L/KE78/T1 |  |  | 0294 |  | 0056 | 2-04-06 |  | 1-38 | 忠78線(KE78) CB |  |  |  | bcgb | B2/D18_D1 | [8 empty] | 忠孝DS.KE78_CB | KE78(23KV忠78線) CB | FEEDER | [5 empty] | 472 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE76 | 忠76線(KE76) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0289 |  |  | 2-04-01 |  |  | 忠76線(KE76) PHA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE76_PHA | 23KV忠76線(KE76) 相間RY | FEEDER | [5 empty] | 473 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE76 | 忠76線(KE76) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0290 |  |  | 2-04-02 |  |  | 忠76線(KE76) GDA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE76_GDA | 23KV忠76線(KE76) 接地RY | FEEDER | [5 empty] | 474 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1510 | 台南～忠孝一路(1510) |  | DS1 | 1511 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0640 | 641 | 0064 | 1-38-00 | 1-38-01 | 1-40 | 台南忠孝一路 1511 DS-AS |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1511_DS | 1511(台南忠孝一路) DS | LINE161 | [5 empty] | 475 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE77 | 忠77線(KE77) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0292 |  |  | 2-04-04 |  |  | 忠77線(KE77) PHA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE77_PHA | 23KV忠77線(KE77) 相間RY | FEEDER | [5 empty] | 476 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE77 | 忠77線(KE77) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0293 |  |  | 2-04-05 |  |  | 忠77線(KE77) GDA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE77_GDA | 23KV忠77線(KE77) 接地RY | FEEDER | [5 empty] | 477 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1510 | 台南～忠孝一路(1510) |  | DS2 | 1512 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0642 | 643 | 0065 | 1-38-02 | 1-38-03 | 1-41 | 台南忠孝一路 1512 DS-AS |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1512_DS | 1512(台南忠孝一路) DS | LINE161 | [5 empty] | 478 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D18 | 忠孝DS | 22 | 22kV | KE78 | 忠78線(KE78) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0295 |  |  | 2-04-07 |  |  | 忠78線(KE78) PHA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE78_PHA | 23KV忠78線(KE78) 相間RY | FEEDER | [5 empty] | 479 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE78 | 忠78線(KE78) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0296 |  |  | 2-05-00 |  |  | 忠78線(KE78) GDA |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE78_GDA | 23KV忠78線(KE78) 接地RY | FEEDER | [5 empty] | 480 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | 81A |  | B3 | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0320 |  |  | 2-08-00 |  |  | 310(M1A) 81A |  |  |  |  | ELEM/D18_A1 | [8 empty] | 忠孝DS.310_81A | #1DTR(310) 81RY動作 | OTHER | [5 empty] | 481 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE51 | 忠51線(KE51) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0321 |  |  | 2-08-01 |  |  | 忠51線(KE51) 81A |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE51_81A | 23KV忠51線(KE51) 81RY | OTHER | [5 empty] | 482 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE52 | 忠52線(KE52) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0322 |  |  | 2-08-02 |  |  | 忠52線(KE52) 81A |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE52_81A | 23KV忠52線(KE52) 81RY | OTHER | [5 empty] | 483 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE53 | 忠53線(KE53) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0323 |  |  | 2-08-03 |  |  | 忠53線(KE53) 81A |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE53_81A | 23KV忠53線(KE53) 81RY | OTHER | [5 empty] | 484 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE54 | 忠54線(KE54) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0324 |  |  | 2-08-04 |  |  | 忠54線(KE54) 81A |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE54_81A | 23KV忠54線(KE54) 81RY | OTHER | [5 empty] | 485 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | 81A |  | B3 | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0325 |  |  | 2-08-05 |  |  | 320(M1B) 81A |  |  |  |  | ELEM/D18_A1 | [8 empty] | 忠孝DS.320_81A | #1DTR(320) 81RY動作 | OTHER | [5 empty] | 486 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE55 | 忠55線(KE55) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0326 |  |  | 2-08-06 |  |  | 忠55線(KE55) 81A |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE55_81A | 23KV忠55線(KE55) 81RY | OTHER | [5 empty] | 487 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE56 | 忠56線(KE56) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0327 |  |  | 2-08-07 |  |  | 忠56線(KE56) 81A |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE56_81A | 23KV忠56線(KE56) 81RY | OTHER | [5 empty] | 488 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE57 | 忠57線(KE57) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0328 |  |  | 2-09-00 |  |  | 忠57線(KE57) 81A |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE57_81A | 23KV忠57線(KE57) 81RY | OTHER | [5 empty] | 489 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE58 | 忠58線(KE58) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0329 |  |  | 2-09-01 |  |  | 忠58線(KE58) 81A |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE58_81A | 23KV忠58線(KE58) 81RY | OTHER | [5 empty] | 490 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | 81A |  | B3 | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0330 |  |  | 2-09-02 |  |  | 330(M2A) 81A |  |  |  |  | ELEM/D18_A1 | [8 empty] | 忠孝DS.330_81A | #2DTR(330) 81RY動作 | OTHER | [5 empty] | 491 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE61 | 忠61線(KE61) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0331 |  |  | 2-09-03 |  |  | 忠61線(KE61) 81A |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE61_81A | 23KV忠61線(KE61) 81RY | OTHER | [5 empty] | 492 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE62 | 忠62線(KE62) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0332 |  |  | 2-09-04 |  |  | 忠62線(KE62) 81A |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE62_81A | 23KV忠62線(KE62) 81RY | OTHER | [5 empty] | 493 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE63 | 忠63線(KE63) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0333 |  |  | 2-09-05 |  |  | 忠63線(KE63) 81A |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE63_81A | 23KV忠63線(KE63) 81RY | OTHER | [5 empty] | 494 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE64 | 忠64線(KE64) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0334 |  |  | 2-09-06 |  |  | 忠64線(KE64) 81A |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE64_81A | 23KV忠64線(KE64) 81RY | OTHER | [5 empty] | 495 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | 81A |  | B3 | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0335 |  |  | 2-09-07 |  |  | 340(M2B) 81A |  |  |  |  | ELEM/D18_A1 | [8 empty] | 忠孝DS.340_81A | #2DTR(340) 81RY動作 | OTHER | [5 empty] | 496 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE65 | 忠65線(KE65) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0336 |  |  | 2-0A-00 |  |  | 忠65線(KE65) 81A |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE65_81A | 23KV忠65線(KE65) 81RY | OTHER | [5 empty] | 497 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE66 | 忠66線(KE66) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0337 |  |  | 2-0A-01 |  |  | 忠66線(KE66) 81A |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE66_81A | 23KV忠66線(KE66) 81RY | OTHER | [5 empty] | 498 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE67 | 忠67線(KE67) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0338 |  |  | 2-0A-02 |  |  | 忠67線(KE67) 81A |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE67_81A | 23KV忠67線(KE67) 81RY | OTHER | [5 empty] | 499 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE68 | 忠68線(KE68) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0339 |  |  | 2-0A-03 |  |  | 忠68線(KE68) 81A |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE68_81A | 23KV忠68線(KE68) 81RY | OTHER | [5 empty] | 500 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | 81A |  | B3 | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0340 |  |  | 2-0A-04 |  |  | 350(M3A) 81A |  |  |  |  | ELEM/D18_A1 | [8 empty] | 忠孝DS.350_81A | #3DTR(350) 81RY動作 | OTHER | [5 empty] | 501 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE71 | 忠71線(KE71) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0341 |  |  | 2-0A-05 |  |  | 忠71線(KE71) 81A |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE71_81A | 23KV忠71線(KE71) 81RY | OTHER | [5 empty] | 502 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE72 | 忠72線(KE72) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0342 |  |  | 2-0A-06 |  |  | 忠72線(KE72) 81A |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE72_81A | 23KV忠72線(KE72) 81RY | OTHER | [5 empty] | 503 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE73 | 忠73線(KE73) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0343 |  |  | 2-0A-07 |  |  | 忠73線(KE73) 81A |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE73_81A | 23KV忠73線(KE73) 81RY | OTHER | [5 empty] | 504 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE74 | 忠74線(KE74) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0344 |  |  | 2-0B-00 |  |  | 忠74線(KE74) 81A |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE74_81A | 23KV忠74線(KE74) 81RY | OTHER | [5 empty] | 505 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | 81A |  | B3 | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0345 |  |  | 2-0B-01 |  |  | 360(M3B) 81A |  |  |  |  | ELEM/D18_A1 | [8 empty] | 忠孝DS.360_81A | #3DTR(360) 81RY動作 | OTHER | [5 empty] | 506 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE75 | 忠75線(KE75) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0346 |  |  | 2-0B-02 |  |  | 忠75線(KE75) 81A |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE75_81A | 23KV忠75線(KE75) 81RY | OTHER | [5 empty] | 507 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE76 | 忠76線(KE76) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0347 |  |  | 2-0B-03 |  |  | 忠76線(KE76) 81A |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE76_81A | 23KV忠76線(KE76) 81RY | OTHER | [5 empty] | 508 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE77 | 忠77線(KE77) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0348 |  |  | 2-0B-04 |  |  | 忠77線(KE77) 81A |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE77_81A | 23KV忠77線(KE77) 81RY | OTHER | [5 empty] | 509 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE78 | 忠78線(KE78) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0349 |  |  | 2-0B-05 |  |  | 忠78線(KE78) 81A |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE78_81A | 23KV忠78線(KE78) 81RY | OTHER | [5 empty] | 510 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1510 | 台南～忠孝一路(1510) |  | DS3 | 1513 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0644 | 645 | 0066 | 1-38-04 | 1-38-05 | 1-42 | 台南忠孝一路 1513 DS-AS |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1513_DS | 1513(台南忠孝一路) DS | LINE161 | [5 empty] | 511 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D18 | 忠孝DS | 0 |  | RTU | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0513 |  |  | 1-30-01 |  |  | L/R STATUS ON/OFF |  |  |  |  | ELEM/D18_A1 | [8 empty] | 忠孝DS.RTU_S/L | RTU SUPY/LOCAL | OTHER | [5 empty] | 512 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
D18 | 忠孝DS | 161 | 161kV | 1510 | 台南～忠孝一路(1510) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0514 |  |  | 1-30-02 |  |  | 台南忠孝一路1510 87CFA |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1510_87CFA | 台南忠孝一路(1510)87RY通訊故障 | OTHER | [5 empty] | 513 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1510 | 台南～忠孝一路(1510) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0515 |  |  | 1-30-03 |  |  | 台南忠孝一路1510 RYFA |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1510_RYFA | 台南忠孝一路(1510)數位電驛故障 | OTHER | [5 empty] | 514 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南～忠孝二路(1520) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0516 |  |  | 1-30-04 |  |  | 台南忠孝二路1520 87CFA |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1520_87CFA | 台南忠孝二路(1520)87RY通訊故障 | OTHER | [5 empty] | 515 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南～忠孝二路(1520) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0517 |  |  | 1-30-05 |  |  | 台南忠孝二路1520 RYFA |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1520_RYFA | 台南忠孝二路(1520)數位電驛故障 | OTHER | [5 empty] | 516 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝～延平線(1530) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0518 |  |  | 1-30-06 |  |  | 忠孝延平線 1530 87CFA |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1530_87CFA | 忠孝延平線(1530)87RY通訊故障 | OTHER | [5 empty] | 517 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝～延平線(1530) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0519 |  |  | 1-30-07 |  |  | 忠孝延平線 1530 RYFA |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1530_RYFA | 忠孝延平線(1530)數位電驛故障 | OTHER | [5 empty] | 518 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 1DTR | #1DTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0529 |  |  | 1-31-01 |  |  | #1DTR 第一套87RY U/L |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#1DTR_87UL1 | #1DTR 第一套87RY U/L | MTR | [5 empty] | 519 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS |  |  | 1DTR | #1DTR |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0530 |  |  | 1-31-02 |  |  | #1DTR 第二套87RY U/L |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#1DTR_87UL2 | #1DTR 第二套87RY U/L | OTHER | [5 empty] | 520 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS |  |  | 1DTR | #1DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0531 |  |  | 1-31-03 |  |  | #1DTR 51Z RY U/L |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#1DTR_51ZUL | #1DTR 51Z RY U/L | OTHER | [5 empty] | 521 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS |  |  | 1DTR | #1DTR |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0532 |  |  | 1-31-04 |  |  | #1DTR 81RY U/L |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#1DTR_81UL | #1DTR 81RY U/L | OTHER | [5 empty] | 522 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS |  |  | 2DTR | #2DTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0534 |  |  | 1-31-06 |  |  | #2DTR 第一套87RY U/L |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#2DTR_87UL1 | #2DTR 第一套87RY U/L | MTR | [5 empty] | 523 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS |  |  | 1DTR | #1DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0535 |  |  | 1-31-07 |  |  | #1DTR 96B1 |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | [5 empty] | 524 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 1DTR | #1DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0536 |  |  | 1-31-08 |  |  | #1DTR 96B2 |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | [5 empty] | 525 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 1DTR | #1DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0537 |  |  | 1-31-09 |  |  | #1DTR 96D |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#1DTR_96D | #1DTR 96D RY | MTR | [5 empty] | 526 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 1DTR | #1DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0538 |  |  | 1-31-10 |  |  | #1DTR 96P |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#1DTR_96P | #1DTR 96P RY | MTR | [5 empty] | 527 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 1DTR | #1DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0539 |  |  | 1-31-11 |  |  | #1DTR 63Q |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#1DTR_63Q | #1DTR 63Q RY | MTR | [5 empty] | 528 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 2DTR | #2DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0540 |  |  | 1-31-12 |  |  | #2DTR 96B1 |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | [5 empty] | 529 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 2DTR | #2DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0541 |  |  | 1-31-13 |  |  | #2DTR 96B2 |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | [5 empty] | 530 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 2DTR | #2DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0542 |  |  | 1-31-14 |  |  | #2DTR 96D |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#2DTR_96D | #2DTR 96D RY | MTR | [5 empty] | 531 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 2DTR | #2DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0543 |  |  | 1-31-15 |  |  | #2DTR 96P |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#2DTR_96P | #2DTR 96P RY | MTR | [5 empty] | 532 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 2DTR | #2DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0544 |  |  | 1-32-00 |  |  | #2DTR 63Q |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#2DTR_63Q | #2DTR 63Q RY | MTR | [5 empty] | 533 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 3DTR | #3DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0545 |  |  | 1-32-01 |  |  | #3DTR 96B1 |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#3DTR_96B1 | #3DTR 96B1 RY | MTR | [5 empty] | 534 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 3DTR | #3DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0546 |  |  | 1-32-02 |  |  | #3DTR 96B2 |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#3DTR_96B2 | #3DTR 96B2 RY | MTR | [5 empty] | 535 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 3DTR | #3DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0547 |  |  | 1-32-03 |  |  | #3DTR 96D |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#3DTR_96D | #3DTR 96D RY | MTR | [5 empty] | 536 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 3DTR | #3DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0548 |  |  | 1-32-04 |  |  | #3DTR 96P |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#3DTR_96P | #3DTR 96P RY | MTR | [5 empty] | 537 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 3DTR | #3DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0549 |  |  | 1-32-05 |  |  | #3DTR 63Q |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#3DTR_63Q | #3DTR 63Q RY | MTR | [5 empty] | 538 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 1DTR | #1DTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0550 |  |  | 1-32-06 |  | 1-63 | #1DTR OLTC R/L |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#1DTR_S/L | #1DTR OLTC S/L | MTR | [5 empty] | 539 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D18 | 忠孝DS | 161 | 161kV | 1510 | 台南～忠孝一路(1510) |  | ES3 | 1513E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0646 | 647 | 0067 | 1-38-06 | 1-38-07 | 1-43 | 台南忠孝一路 1513E ES-AS |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1513E_ES | 1513E(台南忠孝一路) ES | LINE161 | [5 empty] | 540 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D18 | 忠孝DS |  |  | 1DTR | #1DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0552 |  |  | 1-32-08 |  |  | #1DTR TRA |  |  |  | a | B1/D18_A1 | [8 empty] | 忠孝DS.#1DTR_TRA | #1DTR 重故障 | MTR | [5 empty] | 541 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 1DTR | #1DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0553 |  |  | 1-32-09 |  |  | #1DTR TRF |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#1DTR_TRF | #1DTR 輕故障 | MTR | [5 empty] | 542 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 2DTR | #2DTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0554 |  |  | 1-32-10 |  | 1-65 | #2DTR OLTC R/L |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#2DTR_S/L | #2DTR OLTC S/L | MTR | [5 empty] | 543 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南～忠孝二路(1520) |  | DS1 | 1521 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0648 | 649 | 0068 | 1-38-08 | 1-38-09 | 1-44 | 台南忠孝二路 1521 DS-AS |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1521_DS | 1521(台南忠孝二路) DS | LINE161 | [5 empty] | 544 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D18 | 忠孝DS |  |  | 2DTR | #2DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0556 |  |  | 1-32-12 |  |  | #2DTR TRA |  |  |  | a | B1/D18_A1 | [8 empty] | 忠孝DS.#2DTR_TRA | #2DTR 重故障 | MTR | [5 empty] | 545 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 2DTR | #2DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0557 |  |  | 1-32-13 |  |  | #2DTR TRF |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#2DTR_TRF | #2DTR 輕故障 | MTR | [5 empty] | 546 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 3DTR | #3DTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0558 |  |  | 1-32-14 |  | 1-67 | #3DTR OLTC R/L |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#3DTR_S/L | #3DTR OLTC S/L | MTR | [5 empty] | 547 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南～忠孝二路(1520) |  | DS2 | 1522 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0650 | 651 | 0069 | 1-38-10 | 1-38-11 | 1-45 | 台南忠孝二路 1522 DS-AS |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1522_DS | 1522(台南忠孝二路) DS | LINE161 | [5 empty] | 548 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D18 | 忠孝DS |  |  | 3DTR | #3DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0560 |  |  | 1-33-00 |  |  | #3DTR TRF |  |  |  | a | B1/D18_A1 | [8 empty] | 忠孝DS.#3DTR_TRF | #3DTR 輕故障 | MTR | [5 empty] | 549 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 3DTR | #3DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0561 |  |  | 1-33-01 |  |  | #3DTR TRA |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#3DTR_TRA | #3DTR 重故障 | MTR | [5 empty] | 550 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 96B1 |  | B3 | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0562 |  |  | 1-33-02 |  |  | #1SHR 96B1 |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.161#1SHR_96B1 | 161KV #1SHR 96B1 RY | OTHER | [5 empty] | 551 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 96B2 |  | B3 | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0563 |  |  | 1-33-03 |  |  | #1SHR 96B2 |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.161#1SHR_96B2 | 161KV #1SHR 96B2 RY | OTHER | [5 empty] | 552 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 96D |  | B3 | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0564 |  |  | 1-33-04 |  |  | #1SHR 96D |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.161#1SHR_96D | 161KV #1SHR 96D RY | OTHER | [5 empty] | 553 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 96P |  | B3 | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0565 |  |  | 1-33-05 |  |  | #1SHR 96P |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.161#1SHR_96P | 161KV #1SHR 96P RY | OTHER | [5 empty] | 554 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1950 | #1SHR(1950) |  | SHRF |  | B3 | Status | 電抗器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0566 |  |  | 1-33-06 |  |  | #1SHR SRF |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.161#1SHR_SRF | 161KV #1SHR 輕故障 | OTHER | [5 empty] | 555 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1950 | #1SHR(1950) |  | SHRA |  | B3 | Status | 電抗器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0567 |  |  | 1-33-07 |  |  | #1SHR SRA |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.161#1SHR_SRA | 161KV #1SHR 重故障 | OTHER | [5 empty] | 556 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 2DTR | #2DTR |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0568 |  |  | 1-33-08 |  |  | #2DTR 第二套87RY U/L |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#2DTR_87UL2 | #2DTR 第二套87RY U/L | OTHER | [5 empty] | 557 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS |  |  | 2DTR | #2DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0569 |  |  | 1-33-09 |  |  | #2DTR 51Z RY U/L |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#2DTR_51ZUL | #2DTR 51Z RY U/L | OTHER | [5 empty] | 558 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS |  |  | 2DTR | #2DTR |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0570 |  |  | 1-33-10 |  |  | #2DTR 81RY U/L |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#2DTR_81UL | #2DTR 81RY U/L | OTHER | [5 empty] | 559 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS |  |  | 3DTR | #3DTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0572 |  |  | 1-33-12 |  |  | #3DTR 第一套87RY U/L |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#3DTR_87UL1 | #3DTR 第一套87RY U/L | MTR | [5 empty] | 560 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS |  |  | 3DTR | #3DTR |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0573 |  |  | 1-33-13 |  |  | #3DTR 第二套87RY U/L |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#3DTR_87UL2 | #3DTR 第二套87RY U/L | OTHER | [5 empty] | 561 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS |  |  | 3DTR | #3DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0574 |  |  | 1-33-14 |  |  | #3DTR 51Z RY U/L |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#3DTR_51ZUL | #3DTR 51Z RY U/L | OTHER | [5 empty] | 562 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS |  |  | 3DTR | #3DTR |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0575 |  |  | 1-33-15 |  |  | #3DTR 81RY U/L |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#3DTR_81UL | #3DTR 81RY U/L | OTHER | [5 empty] | 563 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南～忠孝二路(1520) |  | DS3 | 1523 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0652 | 653 | 0070 | 1-38-12 | 1-38-13 | 1-46 | 台南忠孝二路 1523 DS-AS |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1523_DS | 1523(台南忠孝二路) DS | LINE161 | [5 empty] | 564 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南～忠孝二路(1520) |  | ES3 | 1523E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0654 | 655 | 0071 | 1-38-14 | 1-38-15 | 1-47 | 台南忠孝二路 1523E ES-AS |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1523E_ES | 1523E(台南忠孝二路) ES | LINE161 | [5 empty] | 565 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D18 | 忠孝DS | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0578 |  |  | 1-34-02 |  |  | TIE (1500) 50SA |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1500_50SA | 161KV TIE(1500) 50RY 測試/正常 | TIE | [5 empty] | 566 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Test | Test | 1 |  |  | TEST/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | ComPoint |  |  | 12B_CTFA | BUS_87CTFA | Element | Status | #1#2 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0579 |  |  | 1-34-03 |  |  | 161KV BUS 87CTFA |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.161KV_BUS_CTFA | 161KV BUS CT回路故障 | OTHER | [5 empty] | 567 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | ComPoint |  |  | BUS_RYFA |  |  | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0580 |  |  | 1-34-04 |  |  | 161KV BUS RYFA |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | [5 empty] | 568 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 1DTR | #1DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0581 |  |  | 1-34-05 |  |  | #1DTR RYFA |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#1DTR_RYFA | #1DTR 數位電驛故障 | OTHER | [5 empty] | 569 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 2DTR | #2DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0582 |  |  | 1-34-06 |  |  | #2DTR RYFA |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#2DTR_RYFA | #2DTR 數位電驛故障 | OTHER | [5 empty] | 570 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS |  |  | 3DTR | #3DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0583 |  |  | 1-34-07 |  |  | #3DTR RYFA |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#3DTR_RYFA | #3DTR 數位電驛故障 | OTHER | [5 empty] | 571 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1950 | #1SHR(1950) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0584 |  |  | 1-34-08 |  |  | #1SHR RYFA |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.161#1SHR_RYFA | 161KV #1SHR 數位電驛故障 | OTHER | [5 empty] | 572 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 1_87UL1 |  | B3 | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0585 |  |  | 1-34-09 |  |  | #1SHR 第一套 87RY U/L |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.161#1SHR_87UL1 | 161KV #1SHR 第一套87RY U/L | OTHER | [5 empty] | 573 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 1_87UL2 |  | B3 | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0586 |  |  | 1-34-10 |  |  | #1SHR 第二套 87RY U/L |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.161#1SHR_87UL2 | 161KV #1SHR 第二套87RY U/L | OTHER | [5 empty] | 574 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 0 |  | ComPoint |  |  | 25PFA |  |  | Status | 同步校核電驛電源 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0591 |  |  | 1-34-15 |  |  | 同步校核裝置電源 25PFA |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER | [5 empty] | 575 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | ComPoint |  |  | 25TA |  |  | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0592 |  |  | 1-35-00 |  |  | 同步校核裝置超時 25TA |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | [5 empty] | 576 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | ComPoint |  |  | COMT |  |  | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0593 |  |  | 1-35-01 |  |  | 空壓機運轉超時 COMT |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.161空壓機COMT | 161KV空壓機運轉超時警報 | OTHER | [5 empty] | 577 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | ComPoint |  |  | OPA |  |  | Status | 充油電纜低壓警報 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0594 |  |  | 1-35-02 |  |  | 充油電纜警報 OPA |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | [5 empty] | 578 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0595 |  |  | 1-35-03 |  |  | 所內電源ACB1 |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | [5 empty] | 579 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D18 | 忠孝DS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0596 |  |  | 1-35-04 |  |  | 所內電源ACB2 |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | [5 empty] | 580 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D18 | 忠孝DS | 0 |  | StaDev | 所內設施 |  | ACBT |  |  | Status | 所內電源ACB TIE | Close/Open | Y | 3 | DI-SP | [6 empty] | 0597 |  |  | 1-35-05 |  |  | 所內電源ACB TIE |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | [5 empty] | 581 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ON/OFF | OFF
D18 | 忠孝DS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0599 |  |  | 1-35-07 |  |  | STUV (所內欠壓警報) |  |  |  |  | ELEM/D18_A1 | [8 empty] | 忠孝DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | [5 empty] | 582 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | StaDev | 所內設施 |  | Door1 | 大小門 |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0600 |  |  | 1-35-08 |  |  | 無人化門禁 (1)大小門 |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.無人化門禁(1) | 無人化門禁(1)圍牆大小門 | OTHER | [5 empty] | 583 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | StaDev | 所內設施 |  | Burglar | 保全系統 |  | Status | 無人化防盜 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0601 |  |  | 1-35-09 |  |  | 無人化防盜 (1)保全系統 |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | [5 empty] | 584 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | StaDev | 所內設施 |  | Door2 |  |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0602 |  |  | 1-35-10 |  |  | 無人化門禁 (2) |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.無人化門禁(3) | 無人化門禁(3) | OTHER | [5 empty] | 585 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | StaDev | 所內設施 |  | Door3 |  |  | Status | 無人化門禁3 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0603 |  |  | 1-35-11 |  |  | 無人化門禁 (3) |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.無人化門禁(4) | 無人化門禁(4) | OTHER | [5 empty] | 586 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | StaDev | 所內設施 |  | Door4 |  |  | Status | 無人化門禁4 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0604 |  |  | 1-35-12 |  |  | 無人化門禁 (4) |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.無人化門禁(5) | 無人化門禁(5) | OTHER | [5 empty] | 587 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | StaDev | 所內設施 |  | Fire1 | 消防火警警報 |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0605 |  |  | 1-35-13 |  |  | 火災警報(1) 消防火警警報 |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.火災警報(1) | 消防火災警報 | OTHER | [5 empty] | 588 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | StaDev | 所內設施 |  | Fire2 | 消防故障警報 |  | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0606 |  |  | 1-35-14 |  |  | 火災警報(2) 消防故障警報 |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.火災警報(2) | 消防故障警報 | OTHER | [5 empty] | 589 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | StaDev | 所內設施 |  | Fire3 | CO2防護區火警 |  | Status | 火災警報3 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0607 |  |  | 1-35-15 |  |  | 火災警報(3) CO2防護區火警 |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.火災警報(3) | CO2防護區火警 | OTHER | [5 empty] | 590 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | StaDev | 所內設施 |  | Fire4 | CO2控制主機故障 |  | Status | 火災警報4 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0608 |  |  | 1-36-00 |  |  | 火災警報(4) CO2控制主機故障 |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.火災警報(4) | CO2主機故障 | OTHER | [5 empty] | 591 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | StaDev | 所內設施 |  | Fire5 | CO2鋼瓶漏氣 |  | Status | 火災警報5 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0609 |  |  | 1-36-01 |  |  | 火災警報(5) CO2鋼瓶漏氣 |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.火災警報(5) | CO2鋼瓶漏氣 | OTHER | [5 empty] | 592 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | StaDev | 所內設施 |  | Water1 |  |  | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0610 |  |  | 1-36-02 |  |  | UW1 (地下室水位警報 1) |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.水位警報(1) | 地下室水位警報(1) | OTHER | [5 empty] | 593 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | StaDev | 所內設施 |  | Water2 |  |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0611 |  |  | 1-36-03 |  |  | UW2 (地下室水位警報 2) |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.水位警報(2) | 地下室水位警報(2) | OTHER | [5 empty] | 594 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | StaDev | 所內設施 |  | OilLeak1 |  |  | Status | 洩油池水位警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0612 |  |  | 1-36-04 |  |  | OF1 (集油池警報 1) |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.集油池警報(1) | 集油池水位警報(1) | OTHER | [5 empty] | 595 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | StaDev | 所內設施 |  | OilLeak2 |  |  | Status | 洩油池水位警報2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0613 |  |  | 1-36-05 |  |  | OF2 (集油池警報 2) |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.集油池警報(2) | 集油池水位警報(2) | OTHER | [5 empty] | 596 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0614 |  |  | 1-36-06 |  |  | 161KV CBA |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.161KV_CBA | 161KV斷路器重故障 | OTHER | [5 empty] | 597 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0615 |  |  | 1-36-07 |  |  | 161KV CBF |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | [5 empty] | 598 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0616 |  |  | 1-36-08 |  |  | DCA (直流電源故障) |  |  |  |  | ELEM/D18_A1 | [8 empty] | 忠孝DS.直流電源DCA | 直流電源故障警報 | OTHER | [5 empty] | 599 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0617 |  |  | 1-36-09 |  |  | ACBA |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.所內電源ACBA | 所內電源故障警報 | OTHER | [5 empty] | 600 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0618 |  |  | 1-36-10 |  |  | VUA1 161kV#1BUS衡相Ry動作 |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | [5 empty] | 601 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0619 |  |  | 1-36-11 |  |  | VUA2 161kV#2BUS衡相Ry動作 |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | [5 empty] | 602 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0620 |  |  | 1-36-12 |  |  | CHG1 (直流充電機故障) |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.直流充電機故障 | 直流充電機故障 | OTHER | [5 empty] | 603 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0621 |  |  | 1-36-13 |  |  | DCE |  |  |  |  | ELEM/D18_A1 | [8 empty] | 忠孝DS.直流電源DCE | 直流電源接地故障警報 | OTHER | [5 empty] | 604 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | ComPoint |  |  | 60A |  |  | Status | 電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0622 |  |  | 1-36-14 |  |  | 23kV SC 60A |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.23KV_SC_60A | 11/23KV SC 60A | OTHER | [5 empty] | 605 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | StaDev | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0626 |  |  | 1-37-02 |  |  | PSF (其他輕故障) |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.其他輕故障 | 變電所內其他輕故障 | OTHER | [5 empty] | 606 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | StaDev | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0627 |  |  | 1-37-03 |  |  | PSA (其他重故障) |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.其他重故障 | 變電所內其他重故障 | OTHER | [5 empty] | 607 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0628 |  |  | 1-37-04 |  |  | CHG2 (通訊充電機故障) |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | [5 empty] | 608 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0629 |  |  | 1-37-05 |  |  | ACFA (通訊設備AC故障) |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | [5 empty] | 609 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | StaDev | 所內設施 |  | R_Temp1 | 通訊室 |  | Status | 溫度警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0632 |  |  | 1-37-08 |  |  | 通訊室溫度警報 |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.通信機房溫度 | 通訊室溫度警報 | OTHER | [5 empty] | 610 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | StaDev | 所內設施 |  | GEN | 緊急發電機運轉 | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0633 |  |  | 1-37-09 |  |  | 緊急發電機運轉 |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.GEN | 緊急發電機運轉 | OTHER | [5 empty] | 611 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ON/OFF | OFF
D18 | 忠孝DS | 0 |  | StaDev | 所內設施 |  | R_Temp2 | 控制室 |  | Status | 溫度警報2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0634 |  |  | 1-37-10 |  |  | 控制室溫度警報 |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.控制室溫度 | 控制室溫度警報 | OTHER | [5 empty] | 612 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0637 |  |  | 1-37-13 |  |  | 23KV CBA |  |  |  |  | ELEM/D18_A1 | [8 empty] | 忠孝DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | [5 empty] | 613 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0638 |  |  | 1-37-14 |  |  | 23KV CBF |  |  |  |  | ELEM/D18_A1 | [8 empty] | 忠孝DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | [5 empty] | 614 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | ComPoint |  |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0639 |  |  | 1-37-15 |  |  | 23KV LOA |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.11/23KV_LOA | 11/23KV饋線復閉失敗閉鎖 | OTHER | [5 empty] | 615 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝～延平線(1530) |  | DS1 | 1531 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0656 | 657 | 0072 | 1-39-00 | 1-39-01 | 1-48 | 忠孝延平線 1531 DS-AS |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1531_DS | 1531(忠孝延平線) DS | LINE161 | [5 empty] | 616 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝～延平線(1530) |  | DS2 | 1532 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0658 | 659 | 0073 | 1-39-02 | 1-39-03 | 1-49 | 忠孝延平線 1532 DS-AS |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1532_DS | 1532(忠孝延平線) DS | LINE161 | [5 empty] | 617 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝～延平線(1530) |  | DS3 | 1533 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0660 | 661 | 0074 | 1-39-04 | 1-39-05 | 1-4A | 忠孝延平線 1533 DS-AS |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1533_DS | 1533(忠孝延平線) DS | LINE161 | [5 empty] | 618 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝～延平線(1530) |  | ES3 | 1533E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0662 | 663 | 0075 | 1-39-06 | 1-39-07 | 1-4B | 忠孝延平線 1533E ES-AS |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1533E_ES | 1533E(忠孝延平線) ES | LINE161 | [5 empty] | 619 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D18 | 忠孝DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0688 | 689 | 0088 | 1-3B-00 | 1-3B-01 | 1-58 | TIE(1501) DS-AS |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1501_DS | 1501(TIE) DS | TIE | [5 empty] | 620 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D18 | 忠孝DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0690 | 691 | 0089 | 1-3B-02 | 1-3B-03 | 1-59 | TIE(1502) DS-AS |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1502_DS | 1502(TIE) DS | TIE | [5 empty] | 621 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D18 | 忠孝DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0692 | 693 | 0090 | 1-3B-04 | 1-3B-05 | 1-5A | #1DTR(1751) DS-AS |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1751_DS | 1751(#1DTR) DS | MTR | [5 empty] | 622 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D18 | 忠孝DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0694 | 695 | 0091 | 1-3B-06 | 1-3B-07 | 1-5B | #1DTR(1752) DS-AS |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1752_DS | 1752(#1DTR) DS | MTR | [5 empty] | 623 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D18 | 忠孝DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0696 | 697 | 0092 | 1-3B-08 | 1-3B-09 | 1-5C | #2DTR(1761) DS-AS |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1761_DS | 1761(#2DTR) DS | MTR | [5 empty] | 624 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D18 | 忠孝DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0698 | 699 | 0093 | 1-3B-10 | 1-3B-11 | 1-5D | #2DTR(1762) DS-AS |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1762_DS | 1762(#2DTR) DS | MTR | [5 empty] | 625 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D18 | 忠孝DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0700 | 701 | 0094 | 1-3B-12 | 1-3B-13 | 1-5E | #3DTR(1771) DS-AS |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1771_DS | 1771(#3DTR) DS | MTR | [5 empty] | 626 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D18 | 忠孝DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0702 | 703 | 0095 | 1-3B-14 | 1-3B-15 | 1-5F | #3DTR(1772) DS-AS |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1772_DS | 1772(#3DTR) DS | MTR | [5 empty] | 627 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D18 | 忠孝DS | 161 | 161kV | 1950 | #1SHR(1950) |  | DS1 | 1951 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0704 | 705 | 0096 | 1-3C-00 | 1-3C-01 | 1-60 | #1SHR(1951) DS-AS |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1951_DS | 1951(161KV #1SHR) DS | OTHER | [5 empty] | 628 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D18 | 忠孝DS | 161 | 161kV | 1950 | #1SHR(1950) |  | DS2 | 1952 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0706 | 707 | 0097 | 1-3C-02 | 1-3C-03 | 1-61 | #1SHR(1952) DS-AS |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1952_DS | 1952(161KV #1SHR) DS | OTHER | [5 empty] | 629 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D18 | 忠孝DS |  |  | 1DTR | #1DTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0551 |  | 0098 | 1-32-07 |  | 1-62 | #1DTR OLTC A/M |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#1DTR_A/M | #1DTR OLTC A/M | MTR | [5 empty] | 630 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D18 | 忠孝DS |  |  | 1DTR | #1DTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0034 |  | 0099 | 1-A2 |  | 1-63 | #1DTR OLTC TAP |  |  | TAP_-8.5_8.5(0_2000) |  | B1/D18_A1 | [8 empty] | 忠孝DS.#1DTR_TAP | #1DTR OLTC TAP | MTR | [5 empty] | 631 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D18 | 忠孝DS |  |  | 2DTR | #2DTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0555 |  | 0100 | 1-32-11 |  | 1-64 | #2DTR OLTC A/M |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#2DTR_A/M | #2DTR OLTC A/M | MTR | [5 empty] | 632 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D18 | 忠孝DS |  |  | 2DTR | #2DTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0037 |  | 0101 | 1-A5 |  | 1-65 | #2DTR OLTC TAP |  |  | TAP_-8.5_8.5(0_2000) |  | B1/D18_A1 | [8 empty] | 忠孝DS.#2DTR_TAP | #2DTR OLTC TAP | MTR | [5 empty] | 633 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D18 | 忠孝DS |  |  | 3DTR | #3DTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0559 |  | 0102 | 1-32-15 |  | 1-66 | #3DTR OLTC A/M |  |  |  |  | B1/D18_A1 | [8 empty] | 忠孝DS.#3DTR_A/M | #3DTR OLTC A/M | MTR | [5 empty] | 634 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D18 | 忠孝DS |  |  | 3DTR | #3DTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0040 |  | 0103 | 1-A8 |  | 1-67 | #3DTR OLTC TAP |  |  | TAP_-8.5_8.5(0_2000) |  | B1/D18_A1 | [8 empty] | 忠孝DS.#3DTR_TAP | #3DTR OLTC TAP | MTR | [5 empty] | 635 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D18 | 忠孝DS | 161 | 161kV | 1510 | 台南～忠孝一路(1510) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0854 |  | 0128 | 2-35-06 |  | 2-00 | 台南忠孝一路1510 第一套87RY U/L |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1510_87UL1 | 台南忠孝一路(1510)#187RY U/L | LINE161 | [5 empty] | 636 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 161 | 161kV | 1510 | 台南～忠孝一路(1510) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0855 |  | 0129 | 2-35-07 |  | 2-01 | 台南忠孝一路1510 79 RY U/L |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1510_79UL | 台南忠孝一路(1510) 79RY U/L | LINE161 | [5 empty] | 637 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 161 | 161kV | 1510 | 台南～忠孝一路(1510) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0856 |  | 0130 | 2-35-08 |  | 2-02 | 台南忠孝一路1510 第二套87RY U/L |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1510_87UL2 | 台南忠孝一路(1510)#287RY U/L | LINE161 | [5 empty] | 638 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南～忠孝二路(1520) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0857 |  | 0131 | 2-35-09 |  | 2-03 | 台南忠孝二路1520 第一套87RY U/L |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1520_87UL1 | 台南忠孝二路(1520)#187RY U/L | LINE161 | [5 empty] | 639 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南～忠孝二路(1520) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0858 |  | 0132 | 2-35-10 |  | 2-04 | 台南忠孝二路1520 79 RY U/L |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1520_79UL | 台南忠孝二路(1520) 79RY U/L | LINE161 | [5 empty] | 640 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南～忠孝二路(1520) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0859 |  | 0133 | 2-35-11 |  | 2-05 | 台南忠孝二路1520 第二套87RY U/L |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1520_87UL2 | 台南忠孝二路(1520)#287RY U/L | LINE161 | [5 empty] | 641 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝～延平線(1530) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0860 |  | 0134 | 2-35-12 |  | 2-06 | 忠孝延平線 1530 第一套87RY U/L |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1530_87UL1 | 忠孝延平線(1530)#187RY U/L | LINE161 | [5 empty] | 642 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝～延平線(1530) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0861 |  | 0135 | 2-35-13 |  | 2-07 | 忠孝延平線 1530 79 RY U/L |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1530_79UL | 忠孝延平線(1530) 79RY U/L | LINE161 | [5 empty] | 643 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝～延平線(1530) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0862 |  | 0136 | 2-35-14 |  | 2-08 | 忠孝延平線 1530 第二套87RY U/L |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.1530_87UL2 | 忠孝延平線(1530)#287RY U/L | LINE161 | [5 empty] | 644 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 161 | 161kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0576 |  | 0148 | 1-34-00 |  | 2-14 | 161KV #1BUS 87RY U/L |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | [5 empty] | 645 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 161 | 161kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0577 |  | 0149 | 1-34-01 |  | 2-15 | 161KV #2BUS 87RY U/L |  |  |  |  | B2/D18_A1 | [8 empty] | 忠孝DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | [5 empty] | 646 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE51 | 忠51線(KE51) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0768 |  | 0184 | 2-30-00 |  | 2-38 | 忠51線(KE51) 79S |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE51_79UL | 23KV忠51線(KE51) 79RY U/L | FEEDER | [5 empty] | 647 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE51 | 忠51線(KE51) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0769 |  | 0185 | 2-30-01 |  | 2-39 | 忠51線(KE51) 51NS |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE51_LCO_TAP | 23KV忠51線(KE51) LCO TAP | FEEDER | [5 empty] | 648 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE52 | 忠52線(KE52) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0770 |  | 0186 | 2-30-02 |  | 2-3A | 忠52線(KE52) 79S |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE52_79UL | 23KV忠52線(KE52) 79RY U/L | FEEDER | [5 empty] | 649 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE52 | 忠52線(KE52) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0771 |  | 0187 | 2-30-03 |  | 2-3B | 忠52線(KE52) 51NS |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE52_LCO_TAP | 23KV忠52線(KE52) LCO TAP | FEEDER | [5 empty] | 650 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE53 | 忠53線(KE53) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0772 |  | 0188 | 2-30-04 |  | 2-3C | 忠53線(KE53) 79S |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE53_79UL | 23KV忠53線(KE53) 79RY U/L | FEEDER | [5 empty] | 651 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE53 | 忠53線(KE53) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0773 |  | 0189 | 2-30-05 |  | 2-3D | 忠53線(KE53) 51NS |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE53_LCO_TAP | 23KV忠53線(KE53) LCO TAP | FEEDER | [5 empty] | 652 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE54 | 忠54線(KE54) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0774 |  | 0190 | 2-30-06 |  | 2-3E | 忠54線(KE54) 79S |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE54_79UL | 23KV忠54線(KE54) 79RY U/L | FEEDER | [5 empty] | 653 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE54 | 忠54線(KE54) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0775 |  | 0191 | 2-30-07 |  | 2-3F | 忠54線(KE54) 51NS |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE54_LCO_TAP | 23KV忠54線(KE54) LCO TAP | FEEDER | [5 empty] | 654 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE55 | 忠55線(KE55) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0776 |  | 0192 | 2-30-08 |  | 2-40 | 忠55線(KE55) 79S |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE55_79UL | 23KV忠55線(KE55) 79RY U/L | FEEDER | [5 empty] | 655 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE55 | 忠55線(KE55) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0777 |  | 0193 | 2-30-09 |  | 2-41 | 忠55線(KE55) 51NS |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE55_LCO_TAP | 23KV忠55線(KE55) LCO TAP | FEEDER | [5 empty] | 656 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE56 | 忠56線(KE56) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0778 |  | 0194 | 2-30-10 |  | 2-42 | 忠56線(KE56) 79S |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE56_79UL | 23KV忠56線(KE56) 79RY U/L | FEEDER | [5 empty] | 657 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE56 | 忠56線(KE56) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0779 |  | 0195 | 2-30-11 |  | 2-43 | 忠56線(KE56) 51NS |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE56_LCO_TAP | 23KV忠56線(KE56) LCO TAP | FEEDER | [5 empty] | 658 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE57 | 忠57線(KE57) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0780 |  | 0196 | 2-30-12 |  | 2-44 | 忠57線(KE57) 79S |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE57_79UL | 23KV忠57線(KE57) 79RY U/L | FEEDER | [5 empty] | 659 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE57 | 忠57線(KE57) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0781 |  | 0197 | 2-30-13 |  | 2-45 | 忠57線(KE57) 51NS |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE57_LCO_TAP | 23KV忠57線(KE57) LCO TAP | FEEDER | [5 empty] | 660 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE58 | 忠58線(KE58) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0782 |  | 0198 | 2-30-14 |  | 2-46 | 忠58線(KE58) 79S |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE58_79UL | 23KV忠58線(KE58) 79RY U/L | FEEDER | [5 empty] | 661 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE58 | 忠58線(KE58) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0783 |  | 0199 | 2-30-15 |  | 2-47 | 忠58線(KE58) 51NS |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE58_LCO_TAP | 23KV忠58線(KE58) LCO TAP | FEEDER | [5 empty] | 662 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE61 | 忠61線(KE61) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0784 |  | 0200 | 2-31-00 |  | 2-48 | 忠61線(KE61) 79S |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE61_79UL | 23KV忠61線(KE61) 79RY U/L | FEEDER | [5 empty] | 663 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE61 | 忠61線(KE61) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0785 |  | 0201 | 2-31-01 |  | 2-49 | 忠61線(KE61) 51NS |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE61_LCO_TAP | 23KV忠61線(KE61) LCO TAP | FEEDER | [5 empty] | 664 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE62 | 忠62線(KE62) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0786 |  | 0202 | 2-31-02 |  | 2-4A | 忠62線(KE62) 79S |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE62_79UL | 23KV忠62線(KE62) 79RY U/L | FEEDER | [5 empty] | 665 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE62 | 忠62線(KE62) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0787 |  | 0203 | 2-31-03 |  | 2-4B | 忠62線(KE62) 51NS |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE62_LCO_TAP | 23KV忠62線(KE62) LCO TAP | FEEDER | [5 empty] | 666 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE63 | 忠63線(KE63) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0788 |  | 0204 | 2-31-04 |  | 2-4C | 忠63線(KE63) 79S |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE63_79UL | 23KV忠63線(KE63) 79RY U/L | FEEDER | [5 empty] | 667 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE63 | 忠63線(KE63) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0789 |  | 0205 | 2-31-05 |  | 2-4D | 忠63線(KE63) 51NS |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE63_LCO_TAP | 23KV忠63線(KE63) LCO TAP | FEEDER | [5 empty] | 668 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE64 | 忠64線(KE64) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0790 |  | 0206 | 2-31-06 |  | 2-4E | 忠64線(KE64) 79S |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE64_79UL | 23KV忠64線(KE64) 79RY U/L | FEEDER | [5 empty] | 669 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE64 | 忠64線(KE64) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0791 |  | 0207 | 2-31-07 |  | 2-4F | 忠64線(KE64) 51NS |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE64_LCO_TAP | 23KV忠64線(KE64) LCO TAP | FEEDER | [5 empty] | 670 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE65 | 忠65線(KE65) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0792 |  | 0208 | 2-31-08 |  | 2-50 | 忠65線(KE65) 79S |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE65_79UL | 23KV忠65線(KE65) 79RY U/L | FEEDER | [5 empty] | 671 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE65 | 忠65線(KE65) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0793 |  | 0209 | 2-31-09 |  | 2-51 | 忠65線(KE65) 51NS |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE65_LCO_TAP | 23KV忠65線(KE65) LCO TAP | FEEDER | [5 empty] | 672 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE66 | 忠66線(KE66) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0794 |  | 0210 | 2-31-10 |  | 2-52 | 忠66線(KE66) 79S |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE66_79UL | 23KV忠66線(KE66) 79RY U/L | FEEDER | [5 empty] | 673 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE66 | 忠66線(KE66) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0795 |  | 0211 | 2-31-11 |  | 2-53 | 忠66線(KE66) 51NS |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE66_LCO_TAP | 23KV忠66線(KE66) LCO TAP | FEEDER | [5 empty] | 674 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE67 | 忠67線(KE67) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0796 |  | 0212 | 2-31-12 |  | 2-54 | 忠67線(KE67) 79S |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE67_79UL | 23KV忠67線(KE67) 79RY U/L | FEEDER | [5 empty] | 675 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE67 | 忠67線(KE67) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0797 |  | 0213 | 2-31-13 |  | 2-55 | 忠67線(KE67) 51NS |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE67_LCO_TAP | 23KV忠67線(KE67) LCO TAP | FEEDER | [5 empty] | 676 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE68 | 忠68線(KE68) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0798 |  | 0214 | 2-31-14 |  | 2-56 | 忠68線(KE68) 79S |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE68_79UL | 23KV忠68線(KE68) 79RY U/L | FEEDER | [5 empty] | 677 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE68 | 忠68線(KE68) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0799 |  | 0215 | 2-31-15 |  | 2-57 | 忠68線(KE68) 51NS |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE68_LCO_TAP | 23KV忠68線(KE68) LCO TAP | FEEDER | [5 empty] | 678 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE71 | 忠71線(KE71) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0800 |  | 0216 | 2-32-00 |  | 2-58 | 忠71線(KE71) 79S |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE71_79UL | 23KV忠71線(KE71) 79RY U/L | FEEDER | [5 empty] | 679 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE71 | 忠71線(KE71) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0801 |  | 0217 | 2-32-01 |  | 2-59 | 忠71線(KE71) 51NS |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE71_LCO_TAP | 23KV忠71線(KE71) LCO TAP | FEEDER | [5 empty] | 680 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE72 | 忠72線(KE72) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0802 |  | 0218 | 2-32-02 |  | 2-5A | 忠72線(KE72) 79S |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE72_79UL | 23KV忠72線(KE72) 79RY U/L | FEEDER | [5 empty] | 681 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE72 | 忠72線(KE72) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0803 |  | 0219 | 2-32-03 |  | 2-5B | 忠72線(KE72) 51NS |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE72_LCO_TAP | 23KV忠72線(KE72) LCO TAP | FEEDER | [5 empty] | 682 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE73 | 忠73線(KE73) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0804 |  | 0220 | 2-32-04 |  | 2-5C | 忠73線(KE73) 79S |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE73_79UL | 23KV忠73線(KE73) 79RY U/L | FEEDER | [5 empty] | 683 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE73 | 忠73線(KE73) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0805 |  | 0221 | 2-32-05 |  | 2-5D | 忠73線(KE73) 51NS |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE73_LCO_TAP | 23KV忠73線(KE73) LCO TAP | FEEDER | [5 empty] | 684 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE74 | 忠74線(KE74) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0806 |  | 0222 | 2-32-06 |  | 2-5E | 忠74線(KE74) 79S |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE74_79UL | 23KV忠74線(KE74) 79RY U/L | FEEDER | [5 empty] | 685 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE74 | 忠74線(KE74) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0807 |  | 0223 | 2-32-07 |  | 2-5F | 忠74線(KE74) 51NS |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE74_LCO_TAP | 23KV忠74線(KE74) LCO TAP | FEEDER | [5 empty] | 686 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE75 | 忠75線(KE75) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0808 |  | 0224 | 2-32-08 |  | 2-60 | 忠75線(KE75) 79S |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE75_79UL | 23KV忠75線(KE75) 79RY U/L | FEEDER | [5 empty] | 687 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE75 | 忠75線(KE75) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0809 |  | 0225 | 2-32-09 |  | 2-61 | 忠75線(KE75) 51NS |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE75_LCO_TAP | 23KV忠75線(KE75) LCO TAP | FEEDER | [5 empty] | 688 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE76 | 忠76線(KE76) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0810 |  | 0226 | 2-32-10 |  | 2-62 | 忠76線(KE76) 79S |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE76_79UL | 23KV忠76線(KE76) 79RY U/L | FEEDER | [5 empty] | 689 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE76 | 忠76線(KE76) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0811 |  | 0227 | 2-32-11 |  | 2-63 | 忠76線(KE76) 51NS |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE76_LCO_TAP | 23KV忠76線(KE76) LCO TAP | FEEDER | [5 empty] | 690 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE77 | 忠77線(KE77) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0812 |  | 0228 | 2-32-12 |  | 2-64 | 忠77線(KE77) 79S |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE77_79UL | 23KV忠77線(KE77) 79RY U/L | FEEDER | [5 empty] | 691 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE77 | 忠77線(KE77) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0813 |  | 0229 | 2-32-13 |  | 2-65 | 忠77線(KE77) 51NS |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE77_LCO_TAP | 23KV忠77線(KE77) LCO TAP | FEEDER | [5 empty] | 692 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE78 | 忠78線(KE78) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0814 |  | 0230 | 2-32-14 |  | 2-66 | 忠78線(KE78) 79S |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE78_79UL | 23KV忠78線(KE78) 79RY U/L | FEEDER | [5 empty] | 693 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE78 | 忠78線(KE78) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0815 |  | 0231 | 2-32-15 |  | 2-67 | 忠78線(KE78) 51NS |  |  |  |  | B2/D18_D1 | [8 empty] | 忠孝DS.KE78_LCO_TAP | 23KV忠78線(KE78) LCO TAP | FEEDER | [5 empty] | 694 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | 81UL |  | B3 | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0848 |  | 0248 | 2-35-00 |  | 2-78 | 310(M1A) 81RY U/L |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.310_81UL | #1DTR(310) 81RY U/L | OTHER | [5 empty] | 695 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | 81UL |  | B3 | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0849 |  | 0249 | 2-35-01 |  | 2-79 | 320(M1B) 81RY U/L |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.320_81UL | #1DTR(320) 81RY U/L | OTHER | [5 empty] | 696 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | 81UL |  | B3 | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0850 |  | 0250 | 2-35-02 |  | 2-7A | 330(M2A) 81RY U/L |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.330_81UL | #2DTR(330) 81RY U/L | OTHER | [5 empty] | 697 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | 81UL |  | B3 | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0851 |  | 0251 | 2-35-03 |  | 2-7B | 340(M2B) 81RY U/L |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.340_81UL | #2DTR(340) 81RY U/L | OTHER | [5 empty] | 698 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | 81UL |  | B3 | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0852 |  | 0252 | 2-35-04 |  | 2-7C | 350(M3A) 81RY U/L |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.350_81UL | #3DTR(350) 81RY U/L | OTHER | [5 empty] | 699 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | 81UL |  | B3 | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0853 |  | 0253 | 2-35-05 |  | 2-7D | 360(M3B) 81RY U/L |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.360_81UL | #3DTR(360) 81RY U/L | OTHER | [5 empty] | 700 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D18 | 忠孝DS | 0 |  | ComPoint |  |  | OLTC_A | OLTC 15分鐘連動3次 | INSERT | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0635 |  |  | 1-37-11 |  |  | Locate Empty |  |  |  |  | B3/D18_A1 | [8 empty] | 忠孝DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | [5 empty] | 701 | DNPDIPoint | DS058 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
D18 | 忠孝DS | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/D18_A1 | [12 empty] | 忠孝DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: D18/161/1BUS/V; OPRD2: D18/161/2BUS/V
D18 | 忠孝DS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/D18_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: D18/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
D18 | 忠孝DS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/D18_A1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_3 | OPRD1: D18/161/1510/MW; OPRD2: D18/161/1520/MW; OPRD3: D18/161/1530/MW
D18 | 忠孝DS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/D18_A1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: D18/0/CalcPoint/OPRN2_MW
D18 | 忠孝DS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/D18_A1 | [17 empty] | none
D18 | 忠孝DS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/D18_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: D18/0/CalcPoint/OPRN1; OPRD2: D18/0/CalcPoint/OPRN2; OPRD3: D18/0/CalcPoint/PRFL_UL
D18 | 忠孝DS |  |  | 1DTR | 1DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D18_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D18/22/310/I_R; OPRD2: D18/22/320/I_R
D18 | 忠孝DS |  |  | 1DTR | 1DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D18_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D18/22/310/I_S; OPRD2: D18/22/320/I_S
D18 | 忠孝DS |  |  | 1DTR | 1DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D18_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D18/22/310/I_T; OPRD2: D18/22/320/I_T
D18 | 忠孝DS |  |  | 2DTR | 2DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D18_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D18/22/330/I_R; OPRD2: D18/22/340/I_R
D18 | 忠孝DS |  |  | 2DTR | 2DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D18_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D18/22/330/I_S; OPRD2: D18/22/340/I_S
D18 | 忠孝DS |  |  | 2DTR | 2DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D18_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D18/22/330/I_T; OPRD2: D18/22/340/I_T
D18 | 忠孝DS |  |  | 3DTR | 3DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D18_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D18/22/350/I_R; OPRD2: D18/22/360/I_R
D18 | 忠孝DS |  |  | 3DTR | 3DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D18_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D18/22/350/I_S; OPRD2: D18/22/360/I_S
D18 | 忠孝DS |  |  | 3DTR | 3DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D18_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D18/22/350/I_T; OPRD2: D18/22/360/I_T
D18 | 忠孝DS | 161 | 161kV | 1510 | 台南～忠孝一路(1510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D18_A1 | [12 empty] | 忠孝DS.1510_AMP | 台南忠孝一路 AMP | LINE161 | AMP_CAL | C20R0964 | amp_cal | OPRD1: D18/161/1510/MW; OPRD2: D18/161/1510/MVAR; OPRD3: D18/0/CalcPoint/Vbs4
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南～忠孝二路(1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D18_A1 | [12 empty] | 忠孝DS.1520_AMP | 台南忠孝二路 AMP | LINE161 | AMP_CAL | C20R1930 | amp_cal | OPRD1: D18/161/1520/MW; OPRD2: D18/161/1520/MVAR; OPRD3: D18/0/CalcPoint/Vbs4
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝～延平線(1530) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D18_A1 | [12 empty] | 忠孝DS.1530_AMP | 忠孝延平線 AMP | LINE161 | AMP_CAL | C20R1930 | amp_cal | OPRD1: D18/161/1530/MW; OPRD2: D18/161/1530/MVAR; OPRD3: D18/0/CalcPoint/Vbs4
D18 | 忠孝DS | 22 | 22kV | 1ABUS | #1ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D18_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D18/22/1ABUS/V
D18 | 忠孝DS | 22 | 22kV | 1BBUS | #1BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D18_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D18/22/1BBUS/V
D18 | 忠孝DS | 22 | 22kV | 2ABUS | #2ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D18_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D18/22/2ABUS/V
D18 | 忠孝DS | 22 | 22kV | 2BBUS | #2BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D18_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D18/22/2BBUS/V
D18 | 忠孝DS | 22 | 22kV | 3ABUS | #3ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D18_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D18/22/3ABUS/V
D18 | 忠孝DS | 22 | 22kV | 3BBUS | #3BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D18_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D18/22/3BBUS/V
D18 | 忠孝DS |  |  | 1DTR | #1DTR |  | TR_PERM | [9 empty] | B1/D18_A1 | [12 empty] | 忠孝DS.#1DTR_PERM | #1DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D18//1DTR/SupLocal; OPRD2: D18//1DTR/Tap Chan
D18 | 忠孝DS |  |  | 2DTR | #2DTR |  | TR_PERM | [9 empty] | B1/D18_A1 | [12 empty] | 忠孝DS.#2DTR_PERM | #2DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D18//2DTR/SupLocal; OPRD2: D18//2DTR/Tap Chan
D18 | 忠孝DS |  |  | 3DTR | #3DTR |  | TR_PERM | [9 empty] | B1/D18_A1 | [12 empty] | 忠孝DS.#3DTR_PERM | #3DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D18//3DTR/SupLocal; OPRD2: D18//3DTR/Tap Chan
D18 | 忠孝DS | 22 | 22kV | KE51 | 忠51線(KE51) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D18/22/1ABUS/V; OPRD2: D18/22/KE51/I_R; OPRD3: D18/22/KE51/I_S; OPRD4: D18/22/KE51/I_T
D18 | 忠孝DS | 22 | 22kV | KE52 | 忠52線(KE52) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D18/22/1ABUS/V; OPRD2: D18/22/KE52/I_R; OPRD3: D18/22/KE52/I_S; OPRD4: D18/22/KE52/I_T
D18 | 忠孝DS | 22 | 22kV | KE53 | 忠53線(KE53) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D18/22/1ABUS/V; OPRD2: D18/22/KE53/I_R; OPRD3: D18/22/KE53/I_S; OPRD4: D18/22/KE53/I_T
D18 | 忠孝DS | 22 | 22kV | KE54 | 忠54線(KE54) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D18/22/1ABUS/V; OPRD2: D18/22/KE54/I_R; OPRD3: D18/22/KE54/I_S; OPRD4: D18/22/KE54/I_T
D18 | 忠孝DS | 22 | 22kV | KE55 | 忠55線(KE55) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D18/22/1BBUS/V; OPRD2: D18/22/KE55/I_R; OPRD3: D18/22/KE55/I_S; OPRD4: D18/22/KE55/I_T
D18 | 忠孝DS | 22 | 22kV | KE56 | 忠56線(KE56) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D18/22/1BBUS/V; OPRD2: D18/22/KE56/I_R; OPRD3: D18/22/KE56/I_S; OPRD4: D18/22/KE56/I_T
D18 | 忠孝DS | 22 | 22kV | KE57 | 忠57線(KE57) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D18/22/1BBUS/V; OPRD2: D18/22/KE57/I_R; OPRD3: D18/22/KE57/I_S; OPRD4: D18/22/KE57/I_T
D18 | 忠孝DS | 22 | 22kV | KE58 | 忠58線(KE58) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D18/22/1BBUS/V; OPRD2: D18/22/KE58/I_R; OPRD3: D18/22/KE58/I_S; OPRD4: D18/22/KE58/I_T
D18 | 忠孝DS | 22 | 22kV | KE61 | 忠61線(KE61) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D18/22/2ABUS/V; OPRD2: D18/22/KE61/I_R; OPRD3: D18/22/KE61/I_S; OPRD4: D18/22/KE61/I_T
D18 | 忠孝DS | 22 | 22kV | KE62 | 忠62線(KE62) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D18/22/2ABUS/V; OPRD2: D18/22/KE62/I_R; OPRD3: D18/22/KE62/I_S; OPRD4: D18/22/KE62/I_T
D18 | 忠孝DS | 22 | 22kV | KE63 | 忠63線(KE63) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D18/22/2ABUS/V; OPRD2: D18/22/KE63/I_R; OPRD3: D18/22/KE63/I_S; OPRD4: D18/22/KE63/I_T
D18 | 忠孝DS | 22 | 22kV | KE64 | 忠64線(KE64) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D18/22/2ABUS/V; OPRD2: D18/22/KE64/I_R; OPRD3: D18/22/KE64/I_S; OPRD4: D18/22/KE64/I_T
D18 | 忠孝DS | 22 | 22kV | KE65 | 忠65線(KE65) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D18/22/2BBUS/V; OPRD2: D18/22/KE65/I_R; OPRD3: D18/22/KE65/I_S; OPRD4: D18/22/KE65/I_T
D18 | 忠孝DS | 22 | 22kV | KE66 | 忠66線(KE66) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D18/22/2BBUS/V; OPRD2: D18/22/KE66/I_R; OPRD3: D18/22/KE66/I_S; OPRD4: D18/22/KE66/I_T
D18 | 忠孝DS | 22 | 22kV | KE67 | 忠67線(KE67) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D18/22/2BBUS/V; OPRD2: D18/22/KE67/I_R; OPRD3: D18/22/KE67/I_S; OPRD4: D18/22/KE67/I_T
D18 | 忠孝DS | 22 | 22kV | KE68 | 忠68線(KE68) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D18/22/2BBUS/V; OPRD2: D18/22/KE68/I_R; OPRD3: D18/22/KE68/I_S; OPRD4: D18/22/KE68/I_T
D18 | 忠孝DS | 22 | 22kV | KE71 | 忠71線(KE71) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D18/22/3ABUS/V; OPRD2: D18/22/KE71/I_R; OPRD3: D18/22/KE71/I_S; OPRD4: D18/22/KE71/I_T
D18 | 忠孝DS | 22 | 22kV | KE72 | 忠72線(KE72) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D18/22/3ABUS/V; OPRD2: D18/22/KE72/I_R; OPRD3: D18/22/KE72/I_S; OPRD4: D18/22/KE72/I_T
D18 | 忠孝DS | 22 | 22kV | KE73 | 忠73線(KE73) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D18/22/3ABUS/V; OPRD2: D18/22/KE73/I_R; OPRD3: D18/22/KE73/I_S; OPRD4: D18/22/KE73/I_T
D18 | 忠孝DS | 22 | 22kV | KE74 | 忠74線(KE74) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D18/22/3ABUS/V; OPRD2: D18/22/KE74/I_R; OPRD3: D18/22/KE74/I_S; OPRD4: D18/22/KE74/I_T
D18 | 忠孝DS | 22 | 22kV | KE75 | 忠75線(KE75) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D18/22/3BBUS/V; OPRD2: D18/22/KE75/I_R; OPRD3: D18/22/KE75/I_S; OPRD4: D18/22/KE75/I_T
D18 | 忠孝DS | 22 | 22kV | KE76 | 忠76線(KE76) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D18/22/3BBUS/V; OPRD2: D18/22/KE76/I_R; OPRD3: D18/22/KE76/I_S; OPRD4: D18/22/KE76/I_T
D18 | 忠孝DS | 22 | 22kV | KE77 | 忠77線(KE77) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D18/22/3BBUS/V; OPRD2: D18/22/KE77/I_R; OPRD3: D18/22/KE77/I_S; OPRD4: D18/22/KE77/I_T
D18 | 忠孝DS | 22 | 22kV | KE78 | 忠78線(KE78) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D18/22/3BBUS/V; OPRD2: D18/22/KE78/I_R; OPRD3: D18/22/KE78/I_S; OPRD4: D18/22/KE78/I_T
D18 | 忠孝DS | 22 | 22kV | KE51 | 忠51線(KE51) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D18/22/KE51/kVA; OPRD2: D18/22/KE51/KVAR
D18 | 忠孝DS | 22 | 22kV | KE52 | 忠52線(KE52) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D18/22/KE52/kVA; OPRD2: D18/22/KE52/KVAR
D18 | 忠孝DS | 22 | 22kV | KE53 | 忠53線(KE53) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D18/22/KE53/kVA; OPRD2: D18/22/KE53/KVAR
D18 | 忠孝DS | 22 | 22kV | KE54 | 忠54線(KE54) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D18/22/KE54/kVA; OPRD2: D18/22/KE54/KVAR
D18 | 忠孝DS | 22 | 22kV | KE55 | 忠55線(KE55) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D18/22/KE55/kVA; OPRD2: D18/22/KE55/KVAR
D18 | 忠孝DS | 22 | 22kV | KE56 | 忠56線(KE56) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D18/22/KE56/kVA; OPRD2: D18/22/KE56/KVAR
D18 | 忠孝DS | 22 | 22kV | KE57 | 忠57線(KE57) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D18/22/KE57/kVA; OPRD2: D18/22/KE57/KVAR
D18 | 忠孝DS | 22 | 22kV | KE58 | 忠58線(KE58) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D18/22/KE58/kVA; OPRD2: D18/22/KE58/KVAR
D18 | 忠孝DS | 22 | 22kV | KE61 | 忠61線(KE61) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D18/22/KE61/kVA; OPRD2: D18/22/KE61/KVAR
D18 | 忠孝DS | 22 | 22kV | KE62 | 忠62線(KE62) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D18/22/KE62/kVA; OPRD2: D18/22/KE62/KVAR
D18 | 忠孝DS | 22 | 22kV | KE63 | 忠63線(KE63) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D18/22/KE63/kVA; OPRD2: D18/22/KE63/KVAR
D18 | 忠孝DS | 22 | 22kV | KE64 | 忠64線(KE64) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D18/22/KE64/kVA; OPRD2: D18/22/KE64/KVAR
D18 | 忠孝DS | 22 | 22kV | KE65 | 忠65線(KE65) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D18/22/KE65/kVA; OPRD2: D18/22/KE65/KVAR
D18 | 忠孝DS | 22 | 22kV | KE66 | 忠66線(KE66) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D18/22/KE66/kVA; OPRD2: D18/22/KE66/KVAR
D18 | 忠孝DS | 22 | 22kV | KE67 | 忠67線(KE67) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D18/22/KE67/kVA; OPRD2: D18/22/KE67/KVAR
D18 | 忠孝DS | 22 | 22kV | KE68 | 忠68線(KE68) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D18/22/KE68/kVA; OPRD2: D18/22/KE68/KVAR
D18 | 忠孝DS | 22 | 22kV | KE71 | 忠71線(KE71) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D18/22/KE71/kVA; OPRD2: D18/22/KE71/KVAR
D18 | 忠孝DS | 22 | 22kV | KE72 | 忠72線(KE72) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D18/22/KE72/kVA; OPRD2: D18/22/KE72/KVAR
D18 | 忠孝DS | 22 | 22kV | KE73 | 忠73線(KE73) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D18/22/KE73/kVA; OPRD2: D18/22/KE73/KVAR
D18 | 忠孝DS | 22 | 22kV | KE74 | 忠74線(KE74) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D18/22/KE74/kVA; OPRD2: D18/22/KE74/KVAR
D18 | 忠孝DS | 22 | 22kV | KE75 | 忠75線(KE75) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D18/22/KE75/kVA; OPRD2: D18/22/KE75/KVAR
D18 | 忠孝DS | 22 | 22kV | KE76 | 忠76線(KE76) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D18/22/KE76/kVA; OPRD2: D18/22/KE76/KVAR
D18 | 忠孝DS | 22 | 22kV | KE77 | 忠77線(KE77) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D18/22/KE77/kVA; OPRD2: D18/22/KE77/KVAR
D18 | 忠孝DS | 22 | 22kV | KE78 | 忠78線(KE78) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D18_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D18/22/KE78/kVA; OPRD2: D18/22/KE78/KVAR
D18 | 忠孝DS | 22 | 22kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D18_A1 | [12 empty] | 忠孝DS.210_SC_MVAR | 23KV#1SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D18/22/210/CB; OPRD2: 13.8; OPRD3: 0
D18 | 忠孝DS | 22 | 22kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D18_A1 | [12 empty] | 忠孝DS.220_SC_MVAR | 23KV#2SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D18/22/220/CB; OPRD2: 13.8; OPRD3: 0
D18 | 忠孝DS | 22 | 22kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D18_A1 | [12 empty] | 忠孝DS.230_SC_MVAR | 23KV#3SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D18/22/230/CB; OPRD2: 13.8; OPRD3: 0
D18 | 忠孝DS | 22 | 22kV | 240 | #4SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D18_A1 | [12 empty] | 忠孝DS.240_SC_MVAR | 23KV#4SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D18/22/240/CB; OPRD2: 13.8; OPRD3: 0
D18 | 忠孝DS | 22 | 22kV | 250 | #5SC(250) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D18_A1 | [12 empty] | 忠孝DS.250_SC_MVAR | 23KV#5SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D18/22/250/CB; OPRD2: 13.8; OPRD3: 0
D18 | 忠孝DS | 22 | 22kV | 260 | #6SC(260) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D18_A1 | [12 empty] | 忠孝DS.260_SC_MVAR | 23KV#6SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D18/22/260/CB; OPRD2: 13.8; OPRD3: 0
D18 | 忠孝DS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/D18_A1 | [12 empty] | 忠孝DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_14 |  | com_alarm_44 | D18//1DTR/GDA | D18//1DTR/PHA | D18//1DTR/TRA | D18//1DTR/63Q | D18//1DTR/96D | D18//1DTR/96B2 | D18//1DTR/96B1 | D18//1DTR/87A | D18//1DTR/51ZA | D18//1DTR/96PA | D18//2DTR/63Q | D18//2DTR/GDA | D18//2DTR/96D | D18//2DTR/96B1 | D18//2DTR/96B2 | D18//2DTR/96PA | D18//2DTR/87A | D18//2DTR/TRA | D18//2DTR/PHA | D18//2DTR/51ZA | D18//3DTR/63Q | D18//3DTR/TRA | D18//3DTR/96B1 | D18//3DTR/96B2 | D18//3DTR/96D | D18//3DTR/51ZA | D18//3DTR/PHA | D18//3DTR/87A | D18//3DTR/96PA | D18//3DTR/GDA | D18/161/1BUS/87A | D18/161/2BUS/87A | D18/22/310/GDA | D18/22/310/PHA | D18/22/320/GDA | D18/22/320/PHA | D18/22/330/PHA | D18/22/330/GDA | D18/22/340/GDA | D18/22/340/PHA | D18/22/350/GDA | D18/22/350/PHA | D18/22/360/GDA | D18/22/360/PHA
D18 | 忠孝DS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/D18_A1 | [12 empty] | 忠孝DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | STATION_FAULT_3 |  | com_alarm_3 | OPRD1: D18//1DTR/TRF; OPRD2: D18//2DTR/TRF; OPRD3: D18//3DTR/TRF
D18 | 忠孝DS | 161 | 161kV | 1750_D1 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D18_D1 | [17 empty] | lamp2CC | OPRD1: D18/161/1750/CB
D18 | 忠孝DS | 161 | 161kV | 1760_D1 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D18_D1 | [17 empty] | lamp2CC | OPRD1: D18/161/1760/CB
D18 | 忠孝DS | 0 |  | StaDev_D1 | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D18_D1 | [17 empty] | lamp2CC | OPRD1: D18/0/StaDev/PMA
D18 | 忠孝DS | 161 | 161kV | 1770_D1 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D18_D1 | [17 empty] | lamp2CC | OPRD1: D18/161/1770/CB
D18 | 忠孝DS | 22 | 22kV | 310_D1 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D18_D1 | [17 empty] | lamp2CC | OPRD1: D18/22/310/CB
D18 | 忠孝DS | 22 | 22kV | 320_D1 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D18_D1 | [17 empty] | lamp2CC | OPRD1: D18/22/320/CB
D18 | 忠孝DS | 22 | 22kV | 330_D1 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D18_D1 | [17 empty] | lamp2CC | OPRD1: D18/22/330/CB
D18 | 忠孝DS | 22 | 22kV | 340_D1 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D18_D1 | [17 empty] | lamp2CC | OPRD1: D18/22/340/CB
D18 | 忠孝DS | 22 | 22kV | 350_D1 | #3DTR(A)(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D18_D1 | [17 empty] | lamp2CC | OPRD1: D18/22/350/CB
D18 | 忠孝DS | 22 | 22kV | 360_D1 | #3DTR(B)(360) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D18_D1 | [17 empty] | lamp2CC | OPRD1: D18/22/360/CB
D18 | 忠孝DS | 22 | 22kV | 310_D1 | #1DTR(A)(310) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/D18_D1 | [17 empty] | lamp2CC | OPRD1: D18/22/310/81A
D18 | 忠孝DS | 22 | 22kV | 320_D1 | #1DTR(B)(320) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/D18_D1 | [17 empty] | lamp2CC | OPRD1: D18/22/320/81A
D18 | 忠孝DS | 22 | 22kV | 330_D1 | #2DTR(A)(330) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/D18_D1 | [17 empty] | lamp2CC | OPRD1: D18/22/330/81A
D18 | 忠孝DS | 22 | 22kV | 340_D1 | #2DTR(B)(340) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/D18_D1 | [17 empty] | lamp2CC | OPRD1: D18/22/340/81A
D18 | 忠孝DS | 22 | 22kV | 350_D1 | #3DTR(A)(350) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/D18_D1 | [17 empty] | lamp2CC | OPRD1: D18/22/350/81A
D18 | 忠孝DS | 22 | 22kV | 360_D1 | #3DTR(B)(360) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/D18_D1 | [17 empty] | lamp2CC | OPRD1: D18/22/360/81A
D18 | 忠孝DS | 0 |  | RTU_D1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/D18_D1 | [17 empty] | lamp2CC | OPRD1: D18/0/RTU/RTU_R_L
D18 | 忠孝DS | 0 |  | StaDev_D1 | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/D18_D1 | [17 empty] | lamp2CC | OPRD1: D18/0/StaDev/STUV
D18 | 忠孝DS | 0 |  | StaDev_D1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D18_D1 | [17 empty] | lamp2CC | OPRD1: D18/0/StaDev/DCA
D18 | 忠孝DS | 0 |  | StaDev_D1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D18_D1 | [17 empty] | lamp2CC | OPRD1: D18/0/StaDev/DCE
D18 | 忠孝DS | 22 | 22kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D18_D1 | [17 empty] | lamp2CC | OPRD1: D18/22/ComPoint/CBA
D18 | 忠孝DS | 22 | 22kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | ELEM/D18_D1 | [17 empty] | lamp2CC | OPRD1: D18/22/ComPoint/CBF

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D18 | 忠孝DS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | D18/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
D18 | 忠孝DS | 161 | 161kV | 1510 | 台南忠孝一路(1510) |  | I | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.1510_AMP | 台南忠孝一路 AMP | LINE161 | D18/161/1510/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C20R0964 | 867.599976 | 867.599976 | 964.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南忠孝二路(1520) |  | I | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.1520_AMP | 台南忠孝二路 AMP | LINE161 | D18/161/1520/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C20R1930 | 1737.800049 | 1737.800049 | 1930.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝延平線(1530) |  | I | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.1530_AMP | 忠孝延平線 AMP | LINE161 | D18/161/1530/I |  | AMP_CAL |  |  | 5 | CalcAIPoint | [21 empty] | C20R1930 | 1737.800049 | 1737.800049 | 1930.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠51線KVA | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠51線KVA | 23KV忠51線KVA | FEEDER |  |  | KVA_CAL |  |  | 6 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠51線KW | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠51線KW | 23KV忠51線KW | FEEDER |  |  | KW_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠52線KVA | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠52線KVA | 23KV忠52線KVA | FEEDER |  |  | KVA_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠52線KW | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠52線KW | 23KV忠52線KW | FEEDER |  |  | KW_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠53線KVA | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠53線KVA | 23KV忠53線KVA | FEEDER |  |  | KVA_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠53線KW | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠53線KW | 23KV忠53線KW | FEEDER |  |  | KW_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠54線KVA | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠54線KVA | 23KV忠54線KVA | FEEDER |  |  | KVA_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠54線KW | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠54線KW | 23KV忠54線KW | FEEDER |  |  | KW_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠55線KVA | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠55線KVA | 23KV忠55線KVA | FEEDER |  |  | KVA_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠55線KW | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠55線KW | 23KV忠55線KW | FEEDER |  |  | KW_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠56線KVA | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠56線KVA | 23KV忠56線KVA | FEEDER |  |  | KVA_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠56線KW | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠56線KW | 23KV忠56線KW | FEEDER |  |  | KW_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠57線KVA | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠57線KVA | 23KV忠57線KVA | FEEDER |  |  | KVA_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠57線KW | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠57線KW | 23KV忠57線KW | FEEDER |  |  | KW_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠58線KVA | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠58線KVA | 23KV忠58線KVA | FEEDER |  |  | KVA_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠58線KW | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠58線KW | 23KV忠58線KW | FEEDER |  |  | KW_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠61線KVA | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠61線KVA | 23KV忠61線KVA | FEEDER |  |  | KVA_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠61線KW | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠61線KW | 23KV忠61線KW | FEEDER |  |  | KW_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠62線KVA | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠62線KVA | 23KV忠62線KVA | FEEDER |  |  | KVA_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠62線KW | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠62線KW | 23KV忠62線KW | FEEDER |  |  | KW_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠63線KVA | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠63線KVA | 23KV忠63線KVA | FEEDER |  |  | KVA_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠63線KW | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠63線KW | 23KV忠63線KW | FEEDER |  |  | KW_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠64線KVA | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠64線KVA | 23KV忠64線KVA | FEEDER |  |  | KVA_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠64線KW | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠64線KW | 23KV忠64線KW | FEEDER |  |  | KW_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠65線KVA | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠65線KVA | 23KV忠65線KVA | FEEDER |  |  | KVA_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠65線KW | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠65線KW | 23KV忠65線KW | FEEDER |  |  | KW_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠66線KVA | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠66線KVA | 23KV忠66線KVA | FEEDER |  |  | KVA_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠66線KW | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠66線KW | 23KV忠66線KW | FEEDER |  |  | KW_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠67線KVA | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠67線KVA | 23KV忠67線KVA | FEEDER |  |  | KVA_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠67線KW | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠67線KW | 23KV忠67線KW | FEEDER |  |  | KW_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠68線KVA | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠68線KVA | 23KV忠68線KVA | FEEDER |  |  | KVA_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠68線KW | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠68線KW | 23KV忠68線KW | FEEDER |  |  | KW_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠71線KVA | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠71線KVA | 23KV忠71線KVA | FEEDER |  |  | KVA_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠71線KW | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠71線KW | 23KV忠71線KW | FEEDER |  |  | KW_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠72線KVA | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠72線KVA | 23KV忠72線KVA | FEEDER |  |  | KVA_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠72線KW | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠72線KW | 23KV忠72線KW | FEEDER |  |  | KW_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠73線KVA | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠73線KVA | 23KV忠73線KVA | FEEDER |  |  | KVA_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠73線KW | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠73線KW | 23KV忠73線KW | FEEDER |  |  | KW_CAL |  |  | 43 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠74線KVA | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠74線KVA | 23KV忠74線KVA | FEEDER |  |  | KVA_CAL |  |  | 44 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠74線KW | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠74線KW | 23KV忠74線KW | FEEDER |  |  | KW_CAL |  |  | 45 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠75線KVA | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠75線KVA | 23KV忠75線KVA | FEEDER |  |  | KVA_CAL |  |  | 46 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠75線KW | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠75線KW | 23KV忠75線KW | FEEDER |  |  | KW_CAL |  |  | 47 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠76線KVA | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠76線KVA | 23KV忠76線KVA | FEEDER |  |  | KVA_CAL |  |  | 48 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠76線KW | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠76線KW | 23KV忠76線KW | FEEDER |  |  | KW_CAL |  |  | 49 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠77線KVA | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠77線KVA | 23KV忠77線KVA | FEEDER |  |  | KVA_CAL |  |  | 50 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠77線KW | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠77線KW | 23KV忠77線KW | FEEDER |  |  | KW_CAL |  |  | 51 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠78線KVA | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠78線KVA | 23KV忠78線KVA | FEEDER |  |  | KVA_CAL |  |  | 52 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  |  |  |  | 忠78線KW | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.忠78線KW | 23KV忠78線KW | FEEDER |  |  | KW_CAL |  |  | 53 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#1DTR(A)_MVA | #1DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 54 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D18 | 忠孝DS | 0 |  | 1DTR(A) | #1DTR(A) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#1DTR(A)_LOAD | #1DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 55 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D18 | 忠孝DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PF | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#1DTR(A)_PF | #1DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 56 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D18 | 忠孝DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#1DTR(B)_MVA | #1DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 57 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D18 | 忠孝DS | 0 |  | 1DTR(B) | #1DTR(B) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#1DTR(B)_LOAD | #1DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 58 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D18 | 忠孝DS | 0 |  | 1DTR(B) | #1DTR(B) |  | PF | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#1DTR(B)_PF | #1DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 59 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D18 | 忠孝DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#2DTR(A)_MVA | #2DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 60 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D18 | 忠孝DS | 0 |  | 2DTR(A) | #2DTR(A) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#2DTR(A)_LOAD | #2DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 61 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D18 | 忠孝DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PF | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#2DTR(A)_PF | #2DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 62 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D18 | 忠孝DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#2DTR(B)_MVA | #2DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 63 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D18 | 忠孝DS | 0 |  | 2DTR(B) | #2DTR(B) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#2DTR(B)_LOAD | #2DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 64 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D18 | 忠孝DS | 0 |  | 2DTR(B) | #2DTR(B) |  | PF | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#2DTR(B)_PF | #2DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 65 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D18 | 忠孝DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#3DTR(A)_MVA | #3DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 66 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D18 | 忠孝DS | 0 |  | 3DTR(A) | #3DTR(A) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#3DTR(A)_LOAD | #3DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 67 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D18 | 忠孝DS | 0 |  | 3DTR(A) | #3DTR(A) |  | PF | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#3DTR(A)_PF | #3DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 68 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D18 | 忠孝DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#3DTR(B)_MVA | #3DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 69 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D18 | 忠孝DS | 0 |  | 3DTR(B) | #3DTR(B) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#3DTR(B)_LOAD | #3DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 70 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D18 | 忠孝DS | 0 |  | 3DTR(B) | #3DTR(B) |  | PF | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#3DTR(B)_PF | #3DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 71 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D18 | 忠孝DS | 0 |  | 1DTR | #1DTR |  | MW | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#1DTR_MW | #1DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 72 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  | 1DTR | #1DTR |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#1DTR_MVAR | #1DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 73 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  | 1DTR | #1DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#1DTR_MVA | #1DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 74 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D18 | 忠孝DS | 0 |  | 1DTR | #1DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#1DTR_LOAD | #1DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 75 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D18 | 忠孝DS | 0 |  | 1DTR | #1DTR |  | PF | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#1DTR_PF | #1DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 76 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D18 | 忠孝DS | 0 |  | 2DTR | #2DTR |  | MW | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#2DTR_MW | #2DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 77 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  | 2DTR | #2DTR |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#2DTR_MVAR | #2DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 78 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  | 2DTR | #2DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#2DTR_MVA | #2DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 79 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D18 | 忠孝DS | 0 |  | 2DTR | #2DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#2DTR_LOAD | #2DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 80 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D18 | 忠孝DS | 0 |  | 2DTR | #2DTR |  | PF | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#2DTR_PF | #2DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 81 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D18 | 忠孝DS | 0 |  | 3DTR | #3DTR |  | MW | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#3DTR_MW | #3DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 82 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  | 3DTR | #3DTR |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#3DTR_MVAR | #3DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 83 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  | 3DTR | #3DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#3DTR_MVA | #3DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 84 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D18 | 忠孝DS | 0 |  | 3DTR | #3DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#3DTR_LOAD | #3DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 85 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D18 | 忠孝DS | 0 |  | 3DTR | #3DTR |  | PF | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#3DTR_PF | #3DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 86 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D18 | 忠孝DS | 22 | 22kV | 210_SC | #1SC | 9 | MVAR | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.210_SC_MVAR | 23KV#1SC MVAR | SC | D18/22/210/MVAR |  | SC_CAL_23 |  |  | 87 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 22 | 22kV | 220_SC | #2SC | 9 | MVAR | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.220_SC_MVAR | 23KV#2SC MVAR | SC | D18/22/220/MVAR |  | SC_CAL_23 |  |  | 88 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 22 | 22kV | 230_SC | #3SC | 9 | MVAR | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.230_SC_MVAR | 23KV#3SC MVAR | SC | D18/22/230/MVAR |  | SC_CAL_23 |  |  | 89 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 22 | 22kV | 240_SC | #4SC | 9 | MVAR | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.240_SC_MVAR | 23KV#4SC MVAR | SC | D18/22/240/MVAR |  | SC_CAL_23 |  |  | 90 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 22 | 22kV | 250_SC | #5SC | 9 | MVAR | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.250_SC_MVAR | 23KV#5SC MVAR | SC | D18/22/250/MVAR |  | SC_CAL_23 |  |  | 91 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 22 | 22kV | 260_SC | #6SC | 9 | MVAR | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.260_SC_MVAR | 23KV#6SC MVAR | SC | D18/22/260/MVAR |  | SC_CAL_23 |  |  | 92 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  | TRTOT | 忠孝主變瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 忠孝DS.TRTOT_MW | 忠孝主變瞬時供電量 MW |  |  |  | TOTAL_PQ_CAL_3 |  |  | 93 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  | TRTOT | 忠孝主變瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 忠孝DS.TRTOT_MVAR | 忠孝主變瞬時供電量 MVAR |  |  |  | TOTAL_PQ_CAL_3 |  |  | 94 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 22 | 22kV | 1BUS | #1BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.23KV#1BUS_KV | 23KV #1BUS BEST SOURCE | BUS |  |  | BEST_1W2CB |  |  | 95 | CalcAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D18 | 忠孝DS | 22 | 22kV | 2BUS | #2BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.23KV#2BUS_KV | 23KV #2BUS BEST SOURCE | BUS |  |  | BEST_1W2CB |  |  | 96 | CalcAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D18 | 忠孝DS | 22 | 22kV | 3BUS | #3BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.23KV#3BUS_KV | 23KV #3BUS BEST SOURCE | BUS |  |  | BEST_1W2CB |  |  | 97 | CalcAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D18 | 忠孝DS | 161 | 161kV | 1950_SHR | #1SHR |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.1950_SHR_MVAR | 161KV#1SHR MVAR | SC |  |  | SHR_CAL_324_5 |  |  | 98 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 0 |  | 100_CB | 100(100_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.100_CB_4 | 100 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 99 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | 200_CB | 200(200_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.200_CB_4 | 200 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 100 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | 300_CB | 300(300_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.300_CB_4 | 300 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 101 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 22 | 22kV | 11__CBA | 11/斷路器重故障(11__CBA) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.11/23KV_CBA_4 | 11/23KV斷路器重故障 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 102 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 11__CBF | 11/斷路器輕故障(11__CBF) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.11/23KV_CBF_4 | 11/23KV斷路器輕故障 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 103 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | _SC_60A | 11/ SC |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.23KV_SC_60A_4 | 11/23KV SC 60A (D4) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 104 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | RTU_S_L | RTU |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 忠孝DS.RTU_S/L_4 | RTU SUPY/LOCAL (D4) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 105 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D18 | 忠孝DS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | D18/0/CalcPoint/SUBA |  | STATION_FAULT_14 |  |  | 106 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 變電所輕故障點燈 | 變電所輕故障點燈 |  | SUBF | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | D18/0/CalcPoint/SUBF |  | STATION_FAULT_3 |  |  | 107 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1510_AMP | 台南忠孝一路 | [27 empty] | ADCS_S | [8 empty] | 忠孝DS.1510_AMP_A | 台南忠孝一路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 108 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1520_AMP | 台南忠孝二路 | [27 empty] | ADCS_S | [8 empty] | 忠孝DS.1520_AMP_A | 台南忠孝二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 109 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1530_AMP | 忠孝延平線 | [27 empty] | ADCS_S | [8 empty] | 忠孝DS.1530_AMP_A | 忠孝延平線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 110 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D18 | 忠孝DS | 0 |  | 1DTR | #1DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#1DTR_PERM | #1DTR TAP PERMISSION POINT | MTR | D18//1DTR/TR_PERM |  | DTR_PERM |  |  | 111 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D18 | 忠孝DS | 0 |  | 2DTR | #2DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#2DTR_PERM | #2DTR TAP PERMISSION POINT | MTR | D18//2DTR/TR_PERM |  | DTR_PERM |  |  | 112 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D18 | 忠孝DS | 0 |  | 3DTR | #3DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.#3DTR_PERM | #3DTR TAP PERMISSION POINT | MTR | D18//3DTR/TR_PERM |  | DTR_PERM |  |  | 113 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D18 | 忠孝DS | 0 |  | 1DTR_MVA | #1DTR | [27 empty] | ADCS_S | [8 empty] | 忠孝DS.#1DTR_MVA_A | #1DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 114 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D18 | 忠孝DS | 0 |  | 2DTR_MVA | #2DTR | [27 empty] | ADCS_S | [8 empty] | 忠孝DS.#2DTR_MVA_A | #2DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 115 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D18 | 忠孝DS | 0 |  | 3DTR_MVA | #3DTR | [27 empty] | ADCS_S | [8 empty] | 忠孝DS.#3DTR_MVA_A | #3DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 116 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D18 | 忠孝DS | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_DS |  |  | 117 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 1ABUS | #1ABUS |  | 23KV#1ABUSC | [25 empty] | CDCS | [8 empty] | 忠孝DS.23KV#1ABUSC | #1ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 118 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D18 | 忠孝DS | 0 |  | 1BBUS | #1BBUS |  | 23KV#1BBUSC | [25 empty] | CDCS | [8 empty] | 忠孝DS.23KV#1BBUSC | #1BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 119 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D18 | 忠孝DS | 0 |  | 2ABUS | #2ABUS |  | 23KV#2ABUSC | [25 empty] | CDCS | [8 empty] | 忠孝DS.23KV#2ABUSC | #2ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 120 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D18 | 忠孝DS | 0 |  | 2BBUS | #2BBUS |  | 23KV#2BBUSC | [25 empty] | CDCS | [8 empty] | 忠孝DS.23KV#2BBUSC | #2BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 121 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D18 | 忠孝DS | 0 |  | 3ABUS | #3ABUS |  | 23KV#3ABUSC | [25 empty] | CDCS | [8 empty] | 忠孝DS.23KV#3ABUSC | #3ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 122 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D18 | 忠孝DS | 0 |  | 3BBUS | #3BBUS |  | 23KV#3BBUSC | [25 empty] | CDCS | [8 empty] | 忠孝DS.23KV#3BBUSC | #3BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 123 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D18 | 忠孝DS | 0 |  | TAP_OVER | TAP |  | SET | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.TAP_OVER_SET | TAP OVER HI/LO ALARM | MTR |  |  | 5000_CB_T3 |  |  | 124 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D18 | 忠孝DS | 0 |  | BUS_OVER | BUS |  | SET | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.BUS_OVER_SET | BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B6 |  |  | 125 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D18 | 忠孝DS | 0 |  | 5000 | 虛擬5000 |  | CB動作 | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.5000_CB動作 | 虛擬5000 CB動作,請查明原因處理 | MTR |  |  | 5000_CB_M |  |  | 126 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 注意OLTC | 注意OLTC |  | BUS電壓異常 | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.BUS電壓異常 | 注意OLTC Tap位置,並將RPDC閉鎖 | OTHER |  |  | STATION_FAULT_2 |  |  | 127 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1BUS | #1BUS |  | V | [14 empty] | 0002 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | D18/161/1BUS/V |  |  |  | DNP | 128 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D18 | 忠孝DS | 161 | 161kV | 2BUS | #2BUS |  | V | [14 empty] | 0003 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | D18/161/2BUS/V |  |  |  | DNP | 129 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D18 | 忠孝DS | 22 | 22kV | 1ABUS | #1ABUS |  | V | [14 empty] | 0133 | [8 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.23KV#1ABUS_KV | 23KV #1ABUS KV | BUS | D18/22/1ABUS/V |  |  |  | DNP | 130 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D18 | 忠孝DS | 22 | 22kV | 1BBUS | #1BBUS |  | V | [14 empty] | 0159 | [8 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.23KV#1BBUS_KV | 23KV #1BBUS KV | BUS | D18/22/1BBUS/V |  |  |  | DNP | 131 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D18 | 忠孝DS | 22 | 22kV | 2ABUS | #2ABUS |  | V | [14 empty] | 0188 | [8 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.23KV#2ABUS_KV | 23KV #2ABUS KV | BUS | D18/22/2ABUS/V |  |  |  | DNP | 132 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D18 | 忠孝DS | 22 | 22kV | 2BBUS | #2BBUS |  | V | [14 empty] | 0214 | [8 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.23KV#2BBUS_KV | 23KV #2BBUS KV | BUS | D18/22/2BBUS/V |  |  |  | DNP | 133 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D18 | 忠孝DS | 22 | 22kV | 3ABUS | #3ABUS |  | V | [14 empty] | 0243 | [8 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.23KV#3ABUS_KV | 23KV #3ABUS KV | BUS | D18/22/3ABUS/V |  |  |  | DNP | 134 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D18 | 忠孝DS | 22 | 22kV | 3BBUS | #3BBUS |  | V | [14 empty] | 0269 | [8 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.23KV#3BBUS_KV | 23KV #3BBUS KV | BUS | D18/22/3BBUS/V |  |  |  | DNP | 135 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D18 | 忠孝DS | 161 | 161kV | 1510 | 台南忠孝一路(1510) |  | MW | [14 empty] | 0004 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.1510_MW | 台南忠孝一路 MW | LINE161 | D18/161/1510/MW |  |  |  | DNP | 136 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D18 | 忠孝DS | 161 | 161kV | 1510 | 台南忠孝一路(1510) |  | MVAR | [14 empty] | 0005 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.1510_MVAR | 台南忠孝一路 MVAR | LINE161 | D18/161/1510/MVAR |  |  |  | DNP | 137 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南忠孝二路(1520) |  | MW | [14 empty] | 0006 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.1520_MW | 台南忠孝二路 MW | LINE161 | D18/161/1520/MW |  |  |  | DNP | 138 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南忠孝二路(1520) |  | MVAR | [14 empty] | 0007 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.1520_MVAR | 台南忠孝二路 MVAR | LINE161 | D18/161/1520/MVAR |  |  |  | DNP | 139 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝延平線(1530) |  | MW | [14 empty] | 0008 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.1530_MW | 忠孝延平線 MW | LINE161 | D18/161/1530/MW |  |  |  | DNP | 140 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝延平線(1530) |  | MVAR | [14 empty] | 0009 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.1530_MVAR | 忠孝延平線 MVAR | LINE161 | D18/161/1530/MVAR |  |  |  | DNP | 141 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠51線 | 忠51線 |  | 忠51線KVAR | [14 empty] | 0134 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠51線KVAR | 23KV忠51線 KVAR | FEEDER | D18/22/KE51/KVAR |  |  |  | DNP | 142 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠51線 | 忠51線 |  | 忠51線A1 | [14 empty] | 0135 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠51線A1 | 23KV忠51線 R相AMP | FEEDER | D18/22/KE51/I_R |  |  |  | DNP | 143 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠51線 | 忠51線 |  | 忠51線A2 | [14 empty] | 0136 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠51線A2 | 23KV忠51線 S相AMP | FEEDER | D18/22/KE51/I_S |  |  |  | DNP | 144 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠51線 | 忠51線 |  | 忠51線A3 | [14 empty] | 0137 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠51線A3 | 23KV忠51線 T相AMP | FEEDER | D18/22/KE51/I_T |  |  |  | DNP | 145 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠51線 | 忠51線 |  | 忠51線A0 | [14 empty] | 0138 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠51線A0 | 23KV忠51線 N相AMP | FEEDER | D18/22/KE51/I_N |  |  |  | DNP | 146 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠52線 | 忠52線 |  | 忠52線KVAR | [14 empty] | 0139 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠52線KVAR | 23KV忠52線 KVAR | FEEDER | D18/22/KE52/KVAR |  |  |  | DNP | 147 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠52線 | 忠52線 |  | 忠52線A1 | [14 empty] | 0140 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠52線A1 | 23KV忠52線 R相AMP | FEEDER | D18/22/KE52/I_R |  |  |  | DNP | 148 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠52線 | 忠52線 |  | 忠52線A2 | [14 empty] | 0141 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠52線A2 | 23KV忠52線 S相AMP | FEEDER | D18/22/KE52/I_S |  |  |  | DNP | 149 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠52線 | 忠52線 |  | 忠52線A3 | [14 empty] | 0142 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠52線A3 | 23KV忠52線 T相AMP | FEEDER | D18/22/KE52/I_T |  |  |  | DNP | 150 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠52線 | 忠52線 |  | 忠52線A0 | [14 empty] | 0143 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠52線A0 | 23KV忠52線 N相AMP | FEEDER | D18/22/KE52/I_N |  |  |  | DNP | 151 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠53線 | 忠53線 |  | 忠53線KVAR | [14 empty] | 0144 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠53線KVAR | 23KV忠53線 KVAR | FEEDER | D18/22/KE53/KVAR |  |  |  | DNP | 152 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠53線 | 忠53線 |  | 忠53線A1 | [14 empty] | 0145 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠53線A1 | 23KV忠53線 R相AMP | FEEDER | D18/22/KE53/I_R |  |  |  | DNP | 153 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠53線 | 忠53線 |  | 忠53線A2 | [14 empty] | 0146 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠53線A2 | 23KV忠53線 S相AMP | FEEDER | D18/22/KE53/I_S |  |  |  | DNP | 154 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠53線 | 忠53線 |  | 忠53線A3 | [14 empty] | 0147 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠53線A3 | 23KV忠53線 T相AMP | FEEDER | D18/22/KE53/I_T |  |  |  | DNP | 155 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠53線 | 忠53線 |  | 忠53線A0 | [14 empty] | 0148 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠53線A0 | 23KV忠53線 N相AMP | FEEDER | D18/22/KE53/I_N |  |  |  | DNP | 156 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠54線 | 忠54線 |  | 忠54線KVAR | [14 empty] | 0149 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠54線KVAR | 23KV忠54線 KVAR | FEEDER | D18/22/KE54/KVAR |  |  |  | DNP | 157 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠54線 | 忠54線 |  | 忠54線A1 | [14 empty] | 0150 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠54線A1 | 23KV忠54線 R相AMP | FEEDER | D18/22/KE54/I_R |  |  |  | DNP | 158 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠54線 | 忠54線 |  | 忠54線A2 | [14 empty] | 0151 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠54線A2 | 23KV忠54線 S相AMP | FEEDER | D18/22/KE54/I_S |  |  |  | DNP | 159 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠54線 | 忠54線 |  | 忠54線A3 | [14 empty] | 0152 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠54線A3 | 23KV忠54線 T相AMP | FEEDER | D18/22/KE54/I_T |  |  |  | DNP | 160 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠54線 | 忠54線 |  | 忠54線A0 | [14 empty] | 0153 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠54線A0 | 23KV忠54線 N相AMP | FEEDER | D18/22/KE54/I_N |  |  |  | DNP | 161 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠55線 | 忠55線 |  | 忠55線KVAR | [14 empty] | 0160 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠55線KVAR | 23KV忠55線 KVAR | FEEDER | D18/22/KE55/KVAR |  |  |  | DNP | 162 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠55線 | 忠55線 |  | 忠55線A1 | [14 empty] | 0161 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠55線A1 | 23KV忠55線 R相AMP | FEEDER | D18/22/KE55/I_R |  |  |  | DNP | 163 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠55線 | 忠55線 |  | 忠55線A2 | [14 empty] | 0162 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠55線A2 | 23KV忠55線 S相AMP | FEEDER | D18/22/KE55/I_S |  |  |  | DNP | 164 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠55線 | 忠55線 |  | 忠55線A3 | [14 empty] | 0163 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠55線A3 | 23KV忠55線 T相AMP | FEEDER | D18/22/KE55/I_T |  |  |  | DNP | 165 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠55線 | 忠55線 |  | 忠55線A0 | [14 empty] | 0164 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠55線A0 | 23KV忠55線 N相AMP | FEEDER | D18/22/KE55/I_N |  |  |  | DNP | 166 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠56線 | 忠56線 |  | 忠56線KVAR | [14 empty] | 0165 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠56線KVAR | 23KV忠56線 KVAR | FEEDER | D18/22/KE56/KVAR |  |  |  | DNP | 167 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠56線 | 忠56線 |  | 忠56線A1 | [14 empty] | 0166 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠56線A1 | 23KV忠56線 R相AMP | FEEDER | D18/22/KE56/I_R |  |  |  | DNP | 168 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠56線 | 忠56線 |  | 忠56線A2 | [14 empty] | 0167 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠56線A2 | 23KV忠56線 S相AMP | FEEDER | D18/22/KE56/I_S |  |  |  | DNP | 169 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠56線 | 忠56線 |  | 忠56線A3 | [14 empty] | 0168 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠56線A3 | 23KV忠56線 T相AMP | FEEDER | D18/22/KE56/I_T |  |  |  | DNP | 170 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠56線 | 忠56線 |  | 忠56線A0 | [14 empty] | 0169 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠56線A0 | 23KV忠56線 N相AMP | FEEDER | D18/22/KE56/I_N |  |  |  | DNP | 171 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠57線 | 忠57線 |  | 忠57線KVAR | [14 empty] | 0170 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠57線KVAR | 23KV忠57線 KVAR | FEEDER | D18/22/KE57/KVAR |  |  |  | DNP | 172 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠57線 | 忠57線 |  | 忠57線A1 | [14 empty] | 0171 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠57線A1 | 23KV忠57線 R相AMP | FEEDER | D18/22/KE57/I_R |  |  |  | DNP | 173 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠57線 | 忠57線 |  | 忠57線A2 | [14 empty] | 0172 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠57線A2 | 23KV忠57線 S相AMP | FEEDER | D18/22/KE57/I_S |  |  |  | DNP | 174 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠57線 | 忠57線 |  | 忠57線A3 | [14 empty] | 0173 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠57線A3 | 23KV忠57線 T相AMP | FEEDER | D18/22/KE57/I_T |  |  |  | DNP | 175 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠57線 | 忠57線 |  | 忠57線A0 | [14 empty] | 0174 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠57線A0 | 23KV忠57線 N相AMP | FEEDER | D18/22/KE57/I_N |  |  |  | DNP | 176 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠58線 | 忠58線 |  | 忠58線KVAR | [14 empty] | 0175 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠58線KVAR | 23KV忠58線 KVAR | FEEDER | D18/22/KE58/KVAR |  |  |  | DNP | 177 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠58線 | 忠58線 |  | 忠58線A1 | [14 empty] | 0176 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠58線A1 | 23KV忠58線 R相AMP | FEEDER | D18/22/KE58/I_R |  |  |  | DNP | 178 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠58線 | 忠58線 |  | 忠58線A2 | [14 empty] | 0177 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠58線A2 | 23KV忠58線 S相AMP | FEEDER | D18/22/KE58/I_S |  |  |  | DNP | 179 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠58線 | 忠58線 |  | 忠58線A3 | [14 empty] | 0178 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠58線A3 | 23KV忠58線 T相AMP | FEEDER | D18/22/KE58/I_T |  |  |  | DNP | 180 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠58線 | 忠58線 |  | 忠58線A0 | [14 empty] | 0179 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠58線A0 | 23KV忠58線 N相AMP | FEEDER | D18/22/KE58/I_N |  |  |  | DNP | 181 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠61線 | 忠61線 |  | 忠61線KVAR | [14 empty] | 0189 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠61線KVAR | 23KV忠61線 KVAR | FEEDER | D18/22/KE61/KVAR |  |  |  | DNP | 182 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠61線 | 忠61線 |  | 忠61線A1 | [14 empty] | 0190 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠61線A1 | 23KV忠61線 R相AMP | FEEDER | D18/22/KE61/I_R |  |  |  | DNP | 183 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠61線 | 忠61線 |  | 忠61線A2 | [14 empty] | 0191 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠61線A2 | 23KV忠61線 S相AMP | FEEDER | D18/22/KE61/I_S |  |  |  | DNP | 184 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠61線 | 忠61線 |  | 忠61線A3 | [14 empty] | 0192 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠61線A3 | 23KV忠61線 T相AMP | FEEDER | D18/22/KE61/I_T |  |  |  | DNP | 185 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠61線 | 忠61線 |  | 忠61線A0 | [14 empty] | 0193 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠61線A0 | 23KV忠61線 N相AMP | FEEDER | D18/22/KE61/I_N |  |  |  | DNP | 186 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠62線 | 忠62線 |  | 忠62線KVAR | [14 empty] | 0194 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠62線KVAR | 23KV忠62線 KVAR | FEEDER | D18/22/KE62/KVAR |  |  |  | DNP | 187 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠62線 | 忠62線 |  | 忠62線A1 | [14 empty] | 0195 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠62線A1 | 23KV忠62線 R相AMP | FEEDER | D18/22/KE62/I_R |  |  |  | DNP | 188 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠62線 | 忠62線 |  | 忠62線A2 | [14 empty] | 0196 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠62線A2 | 23KV忠62線 S相AMP | FEEDER | D18/22/KE62/I_S |  |  |  | DNP | 189 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠62線 | 忠62線 |  | 忠62線A3 | [14 empty] | 0197 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠62線A3 | 23KV忠62線 T相AMP | FEEDER | D18/22/KE62/I_T |  |  |  | DNP | 190 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠62線 | 忠62線 |  | 忠62線A0 | [14 empty] | 0198 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠62線A0 | 23KV忠62線 N相AMP | FEEDER | D18/22/KE62/I_N |  |  |  | DNP | 191 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠63線 | 忠63線 |  | 忠63線KVAR | [14 empty] | 0199 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠63線KVAR | 23KV忠63線 KVAR | FEEDER | D18/22/KE63/KVAR |  |  |  | DNP | 192 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠63線 | 忠63線 |  | 忠63線A1 | [14 empty] | 0200 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠63線A1 | 23KV忠63線 R相AMP | FEEDER | D18/22/KE63/I_R |  |  |  | DNP | 193 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠63線 | 忠63線 |  | 忠63線A2 | [14 empty] | 0201 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠63線A2 | 23KV忠63線 S相AMP | FEEDER | D18/22/KE63/I_S |  |  |  | DNP | 194 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠63線 | 忠63線 |  | 忠63線A3 | [14 empty] | 0202 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠63線A3 | 23KV忠63線 T相AMP | FEEDER | D18/22/KE63/I_T |  |  |  | DNP | 195 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠63線 | 忠63線 |  | 忠63線A0 | [14 empty] | 0203 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠63線A0 | 23KV忠63線 N相AMP | FEEDER | D18/22/KE63/I_N |  |  |  | DNP | 196 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠64線 | 忠64線 |  | 忠64線KVAR | [14 empty] | 0204 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠64線KVAR | 23KV忠64線 KVAR | FEEDER | D18/22/KE64/KVAR |  |  |  | DNP | 197 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠64線 | 忠64線 |  | 忠64線A1 | [14 empty] | 0205 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠64線A1 | 23KV忠64線 R相AMP | FEEDER | D18/22/KE64/I_R |  |  |  | DNP | 198 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠64線 | 忠64線 |  | 忠64線A2 | [14 empty] | 0206 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠64線A2 | 23KV忠64線 S相AMP | FEEDER | D18/22/KE64/I_S |  |  |  | DNP | 199 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠64線 | 忠64線 |  | 忠64線A3 | [14 empty] | 0207 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠64線A3 | 23KV忠64線 T相AMP | FEEDER | D18/22/KE64/I_T |  |  |  | DNP | 200 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠64線 | 忠64線 |  | 忠64線A0 | [14 empty] | 0208 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠64線A0 | 23KV忠64線 N相AMP | FEEDER | D18/22/KE64/I_N |  |  |  | DNP | 201 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠65線 | 忠65線 |  | 忠65線KVAR | [14 empty] | 0215 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠65線KVAR | 23KV忠65線 KVAR | FEEDER | D18/22/KE65/KVAR |  |  |  | DNP | 202 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠65線 | 忠65線 |  | 忠65線A1 | [14 empty] | 0216 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠65線A1 | 23KV忠65線 R相AMP | FEEDER | D18/22/KE65/I_R |  |  |  | DNP | 203 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠65線 | 忠65線 |  | 忠65線A2 | [14 empty] | 0217 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠65線A2 | 23KV忠65線 S相AMP | FEEDER | D18/22/KE65/I_S |  |  |  | DNP | 204 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠65線 | 忠65線 |  | 忠65線A3 | [14 empty] | 0218 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠65線A3 | 23KV忠65線 T相AMP | FEEDER | D18/22/KE65/I_T |  |  |  | DNP | 205 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠65線 | 忠65線 |  | 忠65線A0 | [14 empty] | 0219 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠65線A0 | 23KV忠65線 N相AMP | FEEDER | D18/22/KE65/I_N |  |  |  | DNP | 206 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠66線 | 忠66線 |  | 忠66線KVAR | [14 empty] | 0220 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠66線KVAR | 23KV忠66線 KVAR | FEEDER | D18/22/KE66/KVAR |  |  |  | DNP | 207 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠66線 | 忠66線 |  | 忠66線A1 | [14 empty] | 0221 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠66線A1 | 23KV忠66線 R相AMP | FEEDER | D18/22/KE66/I_R |  |  |  | DNP | 208 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠66線 | 忠66線 |  | 忠66線A2 | [14 empty] | 0222 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠66線A2 | 23KV忠66線 S相AMP | FEEDER | D18/22/KE66/I_S |  |  |  | DNP | 209 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠66線 | 忠66線 |  | 忠66線A3 | [14 empty] | 0223 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠66線A3 | 23KV忠66線 T相AMP | FEEDER | D18/22/KE66/I_T |  |  |  | DNP | 210 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠66線 | 忠66線 |  | 忠66線A0 | [14 empty] | 0224 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠66線A0 | 23KV忠66線 N相AMP | FEEDER | D18/22/KE66/I_N |  |  |  | DNP | 211 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠67線 | 忠67線 |  | 忠67線KVAR | [14 empty] | 0225 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠67線KVAR | 23KV忠67線 KVAR | FEEDER | D18/22/KE67/KVAR |  |  |  | DNP | 212 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠67線 | 忠67線 |  | 忠67線A1 | [14 empty] | 0226 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠67線A1 | 23KV忠67線 R相AMP | FEEDER | D18/22/KE67/I_R |  |  |  | DNP | 213 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠67線 | 忠67線 |  | 忠67線A2 | [14 empty] | 0227 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠67線A2 | 23KV忠67線 S相AMP | FEEDER | D18/22/KE67/I_S |  |  |  | DNP | 214 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠67線 | 忠67線 |  | 忠67線A3 | [14 empty] | 0228 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠67線A3 | 23KV忠67線 T相AMP | FEEDER | D18/22/KE67/I_T |  |  |  | DNP | 215 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠67線 | 忠67線 |  | 忠67線A0 | [14 empty] | 0229 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠67線A0 | 23KV忠67線 N相AMP | FEEDER | D18/22/KE67/I_N |  |  |  | DNP | 216 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠68線 | 忠68線 |  | 忠68線KVAR | [14 empty] | 0230 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠68線KVAR | 23KV忠68線 KVAR | FEEDER | D18/22/KE68/KVAR |  |  |  | DNP | 217 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠68線 | 忠68線 |  | 忠68線A1 | [14 empty] | 0231 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠68線A1 | 23KV忠68線 R相AMP | FEEDER | D18/22/KE68/I_R |  |  |  | DNP | 218 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠68線 | 忠68線 |  | 忠68線A2 | [14 empty] | 0232 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠68線A2 | 23KV忠68線 S相AMP | FEEDER | D18/22/KE68/I_S |  |  |  | DNP | 219 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠68線 | 忠68線 |  | 忠68線A3 | [14 empty] | 0233 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠68線A3 | 23KV忠68線 T相AMP | FEEDER | D18/22/KE68/I_T |  |  |  | DNP | 220 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠68線 | 忠68線 |  | 忠68線A0 | [14 empty] | 0234 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠68線A0 | 23KV忠68線 N相AMP | FEEDER | D18/22/KE68/I_N |  |  |  | DNP | 221 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠71線 | 忠71線 |  | 忠71線KVAR | [14 empty] | 0244 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠71線KVAR | 23KV忠71線 KVAR | FEEDER | D18/22/KE71/KVAR |  |  |  | DNP | 222 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠71線 | 忠71線 |  | 忠71線A1 | [14 empty] | 0245 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠71線A1 | 23KV忠71線 R相AMP | FEEDER | D18/22/KE71/I_R |  |  |  | DNP | 223 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠71線 | 忠71線 |  | 忠71線A2 | [14 empty] | 0246 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠71線A2 | 23KV忠71線 S相AMP | FEEDER | D18/22/KE71/I_S |  |  |  | DNP | 224 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠71線 | 忠71線 |  | 忠71線A3 | [14 empty] | 0247 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠71線A3 | 23KV忠71線 T相AMP | FEEDER | D18/22/KE71/I_T |  |  |  | DNP | 225 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠71線 | 忠71線 |  | 忠71線A0 | [14 empty] | 0248 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠71線A0 | 23KV忠71線 N相AMP | FEEDER | D18/22/KE71/I_N |  |  |  | DNP | 226 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠72線 | 忠72線 |  | 忠72線KVAR | [14 empty] | 0249 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠72線KVAR | 23KV忠72線 KVAR | FEEDER | D18/22/KE72/KVAR |  |  |  | DNP | 227 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠72線 | 忠72線 |  | 忠72線A1 | [14 empty] | 0250 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠72線A1 | 23KV忠72線 R相AMP | FEEDER | D18/22/KE72/I_R |  |  |  | DNP | 228 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠72線 | 忠72線 |  | 忠72線A2 | [14 empty] | 0251 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠72線A2 | 23KV忠72線 S相AMP | FEEDER | D18/22/KE72/I_S |  |  |  | DNP | 229 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠72線 | 忠72線 |  | 忠72線A3 | [14 empty] | 0252 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠72線A3 | 23KV忠72線 T相AMP | FEEDER | D18/22/KE72/I_T |  |  |  | DNP | 230 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠72線 | 忠72線 |  | 忠72線A0 | [14 empty] | 0253 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠72線A0 | 23KV忠72線 N相AMP | FEEDER | D18/22/KE72/I_N |  |  |  | DNP | 231 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠73線 | 忠73線 |  | 忠73線KVAR | [14 empty] | 0254 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠73線KVAR | 23KV忠73線 KVAR | FEEDER | D18/22/KE73/KVAR |  |  |  | DNP | 232 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠73線 | 忠73線 |  | 忠73線A1 | [14 empty] | 0255 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠73線A1 | 23KV忠73線 R相AMP | FEEDER | D18/22/KE73/I_R |  |  |  | DNP | 233 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠73線 | 忠73線 |  | 忠73線A2 | [14 empty] | 0256 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠73線A2 | 23KV忠73線 S相AMP | FEEDER | D18/22/KE73/I_S |  |  |  | DNP | 234 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠73線 | 忠73線 |  | 忠73線A3 | [14 empty] | 0257 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠73線A3 | 23KV忠73線 T相AMP | FEEDER | D18/22/KE73/I_T |  |  |  | DNP | 235 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠73線 | 忠73線 |  | 忠73線A0 | [14 empty] | 0258 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠73線A0 | 23KV忠73線 N相AMP | FEEDER | D18/22/KE73/I_N |  |  |  | DNP | 236 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠74線 | 忠74線 |  | 忠74線KVAR | [14 empty] | 0259 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠74線KVAR | 23KV忠74線 KVAR | FEEDER | D18/22/KE74/KVAR |  |  |  | DNP | 237 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠74線 | 忠74線 |  | 忠74線A1 | [14 empty] | 0260 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠74線A1 | 23KV忠74線 R相AMP | FEEDER | D18/22/KE74/I_R |  |  |  | DNP | 238 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠74線 | 忠74線 |  | 忠74線A2 | [14 empty] | 0261 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠74線A2 | 23KV忠74線 S相AMP | FEEDER | D18/22/KE74/I_S |  |  |  | DNP | 239 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠74線 | 忠74線 |  | 忠74線A3 | [14 empty] | 0262 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠74線A3 | 23KV忠74線 T相AMP | FEEDER | D18/22/KE74/I_T |  |  |  | DNP | 240 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠74線 | 忠74線 |  | 忠74線A0 | [14 empty] | 0263 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠74線A0 | 23KV忠74線 N相AMP | FEEDER | D18/22/KE74/I_N |  |  |  | DNP | 241 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠75線 | 忠75線 |  | 忠75線KVAR | [14 empty] | 0270 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠75線KVAR | 23KV忠75線 KVAR | FEEDER | D18/22/KE75/KVAR |  |  |  | DNP | 242 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠75線 | 忠75線 |  | 忠75線A1 | [14 empty] | 0271 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠75線A1 | 23KV忠75線 R相AMP | FEEDER | D18/22/KE75/I_R |  |  |  | DNP | 243 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠75線 | 忠75線 |  | 忠75線A2 | [14 empty] | 0272 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠75線A2 | 23KV忠75線 S相AMP | FEEDER | D18/22/KE75/I_S |  |  |  | DNP | 244 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠75線 | 忠75線 |  | 忠75線A3 | [14 empty] | 0273 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠75線A3 | 23KV忠75線 T相AMP | FEEDER | D18/22/KE75/I_T |  |  |  | DNP | 245 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠75線 | 忠75線 |  | 忠75線A0 | [14 empty] | 0274 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠75線A0 | 23KV忠75線 N相AMP | FEEDER | D18/22/KE75/I_N |  |  |  | DNP | 246 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠76線 | 忠76線 |  | 忠76線KVAR | [14 empty] | 0275 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠76線KVAR | 23KV忠76線 KVAR | FEEDER | D18/22/KE76/KVAR |  |  |  | DNP | 247 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠76線 | 忠76線 |  | 忠76線A1 | [14 empty] | 0276 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠76線A1 | 23KV忠76線 R相AMP | FEEDER | D18/22/KE76/I_R |  |  |  | DNP | 248 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠76線 | 忠76線 |  | 忠76線A2 | [14 empty] | 0277 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠76線A2 | 23KV忠76線 S相AMP | FEEDER | D18/22/KE76/I_S |  |  |  | DNP | 249 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠76線 | 忠76線 |  | 忠76線A3 | [14 empty] | 0278 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠76線A3 | 23KV忠76線 T相AMP | FEEDER | D18/22/KE76/I_T |  |  |  | DNP | 250 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠76線 | 忠76線 |  | 忠76線A0 | [14 empty] | 0279 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠76線A0 | 23KV忠76線 N相AMP | FEEDER | D18/22/KE76/I_N |  |  |  | DNP | 251 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠77線 | 忠77線 |  | 忠77線KVAR | [14 empty] | 0280 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠77線KVAR | 23KV忠77線 KVAR | FEEDER | D18/22/KE77/KVAR |  |  |  | DNP | 252 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠77線 | 忠77線 |  | 忠77線A1 | [14 empty] | 0281 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠77線A1 | 23KV忠77線 R相AMP | FEEDER | D18/22/KE77/I_R |  |  |  | DNP | 253 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠77線 | 忠77線 |  | 忠77線A2 | [14 empty] | 0282 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠77線A2 | 23KV忠77線 S相AMP | FEEDER | D18/22/KE77/I_S |  |  |  | DNP | 254 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠77線 | 忠77線 |  | 忠77線A3 | [14 empty] | 0283 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠77線A3 | 23KV忠77線 T相AMP | FEEDER | D18/22/KE77/I_T |  |  |  | DNP | 255 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠77線 | 忠77線 |  | 忠77線A0 | [14 empty] | 0284 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠77線A0 | 23KV忠77線 N相AMP | FEEDER | D18/22/KE77/I_N |  |  |  | DNP | 256 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠78線 | 忠78線 |  | 忠78線KVAR | [14 empty] | 0285 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠78線KVAR | 23KV忠78線 KVAR | FEEDER | D18/22/KE78/KVAR |  |  |  | DNP | 257 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠78線 | 忠78線 |  | 忠78線A1 | [14 empty] | 0286 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠78線A1 | 23KV忠78線 R相AMP | FEEDER | D18/22/KE78/I_R |  |  |  | DNP | 258 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠78線 | 忠78線 |  | 忠78線A2 | [14 empty] | 0287 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠78線A2 | 23KV忠78線 S相AMP | FEEDER | D18/22/KE78/I_S |  |  |  | DNP | 259 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠78線 | 忠78線 |  | 忠78線A3 | [14 empty] | 0288 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠78線A3 | 23KV忠78線 T相AMP | FEEDER | D18/22/KE78/I_T |  |  |  | DNP | 260 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | 忠78線 | 忠78線 |  | 忠78線A0 | [14 empty] | 0289 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 忠孝DS.忠78線A0 | 23KV忠78線 N相AMP | FEEDER | D18/22/KE78/I_N |  |  |  | DNP | 261 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 0 |  | 1500TIE | 1500TIE |  | I | [14 empty] | 0024 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.1500TIE_AMP | 1500TIE AMP | TIE | D18/161/1500/I |  |  |  | DNP | 262 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | _100 | 100 |  | I_R | [14 empty] | 0180 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.23KV_100_A1 | 23KV 100 R相AMP | TIE | D18/22/100/I_R |  |  |  | DNP | 263 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | _100 | 100 |  | I_S | [14 empty] | 0181 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.23KV_100_A2 | 23KV 100 S相AMP | TIE | D18/22/100/I_S |  |  |  | DNP | 264 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | _100 | 100 |  | I_T | [14 empty] | 0182 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.23KV_100_A3 | 23KV 100 T相AMP | TIE | D18/22/100/I_T |  |  |  | DNP | 265 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | _200 | 200 |  | I_R | [14 empty] | 0235 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.23KV_200_A1 | 23KV 200 R相AMP | TIE | D18/22/200/I_R |  |  |  | DNP | 266 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | _200 | 200 |  | I_S | [14 empty] | 0236 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.23KV_200_A2 | 23KV 200 S相AMP | TIE | D18/22/200/I_S |  |  |  | DNP | 267 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | _200 | 200 |  | I_T | [14 empty] | 0237 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.23KV_200_A3 | 23KV 200 T相AMP | TIE | D18/22/200/I_T |  |  |  | DNP | 268 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | _300 | 300 |  | I_R | [14 empty] | 0290 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.23KV_300_A1 | 23KV 300 R相AMP | TIE | D18/22/300/I_R |  |  |  | DNP | 269 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | _300 | 300 |  | I_S | [14 empty] | 0291 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.23KV_300_A2 | 23KV 300 S相AMP | TIE | D18/22/300/I_S |  |  |  | DNP | 270 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 22 | 22kV | _300 | 300 |  | I_T | [14 empty] | 0292 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.23KV_300_A3 | 23KV 300 T相AMP | TIE | D18/22/300/I_T |  |  |  | DNP | 271 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 0 |  | 1DTR | #1DTR |  | OilTemp | [14 empty] | 0032 | [8 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#1DTR_OIL | #1DTR 油溫 | MTR | D18//1DTR/OilTemp |  |  |  | DNP | 272 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D18 | 忠孝DS | 0 |  | 1DTR | #1DTR |  | CoilTemp | [14 empty] | 0033 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#1DTR_COIL | #1DTR 線溫 | MTR | D18//1DTR/CoilTemp |  |  |  | DNP | 273 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D18 | 忠孝DS | 0 |  | 1DTR | #1DTR |  | TapPosMv | [14 empty] | 0034 |  | 0099 | [6 empty] | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#1DTR_TAP | #1DTR OLTC TAP | MTR | D18//1DTR/TapPosMv |  |  |  | DNP | 274 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D18 | 忠孝DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MW | [14 empty] | 0128 | [8 empty] | MW_-108_108(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | D18/22/310/KW |  |  |  | DNP | 275 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D18 | 忠孝DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVAR | [14 empty] | 0129 | [8 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | D18/22/310/KVAR |  |  |  | DNP | 276 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D18 | 忠孝DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_R | [14 empty] | 0130 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | D18/22/310/I_R |  |  |  | DNP | 277 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_S | [14 empty] | 0131 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | D18/22/310/I_S |  |  |  | DNP | 278 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_T | [14 empty] | 0132 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | D18/22/310/I_T |  |  |  | DNP | 279 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MW | [14 empty] | 0154 | [8 empty] | MW_-108_108(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | D18/22/320/KW |  |  |  | DNP | 280 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D18 | 忠孝DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVAR | [14 empty] | 0155 | [8 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | D18/22/320/KVAR |  |  |  | DNP | 281 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D18 | 忠孝DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_R | [14 empty] | 0156 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | D18/22/320/I_R |  |  |  | DNP | 282 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_S | [14 empty] | 0157 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | D18/22/320/I_S |  |  |  | DNP | 283 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_T | [14 empty] | 0158 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | D18/22/320/I_T |  |  |  | DNP | 284 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 0 |  | 2DTR | #2DTR |  | OilTemp | [14 empty] | 0035 | [8 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#2DTR_OIL | #2DTR 油溫 | MTR | D18//2DTR/OilTemp |  |  |  | DNP | 285 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D18 | 忠孝DS | 0 |  | 2DTR | #2DTR |  | CoilTemp | [14 empty] | 0036 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#2DTR_COIL | #2DTR 線溫 | MTR | D18//2DTR/CoilTemp |  |  |  | DNP | 286 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D18 | 忠孝DS | 0 |  | 2DTR | #2DTR |  | TapPosMv | [14 empty] | 0037 |  | 0101 | [6 empty] | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#2DTR_TAP | #2DTR OLTC TAP | MTR | D18//2DTR/TapPosMv |  |  |  | DNP | 287 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D18 | 忠孝DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MW | [14 empty] | 0183 | [8 empty] | MW_-108_108(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | D18/22/330/KW |  |  |  | DNP | 288 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D18 | 忠孝DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVAR | [14 empty] | 0184 | [8 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | D18/22/330/KVAR |  |  |  | DNP | 289 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D18 | 忠孝DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_R | [14 empty] | 0185 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | D18/22/330/I_R |  |  |  | DNP | 290 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_S | [14 empty] | 0186 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | D18/22/330/I_S |  |  |  | DNP | 291 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_T | [14 empty] | 0187 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | D18/22/330/I_T |  |  |  | DNP | 292 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MW | [14 empty] | 0209 | [8 empty] | MW_-108_108(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | D18/22/340/KW |  |  |  | DNP | 293 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D18 | 忠孝DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVAR | [14 empty] | 0210 | [8 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | D18/22/340/KVAR |  |  |  | DNP | 294 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D18 | 忠孝DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_R | [14 empty] | 0211 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | D18/22/340/I_R |  |  |  | DNP | 295 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_S | [14 empty] | 0212 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | D18/22/340/I_S |  |  |  | DNP | 296 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_T | [14 empty] | 0213 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | D18/22/340/I_T |  |  |  | DNP | 297 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 0 |  | 3DTR | #3DTR |  | OilTemp | [14 empty] | 0038 | [8 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#3DTR_OIL | #3DTR 油溫 | MTR | D18//3DTR/OilTemp |  |  |  | DNP | 298 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D18 | 忠孝DS | 0 |  | 3DTR | #3DTR |  | CoilTemp | [14 empty] | 0039 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#3DTR_COIL | #3DTR 線溫 | MTR | D18//3DTR/CoilTemp |  |  |  | DNP | 299 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D18 | 忠孝DS | 0 |  | 3DTR | #3DTR |  | TapPosMv | [14 empty] | 0040 |  | 0103 | [6 empty] | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#3DTR_TAP | #3DTR OLTC TAP | MTR | D18//3DTR/TapPosMv |  |  |  | DNP | 300 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D18 | 忠孝DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | MW | [14 empty] | 0238 | [8 empty] | MW_-108_108(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#3DTR(A)_MW | #3DTR二次側(A) MW | MTR | D18/22/350/KW |  |  |  | DNP | 301 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D18 | 忠孝DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | MVAR | [14 empty] | 0239 | [8 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#3DTR(A)_MVAR | #3DTR二次側(A) MVAR | MTR | D18/22/350/KVAR |  |  |  | DNP | 302 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D18 | 忠孝DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | I_R | [14 empty] | 0240 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#3DTR(A)_A1 | #3DTR二次側(A) R相AMP | MTR | D18/22/350/I_R |  |  |  | DNP | 303 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | I_S | [14 empty] | 0241 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#3DTR(A)_A2 | #3DTR二次側(A) S相AMP | MTR | D18/22/350/I_S |  |  |  | DNP | 304 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | I_T | [14 empty] | 0242 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#3DTR(A)_A3 | #3DTR二次側(A) T相AMP | MTR | D18/22/350/I_T |  |  |  | DNP | 305 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | MW | [14 empty] | 0264 | [8 empty] | MW_-108_108(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#3DTR(B)_MW | #3DTR二次側(B) MW | MTR | D18/22/360/KW |  |  |  | DNP | 306 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D18 | 忠孝DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | MVAR | [14 empty] | 0265 | [8 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#3DTR(B)_MVAR | #3DTR二次側(B) MVAR | MTR | D18/22/360/KVAR |  |  |  | DNP | 307 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D18 | 忠孝DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | I_R | [14 empty] | 0266 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#3DTR(B)_A1 | #3DTR二次側(B) R相AMP | MTR | D18/22/360/I_R |  |  |  | DNP | 308 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | I_S | [14 empty] | 0267 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#3DTR(B)_A2 | #3DTR二次側(B) S相AMP | MTR | D18/22/360/I_S |  |  |  | DNP | 309 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | I_T | [14 empty] | 0268 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.#3DTR(B)_A3 | #3DTR二次側(B) T相AMP | MTR | D18/22/360/I_T |  |  |  | DNP | 310 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 0 |  |  |  |  | DCV_N | [14 empty] | 0062 | [8 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.直流N電源電壓 | 直流N電源電壓 | OTHER | D18/0/StaDev/DCV_N |  |  |  | DNP | 311 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D18 | 忠孝DS | 0 |  |  |  |  | DCV_P | [14 empty] | 0061 | [8 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.直流P電源電壓 | 直流P電源電壓 | OTHER | D18/0/StaDev/DCV_P |  |  |  | DNP | 312 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D18 | 忠孝DS | 161 | 161kV | 1611SHR | #1SHR |  | CoilTemp | [14 empty] | 0042 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.161#1SHR_COIL | 161KV #1SHR 線溫 | OTHER | D18//1SHR/CoilTemp |  |  |  | DNP | 313 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D18 | 忠孝DS | 161 | 161kV | 1611SHR | #1SHR |  | OilTemp | [14 empty] | 0041 | [8 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.161#1SHR_OIL | 161KV #1SHR 油溫 | OTHER | D18//1SHR/OilTemp |  |  |  | DNP | 314 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D18 | 忠孝DS | 0 |  | 1520_OF | 台南忠孝二路 |  | R | [14 empty] | 0025 | [8 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.1520_OF_R | 台南忠孝二路 R相 油壓 | OTHER | D18/161/1520/OilPreR |  |  |  | DNP | 315 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 0 |  | 1520_OF | 台南忠孝二路 |  | S | [14 empty] | 0026 | [8 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.1520_OF_S | 台南忠孝二路 S相 油壓 | OTHER | D18/161/1520/OilPreS |  |  |  | DNP | 316 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 0 |  | 1520_OF | 台南忠孝二路 |  | T | [14 empty] | 0027 | [8 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.1520_OF_T | 台南忠孝二路 T相 油壓 | OTHER | D18/161/1520/OilPreT |  |  |  | DNP | 317 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 0 |  | 1530_OF | 忠孝延平線 |  | R | [14 empty] | 0028 | [8 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.1530_OF_R | 忠孝延平線 R相 油壓 | OTHER | D18/161/1530/OilPreR |  |  |  | DNP | 318 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 0 |  | 1530_OF | 忠孝延平線 |  | S | [14 empty] | 0029 | [8 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.1530_OF_S | 忠孝延平線 S相 油壓 | OTHER | D18/161/1530/OilPreS |  |  |  | DNP | 319 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 0 |  | 1530_OF | 忠孝延平線 |  | T | [14 empty] | 0030 | [8 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_S | [8 empty] | 忠孝DS.1530_OF_T | 忠孝延平線 T相 油壓 | OTHER | D18/161/1530/OilPreT |  |  |  | DNP | 320 | DNPAIPoint | DS058 |  |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D18 | 忠孝DS | 161 | 161kV | 1510 | 台南忠孝一路(1510) |  | PHA | [14 empty] | 0002 | [10 empty] | 161KV_S | [8 empty] | 忠孝DS.1510_PHA | 台南忠孝一路(1510) 相間RY | LINE161 | D18/161/1510/PHA |  |  |  | DNP | 321 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1510 | 台南忠孝一路(1510) |  | GDA | [14 empty] | 0003 | [10 empty] | 161KV_S | [8 empty] | 忠孝DS.1510_GDA | 台南忠孝一路(1510) 接地RY | LINE161 | D18/161/1510/GDA |  |  |  | DNP | 322 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1510 | 1510 |  | 87A1 | [14 empty] | 0001 | [10 empty] | 161KV_S | [8 empty] | 忠孝DS.1510_87A1 | 台南忠孝一路(1510)第一套87RY | LINE161 | D18/161/1510/87A1 |  |  |  | DNP | 323 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1510 | 台南忠孝一路(1510)#187RY |  | 1_87UL1 | [14 empty] | 0854 |  | 0128 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.1510_87UL1 | 台南忠孝一路(1510)#187RY U/L | LINE161 | D18/161/1510/1_87UL1 |  |  |  | DNP | 324 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 161 | 161kV | 1510 | 台南忠孝一路(1510)#287RY |  | 1_87UL2 | [14 empty] | 0856 |  | 0130 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.1510_87UL2 | 台南忠孝一路(1510)#287RY U/L | LINE161 | D18/161/1510/1_87UL2 |  |  |  | DNP | 325 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 161 | 161kV | 1510 | 台南忠孝一路(1510) |  | CB | [14 empty] | 0000 |  | 0001 | [8 empty] | 161KV_S | [8 empty] | 忠孝DS.1510_CB | 1510(台南忠孝一路) CB | LINE161 | D18/161/1510/CB |  |  |  | DNP | 326 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 161 | 161kV | 1510 | 台南忠孝一路(1510) |  | 79UL | [14 empty] | 0855 |  | 0129 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.1510_79UL | 台南忠孝一路(1510) 79RY U/L | LINE161 | D18/161/1510/79UL |  |  |  | DNP | 327 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 161 | 161kV | 1510 | 台南忠孝一路(1510) |  | DS1 | 1511 | [13 empty] | 0640 | 641 | 0064 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.1511_DS | 1511(台南忠孝一路) DS | LINE161 | D18/161/1510/DS1 |  |  |  | DNP | 328 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D18 | 忠孝DS | 161 | 161kV | 1510 | 台南忠孝一路(1510) |  | DS2 | 1512 | [13 empty] | 0642 | 643 | 0065 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.1512_DS | 1512(台南忠孝一路) DS | LINE161 | D18/161/1510/DS2 |  |  |  | DNP | 329 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D18 | 忠孝DS | 161 | 161kV | 1510 | 台南忠孝一路(1510) |  | DS3 | 1513 | [13 empty] | 0644 | 645 | 0066 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.1513_DS | 1513(台南忠孝一路) DS | LINE161 | D18/161/1510/DS3 |  |  |  | DNP | 330 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D18 | 忠孝DS | 161 | 161kV | 1510 | 台南忠孝一路(1510) |  | E3 | 1513E | [13 empty] | 0646 | 647 | 0067 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.1513E_ES | 1513E(台南忠孝一路) ES | LINE161 | D18/161/1510/ES3 |  |  |  | DNP | 331 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南忠孝二路(1520) |  | PHA | [14 empty] | 0006 | [10 empty] | 161KV_S | [8 empty] | 忠孝DS.1520_PHA | 台南忠孝二路(1520) 相間RY | LINE161 | D18/161/1520/PHA |  |  |  | DNP | 332 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南忠孝二路(1520) |  | GDA | [14 empty] | 0007 | [10 empty] | 161KV_S | [8 empty] | 忠孝DS.1520_GDA | 台南忠孝二路(1520) 接地RY | LINE161 | D18/161/1520/GDA |  |  |  | DNP | 333 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1520 | 1520 |  | 87A1 | [14 empty] | 0005 | [10 empty] | 161KV_S | [8 empty] | 忠孝DS.1520_87A1 | 台南忠孝二路(1520)第一套87RY | LINE161 | D18/161/1520/87A1 |  |  |  | DNP | 334 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南忠孝二路(1520)#187RY |  | 1_87UL1 | [14 empty] | 0857 |  | 0131 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.1520_87UL1 | 台南忠孝二路(1520)#187RY U/L | LINE161 | D18/161/1520/1_87UL1 |  |  |  | DNP | 335 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南忠孝二路(1520)#287RY |  | 1_87UL2 | [14 empty] | 0859 |  | 0133 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.1520_87UL2 | 台南忠孝二路(1520)#287RY U/L | LINE161 | D18/161/1520/1_87UL2 |  |  |  | DNP | 336 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南忠孝二路(1520) |  | CB | [14 empty] | 0004 |  | 0002 | [8 empty] | 161KV_S | [8 empty] | 忠孝DS.1520_CB | 1520(台南忠孝二路) CB | LINE161 | D18/161/1520/CB |  |  |  | DNP | 337 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南忠孝二路(1520) |  | 79UL | [14 empty] | 0858 |  | 0132 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.1520_79UL | 台南忠孝二路(1520) 79RY U/L | LINE161 | D18/161/1520/79UL |  |  |  | DNP | 338 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南忠孝二路(1520) |  | DS1 | 1521 | [13 empty] | 0648 | 649 | 0068 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.1521_DS | 1521(台南忠孝二路) DS | LINE161 | D18/161/1520/DS1 |  |  |  | DNP | 339 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南忠孝二路(1520) |  | DS2 | 1522 | [13 empty] | 0650 | 651 | 0069 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.1522_DS | 1522(台南忠孝二路) DS | LINE161 | D18/161/1520/DS2 |  |  |  | DNP | 340 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南忠孝二路(1520) |  | DS3 | 1523 | [13 empty] | 0652 | 653 | 0070 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.1523_DS | 1523(台南忠孝二路) DS | LINE161 | D18/161/1520/DS3 |  |  |  | DNP | 341 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南忠孝二路(1520) |  | E3 | 1523E | [13 empty] | 0654 | 655 | 0071 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.1523E_ES | 1523E(台南忠孝二路) ES | LINE161 | D18/161/1520/ES3 |  |  |  | DNP | 342 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝延平線(1530) |  | PHA | [14 empty] | 0010 | [10 empty] | 161KV_S | [8 empty] | 忠孝DS.1530_PHA | 忠孝延平線(1530) 相間RY | LINE161 | D18/161/1530/PHA |  |  |  | DNP | 343 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝延平線(1530) |  | GDA | [14 empty] | 0011 | [10 empty] | 161KV_S | [8 empty] | 忠孝DS.1530_GDA | 忠孝延平線(1530) 接地RY | LINE161 | D18/161/1530/GDA |  |  |  | DNP | 344 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1530 | 1530 |  | 87A1 | [14 empty] | 0009 | [10 empty] | 161KV_S | [8 empty] | 忠孝DS.1530_87A1 | 忠孝延平線(1530)第一套87RY | LINE161 | D18/161/1530/87A1 |  |  |  | DNP | 345 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝延平線(1530)#187RY |  | 1_87UL1 | [14 empty] | 0860 |  | 0134 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.1530_87UL1 | 忠孝延平線(1530)#187RY U/L | LINE161 | D18/161/1530/1_87UL1 |  |  |  | DNP | 346 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝延平線(1530)#287RY |  | 1_87UL2 | [14 empty] | 0862 |  | 0136 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.1530_87UL2 | 忠孝延平線(1530)#287RY U/L | LINE161 | D18/161/1530/1_87UL2 |  |  |  | DNP | 347 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝延平線(1530) |  | CB | [14 empty] | 0008 |  | 0003 | [8 empty] | 161KV_S | [8 empty] | 忠孝DS.1530_CB | 1530(忠孝延平線) CB | LINE161 | D18/161/1530/CB |  |  |  | DNP | 348 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝延平線(1530) |  | 79UL | [14 empty] | 0861 |  | 0135 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.1530_79UL | 忠孝延平線(1530) 79RY U/L | LINE161 | D18/161/1530/79UL |  |  |  | DNP | 349 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝延平線(1530) |  | DS1 | 1531 | [13 empty] | 0656 | 657 | 0072 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.1531_DS | 1531(忠孝延平線) DS | LINE161 | D18/161/1530/DS1 |  |  |  | DNP | 350 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝延平線(1530) |  | DS2 | 1532 | [13 empty] | 0658 | 659 | 0073 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.1532_DS | 1532(忠孝延平線) DS | LINE161 | D18/161/1530/DS2 |  |  |  | DNP | 351 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝延平線(1530) |  | DS3 | 1533 | [13 empty] | 0660 | 661 | 0074 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.1533_DS | 1533(忠孝延平線) DS | LINE161 | D18/161/1530/DS3 |  |  |  | DNP | 352 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝延平線(1530) |  | E3 | 1533E | [13 empty] | 0662 | 663 | 0075 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.1533E_ES | 1533E(忠孝延平線) ES | LINE161 | D18/161/1530/ES3 |  |  |  | DNP | 353 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D18 | 忠孝DS | 22 | 22kV | KE51 | 忠51線(KE51) |  | PHA | [14 empty] | 0199 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE51_PHA | 23KV忠51線(KE51) 相間RY | FEEDER | D18/22/KE51/PHA |  |  |  | DNP | 354 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE51 | 忠51線(KE51) |  | GDA | [14 empty] | 0200 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE51_GDA | 23KV忠51線(KE51) 接地RY | FEEDER | D18/22/KE51/GDA |  |  |  | DNP | 355 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE51 | 忠51線(KE51) 79RY |  | 79UL | [14 empty] | 0768 |  | 0184 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE51_79UL | 23KV忠51線(KE51) 79RY U/L | FEEDER | D18/22/KE51/79UL |  |  |  | DNP | 356 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE51_LCO | 忠51線(KE51) LCO |  | TapPosMv | [14 empty] | 0769 |  | 0185 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE51_LCO_TAP | 23KV忠51線(KE51) LCO TAP | FEEDER | D18/22/KE51/ADJ |  |  |  | DNP | 357 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE51 | KE51(23KV忠51線) |  | CB | [14 empty] | 0198 |  | 0024 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE51_CB | KE51(23KV忠51線) CB | FEEDER | D18/22/KE51/CB |  |  |  | DNP | 358 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE52 | 忠52線(KE52) |  | PHA | [14 empty] | 0202 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE52_PHA | 23KV忠52線(KE52) 相間RY | FEEDER | D18/22/KE52/PHA |  |  |  | DNP | 359 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE52 | 忠52線(KE52) |  | GDA | [14 empty] | 0203 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE52_GDA | 23KV忠52線(KE52) 接地RY | FEEDER | D18/22/KE52/GDA |  |  |  | DNP | 360 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE52 | 忠52線(KE52) 79RY |  | 79UL | [14 empty] | 0770 |  | 0186 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE52_79UL | 23KV忠52線(KE52) 79RY U/L | FEEDER | D18/22/KE52/79UL |  |  |  | DNP | 361 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE52_LCO | 忠52線(KE52) LCO |  | TapPosMv | [14 empty] | 0771 |  | 0187 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE52_LCO_TAP | 23KV忠52線(KE52) LCO TAP | FEEDER | D18/22/KE52/ADJ |  |  |  | DNP | 362 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE52 | KE52(23KV忠52線) |  | CB | [14 empty] | 0201 |  | 0025 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE52_CB | KE52(23KV忠52線) CB | FEEDER | D18/22/KE52/CB |  |  |  | DNP | 363 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE53 | 忠53線(KE53) |  | PHA | [14 empty] | 0205 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE53_PHA | 23KV忠53線(KE53) 相間RY | FEEDER | D18/22/KE53/PHA |  |  |  | DNP | 364 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE53 | 忠53線(KE53) |  | GDA | [14 empty] | 0206 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE53_GDA | 23KV忠53線(KE53) 接地RY | FEEDER | D18/22/KE53/GDA |  |  |  | DNP | 365 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE53 | 忠53線(KE53) 79RY |  | 79UL | [14 empty] | 0772 |  | 0188 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE53_79UL | 23KV忠53線(KE53) 79RY U/L | FEEDER | D18/22/KE53/79UL |  |  |  | DNP | 366 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE53_LCO | 忠53線(KE53) LCO |  | TapPosMv | [14 empty] | 0773 |  | 0189 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE53_LCO_TAP | 23KV忠53線(KE53) LCO TAP | FEEDER | D18/22/KE53/ADJ |  |  |  | DNP | 367 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE53 | KE53(23KV忠53線) |  | CB | [14 empty] | 0204 |  | 0026 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE53_CB | KE53(23KV忠53線) CB | FEEDER | D18/22/KE53/CB |  |  |  | DNP | 368 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE54 | 忠54線(KE54) |  | PHA | [14 empty] | 0208 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE54_PHA | 23KV忠54線(KE54) 相間RY | FEEDER | D18/22/KE54/PHA |  |  |  | DNP | 369 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE54 | 忠54線(KE54) |  | GDA | [14 empty] | 0209 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE54_GDA | 23KV忠54線(KE54) 接地RY | FEEDER | D18/22/KE54/GDA |  |  |  | DNP | 370 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE54 | 忠54線(KE54) 79RY |  | 79UL | [14 empty] | 0774 |  | 0190 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE54_79UL | 23KV忠54線(KE54) 79RY U/L | FEEDER | D18/22/KE54/79UL |  |  |  | DNP | 371 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE54_LCO | 忠54線(KE54) LCO |  | TapPosMv | [14 empty] | 0775 |  | 0191 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE54_LCO_TAP | 23KV忠54線(KE54) LCO TAP | FEEDER | D18/22/KE54/ADJ |  |  |  | DNP | 372 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE54 | KE54(23KV忠54線) |  | CB | [14 empty] | 0207 |  | 0027 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE54_CB | KE54(23KV忠54線) CB | FEEDER | D18/22/KE54/CB |  |  |  | DNP | 373 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE55 | 忠55線(KE55) |  | PHA | [14 empty] | 0217 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE55_PHA | 23KV忠55線(KE55) 相間RY | FEEDER | D18/22/KE55/PHA |  |  |  | DNP | 374 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE55 | 忠55線(KE55) |  | GDA | [14 empty] | 0218 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE55_GDA | 23KV忠55線(KE55) 接地RY | FEEDER | D18/22/KE55/GDA |  |  |  | DNP | 375 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE55 | 忠55線(KE55) 79RY |  | 79UL | [14 empty] | 0776 |  | 0192 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE55_79UL | 23KV忠55線(KE55) 79RY U/L | FEEDER | D18/22/KE55/79UL |  |  |  | DNP | 376 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE55_LCO | 忠55線(KE55) LCO |  | TapPosMv | [14 empty] | 0777 |  | 0193 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE55_LCO_TAP | 23KV忠55線(KE55) LCO TAP | FEEDER | D18/22/KE55/ADJ |  |  |  | DNP | 377 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE55 | KE55(23KV忠55線) |  | CB | [14 empty] | 0216 |  | 0030 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE55_CB | KE55(23KV忠55線) CB | FEEDER | D18/22/KE55/CB |  |  |  | DNP | 378 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE56 | 忠56線(KE56) |  | PHA | [14 empty] | 0220 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE56_PHA | 23KV忠56線(KE56) 相間RY | FEEDER | D18/22/KE56/PHA |  |  |  | DNP | 379 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE56 | 忠56線(KE56) |  | GDA | [14 empty] | 0221 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE56_GDA | 23KV忠56線(KE56) 接地RY | FEEDER | D18/22/KE56/GDA |  |  |  | DNP | 380 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE56 | 忠56線(KE56) 79RY |  | 79UL | [14 empty] | 0778 |  | 0194 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE56_79UL | 23KV忠56線(KE56) 79RY U/L | FEEDER | D18/22/KE56/79UL |  |  |  | DNP | 381 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE56_LCO | 忠56線(KE56) LCO |  | TapPosMv | [14 empty] | 0779 |  | 0195 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE56_LCO_TAP | 23KV忠56線(KE56) LCO TAP | FEEDER | D18/22/KE56/ADJ |  |  |  | DNP | 382 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE56 | KE56(23KV忠56線) |  | CB | [14 empty] | 0219 |  | 0031 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE56_CB | KE56(23KV忠56線) CB | FEEDER | D18/22/KE56/CB |  |  |  | DNP | 383 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE57 | 忠57線(KE57) |  | PHA | [14 empty] | 0223 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE57_PHA | 23KV忠57線(KE57) 相間RY | FEEDER | D18/22/KE57/PHA |  |  |  | DNP | 384 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE57 | 忠57線(KE57) |  | GDA | [14 empty] | 0224 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE57_GDA | 23KV忠57線(KE57) 接地RY | FEEDER | D18/22/KE57/GDA |  |  |  | DNP | 385 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE57 | 忠57線(KE57) 79RY |  | 79UL | [14 empty] | 0780 |  | 0196 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE57_79UL | 23KV忠57線(KE57) 79RY U/L | FEEDER | D18/22/KE57/79UL |  |  |  | DNP | 386 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE57_LCO | 忠57線(KE57) LCO |  | TapPosMv | [14 empty] | 0781 |  | 0197 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE57_LCO_TAP | 23KV忠57線(KE57) LCO TAP | FEEDER | D18/22/KE57/ADJ |  |  |  | DNP | 387 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE57 | KE57(23KV忠57線) |  | CB | [14 empty] | 0222 |  | 0032 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE57_CB | KE57(23KV忠57線) CB | FEEDER | D18/22/KE57/CB |  |  |  | DNP | 388 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE58 | 忠58線(KE58) |  | PHA | [14 empty] | 0226 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE58_PHA | 23KV忠58線(KE58) 相間RY | FEEDER | D18/22/KE58/PHA |  |  |  | DNP | 389 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE58 | 忠58線(KE58) |  | GDA | [14 empty] | 0227 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE58_GDA | 23KV忠58線(KE58) 接地RY | FEEDER | D18/22/KE58/GDA |  |  |  | DNP | 390 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE58 | 忠58線(KE58) 79RY |  | 79UL | [14 empty] | 0782 |  | 0198 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE58_79UL | 23KV忠58線(KE58) 79RY U/L | FEEDER | D18/22/KE58/79UL |  |  |  | DNP | 391 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE58_LCO | 忠58線(KE58) LCO |  | TapPosMv | [14 empty] | 0783 |  | 0199 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE58_LCO_TAP | 23KV忠58線(KE58) LCO TAP | FEEDER | D18/22/KE58/ADJ |  |  |  | DNP | 392 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE58 | KE58(23KV忠58線) |  | CB | [14 empty] | 0225 |  | 0033 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE58_CB | KE58(23KV忠58線) CB | FEEDER | D18/22/KE58/CB |  |  |  | DNP | 393 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE61 | 忠61線(KE61) |  | PHA | [14 empty] | 0232 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE61_PHA | 23KV忠61線(KE61) 相間RY | FEEDER | D18/22/KE61/PHA |  |  |  | DNP | 394 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE61 | 忠61線(KE61) |  | GDA | [14 empty] | 0233 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE61_GDA | 23KV忠61線(KE61) 接地RY | FEEDER | D18/22/KE61/GDA |  |  |  | DNP | 395 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE61 | 忠61線(KE61) 79RY |  | 79UL | [14 empty] | 0784 |  | 0200 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE61_79UL | 23KV忠61線(KE61) 79RY U/L | FEEDER | D18/22/KE61/79UL |  |  |  | DNP | 396 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE61_LCO | 忠61線(KE61) LCO |  | TapPosMv | [14 empty] | 0785 |  | 0201 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE61_LCO_TAP | 23KV忠61線(KE61) LCO TAP | FEEDER | D18/22/KE61/ADJ |  |  |  | DNP | 397 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE61 | KE61(23KV忠61線) |  | CB | [14 empty] | 0231 |  | 0035 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE61_CB | KE61(23KV忠61線) CB | FEEDER | D18/22/KE61/CB |  |  |  | DNP | 398 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE62 | 忠62線(KE62) |  | PHA | [14 empty] | 0235 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE62_PHA | 23KV忠62線(KE62) 相間RY | FEEDER | D18/22/KE62/PHA |  |  |  | DNP | 399 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE62 | 忠62線(KE62) |  | GDA | [14 empty] | 0236 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE62_GDA | 23KV忠62線(KE62) 接地RY | FEEDER | D18/22/KE62/GDA |  |  |  | DNP | 400 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE62 | 忠62線(KE62) 79RY |  | 79UL | [14 empty] | 0786 |  | 0202 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE62_79UL | 23KV忠62線(KE62) 79RY U/L | FEEDER | D18/22/KE62/79UL |  |  |  | DNP | 401 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE62_LCO | 忠62線(KE62) LCO |  | TapPosMv | [14 empty] | 0787 |  | 0203 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE62_LCO_TAP | 23KV忠62線(KE62) LCO TAP | FEEDER | D18/22/KE62/ADJ |  |  |  | DNP | 402 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE62 | KE62(23KV忠62線) |  | CB | [14 empty] | 0234 |  | 0036 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE62_CB | KE62(23KV忠62線) CB | FEEDER | D18/22/KE62/CB |  |  |  | DNP | 403 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE63 | 忠63線(KE63) |  | PHA | [14 empty] | 0238 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE63_PHA | 23KV忠63線(KE63) 相間RY | FEEDER | D18/22/KE63/PHA |  |  |  | DNP | 404 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE63 | 忠63線(KE63) |  | GDA | [14 empty] | 0239 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE63_GDA | 23KV忠63線(KE63) 接地RY | FEEDER | D18/22/KE63/GDA |  |  |  | DNP | 405 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE63 | 忠63線(KE63) 79RY |  | 79UL | [14 empty] | 0788 |  | 0204 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE63_79UL | 23KV忠63線(KE63) 79RY U/L | FEEDER | D18/22/KE63/79UL |  |  |  | DNP | 406 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE63_LCO | 忠63線(KE63) LCO |  | TapPosMv | [14 empty] | 0789 |  | 0205 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE63_LCO_TAP | 23KV忠63線(KE63) LCO TAP | FEEDER | D18/22/KE63/ADJ |  |  |  | DNP | 407 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE63 | KE63(23KV忠63線) |  | CB | [14 empty] | 0237 |  | 0037 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE63_CB | KE63(23KV忠63線) CB | FEEDER | D18/22/KE63/CB |  |  |  | DNP | 408 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE64 | 忠64線(KE64) |  | PHA | [14 empty] | 0241 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE64_PHA | 23KV忠64線(KE64) 相間RY | FEEDER | D18/22/KE64/PHA |  |  |  | DNP | 409 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE64 | 忠64線(KE64) |  | GDA | [14 empty] | 0242 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE64_GDA | 23KV忠64線(KE64) 接地RY | FEEDER | D18/22/KE64/GDA |  |  |  | DNP | 410 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE64 | 忠64線(KE64) 79RY |  | 79UL | [14 empty] | 0790 |  | 0206 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE64_79UL | 23KV忠64線(KE64) 79RY U/L | FEEDER | D18/22/KE64/79UL |  |  |  | DNP | 411 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE64_LCO | 忠64線(KE64) LCO |  | TapPosMv | [14 empty] | 0791 |  | 0207 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE64_LCO_TAP | 23KV忠64線(KE64) LCO TAP | FEEDER | D18/22/KE64/ADJ |  |  |  | DNP | 412 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE64 | KE64(23KV忠64線) |  | CB | [14 empty] | 0240 |  | 0038 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE64_CB | KE64(23KV忠64線) CB | FEEDER | D18/22/KE64/CB |  |  |  | DNP | 413 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE65 | 忠65線(KE65) |  | PHA | [14 empty] | 0253 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE65_PHA | 23KV忠65線(KE65) 相間RY | FEEDER | D18/22/KE65/PHA |  |  |  | DNP | 414 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE65 | 忠65線(KE65) |  | GDA | [14 empty] | 0254 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE65_GDA | 23KV忠65線(KE65) 接地RY | FEEDER | D18/22/KE65/GDA |  |  |  | DNP | 415 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE65 | 忠65線(KE65) 79RY |  | 79UL | [14 empty] | 0792 |  | 0208 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE65_79UL | 23KV忠65線(KE65) 79RY U/L | FEEDER | D18/22/KE65/79UL |  |  |  | DNP | 416 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE65_LCO | 忠65線(KE65) LCO |  | TapPosMv | [14 empty] | 0793 |  | 0209 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE65_LCO_TAP | 23KV忠65線(KE65) LCO TAP | FEEDER | D18/22/KE65/ADJ |  |  |  | DNP | 417 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE65 | KE65(23KV忠65線) |  | CB | [14 empty] | 0252 |  | 0042 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE65_CB | KE65(23KV忠65線) CB | FEEDER | D18/22/KE65/CB |  |  |  | DNP | 418 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE66 | 忠66線(KE66) |  | PHA | [14 empty] | 0256 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE66_PHA | 23KV忠66線(KE66) 相間RY | FEEDER | D18/22/KE66/PHA |  |  |  | DNP | 419 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE66 | 忠66線(KE66) |  | GDA | [14 empty] | 0257 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE66_GDA | 23KV忠66線(KE66) 接地RY | FEEDER | D18/22/KE66/GDA |  |  |  | DNP | 420 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE66 | 忠66線(KE66) 79RY |  | 79UL | [14 empty] | 0794 |  | 0210 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE66_79UL | 23KV忠66線(KE66) 79RY U/L | FEEDER | D18/22/KE66/79UL |  |  |  | DNP | 421 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE66_LCO | 忠66線(KE66) LCO |  | TapPosMv | [14 empty] | 0795 |  | 0211 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE66_LCO_TAP | 23KV忠66線(KE66) LCO TAP | FEEDER | D18/22/KE66/ADJ |  |  |  | DNP | 422 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE66 | KE66(23KV忠66線) |  | CB | [14 empty] | 0255 |  | 0043 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE66_CB | KE66(23KV忠66線) CB | FEEDER | D18/22/KE66/CB |  |  |  | DNP | 423 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE67 | 忠67線(KE67) |  | PHA | [14 empty] | 0259 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE67_PHA | 23KV忠67線(KE67) 相間RY | FEEDER | D18/22/KE67/PHA |  |  |  | DNP | 424 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE67 | 忠67線(KE67) |  | GDA | [14 empty] | 0260 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE67_GDA | 23KV忠67線(KE67) 接地RY | FEEDER | D18/22/KE67/GDA |  |  |  | DNP | 425 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE67 | 忠67線(KE67) 79RY |  | 79UL | [14 empty] | 0796 |  | 0212 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE67_79UL | 23KV忠67線(KE67) 79RY U/L | FEEDER | D18/22/KE67/79UL |  |  |  | DNP | 426 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE67_LCO | 忠67線(KE67) LCO |  | TapPosMv | [14 empty] | 0797 |  | 0213 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE67_LCO_TAP | 23KV忠67線(KE67) LCO TAP | FEEDER | D18/22/KE67/ADJ |  |  |  | DNP | 427 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE67 | KE67(23KV忠67線) |  | CB | [14 empty] | 0258 |  | 0044 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE67_CB | KE67(23KV忠67線) CB | FEEDER | D18/22/KE67/CB |  |  |  | DNP | 428 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE68 | 忠68線(KE68) |  | PHA | [14 empty] | 0262 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE68_PHA | 23KV忠68線(KE68) 相間RY | FEEDER | D18/22/KE68/PHA |  |  |  | DNP | 429 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE68 | 忠68線(KE68) |  | GDA | [14 empty] | 0263 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE68_GDA | 23KV忠68線(KE68) 接地RY | FEEDER | D18/22/KE68/GDA |  |  |  | DNP | 430 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE68 | 忠68線(KE68) 79RY |  | 79UL | [14 empty] | 0798 |  | 0214 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE68_79UL | 23KV忠68線(KE68) 79RY U/L | FEEDER | D18/22/KE68/79UL |  |  |  | DNP | 431 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE68_LCO | 忠68線(KE68) LCO |  | TapPosMv | [14 empty] | 0799 |  | 0215 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE68_LCO_TAP | 23KV忠68線(KE68) LCO TAP | FEEDER | D18/22/KE68/ADJ |  |  |  | DNP | 432 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE68 | KE68(23KV忠68線) |  | CB | [14 empty] | 0261 |  | 0045 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE68_CB | KE68(23KV忠68線) CB | FEEDER | D18/22/KE68/CB |  |  |  | DNP | 433 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE71 | 忠71線(KE71) |  | PHA | [14 empty] | 0268 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE71_PHA | 23KV忠71線(KE71) 相間RY | FEEDER | D18/22/KE71/PHA |  |  |  | DNP | 434 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE71 | 忠71線(KE71) |  | GDA | [14 empty] | 0269 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE71_GDA | 23KV忠71線(KE71) 接地RY | FEEDER | D18/22/KE71/GDA |  |  |  | DNP | 435 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE71 | 忠71線(KE71) 79RY |  | 79UL | [14 empty] | 0800 |  | 0216 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE71_79UL | 23KV忠71線(KE71) 79RY U/L | FEEDER | D18/22/KE71/79UL |  |  |  | DNP | 436 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE71_LCO | 忠71線(KE71) LCO |  | TapPosMv | [14 empty] | 0801 |  | 0217 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE71_LCO_TAP | 23KV忠71線(KE71) LCO TAP | FEEDER | D18/22/KE71/ADJ |  |  |  | DNP | 437 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE71 | KE71(23KV忠71線) |  | CB | [14 empty] | 0267 |  | 0047 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE71_CB | KE71(23KV忠71線) CB | FEEDER | D18/22/KE71/CB |  |  |  | DNP | 438 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE72 | 忠72線(KE72) |  | PHA | [14 empty] | 0271 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE72_PHA | 23KV忠72線(KE72) 相間RY | FEEDER | D18/22/KE72/PHA |  |  |  | DNP | 439 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE72 | 忠72線(KE72) |  | GDA | [14 empty] | 0272 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE72_GDA | 23KV忠72線(KE72) 接地RY | FEEDER | D18/22/KE72/GDA |  |  |  | DNP | 440 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE72 | 忠72線(KE72) 79RY |  | 79UL | [14 empty] | 0802 |  | 0218 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE72_79UL | 23KV忠72線(KE72) 79RY U/L | FEEDER | D18/22/KE72/79UL |  |  |  | DNP | 441 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE72_LCO | 忠72線(KE72) LCO |  | TapPosMv | [14 empty] | 0803 |  | 0219 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE72_LCO_TAP | 23KV忠72線(KE72) LCO TAP | FEEDER | D18/22/KE72/ADJ |  |  |  | DNP | 442 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE72 | KE72(23KV忠72線) |  | CB | [14 empty] | 0270 |  | 0048 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE72_CB | KE72(23KV忠72線) CB | FEEDER | D18/22/KE72/CB |  |  |  | DNP | 443 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE73 | 忠73線(KE73) |  | PHA | [14 empty] | 0274 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE73_PHA | 23KV忠73線(KE73) 相間RY | FEEDER | D18/22/KE73/PHA |  |  |  | DNP | 444 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE73 | 忠73線(KE73) |  | GDA | [14 empty] | 0275 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE73_GDA | 23KV忠73線(KE73) 接地RY | FEEDER | D18/22/KE73/GDA |  |  |  | DNP | 445 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE73 | 忠73線(KE73) 79RY |  | 79UL | [14 empty] | 0804 |  | 0220 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE73_79UL | 23KV忠73線(KE73) 79RY U/L | FEEDER | D18/22/KE73/79UL |  |  |  | DNP | 446 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE73_LCO | 忠73線(KE73) LCO |  | TapPosMv | [14 empty] | 0805 |  | 0221 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE73_LCO_TAP | 23KV忠73線(KE73) LCO TAP | FEEDER | D18/22/KE73/ADJ |  |  |  | DNP | 447 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE73 | KE73(23KV忠73線) |  | CB | [14 empty] | 0273 |  | 0049 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE73_CB | KE73(23KV忠73線) CB | FEEDER | D18/22/KE73/CB |  |  |  | DNP | 448 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE74 | 忠74線(KE74) |  | PHA | [14 empty] | 0277 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE74_PHA | 23KV忠74線(KE74) 相間RY | FEEDER | D18/22/KE74/PHA |  |  |  | DNP | 449 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE74 | 忠74線(KE74) |  | GDA | [14 empty] | 0278 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE74_GDA | 23KV忠74線(KE74) 接地RY | FEEDER | D18/22/KE74/GDA |  |  |  | DNP | 450 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE74 | 忠74線(KE74) 79RY |  | 79UL | [14 empty] | 0806 |  | 0222 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE74_79UL | 23KV忠74線(KE74) 79RY U/L | FEEDER | D18/22/KE74/79UL |  |  |  | DNP | 451 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE74_LCO | 忠74線(KE74) LCO |  | TapPosMv | [14 empty] | 0807 |  | 0223 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE74_LCO_TAP | 23KV忠74線(KE74) LCO TAP | FEEDER | D18/22/KE74/ADJ |  |  |  | DNP | 452 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE74 | KE74(23KV忠74線) |  | CB | [14 empty] | 0276 |  | 0050 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE74_CB | KE74(23KV忠74線) CB | FEEDER | D18/22/KE74/CB |  |  |  | DNP | 453 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE75 | 忠75線(KE75) |  | PHA | [14 empty] | 0286 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE75_PHA | 23KV忠75線(KE75) 相間RY | FEEDER | D18/22/KE75/PHA |  |  |  | DNP | 454 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE75 | 忠75線(KE75) |  | GDA | [14 empty] | 0287 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE75_GDA | 23KV忠75線(KE75) 接地RY | FEEDER | D18/22/KE75/GDA |  |  |  | DNP | 455 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE75 | 忠75線(KE75) 79RY |  | 79UL | [14 empty] | 0808 |  | 0224 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE75_79UL | 23KV忠75線(KE75) 79RY U/L | FEEDER | D18/22/KE75/79UL |  |  |  | DNP | 456 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE75_LCO | 忠75線(KE75) LCO |  | TapPosMv | [14 empty] | 0809 |  | 0225 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE75_LCO_TAP | 23KV忠75線(KE75) LCO TAP | FEEDER | D18/22/KE75/ADJ |  |  |  | DNP | 457 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE75 | KE75(23KV忠75線) |  | CB | [14 empty] | 0285 |  | 0053 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE75_CB | KE75(23KV忠75線) CB | FEEDER | D18/22/KE75/CB |  |  |  | DNP | 458 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE76 | 忠76線(KE76) |  | PHA | [14 empty] | 0289 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE76_PHA | 23KV忠76線(KE76) 相間RY | FEEDER | D18/22/KE76/PHA |  |  |  | DNP | 459 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE76 | 忠76線(KE76) |  | GDA | [14 empty] | 0290 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE76_GDA | 23KV忠76線(KE76) 接地RY | FEEDER | D18/22/KE76/GDA |  |  |  | DNP | 460 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE76 | 忠76線(KE76) 79RY |  | 79UL | [14 empty] | 0810 |  | 0226 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE76_79UL | 23KV忠76線(KE76) 79RY U/L | FEEDER | D18/22/KE76/79UL |  |  |  | DNP | 461 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE76_LCO | 忠76線(KE76) LCO |  | TapPosMv | [14 empty] | 0811 |  | 0227 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE76_LCO_TAP | 23KV忠76線(KE76) LCO TAP | FEEDER | D18/22/KE76/ADJ |  |  |  | DNP | 462 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE76 | KE76(23KV忠76線) |  | CB | [14 empty] | 0288 |  | 0054 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE76_CB | KE76(23KV忠76線) CB | FEEDER | D18/22/KE76/CB |  |  |  | DNP | 463 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE77 | 忠77線(KE77) |  | PHA | [14 empty] | 0292 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE77_PHA | 23KV忠77線(KE77) 相間RY | FEEDER | D18/22/KE77/PHA |  |  |  | DNP | 464 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE77 | 忠77線(KE77) |  | GDA | [14 empty] | 0293 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE77_GDA | 23KV忠77線(KE77) 接地RY | FEEDER | D18/22/KE77/GDA |  |  |  | DNP | 465 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE77 | 忠77線(KE77) 79RY |  | 79UL | [14 empty] | 0812 |  | 0228 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE77_79UL | 23KV忠77線(KE77) 79RY U/L | FEEDER | D18/22/KE77/79UL |  |  |  | DNP | 466 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE77_LCO | 忠77線(KE77) LCO |  | TapPosMv | [14 empty] | 0813 |  | 0229 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE77_LCO_TAP | 23KV忠77線(KE77) LCO TAP | FEEDER | D18/22/KE77/ADJ |  |  |  | DNP | 467 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE77 | KE77(23KV忠77線) |  | CB | [14 empty] | 0291 |  | 0055 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE77_CB | KE77(23KV忠77線) CB | FEEDER | D18/22/KE77/CB |  |  |  | DNP | 468 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | KE78 | 忠78線(KE78) |  | PHA | [14 empty] | 0295 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE78_PHA | 23KV忠78線(KE78) 相間RY | FEEDER | D18/22/KE78/PHA |  |  |  | DNP | 469 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE78 | 忠78線(KE78) |  | GDA | [14 empty] | 0296 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE78_GDA | 23KV忠78線(KE78) 接地RY | FEEDER | D18/22/KE78/GDA |  |  |  | DNP | 470 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE78 | 忠78線(KE78) 79RY |  | 79UL | [14 empty] | 0814 |  | 0230 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE78_79UL | 23KV忠78線(KE78) 79RY U/L | FEEDER | D18/22/KE78/79UL |  |  |  | DNP | 471 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 22 | 22kV | KE78_LCO | 忠78線(KE78) LCO |  | TapPosMv | [14 empty] | 0815 |  | 0231 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE78_LCO_TAP | 23KV忠78線(KE78) LCO TAP | FEEDER | D18/22/KE78/ADJ |  |  |  | DNP | 472 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D18 | 忠孝DS | 22 | 22kV | KE78 | KE78(23KV忠78線) |  | CB | [14 empty] | 0294 |  | 0056 | [8 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE78_CB | KE78(23KV忠78線) CB | FEEDER | D18/22/KE78/CB |  |  |  | DNP | 473 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 100 | TIE(100) |  | CB | [14 empty] | 0210 |  | 0028 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.100_CB | 100(TIE) CB | TIE | D18/22/100/CB |  |  |  | DNP | 474 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | 100 | TIE(100) |  | 51A | [14 empty] | 0211 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.100_51A | 23KV TIE(100) 51RY | TIE | D18/22/100/PHA |  |  |  | DNP | 475 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 100 | TIE(100) |  | 51NA | [14 empty] | 0212 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.100_51NA | 23KV TIE(100) 51N RY | TIE | D18/22/100/GDA |  |  |  | DNP | 476 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [14 empty] | 0040 |  | 0011 | [8 empty] | 161KV_S | [8 empty] | 忠孝DS.1500_CB | 1500(TIE) CB | TIE | D18/161/1500/CB |  |  |  | DNP | 477 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 1500 | TIE(1500) |  | 50A | [14 empty] | 0041 | [10 empty] | 161KV_S | [8 empty] | 忠孝DS.1500_50A | 161KV TIE(1500) 50RY | TIE | D18/161/1500/50A |  |  |  | DNP | 478 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [13 empty] | 0688 | 689 | 0088 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.1501_DS | 1501(TIE) DS | TIE | D18/161/1500/DS1 |  |  |  | DNP | 479 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D18 | 忠孝DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [13 empty] | 0690 | 691 | 0089 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.1502_DS | 1502(TIE) DS | TIE | D18/161/1500/DS2 |  |  |  | DNP | 480 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D18 | 忠孝DS | 0 |  | 1500 | TIE(1500) |  | 50SA | [14 empty] | 0578 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.1500_50SA | 161KV TIE(1500) 50RY 測試/正常 | TIE | D18/161/1500/50SA |  |  |  | DNP | 481 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TEST/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 200 | TIE(200) |  | CB | [14 empty] | 0243 |  | 0039 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.200_CB | 200(TIE) CB | TIE | D18/22/200/CB |  |  |  | DNP | 482 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | 200 | TIE(200) |  | 51A | [14 empty] | 0244 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.200_51A | 23KV TIE(200) 51RY | TIE | D18/22/200/PHA |  |  |  | DNP | 483 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 200 | TIE(200) |  | 51NA | [14 empty] | 0245 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.200_51NA | 23KV TIE(200) 51N RY | TIE | D18/22/200/GDA |  |  |  | DNP | 484 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 300 | TIE(300) |  | CB | [14 empty] | 0279 |  | 0051 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.300_CB | 300(TIE) CB | TIE | D18/22/300/CB |  |  |  | DNP | 485 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | 300 | TIE(300) |  | 51A | [14 empty] | 0280 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.300_51A | 23KV TIE(300) 51RY | TIE | D18/22/300/PHA |  |  |  | DNP | 486 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 300 | TIE(300) |  | 51NA | [14 empty] | 0281 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.300_51NA | 23KV TIE(300) 51N RY | TIE | D18/22/300/GDA |  |  |  | DNP | 487 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 390 | #1SSTR(390) |  | CB | [14 empty] | 0195 |  | 0023 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.390_CB | 390(#1SSTR) CB | OTHER | D18/22/390/CB |  |  |  | DNP | 488 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 1SSTR | #1SSTR |  | 51A | [14 empty] | 0196 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#1SSTR_51A | #1SSTR 51RY | OTHER | D18/22/390/PHA |  |  |  | DNP | 489 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 1SSTR | #1SSTR |  | 51NA | [14 empty] | 0197 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | D18/22/390/GDA |  |  |  | DNP | 490 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 490 | #2SSTR(490) |  | CB | [14 empty] | 0246 |  | 0040 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.490_CB | 490(#2SSTR) CB | OTHER | D18/22/490/CB |  |  |  | DNP | 491 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 2SSTR | #2SSTR |  | 51A | [14 empty] | 0247 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#2SSTR_51A | #2SSTR 51RY | OTHER | D18/22/490/PHA |  |  |  | DNP | 492 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 2SSTR | #2SSTR |  | 51NA | [14 empty] | 0248 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | D18/22/490/GDA |  |  |  | DNP | 493 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB | [14 empty] | 0048 |  | 0012 | [8 empty] | 161KV_S | [8 empty] | 忠孝DS.1750_CB | 1750(#1DTR) CB | MTR | D18/161/1750/CB |  |  |  | DNP | 494 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 310 | #1DTR(310) |  | CB | [14 empty] | 0056 |  | 0016 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.310_CB | 310(#1DTR) CB | MTR | D18/22/310/CB |  |  |  | DNP | 495 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 320 | #1DTR(320) |  | CB | [14 empty] | 0059 |  | 0017 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.320_CB | 320(#1DTR) CB | MTR | D18/22/320/CB |  |  |  | DNP | 496 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 1DTR | #1DTR |  | PHA | [14 empty] | 0052 | [10 empty] | 161KV_S | [8 empty] | 忠孝DS.#1DTR_PHA | #1DTR PHA | MTR | D18//1DTR/PHA |  |  |  | DNP | 497 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 1DTR | #1DTR |  | GDA | [14 empty] | 0055 | [10 empty] | 161KV_S | [8 empty] | 忠孝DS.#1DTR_GDA | #1DTR GDA | MTR | D18//1DTR/GDA |  |  |  | DNP | 498 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 1DTR | #1DTR |  | 51ZA | [14 empty] | 0051 | [10 empty] | 161KV_S | [8 empty] | 忠孝DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | D18//1DTR/51ZA |  |  |  | DNP | 499 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 1DTR | #1DTR |  | 1_87UL1 | [14 empty] | 0529 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#1DTR_87UL1 | #1DTR 第一套87RY U/L | MTR | D18//1DTR/1_87UL1 |  |  |  | DNP | 500 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 0 |  | 310 | #1DTR(310) |  | PHA | [14 empty] | 0057 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.310_PHA | #1DTR二次側(310) PHA | MTR | D18/22/310/PHA |  |  |  | DNP | 501 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 320 | #1DTR(320) |  | PHA | [14 empty] | 0060 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.320_PHA | #1DTR二次側(320) PHA | MTR | D18/22/320/PHA |  |  |  | DNP | 502 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 1DTR | #1DTR |  | 96PA | [14 empty] | 0050 | [10 empty] | 161KV_S | [8 empty] | 忠孝DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | D18//1DTR/96PA |  |  |  | DNP | 503 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 1DTR | #1DTR |  | 96D | [14 empty] | 0537 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#1DTR_96D | #1DTR 96D RY | MTR | D18//1DTR/96D |  |  |  | DNP | 504 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 1DTR | #1DTR |  | 96P | [14 empty] | 0538 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#1DTR_96P | #1DTR 96P RY | MTR | D18//1DTR/96P |  |  |  | DNP | 505 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 1DTR | #1DTR |  | 63Q | [14 empty] | 0539 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#1DTR_63Q | #1DTR 63Q RY | MTR | D18//1DTR/63Q |  |  |  | DNP | 506 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 1DTR | #1DTR |  | 96B1 | [14 empty] | 0535 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | D18//1DTR/96B1 |  |  |  | DNP | 507 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 1DTR | #1DTR |  | 96B2 | [14 empty] | 0536 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | D18//1DTR/96B2 |  |  |  | DNP | 508 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 1DTR | #1DTR |  | TRA | [14 empty] | 0552 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#1DTR_TRA | #1DTR 重故障 | MTR | D18//1DTR/TRA |  |  |  | DNP | 509 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 1DTR | #1DTR |  | TRF | [14 empty] | 0553 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#1DTR_TRF | #1DTR 輕故障 | MTR | D18//1DTR/TRF |  |  |  | DNP | 510 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 1DTR | #1DTR |  | SupLocal | [14 empty] | 0550 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#1DTR_S/L | #1DTR OLTC S/L | MTR | D18//1DTR/SupLocal |  |  |  | DNP | 511 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D18 | 忠孝DS | 0 |  | 1DTR | #1DTR |  | A_M | [14 empty] | 0551 |  | 0098 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.#1DTR_A/M | #1DTR OLTC A/M | MTR | D18//1DTR/Tap Chan |  |  |  | DNP | 512 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D18 | 忠孝DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 | [13 empty] | 0692 | 693 | 0090 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.1751_DS | 1751(#1DTR) DS | MTR | D18/161/1750/DS1 |  |  |  | DNP | 513 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D18 | 忠孝DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 | [13 empty] | 0694 | 695 | 0091 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.1752_DS | 1752(#1DTR) DS | MTR | D18/161/1750/DS2 |  |  |  | DNP | 514 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D18 | 忠孝DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB | [14 empty] | 0062 |  | 0013 | [8 empty] | 161KV_S | [8 empty] | 忠孝DS.1760_CB | 1760(#2DTR) CB | MTR | D18/161/1760/CB |  |  |  | DNP | 515 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 330 | #2DTR(330) |  | CB | [14 empty] | 0070 |  | 0018 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.330_CB | 330(#2DTR) CB | MTR | D18/22/330/CB |  |  |  | DNP | 516 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 340 | #2DTR(340) |  | CB | [14 empty] | 0073 |  | 0019 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.340_CB | 340(#2DTR) CB | MTR | D18/22/340/CB |  |  |  | DNP | 517 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 2DTR | #2DTR |  | PHA | [14 empty] | 0066 | [10 empty] | 161KV_S | [8 empty] | 忠孝DS.#2DTR_PHA | #2DTR PHA | MTR | D18//2DTR/PHA |  |  |  | DNP | 518 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 2DTR | #2DTR |  | GDA | [14 empty] | 0069 | [10 empty] | 161KV_S | [8 empty] | 忠孝DS.#2DTR_GDA | #2DTR GDA | MTR | D18//2DTR/GDA |  |  |  | DNP | 519 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 2DTR | #2DTR |  | 51ZA | [14 empty] | 0065 | [10 empty] | 161KV_S | [8 empty] | 忠孝DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | D18//2DTR/51ZA |  |  |  | DNP | 520 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 2DTR | #2DTR |  | 1_87UL1 | [14 empty] | 0534 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#2DTR_87UL1 | #2DTR 第一套87RY U/L | MTR | D18//2DTR/1_87UL1 |  |  |  | DNP | 521 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 0 |  | 330 | #2DTR(330) |  | PHA | [14 empty] | 0071 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.330_PHA | #2DTR二次側(330) PHA | MTR | D18/22/330/PHA |  |  |  | DNP | 522 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 340 | #2DTR(340) |  | PHA | [14 empty] | 0074 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.340_PHA | #2DTR二次側(340) PHA | MTR | D18/22/340/PHA |  |  |  | DNP | 523 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 2DTR | #2DTR |  | 96PA | [14 empty] | 0064 | [10 empty] | 161KV_S | [8 empty] | 忠孝DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | D18//2DTR/96PA |  |  |  | DNP | 524 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 2DTR | #2DTR |  | 96D | [14 empty] | 0542 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#2DTR_96D | #2DTR 96D RY | MTR | D18//2DTR/96D |  |  |  | DNP | 525 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 2DTR | #2DTR |  | 96P | [14 empty] | 0543 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#2DTR_96P | #2DTR 96P RY | MTR | D18//2DTR/96P |  |  |  | DNP | 526 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 2DTR | #2DTR |  | 63Q | [14 empty] | 0544 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#2DTR_63Q | #2DTR 63Q RY | MTR | D18//2DTR/63Q |  |  |  | DNP | 527 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 2DTR | #2DTR |  | 96B1 | [14 empty] | 0540 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | D18//2DTR/96B1 |  |  |  | DNP | 528 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 2DTR | #2DTR |  | 96B2 | [14 empty] | 0541 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | D18//2DTR/96B2 |  |  |  | DNP | 529 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 2DTR | #2DTR |  | TRA | [14 empty] | 0556 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#2DTR_TRA | #2DTR 重故障 | MTR | D18//2DTR/TRA |  |  |  | DNP | 530 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 2DTR | #2DTR |  | TRF | [14 empty] | 0557 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#2DTR_TRF | #2DTR 輕故障 | MTR | D18//2DTR/TRF |  |  |  | DNP | 531 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 2DTR | #2DTR |  | SupLocal | [14 empty] | 0554 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#2DTR_S/L | #2DTR OLTC S/L | MTR | D18//2DTR/SupLocal |  |  |  | DNP | 532 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D18 | 忠孝DS | 0 |  | 2DTR | #2DTR |  | A_M | [14 empty] | 0555 |  | 0100 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.#2DTR_A/M | #2DTR OLTC A/M | MTR | D18//2DTR/Tap Chan |  |  |  | DNP | 533 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D18 | 忠孝DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 | [13 empty] | 0696 | 697 | 0092 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.1761_DS | 1761(#2DTR) DS | MTR | D18/161/1760/DS1 |  |  |  | DNP | 534 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D18 | 忠孝DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 | [13 empty] | 0698 | 699 | 0093 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.1762_DS | 1762(#2DTR) DS | MTR | D18/161/1760/DS2 |  |  |  | DNP | 535 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D18 | 忠孝DS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB | [14 empty] | 0076 |  | 0014 | [8 empty] | 161KV_S | [8 empty] | 忠孝DS.1770_CB | 1770(#3DTR) CB | MTR | D18/161/1770/CB |  |  |  | DNP | 536 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 350 | #3DTR(350) |  | CB | [14 empty] | 0084 |  | 0020 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.350_CB | 350(#3DTR) CB | MTR | D18/22/350/CB |  |  |  | DNP | 537 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 360 | #3DTR(360) |  | CB | [14 empty] | 0087 |  | 0021 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.360_CB | 360(#3DTR) CB | MTR | D18/22/360/CB |  |  |  | DNP | 538 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 3DTR | #3DTR |  | PHA | [14 empty] | 0080 | [10 empty] | 161KV_S | [8 empty] | 忠孝DS.#3DTR_PHA | #3DTR PHA | MTR | D18//3DTR/PHA |  |  |  | DNP | 539 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 3DTR | #3DTR |  | GDA | [14 empty] | 0083 | [10 empty] | 161KV_S | [8 empty] | 忠孝DS.#3DTR_GDA | #3DTR GDA | MTR | D18//3DTR/GDA |  |  |  | DNP | 540 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 3DTR | #3DTR |  | 51ZA | [14 empty] | 0079 | [10 empty] | 161KV_S | [8 empty] | 忠孝DS.#3DTR_51ZA | #3DTR 51Z RY | MTR | D18//3DTR/51ZA |  |  |  | DNP | 541 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 3DTR | #3DTR |  | 1_87UL1 | [14 empty] | 0572 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#3DTR_87UL1 | #3DTR 第一套87RY U/L | MTR | D18//3DTR/1_87UL1 |  |  |  | DNP | 542 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 0 |  | 350 | #3DTR(350) |  | PHA | [14 empty] | 0085 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.350_PHA | #3DTR二次側(350) PHA | MTR | D18/22/350/PHA |  |  |  | DNP | 543 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 360 | #3DTR(360) |  | PHA | [14 empty] | 0088 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.360_PHA | #3DTR二次側(360) PHA | MTR | D18/22/360/PHA |  |  |  | DNP | 544 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 3DTR | #3DTR |  | 96PA | [14 empty] | 0078 | [10 empty] | 161KV_S | [8 empty] | 忠孝DS.#3DTR_96PA | #3DTR 機械保護動作 | MTR | D18//3DTR/96PA |  |  |  | DNP | 545 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 3DTR | #3DTR |  | 96D | [14 empty] | 0547 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#3DTR_96D | #3DTR 96D RY | MTR | D18//3DTR/96D |  |  |  | DNP | 546 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 3DTR | #3DTR |  | 96P | [14 empty] | 0548 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#3DTR_96P | #3DTR 96P RY | MTR | D18//3DTR/96P |  |  |  | DNP | 547 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 3DTR | #3DTR |  | 63Q | [14 empty] | 0549 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#3DTR_63Q | #3DTR 63Q RY | MTR | D18//3DTR/63Q |  |  |  | DNP | 548 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 3DTR | #3DTR |  | 96B1 | [14 empty] | 0545 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#3DTR_96B1 | #3DTR 96B1 RY | MTR | D18//3DTR/96B1 |  |  |  | DNP | 549 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 3DTR | #3DTR |  | 96B2 | [14 empty] | 0546 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#3DTR_96B2 | #3DTR 96B2 RY | MTR | D18//3DTR/96B2 |  |  |  | DNP | 550 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 3DTR | #3DTR |  | TRA | [14 empty] | 0561 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#3DTR_TRA | #3DTR 重故障 | MTR | D18//3DTR/TRF |  |  |  | DNP | 551 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 3DTR | #3DTR |  | TRF | [14 empty] | 0560 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#3DTR_TRF | #3DTR 輕故障 | MTR | D18//3DTR/TRA |  |  |  | DNP | 552 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 3DTR | #3DTR |  | SupLocal | [14 empty] | 0558 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#3DTR_S/L | #3DTR OLTC S/L | MTR | D18//3DTR/SupLocal |  |  |  | DNP | 553 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D18 | 忠孝DS | 0 |  | 3DTR | #3DTR |  | A_M | [14 empty] | 0559 |  | 0102 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.#3DTR_A/M | #3DTR OLTC A/M | MTR | D18//3DTR/Tap Chan |  |  |  | DNP | 554 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D18 | 忠孝DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 | [13 empty] | 0700 | 701 | 0094 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.1771_DS | 1771(#3DTR) DS | MTR | D18/161/1770/DS1 |  |  |  | DNP | 555 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D18 | 忠孝DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 | [13 empty] | 0702 | 703 | 0095 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.1772_DS | 1772(#3DTR) DS | MTR | D18/161/1770/DS2 |  |  |  | DNP | 556 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D18 | 忠孝DS | 22 | 22kV | 210 | #1SC(210) |  | CB | [14 empty] | 0192 |  | 0022 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.210_CB | 210(23KV #1SC) CB | SC | D18/22/210/CB |  |  |  | DNP | 557 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 210 | #1SC(210) |  | SCA | [14 empty] | 0193 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.210_SCA | 23KV #1SC 51,51N RY | SC | D18/22/210/SCA |  |  |  | DNP | 558 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 210 | #1SC(210) |  | UVA | [14 empty] | 0194 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.210_OUVA | 23KV #1SC 27,59RY(欠壓或過壓) | SC | D18/22/210/UVA |  |  |  | DNP | 559 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 220 | #2SC(220) |  | CB | [14 empty] | 0213 |  | 0029 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.220_CB | 220(23KV #2SC) CB | SC | D18/22/220/CB |  |  |  | DNP | 560 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 220 | #2SC(220) |  | SCA | [14 empty] | 0214 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.220_SCA | 23KV #2SC 51,51N RY | SC | D18/22/220/SCA |  |  |  | DNP | 561 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 220 | #2SC(220) |  | UVA | [14 empty] | 0215 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.220_OUVA | 23KV #2SC 27,59RY(欠壓或過壓) | SC | D18/22/220/UVA |  |  |  | DNP | 562 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 230 | #3SC(230) |  | CB | [14 empty] | 0228 |  | 0034 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.230_CB | 230(23KV #3SC) CB | SC | D18/22/230/CB |  |  |  | DNP | 563 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 230 | #3SC(230) |  | SCA | [14 empty] | 0229 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.230_SCA | 23KV #3SC 51,51N RY | SC | D18/22/230/SCA |  |  |  | DNP | 564 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 230 | #3SC(230) |  | UVA | [14 empty] | 0230 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.230_OUVA | 23KV #3SC 27,59RY(欠壓或過壓) | SC | D18/22/230/UVA |  |  |  | DNP | 565 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 240 | #4SC(240) |  | CB | [14 empty] | 0249 |  | 0041 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.240_CB | 240(23KV #4SC) CB | SC | D18/22/240/CB |  |  |  | DNP | 566 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 240 | #4SC(240) |  | SCA | [14 empty] | 0250 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.240_SCA | 23KV #4SC 51,51N RY | SC | D18/22/240/SCA |  |  |  | DNP | 567 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 240 | #4SC(240) |  | UVA | [14 empty] | 0251 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.240_OUVA | 23KV #4SC 27,59RY(欠壓或過壓) | SC | D18/22/240/UVA |  |  |  | DNP | 568 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 250 | #5SC(250) |  | CB | [14 empty] | 0264 |  | 0046 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.250_CB | 250(23KV #5SC) CB | SC | D18/22/250/CB |  |  |  | DNP | 569 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 250 | #5SC(250) |  | SCA | [14 empty] | 0265 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.250_SCA | 23KV #5SC 51,51N RY | SC | D18/22/250/SCA |  |  |  | DNP | 570 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 250 | #5SC(250) |  | UVA | [14 empty] | 0266 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.250_OUVA | 23KV #5SC 27,59RY(欠壓或過壓) | SC | D18/22/250/UVA |  |  |  | DNP | 571 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 260 | #6SC(260) |  | CB | [14 empty] | 0282 |  | 0052 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.260_CB | 260(23KV #6SC) CB | SC | D18/22/260/CB |  |  |  | DNP | 572 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 22 | 22kV | 260 | #6SC(260) |  | SCA | [14 empty] | 0283 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.260_SCA | 23KV #6SC 51,51N RY | SC | D18/22/260/SCA |  |  |  | DNP | 573 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 260 | #6SC(260) |  | UVA | [14 empty] | 0284 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.260_OUVA | 23KV #6SC 27,59RY(欠壓或過壓) | SC | D18/22/260/UVA |  |  |  | DNP | 574 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1611BUS | #1BUS |  | VUA | [14 empty] | 0618 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | D18/161/1BUS/BUS_VUA |  |  |  | DNP | 575 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1611BUS | #1BUS |  | 87A | [14 empty] | 0042 | [10 empty] | 161KV_S | [8 empty] | 忠孝DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | D18/161/1BUS/87A |  |  |  | DNP | 576 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1612BUS | #2BUS |  | VUA | [14 empty] | 0619 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | D18/161/2BUS/BUS_VUA |  |  |  | DNP | 577 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1612BUS | #2BUS |  | 87A | [14 empty] | 0043 | [10 empty] | 161KV_S | [8 empty] | 忠孝DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | D18/161/2BUS/87A |  |  |  | DNP | 578 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 11_ | 11/ |  | CBA | [14 empty] | 0637 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | D18/22/ComPoint/CBA |  |  |  | DNP | 579 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 11_ | 11/ |  | CBF | [14 empty] | 0638 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | D18/22/ComPoint/CBF |  |  |  | DNP | 580 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV |  |  |  | CBA | [14 empty] | 0614 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.161KV_CBA | 161KV斷路器重故障 | OTHER | D18/161/ComPoint/CBA |  |  |  | DNP | 581 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV |  |  |  | CBF | [14 empty] | 0615 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | D18/161/ComPoint/CBF |  |  |  | DNP | 582 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | LINE | LINE |  | RCA | [14 empty] | 0047 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | D18/161/ComPoint/RCA |  |  |  | DNP | 583 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV |  |  |  | COMT | [14 empty] | 0593 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.161空壓機COMT | 161KV空壓機運轉超時警報 | OTHER | D18/0/ComPoint/COMT |  |  |  | DNP | 584 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | _SC | 11/ SC |  | 60A | [14 empty] | 0622 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.23KV_SC_60A | 11/23KV SC 60A | OTHER | D18/22/ComPoint/60A |  |  |  | DNP | 585 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | RTU | RTU |  | SupLocal | [14 empty] | 0513 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.RTU_S/L | RTU SUPY/LOCAL | OTHER | D18/0/RTU/RTU_R_L |  |  |  | DNP | 586 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D18 | 忠孝DS | 0 |  | TEST | TEST |  | CB | [14 empty] | 0512 |  | 0000 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.TEST_CB | TEST CB | OTHER | D18/0/RTU/Test_CB |  |  |  | DNP | 587 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  |  |  |  | Fire1 | [14 empty] | 0605 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.火災警報(1) | 消防火災警報 | OTHER | D18/0/StaDev/Fire1 |  |  |  | DNP | 588 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  |  |  |  | Fire2 | [14 empty] | 0606 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.火災警報(2) | 消防故障警報 | OTHER | D18/0/StaDev/Fire2 |  |  |  | DNP | 589 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  |  |  |  | Fire3 | [14 empty] | 0607 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.火災警報(3) | CO2防護區火警 | OTHER | D18/0/StaDev/Fire3 |  |  |  | DNP | 590 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  |  |  |  | Fire4 | [14 empty] | 0608 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.火災警報(4) | CO2主機故障 | OTHER | D18/0/StaDev/Fire4 |  |  |  | DNP | 591 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  |  |  |  | 火災警報(5) | [14 empty] | 0609 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.火災警報(5) | CO2鋼瓶漏氣 | OTHER | D18/0/StaDev/Fire5 |  |  |  | DNP | 592 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  |  |  |  | OPA | [14 empty] | 0594 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | D18/0/ComPoint/OPA |  |  |  | DNP | 593 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  |  |  |  | 25PFA | [14 empty] | 0591 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER | D18/0/ComPoint/25PFA |  |  |  | DNP | 594 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  |  |  |  | 25TA | [14 empty] | 0592 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | D18/0/ComPoint/25TA |  |  |  | DNP | 595 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  |  |  |  | SUBA | [14 empty] | 0627 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.其他重故障 | 變電所內其他重故障 | OTHER | D18/0/StaDev/PSA |  |  |  | DNP | 596 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  |  |  |  | SUBF | [14 empty] | 0626 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.其他輕故障 | 變電所內其他輕故障 | OTHER | D18/0/StaDev/PSF |  |  |  | DNP | 597 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  |  |  |  | ACB1 | [14 empty] | 0595 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | D18/0/StaDev/ACB1 |  |  |  | DNP | 598 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ON/OFF | ON
D18 | 忠孝DS | 0 |  |  |  |  | ACB2 | [14 empty] | 0596 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | D18/0/StaDev/ACB2 |  |  |  | DNP | 599 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ON/OFF | ON
D18 | 忠孝DS | 0 |  |  |  |  | ACBA | [14 empty] | 0617 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.所內電源ACBA | 所內電源故障警報 | OTHER | D18/0/StaDev/ACBA |  |  |  | DNP | 600 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 所內電源開關ACB | 所內電源開關ACB |  | ACBT | [14 empty] | 0597 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | D18/0/StaDev/ACBT |  |  |  | DNP | 601 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ON/OFF | OFF
D18 | 忠孝DS | 0 |  |  |  |  | STUV | [14 empty] | 0599 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | D18/0/StaDev/STUV |  |  |  | DNP | 602 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  |  |  |  | CHG1 | [14 empty] | 0620 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.直流充電機故障 | 直流充電機故障 | OTHER | D18/0/StaDev/CHG1 |  |  |  | DNP | 603 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  |  |  |  | DCA | [14 empty] | 0616 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.直流電源DCA | 直流電源故障警報 | OTHER | D18/0/StaDev/DCA |  |  |  | DNP | 604 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  |  |  |  | DCE | [14 empty] | 0621 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.直流電源DCE | 直流電源接地故障警報 | OTHER | D18/0/StaDev/DCE |  |  |  | DNP | 605 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  |  |  |  | CHG2 | [14 empty] | 0628 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | D18/0/StaDev/CHG2 |  |  |  | DNP | 606 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  |  |  |  | CommACF | [14 empty] | 0629 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | D18/0/StaDev/CommACF |  |  |  | DNP | 607 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  |  |  |  | Door1 | [14 empty] | 0600 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.無人化門禁(1) | 無人化門禁(1)圍牆大小門 | OTHER | D18/0/StaDev/Door1 |  |  |  | DNP | 608 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 1DTR | #1DTR |  | 51Z_UL | [14 empty] | 0531 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#1DTR_51ZUL | #1DTR 51Z RY U/L | OTHER | D18//1DTR/51Z_UL |  |  |  | DNP | 609 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 0 |  | 1DTR | #1DTR |  | 81A | [14 empty] | 0054 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#1DTR_81A | #1DTR 81RY動作 | OTHER | D18//1DTR/81A |  |  |  | DNP | 610 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 1DTR | #1DTR |  | 81UL | [14 empty] | 0532 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#1DTR_81UL | #1DTR 81RY U/L | OTHER | D18//1DTR/81UL |  |  |  | DNP | 611 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 0 |  | 1DTR | #1DTR |  | DTR_86A | [14 empty] | 0053 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#1DTR_86A | #1DTR 86(50/50N/51Z/87/96)RY | OTHER | D18//1DTR/DTR_86A |  |  |  | DNP | 612 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 1DTR | #1DTR |  | 1_87UL2 | [14 empty] | 0530 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#1DTR_87UL2 | #1DTR 第二套87RY U/L | OTHER | D18//1DTR/1_87UL2 |  |  |  | DNP | 613 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 0 |  | 1DTR | #1DTR |  | RYFA | [14 empty] | 0581 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#1DTR_RYFA | #1DTR 數位電驛故障 | OTHER | D18//1DTR/RYFA |  |  |  | DNP | 614 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 2DTR | #2DTR |  | 51Z_UL | [14 empty] | 0569 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#2DTR_51ZUL | #2DTR 51Z RY U/L | OTHER | D18//2DTR/51Z_UL |  |  |  | DNP | 615 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 0 |  | 2DTR | #2DTR |  | 81A | [14 empty] | 0068 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#2DTR_81A | #2DTR 81RY動作 | OTHER | D18//2DTR/81A |  |  |  | DNP | 616 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 2DTR | #2DTR |  | 81UL | [14 empty] | 0570 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#2DTR_81UL | #2DTR 81RY U/L | OTHER | D18//2DTR/81UL |  |  |  | DNP | 617 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 0 |  | 2DTR | #2DTR |  | DTR_86A | [14 empty] | 0067 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#2DTR_86A | #2DTR 86(50/50N/51Z/87/96)RY | OTHER | D18//2DTR/DTR_86A |  |  |  | DNP | 618 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 2DTR | #2DTR |  | 1_87UL2 | [14 empty] | 0568 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#2DTR_87UL2 | #2DTR 第二套87RY U/L | OTHER | D18//2DTR/1_87UL2 |  |  |  | DNP | 619 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 0 |  | 2DTR | #2DTR |  | RYFA | [14 empty] | 0582 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#2DTR_RYFA | #2DTR 數位電驛故障 | OTHER | D18//2DTR/RYFA |  |  |  | DNP | 620 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 3DTR | #3DTR |  | 51Z_UL | [14 empty] | 0574 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#3DTR_51ZUL | #3DTR 51Z RY U/L | OTHER | D18//3DTR/51Z_UL |  |  |  | DNP | 621 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 0 |  | 3DTR | #3DTR |  | 81A | [14 empty] | 0082 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#3DTR_81A | #3DTR 81RY動作 | OTHER | D18//3DTR/81A |  |  |  | DNP | 622 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 3DTR | #3DTR |  | 81UL | [14 empty] | 0575 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#3DTR_81UL | #3DTR 81RY U/L | OTHER | D18//3DTR/81UL |  |  |  | DNP | 623 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 0 |  | 3DTR | #3DTR |  | DTR_86A | [14 empty] | 0081 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#3DTR_86A | #3DTR 86(50/50N/51Z/87/96)RY | OTHER | D18//3DTR/DTR_86A |  |  |  | DNP | 624 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 3DTR | #3DTR |  | 1_87UL2 | [14 empty] | 0573 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#3DTR_87UL2 | #3DTR 第二套87RY U/L | OTHER | D18//3DTR/1_87UL2 |  |  |  | DNP | 625 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 0 |  | 3DTR | #3DTR |  | RYFA | [14 empty] | 0583 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.#3DTR_RYFA | #3DTR 數位電驛故障 | OTHER | D18//3DTR/RYFA |  |  |  | DNP | 626 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 11_ | 11/ |  | LOA | [14 empty] | 0639 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.11/23KV_LOA | 11/23KV饋線復閉失敗閉鎖 | OTHER | D18/22/ComPoint/LOA |  |  |  | DNP | 627 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 1510 | 台南忠孝一路(1510) |  | 87A2 | [14 empty] | 0024 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.1510_87A2 | 台南忠孝一路(1510)第二套87RY | OTHER | D18/161/1510/87A2 |  |  |  | DNP | 628 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 1510 | 台南忠孝一路(1510) |  | 87CFA | [14 empty] | 0514 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.1510_87CFA | 台南忠孝一路(1510)87RY通訊故障 | OTHER | D18/161/1510/87CFA |  |  |  | DNP | 629 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 1510 | 台南忠孝一路(1510) |  | RYFA | [14 empty] | 0515 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.1510_RYFA | 台南忠孝一路(1510)數位電驛故障 | OTHER | D18/161/1510/RYFA |  |  |  | DNP | 630 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 1520 | 台南忠孝二路(1520) |  | 87A2 | [14 empty] | 0025 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.1520_87A2 | 台南忠孝二路(1520)第二套87RY | OTHER | D18/161/1520/87A2 |  |  |  | DNP | 631 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 1520 | 台南忠孝二路(1520) |  | 87CFA | [14 empty] | 0516 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.1520_87CFA | 台南忠孝二路(1520)87RY通訊故障 | OTHER | D18/161/1520/87CFA |  |  |  | DNP | 632 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 1520 | 台南忠孝二路(1520) |  | RYFA | [14 empty] | 0517 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.1520_RYFA | 台南忠孝二路(1520)數位電驛故障 | OTHER | D18/161/1520/RYFA |  |  |  | DNP | 633 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 1530 | 忠孝延平線(1530) |  | 87A2 | [14 empty] | 0026 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.1530_87A2 | 忠孝延平線(1530)第二套87RY | OTHER | D18/161/1530/87A2 |  |  |  | DNP | 634 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 1530 | 忠孝延平線(1530) |  | 87CFA | [14 empty] | 0518 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.1530_87CFA | 忠孝延平線(1530)87RY通訊故障 | OTHER | D18/161/1530/87CFA |  |  |  | DNP | 635 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 1530 | 忠孝延平線(1530) |  | RYFA | [14 empty] | 0519 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.1530_RYFA | 忠孝延平線(1530)數位電驛故障 | OTHER | D18/161/1530/RYFA |  |  |  | DNP | 636 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1611BUS | #1BUS |  | 87UL | [14 empty] | 0576 |  | 0148 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | D18/161/1BUS/87UL |  |  |  | DNP | 637 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 161 | 161kV | 1SHR | #1SHR |  | 161#1SHR96PA | [14 empty] | 0094 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.161#1SHR96PA | 161KV #1SHR 機械保護動作 | OTHER | D18/161/1950/96PA |  |  |  | DNP | 638 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1611SHR | #1SHR |  | 51A | [14 empty] | 0093 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.161#1SHR_51A | 161KV #1SHR 51RY | OTHER | D18/161/1950/51A |  |  |  | DNP | 639 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1611SHR | #1SHR |  | 86A | [14 empty] | 0092 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.161#1SHR_86A | 161KV #1SHR 86RY | OTHER | D18/161/1950/1A5Other |  |  |  | DNP | 640 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1611SHR | #1SHR |  | 87A | [14 empty] | 0091 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.161#1SHR_87A | 161KV #1SHR 87RY | OTHER | D18/161/1950/87A |  |  |  | DNP | 641 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1611SHR | #1SHR |  | 1_87UL1 | [14 empty] | 0585 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.161#1SHR_87UL1 | 161KV #1SHR 第一套87RY U/L | OTHER | D18/161/1950/1_87UL1 |  |  |  | DNP | 642 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 161 | 161kV | 1611SHR | #1SHR |  | 1_87UL2 | [14 empty] | 0586 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.161#1SHR_87UL2 | 161KV #1SHR 第二套87RY U/L | OTHER | D18/161/1950/1_87UL2 |  |  |  | DNP | 643 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 161 | 161kV | 1611SHR | #1SHR |  | 96B1 | [14 empty] | 0562 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.161#1SHR_96B1 | 161KV #1SHR 96B1 RY | OTHER | D18/161/1950/96B1 |  |  |  | DNP | 644 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1611SHR | #1SHR |  | 96B2 | [14 empty] | 0563 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.161#1SHR_96B2 | 161KV #1SHR 96B2 RY | OTHER | D18/161/1950/96B2 |  |  |  | DNP | 645 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1611SHR | #1SHR |  | 96D | [14 empty] | 0564 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.161#1SHR_96D | 161KV #1SHR 96D RY | OTHER | D18/161/1950/96D |  |  |  | DNP | 646 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1611SHR | #1SHR |  | 96P | [14 empty] | 0565 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.161#1SHR_96P | 161KV #1SHR 96P RY | OTHER | D18/161/1950/96P |  |  |  | DNP | 647 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1611SHR | #1SHR |  | RYFA | [14 empty] | 0584 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.161#1SHR_RYFA | 161KV #1SHR 數位電驛故障 | OTHER | D18/161/1950/RYFA |  |  |  | DNP | 648 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1611SHR | #1SHR |  | SHRA | [14 empty] | 0567 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.161#1SHR_SRA | 161KV #1SHR 重故障 | OTHER | D18/161/1950/SHRA |  |  |  | DNP | 649 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1611SHR | #1SHR |  | SRF | [14 empty] | 0566 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.161#1SHR_SRF | 161KV #1SHR 輕故障 | OTHER | D18/161/1950/SHRF |  |  |  | DNP | 650 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1612BUS | #2BUS |  | 87UL | [14 empty] | 0577 |  | 0149 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | D18/161/2BUS/87UL |  |  |  | DNP | 651 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 161 | 161kV |  |  |  | OSCA | [14 empty] | 0045 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.161KV_OSCA | 161KV示波器啟動警報 | OTHER | D18/0/ComPoint/OSCA |  |  |  | DNP | 652 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV |  |  |  | OSCF | [14 empty] | 0044 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.161KV_OSCF | 161KV OSC故障/缺紙,電源跳脫 | OTHER | D18/0/ComPoint/OSCF |  |  |  | DNP | 653 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | 1950 | #1SHR(1950) |  | CB | [14 empty] | 0090 |  | 0015 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.1950_CB | 1950(161KV #1SHR) CB | OTHER | D18/161/1950/CB |  |  |  | DNP | 654 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 161 | 161kV | 1950 | #1SHR(1950) |  | DS1 | 1951 | [13 empty] | 0704 | 705 | 0096 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.1951_DS | 1951(161KV #1SHR) DS | OTHER | D18/161/1950/DS1 |  |  |  | DNP | 655 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D18 | 忠孝DS | 161 | 161kV | 1950 | #1SHR(1950) |  | DS2 | 1952 | [13 empty] | 0706 | 707 | 0097 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.1952_DS | 1952(161KV #1SHR) DS | OTHER | D18/161/1950/DS2 |  |  |  | DNP | 656 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D18 | 忠孝DS | 0 |  | 310 | #1DTR(310) |  | 81A | [14 empty] | 0320 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.310_81A | #1DTR(310) 81RY動作 | OTHER | D18/22/310/81A |  |  |  | DNP | 657 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 310 | #1DTR(310) |  | 81UL | [14 empty] | 0848 |  | 0248 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.310_81UL | #1DTR(310) 81RY U/L | OTHER | D18/22/310/81UL |  |  |  | DNP | 658 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 0 |  | 310 | #1DTR(310) |  | GDA | [14 empty] | 0058 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.310_GDA | #1DTR二次側(310) GDA | OTHER | D18/22/310/GDA |  |  |  | DNP | 659 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 320 | #1DTR(320) |  | 81A | [14 empty] | 0325 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.320_81A | #1DTR(320) 81RY動作 | OTHER | D18/22/320/81A |  |  |  | DNP | 660 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 320 | #1DTR(320) |  | 81UL | [14 empty] | 0849 |  | 0249 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.320_81UL | #1DTR(320) 81RY U/L | OTHER | D18/22/320/81UL |  |  |  | DNP | 661 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 0 |  | 320 | #1DTR(320) |  | GDA | [14 empty] | 0061 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.320_GDA | #1DTR二次側(320) GDA | OTHER | D18/22/320/GDA |  |  |  | DNP | 662 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 330 | #2DTR(330) |  | 81A | [14 empty] | 0330 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.330_81A | #2DTR(330) 81RY動作 | OTHER | D18/22/330/81A |  |  |  | DNP | 663 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 330 | #2DTR(330) |  | 81UL | [14 empty] | 0850 |  | 0250 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.330_81UL | #2DTR(330) 81RY U/L | OTHER | D18/22/330/81UL |  |  |  | DNP | 664 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 0 |  | 330 | #2DTR(330) |  | GDA | [14 empty] | 0072 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.330_GDA | #2DTR二次側(330) GDA | OTHER | D18/22/330/GDA |  |  |  | DNP | 665 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 340 | #2DTR(340) |  | 81A | [14 empty] | 0335 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.340_81A | #2DTR(340) 81RY動作 | OTHER | D18/22/340/81A |  |  |  | DNP | 666 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 340 | #2DTR(340) |  | 81UL | [14 empty] | 0851 |  | 0251 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.340_81UL | #2DTR(340) 81RY U/L | OTHER | D18/22/340/81UL |  |  |  | DNP | 667 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 0 |  | 340 | #2DTR(340) |  | GDA | [14 empty] | 0075 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.340_GDA | #2DTR二次側(340) GDA | OTHER | D18/22/340/GDA |  |  |  | DNP | 668 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 350 | #3DTR(350) |  | 81A | [14 empty] | 0340 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.350_81A | #3DTR(350) 81RY動作 | OTHER | D18/22/350/81A |  |  |  | DNP | 669 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 350 | #3DTR(350) |  | 81UL | [14 empty] | 0852 |  | 0252 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.350_81UL | #3DTR(350) 81RY U/L | OTHER | D18/22/350/81UL |  |  |  | DNP | 670 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 0 |  | 350 | #3DTR(350) |  | GDA | [14 empty] | 0086 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.350_GDA | #3DTR二次側(350) GDA | OTHER | D18/22/350/GDA |  |  |  | DNP | 671 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 360 | #3DTR(360) |  | 81A | [14 empty] | 0345 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.360_81A | #3DTR(360) 81RY動作 | OTHER | D18/22/360/81A |  |  |  | DNP | 672 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 360 | #3DTR(360) |  | 81UL | [14 empty] | 0853 |  | 0253 | [8 empty] | ADCS_S | [8 empty] | 忠孝DS.360_81UL | #3DTR(360) 81RY U/L | OTHER | D18/22/360/81UL |  |  |  | DNP | 673 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | USE/LOCK | USE
D18 | 忠孝DS | 0 |  | 360 | #3DTR(360) |  | GDA | [14 empty] | 0089 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.360_GDA | #3DTR二次側(360) GDA | OTHER | D18/22/360/GDA |  |  |  | DNP | 674 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  |  |  |  | GEN | [14 empty] | 0633 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.GEN | 緊急發電機運轉 | OTHER | D18/0/StaDev/2A5Other |  |  |  | DNP | 675 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ON/OFF | OFF
D18 | 忠孝DS | 22 | 22kV | KE51 | 忠51線(KE51) |  | 81A | [14 empty] | 0321 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE51_81A | 23KV忠51線(KE51) 81RY | OTHER | D18/22/KE51/81A |  |  |  | DNP | 676 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE52 | 忠52線(KE52) |  | 81A | [14 empty] | 0322 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE52_81A | 23KV忠52線(KE52) 81RY | OTHER | D18/22/KE52/81A |  |  |  | DNP | 677 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE53 | 忠53線(KE53) |  | 81A | [14 empty] | 0323 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE53_81A | 23KV忠53線(KE53) 81RY | OTHER | D18/22/KE53/81A |  |  |  | DNP | 678 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE54 | 忠54線(KE54) |  | 81A | [14 empty] | 0324 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE54_81A | 23KV忠54線(KE54) 81RY | OTHER | D18/22/KE54/81A |  |  |  | DNP | 679 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE55 | 忠55線(KE55) |  | 81A | [14 empty] | 0326 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE55_81A | 23KV忠55線(KE55) 81RY | OTHER | D18/22/KE55/81A |  |  |  | DNP | 680 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE56 | 忠56線(KE56) |  | 81A | [14 empty] | 0327 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE56_81A | 23KV忠56線(KE56) 81RY | OTHER | D18/22/KE56/81A |  |  |  | DNP | 681 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE57 | 忠57線(KE57) |  | 81A | [14 empty] | 0328 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE57_81A | 23KV忠57線(KE57) 81RY | OTHER | D18/22/KE57/81A |  |  |  | DNP | 682 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE58 | 忠58線(KE58) |  | 81A | [14 empty] | 0329 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE58_81A | 23KV忠58線(KE58) 81RY | OTHER | D18/22/KE58/81A |  |  |  | DNP | 683 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE61 | 忠61線(KE61) |  | 81A | [14 empty] | 0331 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE61_81A | 23KV忠61線(KE61) 81RY | OTHER | D18/22/KE61/81A |  |  |  | DNP | 684 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE62 | 忠62線(KE62) |  | 81A | [14 empty] | 0332 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE62_81A | 23KV忠62線(KE62) 81RY | OTHER | D18/22/KE62/81A |  |  |  | DNP | 685 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE63 | 忠63線(KE63) |  | 81A | [14 empty] | 0333 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE63_81A | 23KV忠63線(KE63) 81RY | OTHER | D18/22/KE63/81A |  |  |  | DNP | 686 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE64 | 忠64線(KE64) |  | 81A | [14 empty] | 0334 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE64_81A | 23KV忠64線(KE64) 81RY | OTHER | D18/22/KE64/81A |  |  |  | DNP | 687 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE65 | 忠65線(KE65) |  | 81A | [14 empty] | 0336 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE65_81A | 23KV忠65線(KE65) 81RY | OTHER | D18/22/KE65/81A |  |  |  | DNP | 688 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE66 | 忠66線(KE66) |  | 81A | [14 empty] | 0337 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE66_81A | 23KV忠66線(KE66) 81RY | OTHER | D18/22/KE66/81A |  |  |  | DNP | 689 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE67 | 忠67線(KE67) |  | 81A | [14 empty] | 0338 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE67_81A | 23KV忠67線(KE67) 81RY | OTHER | D18/22/KE67/81A |  |  |  | DNP | 690 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE68 | 忠68線(KE68) |  | 81A | [14 empty] | 0339 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE68_81A | 23KV忠68線(KE68) 81RY | OTHER | D18/22/KE68/81A |  |  |  | DNP | 691 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE71 | 忠71線(KE71) |  | 81A | [14 empty] | 0341 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE71_81A | 23KV忠71線(KE71) 81RY | OTHER | D18/22/KE71/81A |  |  |  | DNP | 692 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE72 | 忠72線(KE72) |  | 81A | [14 empty] | 0342 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE72_81A | 23KV忠72線(KE72) 81RY | OTHER | D18/22/KE72/81A |  |  |  | DNP | 693 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE73 | 忠73線(KE73) |  | 81A | [14 empty] | 0343 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE73_81A | 23KV忠73線(KE73) 81RY | OTHER | D18/22/KE73/81A |  |  |  | DNP | 694 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE74 | 忠74線(KE74) |  | 81A | [14 empty] | 0344 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE74_81A | 23KV忠74線(KE74) 81RY | OTHER | D18/22/KE74/81A |  |  |  | DNP | 695 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE75 | 忠75線(KE75) |  | 81A | [14 empty] | 0346 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE75_81A | 23KV忠75線(KE75) 81RY | OTHER | D18/22/KE75/81A |  |  |  | DNP | 696 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE76 | 忠76線(KE76) |  | 81A | [14 empty] | 0347 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE76_81A | 23KV忠76線(KE76) 81RY | OTHER | D18/22/KE76/81A |  |  |  | DNP | 697 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE77 | 忠77線(KE77) |  | 81A | [14 empty] | 0348 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE77_81A | 23KV忠77線(KE77) 81RY | OTHER | D18/22/KE77/81A |  |  |  | DNP | 698 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | KE78 | 忠78線(KE78) |  | 81A | [14 empty] | 0349 | [10 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE78_81A | 23KV忠78線(KE78) 81RY | OTHER | D18/22/KE78/81A |  |  |  | DNP | 699 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  |  |  |  | PMA | [14 empty] | 0046 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.PMA | 電力量測表計故障 | OTHER | D18/0/StaDev/PMA |  |  |  | DNP | 700 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  |  |  |  | 水位警報(1) | [14 empty] | 0610 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.水位警報(1) | 地下室水位警報(1) | OTHER | D18/0/StaDev/Water1 |  |  |  | DNP | 701 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  |  |  |  | 水位警報(2) | [14 empty] | 0611 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.水位警報(2) | 地下室水位警報(2) | OTHER | D18/0/StaDev/Water2 |  |  |  | DNP | 702 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  |  |  |  | 通信機房溫度 | [14 empty] | 0632 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.通信機房溫度 | 通訊室溫度警報 | OTHER | D18/0/StaDev/R_Temp1 |  |  |  | DNP | 703 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  |  |  |  | Door3 | [14 empty] | 0602 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.無人化門禁(3) | 無人化門禁(3) | OTHER | D18/0/StaDev/Door2 |  |  |  | DNP | 704 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  |  |  |  | 無人化門禁(4) | [14 empty] | 0603 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.無人化門禁(4) | 無人化門禁(4) | OTHER | D18/0/StaDev/Door3 |  |  |  | DNP | 705 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  |  |  |  | 無人化門禁(5) | [14 empty] | 0604 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.無人化門禁(5) | 無人化門禁(5) | OTHER | D18/0/StaDev/Door4 |  |  |  | DNP | 706 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  |  |  |  | 集油池警報(1) | [14 empty] | 0612 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.集油池警報(1) | 集油池水位警報(1) | OTHER | D18/0/StaDev/OilLeak1 |  |  |  | DNP | 707 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  |  |  |  | 集油池警報(2) | [14 empty] | 0613 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.集油池警報(2) | 集油池水位警報(2) | OTHER | D18/0/StaDev/OilLeak2 |  |  |  | DNP | 708 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 1DTR | #1DTR |  | 87A | [14 empty] | 0049 | [10 empty] | 161KV_S | [8 empty] | 忠孝DS.#1DTR_87A | #1DTR 87RY | MTR | D18//1DTR/87A |  |  |  | DNP | 709 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 2DTR | #2DTR |  | 87A | [14 empty] | 0063 | [10 empty] | 161KV_S | [8 empty] | 忠孝DS.#2DTR_87A | #2DTR 87RY | MTR | D18//2DTR/87A |  |  |  | DNP | 710 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | 3DTR | #3DTR |  | 87A | [14 empty] | 0077 | [10 empty] | 161KV_S | [8 empty] | 忠孝DS.#3DTR_87A | #3DTR 87RY | MTR | D18//3DTR/87A |  |  |  | DNP | 711 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | _BUS | BUS |  | RYFA | [14 empty] | 0580 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | D18/161/ComPoint/BUS_RYFA |  |  |  | DNP | 712 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 161 | 161kV | _BUS | BUS |  | 87CTFA | [14 empty] | 0579 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.161KV_BUS_CTFA | 161KV BUS CT回路故障 | OTHER | D18/161/ComPoint/12B_CTFA |  |  |  | DNP | 713 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  |  |  |  | 控制室溫度 | [14 empty] | 0634 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.控制室溫度 | 控制室溫度警報 | OTHER | D18/0/StaDev/R_Temp2 |  |  |  | DNP | 714 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  |  |  |  | Burglar1 | [14 empty] | 0601 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | D18/0/StaDev/Burglar |  |  |  | DNP | 715 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 0 |  | OLTC | OLTC |  | OLTCA | [14 empty] | 0635 | [10 empty] | ADCS_S | [8 empty] | 忠孝DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | D18/0/ComPoint/OLTC_A |  |  |  | DNP | 716 | DNPDIPoint | DS058 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D18 | 忠孝DS | 22 | 22kV | 210_SC | #1SC | 9 | CAP | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.210_SC_CAP | 23KV#1SC 容量 | SC | [5 empty] | 717 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 22 | 22kV | 220_SC | #2SC | 9 | CAP | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.220_SC_CAP | 23KV#2SC 容量 | SC | [5 empty] | 718 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 22 | 22kV | 230_SC | #3SC | 9 | CAP | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.230_SC_CAP | 23KV#3SC 容量 | SC | [5 empty] | 719 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 22 | 22kV | 240_SC | #4SC | 9 | CAP | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.240_SC_CAP | 23KV#4SC 容量 | SC | [5 empty] | 720 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 22 | 22kV | 250_SC | #5SC | 9 | CAP | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.250_SC_CAP | 23KV#5SC 容量 | SC | [5 empty] | 721 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 22 | 22kV | 260_SC | #6SC | 9 | CAP | [25 empty] | ADCS_S | [8 empty] | 忠孝DS.260_SC_CAP | 23KV#6SC 容量 | SC | [5 empty] | 722 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D18 | 忠孝DS | 161 | 161kV | 1510 | 台南忠孝一路(1510) |  | LE0 | 1510LE | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.1510LE | 1510LE (非取樣點) | LINE161 | D18/161/1510/LE0 |  |  |  |  | 723 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 161 | 161kV | 1510 | 台南忠孝一路(1510) |  | BE0 | 1510BE | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.1510BE | 1510BE (非取樣點) | LINE161 | D18/161/1510/BE0 |  |  |  |  | 724 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南忠孝二路(1520) |  | LE0 | 1520LE | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.1520LE | 1520LE (非取樣點) | LINE161 | D18/161/1520/LE0 |  |  |  |  | 725 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 161 | 161kV | 1520 | 台南忠孝二路(1520) |  | BE0 | 1520BE | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.1520BE | 1520BE (非取樣點) | LINE161 | D18/161/1520/BE0 |  |  |  |  | 726 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝延平線(1530) |  | LE0 | 1530LE | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.1530LE | 1530LE (非取樣點) | LINE161 | D18/161/1530/LE0 |  |  |  |  | 727 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 161 | 161kV | 1530 | 忠孝延平線(1530) |  | BE0 | 1530BE | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.1530BE | 1530BE (非取樣點) | LINE161 | D18/161/1530/BE0 |  |  |  |  | 728 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | KE51 | KE51_DS |  | DS1 | KE51_DS | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE51_DS | KE51_DS (非取樣點) | FEEDER | D18/22/KE51/DS |  |  |  |  | 729 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | KE51 | KE51_ES |  | LE0 | KE51_ES | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE51_ES | KE51_ES (非取樣點) | FEEDER | D18/22/KE51/ES |  |  |  |  | 730 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | KE52 | KE52_DS |  | DS1 | KE52_DS | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE52_DS | KE52_DS (非取樣點) | FEEDER | D18/22/KE52/DS |  |  |  |  | 731 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | KE52 | KE52_ES |  | LE0 | KE52_ES | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE52_ES | KE52_ES (非取樣點) | FEEDER | D18/22/KE52/ES |  |  |  |  | 732 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | KE53 | KE53_DS |  | DS1 | KE53_DS | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE53_DS | KE53_DS (非取樣點) | FEEDER | D18/22/KE53/DS |  |  |  |  | 733 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | KE53 | KE53_ES |  | LE0 | KE53_ES | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE53_ES | KE53_ES (非取樣點) | FEEDER | D18/22/KE53/ES |  |  |  |  | 734 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | KE54 | KE54_DS |  | DS1 | KE54_DS | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE54_DS | KE54_DS (非取樣點) | FEEDER | D18/22/KE54/DS |  |  |  |  | 735 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | KE54 | KE54_ES |  | LE0 | KE54_ES | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE54_ES | KE54_ES (非取樣點) | FEEDER | D18/22/KE54/ES |  |  |  |  | 736 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | KE55 | KE55_DS |  | DS1 | KE55_DS | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE55_DS | KE55_DS (非取樣點) | FEEDER | D18/22/KE55/DS |  |  |  |  | 737 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | KE55 | KE55_ES |  | LE0 | KE55_ES | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE55_ES | KE55_ES (非取樣點) | FEEDER | D18/22/KE55/ES |  |  |  |  | 738 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | KE56 | KE56_DS |  | DS1 | KE56_DS | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE56_DS | KE56_DS (非取樣點) | FEEDER | D18/22/KE56/DS |  |  |  |  | 739 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | KE56 | KE56_ES |  | LE0 | KE56_ES | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE56_ES | KE56_ES (非取樣點) | FEEDER | D18/22/KE56/ES |  |  |  |  | 740 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | KE57 | KE57_DS |  | DS1 | KE57_DS | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE57_DS | KE57_DS (非取樣點) | FEEDER | D18/22/KE57/DS |  |  |  |  | 741 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | KE57 | KE57_ES |  | LE0 | KE57_ES | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE57_ES | KE57_ES (非取樣點) | FEEDER | D18/22/KE57/ES |  |  |  |  | 742 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | KE58 | KE58_DS |  | DS1 | KE58_DS | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE58_DS | KE58_DS (非取樣點) | FEEDER | D18/22/KE58/DS |  |  |  |  | 743 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | KE58 | KE58_ES |  | LE0 | KE58_ES | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE58_ES | KE58_ES (非取樣點) | FEEDER | D18/22/KE58/ES |  |  |  |  | 744 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | KE61 | KE61_DS |  | DS1 | KE61_DS | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE61_DS | KE61_DS (非取樣點) | FEEDER | D18/22/KE61/DS |  |  |  |  | 745 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | KE61 | KE61_ES |  | LE0 | KE61_ES | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE61_ES | KE61_ES (非取樣點) | FEEDER | D18/22/KE61/ES |  |  |  |  | 746 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | KE62 | KE62_DS |  | DS1 | KE62_DS | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE62_DS | KE62_DS (非取樣點) | FEEDER | D18/22/KE62/DS |  |  |  |  | 747 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | KE62 | KE62_ES |  | LE0 | KE62_ES | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE62_ES | KE62_ES (非取樣點) | FEEDER | D18/22/KE62/ES |  |  |  |  | 748 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | KE63 | KE63_DS |  | DS1 | KE63_DS | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE63_DS | KE63_DS (非取樣點) | FEEDER | D18/22/KE63/DS |  |  |  |  | 749 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | KE63 | KE63_ES |  | LE0 | KE63_ES | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE63_ES | KE63_ES (非取樣點) | FEEDER | D18/22/KE63/ES |  |  |  |  | 750 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | KE64 | KE64_DS |  | DS1 | KE64_DS | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE64_DS | KE64_DS (非取樣點) | FEEDER | D18/22/KE64/DS |  |  |  |  | 751 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | KE64 | KE64_ES |  | LE0 | KE64_ES | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE64_ES | KE64_ES (非取樣點) | FEEDER | D18/22/KE64/ES |  |  |  |  | 752 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | KE65 | KE65_DS |  | DS1 | KE65_DS | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE65_DS | KE65_DS (非取樣點) | FEEDER | D18/22/KE65/DS |  |  |  |  | 753 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | KE65 | KE65_ES |  | LE0 | KE65_ES | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE65_ES | KE65_ES (非取樣點) | FEEDER | D18/22/KE65/ES |  |  |  |  | 754 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | KE66 | KE66_DS |  | DS1 | KE66_DS | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE66_DS | KE66_DS (非取樣點) | FEEDER | D18/22/KE66/DS |  |  |  |  | 755 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | KE66 | KE66_ES |  | LE0 | KE66_ES | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE66_ES | KE66_ES (非取樣點) | FEEDER | D18/22/KE66/ES |  |  |  |  | 756 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | KE67 | KE67_DS |  | DS1 | KE67_DS | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE67_DS | KE67_DS (非取樣點) | FEEDER | D18/22/KE67/DS |  |  |  |  | 757 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | KE67 | KE67_ES |  | LE0 | KE67_ES | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE67_ES | KE67_ES (非取樣點) | FEEDER | D18/22/KE67/ES |  |  |  |  | 758 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | KE68 | KE68_DS |  | DS1 | KE68_DS | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE68_DS | KE68_DS (非取樣點) | FEEDER | D18/22/KE68/DS |  |  |  |  | 759 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | KE68 | KE68_ES |  | LE0 | KE68_ES | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE68_ES | KE68_ES (非取樣點) | FEEDER | D18/22/KE68/ES |  |  |  |  | 760 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | KE71 | KE71_DS |  | DS1 | KE71_DS | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE71_DS | KE71_DS (非取樣點) | FEEDER | D18/22/KE71/DS |  |  |  |  | 761 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | KE71 | KE71_ES |  | LE0 | KE71_ES | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE71_ES | KE71_ES (非取樣點) | FEEDER | D18/22/KE71/ES |  |  |  |  | 762 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | KE72 | KE72_DS |  | DS1 | KE72_DS | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE72_DS | KE72_DS (非取樣點) | FEEDER | D18/22/KE72/DS |  |  |  |  | 763 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | KE72 | KE72_ES |  | LE0 | KE72_ES | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE72_ES | KE72_ES (非取樣點) | FEEDER | D18/22/KE72/ES |  |  |  |  | 764 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | KE73 | KE73_DS |  | DS1 | KE73_DS | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE73_DS | KE73_DS (非取樣點) | FEEDER | D18/22/KE73/DS |  |  |  |  | 765 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | KE73 | KE73_ES |  | LE0 | KE73_ES | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE73_ES | KE73_ES (非取樣點) | FEEDER | D18/22/KE73/ES |  |  |  |  | 766 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | KE74 | KE74_DS |  | DS1 | KE74_DS | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE74_DS | KE74_DS (非取樣點) | FEEDER | D18/22/KE74/DS |  |  |  |  | 767 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | KE74 | KE74_ES |  | LE0 | KE74_ES | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE74_ES | KE74_ES (非取樣點) | FEEDER | D18/22/KE74/ES |  |  |  |  | 768 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | KE75 | KE75_DS |  | DS1 | KE75_DS | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE75_DS | KE75_DS (非取樣點) | FEEDER | D18/22/KE75/DS |  |  |  |  | 769 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | KE75 | KE75_ES |  | LE0 | KE75_ES | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE75_ES | KE75_ES (非取樣點) | FEEDER | D18/22/KE75/ES |  |  |  |  | 770 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | KE76 | KE76_DS |  | DS1 | KE76_DS | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE76_DS | KE76_DS (非取樣點) | FEEDER | D18/22/KE76/DS |  |  |  |  | 771 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | KE76 | KE76_ES |  | LE0 | KE76_ES | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE76_ES | KE76_ES (非取樣點) | FEEDER | D18/22/KE76/ES |  |  |  |  | 772 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | KE77 | KE77_DS |  | DS1 | KE77_DS | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE77_DS | KE77_DS (非取樣點) | FEEDER | D18/22/KE77/DS |  |  |  |  | 773 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | KE77 | KE77_ES |  | LE0 | KE77_ES | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE77_ES | KE77_ES (非取樣點) | FEEDER | D18/22/KE77/ES |  |  |  |  | 774 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | KE78 | KE78_DS |  | DS1 | KE78_DS | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE78_DS | KE78_DS (非取樣點) | FEEDER | D18/22/KE78/DS |  |  |  |  | 775 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | KE78 | KE78_ES |  | LE0 | KE78_ES | [24 empty] | DDCS4_1 | [8 empty] | 忠孝DS.KE78_ES | KE78_ES (非取樣點) | FEEDER | D18/22/KE78/ES |  |  |  |  | 776 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | 100 | TIE(100) |  | E1 | 101E | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.101E | 101E (非取樣點) | TIE | D18/22/100/E1 |  |  |  |  | 777 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | 100 | TIE(100) |  | E2 | 102E | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.102E | 102E (非取樣點) | TIE | D18/22/100/E2 |  |  |  |  | 778 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | 101 | 101 |  | 101 | 101 | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.101 | 101 (非取樣點) | TIE | D18/22/100/D1 |  |  |  |  | 779 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 102 | 102 |  | 102 | 102 | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.102 | 102 (非取樣點) | TIE | D18/22/100/D2 |  |  |  |  | 780 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.1501E | 1501E (非取樣點) | TIE | D18/161/1500/E1 |  |  |  |  | 781 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.1502E | 1502E (非取樣點) | TIE | D18/161/1500/E2 |  |  |  |  | 782 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | 200 | TIE(200) |  | E1 | 201E | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.201E | 201E (非取樣點) | TIE | D18/22/200/E1 |  |  |  |  | 783 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | 200 | TIE(200) |  | E2 | 202E | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.202E | 202E (非取樣點) | TIE | D18/22/200/E2 |  |  |  |  | 784 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | 201 | 201 |  | 201 | 201 | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.201 | 201 (非取樣點) | TIE | D18/22/200/D1 |  |  |  |  | 785 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 202 | 202 |  | 202 | 202 | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.202 | 202 (非取樣點) | TIE | D18/22/200/D2 |  |  |  |  | 786 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 300 | TIE(300) |  | E1 | 301E | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.301E | 301E (非取樣點) | TIE | D18/22/300/E1 |  |  |  |  | 787 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | 300 | TIE(300) |  | E2 | 302E | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.302E | 302E (非取樣點) | TIE | D18/22/300/E2 |  |  |  |  | 788 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | 301 | 301 |  | 301 | 301 | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.301 | 301 (非取樣點) | TIE | D18/22/300/D1 |  |  |  |  | 789 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 302 | 302 |  | 302 | 302 | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.302 | 302 (非取樣點) | TIE | D18/22/300/D2 |  |  |  |  | 790 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 391 | 391 |  | 391 | 391 | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.391 | 391 (非取樣點) | OTHER | D18/22/390/D1 |  |  |  |  | 791 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 391E | 391E |  | 391E | 391E | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.391E | 391E (非取樣點) | OTHER | D18/22/390/E1 |  |  |  |  | 792 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | 491 | 491 |  | 491 | 491 | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.491 | 491 (非取樣點) | OTHER | D18/22/490/D1 |  |  |  |  | 793 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 491E | 491E |  | 491E | 491E | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.491E | 491E (非取樣點) | OTHER | D18/22/490/E1 |  |  |  |  | 794 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | 1750TE | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.1750TE | 1750TE (非取樣點) | MTR | D18/161/1750/TE0 |  |  |  |  | 795 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | 1750BE | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.1750BE | 1750BE (非取樣點) | MTR | D18/161/1750/BE0 |  |  |  |  | 796 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | 311 | 311 |  | 311 | 311 | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.311 | 311 (非取樣點) | MTR | D18/22/310/D1 |  |  |  |  | 797 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 310 | #1DTR(310) |  | E1 | 311E | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.311E | 311E (非取樣點) | MTR | D18/22/310/E1 |  |  |  |  | 798 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | 321 | 321 |  | 321 | 321 | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.321 | 321 (非取樣點) | MTR | D18/22/320/D1 |  |  |  |  | 799 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 320 | #1DTR(320) |  | E1 | 321E | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.321E | 321E (非取樣點) | MTR | D18/22/320/E1 |  |  |  |  | 800 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | 1760TE | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.1760TE | 1760TE (非取樣點) | MTR | D18/161/1760/TE0 |  |  |  |  | 801 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | 1760BE | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.1760BE | 1760BE (非取樣點) | MTR | D18/161/1760/BE0 |  |  |  |  | 802 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | 331 | 331 |  | 331 | 331 | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.331 | 331 (非取樣點) | MTR | D18/22/330/D1 |  |  |  |  | 803 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 330 | #2DTR(330) |  | E1 | 331E | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.331E | 331E (非取樣點) | MTR | D18/22/330/E1 |  |  |  |  | 804 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | 341 | 341 |  | 341 | 341 | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.341 | 341 (非取樣點) | MTR | D18/22/340/D1 |  |  |  |  | 805 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 340 | #2DTR(340) |  | E1 | 341E | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.341E | 341E (非取樣點) | MTR | D18/22/340/E1 |  |  |  |  | 806 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | 1770TE | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.1770TE | 1770TE (非取樣點) | MTR | D18/161/1770/TE0 |  |  |  |  | 807 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | 1770BE | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.1770BE | 1770BE (非取樣點) | MTR | D18/161/1770/BE0 |  |  |  |  | 808 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | 351 | 351 |  | 351 | 351 | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.351 | 351 (非取樣點) | MTR | D18/22/350/D1 |  |  |  |  | 809 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 350 | #3DTR(350) |  | E1 | 351E | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.351E | 351E (非取樣點) | MTR | D18/22/350/E1 |  |  |  |  | 810 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | 361 | 361 |  | 361 | 361 | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.361 | 361 (非取樣點) | MTR | D18/22/360/D1 |  |  |  |  | 811 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 360 | #3DTR(360) |  | E1 | 361E | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.361E | 361E (非取樣點) | MTR | D18/22/360/E1 |  |  |  |  | 812 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | 211E | 211E |  | 211E | 211E | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.211E | 211E (非取樣點) | SC | D18/22/210/E1 |  |  |  |  | 813 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | 211 | 211 |  | 211 | 211 | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.211 | 211 (非取樣點) | SC | D18/22/210/D1 |  |  |  |  | 814 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 221E | 221E |  | 221E | 221E | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.221E | 221E (非取樣點) | SC | D18/22/220/E1 |  |  |  |  | 815 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | 221 | 221 |  | 221 | 221 | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.221 | 221 (非取樣點) | SC | D18/22/220/D1 |  |  |  |  | 816 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 231E | 231E |  | 231E | 231E | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.231E | 231E (非取樣點) | SC | D18/22/230/E1 |  |  |  |  | 817 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | 231 | 231 |  | 231 | 231 | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.231 | 231 (非取樣點) | SC | D18/22/230/D1 |  |  |  |  | 818 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 241E | 241E |  | 241E | 241E | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.241E | 241E (非取樣點) | SC | D18/22/240/E1 |  |  |  |  | 819 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | 241 | 241 |  | 241 | 241 | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.241 | 241 (非取樣點) | SC | D18/22/240/D1 |  |  |  |  | 820 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 251E | 251E |  | 251E | 251E | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.251E | 251E (非取樣點) | SC | D18/22/250/E1 |  |  |  |  | 821 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | 251 | 251 |  | 251 | 251 | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.251 | 251 (非取樣點) | SC | D18/22/250/D1 |  |  |  |  | 822 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 261E | 261E |  | 261E | 261E | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.261E | 261E (非取樣點) | SC | D18/22/260/BE0 |  |  |  |  | 823 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | 261 | 261 |  | 261 | 261 | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.261 | 261 (非取樣點) | SC | D18/22/260/D1 |  |  |  |  | 824 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 15B1E | 15B1E |  | BE1 | 15B1E | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.15B1E | 15B1E (非取樣點) | BUS | D18/161/161B1E/BE1 |  |  |  |  | 825 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | 15B2E | 15B2E |  | BE2 | 15B2E | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.15B2E | 15B2E (非取樣點) | BUS | D18/161/161B2E/BE2 |  |  |  |  | 826 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 827 | NotelDIPoint | [38 empty] | START/STOP | STOP
D18 | 忠孝DS | 0 |  |  |  |  | 1950BE | 1950BE | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.1950BE | 1950BE(非取樣點) | OTHER | D18/161/1950/BE0 |  |  |  |  | 828 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  |  |  |  | 1950RE | 1950RE | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.1950RE | 1950RE(非取樣點) | OTHER | D18/161/1950/RE0 |  |  |  |  | 829 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | 1ABUS | 1ABUS |  | PTD | 1ABUS_PTD | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.1ABUS_PTD | #1ABUS_PTD(非取樣點) | OTHER | [5 empty] | 830 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 1ABUS | 1ABUS |  | PTE | 1ABUS_PTE | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.1ABUS_PTE | #1ABUS_PTE(非取樣點) | OTHER | [5 empty] | 831 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | 1BBUS | 1BBUS |  | PTD | 1BBUS_PTD | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.1BBUS_PTD | #1BBUS_PTD(非取樣點) | OTHER | [5 empty] | 832 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 1BBUS | 1BBUS |  | PTE | 1BBUS_PTE | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.1BBUS_PTE | #1BBUS_PTE(非取樣點) | OTHER | [5 empty] | 833 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | 2ABUS | 2ABUS |  | PTD | 2ABUS_PTD | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.2ABUS_PTD | #2ABUS_PTD(非取樣點) | OTHER | [5 empty] | 834 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 2ABUS | 2ABUS |  | PTE | 2ABUS_PTE | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.2ABUS_PTE | #2ABUS_PTE(非取樣點) | OTHER | [5 empty] | 835 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | 2BBUS | 2BBUS |  | PTD | 2BBUS_PTD | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.2BBUS_PTD | #2BBUS_PTD(非取樣點) | OTHER | [5 empty] | 836 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 2BBUS | 2BBUS |  | PTE | 2BBUS_PTE | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.2BBUS_PTE | #2BBUS_PTE(非取樣點) | OTHER | [5 empty] | 837 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | 3ABUS | 3ABUS |  | PTD | 3ABUS_PTD | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.3ABUS_PTD | #3ABUS_PTD(非取樣點) | OTHER | [5 empty] | 838 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 3ABUS | 3ABUS |  | PTE | 3ABUS_PTE | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.3ABUS_PTE | #3ABUS_PTE(非取樣點) | OTHER | [5 empty] | 839 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D18 | 忠孝DS | 0 |  | 3BBUS | 3BBUS |  | PTD | 3BBUS_PTD | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.3BBUS_PTD | #3BBUS_PTD(非取樣點) | OTHER | [5 empty] | 840 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D18 | 忠孝DS | 0 |  | 3BBUS | 3BBUS |  | PTE | 3BBUS_PTE | [24 empty] | ADCS_S | [8 empty] | 忠孝DS.3BBUS_PTE | #3BBUS_PTE(非取樣點) | OTHER | [5 empty] | 841 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo