## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D19 | 槺榔DS | 161 | 161kV | 1510 | 太鐵～槺榔一路(1510) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_A1 | [8 empty] | 糠榔DS.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 2 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 161 | 161kV | 1510 | 太鐵～槺榔一路(1510) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_A1 | [8 empty] | 糠榔DS.1510BE | 1510BE (非取樣點) | LINE161 | [5 empty] | 3 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 161 | 161kV | 1520 | 太鐵～槺榔二路(1520) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_A1 | [8 empty] | 糠榔DS.1520LE | 1520LE (非取樣點) | LINE161 | [5 empty] | 4 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 161 | 161kV | 1520 | 太鐵～槺榔二路(1520) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_A1 | [8 empty] | 糠榔DS.1520BE | 1520BE (非取樣點) | LINE161 | [5 empty] | 5 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_A1 | [8 empty] | 糠榔DS.1750TE | 1750TE (非取樣點) | MTR | [5 empty] | 6 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_A1 | [8 empty] | 糠榔DS.1750BE | 1750BE (非取樣點) | MTR | [5 empty] | 7 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | D1 | 311(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D19_A1 | [8 empty] | 糠榔DS.311 | 311 (非取樣點) | MTR | [5 empty] | 8 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | E1 | 311E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D19_A1 | [8 empty] | 糠榔DS.311E | 311E (非取樣點) | MTR | [5 empty] | 9 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | D1 | 321(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D19_A1 | [8 empty] | 糠榔DS.321 | 321 (非取樣點) | MTR | [5 empty] | 10 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | E1 | 321E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D19_A1 | [8 empty] | 糠榔DS.321E | 321E (非取樣點) | MTR | [5 empty] | 11 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_A1 | [8 empty] | 糠榔DS.1760TE | 1760TE (非取樣點) | MTR | [5 empty] | 12 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_A1 | [8 empty] | 糠榔DS.1760BE | 1760BE (非取樣點) | MTR | [5 empty] | 13 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 22 | 22kV | 330 | #2DTR(330) |  | D1 | 331(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D19_A1 | [8 empty] | 糠榔DS.331 | 331 (非取樣點) | MTR | [5 empty] | 14 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | 330 | #2DTR(330) |  | E1 | 331E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D19_A1 | [8 empty] | 糠榔DS.331E | 331E (非取樣點) | MTR | [5 empty] | 15 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_A1 | [8 empty] | 糠榔DS.1770TE | 1770TE (非取樣點) | MTR | [5 empty] | 16 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_A1 | [8 empty] | 糠榔DS.1770BE | 1770BE (非取樣點) | MTR | [5 empty] | 17 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 22 | 22kV | 350 | #3DTR(350) |  | D1 | 351(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D19_A1 | [8 empty] | 糠榔DS.351 | 351 (非取樣點) | MTR | [5 empty] | 18 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | 350 | #3DTR(350) |  | E1 | 351E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D19_A1 | [8 empty] | 糠榔DS.351E | 351E (非取樣點) | MTR | [5 empty] | 19 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 11 | 11kV | JO21 | 槺21(JO21) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO21_DS | JO21_DS (非取樣點) | FEEDER | [5 empty] | 20 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | JO21 | 槺21(JO21) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO21_ES | JO21_ES (非取樣點) | FEEDER | [5 empty] | 21 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 11 | 11kV | JO22 | 槺22(JO22) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO22_DS | JO22_DS (非取樣點) | FEEDER | [5 empty] | 22 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | JO22 | 槺22(JO22) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO22_ES | JO22_ES (非取樣點) | FEEDER | [5 empty] | 23 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 11 | 11kV | JO23 | 槺23(JO23) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO23_DS | JO23_DS (非取樣點) | FEEDER | [5 empty] | 24 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | JO23 | 槺23(JO23) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO23_ES | JO23_ES (非取樣點) | FEEDER | [5 empty] | 25 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 11 | 11kV | JO24 | 槺24(JO24) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO24_DS | JO24_DS (非取樣點) | FEEDER | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | JO24 | 槺24(JO24) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO24_ES | JO24_ES (非取樣點) | FEEDER | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 11 | 11kV | JO25 | 槺25(JO25) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO25_DS | JO25_DS (非取樣點) | FEEDER | [5 empty] | 28 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | JO25 | 槺25(JO25) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO25_ES | JO25_ES (非取樣點) | FEEDER | [5 empty] | 29 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 11 | 11kV | 210 | #1SC(210) |  | E1 | 211E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D19_A1 | [8 empty] | 糠榔DS.211E | 211E (非取樣點) | SC | [5 empty] | 30 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 11 | 11kV | 210 | #1SC(210) |  | DS1 | 211(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D19_A1 | [8 empty] | 糠榔DS.211 | 211 (非取樣點) | SC | [5 empty] | 31 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | 100 | TIE(100) |  | E1 | 101E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D19_A1 | [8 empty] | 糠榔DS.101E | 101E (非取樣點) | TIE | [5 empty] | 32 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 11 | 11kV | 100 | TIE(100) |  | E2 | 102E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D19_A1 | [8 empty] | 糠榔DS.102E | 102E (非取樣點) | TIE | [5 empty] | 33 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 11 | 11kV | 100 | TIE(100) |  | D1 | 101(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D19_A1 | [8 empty] | 糠榔DS.101 | 101 (非取樣點) | TIE | [5 empty] | 34 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | 100 | TIE(100) |  | D2 | 102(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D19_A1 | [8 empty] | 糠榔DS.102 | 102 (非取樣點) | TIE | [5 empty] | 35 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | JO26 | 槺26(JO26) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO26_DS | JO26_DS (非取樣點) | FEEDER | [5 empty] | 36 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | JO26 | 槺26(JO26) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO26_ES | JO26_ES (非取樣點) | FEEDER | [5 empty] | 37 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 11 | 11kV | JO27 | 槺27(JO27) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO27_DS | JO27_DS (非取樣點) | FEEDER | [5 empty] | 38 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | JO27 | 槺27(JO27) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO27_ES | JO27_ES (非取樣點) | FEEDER | [5 empty] | 39 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 11 | 11kV | JO28 | 槺28(JO28) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO28_DS | JO28_DS (非取樣點) | FEEDER | [5 empty] | 40 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | JO28 | 槺28(JO28) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO28_ES | JO28_ES (非取樣點) | FEEDER | [5 empty] | 41 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 11 | 11kV | JO29 | 槺29(JO29) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO29_DS | JO29_DS (非取樣點) | FEEDER | [5 empty] | 42 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | JO29 | 槺29(JO29) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO29_ES | JO29_ES (非取樣點) | FEEDER | [5 empty] | 43 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 11 | 11kV | JO30 | 槺30(JO30) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO30_DS | JO30_DS (非取樣點) | FEEDER | [5 empty] | 44 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | JO30 | 槺30(JO30) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO30_ES | JO30_ES (非取樣點) | FEEDER | [5 empty] | 45 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 11 | 11kV | 220 | #2SC(220) |  | E1 | 221E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D19_A1 | [8 empty] | 糠榔DS.221E | 221E (非取樣點) | SC | [5 empty] | 46 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 11 | 11kV | 220 | #2SC(220) |  | DS1 | 221(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D19_A1 | [8 empty] | 糠榔DS.221 | 221 (非取樣點) | SC | [5 empty] | 47 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO61 | 槺61(JO61) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO61_DS | JO61_DS (非取樣點) | FEEDER | [5 empty] | 48 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO61 | 槺61(JO61) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO61_ES | JO61_ES (非取樣點) | FEEDER | [5 empty] | 49 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 22 | 22kV | JO62 | 槺62(JO62) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO62_DS | JO62_DS (非取樣點) | FEEDER | [5 empty] | 50 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO62 | 槺62(JO62) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO62_ES | JO62_ES (非取樣點) | FEEDER | [5 empty] | 51 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 22 | 22kV | JO63 | 槺63(JO63) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO63_DS | JO63_DS (非取樣點) | FEEDER | [5 empty] | 52 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO63 | 槺63(JO63) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO63_ES | JO63_ES (非取樣點) | FEEDER | [5 empty] | 53 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 22 | 22kV | JO64 | 槺64(JO64) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO64_DS | JO64_DS (非取樣點) | FEEDER | [5 empty] | 54 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO64 | 槺64(JO64) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO64_ES | JO64_ES (非取樣點) | FEEDER | [5 empty] | 55 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 22 | 22kV | JO65 | 槺65(JO65) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO65_DS | JO65_DS (非取樣點) | FEEDER | [5 empty] | 56 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO65 | 槺65(JO65) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO65_ES | JO65_ES (非取樣點) | FEEDER | [5 empty] | 57 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 22 | 22kV | JO66 | 槺66(JO66) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO66_DS | JO66_DS (非取樣點) | FEEDER | [5 empty] | 58 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO66 | 槺66(JO66) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO66_ES | JO66_ES (非取樣點) | FEEDER | [5 empty] | 59 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 22 | 22kV | JO67 | 槺67(JO67) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO67_DS | JO67_DS (非取樣點) | FEEDER | [5 empty] | 60 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO67 | 槺67(JO67) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO67_ES | JO67_ES (非取樣點) | FEEDER | [5 empty] | 61 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 22 | 22kV | JO68 | 槺68(JO68) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO68_DS | JO68_DS (非取樣點) | FEEDER | [5 empty] | 62 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO68 | 槺68(JO68) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO68_ES | JO68_ES (非取樣點) | FEEDER | [5 empty] | 63 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 22 | 22kV | 390 | #1SSTR(390) |  | D1 | 391(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D19_A1 | [8 empty] | 糠榔DS.391 | 391 (非取樣點) | OTHER | [5 empty] | 64 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | 390 | #1SSTR(390) |  | E1 | 391E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D19_A1 | [8 empty] | 糠榔DS.391E | 391E (非取樣點) | OTHER | [5 empty] | 65 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 22 | 22kV | 230 | #3SC(230) |  | E1 | 231E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D19_A1 | [8 empty] | 糠榔DS.231E | 231E (非取樣點) | SC | [5 empty] | 66 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 22 | 22kV | 230 | #3SC(230) |  | D1 | 231(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D19_A1 | [8 empty] | 糠榔DS.231 | 231 (非取樣點) | SC | [5 empty] | 67 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | 240 | #4SC(240) |  | E1 | 241E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D19_A1 | [8 empty] | 糠榔DS.241E | 241E (非取樣點) | SC | [5 empty] | 68 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 22 | 22kV | 240 | #4SC(240) |  | D1 | 241(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D19_A1 | [8 empty] | 糠榔DS.241 | 241 (非取樣點) | SC | [5 empty] | 69 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO71 | 槺71(JO71) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO71_DS | JO71_DS (非取樣點) | FEEDER | [5 empty] | 70 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO71 | 槺71(JO71) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO71_ES | JO71_ES (非取樣點) | FEEDER | [5 empty] | 71 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 22 | 22kV | JO72 | 槺72(JO72) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO72_DS | JO72_DS (非取樣點) | FEEDER | [5 empty] | 72 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO72 | 槺72(JO72) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO72_ES | JO72_ES (非取樣點) | FEEDER | [5 empty] | 73 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 22 | 22kV | JO73 | 槺73(JO73) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO73_DS | JO73_DS (非取樣點) | FEEDER | [5 empty] | 74 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO73 | 槺73(JO73) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO73_ES | JO73_ES (非取樣點) | FEEDER | [5 empty] | 75 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 22 | 22kV | JO74 | 槺74(JO74) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO74_DS | JO74_DS (非取樣點) | FEEDER | [5 empty] | 76 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO74 | 槺74(JO74) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO74_ES | JO74_ES (非取樣點) | FEEDER | [5 empty] | 77 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 22 | 22kV | JO75 | 槺75(JO75) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO75_DS | JO75_DS (非取樣點) | FEEDER | [5 empty] | 78 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO75 | 槺75(JO75) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO75_ES | JO75_ES (非取樣點) | FEEDER | [5 empty] | 79 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 22 | 22kV | JO76 | 槺76(JO76) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO76_DS | JO76_DS (非取樣點) | FEEDER | [5 empty] | 80 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO76 | 槺76(JO76) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO76_ES | JO76_ES (非取樣點) | FEEDER | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 22 | 22kV | JO77 | 槺77(JO77) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO77_DS | JO77_DS (非取樣點) | FEEDER | [5 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO77 | 槺77(JO77) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO77_ES | JO77_ES (非取樣點) | FEEDER | [5 empty] | 83 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 22 | 22kV | JO78 | 槺78(JO78) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO78_DS | JO78_DS (非取樣點) | FEEDER | [5 empty] | 84 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO78 | 槺78(JO78) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D19_D1 | [8 empty] | 糠榔DS.JO78_ES | JO78_ES (非取樣點) | FEEDER | [5 empty] | 85 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 22 | 22kV | 250 | #5SC(250) |  | E1 | 251E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D19_A1 | [8 empty] | 糠榔DS.251E | 251E (非取樣點) | SC | [5 empty] | 86 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 22 | 22kV | 250 | #5SC(250) |  | D1 | 251(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D19_A1 | [8 empty] | 糠榔DS.251 | 251 (非取樣點) | SC | [5 empty] | 87 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | 260 | #6SC(260) |  | E1 | 261E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D19_A1 | [8 empty] | 糠榔DS.261E | 261E (非取樣點) | SC | [5 empty] | 88 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 22 | 22kV | 260 | #6SC(260) |  | D1 | 261(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D19_A1 | [8 empty] | 糠榔DS.261 | 261 (非取樣點) | SC | [5 empty] | 89 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | 200 | TIE(200) |  | E1 | 201E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D19_A1 | [8 empty] | 糠榔DS.201E | 201E (非取樣點) | TIE | [5 empty] | 90 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 22 | 22kV | 200 | TIE(200) |  | E2 | 202E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D19_A1 | [8 empty] | 糠榔DS.202E | 202E (非取樣點) | TIE | [5 empty] | 91 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 22 | 22kV | 200 | TIE(200) |  | D1 | 201(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D19_A1 | [8 empty] | 糠榔DS.201 | 201 (非取樣點) | TIE | [5 empty] | 92 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | 200 | TIE(200) |  | D2 | 202(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D19_A1 | [8 empty] | 糠榔DS.202 | 202 (非取樣點) | TIE | [5 empty] | 93 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | 490 | #2SSTR(490) |  | D1 | 491(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D19_A1 | [8 empty] | 糠榔DS.491 | 491 (非取樣點) | OTHER | [5 empty] | 94 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | 490 | #2SSTR(490) |  | E1 | 491E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D19_A1 | [8 empty] | 糠榔DS.491E | 491E (非取樣點) | OTHER | [5 empty] | 95 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | 15B1E(非取樣點) | B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aaaz | B2/D19_A1 | [8 empty] | 糠榔DS.15B1E | 15B1E (非取樣點) | BUS | [5 empty] | 96 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | 15B2E(非取樣點) | B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/2Bus | [13 empty] | aaaz | B2/D19_A1 | [8 empty] | 糠榔DS.15B2E | 15B2E (非取樣點) | BUS | [5 empty] | 97 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | RTU | RTU |  | ADCL1 |  |  | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% TEST |  |  |  |  | B3/D19_A1 | [16 empty] | 98 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D19 | 槺榔DS | 0 |  | RTU | RTU |  | ADCH1 |  |  | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% TEST |  |  |  |  | B3/D19_A1 | [16 empty] | 99 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D19 | 槺榔DS |  |  | 1DTR | #1DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0002 |  |  | 1-82 |  |  | NO.1 D.TR. 油溫 |  |  | OIL_-120_120(-2000_2000) |  | B1/D19_A1 | [8 empty] | 糠榔DS.#1DTR_OIL | #1DTR 油溫 | MTR | [5 empty] | 100 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D19 | 槺榔DS |  |  | 1DTR(A) | #1DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0003 |  |  | 1-83 |  |  | NO.1 D.TR.(A) 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/D19_A1 | [8 empty] | 糠榔DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | [5 empty] | 101 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D19 | 槺榔DS |  |  | 1DTR(B) | #1DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | NO.1 D.TR.(B) 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/D19_A1 | [8 empty] | 糠榔DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | [5 empty] | 102 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D19 | 槺榔DS |  |  | 1DTR(A) | #1DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | NO.1 D.TR.(A) TAP |  | 對應CO-58/1 | TAP_-8.5_8.5(0_2000) |  | B1/D19_A1 | [8 empty] | 糠榔DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | [5 empty] | 103 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D19 | 槺榔DS |  |  | 1DTR(B) | #1DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | NO.1 D.TR.(B) TAP |  | 對應CO-60/1 | TAP_-8.5_8.5(0_2000) |  | B1/D19_A1 | [8 empty] | 糠榔DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | [5 empty] | 104 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D19 | 槺榔DS |  |  | 2DTR | #2DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | NO.2 D.TR. 油溫 |  |  | OIL_-120_120(-2000_2000) |  | B1/D19_A1 | [8 empty] | 糠榔DS.#2DTR_OIL | #2DTR 油溫 | MTR | [5 empty] | 105 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D19 | 槺榔DS |  |  | 2DTR | #2DTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | NO.2 D.TR. 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/D19_A1 | [8 empty] | 糠榔DS.#2DTR_COIL | #2DTR 線溫 | MTR | [5 empty] | 106 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D19 | 槺榔DS |  |  | 2DTR | #2DTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | NO.2 D.TR. TAP |  | 對應CO-62/1 | TAP_-8.5_8.5(0_2000) |  | B1/D19_A1 | [8 empty] | 糠榔DS.#2DTR_TAP | #2DTR OLTC TAP | MTR | [5 empty] | 107 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D19 | 槺榔DS |  |  | 3DTR | #3DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | NO.3 D.TR. 油溫 |  |  | OIL_-120_120(-2000_2000) |  | B1/D19_A1 | [8 empty] | 糠榔DS.#3DTR_OIL | #3DTR 油溫 | MTR | [5 empty] | 108 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D19 | 槺榔DS |  |  | 3DTR | #3DTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | NO.3 D.TR. 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/D19_A1 | [8 empty] | 糠榔DS.#3DTR_COIL | #3DTR 線溫 | MTR | [5 empty] | 109 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D19 | 槺榔DS |  |  | 3DTR | #3DTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0012 |  |  | 1-8C |  |  | NO.3 D.TR. TAP |  | 對應CO-64/1 | TAP_-8.5_8.5(0_2000) |  | B1/D19_A1 | [8 empty] | 糠榔DS.#3DTR_TAP | #3DTR OLTC TAP | MTR | [5 empty] | 110 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D19 | 槺榔DS | 0 |  | StaDev | 所內設施 |  | DCV_P |  |  | MvMoment | 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0013 |  |  | 1-8D |  |  | DC 125V P 電壓 |  |  | kV_-150_150(-2000_2000) |  | B3/D19_A1 | [8 empty] | 糠榔DS.直流P電源電壓 | 直流P電源電壓 | OTHER | [5 empty] | 111 |  |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 | 0.01 | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D19 | 槺榔DS | 0 |  | StaDev | 所內設施 |  | DCV_N |  |  | MvMoment | 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0014 |  |  | 1-8E |  |  | DC 125V N 電壓 |  |  | kV_-150_150(-2000_2000) |  | B3/D19_A1 | [8 empty] | 糠榔DS.直流N電源電壓 | 直流N電源電壓 | OTHER | [5 empty] | 112 |  |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 | 0.01 | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D19 | 槺榔DS | 0 |  | RTU | RTU |  | ADCL2 |  |  | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | 10% TEST |  |  |  |  | B3/D19_A1 | [16 empty] | 113 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D19 | 槺榔DS | 0 |  | RTU | RTU |  | ADCH2 |  |  | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | 90% TEST |  |  |  |  | B3/D19_A1 | [16 empty] | 114 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D19 | 槺榔DS | 161 | 161kV | 1BUS | #1BUS |  | V |  | B3 | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0064 |  |  | 1-C0 |  |  | 161KV NO.1 BUS 電壓 |  |  | kV_-210_210(-2000_2000) | aaa | B2/D19_A1 | [8 empty] | 糠榔DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | [5 empty] | 115 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D19 | 槺榔DS | 161 | 161kV | 2BUS | #2BUS |  | V |  | B3 | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0065 |  |  | 1-C1 |  |  | 161KV NO.2 BUS 電壓 |  |  | kV_-210_210(-2000_2000) | aab | B2/D19_A1 | [8 empty] | 糠榔DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | [5 empty] | 116 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D19 | 槺榔DS | 161 | 161kV | 1510 | 太鐵～槺榔一路(1510) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | 太鐵槺榔一路1510 瓦 |  |  | MW_-560_560(-2000_2000) |  | B2/D19_A1 | [8 empty] | 糠榔DS.1510_MW | 太鐵糠榔一路 MW | LINE161 | [5 empty] | 117 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D19 | 槺榔DS | 161 | 161kV | 1510 | 太鐵～槺榔一路(1510) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | 太鐵槺榔一路1510 乏 |  |  | MVAR_-560_560(-2000_2000) |  | B2/D19_A1 | [8 empty] | 糠榔DS.1510_MVAR | 太鐵糠榔一路 MVAR | LINE161 | [5 empty] | 118 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D19 | 槺榔DS | 161 | 161kV | 1520 | 太鐵～槺榔二路(1520) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | 太鐵槺榔二路1520 瓦 |  |  | MW_-560_560(-2000_2000) |  | B2/D19_A1 | [8 empty] | 糠榔DS.1520_MW | 太鐵糠榔二路 MW | LINE161 | [5 empty] | 119 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D19 | 槺榔DS | 161 | 161kV | 1520 | 太鐵～槺榔二路(1520) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | 太鐵槺榔二路1520 乏 |  |  | MVAR_-560_560(-2000_2000) |  | B2/D19_A1 | [8 empty] | 糠榔DS.1520_MVAR | 太鐵糠榔二路 MVAR | LINE161 | [5 empty] | 120 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D19 | 槺榔DS | 161 | 161kV | 1500 | TIE(1500) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | TIE (1500 ) R 相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/D19_A1 | [8 empty] | 糠榔DS.1500TIE_AMP | 1500TIE AMP | TIE | [5 empty] | 121 |  |  |  |  | AI | [5 empty] | C20R1600 | 1520 | 1600 | 1760 | 1968 | 2.27 | -1520 | -1600 | -1760 | -1968 | 1 | 0.01 | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | 310(M-1A) 瓦 |  |  | MW_-54_54(-2000_2000) |  | B3/D19_A1 | [8 empty] | 糠榔DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | [5 empty] | 122 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.054 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.054000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | 310(M-1A) 乏 |  |  | MVAR_-36_36(-2000_2000) |  | B3/D19_A1 | [8 empty] | 糠榔DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | [5 empty] | 123 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.036 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.036000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_R | , |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | 310(M-1A) R 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D19_A1 | [8 empty] | 糠榔DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | [5 empty] | 124 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | 310(M-1A) S 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D19_A1 | [8 empty] | 糠榔DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | [5 empty] | 125 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | 310(M-1A) T 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D19_A1 | [8 empty] | 糠榔DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | [5 empty] | 126 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 1ABUS | #1ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0088 |  |  | 1-D8 |  |  | 11KV-1A BUS(PT-1A) R 相電壓 |  |  | kV_-9_9(-2000_2000) | aaa | B3/D19_A1 | [8 empty] | 糠榔DS.11KV#1ABUS_KV | 11KV #1ABUS KV | BUS | [5 empty] | 127 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D19 | 槺榔DS | 11 | 11kV | JO21 | 槺21(JO21) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | 槺21(JO21) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠21線KVAR | 11KV糠21線 KVAR | FEEDER | [5 empty] | 128 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO21 | 槺21(JO21) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | 槺21(JO21) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠21線A1 | 11KV糠21線 R相AMP | FEEDER | [5 empty] | 129 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO21 | 槺21(JO21) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | 槺21(JO21) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠21線A2 | 11KV糠21線 S相AMP | FEEDER | [5 empty] | 130 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO21 | 槺21(JO21) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | 槺21(JO21) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠21線A3 | 11KV糠21線 T相AMP | FEEDER | [5 empty] | 131 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO21 | 槺21(JO21) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | 槺21(JO21) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠21線A0 | 11KV糠21線 N相AMP | FEEDER | [5 empty] | 132 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO22 | 槺22(JO22) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | 槺22(JO22) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠22線KVAR | 11KV糠22線 KVAR | FEEDER | [5 empty] | 133 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO22 | 槺22(JO22) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | 槺22(JO22) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠22線A1 | 11KV糠22線 R相AMP | FEEDER | [5 empty] | 134 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO22 | 槺22(JO22) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | 槺22(JO22) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠22線A2 | 11KV糠22線 S相AMP | FEEDER | [5 empty] | 135 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO22 | 槺22(JO22) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | 槺22(JO22) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠22線A3 | 11KV糠22線 T相AMP | FEEDER | [5 empty] | 136 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO22 | 槺22(JO22) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0098 |  |  | 1-E2 |  |  | 槺22(JO22) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠22線A0 | 11KV糠22線 N相AMP | FEEDER | [5 empty] | 137 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO23 | 槺23(JO23) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | 槺23(JO23) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠23線KVAR | 11KV糠23線 KVAR | FEEDER | [5 empty] | 138 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO23 | 槺23(JO23) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | 槺23(JO23) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠23線A1 | 11KV糠23線 R相AMP | FEEDER | [5 empty] | 139 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO23 | 槺23(JO23) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0101 |  |  | 1-E5 |  |  | 槺23(JO23) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠23線A2 | 11KV糠23線 S相AMP | FEEDER | [5 empty] | 140 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO23 | 槺23(JO23) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | 槺23(JO23) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠23線A3 | 11KV糠23線 T相AMP | FEEDER | [5 empty] | 141 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO23 | 槺23(JO23) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | 槺23(JO23) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠23線A0 | 11KV糠23線 N相AMP | FEEDER | [5 empty] | 142 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO24 | 槺24(JO24) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | 槺24(JO24) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠24線KVAR | 11KV糠24線 KVAR | FEEDER | [5 empty] | 143 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO24 | 槺24(JO24) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | 槺24(JO24) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠24線A1 | 11KV糠24線 R相AMP | FEEDER | [5 empty] | 144 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO24 | 槺24(JO24) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | 槺24(JO24) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠24線A2 | 11KV糠24線 S相AMP | FEEDER | [5 empty] | 145 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO24 | 槺24(JO24) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | 槺24(JO24) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠24線A3 | 11KV糠24線 T相AMP | FEEDER | [5 empty] | 146 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO24 | 槺24(JO24) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | 槺24(JO24) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠24線A0 | 11KV糠24線 N相AMP | FEEDER | [5 empty] | 147 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO25 | 槺25(JO25) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | 槺25(JO25) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠25線KVAR | 11KV糠25線 KVAR | FEEDER | [5 empty] | 148 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO25 | 槺25(JO25) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | 槺25(JO25) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠25線A1 | 11KV糠25線 R相AMP | FEEDER | [5 empty] | 149 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO25 | 槺25(JO25) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | 槺25(JO25) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠25線A2 | 11KV糠25線 S相AMP | FEEDER | [5 empty] | 150 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO25 | 槺25(JO25) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | 槺25(JO25) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠25線A3 | 11KV糠25線 T相AMP | FEEDER | [5 empty] | 151 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO25 | 槺25(JO25) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | 槺25(JO25) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠25線A0 | 11KV糠25線 N相AMP | FEEDER | [5 empty] | 152 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 100 | TIE(100) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | 100(TIE-1A) R 相電流 |  |  | A_-2000_2000(-2000_2000) |  | B3/D19_A1 | [8 empty] | 糠榔DS.11KV_100_A1 | 11KV 100 R相AMP | TIE | [5 empty] | 153 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 100 | TIE(100) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | 100(TIE-1A) S 相電流 |  |  | A_-2000_2000(-2000_2000) |  | B3/D19_A1 | [8 empty] | 糠榔DS.11KV_100_A2 | 11KV 100 S相AMP | TIE | [5 empty] | 154 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 100 | TIE(100) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | 100(TIE-1A) T 相電流 |  |  | A_-2000_2000(-2000_2000) |  | B3/D19_A1 | [8 empty] | 糠榔DS.11KV_100_A3 | 11KV 100 T相AMP | TIE | [5 empty] | 155 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | 320(M-1B) 瓦 |  |  | MW_-54_54(-2000_2000) |  | B3/D19_A1 | [8 empty] | 糠榔DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | [5 empty] | 156 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.054 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.054000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | 320(M-1B) 乏 |  |  | MVAR_-36_36(-2000_2000) |  | B3/D19_A1 | [8 empty] | 糠榔DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | [5 empty] | 157 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.036 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.036000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | 320(M-1B) R 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D19_A1 | [8 empty] | 糠榔DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | [5 empty] | 158 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | 320(M-1B) S 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D19_A1 | [8 empty] | 糠榔DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | [5 empty] | 159 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | 320(M-1B) T 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D19_A1 | [8 empty] | 糠榔DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | [5 empty] | 160 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 1BBUS | #1BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0122 |  |  | 1-FA |  |  | 11KV-1B BUS(PT-1B) R 相電壓 |  |  | kV_-9_9(-2000_2000) | aba | B3/D19_A1 | [8 empty] | 糠榔DS.11KV#1BBUS_KV | 11KV #1BBUS KV | BUS | [5 empty] | 161 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D19 | 槺榔DS | 11 | 11kV | JO26 | 槺26(JO26) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | 槺26(JO26) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠26線KVAR | 11KV糠26線 KVAR | FEEDER | [5 empty] | 162 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO26 | 槺26(JO26) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | 槺26(JO26) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠26線A1 | 11KV糠26線 R相AMP | FEEDER | [5 empty] | 163 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO26 | 槺26(JO26) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | 槺26(JO26) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠26線A2 | 11KV糠26線 S相AMP | FEEDER | [5 empty] | 164 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO26 | 槺26(JO26) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | 槺26(JO26) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠26線A3 | 11KV糠26線 T相AMP | FEEDER | [5 empty] | 165 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO26 | 槺26(JO26) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | 槺26(JO26) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠26線A0 | 11KV糠26線 N相AMP | FEEDER | [5 empty] | 166 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO27 | 槺27(JO27) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 槺27(JO27) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠27線KVAR | 11KV糠27線 KVAR | FEEDER | [5 empty] | 167 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO27 | 槺27(JO27) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 槺27(JO27) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠27線A1 | 11KV糠27線 R相AMP | FEEDER | [5 empty] | 168 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO27 | 槺27(JO27) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | 槺27(JO27) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠27線A2 | 11KV糠27線 S相AMP | FEEDER | [5 empty] | 169 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO27 | 槺27(JO27) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | 槺27(JO27) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠27線A3 | 11KV糠27線 T相AMP | FEEDER | [5 empty] | 170 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO27 | 槺27(JO27) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | 槺27(JO27) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠27線A0 | 11KV糠27線 N相AMP | FEEDER | [5 empty] | 171 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO28 | 槺28(JO28) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0133 |  |  | 2-85 |  |  | 槺28(JO28) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠28線KVAR | 11KV糠28線 KVAR | FEEDER | [5 empty] | 172 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO28 | 槺28(JO28) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | 槺28(JO28) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠28線A1 | 11KV糠28線 R相AMP | FEEDER | [5 empty] | 173 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO28 | 槺28(JO28) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0135 |  |  | 2-87 |  |  | 槺28(JO28) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠28線A2 | 11KV糠28線 S相AMP | FEEDER | [5 empty] | 174 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO28 | 槺28(JO28) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0136 |  |  | 2-88 |  |  | 槺28(JO28) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠28線A3 | 11KV糠28線 T相AMP | FEEDER | [5 empty] | 175 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO28 | 槺28(JO28) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0137 |  |  | 2-89 |  |  | 槺28(JO28) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠28線A0 | 11KV糠28線 N相AMP | FEEDER | [5 empty] | 176 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO29 | 槺29(JO29) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0138 |  |  | 2-8A |  |  | 槺29(JO29) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠29線KVAR | 11KV糠29線 KVAR | FEEDER | [5 empty] | 177 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO29 | 槺29(JO29) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0139 |  |  | 2-8B |  |  | 槺29(JO29) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠29線A1 | 11KV糠29線 R相AMP | FEEDER | [5 empty] | 178 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO29 | 槺29(JO29) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0140 |  |  | 2-8C |  |  | 槺29(JO29) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠29線A2 | 11KV糠29線 S相AMP | FEEDER | [5 empty] | 179 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO29 | 槺29(JO29) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0141 |  |  | 2-8D |  |  | 槺29(JO29) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠29線A3 | 11KV糠29線 T相AMP | FEEDER | [5 empty] | 180 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO29 | 槺29(JO29) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0142 |  |  | 2-8E |  |  | 槺29(JO29) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠29線A0 | 11KV糠29線 N相AMP | FEEDER | [5 empty] | 181 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO30 | 槺30(JO30) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0143 |  |  | 2-8F |  |  | 槺30(JO30) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠30線KVAR | 11KV糠30線 KVAR | FEEDER | [5 empty] | 182 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO30 | 槺30(JO30) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0144 |  |  | 2-90 |  |  | 槺30(JO30) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠30線A1 | 11KV糠30線 R相AMP | FEEDER | [5 empty] | 183 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO30 | 槺30(JO30) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0145 |  |  | 2-91 |  |  | 槺30(JO30) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠30線A2 | 11KV糠30線 S相AMP | FEEDER | [5 empty] | 184 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO30 | 槺30(JO30) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0146 |  |  | 2-92 |  |  | 槺30(JO30) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠30線A3 | 11KV糠30線 T相AMP | FEEDER | [5 empty] | 185 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | JO30 | 槺30(JO30) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0147 |  |  | 2-93 |  |  | 槺30(JO30) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠30線A0 | 11KV糠30線 N相AMP | FEEDER | [5 empty] | 186 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 330 | #2DTR(330) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0148 |  |  | 2-94 |  |  | 330(M-2) 瓦 |  |  | MW_-108_108(-2000_2000) |  | B3/D19_A1 | [8 empty] | 糠榔DS.#2DTR_MW | #2DTR二次側 MW | MTR | [5 empty] | 187 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 330 | #2DTR(330) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0149 |  |  | 2-95 |  |  | 330(M-2) 乏 |  |  | MVAR_-72_72(-2000_2000) |  | B3/D19_A1 | [8 empty] | 糠榔DS.#2DTR_MVAR | #2DTR二次側 MVAR | MTR | [5 empty] | 188 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 330 | #2DTR(330) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0150 |  |  | 2-96 |  |  | 330(M-2) R 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D19_A1 | [8 empty] | 糠榔DS.#2DTR_A1 | #2DTR二次側 R相AMP | MTR | [5 empty] | 189 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 330 | #2DTR(330) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0151 |  |  | 2-97 |  |  | 330(M-2) S 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D19_A1 | [8 empty] | 糠榔DS.#2DTR_A2 | #2DTR二次側 S相AMP | MTR | [5 empty] | 190 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 330 | #2DTR(330) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0152 |  |  | 2-98 |  |  | 330(M-2) T 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D19_A1 | [8 empty] | 糠榔DS.#2DTR_A3 | #2DTR二次側 T相AMP | MTR | [5 empty] | 191 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0153 |  |  | 2-99 |  |  | PT-2 R 相電壓 |  |  | kV_-18_18(-2000_2000) | aca | B3/D19_A1 | [8 empty] | 糠榔DS.23KV#2BUS_KV | 23KV #2BUS KV | BUS | [5 empty] | 192 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D19 | 槺榔DS | 22 | 22kV | JO61 | 槺61(JO61) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0154 |  |  | 2-9A |  |  | 槺61(JO61) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠61線KVAR | 23KV糠61線 KVAR | FEEDER | [5 empty] | 193 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO61 | 槺61(JO61) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0155 |  |  | 2-9B |  |  | 槺61(JO61) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠61線A1 | 23KV糠61線 R相AMP | FEEDER | [5 empty] | 194 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO61 | 槺61(JO61) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0156 |  |  | 2-9C |  |  | 槺61(JO61) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠61線A2 | 23KV糠61線 S相AMP | FEEDER | [5 empty] | 195 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO61 | 槺61(JO61) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0157 |  |  | 2-9D |  |  | 槺61(JO61) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠61線A3 | 23KV糠61線 T相AMP | FEEDER | [5 empty] | 196 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO61 | 槺61(JO61) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0158 |  |  | 2-9E |  |  | 槺61(JO61) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠61線A0 | 23KV糠61線 N相AMP | FEEDER | [5 empty] | 197 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO62 | 槺62(JO62) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0159 |  |  | 2-9F |  |  | 槺62(JO62) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠62線KVAR | 23KV糠62線 KVAR | FEEDER | [5 empty] | 198 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO62 | 槺62(JO62) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0160 |  |  | 2-A0 |  |  | 槺62(JO62) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠62線A1 | 23KV糠62線 R相AMP | FEEDER | [5 empty] | 199 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO62 | 槺62(JO62) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0161 |  |  | 2-A1 |  |  | 槺62(JO62) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠62線A2 | 23KV糠62線 S相AMP | FEEDER | [5 empty] | 200 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO62 | 槺62(JO62) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0162 |  |  | 2-A2 |  |  | 槺62(JO62) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠62線A3 | 23KV糠62線 T相AMP | FEEDER | [5 empty] | 201 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO62 | 槺62(JO62) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0163 |  |  | 2-A3 |  |  | 槺62(JO62) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠62線A0 | 23KV糠62線 N相AMP | FEEDER | [5 empty] | 202 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO63 | 槺63(JO63) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0164 |  |  | 2-A4 |  |  | 槺63(JO63) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠63線KVAR | 23KV糠63線 KVAR | FEEDER | [5 empty] | 203 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO63 | 槺63(JO63) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0165 |  |  | 2-A5 |  |  | 槺63(JO63) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠63線A1 | 23KV糠63線 R相AMP | FEEDER | [5 empty] | 204 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO63 | 槺63(JO63) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0166 |  |  | 2-A6 |  |  | 槺63(JO63) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠63線A2 | 23KV糠63線 S相AMP | FEEDER | [5 empty] | 205 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO63 | 槺63(JO63) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0167 |  |  | 2-A7 |  |  | 槺63(JO63) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠63線A3 | 23KV糠63線 T相AMP | FEEDER | [5 empty] | 206 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO63 | 槺63(JO63) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0168 |  |  | 2-A8 |  |  | 槺63(JO63) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠63線A0 | 23KV糠63線 N相AMP | FEEDER | [5 empty] | 207 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO64 | 槺64(JO64) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0169 |  |  | 2-A9 |  |  | 槺64(JO64) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠64線KVAR | 23KV糠64線 KVAR | FEEDER | [5 empty] | 208 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO64 | 槺64(JO64) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0170 |  |  | 2-AA |  |  | 槺64(JO64) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠64線A1 | 23KV糠64線 R相AMP | FEEDER | [5 empty] | 209 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO64 | 槺64(JO64) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0171 |  |  | 2-AB |  |  | 槺64(JO64) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠64線A2 | 23KV糠64線 S相AMP | FEEDER | [5 empty] | 210 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO64 | 槺64(JO64) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0172 |  |  | 2-AC |  |  | 槺64(JO64) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠64線A3 | 23KV糠64線 T相AMP | FEEDER | [5 empty] | 211 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO64 | 槺64(JO64) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0173 |  |  | 2-AD |  |  | 槺64(JO64) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠64線A0 | 23KV糠64線 N相AMP | FEEDER | [5 empty] | 212 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO65 | 槺65(JO65) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0174 |  |  | 2-AE |  |  | 槺65(JO65) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠65線KVAR | 23KV糠65線 KVAR | FEEDER | [5 empty] | 213 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO65 | 槺65(JO65) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0175 |  |  | 2-AF |  |  | 槺65(JO65) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠65線A1 | 23KV糠65線 R相AMP | FEEDER | [5 empty] | 214 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO65 | 槺65(JO65) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0176 |  |  | 2-B0 |  |  | 槺65(JO65) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠65線A2 | 23KV糠65線 S相AMP | FEEDER | [5 empty] | 215 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO65 | 槺65(JO65) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0177 |  |  | 2-B1 |  |  | 槺65(JO65) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠65線A3 | 23KV糠65線 T相AMP | FEEDER | [5 empty] | 216 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO65 | 槺65(JO65) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0178 |  |  | 2-B2 |  |  | 槺65(JO65) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠65線A0 | 23KV糠65線 N相AMP | FEEDER | [5 empty] | 217 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO66 | 槺66(JO66) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0179 |  |  | 2-B3 |  |  | 槺66(JO66) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠66線KVAR | 23KV糠66線 KVAR | FEEDER | [5 empty] | 218 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO66 | 槺66(JO66) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0180 |  |  | 2-B4 |  |  | 槺66(JO66) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠66線A1 | 23KV糠66線 R相AMP | FEEDER | [5 empty] | 219 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO66 | 槺66(JO66) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0181 |  |  | 2-B5 |  |  | 槺66(JO66) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠66線A2 | 23KV糠66線 S相AMP | FEEDER | [5 empty] | 220 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO66 | 槺66(JO66) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0182 |  |  | 2-B6 |  |  | 槺66(JO66) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠66線A3 | 23KV糠66線 T相AMP | FEEDER | [5 empty] | 221 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO66 | 槺66(JO66) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0183 |  |  | 2-B7 |  |  | 槺66(JO66) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠66線A0 | 23KV糠66線 N相AMP | FEEDER | [5 empty] | 222 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO67 | 槺67(JO67) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0184 |  |  | 2-B8 |  |  | 槺67(JO67) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠67線KVAR | 23KV糠67線 KVAR | FEEDER | [5 empty] | 223 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO67 | 槺67(JO67) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0185 |  |  | 2-B9 |  |  | 槺67(JO67) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠67線A1 | 23KV糠67線 R相AMP | FEEDER | [5 empty] | 224 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO67 | 槺67(JO67) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0186 |  |  | 2-BA |  |  | 槺67(JO67) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠67線A2 | 23KV糠67線 S相AMP | FEEDER | [5 empty] | 225 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO67 | 槺67(JO67) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0187 |  |  | 2-BB |  |  | 槺67(JO67) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠67線A3 | 23KV糠67線 T相AMP | FEEDER | [5 empty] | 226 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO67 | 槺67(JO67) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0188 |  |  | 2-BC |  |  | 槺67(JO67) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠67線A0 | 23KV糠67線 N相AMP | FEEDER | [5 empty] | 227 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO68 | 槺68(JO68) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0189 |  |  | 2-BD |  |  | 槺68(JO68) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠68線KVAR | 23KV糠68線 KVAR | FEEDER | [5 empty] | 228 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO68 | 槺68(JO68) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0190 |  |  | 2-BE |  |  | 槺68(JO68) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠68線A1 | 23KV糠68線 R相AMP | FEEDER | [5 empty] | 229 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO68 | 槺68(JO68) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0191 |  |  | 2-BF |  |  | 槺68(JO68) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠68線A2 | 23KV糠68線 S相AMP | FEEDER | [5 empty] | 230 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO68 | 槺68(JO68) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0192 |  |  | 2-C0 |  |  | 槺68(JO68) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠68線A3 | 23KV糠68線 T相AMP | FEEDER | [5 empty] | 231 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO68 | 槺68(JO68) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0193 |  |  | 2-C1 |  |  | 槺68(JO68) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠68線A0 | 23KV糠68線 N相AMP | FEEDER | [5 empty] | 232 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 350 | #3DTR(350) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0194 |  |  | 2-C2 |  |  | 350(M-3) 瓦 |  |  | MW_-108_108(-2000_2000) |  | B3/D19_A1 | [8 empty] | 糠榔DS.#3DTR_MW | #3DTR二次側 MW | MTR | [5 empty] | 233 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 350 | #3DTR(350) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0195 |  |  | 2-C3 |  |  | 350(M-3) 乏 |  |  | MVAR_-72_72(-2000_2000) |  | B3/D19_A1 | [8 empty] | 糠榔DS.#3DTR_MVAR | #3DTR二次側 MVAR | MTR | [5 empty] | 234 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 350 | #3DTR(350) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0196 |  |  | 2-C4 |  |  | 350(M-3) R 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D19_A1 | [8 empty] | 糠榔DS.#3DTR_A1 | #3DTR二次側 R相AMP | MTR | [5 empty] | 235 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 350 | #3DTR(350) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0197 |  |  | 2-C5 |  |  | 350(M-3) S 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D19_A1 | [8 empty] | 糠榔DS.#3DTR_A2 | #3DTR二次側 S相AMP | MTR | [5 empty] | 236 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 350 | #3DTR(350) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0198 |  |  | 2-C6 |  |  | 350(M-3) T 相電流 |  |  | A_-3000_3000(-2000_2000) |  | B3/D19_A1 | [8 empty] | 糠榔DS.#3DTR_A3 | #3DTR二次側 T相AMP | MTR | [5 empty] | 237 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 3BUS | #3BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0199 |  |  | 2-C7 |  |  | PT-3 R 相電壓 |  |  | kV_-18_18(-2000_2000) | ada | B3/D19_A1 | [8 empty] | 糠榔DS.23KV#3BUS_KV | 23KV #3BUS KV | BUS | [5 empty] | 238 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D19 | 槺榔DS | 22 | 22kV | JO71 | 槺71(JO71) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0200 |  |  | 2-C8 |  |  | 槺71(JO71) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠71線KVAR | 23KV糠71線 KVAR | FEEDER | [5 empty] | 239 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO71 | 槺71(JO71) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0201 |  |  | 2-C9 |  |  | 槺71(JO71) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠71線A1 | 23KV糠71線 R相AMP | FEEDER | [5 empty] | 240 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO71 | 槺71(JO71) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0202 |  |  | 2-CA |  |  | 槺71(JO71) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠71線A2 | 23KV糠71線 S相AMP | FEEDER | [5 empty] | 241 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO71 | 槺71(JO71) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0203 |  |  | 2-CB |  |  | 槺71(JO71) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠71線A3 | 23KV糠71線 T相AMP | FEEDER | [5 empty] | 242 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO71 | 槺71(JO71) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0204 |  |  | 2-CC |  |  | 槺71(JO71) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠71線A0 | 23KV糠71線 N相AMP | FEEDER | [5 empty] | 243 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO72 | 槺72(JO72) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0205 |  |  | 2-CD |  |  | 槺72(JO72) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠72線KVAR | 23KV糠72線 KVAR | FEEDER | [5 empty] | 244 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO72 | 槺72(JO72) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0206 |  |  | 2-CE |  |  | 槺72(JO72) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠72線A1 | 23KV糠72線 R相AMP | FEEDER | [5 empty] | 245 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO72 | 槺72(JO72) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0207 |  |  | 2-CF |  |  | 槺72(JO72) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠72線A2 | 23KV糠72線 S相AMP | FEEDER | [5 empty] | 246 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO72 | 槺72(JO72) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0208 |  |  | 2-D0 |  |  | 槺72(JO72) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠72線A3 | 23KV糠72線 T相AMP | FEEDER | [5 empty] | 247 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO72 | 槺72(JO72) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0209 |  |  | 2-D1 |  |  | 槺72(JO72) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠72線A0 | 23KV糠72線 N相AMP | FEEDER | [5 empty] | 248 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO73 | 槺73(JO73) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0210 |  |  | 2-D2 |  |  | 槺73(JO73) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠73線KVAR | 23KV糠73線 KVAR | FEEDER | [5 empty] | 249 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO73 | 槺73(JO73) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0211 |  |  | 2-D3 |  |  | 槺73(JO73) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠73線A1 | 23KV糠73線 R相AMP | FEEDER | [5 empty] | 250 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO73 | 槺73(JO73) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0212 |  |  | 2-D4 |  |  | 槺73(JO73) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠73線A2 | 23KV糠73線 S相AMP | FEEDER | [5 empty] | 251 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO73 | 槺73(JO73) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0213 |  |  | 2-D5 |  |  | 槺73(JO73) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠73線A3 | 23KV糠73線 T相AMP | FEEDER | [5 empty] | 252 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO73 | 槺73(JO73) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0214 |  |  | 2-D6 |  |  | 槺73(JO73) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠73線A0 | 23KV糠73線 N相AMP | FEEDER | [5 empty] | 253 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO74 | 槺74(JO74) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0215 |  |  | 2-D7 |  |  | 槺74(JO74) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠74線KVAR | 23KV糠74線 KVAR | FEEDER | [5 empty] | 254 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO74 | 槺74(JO74) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0216 |  |  | 2-D8 |  |  | 槺74(JO74) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠74線A1 | 23KV糠74線 R相AMP | FEEDER | [5 empty] | 255 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO74 | 槺74(JO74) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0217 |  |  | 2-D9 |  |  | 槺74(JO74) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠74線A2 | 23KV糠74線 S相AMP | FEEDER | [5 empty] | 256 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO74 | 槺74(JO74) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0218 |  |  | 2-DA |  |  | 槺74(JO74) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠74線A3 | 23KV糠74線 T相AMP | FEEDER | [5 empty] | 257 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO74 | 槺74(JO74) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0219 |  |  | 2-DB |  |  | 槺74(JO74) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠74線A0 | 23KV糠74線 N相AMP | FEEDER | [5 empty] | 258 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO75 | 槺75(JO75) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0220 |  |  | 2-DC |  |  | 槺75(JO75) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠75線KVAR | 23KV糠75線 KVAR | FEEDER | [5 empty] | 259 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO75 | 槺75(JO75) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0221 |  |  | 2-DD |  |  | 槺75(JO75) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠75線A1 | 23KV糠75線 R相AMP | FEEDER | [5 empty] | 260 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO75 | 槺75(JO75) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0222 |  |  | 2-DE |  |  | 槺75(JO75) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠75線A2 | 23KV糠75線 S相AMP | FEEDER | [5 empty] | 261 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO75 | 槺75(JO75) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0223 |  |  | 2-DF |  |  | 槺75(JO75) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠75線A3 | 23KV糠75線 T相AMP | FEEDER | [5 empty] | 262 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO75 | 槺75(JO75) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0224 |  |  | 2-E0 |  |  | 槺75(JO75) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠75線A0 | 23KV糠75線 N相AMP | FEEDER | [5 empty] | 263 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO76 | 槺76(JO76) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0225 |  |  | 2-E1 |  |  | 槺76(JO76) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠76線KVAR | 23KV糠76線 KVAR | FEEDER | [5 empty] | 264 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO76 | 槺76(JO76) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0226 |  |  | 2-E2 |  |  | 槺76(JO76) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠76線A1 | 23KV糠76線 R相AMP | FEEDER | [5 empty] | 265 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO76 | 槺76(JO76) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0227 |  |  | 2-E3 |  |  | 槺76(JO76) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠76線A2 | 23KV糠76線 S相AMP | FEEDER | [5 empty] | 266 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO76 | 槺76(JO76) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0228 |  |  | 2-E4 |  |  | 槺76(JO76) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠76線A3 | 23KV糠76線 T相AMP | FEEDER | [5 empty] | 267 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO76 | 槺76(JO76) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0229 |  |  | 2-E5 |  |  | 槺76(JO76) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠76線A0 | 23KV糠76線 N相AMP | FEEDER | [5 empty] | 268 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO77 | 槺77(JO77) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0230 |  |  | 2-E6 |  |  | 槺77(JO77) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠77線KVAR | 23KV糠77線 KVAR | FEEDER | [5 empty] | 269 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO77 | 槺77(JO77) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0231 |  |  | 2-E7 |  |  | 槺77(JO77) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠77線A1 | 23KV糠77線 R相AMP | FEEDER | [5 empty] | 270 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO77 | 槺77(JO77) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0232 |  |  | 2-E8 |  |  | 槺77(JO77) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠77線A2 | 23KV糠77線 S相AMP | FEEDER | [5 empty] | 271 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO77 | 槺77(JO77) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0233 |  |  | 2-E9 |  |  | 槺77(JO77) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠77線A3 | 23KV糠77線 T相AMP | FEEDER | [5 empty] | 272 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO77 | 槺77(JO77) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0234 |  |  | 2-EA |  |  | 槺77(JO77) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠77線A0 | 23KV糠77線 N相AMP | FEEDER | [5 empty] | 273 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO78 | 槺78(JO78) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0235 |  |  | 2-EB |  |  | 槺78(JO78) 乏 |  |  | KVAR_-21600_21600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠78線KVAR | 23KV糠78線 KVAR | FEEDER | [5 empty] | 274 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO78 | 槺78(JO78) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0236 |  |  | 2-EC |  |  | 槺78(JO78) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠78線A1 | 23KV糠78線 R相AMP | FEEDER | [5 empty] | 275 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO78 | 槺78(JO78) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0237 |  |  | 2-ED |  |  | 槺78(JO78) S 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠78線A2 | 23KV糠78線 S相AMP | FEEDER | [5 empty] | 276 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO78 | 槺78(JO78) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0238 |  |  | 2-EE |  |  | 槺78(JO78) T 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠78線A3 | 23KV糠78線 T相AMP | FEEDER | [5 empty] | 277 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | JO78 | 槺78(JO78) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0239 |  |  | 2-EF |  |  | 槺78(JO78) N 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/D19_D1 | [8 empty] | 糠榔DS.糠78線A0 | 23KV糠78線 N相AMP | FEEDER | [5 empty] | 278 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 200 | TIE(200) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0240 |  |  | 2-F0 |  |  | 200(TIE-3) R 相電流 |  |  | A_-2000_2000(-2000_2000) |  | B3/D19_A1 | [8 empty] | 糠榔DS.23KV_200_A1 | 23KV 200 R相AMP | TIE | [5 empty] | 279 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 200 | TIE(200) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0241 |  |  | 2-F1 |  |  | 200(TIE-3) S 相電流 |  |  | A_-2000_2000(-2000_2000) |  | B3/D19_A1 | [8 empty] | 糠榔DS.23KV_200_A2 | 23KV 200 S相AMP | TIE | [5 empty] | 280 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 200 | TIE(200) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0242 |  |  | 2-F2 |  |  | 200(TIE-3) T 相電流 |  |  | A_-2000_2000(-2000_2000) |  | B3/D19_A1 | [8 empty] | 糠榔DS.23KV_200_A3 | 23KV 200 T相AMP | TIE | [5 empty] | 281 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 161 | 161kV | 1510 | 太鐵～槺榔一路(1510) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D07D191/T2 |  | 0000 |  |  | 1-00-00 |  |  | 太鐵槺榔一路1510 CB ON/OFF |  | PPU-1 |  | aaca | B2/D19_A1 | [8 empty] | 糠榔DS.1510_CB | 1510(太鐵糠榔一路) CB | LINE161 | [5 empty] | 282 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 161 | 161kV | 1510 | 太鐵～槺榔一路(1510) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0001 |  |  | 1-00-01 |  |  | 太鐵槺榔一路1510 87A |  | PPU-1 |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.1510_87A | 太鐵糠榔一路(1510) 87RY | LINE161 | [5 empty] | 283 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1510 | 太鐵～槺榔一路(1510) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0002 |  |  | 1-00-02 |  |  | 太鐵槺榔一路1510 PHA |  | PPU-1 |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.1510_PHA | 太鐵糠榔一路(1510) 相間RY | LINE161 | [5 empty] | 284 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1510 | 太鐵～槺榔一路(1510) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | 太鐵槺榔一路1510 GDA |  | PPU-1 |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.1510_GDA | 太鐵糠榔一路(1510) 接地RY | LINE161 | [5 empty] | 285 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1520 | 太鐵～槺榔二路(1520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D07D192/T2 |  | 0004 |  |  | 1-00-04 |  |  | 太鐵槺榔二路1520 CB ON/OFF |  | PPU-1 |  | aada | B2/D19_A1 | [8 empty] | 糠榔DS.1520_CB | 1520(太鐵糠榔二路) CB | LINE161 | [5 empty] | 286 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 161 | 161kV | 1520 | 太鐵～槺榔二路(1520) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0005 |  |  | 1-00-05 |  |  | 太鐵槺榔二路1520 87A |  | PPU-1 |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.1520_87A | 太鐵糠榔二路(1520) 87RY | LINE161 | [5 empty] | 287 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1520 | 太鐵～槺榔二路(1520) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | 太鐵槺榔二路1520 PHA |  | PPU-1 |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.1520_PHA | 太鐵糠榔二路(1520) 相間RY | LINE161 | [5 empty] | 288 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1520 | 太鐵～槺榔二路(1520) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-07 |  |  | 太鐵槺榔二路1520 GDA |  | PPU-1 |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.1520_GDA | 太鐵糠榔二路(1520) 接地RY | LINE161 | [5 empty] | 289 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0032 |  |  | 1-04-00 |  |  | 1500 CB ON/OFF |  | PPU-1 |  | aaez | B2/D19_A1 | [8 empty] | 糠榔DS.1500_CB | 1500(TIE) CB | TIE | [5 empty] | 290 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0033 |  |  | 1-04-01 |  |  | 1500 50A |  | PPU-1 |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.1500_50A | 161KV TIE(1500) 50RY | TIE | [5 empty] | 291 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | #1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0034 |  |  | 1-04-02 |  |  | 87B1A |  | PPU-1 |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | [5 empty] | 292 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | #2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0035 |  |  | 1-04-03 |  |  | 87B2A |  | PPU-1 |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | [5 empty] | 293 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0036 |  |  | 1-04-04 |  |  | 161KV RCA |  | PPU-1 |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | [5 empty] | 294 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | ComPoint |  |  | OSCA1 |  |  | Status | #1 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0037 |  |  | 1-04-05 |  |  | #1OSC 示波器啟動警報 OSCA1 |  | PPU-1 |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.161KV_OSCA_1 | 161KV示波器啟動警報(1) | OTHER | [5 empty] | 295 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | ComPoint |  |  | OSCA2 |  |  | Status | #2 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0038 |  |  | 1-04-06 |  |  | #2OSC 示波器故障警報 OSCA2 |  | PPU-1 |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.161KV_OSCA_2 | 161KV示波器啟動警報(2) | OTHER | [5 empty] | 296 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0039 |  |  | 1-04-07 |  |  | #3OSC OSCA3 |  | PPU-1 |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.161KV_OSCA_3 | 161KV示波器啟動警報(3) | OTHER | [5 empty] | 297 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/1DTR |  | 0048 |  |  | 1-06-00 |  |  | 1750 CB ON/OFF |  | PPU-2 |  | aabb | ELEM/D19_A1 | [8 empty] | 糠榔DS.1750_CB | 1750(#1DTR) CB | MTR | [5 empty] | 298 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS |  |  | 1DTR | #1DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0049 |  |  | 1-06-01 |  |  | NO.1 DTR 87A |  | PPU-2 |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#1DTR_87A | #1DTR 87RY | MTR | [5 empty] | 299 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS |  |  | 1DTR | #1DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0050 |  |  | 1-06-02 |  |  | NO.1 DTR 96PA |  | PPU-2 |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | [5 empty] | 300 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS |  |  | 1DTR | #1DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0051 |  |  | 1-06-03 |  |  | NO.1 DTR 51ZA |  | PPU-2 |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | [5 empty] | 301 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1750 | #1DTR(1750) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | NO.1 DTR PHA |  | PPU-2 |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.#1DTR_PHA | #1DTR 50/51 RY | OTHER | [5 empty] | 302 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1750 | #1DTR(1750) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0053 |  |  | 1-06-05 |  |  | NO.1 DTR GDA |  | PPU-2 |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.#1DTR_GDA | #1DTR 50N/51N RY | OTHER | [5 empty] | 303 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0054 |  |  | 1-06-06 |  |  | NO.1 DTR 86A |  | PPU-2 |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.#1DTR_86A | #1DTR 86(50/50N/51Z/87/96)RY | OTHER | [5 empty] | 304 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | T/1DTR(A) |  |  | 0055 |  |  | 1-06-07 |  |  | 310(M-1A) CB ON/OFF |  | PPU-2 |  | aaaa | ELEM/D19_A1 | [8 empty] | 糠榔DS.310_CB | 310(#1DTR) CB | MTR | [5 empty] | 305 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0056 |  |  | 1-07-00 |  |  | 310(M-1A) PHA |  | PPU-2 |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.310_51A | #1DTR二次側(310) 51RY | MTR | [5 empty] | 306 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0057 |  |  | 1-07-01 |  |  | 310(M-1A) GDA |  | PPU-2 |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.310_GDA | 310開關箱IED RY GDA | OTHER | [5 empty] | 307 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0058 |  |  | 1-07-02 |  |  | 310(M-1A) 81A |  | PPU-2 |  |  | ELEM/D19_A1 | [8 empty] | 糠榔DS.310_81A | 310 #1DTR(A) 81RY動作 | OTHER | [5 empty] | 308 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | T/1DTR(B) |  |  | 0059 |  |  | 1-07-03 |  |  | 320(M-1B) CB ON/OFF |  | PPU-2 |  | abha | ELEM/D19_A1 | [8 empty] | 糠榔DS.320_CB | 320(#1DTR) CB | MTR | [5 empty] | 309 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0060 |  |  | 1-07-04 |  |  | 320(M-1B) PHA |  | PPU-2 |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.320_51A | #1DTR二次側(320) 51RY | MTR | [5 empty] | 310 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0061 |  |  | 1-07-05 |  |  | 320(M-1B) GDA |  | PPU-2 |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.320_GDA | 320開關箱IED RY GDA | OTHER | [5 empty] | 311 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0062 |  |  | 1-07-06 |  |  | 320(M-1B) 81A |  | PPU-2 |  |  | ELEM/D19_A1 | [8 empty] | 糠榔DS.320_81A | 320 #1DTR(B) 81RY動作 | OTHER | [5 empty] | 312 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2DTR |  | 0063 |  |  | 1-07-07 |  |  | 1760 CB ON/OFF |  | PPU-2 |  | aafb | ELEM/D19_A1 | [8 empty] | 糠榔DS.1760_CB | 1760(#2DTR) CB | MTR | [5 empty] | 313 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS |  |  | 2DTR | #2DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0064 |  |  | 1-08-00 |  |  | NO.2 DTR 87A |  | PPU-2 |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#2DTR_87A | #2DTR 87RY | MTR | [5 empty] | 314 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS |  |  | 2DTR | #2DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0065 |  |  | 1-08-01 |  |  | NO.2 DTR 96PA |  | PPU-2 |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | [5 empty] | 315 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS |  |  | 2DTR | #2DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0066 |  |  | 1-08-02 |  |  | NO.2 DTR 51ZA |  | PPU-2 |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | [5 empty] | 316 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1760 | #2DTR(1760) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0067 |  |  | 1-08-03 |  |  | NO.2 DTR PHA |  | PPU-2 |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.#2DTR_PHA | #2DTR 50/51 RY | OTHER | [5 empty] | 317 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1760 | #2DTR(1760) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 |  |  | 1-08-04 |  |  | NO.2 DTR GDA |  | PPU-2 |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.#2DTR_GDA | #2DTR 50N/51N RY | OTHER | [5 empty] | 318 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 |  |  | 1-08-05 |  |  | NO.2 DTR 86A |  | PPU-2 |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.#2DTR_86A | #2DTR 86(50/50N/51Z/87/96)RY | OTHER | [5 empty] | 319 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | 330 | #2DTR(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2Bus | T/2DTR |  |  | 0070 |  |  | 1-08-06 |  |  | 330(M2) CB ON/OFF |  | PPU-2 |  | acka | ELEM/D19_A1 | [8 empty] | 糠榔DS.330_CB | 330(#2DTR) CB | MTR | [5 empty] | 320 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | 330 | #2DTR(330) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0071 |  |  | 1-08-07 |  |  | 330(M2) PHA |  | PPU-2 |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.330_51A | #2DTR二次側(330) 51RY | MTR | [5 empty] | 321 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | 330 | #2DTR(330) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0072 |  |  | 1-09-00 |  |  | 330(M2) GDA |  | PPU-2 |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.330_GDA | 330開關箱IED RY GDA | OTHER | [5 empty] | 322 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | 330 | #2DTR(330) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0073 |  |  | 1-09-01 |  |  | 330(M2) 81A |  | PPU-2 |  |  | ELEM/D19_A1 | [8 empty] | 糠榔DS.330_81A | 330 #2DTR 81RY動作 | OTHER | [5 empty] | 323 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/3DTR |  | 0074 |  |  | 1-09-02 |  |  | 1770 CB ON/OFF |  | PPU-2 |  | aagb | ELEM/D19_A1 | [8 empty] | 糠榔DS.1770_CB | 1770(#3DTR) CB | MTR | [5 empty] | 324 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS |  |  | 3DTR | #3DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0075 |  |  | 1-09-03 |  |  | NO.3 DTR 87A |  | PPU-2 |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#3DTR_87A | #3DTR 87RY | MTR | [5 empty] | 325 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS |  |  | 3DTR | #3DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0076 |  |  | 1-09-04 |  |  | NO.3 DTR 96PA |  | PPU-2 |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#3DTR_96PA | #3DTR 機械保護動作 | MTR | [5 empty] | 326 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS |  |  | 3DTR | #3DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0077 |  |  | 1-09-05 |  |  | NO.3 DTR 51ZA |  | PPU-2 |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#3DTR_51ZA | #3DTR 51Z RY | MTR | [5 empty] | 327 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1770 | #3DTR(1770) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0078 |  |  | 1-09-06 |  |  | NO.3 DTR PHA |  | PPU-2 |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.#3DTR_PHA | #3DTR 50/51 RY | OTHER | [5 empty] | 328 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1770 | #3DTR(1770) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0079 |  |  | 1-09-07 |  |  | NO.3 DTR GDA |  | PPU-2 |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.#3DTR_GDA | #3DTR 50N/51N RY | OTHER | [5 empty] | 329 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0080 |  |  | 1-0A-00 |  |  | NO.3 DTR 86A |  | PPU-2 |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.#3DTR_86A | #3DTR 86(50/50N/51Z/87/96)RY | OTHER | [5 empty] | 330 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | 350 | #3DTR(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3Bus | T/3DTR |  |  | 0081 |  |  | 1-0A-01 |  |  | 350(M3) CB ON/OFF |  | PPU-2 |  | adda | ELEM/D19_A1 | [8 empty] | 糠榔DS.350_CB | 350(#3DTR) CB | MTR | [5 empty] | 331 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | 350 | #3DTR(350) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0082 |  |  | 1-0A-02 |  |  | 350(M3) PHA |  | PPU-2 |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.350_51A | #3DTR二次側(350) 51RY | MTR | [5 empty] | 332 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | 350 | #3DTR(350) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0083 |  |  | 1-0A-03 |  |  | 350(M3) GDA |  | PPU-2 |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.350_GDA | 350開關箱IED RY GDA | OTHER | [5 empty] | 333 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | 350 | #3DTR(350) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0084 |  |  | 1-0A-04 |  |  | 350(M3) 81A |  | PPU-2 |  |  | ELEM/D19_A1 | [8 empty] | 糠榔DS.350_81A | 350 #3DTR 81RY動作 | OTHER | [5 empty] | 334 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO21 | 槺21(JO21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/JO21/T1 |  |  | 0192 |  |  | 1-18-00 |  |  | 槺21(JO21) CB ON/OFF |  |  |  | aacb | B2/D19_D1 | [8 empty] | 糠榔DS.JO21_CB | JO21(11KV糠21線) CB | FEEDER | [5 empty] | 335 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | JO21 | 槺21(JO21) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0193 |  |  | 1-18-01 |  |  | 槺21(JO21) PHA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO21_PHA | 11KV糠21線(JO21) 相間RY | FEEDER | [5 empty] | 336 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO21 | 槺21(JO21) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0194 |  |  | 1-18-02 |  |  | 槺21(JO21) GDA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO21_GDA | 11KV糠21線(JO21) 接地RY | FEEDER | [5 empty] | 337 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO21 | 槺21(JO21) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0195 |  |  | 1-18-03 |  |  | 槺21(JO21) 81A |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO21_81A | 11KV糠21線(JO21) 81RY | OTHER | [5 empty] | 338 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO22 | 槺22(JO22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/JO22/T1 |  |  | 0196 |  |  | 1-18-04 |  |  | 槺22(JO22) CB ON/OFF |  |  |  | aaeb | B2/D19_D1 | [8 empty] | 糠榔DS.JO22_CB | JO22(11KV糠22線) CB | FEEDER | [5 empty] | 339 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | JO22 | 槺22(JO22) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0197 |  |  | 1-18-05 |  |  | 槺22(JO22) PHA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO22_PHA | 11KV糠22線(JO22) 相間RY | FEEDER | [5 empty] | 340 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO22 | 槺22(JO22) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0198 |  |  | 1-18-06 |  |  | 槺22(JO22) GDA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO22_GDA | 11KV糠22線(JO22) 接地RY | FEEDER | [5 empty] | 341 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO22 | 槺22(JO22) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0199 |  |  | 1-18-07 |  |  | 槺22(JO22) 81A |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO22_81A | 11KV糠22線(JO22) 81RY | OTHER | [5 empty] | 342 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO23 | 槺23(JO23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/JO23/T1 |  |  | 0200 |  |  | 1-19-00 |  |  | 槺23(JO23) CB ON/OFF |  |  |  | aafb | B2/D19_D1 | [8 empty] | 糠榔DS.JO23_CB | JO23(11KV糠23線) CB | FEEDER | [5 empty] | 343 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | JO23 | 槺23(JO23) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0201 |  |  | 1-19-01 |  |  | 槺23(JO23) PHA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO23_PHA | 11KV糠23線(JO23) 相間RY | FEEDER | [5 empty] | 344 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO23 | 槺23(JO23) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0202 |  |  | 1-19-02 |  |  | 槺23(JO23) GDA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO23_GDA | 11KV糠23線(JO23) 接地RY | FEEDER | [5 empty] | 345 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO23 | 槺23(JO23) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0203 |  |  | 1-19-03 |  |  | 槺23(JO23) 81A |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO23_81A | 11KV糠23線(JO23) 81RY | OTHER | [5 empty] | 346 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO24 | 槺24(JO24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/JO24/T1 |  |  | 0204 |  |  | 1-19-04 |  |  | 槺24(JO24) CB ON/OFF |  |  |  | aagb | B2/D19_D1 | [8 empty] | 糠榔DS.JO24_CB | JO24(11KV糠24線) CB | FEEDER | [5 empty] | 347 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | JO24 | 槺24(JO24) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0205 |  |  | 1-19-05 |  |  | 槺24(JO24) PHA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO24_PHA | 11KV糠24線(JO24) 相間RY | FEEDER | [5 empty] | 348 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO24 | 槺24(JO24) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0206 |  |  | 1-19-06 |  |  | 槺24(JO24) GDA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO24_GDA | 11KV糠24線(JO24) 接地RY | FEEDER | [5 empty] | 349 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO24 | 槺24(JO24) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0207 |  |  | 1-19-07 |  |  | 槺24(JO24) 81A |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO24_81A | 11KV糠24線(JO24) 81RY | OTHER | [5 empty] | 350 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO25 | 槺25(JO25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/JO25/T1 |  |  | 0208 |  |  | 1-1A-00 |  |  | 槺25(JO25) CB ON/OFF |  |  |  | aahb | B2/D19_D1 | [8 empty] | 糠榔DS.JO25_CB | JO25(11KV糠25線) CB | FEEDER | [5 empty] | 351 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | JO25 | 槺25(JO25) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0209 |  |  | 1-1A-01 |  |  | 槺25(JO25) PHA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO25_PHA | 11KV糠25線(JO25) 相間RY | FEEDER | [5 empty] | 352 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO25 | 槺25(JO25) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0210 |  |  | 1-1A-02 |  |  | 槺25(JO25) GDA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO25_GDA | 11KV糠25線(JO25) 接地RY | FEEDER | [5 empty] | 353 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO25 | 槺25(JO25) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0211 |  |  | 1-1A-03 |  |  | 槺25(JO25) 81A |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO25_81A | 11KV糠25線(JO25) 81RY | OTHER | [5 empty] | 354 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | 210 | #1SC(210) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | A/LBS210^C/1SC(A) |  |  | 0212 |  |  | 1-1A-04 |  |  | 210(SC-1) CB ON/OFF |  |  |  | aabb | B3/D19_A1 | [8 empty] | 糠榔DS.210_CB | 210(11KV #1SC) CB | SC | [5 empty] | 355 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0213 |  |  | 1-1A-05 |  |  | 210(SC-1) SCA |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.210_SCA | 11KV #1SC 51,51N RY | SC | [5 empty] | 356 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0214 |  |  | 1-1A-06 |  |  | 210(SC-1) UVA |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.210_OUVA | 11KV #1SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 357 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | 100 | TIE(100) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/1ABus | B/1BBus |  |  | 0215 |  |  | 1-1A-07 |  |  | 100(TIE-1A) CB ON/OFF |  |  |  | aaib | B3/D19_A1 | [8 empty] | 糠榔DS.100_CB | 100(TIE) CB | TIE | [5 empty] | 358 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 11 | 11kV | 100 | TIE(100) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0216 |  |  | 1-1B-00 |  |  | 100(TIE-1A) PHA |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.100_51A | 11KV TIE(100) 51RY | TIE | [5 empty] | 359 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | 100 | TIE(100) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0217 |  |  | 1-1B-01 |  |  | 100(TIE-1A) GDA |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.100_51NA | 11KV TIE(100) 51N RY | TIE | [5 empty] | 360 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO26 | 槺26(JO26) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/JO26/T1 |  |  | 0218 |  |  | 1-1B-02 |  |  | 槺26(JO26) CB ON/OFF |  |  |  | abfb | B2/D19_D1 | [8 empty] | 糠榔DS.JO26_CB | JO26(11KV糠26線) CB | FEEDER | [5 empty] | 361 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | JO26 | 槺26(JO26) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0219 |  |  | 1-1B-03 |  |  | 槺26(JO26) PHA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO26_PHA | 11KV糠26線(JO26) 相間RY | FEEDER | [5 empty] | 362 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO26 | 槺26(JO26) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0220 |  |  | 1-1B-04 |  |  | 槺26(JO26) GDA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO26_GDA | 11KV糠26線(JO26) 接地RY | FEEDER | [5 empty] | 363 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO26 | 槺26(JO26) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0221 |  |  | 1-1B-05 |  |  | 槺26(JO26) 81A |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO26_81A | 11KV糠26線(JO26) 81RY | OTHER | [5 empty] | 364 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO27 | 槺27(JO27) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/JO27/T1 |  |  | 0222 |  |  | 1-1B-06 |  |  | 槺27(JO27) CB ON/OFF |  |  |  | abdb | B2/D19_D1 | [8 empty] | 糠榔DS.JO27_CB | JO27(11KV糠27線) CB | FEEDER | [5 empty] | 365 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | JO27 | 槺27(JO27) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0223 |  |  | 1-1B-07 |  |  | 槺27(JO27) PHA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO27_PHA | 11KV糠27線(JO27) 相間RY | FEEDER | [5 empty] | 366 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO27 | 槺27(JO27) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0224 |  |  | 1-1C-00 |  |  | 槺27(JO27) GDA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO27_GDA | 11KV糠27線(JO27) 接地RY | FEEDER | [5 empty] | 367 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO27 | 槺27(JO27) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0225 |  |  | 1-1C-01 |  |  | 槺27(JO27) 81A |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO27_81A | 11KV糠27線(JO27) 81RY | OTHER | [5 empty] | 368 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO28 | 槺28(JO28) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/JO28/T1 |  |  | 0226 |  |  | 1-1C-02 |  |  | 槺28(JO28) CB ON/OFF |  |  |  | abcb | B2/D19_D1 | [8 empty] | 糠榔DS.JO28_CB | JO28(11KV糠28線) CB | FEEDER | [5 empty] | 369 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | JO28 | 槺28(JO28) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0227 |  |  | 1-1C-03 |  |  | 槺28(JO28) PHA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO28_PHA | 11KV糠28線(JO28) 相間RY | FEEDER | [5 empty] | 370 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO28 | 槺28(JO28) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0228 |  |  | 1-1C-04 |  |  | 槺28(JO28) GDA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO28_GDA | 11KV糠28線(JO28) 接地RY | FEEDER | [5 empty] | 371 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO28 | 槺28(JO28) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0229 |  |  | 1-1C-05 |  |  | 槺28(JO28) 81A |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO28_81A | 11KV糠28線(JO28) 81RY | OTHER | [5 empty] | 372 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO29 | 槺29(JO29) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/JO29/T1 |  |  | 0230 |  |  | 1-1C-06 |  |  | 槺29(JO29) CB ON/OFF |  |  |  | abbb | B2/D19_D1 | [8 empty] | 糠榔DS.JO29_CB | JO29(11KV糠29線) CB | FEEDER | [5 empty] | 373 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | JO29 | 槺29(JO29) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0231 |  |  | 1-1C-07 |  |  | 槺29(JO29) PHA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO29_PHA | 11KV糠29線(JO29) 相間RY | FEEDER | [5 empty] | 374 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO29 | 槺29(JO29) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0232 |  |  | 1-1D-00 |  |  | 槺29(JO29) GDA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO29_GDA | 11KV糠29線(JO29) 接地RY | FEEDER | [5 empty] | 375 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO29 | 槺29(JO29) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0233 |  |  | 1-1D-01 |  |  | 槺29(JO29) 81A |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO29_81A | 11KV糠29線(JO29) 81RY | OTHER | [5 empty] | 376 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO30 | 槺30(JO30) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/JO30/T1 |  |  | 0234 |  |  | 1-1D-02 |  |  | 槺30(JO30) CB ON/OFF |  |  |  | abab | B2/D19_D1 | [8 empty] | 糠榔DS.JO30_CB | JO30(11KV糠30線) CB | FEEDER | [5 empty] | 377 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | JO30 | 槺30(JO30) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0235 |  |  | 1-1D-03 |  |  | 槺30(JO30) PHA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO30_PHA | 11KV糠30線(JO30) 相間RY | FEEDER | [5 empty] | 378 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO30 | 槺30(JO30) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0236 |  |  | 1-1D-04 |  |  | 槺30(JO30) GDA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO30_GDA | 11KV糠30線(JO30) 接地RY | FEEDER | [5 empty] | 379 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO30 | 槺30(JO30) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0237 |  |  | 1-1D-05 |  |  | 槺30(JO30) 81A |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO30_81A | 11KV糠30線(JO30) 81RY | OTHER | [5 empty] | 380 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | 220 | #2SC(220) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | A/LBS220^C/2SC(A) |  |  | 0238 |  |  | 1-1D-06 |  |  | 220(SC-2) CB ON/OFF |  |  |  | abgb | B3/D19_A1 | [8 empty] | 糠榔DS.220_CB | 220(11KV #2SC) CB | SC | [5 empty] | 381 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0239 |  |  | 1-1D-07 |  |  | 220(SC-2) SCA |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.220_SCA | 11KV #2SC 51,51N RY | SC | [5 empty] | 382 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0240 |  |  | 1-1E-00 |  |  | 220(SC-2) UVA |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.220_OUVA | 11KV #2SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 383 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO61 | 槺61(JO61) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2Bus | L/JO61/T1 |  |  | 0241 |  |  | 1-1E-01 |  |  | 槺61(JO61) CB ON/OFF |  |  |  | acib | B2/D19_D1 | [8 empty] | 糠榔DS.JO61_CB | JO61(23KV糠61線) CB | FEEDER | [5 empty] | 384 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO61 | 槺61(JO61) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0242 |  |  | 1-1E-02 |  |  | 槺61(JO61) PHA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO61_PHA | 23KV糠61線(JO61) 相間RY | FEEDER | [5 empty] | 385 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO61 | 槺61(JO61) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0243 |  |  | 1-1E-03 |  |  | 槺61(JO61) GDA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO61_GDA | 23KV糠61線(JO61) 接地RY | FEEDER | [5 empty] | 386 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO61 | 槺61(JO61) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0244 |  |  | 1-1E-04 |  |  | 槺61(JO61) 81A |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO61_81A | 23KV糠61線(JO61) 81RY | OTHER | [5 empty] | 387 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO62 | 槺62(JO62) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2Bus | L/JO62/T1 |  |  | 0245 |  |  | 1-1E-05 |  |  | 槺62(JO62) CB ON/OFF |  |  |  | achb | B2/D19_D1 | [8 empty] | 糠榔DS.JO62_CB | JO62(23KV糠62線) CB | FEEDER | [5 empty] | 388 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO62 | 槺62(JO62) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0246 |  |  | 1-1E-06 |  |  | 槺62(JO62) PHA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO62_PHA | 23KV糠62線(JO62) 相間RY | FEEDER | [5 empty] | 389 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO62 | 槺62(JO62) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0247 |  |  | 1-1E-07 |  |  | 槺62(JO62) GDA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO62_GDA | 23KV糠62線(JO62) 接地RY | FEEDER | [5 empty] | 390 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO62 | 槺62(JO62) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0248 |  |  | 1-1F-00 |  |  | 槺62(JO62) 81A |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO62_81A | 23KV糠62線(JO62) 81RY | OTHER | [5 empty] | 391 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO63 | 槺63(JO63) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2Bus | L/JO63/T1 |  |  | 0249 |  |  | 1-1F-01 |  |  | 槺63(JO63) CB ON/OFF |  |  |  | acgb | B2/D19_D1 | [8 empty] | 糠榔DS.JO63_CB | JO63(23KV糠63線) CB | FEEDER | [5 empty] | 392 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO63 | 槺63(JO63) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0250 |  |  | 1-1F-02 |  |  | 槺63(JO63) PHA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO63_PHA | 23KV糠63線(JO63) 相間RY | FEEDER | [5 empty] | 393 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO63 | 槺63(JO63) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0251 |  |  | 1-1F-03 |  |  | 槺63(JO63) GDA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO63_GDA | 23KV糠63線(JO63) 接地RY | FEEDER | [5 empty] | 394 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO63 | 槺63(JO63) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0252 |  |  | 1-1F-04 |  |  | 槺63(JO63) 81A |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO63_81A | 23KV糠63線(JO63) 81RY | OTHER | [5 empty] | 395 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO64 | 槺64(JO64) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2Bus | L/JO64/T1 |  |  | 0253 |  |  | 1-1F-05 |  |  | 槺64(JO64) CB ON/OFF |  |  |  | acfb | B2/D19_D1 | [8 empty] | 糠榔DS.JO64_CB | JO64(23KV糠64線) CB | FEEDER | [5 empty] | 396 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO64 | 槺64(JO64) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0254 |  |  | 1-1F-06 |  |  | 槺64(JO64) PHA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO64_PHA | 23KV糠64線(JO64) 相間RY | FEEDER | [5 empty] | 397 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO64 | 槺64(JO64) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0255 |  |  | 1-1F-07 |  |  | 槺64(JO64) GDA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO64_GDA | 23KV糠64線(JO64) 接地RY | FEEDER | [5 empty] | 398 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO64 | 槺64(JO64) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0256 |  |  | 2-00-00 |  |  | 槺64(JO64) 81A |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO64_81A | 23KV糠64線(JO64) 81RY | OTHER | [5 empty] | 399 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO65 | 槺65(JO65) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2Bus | L/JO65/T1 |  |  | 0257 |  |  | 2-00-01 |  |  | 槺65(JO65) CB ON/OFF |  |  |  | aceb | B2/D19_D1 | [8 empty] | 糠榔DS.JO65_CB | JO65(23KV糠65線) CB | FEEDER | [5 empty] | 400 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO65 | 槺65(JO65) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0258 |  |  | 2-00-02 |  |  | 槺65(JO65) PHA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO65_PHA | 23KV糠65線(JO65) 相間RY | FEEDER | [5 empty] | 401 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO65 | 槺65(JO65) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0259 |  |  | 2-00-03 |  |  | 槺65(JO65) GDA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO65_GDA | 23KV糠65線(JO65) 接地RY | FEEDER | [5 empty] | 402 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO65 | 槺65(JO65) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0260 |  |  | 2-00-04 |  |  | 槺65(JO65) 81A |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO65_81A | 23KV糠65線(JO65) 81RY | OTHER | [5 empty] | 403 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO66 | 槺66(JO66) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2Bus | L/JO66/T1 |  |  | 0261 |  |  | 2-00-05 |  |  | 槺66(JO66) CB ON/OFF |  |  |  | acdb | B2/D19_D1 | [8 empty] | 糠榔DS.JO66_CB | JO66(23KV糠66線) CB | FEEDER | [5 empty] | 404 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO66 | 槺66(JO66) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0262 |  |  | 2-00-06 |  |  | 槺66(JO66) PHA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO66_PHA | 23KV糠66線(JO66) 相間RY | FEEDER | [5 empty] | 405 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO66 | 槺66(JO66) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0263 |  |  | 2-00-07 |  |  | 槺66(JO66) GDA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO66_GDA | 23KV糠66線(JO66) 接地RY | FEEDER | [5 empty] | 406 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO66 | 槺66(JO66) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0264 |  |  | 2-01-00 |  |  | 槺66(JO66) 81A |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO66_81A | 23KV糠66線(JO66) 81RY | OTHER | [5 empty] | 407 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO67 | 槺67(JO67) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2Bus | L/JO67/T1 |  |  | 0265 |  |  | 2-01-01 |  |  | 槺67(JO67) CB ON/OFF |  |  |  | accb | B2/D19_D1 | [8 empty] | 糠榔DS.JO67_CB | JO67(23KV糠67線) CB | FEEDER | [5 empty] | 408 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO67 | 槺67(JO67) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0266 |  |  | 2-01-02 |  |  | 槺67(JO67) PHA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO67_PHA | 23KV糠67線(JO67) 相間RY | FEEDER | [5 empty] | 409 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO67 | 槺67(JO67) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0267 |  |  | 2-01-03 |  |  | 槺67(JO67) GDA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO67_GDA | 23KV糠67線(JO67) 接地RY | FEEDER | [5 empty] | 410 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO67 | 槺67(JO67) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0268 |  |  | 2-01-04 |  |  | 槺67(JO67) 81A |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO67_81A | 23KV糠67線(JO67) 81RY | OTHER | [5 empty] | 411 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO68 | 槺68(JO68) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2Bus | L/JO68/T1 |  |  | 0269 |  |  | 2-01-05 |  |  | 槺68(JO68) CB ON/OFF |  |  |  | acbb | B2/D19_D1 | [8 empty] | 糠榔DS.JO68_CB | JO68(23KV糠68線) CB | FEEDER | [5 empty] | 412 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO68 | 槺68(JO68) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0270 |  |  | 2-01-06 |  |  | 槺68(JO68) PHA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO68_PHA | 23KV糠68線(JO68) 相間RY | FEEDER | [5 empty] | 413 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO68 | 槺68(JO68) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0271 |  |  | 2-01-07 |  |  | 槺68(JO68) GDA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO68_GDA | 23KV糠68線(JO68) 接地RY | FEEDER | [5 empty] | 414 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO68 | 槺68(JO68) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0272 |  |  | 2-02-00 |  |  | 槺68(JO68) 81A |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO68_81A | 23KV糠68線(JO68) 81RY | OTHER | [5 empty] | 415 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | 390 | #1SSTR(390) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2Bus | T/1SSTR |  |  | 0273 |  |  | 2-02-01 |  |  | #1 SSTR CB ON/OFF |  |  |  | aclb | B3/D19_A1 | [8 empty] | 糠榔DS.390_CB | 390(#1SSTR) CB | OTHER | [5 empty] | 416 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | 390 | #1SSTR(390) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0274 |  |  | 2-02-02 |  |  | #1 SSTR PHA |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.#1SSTR_51A | #1SSTR 51RY | OTHER | [5 empty] | 417 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | 390 | #1SSTR(390) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0275 |  |  | 2-02-03 |  |  | #1 SSTR GDA |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | [5 empty] | 418 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | 230 | #3SC(230) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2Bus | C/3SC |  |  | 0276 |  |  | 2-02-04 |  |  | 230(SC-3) CB ON/OFF |  |  |  | acmb | B3/D19_A1 | [8 empty] | 糠榔DS.230_CB | 230(23KV #3SC) CB | SC | [5 empty] | 419 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | 230 | #3SC(230) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0277 |  |  | 2-02-05 |  |  | 230(SC-3) SCA |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.230_SCA | 23KV #3SC 51,51N RY | SC | [5 empty] | 420 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | 230 | #3SC(230) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0278 |  |  | 2-02-06 |  |  | 230(SC-3) UVA |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.230_OUVA | 23KV #3SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 421 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | 240 | #4SC(240) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2Bus | C/4SC |  |  | 0279 |  |  | 2-02-07 |  |  | 240(SC-4) CB ON/OFF |  |  |  | acab | B3/D19_A1 | [8 empty] | 糠榔DS.240_CB | 240(23KV #4SC) CB | SC | [5 empty] | 422 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | 240 | #4SC(240) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0280 |  |  | 2-03-00 |  |  | 240(SC-4) SCA |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.240_SCA | 23KV #4SC 51,51N RY | SC | [5 empty] | 423 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | 240 | #4SC(240) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0281 |  |  | 2-03-01 |  |  | 240(SC-4) UVA |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.240_OUVA | 23KV #4SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 424 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO71 | 槺71(JO71) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/JO71/T1 |  |  | 0282 |  |  | 2-03-02 |  |  | 槺71(JO71) CB ON/OFF |  |  |  | adfb | B2/D19_D1 | [8 empty] | 糠榔DS.JO71_CB | JO71(23KV糠71線) CB | FEEDER | [5 empty] | 425 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO71 | 槺71(JO71) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0283 |  |  | 2-03-03 |  |  | 槺71(JO71) PHA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO71_PHA | 23KV糠71線(JO71) 相間RY | FEEDER | [5 empty] | 426 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO71 | 槺71(JO71) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0284 |  |  | 2-03-04 |  |  | 槺71(JO71) GDA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO71_GDA | 23KV糠71線(JO71) 接地RY | FEEDER | [5 empty] | 427 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO71 | 槺71(JO71) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0285 |  |  | 2-03-05 |  |  | 槺71(JO71) 81A |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO71_81A | 23KV糠71線(JO71) 81RY | OTHER | [5 empty] | 428 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO72 | 槺72(JO72) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/JO72/T1 |  |  | 0286 |  |  | 2-03-06 |  |  | 槺72(JO72) CB ON/OFF |  |  |  | adgb | B2/D19_D1 | [8 empty] | 糠榔DS.JO72_CB | JO72(23KV糠72線) CB | FEEDER | [5 empty] | 429 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO72 | 槺72(JO72) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0287 |  |  | 2-03-07 |  |  | 槺72(JO72) PHA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO72_PHA | 23KV糠72線(JO72) 相間RY | FEEDER | [5 empty] | 430 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO72 | 槺72(JO72) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0288 |  |  | 2-04-00 |  |  | 槺72(JO72) GDA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO72_GDA | 23KV糠72線(JO72) 接地RY | FEEDER | [5 empty] | 431 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO72 | 槺72(JO72) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0289 |  |  | 2-04-01 |  |  | 槺72(JO72) 81A |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO72_81A | 23KV糠72線(JO72) 81RY | OTHER | [5 empty] | 432 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO73 | 槺73(JO73) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/JO73/T1 |  |  | 0290 |  |  | 2-04-02 |  |  | 槺73(JO73) CB ON/OFF |  |  |  | adhb | B2/D19_D1 | [8 empty] | 糠榔DS.JO73_CB | JO73(23KV糠73線) CB | FEEDER | [5 empty] | 433 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO73 | 槺73(JO73) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0291 |  |  | 2-04-03 |  |  | 槺73(JO73) PHA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO73_PHA | 23KV糠73線(JO73) 相間RY | FEEDER | [5 empty] | 434 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO73 | 槺73(JO73) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0292 |  |  | 2-04-04 |  |  | 槺73(JO73) GDA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO73_GDA | 23KV糠73線(JO73) 接地RY | FEEDER | [5 empty] | 435 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO73 | 槺73(JO73) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0293 |  |  | 2-04-05 |  |  | 槺73(JO73) 81A |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO73_81A | 23KV糠73線(JO73) 81RY | OTHER | [5 empty] | 436 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO74 | 槺74(JO74) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/JO74/T1 |  |  | 0294 |  |  | 2-04-06 |  |  | 槺74(JO74) CB ON/OFF |  |  |  | adib | B2/D19_D1 | [8 empty] | 糠榔DS.JO74_CB | JO74(23KV糠74線) CB | FEEDER | [5 empty] | 437 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO74 | 槺74(JO74) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0295 |  |  | 2-04-07 |  |  | 槺74(JO74) PHA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO74_PHA | 23KV糠74線(JO74) 相間RY | FEEDER | [5 empty] | 438 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO74 | 槺74(JO74) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0296 |  |  | 2-05-00 |  |  | 槺74(JO74) GDA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO74_GDA | 23KV糠74線(JO74) 接地RY | FEEDER | [5 empty] | 439 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO74 | 槺74(JO74) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0297 |  |  | 2-05-01 |  |  | 槺74(JO74) 81A |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO74_81A | 23KV糠74線(JO74) 81RY | OTHER | [5 empty] | 440 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO75 | 槺75(JO75) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/JO75/T1 |  |  | 0298 |  |  | 2-05-02 |  |  | 槺75(JO75) CB ON/OFF |  |  |  | adjb | B2/D19_D1 | [8 empty] | 糠榔DS.JO75_CB | JO75(23KV糠75線) CB | FEEDER | [5 empty] | 441 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO75 | 槺75(JO75) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0299 |  |  | 2-05-03 |  |  | 槺75(JO75) PHA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO75_PHA | 23KV糠75線(JO75) 相間RY | FEEDER | [5 empty] | 442 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO75 | 槺75(JO75) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0300 |  |  | 2-05-04 |  |  | 槺75(JO75) GDA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO75_GDA | 23KV糠75線(JO75) 接地RY | FEEDER | [5 empty] | 443 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO75 | 槺75(JO75) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0301 |  |  | 2-05-05 |  |  | 槺75(JO75) 81A |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO75_81A | 23KV糠75線(JO75) 81RY | OTHER | [5 empty] | 444 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO76 | 槺76(JO76) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/JO76/T1 |  |  | 0302 |  |  | 2-05-06 |  |  | 槺76(JO76) CB ON/OFF |  |  |  | adkb | B2/D19_D1 | [8 empty] | 糠榔DS.JO76_CB | JO76(23KV糠76線) CB | FEEDER | [5 empty] | 445 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO76 | 槺76(JO76) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0303 |  |  | 2-05-07 |  |  | 槺76(JO76) PHA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO76_PHA | 23KV糠76線(JO76) 相間RY | FEEDER | [5 empty] | 446 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO76 | 槺76(JO76) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0304 |  |  | 2-06-00 |  |  | 槺76(JO76) GDA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO76_GDA | 23KV糠76線(JO76) 接地RY | FEEDER | [5 empty] | 447 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO76 | 槺76(JO76) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0305 |  |  | 2-06-01 |  |  | 槺76(JO76) 81A |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO76_81A | 23KV糠76線(JO76) 81RY | OTHER | [5 empty] | 448 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO77 | 槺77(JO77) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/JO77/T1 |  |  | 0306 |  |  | 2-06-02 |  |  | 槺77(JO77) CB ON/OFF |  |  |  | adlb | B2/D19_D1 | [8 empty] | 糠榔DS.JO77_CB | JO77(23KV糠77線) CB | FEEDER | [5 empty] | 449 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO77 | 槺77(JO77) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0307 |  |  | 2-06-03 |  |  | 槺77(JO77) PHA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO77_PHA | 23KV糠77線(JO77) 相間RY | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO77 | 槺77(JO77) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0308 |  |  | 2-06-04 |  |  | 槺77(JO77) GDA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO77_GDA | 23KV糠77線(JO77) 接地RY | FEEDER | [5 empty] | 451 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO77 | 槺77(JO77) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0309 |  |  | 2-06-05 |  |  | 槺77(JO77) 81A |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO77_81A | 23KV糠77線(JO77) 81RY | OTHER | [5 empty] | 452 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO78 | 槺78(JO78) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/JO78/T1 |  |  | 0310 |  |  | 2-06-06 |  |  | 槺78(JO78) CB ON/OFF |  |  |  | admb | B2/D19_D1 | [8 empty] | 糠榔DS.JO78_CB | JO78(23KV糠78線) CB | FEEDER | [5 empty] | 453 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO78 | 槺78(JO78) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0311 |  |  | 2-06-07 |  |  | 槺78(JO78) PHA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO78_PHA | 23KV糠78線(JO78) 相間RY | FEEDER | [5 empty] | 454 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO78 | 槺78(JO78) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0312 |  |  | 2-07-00 |  |  | 槺78(JO78) GDA |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO78_GDA | 23KV糠78線(JO78) 接地RY | FEEDER | [5 empty] | 455 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO78 | 槺78(JO78) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0313 |  |  | 2-07-01 |  |  | 槺78(JO78) 81A |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO78_81A | 23KV糠78線(JO78) 81RY | OTHER | [5 empty] | 456 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | 250 | #5SC(250) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3Bus | C/5SC |  |  | 0314 |  |  | 2-07-02 |  |  | 250(SC-5) CB ON/OFF |  |  |  | adbb | B3/D19_A1 | [8 empty] | 糠榔DS.250_CB | 250(23KV #5SC) CB | SC | [5 empty] | 457 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | 250 | #5SC(250) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0315 |  |  | 2-07-03 |  |  | 250(SC-5) SCA |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.250_SCA | 23KV #5SC 51,51N RY | SC | [5 empty] | 458 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | 250 | #5SC(250) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0316 |  |  | 2-07-04 |  |  | 250(SC-5) UVA |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.250_OUVA | 23KV #5SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 459 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | 260 | #6SC(260) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3Bus | C/6SC |  |  | 0317 |  |  | 2-07-05 |  |  | 260(SC-6) CB ON/OFF |  |  |  | adnb | B3/D19_A1 | [8 empty] | 糠榔DS.260_CB | 260(23KV #6SC) CB | SC | [5 empty] | 460 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | 260 | #6SC(260) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0318 |  |  | 2-07-06 |  |  | 260(SC-6) SCA |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.260_SCA | 23KV #6SC 51,51N RY | SC | [5 empty] | 461 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | 260 | #6SC(260) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0319 |  |  | 2-07-07 |  |  | 260(SC-6) UVA |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.260_OUVA | 23KV #6SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 462 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | 200 | TIE(200) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/3Bus | B/2Bus |  |  | 0320 |  |  | 2-08-00 |  |  | 200(TIE-3) CB ON/OFF |  |  |  | adab | B3/D19_A1 | [8 empty] | 糠榔DS.200_CB | 200(TIE) CB | TIE | [5 empty] | 463 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 22 | 22kV | 200 | TIE(200) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0321 |  |  | 2-08-01 |  |  | 200(TIE-3) PHA |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.200_51A | 23KV TIE(200) 51RY | TIE | [5 empty] | 464 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | 200 | TIE(200) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0322 |  |  | 2-08-02 |  |  | 200(TIE-3) GDA |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.200_51NA | 23KV TIE(200) 51N RY | TIE | [5 empty] | 465 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | 490 | #2SSTR(490) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3Bus | T/2SSTR |  |  | 0323 |  |  | 2-08-03 |  |  | #2 SSTR CB ON/OFF |  |  |  | adcb | B3/D19_A1 | [8 empty] | 糠榔DS.490_CB | 490(#2SSTR) CB | OTHER | [5 empty] | 466 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | 490 | #2SSTR(490) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0324 |  |  | 2-08-04 |  |  | #2 SSTR PHA |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.#2SSTR_51A | #2SSTR 51RY | OTHER | [5 empty] | 467 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | 490 | #2SSTR(490) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0325 |  |  | 2-08-05 |  |  | #2 SSTR GDA |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | [5 empty] | 468 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | ComPoint |  |  | 25TA |  |  | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0326 |  |  | 2-08-06 |  |  | 25TA 同步校核裝置超時 |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | [5 empty] | 469 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | ComPoint |  |  | 25PFA |  |  | Status | 同步校核電驛電源 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0327 |  |  | 2-08-07 |  |  | 25PFA同步校核裝置電源 |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER | [5 empty] | 470 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0512 |  |  | 1-30-00 |  |  | TEST CB ON/OFF |  |  |  |  | ELEM/ALL | [8 empty] | 糠榔DS.TEST_CB | TEST CB | OTHER | [5 empty] | 471 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | RTU | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0513 |  |  | 1-30-01 |  |  | L/R STATUS ON/OFF |  |  |  |  | ELEM/D19_A1 | [8 empty] | 糠榔DS.RTU_S/L | RTU SUPY/LOCAL | OTHER | [5 empty] | 472 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
D19 | 槺榔DS | 161 | 161kV | 1510 | 太鐵～槺榔一路(1510) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0514 |  |  | 1-30-02 |  |  | 太鐵槺榔一路1510 87S |  |  |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.1510_87UL | 太鐵糠榔一路(1510) 87RY U/L | LINE161 | [5 empty] | 473 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 161 | 161kV | 1510 | 太鐵～槺榔一路(1510) |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0515 |  |  | 1-30-03 |  |  | 太鐵槺榔一路1510 79S |  |  |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.1510_79UL | 太鐵糠榔一路(1510) 79RY U/L | LINE161 | [5 empty] | 474 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 161 | 161kV | 1520 | 太鐵～槺榔二路(1520) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0516 |  |  | 1-30-04 |  |  | 太鐵槺榔二路1520 87S |  |  |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.1520_87UL | 太鐵糠榔二路(1520) 87RY U/L | LINE161 | [5 empty] | 475 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 161 | 161kV | 1520 | 太鐵～槺榔二路(1520) |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0517 |  |  | 1-30-05 |  |  | 太鐵槺榔二路1520 79S |  |  |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.1520_79UL | 太鐵糠榔二路(1520) 79RY U/L | LINE161 | [5 empty] | 476 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 161 | 161kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0530 |  |  | 1-31-02 |  |  | 161kV #1BUS 87Ry U/L |  |  |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | [5 empty] | 477 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 161 | 161kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0531 |  |  | 1-31-03 |  |  | 161kV #2BUS 87Ry U/L |  |  |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | [5 empty] | 478 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0532 |  |  | 1-31-04 |  |  | 1500SA |  |  |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.1500_50SA | 161KV TIE(1500) 50RY 測試/正常 | TIE | [5 empty] | 479 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Test | Test | 1 |  |  | TEST/NORMAL | NORMAL
D19 | 槺榔DS |  |  | 1DTR | #1DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0533 |  |  | 1-31-05 |  |  | NO.1 DTR 87S |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#1DTR_87UL | #1DTR 87RY U/L | MTR | [5 empty] | 480 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS |  |  | 1DTR | #1DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0534 |  |  | 1-31-06 |  |  | NO.1 DTR 51S |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#1DTR_50/51NUL | #1DTR 50/50N/51/51N RY U/L | OTHER | [5 empty] | 481 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Normal | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS |  |  | 1DTR | #1DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0535 |  |  | 1-31-07 |  |  | NO.1 DTR 51ZS |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#1DTR_51ZUL | #1DTR 51Z RY U/L | OTHER | [5 empty] | 482 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Normal | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS |  |  | 1DTR(A) | #1DTR(A) |  | SupLocal |  | B2,B3 | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0536 |  |  | 1-31-08 |  |  | NO.1A DTR OLTC S/L |  |  |  | c | B1/D19_A1 | [8 empty] | 糠榔DS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | [5 empty] | 483 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D19 | 槺榔DS |  |  | 1DTR(A) | #1DTR(A) |  | Tap Chan |  | B2,B3,Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0537 |  |  | 1-31-09 |  |  | NO.1A DTR OLTC A/M |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | [5 empty] | 484 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D19 | 槺榔DS |  |  | 1DTR(B) | #1DTR(B) |  | SupLocal |  | B2,B3 | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0538 |  |  | 1-31-10 |  |  | NO.1B DTR OLTC S/L |  |  |  | b | B1/D19_A1 | [8 empty] | 糠榔DS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | [5 empty] | 485 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D19 | 槺榔DS |  |  | 1DTR(B) | #1DTR(B) |  | Tap Chan |  | B2,B3,Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0539 |  |  | 1-31-11 |  |  | NO.1B DTR OLTC A/M |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | [5 empty] | 486 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D19 | 槺榔DS |  |  | 1DTR | #1DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0540 |  |  | 1-31-12 |  |  | NO.1 DTR 96B1 |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | [5 empty] | 487 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS |  |  | 1DTR | #1DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0541 |  |  | 1-31-13 |  |  | NO.1 DTR 96B2 |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | [5 empty] | 488 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS |  |  | 1DTR | #1DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0542 |  |  | 1-31-14 |  |  | NO.1 DTR 96D |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#1DTR_96D | #1DTR 96D RY | MTR | [5 empty] | 489 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS |  |  | 1DTR | #1DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0543 |  |  | 1-31-15 |  |  | NO.1 DTR 96P |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#1DTR_96P | #1DTR 96P RY | MTR | [5 empty] | 490 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS |  |  | 1DTR | #1DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0544 |  |  | 1-32-00 |  |  | NO.1 DTR 63Q |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#1DTR_63Q | #1DTR 63Q RY | MTR | [5 empty] | 491 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS |  |  | 1DTR | #1DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0545 |  |  | 1-32-01 |  |  | NO.1 DTR TRA |  |  |  | a | B1/D19_A1 | [8 empty] | 糠榔DS.#1DTR_TRA | #1DTR 重故障 | MTR | [5 empty] | 492 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D19 | 槺榔DS |  |  | 1DTR | #1DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0546 |  |  | 1-32-02 |  |  | NO.1 DTR TRF |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#1DTR_TRF | #1DTR 輕故障 | MTR | [5 empty] | 493 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D19 | 槺榔DS |  |  | 2DTR | #2DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0547 |  |  | 1-32-03 |  |  | NO.2 DTR 87S |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#2DTR_87UL | #2DTR 87RY U/L | MTR | [5 empty] | 494 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS |  |  | 2DTR | #2DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0548 |  |  | 1-32-04 |  |  | NO.2 DTR 51S |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#2DTR_50/51NUL | #2DTR 50/50N/51/51N RY U/L | OTHER | [5 empty] | 495 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Normal | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS |  |  | 2DTR | #2DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0549 |  |  | 1-32-05 |  |  | NO.2 DTR 51ZS |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#2DTR_51ZUL | #2DTR 51Z RY U/L | OTHER | [5 empty] | 496 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Normal | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS |  |  | 2DTR | #2DTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0550 |  |  | 1-32-06 |  |  | NO.2 DTR OLTC S/L |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#2DTR_S/L | #2DTR OLTC S/L | MTR | [5 empty] | 497 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D19 | 槺榔DS |  |  | 2DTR | #2DTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0551 |  |  | 1-32-07 |  |  | NO.2 DTR OLTC A/M |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#2DTR_A/M | #2DTR OLTC A/M | MTR | [5 empty] | 498 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D19 | 槺榔DS |  |  | 2DTR | #2DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0552 |  |  | 1-32-08 |  |  | NO.2 DTR 96B1 |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | [5 empty] | 499 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS |  |  | 2DTR | #2DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0553 |  |  | 1-32-09 |  |  | NO.2 DTR 96B2 |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | [5 empty] | 500 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS |  |  | 2DTR | #2DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0554 |  |  | 1-32-10 |  |  | NO.2 DTR 96D |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#2DTR_96D | #2DTR 96D RY | MTR | [5 empty] | 501 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS |  |  | 2DTR | #2DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0555 |  |  | 1-32-11 |  |  | NO.2 DTR 96P |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#2DTR_96P | #2DTR 96P RY | MTR | [5 empty] | 502 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS |  |  | 2DTR | #2DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0556 |  |  | 1-32-12 |  |  | NO.2 DTR 63Q |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#2DTR_63Q | #2DTR 63Q RY | MTR | [5 empty] | 503 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS |  |  | 2DTR | #2DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR |  |  |  |  | 0557 |  |  | 1-32-13 |  |  | NO.2 DTR TRA |  |  |  | a | B1/D19_A1 | [8 empty] | 糠榔DS.#2DTR_TRA | #2DTR 重故障 | MTR | [5 empty] | 504 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D19 | 槺榔DS |  |  | 2DTR | #2DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0558 |  |  | 1-32-14 |  |  | NO.2 DTR TRF |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#2DTR_TRF | #2DTR 輕故障 | MTR | [5 empty] | 505 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D19 | 槺榔DS |  |  | 3DTR | #3DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0559 |  |  | 1-32-15 |  |  | NO.3 DTR 87S |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#3DTR_87UL | #3DTR 87RY U/L | MTR | [5 empty] | 506 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS |  |  | 3DTR | #3DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0560 |  |  | 1-33-00 |  |  | NO.3 DTR 51S |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#3DTR_50/51NUL | #3DTR 50/50N/51/51N RY U/L | OTHER | [5 empty] | 507 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Normal | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS |  |  | 3DTR | #3DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0561 |  |  | 1-33-01 |  |  | NO.3 DTR 51ZS |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#3DTR_51ZUL | #3DTR 51Z RY U/L | OTHER | [5 empty] | 508 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Normal | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS |  |  | 3DTR | #3DTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0562 |  |  | 1-33-02 |  |  | NO.3 DTR OLTC S/L |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#3DTR_S/L | #3DTR OLTC S/L | MTR | [5 empty] | 509 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D19 | 槺榔DS |  |  | 3DTR | #3DTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0563 |  |  | 1-33-03 |  |  | NO.3 DTR OLTC A/M |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#3DTR_A/M | #3DTR OLTC A/M | MTR | [5 empty] | 510 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D19 | 槺榔DS |  |  | 3DTR | #3DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0564 |  |  | 1-33-04 |  |  | NO.3 DTR 96B1 |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#3DTR_96B1 | #3DTR 96B1 RY | MTR | [5 empty] | 511 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS |  |  | 3DTR | #3DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0565 |  |  | 1-33-05 |  |  | NO.3 DTR 96B2 |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#3DTR_96B2 | #3DTR 96B2 RY | MTR | [5 empty] | 512 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS |  |  | 3DTR | #3DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0566 |  |  | 1-33-06 |  |  | NO.3 DTR 96D |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#3DTR_96D | #3DTR 96D RY | MTR | [5 empty] | 513 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS |  |  | 3DTR | #3DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0567 |  |  | 1-33-07 |  |  | NO.3 DTR 96P |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#3DTR_96P | #3DTR 96P RY | MTR | [5 empty] | 514 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS |  |  | 3DTR | #3DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0568 |  |  | 1-33-08 |  |  | NO.3 DTR 63Q |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#3DTR_63Q | #3DTR 63Q RY | MTR | [5 empty] | 515 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS |  |  | 3DTR | #3DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR |  |  |  |  | 0569 |  |  | 1-33-09 |  |  | NO.3 DTR TRA |  |  |  | a | B1/D19_A1 | [8 empty] | 糠榔DS.#3DTR_TRA | #3DTR 重故障 | MTR | [5 empty] | 516 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D19 | 槺榔DS |  |  | 3DTR | #3DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0570 |  |  | 1-33-10 |  |  | NO.3 DTR TRF |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#3DTR_TRF | #3DTR 輕故障 | MTR | [5 empty] | 517 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | ComPoint |  |  | OLTC_A |  |  | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0571 |  |  | 1-33-11 |  |  | OLTC 15分鐘內連動3次警報 OLTCA |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | [5 empty] | 518 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1510 | 太鐵～槺榔一路(1510) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0576 |  |  | 1-34-00 |  |  | 1510 87CFA 通訊 故障 |  |  |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.1510_87CFA | 太鐵糠榔一路(1510)87RY通訊故障 | OTHER | [5 empty] | 519 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1510 | 太鐵～槺榔一路(1510) |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0577 |  |  | 1-34-01 |  |  | 1510 RYFA 電驛 故障 |  |  |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.1510_RYFA | 太鐵糠榔一路(1510)數位電驛故障 | OTHER | [5 empty] | 520 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1520 | 太鐵～槺榔二路(1520) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0578 |  |  | 1-34-02 |  |  | 1520 87CFA 通訊 故障 |  |  |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.1520_87CFA | 太鐵糠榔二路(1520)87RY通訊故障 | OTHER | [5 empty] | 521 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1520 | 太鐵～槺榔二路(1520) |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0579 |  |  | 1-34-03 |  |  | 1520 RYFA 電驛 故障 |  |  |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.1520_RYFA | 太鐵糠榔二路(1520)數位電驛故障 | OTHER | [5 empty] | 522 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | ComPoint |  |  | 12B_CTFA | 待新增!!__BUS_87CTFA | Element | Status | #1#2 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0592 |  |  | 1-35-00 |  |  | 161KV BUS RY CT故障 CTFA |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.161KV_BUS_CTFA | 161KV BUS CT 回路故障 | OTHER | [5 empty] | 523 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | ComPoint |  |  | BUS_RYFA |  |  | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0593 |  |  | 1-35-01 |  |  | 161KV BUS RY 故障 87BF |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | [5 empty] | 524 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D19 | 槺榔DS |  |  | 1DTR | #1DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0594 |  |  | 1-35-02 |  |  | NO.1 DTR RY故障 RYFA |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#1DTR_RYFA | #1DTR 數位電驛故障 | OTHER | [5 empty] | 525 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D19 | 槺榔DS |  |  | 2DTR | #2DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0595 |  |  | 1-35-03 |  |  | NO.2 DTR RY故障 RYFA |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#2DTR_RYFA | #2DTR 數位電驛故障 | OTHER | [5 empty] | 526 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D19 | 槺榔DS |  |  | 3DTR | #3DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0596 |  |  | 1-35-04 |  |  | NO.3 DTR RY故障 RYFA |  |  |  |  | B1/D19_A1 | [8 empty] | 糠榔DS.#3DTR_RYFA | #3DTR 數位電驛故障 | OTHER | [5 empty] | 527 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0608 | 609 |  | 1-36-00 | 1-36-01 |  | TIE(1501) DS-AS |  |  |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.1501_DS | 1501(TIE) DS | TIE | [5 empty] | 528 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D19 | 槺榔DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0610 | 611 |  | 1-36-02 | 1-36-03 |  | TIE(1502) DS-AS |  |  |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.1502_DS | 1502(TIE) DS | TIE | [5 empty] | 529 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D19 | 槺榔DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | ADD | Status | E1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0608 | 609 |  | 1-36-00 | 1-36-01 |  | TIE(1501) DS-AS |  |  |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.1501_DS | 1501(TIE) DS | TIE | [5 empty] | 528 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D19 | 槺榔DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | ADD | Status | E2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0610 | 611 |  | 1-36-02 | 1-36-03 |  | TIE(1502) DS-AS |  |  |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.1502_DS | 1502(TIE) DS | TIE | [5 empty] | 529 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D19 | 槺榔DS | 161 | 161kV | 1510 | 太鐵～槺榔一路(1510) |  | DS1 | 1511 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0612 | 613 |  | 1-36-04 | 1-36-05 |  | 太鐵槺榔一路1511 DS-AS |  |  |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.1511_DS | 1511(太鐵糠榔一路) DS | LINE161 | [5 empty] | 530 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D19 | 槺榔DS | 161 | 161kV | 1510 | 太鐵～槺榔一路(1510) |  | DS2 | 1512 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0614 | 615 |  | 1-36-06 | 1-36-07 |  | 太鐵槺榔一路1512 DS-AS |  |  |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.1512_DS | 1512(太鐵糠榔一路) DS | LINE161 | [5 empty] | 531 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D19 | 槺榔DS | 161 | 161kV | 1510 | 太鐵～槺榔一路(1510) |  | DS3 | 1513 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0616 | 617 |  | 1-36-08 | 1-36-09 |  | 太鐵槺榔一路1513 DS-AS |  |  |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.1513_DS | 1513(太鐵糠榔一路) DS | LINE161 | [5 empty] | 532 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D19 | 槺榔DS | 161 | 161kV | 1510 | 太鐵～槺榔一路(1510) |  | ES3 | 1513E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0618 | 619 |  | 1-36-10 | 1-36-11 |  | 太鐵槺榔一路1513E ES-AS |  |  |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.1513E_ES | 1513E(太鐵糠榔一路) ES | LINE161 | [5 empty] | 533 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D19 | 槺榔DS | 161 | 161kV | 1520 | 太鐵～槺榔二路(1520) |  | DS1 | 1521 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0620 | 621 |  | 1-36-12 | 1-36-13 |  | 太鐵槺榔二路1521 DS-AS |  |  |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.1521_DS | 1521(太鐵糠榔二路) DS | LINE161 | [5 empty] | 534 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D19 | 槺榔DS | 161 | 161kV | 1520 | 太鐵～槺榔二路(1520) |  | DS2 | 1522 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0622 | 623 |  | 1-36-14 | 1-36-15 |  | 太鐵槺榔二路1522 DS-AS |  |  |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.1522_DS | 1522(太鐵糠榔二路) DS | LINE161 | [5 empty] | 535 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D19 | 槺榔DS | 161 | 161kV | 1520 | 太鐵～槺榔二路(1520) |  | DS3 | 1523 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0624 | 625 |  | 1-37-00 | 1-37-01 |  | 太鐵槺榔二路1523 DS-AS |  |  |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.1523_DS | 1523(太鐵糠榔二路) DS | LINE161 | [5 empty] | 536 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D19 | 槺榔DS | 161 | 161kV | 1520 | 太鐵～槺榔二路(1520) |  | ES3 | 1523E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0626 | 627 |  | 1-37-02 | 1-37-03 |  | 太鐵槺榔二路1523E ES-AS |  |  |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.1523E_ES | 1523E(太鐵糠榔二路) ES | LINE161 | [5 empty] | 537 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D19 | 槺榔DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0676 | 677 |  | 1-3A-04 | 1-3A-05 |  | NO.1 DTR(1751) DS-AS |  |  |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.1751_DS | 1751(#1DTR) DS | MTR | [5 empty] | 538 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D19 | 槺榔DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0678 | 679 |  | 1-3A-06 | 1-3A-08 |  | NO.1 DTR(1752) DS-AS |  |  |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.1752_DS | 1752(#1DTR) DS | MTR |  | CDC_Mon1_DPC |  |  |  | 539 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D19 | 槺榔DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0680 | 681 |  | 1-3A-08 | 1-3A-09 |  | NO.1 DTR(1752) DS-BS |  |  |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.1761_DS | 1761(#2DTR) DS | MTR |  | CDC_Mon1_DPC |  |  |  | 540 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D19 | 槺榔DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0682 | 683 |  | 1-3A-10 | 1-3A-11 |  | NO.2 DTR(1762) DS-AS |  |  |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.1762_DS | 1762(#2DTR) DS | MTR | [5 empty] | 541 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D19 | 槺榔DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0684 | 685 |  | 1-3A-12 | 1-3A-13 |  | NO.3 DTR(1771) DS-AS |  |  |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.1771_DS | 1771(#3DTR) DS | MTR | [5 empty] | 542 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D19 | 槺榔DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0686 | 687 |  | 1-3A-14 | 1-3A-15 |  | NO.3 DTR(1772) DS-AS |  |  |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.1772_DS | 1772(#3DTR) DS | MTR | [5 empty] | 543 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D19 | 槺榔DS | 11 | 11kV | LBS210 | #1SC(210) |  | LBS |  |  | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/210 | C/1SC(B) |  |  | 0688 | 689 |  | 1-3B-00 | 1-3B-01 |  | SC-1 LBS AS |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.210_LBS | 210(11KV #1SC) LBS | SC | [5 empty] | 544 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D19 | 槺榔DS | 11 | 11kV | LBS220 | #2SC(220) |  | LBS |  |  | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/220 | C/2SC(B) |  |  | 0690 | 691 |  | 1-3B-02 | 1-3B-03 |  | SC-2 LBS AS |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.220_LBS | 220(11KV #2SC) LBS | SC | [5 empty] | 545 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D19 | 槺榔DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0896 |  |  | 2-38-00 |  |  | 310(M1A) 81S |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.310_81UL | 310 #1DTR(A) 81RY U/L | OTHER | [5 empty] | 546 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 11 | 11kV | JO21 | 槺21(JO21) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0897 |  |  | 2-38-01 |  |  | 槺21(JO21) 79S |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO21_79UL | 11KV糠21線(JO21) 79RY U/L | FEEDER | [5 empty] | 547 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 11 | 11kV | JO21 | 槺21(JO21) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0898 |  |  | 2-38-02 |  |  | 槺21(JO21) 51NS |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO21_LCO_TAP | 11KV糠21線(JO21) LCO TAP | FEEDER | [5 empty] | 548 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D19 | 槺榔DS | 11 | 11kV | JO22 | 槺22(JO22) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0899 |  |  | 2-38-03 |  |  | 槺22(JO22) 79S |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO22_79UL | 11KV糠22線(JO22) 79RY U/L | FEEDER | [5 empty] | 549 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 11 | 11kV | JO22 | 槺22(JO22) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0900 |  |  | 2-38-04 |  |  | 槺22(JO22) 51NS |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO22_LCO_TAP | 11KV糠22線(JO22) LCO TAP | FEEDER | [5 empty] | 550 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D19 | 槺榔DS | 11 | 11kV | JO23 | 槺23(JO23) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0901 |  |  | 2-38-05 |  |  | 槺23(JO23) 79S |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO23_79UL | 11KV糠23線(JO23) 79RY U/L | FEEDER | [5 empty] | 551 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 11 | 11kV | JO23 | 槺23(JO23) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0902 |  |  | 2-38-06 |  |  | 槺23(JO23) 51NS |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO23_LCO_TAP | 11KV糠23線(JO23) LCO TAP | FEEDER | [5 empty] | 552 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D19 | 槺榔DS | 11 | 11kV | JO24 | 槺24(JO24) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0903 |  |  | 2-38-07 |  |  | 槺24(JO24) 79S |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO24_79UL | 11KV糠24線(JO24) 79RY U/L | FEEDER | [5 empty] | 553 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 11 | 11kV | JO24 | 槺24(JO24) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0904 |  |  | 2-38-08 |  |  | 槺24(JO24) 51NS |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO24_LCO_TAP | 11KV糠24線(JO24) LCO TAP | FEEDER | [5 empty] | 554 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D19 | 槺榔DS | 11 | 11kV | JO25 | 槺25(JO25) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0905 |  |  | 2-38-09 |  |  | 槺25(JO25) 79S |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO25_79UL | 11KV糠25線(JO25) 79RY U/L | FEEDER | [5 empty] | 555 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 11 | 11kV | JO25 | 槺25(JO25) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0906 |  |  | 2-38-10 |  |  | 槺25(JO25) 51NS |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO25_LCO_TAP | 11KV糠25線(JO25) LCO TAP | FEEDER | [5 empty] | 556 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D19 | 槺榔DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0909 |  |  | 2-38-13 |  |  | 320(M1B) 81S |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.320_81UL | 320 #1DTR(B) 81RY U/L | OTHER | [5 empty] | 557 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 11 | 11kV | JO26 | 槺26(JO26) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0910 |  |  | 2-38-14 |  |  | 槺26(JO26) 79S |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO26_79UL | 11KV糠26線(JO26) 79RY U/L | FEEDER | [5 empty] | 558 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 11 | 11kV | JO26 | 槺26(JO26) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0911 |  |  | 2-38-15 |  |  | 槺26(JO26) 51NS |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO26_LCO_TAP | 11KV糠26線(JO26) LCO TAP | FEEDER | [5 empty] | 559 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D19 | 槺榔DS | 11 | 11kV | JO27 | 槺27(JO27) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0912 |  |  | 2-39-00 |  |  | 槺27(JO27) 79S |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO27_79UL | 11KV糠27線(JO27) 79RY U/L | FEEDER | [5 empty] | 560 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 11 | 11kV | JO27 | 槺27(JO27) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0913 |  |  | 2-39-01 |  |  | 槺27(JO27) 51NS |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO27_LCO_TAP | 11KV糠27線(JO27) LCO TAP | FEEDER | [5 empty] | 561 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D19 | 槺榔DS | 11 | 11kV | JO28 | 槺28(JO28) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0914 |  |  | 2-39-02 |  |  | 槺28(JO28) 79S |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO28_79UL | 11KV糠28線(JO28) 79RY U/L | FEEDER | [5 empty] | 562 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 11 | 11kV | JO28 | 槺28(JO28) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0915 |  |  | 2-39-03 |  |  | 槺28(JO28) 51NS |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO28_LCO_TAP | 11KV糠28線(JO28) LCO TAP | FEEDER | [5 empty] | 563 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D19 | 槺榔DS | 11 | 11kV | JO29 | 槺29(JO29) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0916 |  |  | 2-39-04 |  |  | 槺29(JO29) 79S |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO29_79UL | 11KV糠29線(JO29) 79RY U/L | FEEDER | [5 empty] | 564 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 11 | 11kV | JO29 | 槺29(JO29) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0917 |  |  | 2-39-05 |  |  | 槺29(JO29) 51NS |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO29_LCO_TAP | 11KV糠29線(JO29) LCO TAP | FEEDER | [5 empty] | 565 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D19 | 槺榔DS | 11 | 11kV | JO30 | 槺30(JO30) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0918 |  |  | 2-39-06 |  |  | 槺30(JO30) 79S |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO30_79UL | 11KV糠30線(JO30) 79RY U/L | FEEDER | [5 empty] | 566 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 11 | 11kV | JO30 | 槺30(JO30) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0919 |  |  | 2-39-07 |  |  | 槺30(JO30) 51NS |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO30_LCO_TAP | 11KV糠30線(JO30) LCO TAP | FEEDER | [5 empty] | 567 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D19 | 槺榔DS | 22 | 22kV | 330 | #2DTR(330) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0922 |  |  | 2-39-10 |  |  | 330(M2) 81S |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.330_81UL | 330 #2DTR 81RY U/L | OTHER | [5 empty] | 568 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 22 | 22kV | JO61 | 槺61(JO61) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0923 |  |  | 2-39-11 |  |  | 槺61(JO61) 79S |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO61_79UL | 23KV糠61線(JO61) 79RY U/L | FEEDER | [5 empty] | 569 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 22 | 22kV | JO61 | 槺61(JO61) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0924 |  |  | 2-39-12 |  |  | 槺61(JO61) 51NS |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO61_LCO_TAP | 23KV糠61線(JO61) LCO TAP | FEEDER | [5 empty] | 570 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D19 | 槺榔DS | 22 | 22kV | JO62 | 槺62(JO62) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0925 |  |  | 2-39-13 |  |  | 槺62(JO62) 79S |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO62_79UL | 23KV糠62線(JO62) 79RY U/L | FEEDER | [5 empty] | 571 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 22 | 22kV | JO62 | 槺62(JO62) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0926 |  |  | 2-39-14 |  |  | 槺62(JO62) 51NS |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO62_LCO_TAP | 23KV糠62線(JO62) LCO TAP | FEEDER | [5 empty] | 572 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D19 | 槺榔DS | 22 | 22kV | JO63 | 槺63(JO63) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0927 |  |  | 2-39-15 |  |  | 槺63(JO63) 79S |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO63_79UL | 23KV糠63線(JO63) 79RY U/L | FEEDER | [5 empty] | 573 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 22 | 22kV | JO63 | 槺63(JO63) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0928 |  |  | 2-3A-00 |  |  | 槺63(JO63) 51NS |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO63_LCO_TAP | 23KV糠63線(JO63) LCO TAP | FEEDER | [5 empty] | 574 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D19 | 槺榔DS | 22 | 22kV | JO64 | 槺64(JO64) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0929 |  |  | 2-3A-01 |  |  | 槺64(JO64) 79S |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO64_79UL | 23KV糠64線(JO64) 79RY U/L | FEEDER | [5 empty] | 575 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 22 | 22kV | JO64 | 槺64(JO64) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0930 |  |  | 2-3A-02 |  |  | 槺64(JO64) 51NS |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO64_LCO_TAP | 23KV糠64線(JO64) LCO TAP | FEEDER | [5 empty] | 576 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D19 | 槺榔DS | 22 | 22kV | JO65 | 槺65(JO65) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0931 |  |  | 2-3A-03 |  |  | 槺65(JO65) 79S |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO65_79UL | 23KV糠65線(JO65) 79RY U/L | FEEDER | [5 empty] | 577 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 22 | 22kV | JO65 | 槺65(JO65) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0932 |  |  | 2-3A-04 |  |  | 槺65(JO65) 51NS |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO65_LCO_TAP | 23KV糠65線(JO65) LCO TAP | FEEDER | [5 empty] | 578 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D19 | 槺榔DS | 22 | 22kV | JO66 | 槺66(JO66) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0933 |  |  | 2-3A-05 |  |  | 槺66(JO66) 79S |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO66_79UL | 23KV糠66線(JO66) 79RY U/L | FEEDER | [5 empty] | 579 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 22 | 22kV | JO66 | 槺66(JO66) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0934 |  |  | 2-3A-06 |  |  | 槺66(JO66) 51NS |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO66_LCO_TAP | 23KV糠66線(JO66) LCO TAP | FEEDER | [5 empty] | 580 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D19 | 槺榔DS | 22 | 22kV | JO67 | 槺67(JO67) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0935 |  |  | 2-3A-07 |  |  | 槺67(JO67) 79S |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO67_79UL | 23KV糠67線(JO67) 79RY U/L | FEEDER | [5 empty] | 581 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 22 | 22kV | JO67 | 槺67(JO67) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0936 |  |  | 2-3A-08 |  |  | 槺67(JO67) 51NS |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO67_LCO_TAP | 23KV糠67線(JO67) LCO TAP | FEEDER | [5 empty] | 582 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D19 | 槺榔DS | 22 | 22kV | JO68 | 槺68(JO68) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0937 |  |  | 2-3A-09 |  |  | 槺68(JO68) 79S |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO68_79UL | 23KV糠68線(JO68) 79RY U/L | FEEDER | [5 empty] | 583 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 22 | 22kV | JO68 | 槺68(JO68) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0938 |  |  | 2-3A-10 |  |  | 槺68(JO68) 51NS |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO68_LCO_TAP | 23KV糠68線(JO68) LCO TAP | FEEDER | [5 empty] | 584 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D19 | 槺榔DS | 22 | 22kV | 350 | #3DTR(350) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0941 |  |  | 2-3A-13 |  |  | 350(M3) 81S |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.350_81UL | 350 #3DTR 81RY U/L | OTHER | [5 empty] | 585 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 22 | 22kV | JO71 | 槺71(JO71) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0942 |  |  | 2-3A-14 |  |  | 槺71(JO71) 79S |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO71_79UL | 23KV糠71線(JO71) 79RY U/L | FEEDER | [5 empty] | 586 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 22 | 22kV | JO71 | 槺71(JO71) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0943 |  |  | 2-3A-15 |  |  | 槺71(JO71) 51NS |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO71_LCO_TAP | 23KV糠71線(JO71) LCO TAP | FEEDER | [5 empty] | 587 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D19 | 槺榔DS | 22 | 22kV | JO72 | 槺72(JO72) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0944 |  |  | 2-3B-00 |  |  | 槺72(JO72) 79S |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO72_79UL | 23KV糠72線(JO72) 79RY U/L | FEEDER | [5 empty] | 588 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 22 | 22kV | JO72 | 槺72(JO72) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0945 |  |  | 2-3B-01 |  |  | 槺72(JO72) 51NS |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO72_LCO_TAP | 23KV糠72線(JO72) LCO TAP | FEEDER | [5 empty] | 589 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D19 | 槺榔DS | 22 | 22kV | JO73 | 槺73(JO73) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0946 |  |  | 2-3B-02 |  |  | 槺73(JO73) 79S |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO73_79UL | 23KV糠73線(JO73) 79RY U/L | FEEDER | [5 empty] | 590 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 22 | 22kV | JO73 | 槺73(JO73) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0947 |  |  | 2-3B-03 |  |  | 槺73(JO73) 51NS |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO73_LCO_TAP | 23KV糠73線(JO73) LCO TAP | FEEDER | [5 empty] | 591 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D19 | 槺榔DS | 22 | 22kV | JO74 | 槺74(JO74) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0948 |  |  | 2-3B-04 |  |  | 槺74(JO74) 79S |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO74_79UL | 23KV糠74線(JO74) 79RY U/L | FEEDER | [5 empty] | 592 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 22 | 22kV | JO74 | 槺74(JO74) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0949 |  |  | 2-3B-05 |  |  | 槺74(JO74) 51NS |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO74_LCO_TAP | 23KV糠74線(JO74) LCO TAP | FEEDER | [5 empty] | 593 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D19 | 槺榔DS | 22 | 22kV | JO75 | 槺75(JO75) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0950 |  |  | 2-3B-06 |  |  | 槺75(JO75) 79S |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO75_79UL | 23KV糠75線(JO75) 79RY U/L | FEEDER | [5 empty] | 594 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 22 | 22kV | JO75 | 槺75(JO75) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0951 |  |  | 2-3B-07 |  |  | 槺75(JO75) 51NS |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO75_LCO_TAP | 23KV糠75線(JO75) LCO TAP | FEEDER | [5 empty] | 595 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D19 | 槺榔DS | 22 | 22kV | JO76 | 槺76(JO76) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0952 |  |  | 2-3B-08 |  |  | 槺76(JO76) 79S |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO76_79UL | 23KV糠76線(JO76) 79RY U/L | FEEDER | [5 empty] | 596 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 22 | 22kV | JO76 | 槺76(JO76) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0953 |  |  | 2-3B-09 |  |  | 槺76(JO76) 51NS |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO76_LCO_TAP | 23KV糠76線(JO76) LCO TAP | FEEDER | [5 empty] | 597 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D19 | 槺榔DS | 22 | 22kV | JO77 | 槺77(JO77) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0954 |  |  | 2-3B-10 |  |  | 槺77(JO77) 79S |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO77_79UL | 23KV糠77線(JO77) 79RY U/L | FEEDER | [5 empty] | 598 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 22 | 22kV | JO77 | 槺77(JO77) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0955 |  |  | 2-3B-11 |  |  | 槺77(JO77) 51NS |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO77_LCO_TAP | 23KV糠77線(JO77) LCO TAP | FEEDER | [5 empty] | 599 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D19 | 槺榔DS | 22 | 22kV | JO78 | 槺78(JO78) |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0956 |  |  | 2-3B-12 |  |  | 槺78(JO78) 79S |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO78_79UL | 23KV糠78線(JO78) 79RY U/L | FEEDER | [5 empty] | 600 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D19 | 槺榔DS | 22 | 22kV | JO78 | 槺78(JO78) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0957 |  |  | 2-3B-13 |  |  | 槺78(JO78) 51NS |  |  |  |  | B2/D19_D1 | [8 empty] | 糠榔DS.JO78_LCO_TAP | 23KV糠78線(JO78) LCO TAP | FEEDER | [5 empty] | 601 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | USE/LOCK | LOCK
D19 | 槺榔DS | 0 |  | StaDev | 所內設施 |  | GEN | 緊急發電機運轉 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0975 |  |  | 2-3C-15 |  |  | 緊急發電機運轉 |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.GEN | 緊急發電機運轉 | OTHER | [5 empty] | 602 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ON/OFF | OFF
D19 | 槺榔DS | 0 |  | StaDev | 所內設施 |  | Fire1 | 受信總機 |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0976 |  |  | 2-3D-00 |  |  | 火災警報(1)受信總機 |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | [5 empty] | 603 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | StaDev | 所內設施 |  | Fire2 |  |  | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0977 |  |  | 2-3D-01 |  |  | 火災警報(2) |  | (無接線) |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.火災警報(2) | 火災警報(2) | OTHER | [5 empty] | 604 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | StaDev | 所內設施 |  | Fire3 |  |  | Status | 火災警報3 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0978 |  |  | 2-3D-02 |  |  | 火災警報(3) |  | (無接線) |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.火災警報(3) | 火災警報(3) | OTHER | [5 empty] | 605 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | StaDev | 所內設施 |  | Fire4 |  |  | Status | 火災警報4 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0979 |  |  | 2-3D-03 |  |  | 火災警報(4) |  | (無接線) |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.火災警報(4) | 火災警報(4) | OTHER | [5 empty] | 606 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | StaDev | 所內設施 |  | Fire5 |  |  | Status | 火災警報5 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0980 |  |  | 2-3D-04 |  |  | 火災警報(5) |  | (無接線) |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.火災警報(5) | 火災警報(5) | OTHER | [5 empty] | 607 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | StaDev | 所內設施 |  | Door1 |  |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0981 |  |  | 2-3D-05 |  |  | 無人化門禁 (一) DOOR1 |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.無人化門禁(1) | 無人化門禁(1)圍牆大門 | OTHER | [5 empty] | 608 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | StaDev | 所內設施 |  | Door2 |  |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0982 |  |  | 2-3D-06 |  |  | 無人化門禁 (二) DOOR2 |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.無人化門禁(2) | 無人化門禁(2)建築物大小門 | OTHER | [5 empty] | 609 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | StaDev | 所內設施 |  | Door3 | 無人化防盜 |  | Status | 無人化門禁3 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0983 |  |  | 2-3D-08 |  |  | 無人化防盜 DOOR3 |  | 保全用 |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.無人化門禁(3) | 無人化門禁(3)保全 | OTHER |  | CDC_Mon1_DPC |  |  |  | 610 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | StaDev | 所內設施 |  | Door4 |  |  | Status | 無人化門禁4 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0984 |  |  | 2-3D-08 |  |  | 無人化防盜 DOOR3 |  | 保全用 |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.無人化門禁(4) | 無人化門禁(4) | OTHER |  | CDC_Mon1_DPC |  |  |  | 611 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | StaDev | 所內設施 |  | Door5 |  | Element | Status | 無人化門禁5 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0985 |  |  | 2-3D-09 |  |  | 無人化門禁 (五) DOOR5 |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.無人化門禁(5) | 無人化門禁(5) | OTHER | [5 empty] | 612 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | StaDev | 所內設施 |  | Lights1 |  |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0986 |  |  | 2-3D-10 |  |  | 無人化開關場照明(A) FLA |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.開關場照明(A) | 開關場照明(A) | OTHER | [5 empty] | 613 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
D19 | 槺榔DS | 0 |  | StaDev | 所內設施 |  | Lights2 |  |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0987 |  |  | 2-3D-11 |  |  | 無人化開關場照明(B) FLB |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.開關場照明(B) | 開關場照明(B) | OTHER | [5 empty] | 614 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
D19 | 槺榔DS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0988 |  |  | 2-3D-12 |  |  | ACBS1 |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | [5 empty] | 615 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D19 | 槺榔DS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0989 |  |  | 2-3D-13 |  |  | ACBS2 |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | [5 empty] | 616 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D19 | 槺榔DS | 0 |  | StaDev | 所內設施 |  | ACBT |  |  | Status | 所內電源ACB TIE | Close/Open | Y | 3 | DI-SP | [6 empty] | 0990 |  |  | 2-3D-14 |  |  | ACBS3 |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | [5 empty] | 617 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ON/OFF | OFF
D19 | 槺榔DS | 0 |  | ComPoint |  |  | OPA |  |  | Status | 充油電纜低壓警報 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0991 |  |  | 2-3D-15 |  |  | 充油電纜警報 OPA |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | [5 empty] | 618 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0992 |  |  | 2-3E-00 |  |  | STUV (所內欠壓警報) |  |  |  |  | ELEM/D19_A1 | [8 empty] | 糠榔DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | [5 empty] | 619 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | StaDev | 所內設施 |  | Water1 |  |  | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0993 |  |  | 2-3E-01 |  |  | UW1 (地下室水位警報 1) |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.水位警報(1) | 地下室水位警報(1) | OTHER | [5 empty] | 620 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | StaDev | 所內設施 |  | Water2 |  |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0994 |  |  | 2-3E-02 |  |  | UW2 (地下室水位警報 2) |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.水位警報(2) | 地下室水位警報(2) | OTHER | [5 empty] | 621 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0995 |  |  | 2-3E-03 |  |  | 161KV CBA |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.161KV_CBA | 161KV斷路器重故障 | OTHER | [5 empty] | 622 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0996 |  |  | 2-3E-04 |  |  | 161KV CBF |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | [5 empty] | 623 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0997 |  |  | 2-3E-05 |  |  | DCA |  |  |  |  | ELEM/D19_A1 | [8 empty] | 糠榔DS.直流電源DCA | 直流電源故障警報 | OTHER | [5 empty] | 624 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0998 |  |  | 2-3E-06 |  |  | ACBA |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.所內電源ACBA | 所內電源故障警報 | OTHER | [5 empty] | 625 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0999 |  |  | 2-3E-07 |  |  | VUA1 161kV#1BUS衡相Ry動作 |  |  |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | [5 empty] | 626 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1000 |  |  | 2-3E-08 |  |  | VUA2 161kV#2BUS衡相Ry動作 |  |  |  |  | B2/D19_A1 | [8 empty] | 糠榔DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | [5 empty] | 627 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1001 |  |  | 2-3E-09 |  |  | CHG1 (直流電源故障) |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.直流充電機故障 | 直流充電機故障 | OTHER | [5 empty] | 628 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1002 |  |  | 2-3E-10 |  |  | DCE |  |  |  |  | ELEM/D19_A1 | [8 empty] | 糠榔DS.直流電源DCE | 直流電源接地故障警報 | OTHER | [5 empty] | 629 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | StaDev | 所內設施 |  | OilLeak1 |  |  | Status | 洩油池水位警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1003 |  |  | 2-3E-11 |  |  | 集油池（中水位） WPA |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.集油池警報(1) | 蓄油池中水位警報 | OTHER | [5 empty] | 630 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | StaDev | 所內設施 |  | OilLeak2 |  |  | Status | 洩油池水位警報2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1004 |  |  | 2-3E-12 |  |  | 集油池（高水位） WPF |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.集油池警報(2) | 蓄油池高水位警報 | OTHER | [5 empty] | 631 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | StaDev | 所內設施 |  | R_Temp1 | 控制室及電驛室 |  | Status | 溫度警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1005 |  |  | 2-3E-13 |  |  | 控制室及電驛室溫度警報 |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.通信機房溫度_1 | 電驛室溫度警報 | OTHER | [5 empty] | 632 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | ComPoint |  |  | 60A |  |  | Status | 電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 1006 |  |  | 2-3E-14 |  |  | 23KV SC 60 RY 警報 60A |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.23KV_SC_60A | 11/23KV SC 60A | OTHER | [5 empty] | 633 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1007 |  |  | 2-3E-15 |  |  | 23KV CBA |  |  |  |  | ELEM/D19_A1 | [8 empty] | 糠榔DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | [5 empty] | 634 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1008 |  |  | 2-3F-00 |  |  | 23KV CBF |  |  |  |  | ELEM/D19_A1 | [8 empty] | 糠榔DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | [5 empty] | 635 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | ComPoint |  |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1009 |  |  | 2-3F-01 |  |  | 23KV LOA |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.11/23KV_LOA | 11/23KV饋線復閉失敗閉鎖 | OTHER | [5 empty] | 636 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1012 |  |  | 2-3F-04 |  |  | CHG2 (通訊用直流電源故障) |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | [5 empty] | 637 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1013 |  |  | 2-3F-05 |  |  | ACFA (通訊設備AC故障) |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | [5 empty] | 638 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | StaDev | 所內設施 |  | R_Temp2 | 通訊用 |  | Status | 溫度警報2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1016 |  |  | 2-3F-08 |  |  | OLTNA (通訊設備光纖次故障) |  |  |  |  | B3/D19_A1 | [8 empty] | 糠榔DS.通信機房溫度_2 | 通訊室或控制室溫度警報 | OTHER | [5 empty] | 639 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | StaDev | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1023 |  |  | 2-3F-15 |  |  | PMA |  |  |  |  | ELEM/D19_A1 | [8 empty] | 糠榔DS.PMA | 電力量測表計故障 | OTHER | [5 empty] | 640 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
D19 | 槺榔DS | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/D19_A1 | [12 empty] | 糠榔DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: D19/161/1BUS/V; OPRD2: D19/161/2BUS/V
D19 | 槺榔DS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/D19_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: D19/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
D19 | 槺榔DS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/D19_A1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_2 | OPRD1: D19/161/1510/MW; OPRD2: D19/161/1520/MW
D19 | 槺榔DS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/D19_A1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: D19/0/CalcPoint/OPRN2_MW
D19 | 槺榔DS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/D19_A1 | [17 empty] | none
D19 | 槺榔DS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/D19_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: D19/0/CalcPoint/OPRN1; OPRD2: D19/0/CalcPoint/OPRN2; OPRD3: D19/0/CalcPoint/PRFL_UL
D19 | 槺榔DS |  |  | 1DTR | 1DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D19_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D19/11/310/I_R; OPRD2: D19/11/320/I_R
D19 | 槺榔DS |  |  | 1DTR | 1DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D19_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D19/11/310/I_S; OPRD2: D19/11/320/I_S
D19 | 槺榔DS |  |  | 1DTR | 1DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D19_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D19/11/310/I_T; OPRD2: D19/11/320/I_T
D19 | 槺榔DS | 161 | 161kV | 1510 | 太鐵～槺榔一路(1510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D19_A1 | [12 empty] | 糠榔DS.1510_AMP | 太鐵糠榔一路 AMP | LINE161 | AMP_CAL | C20R1930 | amp_cal | OPRD1: D19/161/1510/MW; OPRD2: D19/161/1510/MVAR; OPRD3: D19/0/CalcPoint/Vbs4
D19 | 槺榔DS | 161 | 161kV | 1520 | 太鐵～槺榔二路(1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D19_A1 | [12 empty] | 糠榔DS.1520_AMP | 太鐵糠榔二路 AMP | LINE161 | AMP_CAL | C20R1930 | amp_cal | OPRD1: D19/161/1520/MW; OPRD2: D19/161/1520/MVAR; OPRD3: D19/0/CalcPoint/Vbs4
D19 | 槺榔DS | 11 | 11kV | 1ABUS | #1ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D19_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D19/11/1ABUS/V
D19 | 槺榔DS | 11 | 11kV | 1BBUS | #1BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D19_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D19/11/1BBUS/V
D19 | 槺榔DS | 11 | 11kV | 2BUS | #2BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D19_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D19/11/2BUS/V
D19 | 槺榔DS | 11 | 11kV | 3BUS | #3BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D19_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D19/11/3BUS/V
D19 | 槺榔DS |  |  | 1DTR(A) | #1DTR(A) |  | TR_PERM | [9 empty] | B1/D19_A1 | [12 empty] | 糠榔DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D19//1DTR(A)/SupLocal; OPRD2: D19//1DTR(A)/Tap Chan
D19 | 槺榔DS |  |  | 1DTR(B) | #1DTR(B) |  | TR_PERM | [9 empty] | B1/D19_A1 | [12 empty] | 糠榔DS.#1DTR(B)_PERM | #1DTR(B) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D19//1DTR(B)/SupLocal; OPRD2: D19//1DTR(B)/Tap Chan
D19 | 槺榔DS |  |  | 2DTR | #2DTR |  | TR_PERM | [9 empty] | B1/D19_A1 | [12 empty] | 糠榔DS.#2DTR_PERM | #2DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D19//2DTR/SupLocal; OPRD2: D19//2DTR/Tap Chan
D19 | 槺榔DS |  |  | 3DTR | #3DTR |  | TR_PERM | [9 empty] | B1/D19_A1 | [12 empty] | 糠榔DS.#3DTR_PERM | #3DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D19//3DTR/SupLocal; OPRD2: D19//3DTR/Tap Chan
D19 | 槺榔DS | 11 | 11kV | JO21 | 槺21(JO21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D19/11/1ABUS/V; OPRD2: D19/11/JO21/I_R; OPRD3: D19/11/JO21/I_S; OPRD4: D19/11/JO21/I_T
D19 | 槺榔DS | 11 | 11kV | JO22 | 槺22(JO22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D19/11/1ABUS/V; OPRD2: D19/11/JO22/I_R; OPRD3: D19/11/JO22/I_S; OPRD4: D19/11/JO22/I_T
D19 | 槺榔DS | 11 | 11kV | JO23 | 槺23(JO23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D19/11/1ABUS/V; OPRD2: D19/11/JO23/I_R; OPRD3: D19/11/JO23/I_S; OPRD4: D19/11/JO23/I_T
D19 | 槺榔DS | 11 | 11kV | JO24 | 槺24(JO24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D19/11/1ABUS/V; OPRD2: D19/11/JO24/I_R; OPRD3: D19/11/JO24/I_S; OPRD4: D19/11/JO24/I_T
D19 | 槺榔DS | 11 | 11kV | JO25 | 槺25(JO25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D19/11/1ABUS/V; OPRD2: D19/11/JO25/I_R; OPRD3: D19/11/JO25/I_S; OPRD4: D19/11/JO25/I_T
D19 | 槺榔DS | 11 | 11kV | JO26 | 槺26(JO26) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D19/11/1BBUS/V; OPRD2: D19/11/JO26/I_R; OPRD3: D19/11/JO26/I_S; OPRD4: D19/11/JO26/I_T
D19 | 槺榔DS | 11 | 11kV | JO27 | 槺27(JO27) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D19/11/1BBUS/V; OPRD2: D19/11/JO27/I_R; OPRD3: D19/11/JO27/I_S; OPRD4: D19/11/JO27/I_T
D19 | 槺榔DS | 11 | 11kV | JO28 | 槺28(JO28) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D19/11/1BBUS/V; OPRD2: D19/11/JO28/I_R; OPRD3: D19/11/JO28/I_S; OPRD4: D19/11/JO28/I_T
D19 | 槺榔DS | 11 | 11kV | JO29 | 槺29(JO29) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D19/11/1BBUS/V; OPRD2: D19/11/JO29/I_R; OPRD3: D19/11/JO29/I_S; OPRD4: D19/11/JO29/I_T
D19 | 槺榔DS | 11 | 11kV | JO30 | 槺30(JO30) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D19/11/1BBUS/V; OPRD2: D19/11/JO30/I_R; OPRD3: D19/11/JO30/I_S; OPRD4: D19/11/JO30/I_T
D19 | 槺榔DS | 22 | 22kV | JO61 | 槺61(JO61) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D19/22/JO61/I_R; OPRD3: D19/22/JO61/I_S; OPRD4: D19/22/JO61/I_T
D19 | 槺榔DS | 22 | 22kV | JO62 | 槺62(JO62) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D19/22/JO62/I_R; OPRD3: D19/22/JO62/I_S; OPRD4: D19/22/JO62/I_T
D19 | 槺榔DS | 22 | 22kV | JO63 | 槺63(JO63) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D19/22/JO63/I_R; OPRD3: D19/22/JO63/I_S; OPRD4: D19/22/JO63/I_T
D19 | 槺榔DS | 22 | 22kV | JO64 | 槺64(JO64) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D19/22/JO64/I_R; OPRD3: D19/22/JO64/I_S; OPRD4: D19/22/JO64/I_T
D19 | 槺榔DS | 22 | 22kV | JO65 | 槺65(JO65) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D19/22/JO65/I_R; OPRD3: D19/22/JO65/I_S; OPRD4: D19/22/JO65/I_T
D19 | 槺榔DS | 22 | 22kV | JO66 | 槺66(JO66) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D19/22/JO66/I_R; OPRD3: D19/22/JO66/I_S; OPRD4: D19/22/JO66/I_T
D19 | 槺榔DS | 22 | 22kV | JO67 | 槺67(JO67) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D19/22/JO67/I_R; OPRD3: D19/22/JO67/I_S; OPRD4: D19/22/JO67/I_T
D19 | 槺榔DS | 22 | 22kV | JO68 | 槺68(JO68) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D19/22/JO68/I_R; OPRD3: D19/22/JO68/I_S; OPRD4: D19/22/JO68/I_T
D19 | 槺榔DS | 22 | 22kV | JO71 | 槺71(JO71) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D19/22/JO71/I_R; OPRD3: D19/22/JO71/I_S; OPRD4: D19/22/JO71/I_T
D19 | 槺榔DS | 22 | 22kV | JO72 | 槺72(JO72) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D19/22/JO72/I_R; OPRD3: D19/22/JO72/I_S; OPRD4: D19/22/JO72/I_T
D19 | 槺榔DS | 22 | 22kV | JO73 | 槺73(JO73) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D19/22/JO73/I_R; OPRD3: D19/22/JO73/I_S; OPRD4: D19/22/JO73/I_T
D19 | 槺榔DS | 22 | 22kV | JO74 | 槺74(JO74) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D19/22/JO74/I_R; OPRD3: D19/22/JO74/I_S; OPRD4: D19/22/JO74/I_T
D19 | 槺榔DS | 22 | 22kV | JO75 | 槺75(JO75) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D19/22/JO75/I_R; OPRD3: D19/22/JO75/I_S; OPRD4: D19/22/JO75/I_T
D19 | 槺榔DS | 22 | 22kV | JO76 | 槺76(JO76) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D19/22/JO76/I_R; OPRD3: D19/22/JO76/I_S; OPRD4: D19/22/JO76/I_T
D19 | 槺榔DS | 22 | 22kV | JO77 | 槺77(JO77) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D19/22/JO77/I_R; OPRD3: D19/22/JO77/I_S; OPRD4: D19/22/JO77/I_T
D19 | 槺榔DS | 22 | 22kV | JO78 | 槺78(JO78) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D19/22/JO78/I_R; OPRD3: D19/22/JO78/I_S; OPRD4: D19/22/JO78/I_T
D19 | 槺榔DS | 11 | 11kV | JO21 | 槺21(JO21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D19/11/JO21/kVA; OPRD2: D19/11/JO21/KVAR
D19 | 槺榔DS | 11 | 11kV | JO22 | 槺22(JO22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D19/11/JO22/kVA; OPRD2: D19/11/JO22/KVAR
D19 | 槺榔DS | 11 | 11kV | JO23 | 槺23(JO23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D19/11/JO23/kVA; OPRD2: D19/11/JO23/KVAR
D19 | 槺榔DS | 11 | 11kV | JO24 | 槺24(JO24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D19/11/JO24/kVA; OPRD2: D19/11/JO24/KVAR
D19 | 槺榔DS | 11 | 11kV | JO25 | 槺25(JO25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D19/11/JO25/kVA; OPRD2: D19/11/JO25/KVAR
D19 | 槺榔DS | 11 | 11kV | JO26 | 槺26(JO26) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D19/11/JO26/kVA; OPRD2: D19/11/JO26/KVAR
D19 | 槺榔DS | 11 | 11kV | JO27 | 槺27(JO27) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D19/11/JO27/kVA; OPRD2: D19/11/JO27/KVAR
D19 | 槺榔DS | 11 | 11kV | JO28 | 槺28(JO28) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D19/11/JO28/kVA; OPRD2: D19/11/JO28/KVAR
D19 | 槺榔DS | 11 | 11kV | JO29 | 槺29(JO29) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D19/11/JO29/kVA; OPRD2: D19/11/JO29/KVAR
D19 | 槺榔DS | 11 | 11kV | JO30 | 槺30(JO30) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D19/11/JO30/kVA; OPRD2: D19/11/JO30/KVAR
D19 | 槺榔DS | 22 | 22kV | JO61 | 槺61(JO61) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D19/22/JO61/kVA; OPRD2: D19/22/JO61/KVAR
D19 | 槺榔DS | 22 | 22kV | JO62 | 槺62(JO62) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D19/22/JO62/kVA; OPRD2: D19/22/JO62/KVAR
D19 | 槺榔DS | 22 | 22kV | JO63 | 槺63(JO63) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D19/22/JO63/kVA; OPRD2: D19/22/JO63/KVAR
D19 | 槺榔DS | 22 | 22kV | JO64 | 槺64(JO64) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D19/22/JO64/kVA; OPRD2: D19/22/JO64/KVAR
D19 | 槺榔DS | 22 | 22kV | JO65 | 槺65(JO65) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D19/22/JO65/kVA; OPRD2: D19/22/JO65/KVAR
D19 | 槺榔DS | 22 | 22kV | JO66 | 槺66(JO66) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D19/22/JO66/kVA; OPRD2: D19/22/JO66/KVAR
D19 | 槺榔DS | 22 | 22kV | JO67 | 槺67(JO67) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D19/22/JO67/kVA; OPRD2: D19/22/JO67/KVAR
D19 | 槺榔DS | 22 | 22kV | JO68 | 槺68(JO68) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D19/22/JO68/kVA; OPRD2: D19/22/JO68/KVAR
D19 | 槺榔DS | 22 | 22kV | JO71 | 槺71(JO71) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D19/22/JO71/kVA; OPRD2: D19/22/JO71/KVAR
D19 | 槺榔DS | 22 | 22kV | JO72 | 槺72(JO72) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D19/22/JO72/kVA; OPRD2: D19/22/JO72/KVAR
D19 | 槺榔DS | 22 | 22kV | JO73 | 槺73(JO73) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D19/22/JO73/kVA; OPRD2: D19/22/JO73/KVAR
D19 | 槺榔DS | 22 | 22kV | JO74 | 槺74(JO74) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D19/22/JO74/kVA; OPRD2: D19/22/JO74/KVAR
D19 | 槺榔DS | 22 | 22kV | JO75 | 槺75(JO75) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D19/22/JO75/kVA; OPRD2: D19/22/JO75/KVAR
D19 | 槺榔DS | 22 | 22kV | JO76 | 槺76(JO76) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D19/22/JO76/kVA; OPRD2: D19/22/JO76/KVAR
D19 | 槺榔DS | 22 | 22kV | JO77 | 槺77(JO77) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D19/22/JO77/kVA; OPRD2: D19/22/JO77/KVAR
D19 | 槺榔DS | 22 | 22kV | JO78 | 槺78(JO78) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D19_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D19/22/JO78/kVA; OPRD2: D19/22/JO78/KVAR
D19 | 槺榔DS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D19_A1 | [12 empty] | 糠榔DS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D19/11/210/CB; OPRD2: 6.9; OPRD3: 0
D19 | 槺榔DS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D19_A1 | [12 empty] | 糠榔DS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D19/11/220/CB; OPRD2: 6.9; OPRD3: 0
D19 | 槺榔DS | 22 | 22kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D19_A1 | [12 empty] | 糠榔DS.230_SC_MVAR | 23KV#3SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D19/22/230/CB; OPRD2: 13.8; OPRD3: 0
D19 | 槺榔DS | 22 | 22kV | 240 | #4SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D19_A1 | [12 empty] | 糠榔DS.240_SC_MVAR | 23KV#4SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D19/22/240/CB; OPRD2: 13.8; OPRD3: 0
D19 | 槺榔DS | 22 | 22kV | 250 | #5SC(250) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D19_A1 | [12 empty] | 糠榔DS.250_SC_MVAR | 23KV#5SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D19/22/250/CB; OPRD2: 13.8; OPRD3: 0
D19 | 槺榔DS | 22 | 22kV | 260 | #6SC(260) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D19_A1 | [12 empty] | 糠榔DS.260_SC_MVAR | 23KV#6SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D19/22/260/CB; OPRD2: 13.8; OPRD3: 0
D19 | 槺榔DS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/D19_A1 | [12 empty] | 糠榔DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_14 |  | com_alarm_43 | D19//1DTR/96D | D19//1DTR/63Q | D19//1DTR/TRA | D19//1DTR/PHA | D19//1DTR/96B1 | D19//1DTR/96B2 | D19//1DTR/96PA | D19//1DTR/87A | D19//1DTR/51ZA | D19//2DTR/96D | D19//2DTR/96B2 | D19//2DTR/63Q | D19//2DTR/TRA | D19//2DTR/51ZA | D19//2DTR/96B1 | D19//2DTR/PHA | D19//2DTR/96PA | D19//2DTR/87A | D19//3DTR/96B1 | D19//3DTR/PHA | D19//3DTR/51ZA | D19//3DTR/96D | D19//3DTR/TRA | D19//3DTR/63Q | D19//3DTR/96PA | D19//3DTR/87A | D19//3DTR/96B2 | D19/11/310/GDA | D19/11/310/PHA | D19/11/320/GDA | D19/11/320/PHA | D19/161/1750/PHA | D19/161/1750/GDA | D19/161/1760/GDA | D19/161/1760/PHA | D19/161/1770/GDA | D19/161/1770/PHA | D19/161/1BUS/87A | D19/161/2BUS/87A | D19/22/330/PHA | D19/22/330/GDA | D19/22/350/PHA | D19/22/350/GDA
D19 | 槺榔DS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/D19_A1 | [12 empty] | 糠榔DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | STATION_FAULT_3 |  | com_alarm_3 | OPRD1: D19//1DTR/TRF; OPRD2: D19//2DTR/TRF; OPRD3: D19//3DTR/TRF
D19 | 槺榔DS | 161 | 161kV | 1750_D1 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D19_D1 | [17 empty] | lamp2CC | OPRD1: D19/161/1750/CB
D19 | 槺榔DS | 11 | 11kV | 310_D1 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D19_D1 | [17 empty] | lamp2CC | OPRD1: D19/11/310/CB
D19 | 槺榔DS | 11 | 11kV | 310_D1 | #1DTR(A)(310) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/D19_D1 | [17 empty] | lamp2CC | OPRD1: D19/11/310/81A
D19 | 槺榔DS | 11 | 11kV | 320_D1 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D19_D1 | [17 empty] | lamp2CC | OPRD1: D19/11/320/CB
D19 | 槺榔DS | 11 | 11kV | 320_D1 | #1DTR(B)(320) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/D19_D1 | [17 empty] | lamp2CC | OPRD1: D19/11/320/81A
D19 | 槺榔DS | 161 | 161kV | 1760_D1 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D19_D1 | [17 empty] | lamp2CC | OPRD1: D19/161/1760/CB
D19 | 槺榔DS | 22 | 22kV | 330_D1 | #2DTR(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D19_D1 | [17 empty] | lamp2CC | OPRD1: D19/22/330/CB
D19 | 槺榔DS | 22 | 22kV | 330_D1 | #2DTR(330) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/D19_D1 | [17 empty] | lamp2CC | OPRD1: D19/22/330/81A
D19 | 槺榔DS | 161 | 161kV | 1770_D1 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D19_D1 | [17 empty] | lamp2CC | OPRD1: D19/161/1770/CB
D19 | 槺榔DS | 22 | 22kV | 350_D1 | #3DTR(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D19_D1 | [17 empty] | lamp2CC | OPRD1: D19/22/350/CB
D19 | 槺榔DS | 22 | 22kV | 350_D1 | #3DTR(350) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/D19_D1 | [17 empty] | lamp2CC | OPRD1: D19/22/350/81A
D19 | 槺榔DS | 0 |  | RTU_D1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/D19_D1 | [17 empty] | lamp2CC | OPRD1: D19/0/RTU/RTU_R_L
D19 | 槺榔DS | 0 |  | StaDev_D1 | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/D19_D1 | [17 empty] | lamp2CC | OPRD1: D19/0/StaDev/STUV
D19 | 槺榔DS | 0 |  | StaDev_D1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D19_D1 | [17 empty] | lamp2CC | OPRD1: D19/0/StaDev/DCA
D19 | 槺榔DS | 0 |  | StaDev_D1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D19_D1 | [17 empty] | lamp2CC | OPRD1: D19/0/StaDev/DCE
D19 | 槺榔DS | 22 | 22kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D19_D1 | [17 empty] | lamp2CC | OPRD1: D19/22/ComPoint/CBA
D19 | 槺榔DS | 22 | 22kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | ELEM/D19_D1 | [17 empty] | lamp2CC | OPRD1: D19/22/ComPoint/CBF
D19 | 槺榔DS | 0 |  | StaDev_D1 | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D19_D1 | [17 empty] | lamp2CC | OPRD1: D19/0/StaDev/PMA

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D19 | 槺榔DS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | D19/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
D19 | 槺榔DS | 161 | 161kV | 1510 | 太鐵糠榔一路(1510) |  | I | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.1510_AMP | 太鐵糠榔一路 AMP | LINE161 | D19/161/1510/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C20R1930 | 1737.800049 | 1737.800049 | 1930.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D19 | 槺榔DS | 161 | 161kV | 1520 | 太鐵糠榔二路(1520) |  | I | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.1520_AMP | 太鐵糠榔二路 AMP | LINE161 | D19/161/1520/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C20R1930 | 1737.800049 | 1737.800049 | 1930.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠21線KVA | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠21線KVA | 11KV糠21線KVA | FEEDER |  |  | KVA_CAL |  |  | 5 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠21線KW | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠21線KW | 11KV糠21線KW | FEEDER |  |  | KW_CAL |  |  | 6 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠22線KVA | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠22線KVA | 11KV糠22線KVA | FEEDER |  |  | KVA_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠22線KW | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠22線KW | 11KV糠22線KW | FEEDER |  |  | KW_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠23線KVA | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠23線KVA | 11KV糠23線KVA | FEEDER |  |  | KVA_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠23線KW | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠23線KW | 11KV糠23線KW | FEEDER |  |  | KW_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠24線KVA | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠24線KVA | 11KV糠24線KVA | FEEDER |  |  | KVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠24線KW | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠24線KW | 11KV糠24線KW | FEEDER |  |  | KW_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠25線KVA | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠25線KVA | 11KV糠25線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠25線KW | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠25線KW | 11KV糠25線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠26線KVA | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠26線KVA | 11KV糠26線KVA | FEEDER |  |  | KVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠26線KW | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠26線KW | 11KV糠26線KW | FEEDER |  |  | KW_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠27線KVA | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠27線KVA | 11KV糠27線KVA | FEEDER |  |  | KVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠27線KW | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠27線KW | 11KV糠27線KW | FEEDER |  |  | KW_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠28線KVA | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠28線KVA | 11KV糠28線KVA | FEEDER |  |  | KVA_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠28線KW | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠28線KW | 11KV糠28線KW | FEEDER |  |  | KW_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠29線KVA | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠29線KVA | 11KV糠29線KVA | FEEDER |  |  | KVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠29線KW | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠29線KW | 11KV糠29線KW | FEEDER |  |  | KW_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠30線KVA | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠30線KVA | 11KV糠30線KVA | FEEDER |  |  | KVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠30線KW | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠30線KW | 11KV糠30線KW | FEEDER |  |  | KW_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠61線KVA | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠61線KVA | 23KV糠61線KVA | FEEDER |  |  | KVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠61線KW | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠61線KW | 23KV糠61線KW | FEEDER |  |  | KW_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠62線KVA | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠62線KVA | 23KV糠62線KVA | FEEDER |  |  | KVA_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠62線KW | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠62線KW | 23KV糠62線KW | FEEDER |  |  | KW_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠63線KVA | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠63線KVA | 23KV糠63線KVA | FEEDER |  |  | KVA_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠63線KW | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠63線KW | 23KV糠63線KW | FEEDER |  |  | KW_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠64線KVA | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠64線KVA | 23KV糠64線KVA | FEEDER |  |  | KVA_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠64線KW | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠64線KW | 23KV糠64線KW | FEEDER |  |  | KW_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠65線KVA | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠65線KVA | 23KV糠65線KVA | FEEDER |  |  | KVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠65線KW | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠65線KW | 23KV糠65線KW | FEEDER |  |  | KW_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠66線KVA | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠66線KVA | 23KV糠66線KVA | FEEDER |  |  | KVA_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠66線KW | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠66線KW | 23KV糠66線KW | FEEDER |  |  | KW_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠67線KVA | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠67線KVA | 23KV糠67線KVA | FEEDER |  |  | KVA_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠67線KW | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠67線KW | 23KV糠67線KW | FEEDER |  |  | KW_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠68線KVA | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠68線KVA | 23KV糠68線KVA | FEEDER |  |  | KVA_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠68線KW | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠68線KW | 23KV糠68線KW | FEEDER |  |  | KW_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠71線KVA | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠71線KVA | 23KV糠71線KVA | FEEDER |  |  | KVA_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠71線KW | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠71線KW | 23KV糠71線KW | FEEDER |  |  | KW_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠72線KVA | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠72線KVA | 23KV糠72線KVA | FEEDER |  |  | KVA_CAL |  |  | 43 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠72線KW | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠72線KW | 23KV糠72線KW | FEEDER |  |  | KW_CAL |  |  | 44 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠73線KVA | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠73線KVA | 23KV糠73線KVA | FEEDER |  |  | KVA_CAL |  |  | 45 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠73線KW | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠73線KW | 23KV糠73線KW | FEEDER |  |  | KW_CAL |  |  | 46 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠74線KVA | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠74線KVA | 23KV糠74線KVA | FEEDER |  |  | KVA_CAL |  |  | 47 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠74線KW | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠74線KW | 23KV糠74線KW | FEEDER |  |  | KW_CAL |  |  | 48 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠75線KVA | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠75線KVA | 23KV糠75線KVA | FEEDER |  |  | KVA_CAL |  |  | 49 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠75線KW | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠75線KW | 23KV糠75線KW | FEEDER |  |  | KW_CAL |  |  | 50 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠76線KVA | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠76線KVA | 23KV糠76線KVA | FEEDER |  |  | KVA_CAL |  |  | 51 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠76線KW | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠76線KW | 23KV糠76線KW | FEEDER |  |  | KW_CAL |  |  | 52 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠77線KVA | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠77線KVA | 23KV糠77線KVA | FEEDER |  |  | KVA_CAL |  |  | 53 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠77線KW | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠77線KW | 23KV糠77線KW | FEEDER |  |  | KW_CAL |  |  | 54 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠78線KVA | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠78線KVA | 23KV糠78線KVA | FEEDER |  |  | KVA_CAL |  |  | 55 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  |  |  |  | 糠78線KW | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.糠78線KW | 23KV糠78線KW | FEEDER |  |  | KW_CAL |  |  | 56 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.#1DTR(A)_MVA | #1DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 57 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D19 | 槺榔DS | 0 |  | 1DTR(A) | #1DTR(A) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.#1DTR(A)_LOAD | #1DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 58 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D19 | 槺榔DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PF | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.#1DTR(A)_PF | #1DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 59 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D19 | 槺榔DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.#1DTR(B)_MVA | #1DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 60 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D19 | 槺榔DS | 0 |  | 1DTR(B) | #1DTR(B) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.#1DTR(B)_LOAD | #1DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 61 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D19 | 槺榔DS | 0 |  | 1DTR(B) | #1DTR(B) |  | PF | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.#1DTR(B)_PF | #1DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 62 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D19 | 槺榔DS | 0 |  | 2DTR | #2DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.#2DTR_MVA | #2DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 63 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D19 | 槺榔DS | 0 |  | 2DTR | #2DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.#2DTR_LOAD | #2DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 64 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D19 | 槺榔DS | 0 |  | 2DTR | #2DTR |  | PF | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.#2DTR_PF | #2DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 65 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D19 | 槺榔DS | 0 |  | 3DTR | #3DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.#3DTR_MVA | #3DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 66 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D19 | 槺榔DS | 0 |  | 3DTR | #3DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.#3DTR_LOAD | #3DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 67 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D19 | 槺榔DS | 0 |  | 3DTR | #3DTR |  | PF | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.#3DTR_PF | #3DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 68 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D19 | 槺榔DS | 0 |  | 1DTR | #1DTR |  | MW | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.#1DTR_MW | #1DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 69 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  | 1DTR | #1DTR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.#1DTR_MVAR | #1DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 70 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  | 1DTR | #1DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.#1DTR_MVA | #1DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 71 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D19 | 槺榔DS | 0 |  | 1DTR | #1DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.#1DTR_LOAD | #1DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 72 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D19 | 槺榔DS | 0 |  | 1DTR | #1DTR |  | PF | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.#1DTR_PF | #1DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 73 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D19 | 槺榔DS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.210_SC_MVAR | 11KV#1SC MVAR | SC | D19/11/210/MVAR |  | SC_LBS_11 |  |  | 74 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 11 | 11kV | 220_SC | #2SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.220_SC_MVAR | 11KV#2SC MVAR | SC | D19/11/220/MVAR |  | SC_LBS_11 |  |  | 75 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 22 | 22kV | 230_SC | #3SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.230_SC_MVAR | 23KV#3SC MVAR | SC | D19/22/230/MVAR |  | SC_CAL_23 |  |  | 76 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 22 | 22kV | 240_SC | #4SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.240_SC_MVAR | 23KV#4SC MVAR | SC | D19/22/240/MVAR |  | SC_CAL_23 |  |  | 77 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 22 | 22kV | 250_SC | #5SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.250_SC_MVAR | 23KV#5SC MVAR | SC | D19/22/250/MVAR |  | SC_CAL_23 |  |  | 78 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 22 | 22kV | 260_SC | #6SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.260_SC_MVAR | 23KV#6SC MVAR | SC | D19/22/260/MVAR |  | SC_CAL_23 |  |  | 79 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  | TRTOT | 糠榔主變瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 糠榔DS.TRTOT_MW | 糠榔主變瞬時供電量 MW |  |  |  | TOTAL_PQ_CAL_3 |  |  | 80 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  | TRTOT | 糠榔主變瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 糠榔DS.TRTOT_MVAR | 糠榔主變瞬時供電量 MVAR |  |  |  | TOTAL_PQ_CAL_3 |  |  | 81 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 0 |  | 100_CB | 100(100_CB) | [27 empty] | DDCS2_2 | [8 empty] | 糠榔DS.100_CB_2 | 100 CB (D2) | TIE |  |  | AD_LAMP_DD_1 |  |  | 82 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | 200_CB | 200(200_CB) | [27 empty] | DDCS2_2 | [8 empty] | 糠榔DS.200_CB_2 | 200 CB (D2) | TIE |  |  | AD_LAMP_DD_1 |  |  | 83 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | 310_CB | #1DTR(310_CB) | [27 empty] | DDCS2_2 | [8 empty] | 糠榔DS.310_CB_2 | 310(#1DTR) CB (D2) | MTR |  |  | AD_LAMP_DD_1 |  |  | 84 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | 320_CB | #1DTR(320_CB) | [27 empty] | DDCS2_2 | [8 empty] | 糠榔DS.320_CB_2 | 320(#1DTR) CB (D2) | MTR |  |  | AD_LAMP_DD_1 |  |  | 85 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | 330_CB | #2DTR(330_CB) | [27 empty] | DDCS2_2 | [8 empty] | 糠榔DS.330_CB_2 | 330(#2DTR) CB (D2) | MTR |  |  | AD_LAMP_DD_1 |  |  | 86 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | 350_CB | #3DTR(350_CB) | [27 empty] | DDCS2_2 | [8 empty] | 糠榔DS.350_CB_2 | 350(#3DTR) CB (D2) | MTR |  |  | AD_LAMP_DD_1 |  |  | 87 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | 210_CB | #1SC(210_CB) | [27 empty] | DDCS2_2 | [8 empty] | 糠榔DS.210_CB_2 | 210(11KV #1SC) CB (D2) | SC |  |  | AD_LAMP_DD_1 |  |  | 88 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | 220_CB | #2SC(220_CB) | [27 empty] | DDCS2_2 | [8 empty] | 糠榔DS.220_CB_2 | 220(11KV #2SC) CB (D2) | SC |  |  | AD_LAMP_DD_1 |  |  | 89 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | 230_CB | #3SC(230_CB) | [27 empty] | DDCS2_2 | [8 empty] | 糠榔DS.230_CB_2 | 230(23KV #3SC) CB (D2) | SC |  |  | AD_LAMP_DD_1 |  |  | 90 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | 240_CB | #4SC(240_CB) | [27 empty] | DDCS2_2 | [8 empty] | 糠榔DS.240_CB_2 | 240(23KV #4SC) CB (D2) | SC |  |  | AD_LAMP_DD_1 |  |  | 91 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | 250_CB | #5SC(250_CB) | [27 empty] | DDCS2_2 | [8 empty] | 糠榔DS.250_CB_2 | 250(23KV #5SC) CB (D2) | SC |  |  | AD_LAMP_DD_1 |  |  | 92 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | 260_CB | #6SC(260_CB) | [27 empty] | DDCS2_2 | [8 empty] | 糠榔DS.260_CB_2 | 260(23KV #6SC) CB (D2) | SC |  |  | AD_LAMP_DD_1 |  |  | 93 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | 11__CBA | 11/斷路器重故障(11__CBA) | [27 empty] | DDCS2_2 | [8 empty] | 糠榔DS.11/23KV_CBA_2 | 11/23KV斷路器重故障 (D2) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 94 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | 11__CBF | 11/斷路器輕故障(11__CBF) | [27 empty] | DDCS2_2 | [8 empty] | 糠榔DS.11/23KV_CBF_2 | 11/23KV斷路器輕故障 (D2) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 95 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | RTU_S_L | RTU | [27 empty] | DDCS2_2 | [8 empty] | 糠榔DS.RTU_S/L_2 | RTU SUPY/LOCAL (D2) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 96 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D19 | 槺榔DS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | D19/0/CalcPoint/SUBA |  | STATION_FAULT_14 |  |  | 97 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 變電所輕故障點燈 | 變電所輕故障點燈 |  | SUBF | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | D19/0/CalcPoint/SUBF |  | STATION_FAULT_3 |  |  | 98 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 變電所重故障 | 變電所重故障點燈 | [27 empty] | DDCS2_2 | [8 empty] | 糠榔DS.變電所重故障_2 | 變電所重故障點燈 (D2) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 99 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 | [27 empty] | DDCS2_2 | [8 empty] | 糠榔DS.變電所輕故障_2 | 變電所輕故障點燈 (D2) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 100 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1510_AMP | 太鐵糠榔一路 | [27 empty] | ADCS_N | [8 empty] | 糠榔DS.1510_AMP_A | 太鐵糠榔一路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 101 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1520_AMP | 太鐵糠榔二路 | [27 empty] | ADCS_N | [8 empty] | 糠榔DS.1520_AMP_A | 太鐵糠榔二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 102 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D19 | 槺榔DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PERM | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | D19//1DTR(A)/TR_PERM |  | DTR_PERM |  |  | 103 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D19 | 槺榔DS | 0 |  | 1DTR(B) | #1DTR(B) |  | PERM | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.#1DTR(B)_PERM | #1DTR(B) TAP PERMISSION POINT | MTR | D19//1DTR(B)/TR_PERM |  | DTR_PERM |  |  | 104 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D19 | 槺榔DS | 0 |  | 2DTR | #2DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.#2DTR_PERM | #2DTR TAP PERMISSION POINT | MTR | D19//2DTR/TR_PERM |  | DTR_PERM |  |  | 105 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D19 | 槺榔DS | 0 |  | 3DTR | #3DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.#3DTR_PERM | #3DTR TAP PERMISSION POINT | MTR | D19//3DTR/TR_PERM |  | DTR_PERM |  |  | 106 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D19 | 槺榔DS | 0 |  | 1DTR_MVA | #1DTR | [27 empty] | ADCS_N | [8 empty] | 糠榔DS.#1DTR_MVA_A | #1DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 107 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D19 | 槺榔DS | 0 |  | 1DTR_MVA | #1DTR(A) | [27 empty] | DDCS2_2 | [8 empty] | 糠榔DS.#1DTR_MVA_2 | #1DTR(A) MVA 點燈 (D2) | MTR |  |  | MAP_SET |  |  | 108 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
D19 | 槺榔DS | 0 |  | 1DTR_MVA | #1DTR(B) |  | 3 | [25 empty] | DDCS2_2 | [8 empty] | 糠榔DS.#1DTR_MVA_3 | #1DTR(B) MVA 點燈 (D2) | MTR |  |  | MAP_SET |  |  | 109 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D19 | 槺榔DS | 0 |  | 2DTR_MVA | #2DTR | [27 empty] | ADCS_N | [8 empty] | 糠榔DS.#2DTR_MVA_A | #2DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 110 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D19 | 槺榔DS | 0 |  | 2DTR_MVA | #2DTR | [27 empty] | DDCS2_2 | [8 empty] | 糠榔DS.#2DTR_MVA_2 | #2DTR MVA 點燈 (D2) | MTR |  |  | AD_LAMP_DD_2 |  |  | 111 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
D19 | 槺榔DS | 0 |  | 3DTR_MVA | #3DTR | [27 empty] | ADCS_N | [8 empty] | 糠榔DS.#3DTR_MVA_A | #3DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 112 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D19 | 槺榔DS | 0 |  | 3DTR_MVA | #3DTR | [27 empty] | DDCS2_2 | [8 empty] | 糠榔DS.#3DTR_MVA_2 | #3DTR MVA 點燈 (D2) | MTR |  |  | AD_LAMP_DD_2 |  |  | 113 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
D19 | 槺榔DS | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_DS |  |  | 114 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | TAP_OVER | TAP |  | SET | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.TAP_OVER_SET | TAP OVER HI/LO ALARM | MTR |  |  | 5000_CB_T4 |  |  | 115 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D19 | 槺榔DS | 0 |  | BUS_OVER | BUS |  | SET | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.BUS_OVER_SET | BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B4 |  |  | 116 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D19 | 槺榔DS | 0 |  | 5000 | 虛擬5000 |  | CB動作 | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.5000_CB動作 | 虛擬5000 CB動作,請查明原因處理 | MTR |  |  | 5000_CB_M |  |  | 117 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | 1ABUS | #1ABUS |  | 11KV#1ABUSC | [25 empty] | CDCS | [8 empty] | 糠榔DS.11KV#1ABUSC | #1ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 118 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D19 | 槺榔DS | 0 |  | 1BBUS | #1BBUS |  | 11KV#1BBUSC | [25 empty] | CDCS | [8 empty] | 糠榔DS.11KV#1BBUSC | #1BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 119 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D19 | 槺榔DS | 0 |  | 2BUS | #2BUS |  | 23KV#2BUSC | [25 empty] | CDCS | [8 empty] | 糠榔DS.23KV#2BUSC | #2BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 120 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D19 | 槺榔DS | 0 |  | 3BUS | #3BUS |  | 23KV#3BUSC | [25 empty] | CDCS | [8 empty] | 糠榔DS.23KV#3BUSC | #3BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 121 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D19 | 槺榔DS | 0 |  | 注意OLTC | 注意OLTC |  | BUS電壓異常 | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.BUS電壓異常 | 注意OLTC Tap位置,並將RPDC閉鎖 | OTHER |  |  | STATION_FAULT_2 |  |  | 122 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1BUS | #1BUS |  | V | [14 empty] | 0064 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | D19/161/1BUS/V |  |  |  | DNP | 123 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D19 | 槺榔DS | 161 | 161kV | 2BUS | #2BUS |  | V | [14 empty] | 0065 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | D19/161/2BUS/V |  |  |  | DNP | 124 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D19 | 槺榔DS | 11 | 11kV | 1ABUS | #1ABUS |  | V | [14 empty] | 0088 | [8 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.11KV#1ABUS_KV | 11KV #1ABUS KV | BUS | D19/11/1ABUS/V |  |  |  | DNP | 125 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D19 | 槺榔DS | 11 | 11kV | 1BBUS | #1BBUS |  | V | [14 empty] | 0122 | [8 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.11KV#1BBUS_KV | 11KV #1BBUS KV | BUS | D19/11/1BBUS/V |  |  |  | DNP | 126 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D19 | 槺榔DS | 22 | 22kV | 2BUS | #2BUS |  | V | [14 empty] | 0153 | [8 empty] | kV_-18_18(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.23KV#2BUS_KV | 23KV #2BUS KV | BUS | D19/11/2BUS/V |  |  |  | DNP | 127 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D19 | 槺榔DS | 22 | 22kV | 3BUS | #3BUS |  | V | [14 empty] | 0199 | [8 empty] | kV_-18_18(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.23KV#3BUS_KV | 23KV #3BUS KV | BUS | D19/11/3BUS/V |  |  |  | DNP | 128 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D19 | 槺榔DS | 161 | 161kV | 1510 | 太鐵糠榔一路(1510) |  | MW | [14 empty] | 0066 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.1510_MW | 太鐵糠榔一路 MW | LINE161 | D19/161/1510/MW |  |  |  | DNP | 129 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D19 | 槺榔DS | 161 | 161kV | 1510 | 太鐵糠榔一路(1510) |  | MVAR | [14 empty] | 0067 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.1510_MVAR | 太鐵糠榔一路 MVAR | LINE161 | D19/161/1510/MVAR |  |  |  | DNP | 130 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D19 | 槺榔DS | 161 | 161kV | 1520 | 太鐵糠榔二路(1520) |  | MW | [14 empty] | 0068 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.1520_MW | 太鐵糠榔二路 MW | LINE161 | D19/161/1520/MW |  |  |  | DNP | 131 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D19 | 槺榔DS | 161 | 161kV | 1520 | 太鐵糠榔二路(1520) |  | MVAR | [14 empty] | 0069 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.1520_MVAR | 太鐵糠榔二路 MVAR | LINE161 | D19/161/1520/MVAR |  |  |  | DNP | 132 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠21線 | 糠21線 |  | 糠21線KVAR | [14 empty] | 0089 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠21線KVAR | 11KV糠21線 KVAR | FEEDER | D19/11/JO21/KVAR |  |  |  | DNP | 133 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠21線 | 糠21線 |  | 糠21線A1 | [14 empty] | 0090 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠21線A1 | 11KV糠21線 R相AMP | FEEDER | D19/11/JO21/I_R |  |  |  | DNP | 134 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠21線 | 糠21線 |  | 糠21線A2 | [14 empty] | 0091 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠21線A2 | 11KV糠21線 S相AMP | FEEDER | D19/11/JO21/I_S |  |  |  | DNP | 135 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠21線 | 糠21線 |  | 糠21線A3 | [14 empty] | 0092 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠21線A3 | 11KV糠21線 T相AMP | FEEDER | D19/11/JO21/I_T |  |  |  | DNP | 136 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠21線 | 糠21線 |  | 糠21線A0 | [14 empty] | 0093 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠21線A0 | 11KV糠21線 N相AMP | FEEDER | D19/11/JO21/I_N |  |  |  | DNP | 137 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠22線 | 糠22線 |  | 糠22線KVAR | [14 empty] | 0094 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠22線KVAR | 11KV糠22線 KVAR | FEEDER | D19/11/JO22/KVAR |  |  |  | DNP | 138 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠22線 | 糠22線 |  | 糠22線A1 | [14 empty] | 0095 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠22線A1 | 11KV糠22線 R相AMP | FEEDER | D19/11/JO22/I_R |  |  |  | DNP | 139 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠22線 | 糠22線 |  | 糠22線A2 | [14 empty] | 0096 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠22線A2 | 11KV糠22線 S相AMP | FEEDER | D19/11/JO22/I_S |  |  |  | DNP | 140 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠22線 | 糠22線 |  | 糠22線A3 | [14 empty] | 0097 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠22線A3 | 11KV糠22線 T相AMP | FEEDER | D19/11/JO22/I_T |  |  |  | DNP | 141 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠22線 | 糠22線 |  | 糠22線A0 | [14 empty] | 0098 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠22線A0 | 11KV糠22線 N相AMP | FEEDER | D19/11/JO22/I_N |  |  |  | DNP | 142 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠23線 | 糠23線 |  | 糠23線KVAR | [14 empty] | 0099 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠23線KVAR | 11KV糠23線 KVAR | FEEDER | D19/11/JO23/KVAR |  |  |  | DNP | 143 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠23線 | 糠23線 |  | 糠23線A1 | [14 empty] | 0100 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠23線A1 | 11KV糠23線 R相AMP | FEEDER | D19/11/JO23/I_R |  |  |  | DNP | 144 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠23線 | 糠23線 |  | 糠23線A2 | [14 empty] | 0101 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠23線A2 | 11KV糠23線 S相AMP | FEEDER | D19/11/JO23/I_S |  |  |  | DNP | 145 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠23線 | 糠23線 |  | 糠23線A3 | [14 empty] | 0102 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠23線A3 | 11KV糠23線 T相AMP | FEEDER | D19/11/JO23/I_T |  |  |  | DNP | 146 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠23線 | 糠23線 |  | 糠23線A0 | [14 empty] | 0103 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠23線A0 | 11KV糠23線 N相AMP | FEEDER | D19/11/JO23/I_N |  |  |  | DNP | 147 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠24線 | 糠24線 |  | 糠24線KVAR | [14 empty] | 0104 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠24線KVAR | 11KV糠24線 KVAR | FEEDER | D19/11/JO24/KVAR |  |  |  | DNP | 148 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠24線 | 糠24線 |  | 糠24線A1 | [14 empty] | 0105 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠24線A1 | 11KV糠24線 R相AMP | FEEDER | D19/11/JO24/I_R |  |  |  | DNP | 149 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠24線 | 糠24線 |  | 糠24線A2 | [14 empty] | 0106 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠24線A2 | 11KV糠24線 S相AMP | FEEDER | D19/11/JO24/I_S |  |  |  | DNP | 150 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠24線 | 糠24線 |  | 糠24線A3 | [14 empty] | 0107 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠24線A3 | 11KV糠24線 T相AMP | FEEDER | D19/11/JO24/I_T |  |  |  | DNP | 151 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠24線 | 糠24線 |  | 糠24線A0 | [14 empty] | 0108 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠24線A0 | 11KV糠24線 N相AMP | FEEDER | D19/11/JO24/I_N |  |  |  | DNP | 152 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠25線 | 糠25線 |  | 糠25線KVAR | [14 empty] | 0109 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠25線KVAR | 11KV糠25線 KVAR | FEEDER | D19/11/JO25/KVAR |  |  |  | DNP | 153 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠25線 | 糠25線 |  | 糠25線A1 | [14 empty] | 0110 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠25線A1 | 11KV糠25線 R相AMP | FEEDER | D19/11/JO25/I_R |  |  |  | DNP | 154 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠25線 | 糠25線 |  | 糠25線A2 | [14 empty] | 0111 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠25線A2 | 11KV糠25線 S相AMP | FEEDER | D19/11/JO25/I_S |  |  |  | DNP | 155 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠25線 | 糠25線 |  | 糠25線A3 | [14 empty] | 0112 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠25線A3 | 11KV糠25線 T相AMP | FEEDER | D19/11/JO25/I_T |  |  |  | DNP | 156 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠25線 | 糠25線 |  | 糠25線A0 | [14 empty] | 0113 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠25線A0 | 11KV糠25線 N相AMP | FEEDER | D19/11/JO25/I_N |  |  |  | DNP | 157 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠26線 | 糠26線 |  | 糠26線KVAR | [14 empty] | 0123 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠26線KVAR | 11KV糠26線 KVAR | FEEDER | D19/11/JO26/KVAR |  |  |  | DNP | 158 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠26線 | 糠26線 |  | 糠26線A1 | [14 empty] | 0124 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠26線A1 | 11KV糠26線 R相AMP | FEEDER | D19/11/JO26/I_R |  |  |  | DNP | 159 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠26線 | 糠26線 |  | 糠26線A2 | [14 empty] | 0125 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠26線A2 | 11KV糠26線 S相AMP | FEEDER | D19/11/JO26/I_S |  |  |  | DNP | 160 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠26線 | 糠26線 |  | 糠26線A3 | [14 empty] | 0126 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠26線A3 | 11KV糠26線 T相AMP | FEEDER | D19/11/JO26/I_T |  |  |  | DNP | 161 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠26線 | 糠26線 |  | 糠26線A0 | [14 empty] | 0127 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠26線A0 | 11KV糠26線 N相AMP | FEEDER | D19/11/JO26/I_N |  |  |  | DNP | 162 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠27線 | 糠27線 |  | 糠27線KVAR | [14 empty] | 0128 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠27線KVAR | 11KV糠27線 KVAR | FEEDER | D19/11/JO27/KVAR |  |  |  | DNP | 163 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠27線 | 糠27線 |  | 糠27線A1 | [14 empty] | 0129 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠27線A1 | 11KV糠27線 R相AMP | FEEDER | D19/11/JO27/I_R |  |  |  | DNP | 164 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠27線 | 糠27線 |  | 糠27線A2 | [14 empty] | 0130 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠27線A2 | 11KV糠27線 S相AMP | FEEDER | D19/11/JO27/I_S |  |  |  | DNP | 165 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠27線 | 糠27線 |  | 糠27線A3 | [14 empty] | 0131 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠27線A3 | 11KV糠27線 T相AMP | FEEDER | D19/11/JO27/I_T |  |  |  | DNP | 166 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠27線 | 糠27線 |  | 糠27線A0 | [14 empty] | 0132 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠27線A0 | 11KV糠27線 N相AMP | FEEDER | D19/11/JO27/I_N |  |  |  | DNP | 167 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠28線 | 糠28線 |  | 糠28線KVAR | [14 empty] | 0133 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠28線KVAR | 11KV糠28線 KVAR | FEEDER | D19/11/JO28/KVAR |  |  |  | DNP | 168 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠28線 | 糠28線 |  | 糠28線A1 | [14 empty] | 0134 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠28線A1 | 11KV糠28線 R相AMP | FEEDER | D19/11/JO28/I_R |  |  |  | DNP | 169 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠28線 | 糠28線 |  | 糠28線A2 | [14 empty] | 0135 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠28線A2 | 11KV糠28線 S相AMP | FEEDER | D19/11/JO28/I_S |  |  |  | DNP | 170 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠28線 | 糠28線 |  | 糠28線A3 | [14 empty] | 0136 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠28線A3 | 11KV糠28線 T相AMP | FEEDER | D19/11/JO28/I_T |  |  |  | DNP | 171 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠28線 | 糠28線 |  | 糠28線A0 | [14 empty] | 0137 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠28線A0 | 11KV糠28線 N相AMP | FEEDER | D19/11/JO28/I_N |  |  |  | DNP | 172 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠29線 | 糠29線 |  | 糠29線KVAR | [14 empty] | 0138 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠29線KVAR | 11KV糠29線 KVAR | FEEDER | D19/11/JO29/KVAR |  |  |  | DNP | 173 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠29線 | 糠29線 |  | 糠29線A1 | [14 empty] | 0139 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠29線A1 | 11KV糠29線 R相AMP | FEEDER | D19/11/JO29/I_R |  |  |  | DNP | 174 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠29線 | 糠29線 |  | 糠29線A2 | [14 empty] | 0140 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠29線A2 | 11KV糠29線 S相AMP | FEEDER | D19/11/JO29/I_S |  |  |  | DNP | 175 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠29線 | 糠29線 |  | 糠29線A3 | [14 empty] | 0141 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠29線A3 | 11KV糠29線 T相AMP | FEEDER | D19/11/JO29/I_T |  |  |  | DNP | 176 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠29線 | 糠29線 |  | 糠29線A0 | [14 empty] | 0142 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠29線A0 | 11KV糠29線 N相AMP | FEEDER | D19/11/JO29/I_N |  |  |  | DNP | 177 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠30線 | 糠30線 |  | 糠30線KVAR | [14 empty] | 0143 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠30線KVAR | 11KV糠30線 KVAR | FEEDER | D19/11/JO30/KVAR |  |  |  | DNP | 178 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠30線 | 糠30線 |  | 糠30線A1 | [14 empty] | 0144 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠30線A1 | 11KV糠30線 R相AMP | FEEDER | D19/11/JO30/I_R |  |  |  | DNP | 179 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠30線 | 糠30線 |  | 糠30線A2 | [14 empty] | 0145 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠30線A2 | 11KV糠30線 S相AMP | FEEDER | D19/11/JO30/I_S |  |  |  | DNP | 180 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠30線 | 糠30線 |  | 糠30線A3 | [14 empty] | 0146 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠30線A3 | 11KV糠30線 T相AMP | FEEDER | D19/11/JO30/I_T |  |  |  | DNP | 181 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | 糠30線 | 糠30線 |  | 糠30線A0 | [14 empty] | 0147 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠30線A0 | 11KV糠30線 N相AMP | FEEDER | D19/11/JO30/I_N |  |  |  | DNP | 182 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠61線 | 糠61線 |  | 糠61線KVAR | [14 empty] | 0154 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠61線KVAR | 23KV糠61線 KVAR | FEEDER | D19/22/JO61/KVAR |  |  |  | DNP | 183 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠61線 | 糠61線 |  | 糠61線A1 | [14 empty] | 0155 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠61線A1 | 23KV糠61線 R相AMP | FEEDER | D19/22/JO61/I_R |  |  |  | DNP | 184 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠61線 | 糠61線 |  | 糠61線A2 | [14 empty] | 0156 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠61線A2 | 23KV糠61線 S相AMP | FEEDER | D19/22/JO61/I_S |  |  |  | DNP | 185 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠61線 | 糠61線 |  | 糠61線A3 | [14 empty] | 0157 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠61線A3 | 23KV糠61線 T相AMP | FEEDER | D19/22/JO61/I_T |  |  |  | DNP | 186 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠61線 | 糠61線 |  | 糠61線A0 | [14 empty] | 0158 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠61線A0 | 23KV糠61線 N相AMP | FEEDER | D19/22/JO61/I_N |  |  |  | DNP | 187 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠62線 | 糠62線 |  | 糠62線KVAR | [14 empty] | 0159 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠62線KVAR | 23KV糠62線 KVAR | FEEDER | D19/22/JO62/KVAR |  |  |  | DNP | 188 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠62線 | 糠62線 |  | 糠62線A1 | [14 empty] | 0160 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠62線A1 | 23KV糠62線 R相AMP | FEEDER | D19/22/JO62/I_R |  |  |  | DNP | 189 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠62線 | 糠62線 |  | 糠62線A2 | [14 empty] | 0161 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠62線A2 | 23KV糠62線 S相AMP | FEEDER | D19/22/JO62/I_S |  |  |  | DNP | 190 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠62線 | 糠62線 |  | 糠62線A3 | [14 empty] | 0162 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠62線A3 | 23KV糠62線 T相AMP | FEEDER | D19/22/JO62/I_T |  |  |  | DNP | 191 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠62線 | 糠62線 |  | 糠62線A0 | [14 empty] | 0163 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠62線A0 | 23KV糠62線 N相AMP | FEEDER | D19/22/JO62/I_N |  |  |  | DNP | 192 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠63線 | 糠63線 |  | 糠63線KVAR | [14 empty] | 0164 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠63線KVAR | 23KV糠63線 KVAR | FEEDER | D19/22/JO63/KVAR |  |  |  | DNP | 193 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠63線 | 糠63線 |  | 糠63線A1 | [14 empty] | 0165 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠63線A1 | 23KV糠63線 R相AMP | FEEDER | D19/22/JO63/I_R |  |  |  | DNP | 194 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠63線 | 糠63線 |  | 糠63線A2 | [14 empty] | 0166 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠63線A2 | 23KV糠63線 S相AMP | FEEDER | D19/22/JO63/I_S |  |  |  | DNP | 195 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠63線 | 糠63線 |  | 糠63線A3 | [14 empty] | 0167 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠63線A3 | 23KV糠63線 T相AMP | FEEDER | D19/22/JO63/I_T |  |  |  | DNP | 196 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠63線 | 糠63線 |  | 糠63線A0 | [14 empty] | 0168 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠63線A0 | 23KV糠63線 N相AMP | FEEDER | D19/22/JO63/I_N |  |  |  | DNP | 197 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠64線 | 糠64線 |  | 糠64線KVAR | [14 empty] | 0169 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠64線KVAR | 23KV糠64線 KVAR | FEEDER | D19/22/JO64/KVAR |  |  |  | DNP | 198 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠64線 | 糠64線 |  | 糠64線A1 | [14 empty] | 0170 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠64線A1 | 23KV糠64線 R相AMP | FEEDER | D19/22/JO64/I_R |  |  |  | DNP | 199 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠64線 | 糠64線 |  | 糠64線A2 | [14 empty] | 0171 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠64線A2 | 23KV糠64線 S相AMP | FEEDER | D19/22/JO64/I_S |  |  |  | DNP | 200 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠64線 | 糠64線 |  | 糠64線A3 | [14 empty] | 0172 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠64線A3 | 23KV糠64線 T相AMP | FEEDER | D19/22/JO64/I_T |  |  |  | DNP | 201 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠64線 | 糠64線 |  | 糠64線A0 | [14 empty] | 0173 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠64線A0 | 23KV糠64線 N相AMP | FEEDER | D19/22/JO64/I_N |  |  |  | DNP | 202 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠65線 | 糠65線 |  | 糠65線KVAR | [14 empty] | 0174 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠65線KVAR | 23KV糠65線 KVAR | FEEDER | D19/22/JO65/KVAR |  |  |  | DNP | 203 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠65線 | 糠65線 |  | 糠65線A1 | [14 empty] | 0175 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠65線A1 | 23KV糠65線 R相AMP | FEEDER | D19/22/JO65/I_R |  |  |  | DNP | 204 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠65線 | 糠65線 |  | 糠65線A2 | [14 empty] | 0176 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠65線A2 | 23KV糠65線 S相AMP | FEEDER | D19/22/JO65/I_S |  |  |  | DNP | 205 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠65線 | 糠65線 |  | 糠65線A3 | [14 empty] | 0177 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠65線A3 | 23KV糠65線 T相AMP | FEEDER | D19/22/JO65/I_T |  |  |  | DNP | 206 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠65線 | 糠65線 |  | 糠65線A0 | [14 empty] | 0178 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠65線A0 | 23KV糠65線 N相AMP | FEEDER | D19/22/JO65/I_N |  |  |  | DNP | 207 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠66線 | 糠66線 |  | 糠66線KVAR | [14 empty] | 0179 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠66線KVAR | 23KV糠66線 KVAR | FEEDER | D19/22/JO66/KVAR |  |  |  | DNP | 208 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠66線 | 糠66線 |  | 糠66線A1 | [14 empty] | 0180 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠66線A1 | 23KV糠66線 R相AMP | FEEDER | D19/22/JO66/I_R |  |  |  | DNP | 209 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠66線 | 糠66線 |  | 糠66線A2 | [14 empty] | 0181 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠66線A2 | 23KV糠66線 S相AMP | FEEDER | D19/22/JO66/I_S |  |  |  | DNP | 210 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠66線 | 糠66線 |  | 糠66線A3 | [14 empty] | 0182 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠66線A3 | 23KV糠66線 T相AMP | FEEDER | D19/22/JO66/I_T |  |  |  | DNP | 211 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠66線 | 糠66線 |  | 糠66線A0 | [14 empty] | 0183 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠66線A0 | 23KV糠66線 N相AMP | FEEDER | D19/22/JO66/I_N |  |  |  | DNP | 212 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠67線 | 糠67線 |  | 糠67線KVAR | [14 empty] | 0184 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠67線KVAR | 23KV糠67線 KVAR | FEEDER | D19/22/JO67/KVAR |  |  |  | DNP | 213 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠67線 | 糠67線 |  | 糠67線A1 | [14 empty] | 0185 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠67線A1 | 23KV糠67線 R相AMP | FEEDER | D19/22/JO67/I_R |  |  |  | DNP | 214 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠67線 | 糠67線 |  | 糠67線A2 | [14 empty] | 0186 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠67線A2 | 23KV糠67線 S相AMP | FEEDER | D19/22/JO67/I_S |  |  |  | DNP | 215 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠67線 | 糠67線 |  | 糠67線A3 | [14 empty] | 0187 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠67線A3 | 23KV糠67線 T相AMP | FEEDER | D19/22/JO67/I_T |  |  |  | DNP | 216 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠67線 | 糠67線 |  | 糠67線A0 | [14 empty] | 0188 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠67線A0 | 23KV糠67線 N相AMP | FEEDER | D19/22/JO67/I_N |  |  |  | DNP | 217 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠68線 | 糠68線 |  | 糠68線KVAR | [14 empty] | 0189 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠68線KVAR | 23KV糠68線 KVAR | FEEDER | D19/22/JO68/KVAR |  |  |  | DNP | 218 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠68線 | 糠68線 |  | 糠68線A1 | [14 empty] | 0190 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠68線A1 | 23KV糠68線 R相AMP | FEEDER | D19/22/JO68/I_R |  |  |  | DNP | 219 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠68線 | 糠68線 |  | 糠68線A2 | [14 empty] | 0191 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠68線A2 | 23KV糠68線 S相AMP | FEEDER | D19/22/JO68/I_S |  |  |  | DNP | 220 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠68線 | 糠68線 |  | 糠68線A3 | [14 empty] | 0192 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠68線A3 | 23KV糠68線 T相AMP | FEEDER | D19/22/JO68/I_T |  |  |  | DNP | 221 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠68線 | 糠68線 |  | 糠68線A0 | [14 empty] | 0193 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠68線A0 | 23KV糠68線 N相AMP | FEEDER | D19/22/JO68/I_N |  |  |  | DNP | 222 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠71線 | 糠71線 |  | 糠71線KVAR | [14 empty] | 0200 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠71線KVAR | 23KV糠71線 KVAR | FEEDER | D19/22/JO71/KVAR |  |  |  | DNP | 223 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠71線 | 糠71線 |  | 糠71線A1 | [14 empty] | 0201 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠71線A1 | 23KV糠71線 R相AMP | FEEDER | D19/22/JO71/I_R |  |  |  | DNP | 224 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠71線 | 糠71線 |  | 糠71線A2 | [14 empty] | 0202 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠71線A2 | 23KV糠71線 S相AMP | FEEDER | D19/22/JO71/I_S |  |  |  | DNP | 225 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠71線 | 糠71線 |  | 糠71線A3 | [14 empty] | 0203 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠71線A3 | 23KV糠71線 T相AMP | FEEDER | D19/22/JO71/I_T |  |  |  | DNP | 226 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠71線 | 糠71線 |  | 糠71線A0 | [14 empty] | 0204 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠71線A0 | 23KV糠71線 N相AMP | FEEDER | D19/22/JO71/I_N |  |  |  | DNP | 227 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠72線 | 糠72線 |  | 糠72線KVAR | [14 empty] | 0205 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠72線KVAR | 23KV糠72線 KVAR | FEEDER | D19/22/JO72/KVAR |  |  |  | DNP | 228 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠72線 | 糠72線 |  | 糠72線A1 | [14 empty] | 0206 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠72線A1 | 23KV糠72線 R相AMP | FEEDER | D19/22/JO72/I_R |  |  |  | DNP | 229 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠72線 | 糠72線 |  | 糠72線A2 | [14 empty] | 0207 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠72線A2 | 23KV糠72線 S相AMP | FEEDER | D19/22/JO72/I_S |  |  |  | DNP | 230 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠72線 | 糠72線 |  | 糠72線A3 | [14 empty] | 0208 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠72線A3 | 23KV糠72線 T相AMP | FEEDER | D19/22/JO72/I_T |  |  |  | DNP | 231 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠72線 | 糠72線 |  | 糠72線A0 | [14 empty] | 0209 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠72線A0 | 23KV糠72線 N相AMP | FEEDER | D19/22/JO72/I_N |  |  |  | DNP | 232 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠73線 | 糠73線 |  | 糠73線KVAR | [14 empty] | 0210 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠73線KVAR | 23KV糠73線 KVAR | FEEDER | D19/22/JO73/KVAR |  |  |  | DNP | 233 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠73線 | 糠73線 |  | 糠73線A1 | [14 empty] | 0211 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠73線A1 | 23KV糠73線 R相AMP | FEEDER | D19/22/JO73/I_R |  |  |  | DNP | 234 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠73線 | 糠73線 |  | 糠73線A2 | [14 empty] | 0212 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠73線A2 | 23KV糠73線 S相AMP | FEEDER | D19/22/JO73/I_S |  |  |  | DNP | 235 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠73線 | 糠73線 |  | 糠73線A3 | [14 empty] | 0213 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠73線A3 | 23KV糠73線 T相AMP | FEEDER | D19/22/JO73/I_T |  |  |  | DNP | 236 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠73線 | 糠73線 |  | 糠73線A0 | [14 empty] | 0214 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠73線A0 | 23KV糠73線 N相AMP | FEEDER | D19/22/JO73/I_N |  |  |  | DNP | 237 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠74線 | 糠74線 |  | 糠74線KVAR | [14 empty] | 0215 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠74線KVAR | 23KV糠74線 KVAR | FEEDER | D19/22/JO74/KVAR |  |  |  | DNP | 238 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠74線 | 糠74線 |  | 糠74線A1 | [14 empty] | 0216 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠74線A1 | 23KV糠74線 R相AMP | FEEDER | D19/22/JO74/I_R |  |  |  | DNP | 239 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠74線 | 糠74線 |  | 糠74線A2 | [14 empty] | 0217 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠74線A2 | 23KV糠74線 S相AMP | FEEDER | D19/22/JO74/I_S |  |  |  | DNP | 240 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠74線 | 糠74線 |  | 糠74線A3 | [14 empty] | 0218 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠74線A3 | 23KV糠74線 T相AMP | FEEDER | D19/22/JO74/I_T |  |  |  | DNP | 241 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠74線 | 糠74線 |  | 糠74線A0 | [14 empty] | 0219 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠74線A0 | 23KV糠74線 N相AMP | FEEDER | D19/22/JO74/I_N |  |  |  | DNP | 242 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠75線 | 糠75線 |  | 糠75線KVAR | [14 empty] | 0220 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠75線KVAR | 23KV糠75線 KVAR | FEEDER | D19/22/JO75/KVAR |  |  |  | DNP | 243 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠75線 | 糠75線 |  | 糠75線A1 | [14 empty] | 0221 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠75線A1 | 23KV糠75線 R相AMP | FEEDER | D19/22/JO75/I_R |  |  |  | DNP | 244 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠75線 | 糠75線 |  | 糠75線A2 | [14 empty] | 0222 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠75線A2 | 23KV糠75線 S相AMP | FEEDER | D19/22/JO75/I_S |  |  |  | DNP | 245 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠75線 | 糠75線 |  | 糠75線A3 | [14 empty] | 0223 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠75線A3 | 23KV糠75線 T相AMP | FEEDER | D19/22/JO75/I_T |  |  |  | DNP | 246 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠75線 | 糠75線 |  | 糠75線A0 | [14 empty] | 0224 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠75線A0 | 23KV糠75線 N相AMP | FEEDER | D19/22/JO75/I_N |  |  |  | DNP | 247 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠76線 | 糠76線 |  | 糠76線KVAR | [14 empty] | 0225 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠76線KVAR | 23KV糠76線 KVAR | FEEDER | D19/22/JO76/KVAR |  |  |  | DNP | 248 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠76線 | 糠76線 |  | 糠76線A1 | [14 empty] | 0226 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠76線A1 | 23KV糠76線 R相AMP | FEEDER | D19/22/JO76/I_R |  |  |  | DNP | 249 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠76線 | 糠76線 |  | 糠76線A2 | [14 empty] | 0227 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠76線A2 | 23KV糠76線 S相AMP | FEEDER | D19/22/JO76/I_S |  |  |  | DNP | 250 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠76線 | 糠76線 |  | 糠76線A3 | [14 empty] | 0228 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠76線A3 | 23KV糠76線 T相AMP | FEEDER | D19/22/JO76/I_T |  |  |  | DNP | 251 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠76線 | 糠76線 |  | 糠76線A0 | [14 empty] | 0229 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠76線A0 | 23KV糠76線 N相AMP | FEEDER | D19/22/JO76/I_N |  |  |  | DNP | 252 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠77線 | 糠77線 |  | 糠77線KVAR | [14 empty] | 0230 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠77線KVAR | 23KV糠77線 KVAR | FEEDER | D19/22/JO77/KVAR |  |  |  | DNP | 253 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠77線 | 糠77線 |  | 糠77線A1 | [14 empty] | 0231 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠77線A1 | 23KV糠77線 R相AMP | FEEDER | D19/22/JO77/I_R |  |  |  | DNP | 254 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠77線 | 糠77線 |  | 糠77線A2 | [14 empty] | 0232 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠77線A2 | 23KV糠77線 S相AMP | FEEDER | D19/22/JO77/I_S |  |  |  | DNP | 255 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠77線 | 糠77線 |  | 糠77線A3 | [14 empty] | 0233 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠77線A3 | 23KV糠77線 T相AMP | FEEDER | D19/22/JO77/I_T |  |  |  | DNP | 256 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠77線 | 糠77線 |  | 糠77線A0 | [14 empty] | 0234 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠77線A0 | 23KV糠77線 N相AMP | FEEDER | D19/22/JO77/I_N |  |  |  | DNP | 257 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠78線 | 糠78線 |  | 糠78線KVAR | [14 empty] | 0235 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠78線KVAR | 23KV糠78線 KVAR | FEEDER | D19/22/JO78/KVAR |  |  |  | DNP | 258 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠78線 | 糠78線 |  | 糠78線A1 | [14 empty] | 0236 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠78線A1 | 23KV糠78線 R相AMP | FEEDER | D19/22/JO78/I_R |  |  |  | DNP | 259 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠78線 | 糠78線 |  | 糠78線A2 | [14 empty] | 0237 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠78線A2 | 23KV糠78線 S相AMP | FEEDER | D19/22/JO78/I_S |  |  |  | DNP | 260 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠78線 | 糠78線 |  | 糠78線A3 | [14 empty] | 0238 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠78線A3 | 23KV糠78線 T相AMP | FEEDER | D19/22/JO78/I_T |  |  |  | DNP | 261 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | 糠78線 | 糠78線 |  | 糠78線A0 | [14 empty] | 0239 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS2_2 | [8 empty] | 糠榔DS.糠78線A0 | 23KV糠78線 N相AMP | FEEDER | D19/22/JO78/I_N |  |  |  | DNP | 262 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 0 |  | 1500TIE | 1500TIE |  | I | [14 empty] | 0082 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.1500TIE_AMP | 1500TIE AMP | TIE | D19/161/1500/I_R |  |  |  | DNP | 263 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | _100 | 100 |  | I_R | [14 empty] | 0114 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.11KV_100_A1 | 11KV 100 R相AMP | TIE | D19/11/100/I_R |  |  |  | DNP | 264 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | _100 | 100 |  | I_S | [14 empty] | 0115 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.11KV_100_A2 | 11KV 100 S相AMP | TIE | D19/11/100/I_S |  |  |  | DNP | 265 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 11 | 11kV | _100 | 100 |  | I_T | [14 empty] | 0116 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.11KV_100_A3 | 11KV 100 T相AMP | TIE | D19/11/100/I_T |  |  |  | DNP | 266 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | _200 | 200 |  | I_R | [14 empty] | 0240 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.23KV_200_A1 | 23KV 200 R相AMP | TIE | D19/22/200/I_R |  |  |  | DNP | 267 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | _200 | 200 |  | I_S | [14 empty] | 0241 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.23KV_200_A2 | 23KV 200 S相AMP | TIE | D19/22/200/I_S |  |  |  | DNP | 268 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 22 | 22kV | _200 | 200 |  | I_T | [14 empty] | 0242 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.23KV_200_A3 | 23KV 200 T相AMP | TIE | D19/22/200/I_T |  |  |  | DNP | 269 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MW | [14 empty] | 0083 | [8 empty] | MW_-54_54(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | D19/11/310/KW |  |  |  | DNP | 270 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.054000 | 0.010000
D19 | 槺榔DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVAR | [14 empty] | 0084 | [8 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | D19/11/310/KVAR |  |  |  | DNP | 271 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.036000 | 0.010000
D19 | 槺榔DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_R | [14 empty] | 0085 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | D19/11/310/I_R |  |  |  | DNP | 272 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_S | [14 empty] | 0086 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | D19/11/310/I_S |  |  |  | DNP | 273 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_T | [14 empty] | 0087 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | D19/11/310/I_T |  |  |  | DNP | 274 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 0 |  | 1DTR | #1DTR |  | OilTemp | [14 empty] | 0002 | [8 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.#1DTR_OIL | #1DTR 油溫 | MTR | D19//1DTR/OilTemp |  |  |  | DNP | 275 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D19 | 槺榔DS | 0 |  | 1DTR(A) | #1DTR(A) |  | CoilTemp | [14 empty] | 0003 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | D19//1DTR(A)/CoilTemp |  |  |  | DNP | 276 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D19 | 槺榔DS | 0 |  | 1DTR(A) | #1DTR(A) |  | TapPosMv | [14 empty] | 0005 |  | 0057 | [6 empty] | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 糠榔DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | D19//1DTR(A)/TapPosMv |  |  |  | DNP | 277 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D19 | 槺榔DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MW | [14 empty] | 0117 | [8 empty] | MW_-54_54(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | D19/11/320/KW |  |  |  | DNP | 278 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.054000 | 0.010000
D19 | 槺榔DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVAR | [14 empty] | 0118 | [8 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | D19/11/320/KVAR |  |  |  | DNP | 279 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.036000 | 0.010000
D19 | 槺榔DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_R | [14 empty] | 0119 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | D19/11/320/I_R |  |  |  | DNP | 280 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_S | [14 empty] | 0120 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | D19/11/320/I_S |  |  |  | DNP | 281 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_T | [14 empty] | 0121 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | D19/11/320/I_T |  |  |  | DNP | 282 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 0 |  | 1DTR(B) | #1DTR(B) |  | CoilTemp | [14 empty] | 0004 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | D19//1DTR(B)/CoilTemp |  |  |  | DNP | 283 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D19 | 槺榔DS | 0 |  | 1DTR(B) | #1DTR(B) |  | TapPosMv | [14 empty] | 0006 |  | 0059 | [6 empty] | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 糠榔DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | D19//1DTR(B)/TapPosMv |  |  |  | DNP | 284 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D19 | 槺榔DS | 0 |  | 2DTR | #2DTR二次側 |  | MW | [14 empty] | 0148 | [8 empty] | MW_-108_108(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.#2DTR_MW | #2DTR二次側 MW | MTR | D19/22/330/KW |  |  |  | DNP | 285 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D19 | 槺榔DS | 0 |  | 2DTR | #2DTR二次側 |  | MVAR | [14 empty] | 0149 | [8 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.#2DTR_MVAR | #2DTR二次側 MVAR | MTR | D19/22/330/KVAR |  |  |  | DNP | 286 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D19 | 槺榔DS | 0 |  | 2DTR | #2DTR二次側 |  | I_R | [14 empty] | 0150 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.#2DTR_A1 | #2DTR二次側 R相AMP | MTR | D19/22/330/I_R |  |  |  | DNP | 287 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 0 |  | 2DTR | #2DTR二次側 |  | I_S | [14 empty] | 0151 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.#2DTR_A2 | #2DTR二次側 S相AMP | MTR | D19/22/330/I_S |  |  |  | DNP | 288 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 0 |  | 2DTR | #2DTR二次側 |  | I_T | [14 empty] | 0152 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.#2DTR_A3 | #2DTR二次側 T相AMP | MTR | D19/22/330/I_T |  |  |  | DNP | 289 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 0 |  | 2DTR | #2DTR |  | OilTemp | [14 empty] | 0007 | [8 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.#2DTR_OIL | #2DTR 油溫 | MTR | D19//2DTR/OilTemp |  |  |  | DNP | 290 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D19 | 槺榔DS | 0 |  | 2DTR | #2DTR |  | CoilTemp | [14 empty] | 0008 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.#2DTR_COIL | #2DTR 線溫 | MTR | D19//2DTR/CoilTemp |  |  |  | DNP | 291 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D19 | 槺榔DS | 0 |  | 2DTR | #2DTR |  | TapPosMv | [14 empty] | 0009 |  | 0061 | [6 empty] | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 糠榔DS.#2DTR_TAP | #2DTR OLTC TAP | MTR | D19//2DTR/TapPosMv |  |  |  | DNP | 292 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D19 | 槺榔DS | 0 |  | 3DTR | #3DTR二次側 |  | MW | [14 empty] | 0194 | [8 empty] | MW_-108_108(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.#3DTR_MW | #3DTR二次側 MW | MTR | D19/22/350/KW |  |  |  | DNP | 293 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D19 | 槺榔DS | 0 |  | 3DTR | #3DTR二次側 |  | MVAR | [14 empty] | 0195 | [8 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.#3DTR_MVAR | #3DTR二次側 MVAR | MTR | D19/22/350/KVAR |  |  |  | DNP | 294 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D19 | 槺榔DS | 0 |  | 3DTR | #3DTR二次側 |  | I_R | [14 empty] | 0196 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.#3DTR_A1 | #3DTR二次側 R相AMP | MTR | D19/22/350/I_R |  |  |  | DNP | 295 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 0 |  | 3DTR | #3DTR二次側 |  | I_S | [14 empty] | 0197 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.#3DTR_A2 | #3DTR二次側 S相AMP | MTR | D19/22/350/I_S |  |  |  | DNP | 296 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 0 |  | 3DTR | #3DTR二次側 |  | I_T | [14 empty] | 0198 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.#3DTR_A3 | #3DTR二次側 T相AMP | MTR | D19/22/350/I_T |  |  |  | DNP | 297 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D19 | 槺榔DS | 0 |  | 3DTR | #3DTR |  | OilTemp | [14 empty] | 0010 | [8 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.#3DTR_OIL | #3DTR 油溫 | MTR | D19//3DTR/OilTemp |  |  |  | DNP | 298 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D19 | 槺榔DS | 0 |  | 3DTR | #3DTR |  | CoilTemp | [14 empty] | 0011 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.#3DTR_COIL | #3DTR 線溫 | MTR | D19//3DTR/CoilTemp |  |  |  | DNP | 299 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D19 | 槺榔DS | 0 |  | 3DTR | #3DTR |  | TapPosMv | [14 empty] | 0012 |  | 0063 | [6 empty] | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 糠榔DS.#3DTR_TAP | #3DTR OLTC TAP | MTR | D19//3DTR/TapPosMv |  |  |  | DNP | 300 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D19 | 槺榔DS | 0 |  |  |  |  | DCV_N | [14 empty] | 0014 | [8 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.直流N電源電壓 | 直流N電源電壓 | OTHER | D19/0/StaDev/DCV_N |  |  |  | DNP | 301 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D19 | 槺榔DS | 0 |  |  |  |  | DCV_P | [14 empty] | 0013 | [8 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 糠榔DS.直流P電源電壓 | 直流P電源電壓 | OTHER | D19/0/StaDev/DCV_P |  |  |  | DNP | 302 | DNPAIPoint | DS057 |  |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D19 | 槺榔DS | 161 | 161kV | 1510 | 太鐵糠榔一路(1510) |  | PHA | [14 empty] | 0002 | [10 empty] | 161KV_N | [8 empty] | 糠榔DS.1510_PHA | 太鐵糠榔一路(1510) 相間RY | LINE161 | D19/161/1510/PHA |  |  |  | DNP | 303 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1510 | 太鐵糠榔一路(1510) |  | GDA | [14 empty] | 0003 | [10 empty] | 161KV_N | [8 empty] | 糠榔DS.1510_GDA | 太鐵糠榔一路(1510) 接地RY | LINE161 | D19/161/1510/GDA |  |  |  | DNP | 304 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1510 | 太鐵糠榔一路(1510) |  | 87A | [14 empty] | 0001 | [10 empty] | 161KV_N | [8 empty] | 糠榔DS.1510_87A | 太鐵糠榔一路(1510) 87RY | LINE161 | D19/161/1510/87A |  |  |  | DNP | 305 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1510 | 太鐵糠榔一路(1510) |  | 87UL | [14 empty] | 0514 |  | 0024 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.1510_87UL | 太鐵糠榔一路(1510) 87RY U/L | LINE161 | D19/161/1510/87UL |  |  |  | DNP | 306 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 161 | 161kV | 1510 | 太鐵糠榔一路(1510) |  | CB | [14 empty] | 0000 |  | 0001 | [8 empty] | 161KV_N | [8 empty] | 糠榔DS.1510_CB | 1510(太鐵糠榔一路) CB | LINE161 | D19/161/1510/CB |  |  |  | DNP | 307 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 161 | 161kV | 1510 | 太鐵糠榔一路(1510) |  | 79UL | [14 empty] | 0515 |  | 0025 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.1510_79UL | 太鐵糠榔一路(1510) 79RY U/L | LINE161 | D19/161/1510/RCA |  |  |  | DNP | 308 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 161 | 161kV | 1510 | 太鐵糠榔一路(1510) |  | DS1 | 1511 | [13 empty] | 0612 | 613 | 0072 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.1511_DS | 1511(太鐵糠榔一路) DS | LINE161 | D19/161/1510/DS1 |  |  |  | DNP | 309 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D19 | 槺榔DS | 161 | 161kV | 1510 | 太鐵糠榔一路(1510) |  | DS2 | 1512 | [13 empty] | 0614 | 615 | 0073 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.1512_DS | 1512(太鐵糠榔一路) DS | LINE161 | D19/161/1510/DS2 |  |  |  | DNP | 310 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D19 | 槺榔DS | 161 | 161kV | 1510 | 太鐵糠榔一路(1510) |  | DS3 | 1513 | [13 empty] | 0616 | 617 | 0074 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.1513_DS | 1513(太鐵糠榔一路) DS | LINE161 | D19/161/1510/DS3 |  |  |  | DNP | 311 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D19 | 槺榔DS | 161 | 161kV | 1510 | 太鐵糠榔一路(1510) |  | E3 | 1513E | [13 empty] | 0618 | 619 | 0075 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.1513E_ES | 1513E(太鐵糠榔一路) ES | LINE161 | D19/161/1510/ES3 |  |  |  | DNP | 312 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D19 | 槺榔DS | 161 | 161kV | 1520 | 太鐵糠榔二路(1520) |  | PHA | [14 empty] | 0006 | [10 empty] | 161KV_N | [8 empty] | 糠榔DS.1520_PHA | 太鐵糠榔二路(1520) 相間RY | LINE161 | D19/161/1520/PHA |  |  |  | DNP | 313 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1520 | 太鐵糠榔二路(1520) |  | GDA | [14 empty] | 0007 | [10 empty] | 161KV_N | [8 empty] | 糠榔DS.1520_GDA | 太鐵糠榔二路(1520) 接地RY | LINE161 | D19/161/1520/GDA |  |  |  | DNP | 314 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1520 | 太鐵糠榔二路(1520) |  | 87A | [14 empty] | 0005 | [10 empty] | 161KV_N | [8 empty] | 糠榔DS.1520_87A | 太鐵糠榔二路(1520) 87RY | LINE161 | D19/161/1520/87A |  |  |  | DNP | 315 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1520 | 太鐵糠榔二路(1520) |  | 87UL | [14 empty] | 0516 |  | 0026 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.1520_87UL | 太鐵糠榔二路(1520) 87RY U/L | LINE161 | D19/161/1520/87UL |  |  |  | DNP | 316 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 161 | 161kV | 1520 | 太鐵糠榔二路(1520) |  | CB | [14 empty] | 0004 |  | 0002 | [8 empty] | 161KV_N | [8 empty] | 糠榔DS.1520_CB | 1520(太鐵糠榔二路) CB | LINE161 | D19/161/1520/CB |  |  |  | DNP | 317 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 161 | 161kV | 1520 | 太鐵糠榔二路(1520) |  | 79UL | [14 empty] | 0517 |  | 0027 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.1520_79UL | 太鐵糠榔二路(1520) 79RY U/L | LINE161 | D19/161/1520/RCA |  |  |  | DNP | 318 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 161 | 161kV | 1520 | 太鐵糠榔二路(1520) |  | DS1 | 1521 | [13 empty] | 0620 | 621 | 0076 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.1521_DS | 1521(太鐵糠榔二路) DS | LINE161 | D19/161/1520/DS1 |  |  |  | DNP | 319 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D19 | 槺榔DS | 161 | 161kV | 1520 | 太鐵糠榔二路(1520) |  | DS2 | 1522 | [13 empty] | 0622 | 623 | 0077 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.1522_DS | 1522(太鐵糠榔二路) DS | LINE161 | D19/161/1520/DS2 |  |  |  | DNP | 320 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D19 | 槺榔DS | 161 | 161kV | 1520 | 太鐵糠榔二路(1520) |  | DS3 | 1523 | [13 empty] | 0624 | 625 | 0078 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.1523_DS | 1523(太鐵糠榔二路) DS | LINE161 | D19/161/1520/DS3 |  |  |  | DNP | 321 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D19 | 槺榔DS | 161 | 161kV | 1520 | 太鐵糠榔二路(1520) |  | E3 | 1523E | [13 empty] | 0626 | 627 | 0079 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.1523E_ES | 1523E(太鐵糠榔二路) ES | LINE161 | D19/161/1520/ES3 |  |  |  | DNP | 322 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D19 | 槺榔DS | 11 | 11kV | JO21 | 糠21線(JO21) |  | PHA | [14 empty] | 0193 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO21_PHA | 11KV糠21線(JO21) 相間RY | FEEDER | D19/11/JO21/PHA |  |  |  | DNP | 323 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO21 | 糠21線(JO21) |  | GDA | [14 empty] | 0194 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO21_GDA | 11KV糠21線(JO21) 接地RY | FEEDER | D19/11/JO21/GDA |  |  |  | DNP | 324 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO21 | 糠21線(JO21) 79RY |  | 79UL | [14 empty] | 0897 |  | 0180 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO21_79UL | 11KV糠21線(JO21) 79RY U/L | FEEDER | D19/11/JO21/FDR_RCA |  |  |  | DNP | 325 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 11 | 11kV | JO21_LCO | 糠21線(JO21) LCO |  | TapPosMv | [14 empty] | 0898 |  | 0181 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO21_LCO_TAP | 11KV糠21線(JO21) LCO TAP | FEEDER | D19/11/JO21/51NA |  |  |  | DNP | 326 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D19 | 槺榔DS | 11 | 11kV | JO21 | JO21(11KV糠21線) |  | CB | [14 empty] | 0192 |  | 0128 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO21_CB | JO21(11KV糠21線) CB | FEEDER | D19/11/JO21/CB |  |  |  | DNP | 327 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | JO22 | 糠22線(JO22) |  | PHA | [14 empty] | 0197 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO22_PHA | 11KV糠22線(JO22) 相間RY | FEEDER | D19/11/JO22/PHA |  |  |  | DNP | 328 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO22 | 糠22線(JO22) |  | GDA | [14 empty] | 0198 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO22_GDA | 11KV糠22線(JO22) 接地RY | FEEDER | D19/11/JO22/GDA |  |  |  | DNP | 329 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO22 | 糠22線(JO22) 79RY |  | 79UL | [14 empty] | 0899 |  | 0182 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO22_79UL | 11KV糠22線(JO22) 79RY U/L | FEEDER | D19/11/JO22/FDR_RCA |  |  |  | DNP | 330 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 11 | 11kV | JO22_LCO | 糠22線(JO22) LCO |  | TapPosMv | [14 empty] | 0900 |  | 0183 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO22_LCO_TAP | 11KV糠22線(JO22) LCO TAP | FEEDER | D19/11/JO22/51NA |  |  |  | DNP | 331 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D19 | 槺榔DS | 11 | 11kV | JO22 | JO22(11KV糠22線) |  | CB | [14 empty] | 0196 |  | 0129 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO22_CB | JO22(11KV糠22線) CB | FEEDER | D19/11/JO22/CB |  |  |  | DNP | 332 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | JO23 | 糠23線(JO23) |  | PHA | [14 empty] | 0201 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO23_PHA | 11KV糠23線(JO23) 相間RY | FEEDER | D19/11/JO23/PHA |  |  |  | DNP | 333 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO23 | 糠23線(JO23) |  | GDA | [14 empty] | 0202 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO23_GDA | 11KV糠23線(JO23) 接地RY | FEEDER | D19/11/JO23/GDA |  |  |  | DNP | 334 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO23 | 糠23線(JO23) 79RY |  | 79UL | [14 empty] | 0901 |  | 0184 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO23_79UL | 11KV糠23線(JO23) 79RY U/L | FEEDER | D19/11/JO23/FDR_RCA |  |  |  | DNP | 335 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 11 | 11kV | JO23_LCO | 糠23線(JO23) LCO |  | TapPosMv | [14 empty] | 0902 |  | 0185 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO23_LCO_TAP | 11KV糠23線(JO23) LCO TAP | FEEDER | D19/11/JO23/51NA |  |  |  | DNP | 336 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D19 | 槺榔DS | 11 | 11kV | JO23 | JO23(11KV糠23線) |  | CB | [14 empty] | 0200 |  | 0130 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO23_CB | JO23(11KV糠23線) CB | FEEDER | D19/11/JO23/CB |  |  |  | DNP | 337 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | JO24 | 糠24線(JO24) |  | PHA | [14 empty] | 0205 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO24_PHA | 11KV糠24線(JO24) 相間RY | FEEDER | D19/11/JO24/PHA |  |  |  | DNP | 338 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO24 | 糠24線(JO24) |  | GDA | [14 empty] | 0206 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO24_GDA | 11KV糠24線(JO24) 接地RY | FEEDER | D19/11/JO24/GDA |  |  |  | DNP | 339 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO24 | 糠24線(JO24) 79RY |  | 79UL | [14 empty] | 0903 |  | 0186 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO24_79UL | 11KV糠24線(JO24) 79RY U/L | FEEDER | D19/11/JO24/FDR_RCA |  |  |  | DNP | 340 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 11 | 11kV | JO24_LCO | 糠24線(JO24) LCO |  | TapPosMv | [14 empty] | 0904 |  | 0187 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO24_LCO_TAP | 11KV糠24線(JO24) LCO TAP | FEEDER | D19/11/JO24/51NA |  |  |  | DNP | 341 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D19 | 槺榔DS | 11 | 11kV | JO24 | JO24(11KV糠24線) |  | CB | [14 empty] | 0204 |  | 0131 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO24_CB | JO24(11KV糠24線) CB | FEEDER | D19/11/JO24/CB |  |  |  | DNP | 342 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | JO25 | 糠25線(JO25) |  | PHA | [14 empty] | 0209 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO25_PHA | 11KV糠25線(JO25) 相間RY | FEEDER | D19/11/JO25/PHA |  |  |  | DNP | 343 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO25 | 糠25線(JO25) |  | GDA | [14 empty] | 0210 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO25_GDA | 11KV糠25線(JO25) 接地RY | FEEDER | D19/11/JO25/GDA |  |  |  | DNP | 344 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO25 | 糠25線(JO25) 79RY |  | 79UL | [14 empty] | 0905 |  | 0188 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO25_79UL | 11KV糠25線(JO25) 79RY U/L | FEEDER | D19/11/JO25/FDR_RCA |  |  |  | DNP | 345 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 11 | 11kV | JO25_LCO | 糠25線(JO25) LCO |  | TapPosMv | [14 empty] | 0906 |  | 0189 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO25_LCO_TAP | 11KV糠25線(JO25) LCO TAP | FEEDER | D19/11/JO25/51NA |  |  |  | DNP | 346 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D19 | 槺榔DS | 11 | 11kV | JO25 | JO25(11KV糠25線) |  | CB | [14 empty] | 0208 |  | 0132 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO25_CB | JO25(11KV糠25線) CB | FEEDER | D19/11/JO25/CB |  |  |  | DNP | 347 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | JO26 | 糠26線(JO26) |  | PHA | [14 empty] | 0219 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO26_PHA | 11KV糠26線(JO26) 相間RY | FEEDER | D19/11/JO26/PHA |  |  |  | DNP | 348 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO26 | 糠26線(JO26) |  | GDA | [14 empty] | 0220 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO26_GDA | 11KV糠26線(JO26) 接地RY | FEEDER | D19/11/JO26/GDA |  |  |  | DNP | 349 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO26 | 糠26線(JO26) 79RY |  | 79UL | [14 empty] | 0910 |  | 0192 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO26_79UL | 11KV糠26線(JO26) 79RY U/L | FEEDER | D19/11/JO26/FDR_RCA |  |  |  | DNP | 350 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 11 | 11kV | JO26_LCO | 糠26線(JO26) LCO |  | TapPosMv | [14 empty] | 0911 |  | 0193 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO26_LCO_TAP | 11KV糠26線(JO26) LCO TAP | FEEDER | D19/11/JO26/51NA |  |  |  | DNP | 351 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D19 | 槺榔DS | 11 | 11kV | JO26 | JO26(11KV糠26線) |  | CB | [14 empty] | 0218 |  | 0135 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO26_CB | JO26(11KV糠26線) CB | FEEDER | D19/11/JO26/CB |  |  |  | DNP | 352 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | JO27 | 糠27線(JO27) |  | PHA | [14 empty] | 0223 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO27_PHA | 11KV糠27線(JO27) 相間RY | FEEDER | D19/11/JO27/PHA |  |  |  | DNP | 353 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO27 | 糠27線(JO27) |  | GDA | [14 empty] | 0224 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO27_GDA | 11KV糠27線(JO27) 接地RY | FEEDER | D19/11/JO27/GDA |  |  |  | DNP | 354 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO27 | 糠27線(JO27) 79RY |  | 79UL | [14 empty] | 0912 |  | 0194 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO27_79UL | 11KV糠27線(JO27) 79RY U/L | FEEDER | D19/11/JO27/FDR_RCA |  |  |  | DNP | 355 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 11 | 11kV | JO27_LCO | 糠27線(JO27) LCO |  | TapPosMv | [14 empty] | 0913 |  | 0195 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO27_LCO_TAP | 11KV糠27線(JO27) LCO TAP | FEEDER | D19/11/JO27/51NA |  |  |  | DNP | 356 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D19 | 槺榔DS | 11 | 11kV | JO27 | JO27(11KV糠27線) |  | CB | [14 empty] | 0222 |  | 0136 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO27_CB | JO27(11KV糠27線) CB | FEEDER | D19/11/JO27/CB |  |  |  | DNP | 357 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | JO28 | 糠28線(JO28) |  | PHA | [14 empty] | 0227 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO28_PHA | 11KV糠28線(JO28) 相間RY | FEEDER | D19/11/JO28/PHA |  |  |  | DNP | 358 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO28 | 糠28線(JO28) |  | GDA | [14 empty] | 0228 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO28_GDA | 11KV糠28線(JO28) 接地RY | FEEDER | D19/11/JO28/GDA |  |  |  | DNP | 359 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO28 | 糠28線(JO28) 79RY |  | 79UL | [14 empty] | 0914 |  | 0196 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO28_79UL | 11KV糠28線(JO28) 79RY U/L | FEEDER | D19/11/JO28/FDR_RCA |  |  |  | DNP | 360 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 11 | 11kV | JO28_LCO | 糠28線(JO28) LCO |  | TapPosMv | [14 empty] | 0915 |  | 0197 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO28_LCO_TAP | 11KV糠28線(JO28) LCO TAP | FEEDER | D19/11/JO28/51NA |  |  |  | DNP | 361 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D19 | 槺榔DS | 11 | 11kV | JO28 | JO28(11KV糠28線) |  | CB | [14 empty] | 0226 |  | 0137 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO28_CB | JO28(11KV糠28線) CB | FEEDER | D19/11/JO28/CB |  |  |  | DNP | 362 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | JO29 | 糠29線(JO29) |  | PHA | [14 empty] | 0231 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO29_PHA | 11KV糠29線(JO29) 相間RY | FEEDER | D19/11/JO29/PHA |  |  |  | DNP | 363 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO29 | 糠29線(JO29) |  | GDA | [14 empty] | 0232 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO29_GDA | 11KV糠29線(JO29) 接地RY | FEEDER | D19/11/JO29/GDA |  |  |  | DNP | 364 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO29 | 糠29線(JO29) 79RY |  | 79UL | [14 empty] | 0916 |  | 0198 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO29_79UL | 11KV糠29線(JO29) 79RY U/L | FEEDER | D19/11/JO29/FDR_RCA |  |  |  | DNP | 365 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 11 | 11kV | JO29_LCO | 糠29線(JO29) LCO |  | TapPosMv | [14 empty] | 0917 |  | 0199 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO29_LCO_TAP | 11KV糠29線(JO29) LCO TAP | FEEDER | D19/11/JO29/51NA |  |  |  | DNP | 366 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D19 | 槺榔DS | 11 | 11kV | JO29 | JO29(11KV糠29線) |  | CB | [14 empty] | 0230 |  | 0138 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO29_CB | JO29(11KV糠29線) CB | FEEDER | D19/11/JO29/CB |  |  |  | DNP | 367 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | JO30 | 糠30線(JO30) |  | PHA | [14 empty] | 0235 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO30_PHA | 11KV糠30線(JO30) 相間RY | FEEDER | D19/11/JO30/PHA |  |  |  | DNP | 368 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO30 | 糠30線(JO30) |  | GDA | [14 empty] | 0236 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO30_GDA | 11KV糠30線(JO30) 接地RY | FEEDER | D19/11/JO30/GDA |  |  |  | DNP | 369 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO30 | 糠30線(JO30) 79RY |  | 79UL | [14 empty] | 0918 |  | 0200 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO30_79UL | 11KV糠30線(JO30) 79RY U/L | FEEDER | D19/11/JO30/FDR_RCA |  |  |  | DNP | 370 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 11 | 11kV | JO30_LCO | 糠30線(JO30) LCO |  | TapPosMv | [14 empty] | 0919 |  | 0201 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO30_LCO_TAP | 11KV糠30線(JO30) LCO TAP | FEEDER | D19/11/JO30/51NA |  |  |  | DNP | 371 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D19 | 槺榔DS | 11 | 11kV | JO30 | JO30(11KV糠30線) |  | CB | [14 empty] | 0234 |  | 0139 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO30_CB | JO30(11KV糠30線) CB | FEEDER | D19/11/JO30/CB |  |  |  | DNP | 372 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO61 | 糠61線(JO61) |  | PHA | [14 empty] | 0242 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO61_PHA | 23KV糠61線(JO61) 相間RY | FEEDER | D19/22/JO61/PHA |  |  |  | DNP | 373 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO61 | 糠61線(JO61) |  | GDA | [14 empty] | 0243 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO61_GDA | 23KV糠61線(JO61) 接地RY | FEEDER | D19/22/JO61/GDA |  |  |  | DNP | 374 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO61 | 糠61線(JO61) 79RY |  | 79UL | [14 empty] | 0923 |  | 0204 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO61_79UL | 23KV糠61線(JO61) 79RY U/L | FEEDER | D19/22/JO61/FDR_RCA |  |  |  | DNP | 375 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 22 | 22kV | JO61_LCO | 糠61線(JO61) LCO |  | TapPosMv | [14 empty] | 0924 |  | 0205 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO61_LCO_TAP | 23KV糠61線(JO61) LCO TAP | FEEDER | D19/22/JO61/51NA |  |  |  | DNP | 376 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D19 | 槺榔DS | 22 | 22kV | JO61 | JO61(23KV糠61線) |  | CB | [14 empty] | 0241 |  | 0141 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO61_CB | JO61(23KV糠61線) CB | FEEDER | D19/22/JO61/CB |  |  |  | DNP | 377 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO62 | 糠62線(JO62) |  | PHA | [14 empty] | 0246 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO62_PHA | 23KV糠62線(JO62) 相間RY | FEEDER | D19/22/JO62/PHA |  |  |  | DNP | 378 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO62 | 糠62線(JO62) |  | GDA | [14 empty] | 0247 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO62_GDA | 23KV糠62線(JO62) 接地RY | FEEDER | D19/22/JO62/GDA |  |  |  | DNP | 379 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO62 | 糠62線(JO62) 79RY |  | 79UL | [14 empty] | 0925 |  | 0206 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO62_79UL | 23KV糠62線(JO62) 79RY U/L | FEEDER | D19/22/JO62/FDR_RCA |  |  |  | DNP | 380 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 22 | 22kV | JO62_LCO | 糠62線(JO62) LCO |  | TapPosMv | [14 empty] | 0926 |  | 0207 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO62_LCO_TAP | 23KV糠62線(JO62) LCO TAP | FEEDER | D19/22/JO62/51NA |  |  |  | DNP | 381 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D19 | 槺榔DS | 22 | 22kV | JO62 | JO62(23KV糠62線) |  | CB | [14 empty] | 0245 |  | 0142 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO62_CB | JO62(23KV糠62線) CB | FEEDER | D19/22/JO62/CB |  |  |  | DNP | 382 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO63 | 糠63線(JO63) |  | PHA | [14 empty] | 0250 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO63_PHA | 23KV糠63線(JO63) 相間RY | FEEDER | D19/22/JO63/PHA |  |  |  | DNP | 383 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO63 | 糠63線(JO63) |  | GDA | [14 empty] | 0251 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO63_GDA | 23KV糠63線(JO63) 接地RY | FEEDER | D19/22/JO63/GDA |  |  |  | DNP | 384 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO63 | 糠63線(JO63) 79RY |  | 79UL | [14 empty] | 0927 |  | 0208 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO63_79UL | 23KV糠63線(JO63) 79RY U/L | FEEDER | D19/22/JO63/FDR_RCA |  |  |  | DNP | 385 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 22 | 22kV | JO63_LCO | 糠63線(JO63) LCO |  | TapPosMv | [14 empty] | 0928 |  | 0209 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO63_LCO_TAP | 23KV糠63線(JO63) LCO TAP | FEEDER | D19/22/JO63/51NA |  |  |  | DNP | 386 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D19 | 槺榔DS | 22 | 22kV | JO63 | JO63(23KV糠63線) |  | CB | [14 empty] | 0249 |  | 0143 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO63_CB | JO63(23KV糠63線) CB | FEEDER | D19/22/JO63/CB |  |  |  | DNP | 387 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO64 | 糠64線(JO64) |  | PHA | [14 empty] | 0254 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO64_PHA | 23KV糠64線(JO64) 相間RY | FEEDER | D19/22/JO64/PHA |  |  |  | DNP | 388 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO64 | 糠64線(JO64) |  | GDA | [14 empty] | 0255 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO64_GDA | 23KV糠64線(JO64) 接地RY | FEEDER | D19/22/JO64/GDA |  |  |  | DNP | 389 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO64 | 糠64線(JO64) 79RY |  | 79UL | [14 empty] | 0929 |  | 0210 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO64_79UL | 23KV糠64線(JO64) 79RY U/L | FEEDER | D19/22/JO64/FDR_RCA |  |  |  | DNP | 390 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 22 | 22kV | JO64_LCO | 糠64線(JO64) LCO |  | TapPosMv | [14 empty] | 0930 |  | 0211 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO64_LCO_TAP | 23KV糠64線(JO64) LCO TAP | FEEDER | D19/22/JO64/51NA |  |  |  | DNP | 391 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D19 | 槺榔DS | 22 | 22kV | JO64 | JO64(23KV糠64線) |  | CB | [14 empty] | 0253 |  | 0144 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO64_CB | JO64(23KV糠64線) CB | FEEDER | D19/22/JO64/CB |  |  |  | DNP | 392 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO65 | 糠65線(JO65) |  | PHA | [14 empty] | 0258 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO65_PHA | 23KV糠65線(JO65) 相間RY | FEEDER | D19/22/JO65/PHA |  |  |  | DNP | 393 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO65 | 糠65線(JO65) |  | GDA | [14 empty] | 0259 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO65_GDA | 23KV糠65線(JO65) 接地RY | FEEDER | D19/22/JO65/GDA |  |  |  | DNP | 394 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO65 | 糠65線(JO65) 79RY |  | 79UL | [14 empty] | 0931 |  | 0212 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO65_79UL | 23KV糠65線(JO65) 79RY U/L | FEEDER | D19/22/JO65/FDR_RCA |  |  |  | DNP | 395 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 22 | 22kV | JO65_LCO | 糠65線(JO65) LCO |  | TapPosMv | [14 empty] | 0932 |  | 0213 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO65_LCO_TAP | 23KV糠65線(JO65) LCO TAP | FEEDER | D19/22/JO65/51NA |  |  |  | DNP | 396 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D19 | 槺榔DS | 22 | 22kV | JO65 | JO65(23KV糠65線) |  | CB | [14 empty] | 0257 |  | 0145 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO65_CB | JO65(23KV糠65線) CB | FEEDER | D19/22/JO65/CB |  |  |  | DNP | 397 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO66 | 糠66線(JO66) |  | PHA | [14 empty] | 0262 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO66_PHA | 23KV糠66線(JO66) 相間RY | FEEDER | D19/22/JO66/PHA |  |  |  | DNP | 398 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO66 | 糠66線(JO66) |  | GDA | [14 empty] | 0263 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO66_GDA | 23KV糠66線(JO66) 接地RY | FEEDER | D19/22/JO66/GDA |  |  |  | DNP | 399 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO66 | 糠66線(JO66) 79RY |  | 79UL | [14 empty] | 0933 |  | 0214 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO66_79UL | 23KV糠66線(JO66) 79RY U/L | FEEDER | D19/22/JO66/FDR_RCA |  |  |  | DNP | 400 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 22 | 22kV | JO66_LCO | 糠66線(JO66) LCO |  | TapPosMv | [14 empty] | 0934 |  | 0215 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO66_LCO_TAP | 23KV糠66線(JO66) LCO TAP | FEEDER | D19/22/JO66/51NA |  |  |  | DNP | 401 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D19 | 槺榔DS | 22 | 22kV | JO66 | JO66(23KV糠66線) |  | CB | [14 empty] | 0261 |  | 0146 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO66_CB | JO66(23KV糠66線) CB | FEEDER | D19/22/JO66/CB |  |  |  | DNP | 402 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO67 | 糠67線(JO67) |  | PHA | [14 empty] | 0266 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO67_PHA | 23KV糠67線(JO67) 相間RY | FEEDER | D19/22/JO67/PHA |  |  |  | DNP | 403 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO67 | 糠67線(JO67) |  | GDA | [14 empty] | 0267 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO67_GDA | 23KV糠67線(JO67) 接地RY | FEEDER | D19/22/JO67/GDA |  |  |  | DNP | 404 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO67 | 糠67線(JO67) 79RY |  | 79UL | [14 empty] | 0935 |  | 0216 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO67_79UL | 23KV糠67線(JO67) 79RY U/L | FEEDER | D19/22/JO67/FDR_RCA |  |  |  | DNP | 405 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 22 | 22kV | JO67_LCO | 糠67線(JO67) LCO |  | TapPosMv | [14 empty] | 0936 |  | 0217 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO67_LCO_TAP | 23KV糠67線(JO67) LCO TAP | FEEDER | D19/22/JO67/51NA |  |  |  | DNP | 406 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D19 | 槺榔DS | 22 | 22kV | JO67 | JO67(23KV糠67線) |  | CB | [14 empty] | 0265 |  | 0147 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO67_CB | JO67(23KV糠67線) CB | FEEDER | D19/22/JO67/CB |  |  |  | DNP | 407 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO68 | 糠68線(JO68) |  | PHA | [14 empty] | 0270 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO68_PHA | 23KV糠68線(JO68) 相間RY | FEEDER | D19/22/JO68/PHA |  |  |  | DNP | 408 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO68 | 糠68線(JO68) |  | GDA | [14 empty] | 0271 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO68_GDA | 23KV糠68線(JO68) 接地RY | FEEDER | D19/22/JO68/GDA |  |  |  | DNP | 409 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO68 | 糠68線(JO68) 79RY |  | 79UL | [14 empty] | 0937 |  | 0218 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO68_79UL | 23KV糠68線(JO68) 79RY U/L | FEEDER | D19/22/JO68/FDR_RCA |  |  |  | DNP | 410 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 22 | 22kV | JO68_LCO | 糠68線(JO68) LCO |  | TapPosMv | [14 empty] | 0938 |  | 0219 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO68_LCO_TAP | 23KV糠68線(JO68) LCO TAP | FEEDER | D19/22/JO68/51NA |  |  |  | DNP | 411 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D19 | 槺榔DS | 22 | 22kV | JO68 | JO68(23KV糠68線) |  | CB | [14 empty] | 0269 |  | 0148 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO68_CB | JO68(23KV糠68線) CB | FEEDER | D19/22/JO68/CB |  |  |  | DNP | 412 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO71 | 糠71線(JO71) |  | PHA | [14 empty] | 0283 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO71_PHA | 23KV糠71線(JO71) 相間RY | FEEDER | D19/22/JO71/PHA |  |  |  | DNP | 413 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO71 | 糠71線(JO71) |  | GDA | [14 empty] | 0284 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO71_GDA | 23KV糠71線(JO71) 接地RY | FEEDER | D19/22/JO71/GDA |  |  |  | DNP | 414 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO71 | 糠71線(JO71) 79RY |  | 79UL | [14 empty] | 0942 |  | 0222 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO71_79UL | 23KV糠71線(JO71) 79RY U/L | FEEDER | D19/22/JO71/FDR_RCA |  |  |  | DNP | 415 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 22 | 22kV | JO71_LCO | 糠71線(JO71) LCO |  | TapPosMv | [14 empty] | 0943 |  | 0223 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO71_LCO_TAP | 23KV糠71線(JO71) LCO TAP | FEEDER | D19/22/JO71/51NA |  |  |  | DNP | 416 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D19 | 槺榔DS | 22 | 22kV | JO71 | JO71(23KV糠71線) |  | CB | [14 empty] | 0282 |  | 0152 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO71_CB | JO71(23KV糠71線) CB | FEEDER | D19/22/JO71/CB |  |  |  | DNP | 417 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO72 | 糠72線(JO72) |  | PHA | [14 empty] | 0287 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO72_PHA | 23KV糠72線(JO72) 相間RY | FEEDER | D19/22/JO72/PHA |  |  |  | DNP | 418 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO72 | 糠72線(JO72) |  | GDA | [14 empty] | 0288 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO72_GDA | 23KV糠72線(JO72) 接地RY | FEEDER | D19/22/JO72/GDA |  |  |  | DNP | 419 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO72 | 糠72線(JO72) 79RY |  | 79UL | [14 empty] | 0944 |  | 0224 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO72_79UL | 23KV糠72線(JO72) 79RY U/L | FEEDER | D19/22/JO72/FDR_RCA |  |  |  | DNP | 420 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 22 | 22kV | JO72_LCO | 糠72線(JO72) LCO |  | TapPosMv | [14 empty] | 0945 |  | 0225 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO72_LCO_TAP | 23KV糠72線(JO72) LCO TAP | FEEDER | D19/22/JO72/51NA |  |  |  | DNP | 421 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D19 | 槺榔DS | 22 | 22kV | JO72 | JO72(23KV糠72線) |  | CB | [14 empty] | 0286 |  | 0153 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO72_CB | JO72(23KV糠72線) CB | FEEDER | D19/22/JO72/CB |  |  |  | DNP | 422 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO73 | 糠73線(JO73) |  | PHA | [14 empty] | 0291 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO73_PHA | 23KV糠73線(JO73) 相間RY | FEEDER | D19/22/JO73/PHA |  |  |  | DNP | 423 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO73 | 糠73線(JO73) |  | GDA | [14 empty] | 0292 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO73_GDA | 23KV糠73線(JO73) 接地RY | FEEDER | D19/22/JO73/GDA |  |  |  | DNP | 424 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO73 | 糠73線(JO73) 79RY |  | 79UL | [14 empty] | 0946 |  | 0226 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO73_79UL | 23KV糠73線(JO73) 79RY U/L | FEEDER | D19/22/JO73/FDR_RCA |  |  |  | DNP | 425 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 22 | 22kV | JO73_LCO | 糠73線(JO73) LCO |  | TapPosMv | [14 empty] | 0947 |  | 0227 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO73_LCO_TAP | 23KV糠73線(JO73) LCO TAP | FEEDER | D19/22/JO73/51NA |  |  |  | DNP | 426 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D19 | 槺榔DS | 22 | 22kV | JO73 | JO73(23KV糠73線) |  | CB | [14 empty] | 0290 |  | 0154 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO73_CB | JO73(23KV糠73線) CB | FEEDER | D19/22/JO73/CB |  |  |  | DNP | 427 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO74 | 糠74線(JO74) |  | PHA | [14 empty] | 0295 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO74_PHA | 23KV糠74線(JO74) 相間RY | FEEDER | D19/22/JO74/PHA |  |  |  | DNP | 428 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO74 | 糠74線(JO74) |  | GDA | [14 empty] | 0296 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO74_GDA | 23KV糠74線(JO74) 接地RY | FEEDER | D19/22/JO74/GDA |  |  |  | DNP | 429 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO74 | 糠74線(JO74) 79RY |  | 79UL | [14 empty] | 0948 |  | 0228 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO74_79UL | 23KV糠74線(JO74) 79RY U/L | FEEDER | D19/22/JO74/FDR_RCA |  |  |  | DNP | 430 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 22 | 22kV | JO74_LCO | 糠74線(JO74) LCO |  | TapPosMv | [14 empty] | 0949 |  | 0229 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO74_LCO_TAP | 23KV糠74線(JO74) LCO TAP | FEEDER | D19/22/JO74/51NA |  |  |  | DNP | 431 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D19 | 槺榔DS | 22 | 22kV | JO74 | JO74(23KV糠74線) |  | CB | [14 empty] | 0294 |  | 0155 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO74_CB | JO74(23KV糠74線) CB | FEEDER | D19/22/JO74/CB |  |  |  | DNP | 432 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO75 | 糠75線(JO75) |  | PHA | [14 empty] | 0299 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO75_PHA | 23KV糠75線(JO75) 相間RY | FEEDER | D19/22/JO75/PHA |  |  |  | DNP | 433 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO75 | 糠75線(JO75) |  | GDA | [14 empty] | 0300 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO75_GDA | 23KV糠75線(JO75) 接地RY | FEEDER | D19/22/JO75/GDA |  |  |  | DNP | 434 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO75 | 糠75線(JO75) 79RY |  | 79UL | [14 empty] | 0950 |  | 0230 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO75_79UL | 23KV糠75線(JO75) 79RY U/L | FEEDER | D19/22/JO75/FDR_RCA |  |  |  | DNP | 435 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 22 | 22kV | JO75_LCO | 糠75線(JO75) LCO |  | TapPosMv | [14 empty] | 0951 |  | 0231 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO75_LCO_TAP | 23KV糠75線(JO75) LCO TAP | FEEDER | D19/22/JO75/51NA |  |  |  | DNP | 436 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D19 | 槺榔DS | 22 | 22kV | JO75 | JO75(23KV糠75線) |  | CB | [14 empty] | 0298 |  | 0156 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO75_CB | JO75(23KV糠75線) CB | FEEDER | D19/22/JO75/CB |  |  |  | DNP | 437 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO76 | 糠76線(JO76) |  | PHA | [14 empty] | 0303 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO76_PHA | 23KV糠76線(JO76) 相間RY | FEEDER | D19/22/JO76/PHA |  |  |  | DNP | 438 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO76 | 糠76線(JO76) |  | GDA | [14 empty] | 0304 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO76_GDA | 23KV糠76線(JO76) 接地RY | FEEDER | D19/22/JO76/GDA |  |  |  | DNP | 439 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO76 | 糠76線(JO76) 79RY |  | 79UL | [14 empty] | 0952 |  | 0232 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO76_79UL | 23KV糠76線(JO76) 79RY U/L | FEEDER | D19/22/JO76/FDR_RCA |  |  |  | DNP | 440 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 22 | 22kV | JO76_LCO | 糠76線(JO76) LCO |  | TapPosMv | [14 empty] | 0953 |  | 0233 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO76_LCO_TAP | 23KV糠76線(JO76) LCO TAP | FEEDER | D19/22/JO76/51NA |  |  |  | DNP | 441 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D19 | 槺榔DS | 22 | 22kV | JO76 | JO76(23KV糠76線) |  | CB | [14 empty] | 0302 |  | 0157 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO76_CB | JO76(23KV糠76線) CB | FEEDER | D19/22/JO76/CB |  |  |  | DNP | 442 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO77 | 糠77線(JO77) |  | PHA | [14 empty] | 0307 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO77_PHA | 23KV糠77線(JO77) 相間RY | FEEDER | D19/22/JO77/PHA |  |  |  | DNP | 443 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO77 | 糠77線(JO77) |  | GDA | [14 empty] | 0308 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO77_GDA | 23KV糠77線(JO77) 接地RY | FEEDER | D19/22/JO77/GDA |  |  |  | DNP | 444 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO77 | 糠77線(JO77) 79RY |  | 79UL | [14 empty] | 0954 |  | 0234 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO77_79UL | 23KV糠77線(JO77) 79RY U/L | FEEDER | D19/22/JO77/FDR_RCA |  |  |  | DNP | 445 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 22 | 22kV | JO77_LCO | 糠77線(JO77) LCO |  | TapPosMv | [14 empty] | 0955 |  | 0235 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO77_LCO_TAP | 23KV糠77線(JO77) LCO TAP | FEEDER | D19/22/JO77/51NA |  |  |  | DNP | 446 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D19 | 槺榔DS | 22 | 22kV | JO77 | JO77(23KV糠77線) |  | CB | [14 empty] | 0306 |  | 0158 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO77_CB | JO77(23KV糠77線) CB | FEEDER | D19/22/JO77/CB |  |  |  | DNP | 447 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | JO78 | 糠78線(JO78) |  | PHA | [14 empty] | 0311 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO78_PHA | 23KV糠78線(JO78) 相間RY | FEEDER | D19/22/JO78/PHA |  |  |  | DNP | 448 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO78 | 糠78線(JO78) |  | GDA | [14 empty] | 0312 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO78_GDA | 23KV糠78線(JO78) 接地RY | FEEDER | D19/22/JO78/GDA |  |  |  | DNP | 449 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO78 | 糠78線(JO78) 79RY |  | 79UL | [14 empty] | 0956 |  | 0236 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO78_79UL | 23KV糠78線(JO78) 79RY U/L | FEEDER | D19/22/JO78/FDR_RCA |  |  |  | DNP | 450 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 22 | 22kV | JO78_LCO | 糠78線(JO78) LCO |  | TapPosMv | [14 empty] | 0957 |  | 0237 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO78_LCO_TAP | 23KV糠78線(JO78) LCO TAP | FEEDER | D19/22/JO78/51NA |  |  |  | DNP | 451 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D19 | 槺榔DS | 22 | 22kV | JO78 | JO78(23KV糠78線) |  | CB | [14 empty] | 0310 |  | 0159 | [8 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO78_CB | JO78(23KV糠78線) CB | FEEDER | D19/22/JO78/CB |  |  |  | DNP | 452 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | 100 | TIE(100) |  | CB | [14 empty] | 0215 |  | 0134 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.100_CB | 100(TIE) CB | TIE | D19/11/100/CB |  |  |  | DNP | 453 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | 100 | TIE(100) |  | 51A | [14 empty] | 0216 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.100_51A | 11KV TIE(100) 51RY | TIE | D19/11/100/PHA |  |  |  | DNP | 454 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 100 | TIE(100) |  | 51NA | [14 empty] | 0217 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.100_51NA | 11KV TIE(100) 51N RY | TIE | D19/11/100/GDA |  |  |  | DNP | 455 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [14 empty] | 0032 |  | 0009 | [8 empty] | 161KV_N | [8 empty] | 糠榔DS.1500_CB | 1500(TIE) CB | TIE | D19/161/1500/CB |  |  |  | DNP | 456 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | 1500 | TIE(1500) |  | 50A | [14 empty] | 0033 | [10 empty] | 161KV_N | [8 empty] | 糠榔DS.1500_50A | 161KV TIE(1500) 50RY | TIE | D19/161/1500/50A |  |  |  | DNP | 457 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [13 empty] | 0608 | 609 | 0104 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.1501_DS | 1501(TIE) DS | TIE | D19/161/1500/DS1 |  |  |  | DNP | 458 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D19 | 槺榔DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [13 empty] | 0610 | 611 | 0105 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.1502_DS | 1502(TIE) DS | TIE | D19/161/1500/DS2 |  |  |  | DNP | 459 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D19 | 槺榔DS | 0 |  | 1500 | TIE(1500) |  | 50SA | [14 empty] | 0532 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.1500_50SA | 161KV TIE(1500) 50RY 測試/正常 | TIE | D19/161/1500/50SA |  |  |  | DNP | 460 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TEST/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 200 | TIE(200) |  | CB | [14 empty] | 0320 |  | 0163 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.200_CB | 200(TIE) CB | TIE | D19/22/200/CB |  |  |  | DNP | 461 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | 200 | TIE(200) |  | 51A | [14 empty] | 0321 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.200_51A | 23KV TIE(200) 51RY | TIE | D19/22/200/PHA |  |  |  | DNP | 462 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 200 | TIE(200) |  | 51NA | [14 empty] | 0322 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.200_51NA | 23KV TIE(200) 51N RY | TIE | D19/22/200/GDA |  |  |  | DNP | 463 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 390 | #1SSTR(390) |  | CB | [14 empty] | 0273 |  | 0149 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.390_CB | 390(#1SSTR) CB | OTHER | D19/22/390/CB |  |  |  | DNP | 464 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | 1SSTR | #1SSTR |  | 51A | [14 empty] | 0274 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#1SSTR_51A | #1SSTR 51RY | OTHER | D19/22/390/PHA |  |  |  | DNP | 465 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 1SSTR | #1SSTR |  | 51NA | [14 empty] | 0275 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | D19/22/390/GDA |  |  |  | DNP | 466 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 490 | #2SSTR(490) |  | CB | [14 empty] | 0323 |  | 0160 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.490_CB | 490(#2SSTR) CB | OTHER | D19/22/490/CB |  |  |  | DNP | 467 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | 2SSTR | #2SSTR |  | 51A | [14 empty] | 0324 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#2SSTR_51A | #2SSTR 51RY | OTHER | D19/22/490/PHA |  |  |  | DNP | 468 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 2SSTR | #2SSTR |  | 51NA | [14 empty] | 0325 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | D19/22/490/GDA |  |  |  | DNP | 469 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB | [14 empty] | 0048 |  | 0010 | [8 empty] | 161KV_N | [8 empty] | 糠榔DS.1750_CB | 1750(#1DTR) CB | MTR | D19/161/1750/CB |  |  |  | DNP | 470 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | 310 | #1DTR(310) |  | CB | [14 empty] | 0055 |  | 0013 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.310_CB | 310(#1DTR) CB | MTR | D19/11/310/CB |  |  |  | DNP | 471 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | 320 | #1DTR(320) |  | CB | [14 empty] | 0059 |  | 0014 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.320_CB | 320(#1DTR) CB | MTR | D19/11/320/CB |  |  |  | DNP | 472 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | 1DTR | #1DTR |  | 51ZA | [14 empty] | 0051 | [10 empty] | 161KV_N | [8 empty] | 糠榔DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | D19//1DTR/51ZA |  |  |  | DNP | 473 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 1DTR | #1DTR |  | 87A | [14 empty] | 0049 | [10 empty] | 161KV_N | [8 empty] | 糠榔DS.#1DTR_87A | #1DTR 87RY | MTR | D19//1DTR/87A |  |  |  | DNP | 474 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 1DTR | #1DTR |  | 87UL | [14 empty] | 0533 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#1DTR_87UL | #1DTR 87RY U/L | MTR | D19//1DTR/87UL |  |  |  | DNP | 475 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 0 |  | 310 | #1DTR(310) |  | 51A | [14 empty] | 0056 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.310_51A | #1DTR二次側(310) 51RY | MTR | D19/11/310/PHA |  |  |  | DNP | 476 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 320 | #1DTR(320) |  | 51A | [14 empty] | 0060 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.320_51A | #1DTR二次側(320) 51RY | MTR | D19/11/320/PHA |  |  |  | DNP | 477 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 1DTR | #1DTR |  | 96PA | [14 empty] | 0050 | [10 empty] | 161KV_N | [8 empty] | 糠榔DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | D19//1DTR/96PA |  |  |  | DNP | 478 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 1DTR | #1DTR |  | 96D | [14 empty] | 0542 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#1DTR_96D | #1DTR 96D RY | MTR | D19//1DTR/96D |  |  |  | DNP | 479 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 1DTR | #1DTR |  | 96P | [14 empty] | 0543 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#1DTR_96P | #1DTR 96P RY | MTR | D19//1DTR/96P |  |  |  | DNP | 480 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 1DTR | #1DTR |  | 63Q | [14 empty] | 0544 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#1DTR_63Q | #1DTR 63Q RY | MTR | D19//1DTR/63Q |  |  |  | DNP | 481 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 1DTR | #1DTR |  | 96B1 | [14 empty] | 0540 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | D19//1DTR/96B1 |  |  |  | DNP | 482 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 1DTR | #1DTR |  | 96B2 | [14 empty] | 0541 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | D19//1DTR/96B2 |  |  |  | DNP | 483 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 1DTR | #1DTR |  | TRA | [14 empty] | 0545 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#1DTR_TRA | #1DTR 重故障 | MTR | D19//1DTR/TRA |  |  |  | DNP | 484 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 1DTR | #1DTR |  | TRF | [14 empty] | 0546 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#1DTR_TRF | #1DTR 輕故障 | MTR | D19//1DTR/TRF |  |  |  | DNP | 485 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 1DTR(A) | #1DTR(A) |  | SupLocal | [14 empty] | 0536 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | D19//1DTR(A)/SupLocal |  |  |  | DNP | 486 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D19 | 槺榔DS | 0 |  | 1DTR(A) | #1DTR(A) |  | A_M | [14 empty] | 0537 |  | 0056 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | D19//1DTR(A)/Tap Chan |  |  |  | DNP | 487 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D19 | 槺榔DS | 0 |  | 1DTR(B) | #1DTR(B) |  | SupLocal | [14 empty] | 0538 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | D19//1DTR(B)/SupLocal |  |  |  | DNP | 488 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D19 | 槺榔DS | 0 |  | 1DTR(B) | #1DTR(B) |  | A_M | [14 empty] | 0539 |  | 0058 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | D19//1DTR(B)/Tap Chan |  |  |  | DNP | 489 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D19 | 槺榔DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 | [13 empty] | 0676 | 677 | 0106 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.1751_DS | 1751(#1DTR) DS | MTR | D19/161/1750/DS1 |  |  |  | DNP | 490 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D19 | 槺榔DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 | [13 empty] | 0678 | 679 | 0107 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.1752_DS | 1752(#1DTR) DS | MTR | D19/161/1750/DS2 |  |  |  | DNP | 491 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D19 | 槺榔DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB | [14 empty] | 0063 |  | 0011 | [8 empty] | 161KV_N | [8 empty] | 糠榔DS.1760_CB | 1760(#2DTR) CB | MTR | D19/161/1760/CB |  |  |  | DNP | 492 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | 330 | #2DTR(330) |  | CB | [14 empty] | 0070 |  | 0015 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.330_CB | 330(#2DTR) CB | MTR | D19/22/330/CB |  |  |  | DNP | 493 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | 2DTR | #2DTR |  | 51ZA | [14 empty] | 0066 | [10 empty] | 161KV_N | [8 empty] | 糠榔DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | D19//2DTR/51ZA |  |  |  | DNP | 494 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 2DTR | #2DTR |  | 87A | [14 empty] | 0064 | [10 empty] | 161KV_N | [8 empty] | 糠榔DS.#2DTR_87A | #2DTR 87RY | MTR | D19//2DTR/87A |  |  |  | DNP | 495 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 2DTR | #2DTR |  | 87UL | [14 empty] | 0547 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#2DTR_87UL | #2DTR 87RY U/L | MTR | D19//2DTR/87UL |  |  |  | DNP | 496 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 0 |  | 330 | #2DTR(330) |  | 51A | [14 empty] | 0071 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.330_51A | #2DTR二次側(330) 51RY | MTR | D19/22/330/PHA |  |  |  | DNP | 497 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 2DTR | #2DTR |  | 96PA | [14 empty] | 0065 | [10 empty] | 161KV_N | [8 empty] | 糠榔DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | D19//2DTR/96PA |  |  |  | DNP | 498 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 2DTR | #2DTR |  | 96D | [14 empty] | 0554 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#2DTR_96D | #2DTR 96D RY | MTR | D19//2DTR/96D |  |  |  | DNP | 499 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 2DTR | #2DTR |  | 96P | [14 empty] | 0555 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#2DTR_96P | #2DTR 96P RY | MTR | D19//2DTR/96P |  |  |  | DNP | 500 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 2DTR | #2DTR |  | 63Q | [14 empty] | 0556 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#2DTR_63Q | #2DTR 63Q RY | MTR | D19//2DTR/63Q |  |  |  | DNP | 501 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 2DTR | #2DTR |  | 96B1 | [14 empty] | 0552 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | D19//2DTR/96B1 |  |  |  | DNP | 502 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 2DTR | #2DTR |  | 96B2 | [14 empty] | 0553 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | D19//2DTR/96B2 |  |  |  | DNP | 503 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 2DTR | #2DTR |  | TRA | [14 empty] | 0557 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#2DTR_TRA | #2DTR 重故障 | MTR | D19//2DTR/TRA |  |  |  | DNP | 504 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 2DTR | #2DTR |  | TRF | [14 empty] | 0558 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#2DTR_TRF | #2DTR 輕故障 | MTR | D19//2DTR/TRF |  |  |  | DNP | 505 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 2DTR | #2DTR |  | SupLocal | [14 empty] | 0550 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#2DTR_S/L | #2DTR OLTC S/L | MTR | D19//2DTR/SupLocal |  |  |  | DNP | 506 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D19 | 槺榔DS | 0 |  | 2DTR | #2DTR |  | A_M | [14 empty] | 0551 |  | 0060 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.#2DTR_A/M | #2DTR OLTC A/M | MTR | D19//2DTR/Tap Chan |  |  |  | DNP | 507 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D19 | 槺榔DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 | [13 empty] | 0680 | 681 | 0108 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.1761_DS | 1761(#2DTR) DS | MTR | D19/161/1760/DS1 |  |  |  | DNP | 508 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D19 | 槺榔DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 | [13 empty] | 0682 | 683 | 0109 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.1762_DS | 1762(#2DTR) DS | MTR | D19/161/1760/DS2 |  |  |  | DNP | 509 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D19 | 槺榔DS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB | [14 empty] | 0074 |  | 0012 | [8 empty] | 161KV_N | [8 empty] | 糠榔DS.1770_CB | 1770(#3DTR) CB | MTR | D19/161/1770/CB |  |  |  | DNP | 510 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | 350 | #3DTR(350) |  | CB | [14 empty] | 0081 |  | 0016 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.350_CB | 350(#3DTR) CB | MTR | D19/22/350/CB |  |  |  | DNP | 511 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | 3DTR | #3DTR |  | 51ZA | [14 empty] | 0077 | [10 empty] | 161KV_N | [8 empty] | 糠榔DS.#3DTR_51ZA | #3DTR 51Z RY | MTR | D19//3DTR/51ZA |  |  |  | DNP | 512 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 3DTR | #3DTR |  | 87A | [14 empty] | 0075 | [10 empty] | 161KV_N | [8 empty] | 糠榔DS.#3DTR_87A | #3DTR 87RY | MTR | D19//3DTR/87A |  |  |  | DNP | 513 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 3DTR | #3DTR |  | 87UL | [14 empty] | 0559 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#3DTR_87UL | #3DTR 87RY U/L | MTR | D19//3DTR/87UL |  |  |  | DNP | 514 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 0 |  | 350 | #3DTR(350) |  | 51A | [14 empty] | 0082 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.350_51A | #3DTR二次側(350) 51RY | MTR | D19/22/350/PHA |  |  |  | DNP | 515 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 3DTR | #3DTR |  | 96PA | [14 empty] | 0076 | [10 empty] | 161KV_N | [8 empty] | 糠榔DS.#3DTR_96PA | #3DTR 機械保護動作 | MTR | D19//3DTR/96PA |  |  |  | DNP | 516 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 3DTR | #3DTR |  | 96D | [14 empty] | 0566 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#3DTR_96D | #3DTR 96D RY | MTR | D19//3DTR/96D |  |  |  | DNP | 517 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 3DTR | #3DTR |  | 96P | [14 empty] | 0567 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#3DTR_96P | #3DTR 96P RY | MTR | D19//3DTR/96P |  |  |  | DNP | 518 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 3DTR | #3DTR |  | 63Q | [14 empty] | 0568 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#3DTR_63Q | #3DTR 63Q RY | MTR | D19//3DTR/63Q |  |  |  | DNP | 519 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 3DTR | #3DTR |  | 96B1 | [14 empty] | 0564 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#3DTR_96B1 | #3DTR 96B1 RY | MTR | D19//3DTR/96B1 |  |  |  | DNP | 520 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 3DTR | #3DTR |  | 96B2 | [14 empty] | 0565 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#3DTR_96B2 | #3DTR 96B2 RY | MTR | D19//3DTR/96B2 |  |  |  | DNP | 521 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 3DTR | #3DTR |  | TRA | [14 empty] | 0569 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#3DTR_TRA | #3DTR 重故障 | MTR | D19//3DTR/TRA |  |  |  | DNP | 522 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 3DTR | #3DTR |  | TRF | [14 empty] | 0570 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#3DTR_TRF | #3DTR 輕故障 | MTR | D19//3DTR/TRF |  |  |  | DNP | 523 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 3DTR | #3DTR |  | SupLocal | [14 empty] | 0562 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#3DTR_S/L | #3DTR OLTC S/L | MTR | D19//3DTR/SupLocal |  |  |  | DNP | 524 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D19 | 槺榔DS | 0 |  | 3DTR | #3DTR |  | A_M | [14 empty] | 0563 |  | 0062 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.#3DTR_A/M | #3DTR OLTC A/M | MTR | D19//3DTR/Tap Chan |  |  |  | DNP | 525 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D19 | 槺榔DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 | [13 empty] | 0684 | 685 | 0110 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.1771_DS | 1771(#3DTR) DS | MTR | D19/161/1770/DS1 |  |  |  | DNP | 526 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D19 | 槺榔DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 | [13 empty] | 0686 | 687 | 0111 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.1772_DS | 1772(#3DTR) DS | MTR | D19/161/1770/DS2 |  |  |  | DNP | 527 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D19 | 槺榔DS | 11 | 11kV | 210 | #1SC(210) |  | CB | [14 empty] | 0212 |  | 0133 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.210_CB | 210(11KV #1SC) CB | SC | D19/11/210/CB |  |  |  | DNP | 528 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [14 empty] | 0213 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.210_SCA | 11KV #1SC 51,51N RY | SC | D19/11/210/SCA |  |  |  | DNP | 529 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [14 empty] | 0214 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.210_OUVA | 11KV #1SC 27,59RY(欠壓或過壓) | SC | D19/11/210/UVA |  |  |  | DNP | 530 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | 210 | #1SC(210) |  | LBS | [14 empty] | 0688 | 689 | 0112 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.210_LBS | 210(11KV #1SC) LBS | SC | D19/11/210/LBS |  |  |  | DNP | 531 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D19 | 槺榔DS | 11 | 11kV | 220 | #2SC(220) |  | CB | [14 empty] | 0238 |  | 0140 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.220_CB | 220(11KV #2SC) CB | SC | D19/11/220/CB |  |  |  | DNP | 532 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [14 empty] | 0239 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.220_SCA | 11KV #2SC 51,51N RY | SC | D19/11/220/SCA |  |  |  | DNP | 533 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [14 empty] | 0240 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.220_OUVA | 11KV #2SC 27,59RY(欠壓或過壓) | SC | D19/11/220/UVA |  |  |  | DNP | 534 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | 220 | #2SC(220) |  | LBS | [14 empty] | 0690 | 691 | 0113 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.220_LBS | 220(11KV #2SC) LBS | SC | D19/11/220/LBS |  |  |  | DNP | 535 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D19 | 槺榔DS | 22 | 22kV | 230 | #3SC(230) |  | CB | [14 empty] | 0276 |  | 0150 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.230_CB | 230(23KV #3SC) CB | SC | D19/22/230/CB |  |  |  | DNP | 536 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | 230 | #3SC(230) |  | SCA | [14 empty] | 0277 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.230_SCA | 23KV #3SC 51,51N RY | SC | D19/22/230/SCA |  |  |  | DNP | 537 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | 230 | #3SC(230) |  | UVA | [14 empty] | 0278 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.230_OUVA | 23KV #3SC 27,59RY(欠壓或過壓) | SC | D19/22/230/UVA |  |  |  | DNP | 538 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | 240 | #4SC(240) |  | CB | [14 empty] | 0279 |  | 0151 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.240_CB | 240(23KV #4SC) CB | SC | D19/22/240/CB |  |  |  | DNP | 539 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | 240 | #4SC(240) |  | SCA | [14 empty] | 0280 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.240_SCA | 23KV #4SC 51,51N RY | SC | D19/22/240/SCA |  |  |  | DNP | 540 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | 240 | #4SC(240) |  | UVA | [14 empty] | 0281 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.240_OUVA | 23KV #4SC 27,59RY(欠壓或過壓) | SC | D19/22/240/UVA |  |  |  | DNP | 541 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | 250 | #5SC(250) |  | CB | [14 empty] | 0314 |  | 0161 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.250_CB | 250(23KV #5SC) CB | SC | D19/22/250/CB |  |  |  | DNP | 542 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | 250 | #5SC(250) |  | SCA | [14 empty] | 0315 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.250_SCA | 23KV #5SC 51,51N RY | SC | D19/22/250/SCA |  |  |  | DNP | 543 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | 250 | #5SC(250) |  | UVA | [14 empty] | 0316 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.250_OUVA | 23KV #5SC 27,59RY(欠壓或過壓) | SC | D19/22/250/UVA |  |  |  | DNP | 544 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | 260 | #6SC(260) |  | CB | [14 empty] | 0317 |  | 0162 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.260_CB | 260(23KV #6SC) CB | SC | D19/22/260/CB |  |  |  | DNP | 545 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 22 | 22kV | 260 | #6SC(260) |  | SCA | [14 empty] | 0318 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.260_SCA | 23KV #6SC 51,51N RY | SC | D19/22/260/SCA |  |  |  | DNP | 546 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | 260 | #6SC(260) |  | UVA | [14 empty] | 0319 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.260_OUVA | 23KV #6SC 27,59RY(欠壓或過壓) | SC | D19/22/260/UVA |  |  |  | DNP | 547 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1611BUS | #1BUS |  | VUA | [14 empty] | 0999 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | D19/161/1BUS/BUS_VUA |  |  |  | DNP | 548 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1611BUS | #1BUS |  | 87A | [14 empty] | 0034 | [10 empty] | 161KV_N | [8 empty] | 糠榔DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | D19/161/1BUS/87A |  |  |  | DNP | 549 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1612BUS | #2BUS |  | VUA | [14 empty] | 1000 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | D19/161/2BUS/BUS_VUA |  |  |  | DNP | 550 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1612BUS | #2BUS |  | 87A | [14 empty] | 0035 | [10 empty] | 161KV_N | [8 empty] | 糠榔DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | D19/161/2BUS/87A |  |  |  | DNP | 551 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | 11_ | 11/ |  | CBA | [14 empty] | 1007 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | D19/22/ComPoint/CBA |  |  |  | DNP | 552 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | 11_ | 11/ |  | CBF | [14 empty] | 1008 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | D19/22/ComPoint/CBF |  |  |  | DNP | 553 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV |  |  |  | CBA | [14 empty] | 0995 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.161KV_CBA | 161KV斷路器重故障 | OTHER | D19/161/ComPoint/CBA |  |  |  | DNP | 554 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV |  |  |  | CBF | [14 empty] | 0996 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | D19/161/ComPoint/CBF |  |  |  | DNP | 555 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | LINE | LINE |  | RCA | [14 empty] | 0036 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | D19/161/ComPoint/RCA |  |  |  | DNP | 556 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | _SC | 11/ SC |  | 60A | [14 empty] | 1006 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.23KV_SC_60A | 11/23KV SC 60A | OTHER | D19/22/ComPoint/60A |  |  |  | DNP | 557 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | RTU | RTU |  | SupLocal | [14 empty] | 0513 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.RTU_S/L | RTU SUPY/LOCAL | OTHER | D19/0/RTU/RTU_R_L |  |  |  | DNP | 558 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D19 | 槺榔DS | 0 |  | TEST | TEST |  | CB | [14 empty] | 0512 |  | 0000 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.TEST_CB | TEST CB | OTHER | D19/0/RTU/Test_CB |  |  |  | DNP | 559 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  |  |  |  | Fire1 | [14 empty] | 0976 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | D19/0/StaDev/Fire1 |  |  |  | DNP | 560 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  |  |  |  | Fire2 | [14 empty] | 0977 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.火災警報(2) | 火災警報(2) | OTHER | D19/0/StaDev/Fire2 |  |  |  | DNP | 561 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  |  |  |  | Fire3 | [14 empty] | 0978 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.火災警報(3) | 火災警報(3) | OTHER | D19/0/StaDev/Fire3 |  |  |  | DNP | 562 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  |  |  |  | Fire4 | [14 empty] | 0979 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.火災警報(4) | 火災警報(4) | OTHER | D19/0/StaDev/Fire4 |  |  |  | DNP | 563 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  |  |  |  | 火災警報(5) | [14 empty] | 0980 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.火災警報(5) | 火災警報(5) | OTHER | D19/0/StaDev/Fire5 |  |  |  | DNP | 564 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  |  |  |  | OPA | [14 empty] | 0991 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | D19/0/ComPoint/OPA |  |  |  | DNP | 565 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  |  |  |  | 25PFA | [14 empty] | 0327 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER | D19/0/ComPoint/25PFA |  |  |  | DNP | 566 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  |  |  |  | 25TA | [14 empty] | 0326 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | D19/0/ComPoint/25TA |  |  |  | DNP | 567 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  |  |  |  | ACB1 | [14 empty] | 0988 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | D19/0/StaDev/ACB1 |  |  |  | DNP | 568 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ON/OFF | ON
D19 | 槺榔DS | 0 |  |  |  |  | ACB2 | [14 empty] | 0989 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | D19/0/StaDev/ACB2 |  |  |  | DNP | 569 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ON/OFF | ON
D19 | 槺榔DS | 0 |  |  |  |  | ACBA | [14 empty] | 0998 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.所內電源ACBA | 所內電源故障警報 | OTHER | D19/0/StaDev/ACBA |  |  |  | DNP | 570 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 所內電源開關ACB | 所內電源開關ACB |  | ACBT | [14 empty] | 0990 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | D19/0/StaDev/ACBT |  |  |  | DNP | 571 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ON/OFF | OFF
D19 | 槺榔DS | 0 |  |  |  |  | STUV | [14 empty] | 0992 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | D19/0/StaDev/STUV |  |  |  | DNP | 572 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  |  |  |  | CHG1 | [14 empty] | 1001 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.直流充電機故障 | 直流充電機故障 | OTHER | D19/0/StaDev/CHG1 |  |  |  | DNP | 573 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  |  |  |  | DCA | [14 empty] | 0997 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.直流電源DCA | 直流電源故障警報 | OTHER | D19/0/StaDev/DCA |  |  |  | DNP | 574 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  |  |  |  | DCE | [14 empty] | 1002 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.直流電源DCE | 直流電源接地故障警報 | OTHER | D19/0/StaDev/DCE |  |  |  | DNP | 575 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  |  |  |  | CHG2 | [14 empty] | 1012 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | D19/0/StaDev/CHG2 |  |  |  | DNP | 576 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  |  |  |  | CommACF | [14 empty] | 1013 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | D19/0/StaDev/CommACF |  |  |  | DNP | 577 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  |  |  |  | Door1 | [14 empty] | 0981 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.無人化門禁(1) | 無人化門禁(1)圍牆大門 | OTHER | D19/0/StaDev/Door1 |  |  |  | DNP | 578 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  |  |  |  | Door2 | [14 empty] | 0982 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.無人化門禁(2) | 無人化門禁(2)建築物大小門 | OTHER | D19/0/StaDev/Door2 |  |  |  | DNP | 579 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  |  |  |  | Door3 | [14 empty] | 0983 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.無人化門禁(3) | 無人化門禁(3)保全 | OTHER | D19/0/StaDev/Door3 |  |  |  | DNP | 580 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  |  |  |  | Lights1 | [14 empty] | 0986 |  | 0240 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.開關場照明(A) | 開關場照明(A) | OTHER | D19/0/StaDev/Lights1 |  |  |  | DNP | 581 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ON/OFF | OFF
D19 | 槺榔DS | 0 |  |  |  |  | Lights2 | [14 empty] | 0987 |  | 0241 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.開關場照明(B) | 開關場照明(B) | OTHER | D19/0/StaDev/Lights2 |  |  |  | DNP | 582 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ON/OFF | OFF
D19 | 槺榔DS | 0 |  | 1DTR | #1DTR |  | 50_51NUL | [14 empty] | 0534 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#1DTR_50/51NUL | #1DTR 50/50N/51/51N RY U/L | OTHER | D19//1DTR/PHA |  |  |  | DNP | 583 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 0 |  | 1DTR | #1DTR |  | 51Z_UL | [14 empty] | 0535 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#1DTR_51ZUL | #1DTR 51Z RY U/L | OTHER | D19//1DTR/DTR_86A |  |  |  | DNP | 584 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 0 |  | 1DTR | #1DTR |  | DTR_86A | [14 empty] | 0054 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#1DTR_86A | #1DTR 86(50/50N/51Z/87/96)RY | OTHER | D19/161/1750/DTR_86A |  |  |  | DNP | 585 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 1DTR | #1DTR |  | RYFA | [14 empty] | 0594 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#1DTR_RYFA | #1DTR 數位電驛故障 | OTHER | D19//1DTR/RYFA |  |  |  | DNP | 586 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 2DTR | #2DTR |  | 50_51NUL | [14 empty] | 0548 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#2DTR_50/51NUL | #2DTR 50/50N/51/51N RY U/L | OTHER | D19//2DTR/PHA |  |  |  | DNP | 587 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 0 |  | 2DTR | #2DTR |  | 51Z_UL | [14 empty] | 0549 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#2DTR_51ZUL | #2DTR 51Z RY U/L | OTHER | D19//2DTR/DTR_86A |  |  |  | DNP | 588 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 0 |  | 2DTR | #2DTR |  | DTR_86A | [14 empty] | 0069 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#2DTR_86A | #2DTR 86(50/50N/51Z/87/96)RY | OTHER | D19/161/1760/DTR_86A |  |  |  | DNP | 589 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 2DTR | #2DTR |  | RYFA | [14 empty] | 0595 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#2DTR_RYFA | #2DTR 數位電驛故障 | OTHER | D19//2DTR/RYFA |  |  |  | DNP | 590 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 3DTR | #3DTR |  | 50_51NUL | [14 empty] | 0560 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#3DTR_50/51NUL | #3DTR 50/50N/51/51N RY U/L | OTHER | D19//3DTR/PHA |  |  |  | DNP | 591 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 0 |  | 3DTR | #3DTR |  | 51Z_UL | [14 empty] | 0561 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#3DTR_51ZUL | #3DTR 51Z RY U/L | OTHER | D19//3DTR/DTR_86A |  |  |  | DNP | 592 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 0 |  | 3DTR | #3DTR |  | DTR_86A | [14 empty] | 0080 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#3DTR_86A | #3DTR 86(50/50N/51Z/87/96)RY | OTHER | D19/161/1770/DTR_86A |  |  |  | DNP | 593 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 3DTR | #3DTR |  | RYFA | [14 empty] | 0596 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#3DTR_RYFA | #3DTR 數位電驛故障 | OTHER | D19//3DTR/RYFA |  |  |  | DNP | 594 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | 11_ | 11/ |  | LOA | [14 empty] | 1009 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.11/23KV_LOA | 11/23KV饋線復閉失敗閉鎖 | OTHER | D19/22/ComPoint/LOA |  |  |  | DNP | 595 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 1510 | 太鐵糠榔一路(1510) |  | 87CFA | [14 empty] | 0576 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.1510_87CFA | 太鐵糠榔一路(1510)87RY通訊故障 | OTHER | D19/161/1510/87CFA |  |  |  | DNP | 596 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 1510 | 太鐵糠榔一路(1510) |  | RYFA | [14 empty] | 0577 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.1510_RYFA | 太鐵糠榔一路(1510)數位電驛故障 | OTHER | D19/161/1510/RYFA |  |  |  | DNP | 597 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 1520 | 太鐵糠榔二路(1520) |  | 87CFA | [14 empty] | 0578 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.1520_87CFA | 太鐵糠榔二路(1520)87RY通訊故障 | OTHER | D19/161/1520/87CFA |  |  |  | DNP | 598 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 1520 | 太鐵糠榔二路(1520) |  | RYFA | [14 empty] | 0579 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.1520_RYFA | 太鐵糠榔二路(1520)數位電驛故障 | OTHER | D19/161/1520/RYFA |  |  |  | DNP | 599 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | 1611BUS | #1BUS |  | 87UL | [14 empty] | 0530 |  | 0238 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | D19/161/1BUS/87UL |  |  |  | DNP | 600 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 161 | 161kV | 1612BUS | #2BUS |  | 87UL | [14 empty] | 0531 |  | 0239 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | D19/161/2BUS/87UL |  |  |  | DNP | 601 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 161 | 161kV | _BUS | BUS |  | 87CTFA | [14 empty] | 0592 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.161KV_BUS_CTFA | 161KV BUS CT 回路故障 | OTHER | D19/161/ComPoint/12B_CTFA |  |  |  | DNP | 602 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | _BUS | BUS |  | RYFA | [14 empty] | 0593 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | D19/161/ComPoint/BUS_RYFA |  |  |  | DNP | 603 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | _OSCA | _OSCA |  | 1 | [14 empty] | 0037 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.161KV_OSCA_1 | 161KV示波器啟動警報(1) | OTHER | D19/161/ComPoint/OSCA1 |  |  |  | DNP | 604 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | _OSCA | _OSCA | [16 empty] | 0038 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.161KV_OSCA_2 | 161KV示波器啟動警報(2) | OTHER | D19/161/ComPoint/OSCA2 |  |  |  | DNP | 605 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | _OSCA | _OSCA |  | 3 | [14 empty] | 0039 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.161KV_OSCA_3 | 161KV示波器啟動警報(3) | OTHER | D19/161/ComPoint/OSCA |  |  |  | DNP | 606 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | _OSCF | _OSCF |  | 1 | [14 empty] | 0647 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.161KV_OSCF_1 | 161KV示波器故障/缺紙(1) | OTHER |  |  |  |  | DNP | 607 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 161 | 161kV | _OSCF | _OSCF | [16 empty] | 0648 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.161KV_OSCF_2 | 161KV示波器故障/缺紙(2) | OTHER |  |  |  |  | DNP | 608 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 310 | #1DTR(310) |  | 81A | [14 empty] | 0058 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.310_81A | 310 #1DTR(A) 81RY動作 | OTHER | D19/11/310/81A |  |  |  | DNP | 609 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 310 | #1DTR(310) |  | 81UL | [14 empty] | 0896 |  | 0176 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.310_81UL | 310 #1DTR(A) 81RY U/L | OTHER | D19/11/310/81UL |  |  |  | DNP | 610 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 0 |  | 310 | #1DTR(310) |  | GDA | [14 empty] | 0057 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.310_GDA | 310開關箱IED RY GDA | OTHER | D19/11/310/GDA |  |  |  | DNP | 611 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 320 | #1DTR(320) |  | 81A | [14 empty] | 0062 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.320_81A | 320 #1DTR(B) 81RY動作 | OTHER | D19/11/320/81A |  |  |  | DNP | 612 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 320 | #1DTR(320) |  | 81UL | [14 empty] | 0909 |  | 0177 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.320_81UL | 320 #1DTR(B) 81RY U/L | OTHER | D19/11/320/81UL |  |  |  | DNP | 613 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 0 |  | 320 | #1DTR(320) |  | GDA | [14 empty] | 0061 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.320_GDA | 320開關箱IED RY GDA | OTHER | D19/11/320/GDA |  |  |  | DNP | 614 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 330 | #2DTR(330) |  | 81A | [14 empty] | 0073 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.330_81A | 330 #2DTR 81RY動作 | OTHER | D19/22/330/81A |  |  |  | DNP | 615 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 330 | #2DTR(330) |  | 81UL | [14 empty] | 0922 |  | 0178 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.330_81UL | 330 #2DTR 81RY U/L | OTHER | D19/22/330/81UL |  |  |  | DNP | 616 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 0 |  | 330 | #2DTR(330) |  | GDA | [14 empty] | 0072 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.330_GDA | 330開關箱IED RY GDA | OTHER | D19/22/330/GDA |  |  |  | DNP | 617 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 350 | #3DTR(350) |  | 81A | [14 empty] | 0084 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.350_81A | 350 #3DTR 81RY動作 | OTHER | D19/22/350/81A |  |  |  | DNP | 618 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 350 | #3DTR(350) |  | 81UL | [14 empty] | 0941 |  | 0179 | [8 empty] | ADCS_N | [8 empty] | 糠榔DS.350_81UL | 350 #3DTR 81RY U/L | OTHER | D19/22/350/81UL |  |  |  | DNP | 619 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | USE/LOCK | USE
D19 | 槺榔DS | 0 |  | 350 | #3DTR(350) |  | GDA | [14 empty] | 0083 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.350_GDA | 350開關箱IED RY GDA | OTHER | D19/22/350/GDA |  |  |  | DNP | 620 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO21 | 糠21線(JO21) |  | 81A | [14 empty] | 0195 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO21_81A | 11KV糠21線(JO21) 81RY | OTHER | D19/11/JO21/81A |  |  |  | DNP | 621 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO22 | 糠22線(JO22) |  | 81A | [14 empty] | 0199 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO22_81A | 11KV糠22線(JO22) 81RY | OTHER | D19/11/JO22/81A |  |  |  | DNP | 622 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO23 | 糠23線(JO23) |  | 81A | [14 empty] | 0203 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO23_81A | 11KV糠23線(JO23) 81RY | OTHER | D19/11/JO23/81A |  |  |  | DNP | 623 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO24 | 糠24線(JO24) |  | 81A | [14 empty] | 0207 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO24_81A | 11KV糠24線(JO24) 81RY | OTHER | D19/11/JO24/81A |  |  |  | DNP | 624 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO25 | 糠25線(JO25) |  | 81A | [14 empty] | 0211 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO25_81A | 11KV糠25線(JO25) 81RY | OTHER | D19/11/JO25/81A |  |  |  | DNP | 625 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO26 | 糠26線(JO26) |  | 81A | [14 empty] | 0221 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO26_81A | 11KV糠26線(JO26) 81RY | OTHER | D19/11/JO26/81A |  |  |  | DNP | 626 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO27 | 糠27線(JO27) |  | 81A | [14 empty] | 0225 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO27_81A | 11KV糠27線(JO27) 81RY | OTHER | D19/11/JO27/81A |  |  |  | DNP | 627 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO28 | 糠28線(JO28) |  | 81A | [14 empty] | 0229 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO28_81A | 11KV糠28線(JO28) 81RY | OTHER | D19/11/JO28/81A |  |  |  | DNP | 628 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO29 | 糠29線(JO29) |  | 81A | [14 empty] | 0233 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO29_81A | 11KV糠29線(JO29) 81RY | OTHER | D19/11/JO29/81A |  |  |  | DNP | 629 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | JO30 | 糠30線(JO30) |  | 81A | [14 empty] | 0237 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO30_81A | 11KV糠30線(JO30) 81RY | OTHER | D19/11/JO30/81A |  |  |  | DNP | 630 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO61 | 糠61線(JO61) |  | 81A | [14 empty] | 0244 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO61_81A | 23KV糠61線(JO61) 81RY | OTHER | D19/22/JO61/81A |  |  |  | DNP | 631 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO62 | 糠62線(JO62) |  | 81A | [14 empty] | 0248 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO62_81A | 23KV糠62線(JO62) 81RY | OTHER | D19/22/JO62/81A |  |  |  | DNP | 632 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO63 | 糠63線(JO63) |  | 81A | [14 empty] | 0252 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO63_81A | 23KV糠63線(JO63) 81RY | OTHER | D19/22/JO63/81A |  |  |  | DNP | 633 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO64 | 糠64線(JO64) |  | 81A | [14 empty] | 0256 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO64_81A | 23KV糠64線(JO64) 81RY | OTHER | D19/22/JO64/81A |  |  |  | DNP | 634 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO65 | 糠65線(JO65) |  | 81A | [14 empty] | 0260 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO65_81A | 23KV糠65線(JO65) 81RY | OTHER | D19/22/JO65/81A |  |  |  | DNP | 635 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO66 | 糠66線(JO66) |  | 81A | [14 empty] | 0264 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO66_81A | 23KV糠66線(JO66) 81RY | OTHER | D19/22/JO66/81A |  |  |  | DNP | 636 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO67 | 糠67線(JO67) |  | 81A | [14 empty] | 0268 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO67_81A | 23KV糠67線(JO67) 81RY | OTHER | D19/22/JO67/81A |  |  |  | DNP | 637 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO68 | 糠68線(JO68) |  | 81A | [14 empty] | 0272 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO68_81A | 23KV糠68線(JO68) 81RY | OTHER | D19/22/JO68/81A |  |  |  | DNP | 638 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO71 | 糠71線(JO71) |  | 81A | [14 empty] | 0285 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO71_81A | 23KV糠71線(JO71) 81RY | OTHER | D19/22/JO71/81A |  |  |  | DNP | 639 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO72 | 糠72線(JO72) |  | 81A | [14 empty] | 0289 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO72_81A | 23KV糠72線(JO72) 81RY | OTHER | D19/22/JO72/81A |  |  |  | DNP | 640 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO73 | 糠73線(JO73) |  | 81A | [14 empty] | 0293 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO73_81A | 23KV糠73線(JO73) 81RY | OTHER | D19/22/JO73/81A |  |  |  | DNP | 641 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO74 | 糠74線(JO74) |  | 81A | [14 empty] | 0297 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO74_81A | 23KV糠74線(JO74) 81RY | OTHER | D19/22/JO74/81A |  |  |  | DNP | 642 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO75 | 糠75線(JO75) |  | 81A | [14 empty] | 0301 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO75_81A | 23KV糠75線(JO75) 81RY | OTHER | D19/22/JO75/81A |  |  |  | DNP | 643 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO76 | 糠76線(JO76) |  | 81A | [14 empty] | 0305 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO76_81A | 23KV糠76線(JO76) 81RY | OTHER | D19/22/JO76/81A |  |  |  | DNP | 644 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO77 | 糠77線(JO77) |  | 81A | [14 empty] | 0309 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO77_81A | 23KV糠77線(JO77) 81RY | OTHER | D19/22/JO77/81A |  |  |  | DNP | 645 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 22 | 22kV | JO78 | 糠78線(JO78) |  | 81A | [14 empty] | 0313 | [10 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO78_81A | 23KV糠78線(JO78) 81RY | OTHER | D19/22/JO78/81A |  |  |  | DNP | 646 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  |  |  |  | PMA | [14 empty] | 1023 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.PMA | 電力量測表計故障 | OTHER | D19/0/StaDev/PMA |  |  |  | DNP | 647 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  |  |  |  | 水位警報(1) | [14 empty] | 0993 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.水位警報(1) | 地下室水位警報(1) | OTHER | D19/0/StaDev/Water1 |  |  |  | DNP | 648 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  |  |  |  | 水位警報(2) | [14 empty] | 0994 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.水位警報(2) | 地下室水位警報(2) | OTHER | D19/0/StaDev/Water2 |  |  |  | DNP | 649 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 通信機房溫度 | 通信機房溫度 |  | 1 | [14 empty] | 1005 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.通信機房溫度_1 | 電驛室溫度警報 | OTHER | D19/0/StaDev/R_Temp1 |  |  |  | DNP | 650 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 通信機房溫度 | 通信機房溫度 | [16 empty] | 1016 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.通信機房溫度_2 | 通訊室或控制室溫度警報 | OTHER | D19/0/StaDev/R_Temp2 |  |  |  | DNP | 651 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  |  |  |  | 無人化門禁(4) | [14 empty] | 0984 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.無人化門禁(4) | 無人化門禁(4) | OTHER | D19/0/StaDev/Door4 |  |  |  | DNP | 652 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  |  |  |  | 無人化門禁(5) | [14 empty] | 0985 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.無人化門禁(5) | 無人化門禁(5) | OTHER | D19/0/StaDev/Door5 |  |  |  | DNP | 653 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  |  |  |  | 集油池警報(1) | [14 empty] | 1003 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.集油池警報(1) | 蓄油池中水位警報 | OTHER | D19/0/StaDev/OilLeak1 |  |  |  | DNP | 654 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  |  |  |  | 集油池警報(2) | [14 empty] | 1004 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.集油池警報(2) | 蓄油池高水位警報 | OTHER | D19/0/StaDev/OilLeak2 |  |  |  | DNP | 655 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  |  |  |  | GEN | [14 empty] | 0975 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.GEN | 緊急發電機運轉 | OTHER | D19/0/StaDev/1A5Other |  |  |  | DNP | 656 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ON/OFF | OFF
D19 | 槺榔DS | 0 |  | 1DTR | #1DTR |  | GDA | [14 empty] | 0053 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#1DTR_GDA | #1DTR 50N/51N RY | OTHER | D19/161/1750/GDA |  |  |  | DNP | 657 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 1DTR | #1DTR |  | PHA | [14 empty] | 0052 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#1DTR_PHA | #1DTR 50/51 RY | OTHER | D19/161/1750/PHA |  |  |  | DNP | 658 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 2DTR | #2DTR |  | GDA | [14 empty] | 0068 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#2DTR_GDA | #2DTR 50N/51N RY | OTHER | D19/161/1760/GDA |  |  |  | DNP | 659 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 2DTR | #2DTR |  | PHA | [14 empty] | 0067 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#2DTR_PHA | #2DTR 50/51 RY | OTHER | D19/161/1760/PHA |  |  |  | DNP | 660 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 3DTR | #3DTR |  | GDA | [14 empty] | 0079 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#3DTR_GDA | #3DTR 50N/51N RY | OTHER | D19/161/1770/GDA |  |  |  | DNP | 661 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | 3DTR | #3DTR |  | PHA | [14 empty] | 0078 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.#3DTR_PHA | #3DTR 50/51 RY | OTHER | D19/161/1770/PHA |  |  |  | DNP | 662 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D19 | 槺榔DS | 0 |  | OLTC | OLTC |  | OLTCA | [14 empty] | 0571 | [10 empty] | ADCS_N | [8 empty] | 糠榔DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | D19/0/ComPoint/OLTC_A |  |  |  | DNP | 663 | DNPDIPoint | DS057 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D19 | 槺榔DS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 664 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 11 | 11kV | 220_SC | #2SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 665 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 22 | 22kV | 230_SC | #3SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.230_SC_CAP | 23KV#3SC 容量 | SC | [5 empty] | 666 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 22 | 22kV | 240_SC | #4SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.240_SC_CAP | 23KV#4SC 容量 | SC | [5 empty] | 667 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 22 | 22kV | 250_SC | #5SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.250_SC_CAP | 23KV#5SC 容量 | SC | [5 empty] | 668 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 22 | 22kV | 260_SC | #6SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 糠榔DS.260_SC_CAP | 23KV#6SC 容量 | SC | [5 empty] | 669 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D19 | 槺榔DS | 161 | 161kV | 1510 | 太鐵糠榔一路(1510) |  | LE0 | 1510LE | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.1510LE | 1510LE (非取樣點) | LINE161 | D19/161/1510/LE0 |  |  |  |  | 670 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 161 | 161kV | 1510 | 太鐵糠榔一路(1510) |  | BE0 | 1510BE | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.1510BE | 1510BE (非取樣點) | LINE161 | D19/161/1510/BE0 |  |  |  |  | 671 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 161 | 161kV | 1520 | 太鐵糠榔二路(1520) |  | LE0 | 1520LE | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.1520LE | 1520LE (非取樣點) | LINE161 | D19/161/1520/LE0 |  |  |  |  | 672 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 161 | 161kV | 1520 | 太鐵糠榔二路(1520) |  | BE0 | 1520BE | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.1520BE | 1520BE (非取樣點) | LINE161 | D19/161/1520/BE0 |  |  |  |  | 673 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | JO21 | JO21_DS |  | DS1 | JO21_DS | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO21_DS | JO21_DS (非取樣點) | FEEDER | D19/11/JO21/DS |  |  |  |  | 674 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | JO21 | JO21_ES |  | LE0 | JO21_ES | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO21_ES | JO21_ES (非取樣點) | FEEDER | D19/11/JO21/ES |  |  |  |  | 675 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | JO22 | JO22_DS |  | DS1 | JO22_DS | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO22_DS | JO22_DS (非取樣點) | FEEDER | D19/11/JO22/DS |  |  |  |  | 676 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | JO22 | JO22_ES |  | LE0 | JO22_ES | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO22_ES | JO22_ES (非取樣點) | FEEDER | D19/11/JO22/ES |  |  |  |  | 677 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | JO23 | JO23_DS |  | DS1 | JO23_DS | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO23_DS | JO23_DS (非取樣點) | FEEDER | D19/11/JO23/DS |  |  |  |  | 678 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | JO23 | JO23_ES |  | LE0 | JO23_ES | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO23_ES | JO23_ES (非取樣點) | FEEDER | D19/11/JO23/ES |  |  |  |  | 679 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | JO24 | JO24_DS |  | DS1 | JO24_DS | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO24_DS | JO24_DS (非取樣點) | FEEDER | D19/11/JO24/DS |  |  |  |  | 680 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | JO24 | JO24_ES |  | LE0 | JO24_ES | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO24_ES | JO24_ES (非取樣點) | FEEDER | D19/11/JO24/ES |  |  |  |  | 681 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | JO25 | JO25_DS |  | DS1 | JO25_DS | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO25_DS | JO25_DS (非取樣點) | FEEDER | D19/11/JO25/DS |  |  |  |  | 682 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | JO25 | JO25_ES |  | LE0 | JO25_ES | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO25_ES | JO25_ES (非取樣點) | FEEDER | D19/11/JO25/ES |  |  |  |  | 683 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | JO26 | JO26_DS |  | DS1 | JO26_DS | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO26_DS | JO26_DS (非取樣點) | FEEDER | D19/11/JO26/DS |  |  |  |  | 684 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | JO26 | JO26_ES |  | LE0 | JO26_ES | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO26_ES | JO26_ES (非取樣點) | FEEDER | D19/11/JO26/ES |  |  |  |  | 685 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | JO27 | JO27_DS |  | DS1 | JO27_DS | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO27_DS | JO27_DS (非取樣點) | FEEDER | D19/11/JO27/DS |  |  |  |  | 686 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | JO27 | JO27_ES |  | LE0 | JO27_ES | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO27_ES | JO27_ES (非取樣點) | FEEDER | D19/11/JO27/ES |  |  |  |  | 687 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | JO28 | JO28_DS |  | DS1 | JO28_DS | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO28_DS | JO28_DS (非取樣點) | FEEDER | D19/11/JO28/DS |  |  |  |  | 688 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | JO28 | JO28_ES |  | LE0 | JO28_ES | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO28_ES | JO28_ES (非取樣點) | FEEDER | D19/11/JO28/ES |  |  |  |  | 689 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | JO29 | JO29_DS |  | DS1 | JO29_DS | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO29_DS | JO29_DS (非取樣點) | FEEDER | D19/11/JO29/DS |  |  |  |  | 690 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | JO29 | JO29_ES |  | LE0 | JO29_ES | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO29_ES | JO29_ES (非取樣點) | FEEDER | D19/11/JO29/ES |  |  |  |  | 691 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | JO30 | JO30_DS |  | DS1 | JO30_DS | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO30_DS | JO30_DS (非取樣點) | FEEDER | D19/11/JO30/DS |  |  |  |  | 692 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | JO30 | JO30_ES |  | LE0 | JO30_ES | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO30_ES | JO30_ES (非取樣點) | FEEDER | D19/11/JO30/ES |  |  |  |  | 693 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | JO61 | JO61_DS |  | DS1 | JO61_DS | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO61_DS | JO61_DS (非取樣點) | FEEDER | D19/22/JO61/DS |  |  |  |  | 694 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | JO61 | JO61_ES |  | LE0 | JO61_ES | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO61_ES | JO61_ES (非取樣點) | FEEDER | D19/22/JO61/ES |  |  |  |  | 695 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | JO62 | JO62_DS |  | DS1 | JO62_DS | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO62_DS | JO62_DS (非取樣點) | FEEDER | D19/22/JO62/DS |  |  |  |  | 696 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | JO62 | JO62_ES |  | LE0 | JO62_ES | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO62_ES | JO62_ES (非取樣點) | FEEDER | D19/22/JO62/ES |  |  |  |  | 697 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | JO63 | JO63_DS |  | DS1 | JO63_DS | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO63_DS | JO63_DS (非取樣點) | FEEDER | D19/22/JO63/DS |  |  |  |  | 698 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | JO63 | JO63_ES |  | LE0 | JO63_ES | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO63_ES | JO63_ES (非取樣點) | FEEDER | D19/22/JO63/ES |  |  |  |  | 699 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | JO64 | JO64_DS |  | DS1 | JO64_DS | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO64_DS | JO64_DS (非取樣點) | FEEDER | D19/22/JO64/DS |  |  |  |  | 700 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | JO64 | JO64_ES |  | LE0 | JO64_ES | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO64_ES | JO64_ES (非取樣點) | FEEDER | D19/22/JO64/ES |  |  |  |  | 701 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | JO65 | JO65_DS |  | DS1 | JO65_DS | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO65_DS | JO65_DS (非取樣點) | FEEDER | D19/22/JO65/DS |  |  |  |  | 702 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | JO65 | JO65_ES |  | LE0 | JO65_ES | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO65_ES | JO65_ES (非取樣點) | FEEDER | D19/22/JO65/ES |  |  |  |  | 703 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | JO66 | JO66_DS |  | DS1 | JO66_DS | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO66_DS | JO66_DS (非取樣點) | FEEDER | D19/22/JO66/DS |  |  |  |  | 704 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | JO66 | JO66_ES |  | LE0 | JO66_ES | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO66_ES | JO66_ES (非取樣點) | FEEDER | D19/22/JO66/ES |  |  |  |  | 705 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | JO67 | JO67_DS |  | DS1 | JO67_DS | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO67_DS | JO67_DS (非取樣點) | FEEDER | D19/22/JO67/DS |  |  |  |  | 706 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | JO67 | JO67_ES |  | LE0 | JO67_ES | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO67_ES | JO67_ES (非取樣點) | FEEDER | D19/22/JO67/ES |  |  |  |  | 707 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | JO68 | JO68_DS |  | DS1 | JO68_DS | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO68_DS | JO68_DS (非取樣點) | FEEDER | D19/22/JO68/DS |  |  |  |  | 708 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | JO68 | JO68_ES |  | LE0 | JO68_ES | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO68_ES | JO68_ES (非取樣點) | FEEDER | D19/22/JO68/ES |  |  |  |  | 709 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | JO71 | JO71_DS |  | DS1 | JO71_DS | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO71_DS | JO71_DS (非取樣點) | FEEDER | D19/22/JO71/DS |  |  |  |  | 710 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | JO71 | JO71_ES |  | LE0 | JO71_ES | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO71_ES | JO71_ES (非取樣點) | FEEDER | D19/22/JO71/ES |  |  |  |  | 711 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | JO72 | JO72_DS |  | DS1 | JO72_DS | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO72_DS | JO72_DS (非取樣點) | FEEDER | D19/22/JO72/DS |  |  |  |  | 712 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | JO72 | JO72_ES |  | LE0 | JO72_ES | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO72_ES | JO72_ES (非取樣點) | FEEDER | D19/22/JO72/ES |  |  |  |  | 713 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | JO73 | JO73_DS |  | DS1 | JO73_DS | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO73_DS | JO73_DS (非取樣點) | FEEDER | D19/22/JO73/DS |  |  |  |  | 714 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | JO73 | JO73_ES |  | LE0 | JO73_ES | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO73_ES | JO73_ES (非取樣點) | FEEDER | D19/22/JO73/ES |  |  |  |  | 715 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | JO74 | JO74_DS |  | DS1 | JO74_DS | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO74_DS | JO74_DS (非取樣點) | FEEDER | D19/22/JO74/DS |  |  |  |  | 716 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | JO74 | JO74_ES |  | LE0 | JO74_ES | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO74_ES | JO74_ES (非取樣點) | FEEDER | D19/22/JO74/ES |  |  |  |  | 717 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | JO75 | JO75_DS |  | DS1 | JO75_DS | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO75_DS | JO75_DS (非取樣點) | FEEDER | D19/22/JO75/DS |  |  |  |  | 718 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | JO75 | JO75_ES |  | LE0 | JO75_ES | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO75_ES | JO75_ES (非取樣點) | FEEDER | D19/22/JO75/ES |  |  |  |  | 719 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | JO76 | JO76_DS |  | DS1 | JO76_DS | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO76_DS | JO76_DS (非取樣點) | FEEDER | D19/22/JO76/DS |  |  |  |  | 720 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | JO76 | JO76_ES |  | LE0 | JO76_ES | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO76_ES | JO76_ES (非取樣點) | FEEDER | D19/22/JO76/ES |  |  |  |  | 721 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | JO77 | JO77_DS |  | DS1 | JO77_DS | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO77_DS | JO77_DS (非取樣點) | FEEDER | D19/22/JO77/DS |  |  |  |  | 722 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | JO77 | JO77_ES |  | LE0 | JO77_ES | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO77_ES | JO77_ES (非取樣點) | FEEDER | D19/22/JO77/ES |  |  |  |  | 723 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | JO78 | JO78_DS |  | DS1 | JO78_DS | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO78_DS | JO78_DS (非取樣點) | FEEDER | D19/22/JO78/DS |  |  |  |  | 724 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | JO78 | JO78_ES |  | LE0 | JO78_ES | [24 empty] | DDCS2_2 | [8 empty] | 糠榔DS.JO78_ES | JO78_ES (非取樣點) | FEEDER | D19/22/JO78/ES |  |  |  |  | 725 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | 100 | TIE(100) |  | E1 | 101E | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.101E | 101E (非取樣點) | TIE | D19/11/100/E1 |  |  |  |  | 726 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | 100 | TIE(100) |  | E2 | 102E | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.102E | 102E (非取樣點) | TIE | D19/11/100/E2 |  |  |  |  | 727 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | 101 | 101 |  | 101 | 101 | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.101 | 101 (非取樣點) | TIE | D19/11/100/D1 |  |  |  |  | 728 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | 102 | 102 |  | 102 | 102 | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.102 | 102 (非取樣點) | TIE | D19/11/100/D2 |  |  |  |  | 729 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.1501E | 1501E (非取樣點) | TIE | [5 empty] | 730 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.1502E | 1502E (非取樣點) | TIE | [5 empty] | 731 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | 200 | TIE(200) |  | E1 | 201E | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.201E | 201E (非取樣點) | TIE | D19/22/200/E1 |  |  |  |  | 732 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | 200 | TIE(200) |  | E2 | 202E | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.202E | 202E (非取樣點) | TIE | D19/22/200/E2 |  |  |  |  | 733 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | 201 | 201 |  | 201 | 201 | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.201 | 201 (非取樣點) | TIE | D19/22/200/D1 |  |  |  |  | 734 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | 202 | 202 |  | 202 | 202 | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.202 | 202 (非取樣點) | TIE | D19/22/200/D2 |  |  |  |  | 735 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | 391 | 391 |  | 391 | 391 | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.391 | 391 (非取樣點) | OTHER | D19/22/390/D1 |  |  |  |  | 736 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | 391E | 391E |  | 391E | 391E | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.391E | 391E (非取樣點) | OTHER | D19/22/390/E1 |  |  |  |  | 737 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | 491 | 491 |  | 491 | 491 | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.491 | 491 (非取樣點) | OTHER | D19/22/490/D1 |  |  |  |  | 738 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | 491E | 491E |  | 491E | 491E | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.491E | 491E (非取樣點) | OTHER | D19/22/490/E1 |  |  |  |  | 739 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | 1750TE | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.1750TE | 1750TE (非取樣點) | MTR | D19/161/1750/TE0 |  |  |  |  | 740 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | 1750BE | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.1750BE | 1750BE (非取樣點) | MTR | D19/161/1750/BE0 |  |  |  |  | 741 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | 311 | 311 |  | 311 | 311 | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.311 | 311 (非取樣點) | MTR | D19/11/310/D1 |  |  |  |  | 742 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | 310 | #1DTR(310) |  | E1 | 311E | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.311E | 311E (非取樣點) | MTR | D19/11/310/E1 |  |  |  |  | 743 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | 321 | 321 |  | 321 | 321 | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.321 | 321 (非取樣點) | MTR | D19/11/320/D1 |  |  |  |  | 744 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | 320 | #1DTR(320) |  | E1 | 321E | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.321E | 321E (非取樣點) | MTR | D19/11/320/E1 |  |  |  |  | 745 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | 1760TE | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.1760TE | 1760TE (非取樣點) | MTR | D19/161/1760/TE0 |  |  |  |  | 746 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | 1760BE | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.1760BE | 1760BE (非取樣點) | MTR | D19/161/1760/BE0 |  |  |  |  | 747 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | 331 | 331 |  | 331 | 331 | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.331 | 331 (非取樣點) | MTR | D19/22/330/D1 |  |  |  |  | 748 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | 330 | #2DTR(330) |  | E1 | 331E | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.331E | 331E (非取樣點) | MTR | D19/22/330/E1 |  |  |  |  | 749 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | 1770TE | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.1770TE | 1770TE (非取樣點) | MTR | D19/161/1770/TE0 |  |  |  |  | 750 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | 1770BE | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.1770BE | 1770BE (非取樣點) | MTR | D19/161/1770/BE0 |  |  |  |  | 751 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | 351 | 351 |  | 351 | 351 | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.351 | 351 (非取樣點) | MTR | D19/22/350/D1 |  |  |  |  | 752 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | 350 | #3DTR(350) |  | E1 | 351E | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.351E | 351E (非取樣點) | MTR | D19/22/350/E1 |  |  |  |  | 753 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | 211E | 211E |  | 211E | 211E | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.211E | 211E (非取樣點) | SC | D19/11/210/E1 |  |  |  |  | 754 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | 211 | 211 |  | 211 | 211 | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.211 | 211 (非取樣點) | SC | D19/11/210/D1 |  |  |  |  | 755 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | 221E | 221E |  | 221E | 221E | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.221E | 221E (非取樣點) | SC | D19/11/220/E1 |  |  |  |  | 756 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | 221 | 221 |  | 221 | 221 | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.221 | 221 (非取樣點) | SC | D19/11/220/D1 |  |  |  |  | 757 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | 231E | 231E |  | 231E | 231E | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.231E | 231E (非取樣點) | SC | D19/22/230/E1 |  |  |  |  | 758 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | 231 | 231 |  | 231 | 231 | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.231 | 231 (非取樣點) | SC | D19/22/230/D1 |  |  |  |  | 759 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | 241E | 241E |  | 241E | 241E | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.241E | 241E (非取樣點) | SC | D19/22/240/E1 |  |  |  |  | 760 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | 241 | 241 |  | 241 | 241 | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.241 | 241 (非取樣點) | SC | D19/22/240/D1 |  |  |  |  | 761 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | 251E | 251E |  | 251E | 251E | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.251E | 251E (非取樣點) | SC | D19/22/250/E1 |  |  |  |  | 762 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | 251 | 251 |  | 251 | 251 | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.251 | 251 (非取樣點) | SC | D19/22/250/D1 |  |  |  |  | 763 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | 261E | 261E |  | 261E | 261E | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.261E | 261E (非取樣點) | SC | D19/22/260/E1 |  |  |  |  | 764 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | 261 | 261 |  | 261 | 261 | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.261 | 261 (非取樣點) | SC | D19/22/260/D1 |  |  |  |  | 765 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | 15B1E | 15B1E |  | BE1 | 15B1E | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.15B1E | 15B1E (非取樣點) | BUS | D19/161/161B1E/BE1 |  |  |  |  | 766 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | 15B2E | 15B2E |  | BE2 | 15B2E | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.15B2E | 15B2E (非取樣點) | BUS | D19/161/161B2E/BE2 |  |  |  |  | 767 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 768 | NotelDIPoint | [38 empty] | START/STOP | STOP
D19 | 槺榔DS | 0 |  | 1ABUS | 1ABUS |  | PTD | 1ABUS_PTD | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.1ABUS_PTD | #1ABUS_PTD(非取樣點) | OTHER | [5 empty] | 769 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | 1ABUS | 1ABUS |  | PTE | 1ABUS_PTE | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.1ABUS_PTE | #1ABUS_PTE(非取樣點) | OTHER | [5 empty] | 770 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | 1BBUS | 1BBUS |  | PTD | 1BBUS_PTD | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.1BBUS_PTD | #1BBUS_PTD(非取樣點) | OTHER | [5 empty] | 771 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | 1BBUS | 1BBUS |  | PTE | 1BBUS_PTE | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.1BBUS_PTE | #1BBUS_PTE(非取樣點) | OTHER | [5 empty] | 772 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | 2BUS | 2BUS |  | PTD | 2BUS_PTD | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.2BUS_PTD | #2BUS_PTD(非取樣點) | OTHER | [5 empty] | 773 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | 2BUS | 2BUS |  | PTE | 2BUS_PTE | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.2BUS_PTE | #2BUS_PTE(非取樣點) | OTHER | [5 empty] | 774 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D19 | 槺榔DS | 0 |  | 3BUS | 3BUS |  | PTD | 3BUS_PTD | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.3BUS_PTD | #3BUS_PTD(非取樣點) | OTHER | [5 empty] | 775 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D19 | 槺榔DS | 0 |  | 3BUS | 3BUS |  | PTE | 3BUS_PTE | [24 empty] | ADCS_N | [8 empty] | 糠榔DS.3BUS_PTE | #3BUS_PTE(非取樣點) | OTHER | [5 empty] | 776 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo